## Sheet1
VERTICAL WALL MOUNTED AIR CONDITIONER SCHEDULE | [16 empty] | FILTERS |  |  | DOCUMENTATION
TAG | MODEL (MARVAIR) | NOMINAL SIZE (TONS) | CFM | TOTAL CAPACITY | SENSIBLE CAPACITY | OUTSIDE AIR (°F) | ENTERING AIR DB/WB (°F) | ELECTRIC HEAT (KW) | VOLTS-HZ-PH | MCA | MOCP | REFRIGERANT | EER | IEER | CONFIGURATION | OPTIONS FOR OUTSIDE AIR VENTILATION | TONS | ELECTRICAL | ELECTRIC HEAT | DATA SHEET | IOM
| MGH3090AA | 7.5 | 3500 | 89000 | 69092 | 95 | 80/67 | 0 | 208/60/1 | 54.5 | 60 | R-454B | 11.2 | 11.8 |  |  | 7.5 | 208/60/1 | 0 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3090AA | 7.5 | 3500 | 89000 | 69092 | 95 | 80/67 | 5 | 208/60/1 | 57.6 | 70 | R-454B | 11.2 | 11.8 |  |  | 7.5 | 208/60/1 | 5 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3090AA | 7.5 | 3500 | 89000 | 69092 | 95 | 80/67 | 10 | 208/60/1 | 83.7 | 90 | R-454B | 11.2 | 11.8 |  |  | 7.5 | 208/60/1 | 10 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3090AA | 7.5 | 3500 | 89000 | 69092 | 95 | 80/67 | 15 | 208/60/1 | 109.7 | 110 | R-454B | 11.2 | 11.8 |  |  | 7.5 | 208/60/1 | 15 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3090AC | 7.5 | 3500 | 89000 | 69092 | 95 | 80/67 | 0 | 208/60/3 | 38.5 | 40 | R-454B | 11.2 | 11.8 |  |  | 7.5 | 208/60/3 | 0 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3090AC | 7.5 | 3500 | 89000 | 69092 | 95 | 80/67 | 9 | 208/60/3 | 50.6 | 60 | R-454B | 11.2 | 11.8 |  |  | 7.5 | 208/60/3 | 9 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3090AC | 7.5 | 3500 | 89000 | 69092 | 95 | 80/67 | 15 | 208/60/3 | 68.7 | 70 | R-454B | 11.2 | 11.8 |  |  | 7.5 | 208/60/3 | 15 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3090AC | 7.5 | 3500 | 89000 | 69092 | 95 | 80/67 | 18 | 208/60/3 | 77.7 | 80 | R-454B | 11.2 | 11.8 |  |  | 7.5 | 208/60/3 | 18 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3090AD | 7.5 | 3500 | 89000 | 69092 | 95 | 80/67 | 0 | 460/60/3 | 21.4 | 25 | R-454B | 11.2 | 11.8 |  |  | 7.5 | 460/60/3 | 0 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3090AD | 7.5 | 3500 | 89000 | 69092 | 95 | 80/67 | 9 | 460/60/3 | 26.4 | 30 | R-454B | 11.2 | 11.8 |  |  | 7.5 | 460/60/3 | 9 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3090AD | 7.5 | 3500 | 89000 | 69092 | 95 | 80/67 | 15 | 460/60/3 | 35.4 | 40 | R-454B | 11.2 | 11.8 |  |  | 7.5 | 460/60/3 | 15 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3090AD | 7.5 | 3500 | 89000 | 69092 | 95 | 80/67 | 18 | 460/60/3 | 39.9 | 40 | R-454B | 11.2 | 11.8 |  |  | 7.5 | 460/60/3 | 18 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3120AA | 10 | 4000 | 118000 | 91706 | 95 | 80/67 | 0 | 208/60/1 | 82.3 | 90 | R-454B | 11.6 | 11.5 |  |  | 10 | 208/60/1 | 0 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3120AA | 10 | 4000 | 118000 | 91706 | 95 | 80/67 | 5 | 208/60/1 | 82.3 | 90 | R-454B | 11.6 | 11.5 |  |  | 10 | 208/60/1 | 5 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3120AA | 10 | 4000 | 118000 | 91706 | 95 | 80/67 | 10 | 208/60/1 | 102.9 | 110 | R-454B | 11.6 | 11.5 |  |  | 10 | 208/60/1 | 10 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3120AA | 10 | 4000 | 118000 | 91706 | 95 | 80/67 | 15 | 208/60/1 | 128.9 | 150 | R-454B | 11.6 | 11.5 |  |  | 10 | 208/60/1 | 15 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3120AC | 10 | 4000 | 118000 | 91706 | 95 | 80/67 | 0 | 208/60/3 | 57.5 | 60 | R-454B | 11.6 | 11.5 |  |  | 10 | 208/60/3 | 0 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3120AC | 10 | 4000 | 118000 | 91706 | 95 | 80/67 | 9 | 208/60/3 | 67.3 | 70 | R-454B | 11.6 | 11.5 |  |  | 10 | 208/60/3 | 9 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3120AC | 10 | 4000 | 118000 | 91706 | 95 | 80/67 | 15 | 208/60/3 | 85.4 | 90 | R-454B | 11.6 | 11.5 |  |  | 10 | 208/60/3 | 15 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3120AC | 10 | 4000 | 118000 | 91706 | 95 | 80/67 | 18 | 208/60/3 | 94.4 | 100 | R-454B | 11.6 | 11.5 |  |  | 10 | 208/60/3 | 18 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3120AD | 10 | 4000 | 118000 | 91706 | 95 | 80/67 | 0 | 460/60/3 | 28.5 | 30 | R-454B | 11.6 | 11.5 |  |  | 10 | 460/60/3 | 0 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3120AD | 10 | 4000 | 118000 | 91706 | 95 | 80/67 | 9 | 460/60/3 | 33.4 | 35 | R-454B | 11.6 | 11.5 |  |  | 10 | 460/60/3 | 9 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3120AD | 10 | 4000 | 118000 | 91706 | 95 | 80/67 | 15 | 460/60/3 | 42.4 | 45 | R-454B | 11.6 | 11.5 |  |  | 10 | 460/60/3 | 15 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3120AD | 10 | 4000 | 118000 | 91706 | 95 | 80/67 | 18 | 460/60/3 | 46.9 | 50 | R-454B | 11.6 | 11.5 |  |  | 10 | 460/60/3 | 18 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3150AC | 12.5 | 4500 | 146000 | 106434 | 95 | 80/67 | 0 | 208/60/3 | 81 | 90 | R-454B | 10.2 | 10.9 |  |  | 12.5 | 208/60/3 | 0 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3150AC | 12.5 | 4500 | 146000 | 106434 | 95 | 80/67 | 9 | 208/60/3 | 81 | 90 | R-454B | 10.2 | 10.9 |  |  | 12.5 | 208/60/3 | 9 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3150AC | 12.5 | 4500 | 146000 | 106434 | 95 | 80/67 | 15 | 208/60/3 | 97.1 | 110 | R-454B | 10.2 | 10.9 |  |  | 12.5 | 208/60/3 | 15 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3150AC | 12.5 | 4500 | 146000 | 106434 | 95 | 80/67 | 18 | 208/60/3 | 106.1 | 110 | R-454B | 10.2 | 10.9 |  |  | 12.5 | 208/60/3 | 18 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3150AD | 12.5 | 4500 | 146000 | 106434 | 95 | 80/67 | 0 | 460/60/3 | 35 | 35 | R-454B | 10.2 | 10.9 |  |  | 12.5 | 460/60/3 | 0 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3150AD | 12.5 | 4500 | 146000 | 106434 | 95 | 80/67 | 9 | 460/60/3 | 36.6 | 40 | R-454B | 10.2 | 10.9 |  |  | 12.5 | 460/60/3 | 9 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3150AD | 12.5 | 4500 | 146000 | 106434 | 95 | 80/67 | 15 | 460/60/3 | 45.6 | 50 | R-454B | 10.2 | 10.9 |  |  | 12.5 | 460/60/3 | 15 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3150AD | 12.5 | 4500 | 146000 | 106434 | 95 | 80/67 | 18 | 460/60/3 | 50.1 | 60 | R-454B | 10.2 | 10.9 |  |  | 12.5 | 460/60/3 | 18 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3180AC | 15 | 6000 | 182000 | 136830 | 95 | 80/67 | 0 | 208/60/3 | 100.4 | 110 | R-454B | 9.8 | 11.1 |  |  | 15 | 208/60/3 | 0 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3180AC | 15 | 6000 | 182000 | 136830 | 95 | 80/67 | 9 | 208/60/3 | 100.4 | 110 | R-454B | 9.8 | 11.1 |  |  | 15 | 208/60/3 | 9 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3180AC | 15 | 6000 | 182000 | 136830 | 95 | 80/67 | 15 | 208/60/3 | 112 | 125 | R-454B | 9.8 | 11.1 |  |  | 15 | 208/60/3 | 15 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3180AC | 15 | 6000 | 182000 | 136830 | 95 | 80/67 | 18 | 208/60/3 | 121 | 125 | R-454B | 9.8 | 11.1 |  |  | 15 | 208/60/3 | 18 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3180AD | 15 | 6000 | 182000 | 136830 | 95 | 80/67 | 0 | 460/60/3 | 47.7 | 50 | R-454B | 9.8 | 11.1 |  |  | 15 | 460/60/3 | 0 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3180AD | 15 | 6000 | 182000 | 136830 | 95 | 80/67 | 9 | 460/60/3 | 47.7 | 50 | R-454B | 9.8 | 11.1 |  |  | 15 | 460/60/3 | 9 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3180AD | 15 | 6000 | 182000 | 136830 | 95 | 80/67 | 15 | 460/60/3 | 54.6 | 60 | R-454B | 9.8 | 11.1 |  |  | 15 | 460/60/3 | 15 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
| MGH3180AD | 15 | 6000 | 182000 | 136830 | 95 | 80/67 | 18 | 460/60/3 | 59.1 | 60 | R-454B | 9.8 | 11.1 |  |  | 15 | 460/60/3 | 18 | MARVAIR MGH DATA SHEET | MARVAIR MGH IOM
COMMON TO ALL UNITS:
1- | Baked on finish over galvanneal steel outer panel |  |  |  |  | 8- | Internal motor overload protection
2- | Copper tube, aluminum fin evaporator & condenser coil |  |  |  |  | 9- | Dual high-efficiency scroll compressor
3- | High & low pressure switch |  |  |  |  | 10- | Thermal expansion valve
4- | Liquid line temperature monitoring & control |  |  |  |  | 11- | Low ambient control
5- | Adjustable short cycle protection |  |  |  |  | 12- | Factory installed disconnect
6- | Phase monitor (3-phase units only) |  |  |  |  | 13- | 2" MERV-8 filter
7- | High compressor temperature switch |  |  |  |  | 14- | Electric heat, if scheduled, shall be single point power
OPTIONS FOR OUTSIDE AIR VENTILATION:
1- | Factory installed economizer | [7 empty] | CONFIGURATION:
2- | 2-Position motorized fresh air damper w/ pressure relief ventilation | [7 empty] | 1- | Top supply
3- | 2-Position motorized fresh air damper w/ pressure relief ventilation & independent control | [7 empty] | 2- | Center Supply/Top Return
4- | No free cooling, 100% damper opening, emergency ventilation only w/ pressure relief & independent control
OPTIONAL ACCESSORIES:
1- | Coastal environmental package:
| - | Corrosion resistant fasteners
| - | Sealed or partially sealed condenser fan motor
| - | Insitu coating applied to all exposed internal copper and metal in the condenser section
| - | Protective coating on condenser coil
2- | All coat package:
| - | Corrosion resistant fasteners
| - | Sealed or partially sealed condenser fan motor
| - | Insitu coating applied to all exposed internal copper and metal in the condenser section
| - | Protective coating on condenser coil
| - | Impregnated polyurethane on evaporator coil and Insitu coating on all exterior and interior components and sheet metal
3- | Stainless steel exterior (replaces all standard exterior painted surfaces with stainless steel)
4- | Stainless steel unit (replaces all interior and exterior steel sheet metal parts with stainless steel)
5- | Dirty filter indicator
6- | Fresh air damper (field installed on either the left or right hand side of the unit)
7- | Filter access from the return air opening
8- | Freeze sensor
9- | Hot gas bypass