## Multi Position Splits
MULTI POSITION SPLIT SYSTEM SCHEDULE | [29 empty] | NOTES
INDOOR AIR HANDLING UNIT | [16 empty] | OUTDOOR CONDENSING UNIT
TAG | MODEL (DAIKIN) | SUPPLY FAN |  |  | COOLING |  |  |  |  | HEAT PUMP TOTAL CAPACITY | AUX. ELECTRIC HEAT |  | ELECTRICAL DATA |  |  | WEIGHT | TAG | MODEL (DAIKIN) | HEAT PUMP HEATING DATA |  |  | ELECTRICAL DATA |  |  | OUTDOOR AMBIENT (COOLING) | REFRIGERANT | EFFICIENCY | WEIGHT | COMPRESSOR STAGES |  | FILTERS | [6 empty] | DOCUMENTATION
|  | AIRFLOW (CFM) | MOTOR (HP) | MOTOR TYPE | EAT (DB) | EAT (WB) | LAT (DB) | TOTAL CAPACITY | SENSIBLE CAPACITY |  | kW | TEMPERATURE RISE (DB) | VOLTAGE / PHASE | MCA | MOP |  |  |  | OUTDOOR AMBIENT (DB) | TOTAL CAPACITY | EFFICIENCY | VOLTAGE / PHASE | MCA | MOP | [6 empty] | SIZE | COOLING ONLY OR HEAT PUMP | NOMINAL EFFICIENCY | ELECTRICAL | ELECTRIC HEAT KW | COMPRESSOR STAGES | FAN TYPE | SUBMITTAL (SYSTEM) | SUBMITTAL (OUTDOOR UNIT) | SUBMITTAL (INDOOR UNIT) | ENGINEERING MANUAL (SYSTEM) | ENGINEERING MANUAL (OUTDOOR UNIT) | ENGINEERING MANUAL (INDOOR UNIT) | CAPACITY TABLE | INSTALLATION MANUAL (OUTDOOR) | INSTALLATION MANUAL (INDOOR) | REVIT (OUTDOOR) | REVIT (INDOOR) | CAD (OUTDOOR) | CAD (INDOOR)
AHU- | FTA18AAVJUD | 600 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 17200 | 12100 | 21000 | - | - | 208/1 | 4.9 | 15 | 115 | CU- | RZA18AAVJU | 47 | 21000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.5/11.7 (SEER2/EER2) | 234 | Inverter |  | 1.5 | HEAT PUMP | Sky Air | 208/1 | - | Inverter | Variable Speed ECM | FTA18AAVJUD-RZA18AAVJU - 0 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA18AAVJU | FTA18AAVJUD | RZA18AAVJU | FTA18AAVJUD
AHU- | FTA18AAVJUD | 600 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 17200 | 12100 | 21000 | 3 | 15.965 | 208/1 | 18.4 | 20 | 115 | CU- | RZA18AAVJU | 47 | 21000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.5/11.7 (SEER2/EER2) | 234 | Inverter |  | 1.5 | HEAT PUMP | Sky Air | 208/1 | 3 | Inverter | Variable Speed ECM | FTA18AAVJUD-RZA18AAVJU - 3 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA18AAVJU | FTA18AAVJUD | RZA18AAVJU | FTA18AAVJUD
AHU- | FTA18AAVJUD | 600 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 17200 | 12100 | 21000 | 5 | 26.6083 | 208/1 | 26.5 | 30 | 115 | CU- | RZA18AAVJU | 47 | 21000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.5/11.7 (SEER2/EER2) | 234 | Inverter |  | 1.5 | HEAT PUMP | Sky Air | 208/1 | 5 | Inverter | Variable Speed ECM | FTA18AAVJUD-RZA18AAVJU - 5 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA18AAVJU | FTA18AAVJUD | RZA18AAVJU | FTA18AAVJUD
AHU- | FTA18AAVJUD | 600 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 17200 | 12100 | 21000 | 6 | 31.93 | 208/1 | 32 | 35 | 115 | CU- | RZA18AAVJU | 47 | 21000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.5/11.7 (SEER2/EER2) | 234 | Inverter |  | 1.5 | HEAT PUMP | Sky Air | 208/1 | 6 | Inverter | Variable Speed ECM | FTA18AAVJUD-RZA18AAVJU - 6 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA18AAVJU | FTA18AAVJUD | RZA18AAVJU | FTA18AAVJUD
AHU- | FTA18AAVJUD | 600 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 17200 | 12100 | 21000 | 8 | 42.5733 | 208/1 | 41 | 45 | 115 | CU- | RZA18AAVJU | 47 | 21000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.5/11.7 (SEER2/EER2) | 234 | Inverter |  | 1.5 | HEAT PUMP | Sky Air | 208/1 | 8 | Inverter | Variable Speed ECM | FTA18AAVJUD-RZA18AAVJU - 8 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA18AAVJU | FTA18AAVJUD | RZA18AAVJU | FTA18AAVJUD
AHU- | FTA18AAVJUD | 600 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 17200 | 12100 | 21000 | 10 | 53.2167 | 208/1 | 48.2 | 50 | 115 | CU- | RZA18AAVJU | 47 | 21000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.5/11.7 (SEER2/EER2) | 234 | Inverter |  | 1.5 | HEAT PUMP | Sky Air | 208/1 | 10 | Inverter | Variable Speed ECM | FTA18AAVJUD-RZA18AAVJU - 10 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA18AAVJU | FTA18AAVJUD | RZA18AAVJU | FTA18AAVJUD
AHU- | FTA24AAVJUD | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 24000 | 16900 | 27000 | - | - | 208/1 | 4.9 | 15 | 115 | CU- | RZA24AAVJU | 47 | 27000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.0/11.7 (SEER2/EER2) | 234 | Inverter |  | 2 | HEAT PUMP | Sky Air | 208/1 | - | Inverter | Variable Speed ECM | FTA24AAVJUD-RZA24AAVJU - 0 Kw |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA24AAVJU | FTA24AAVJUD | RZA24AAVJU | FTA24AAVJUD
AHU- | FTA24AAVJUD | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 24000 | 16900 | 27000 | 3 | 11.9738 | 208/1 | 18.4 | 20 | 115 | CU- | RZA24AAVJU | 47 | 27000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.0/11.7 (SEER2/EER2) | 234 | Inverter |  | 2 | HEAT PUMP | Sky Air | 208/1 | 3 | Inverter | Variable Speed ECM | FTA24AAVJUD-RZA24AAVJU - 3 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA24AAVJU | FTA24AAVJUD | RZA24AAVJU | FTA24AAVJUD
AHU- | FTA24AAVJUD | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 24000 | 16900 | 27000 | 5 | 19.9563 | 208/1 | 26.5 | 30 | 115 | CU- | RZA24AAVJU | 47 | 27000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.0/11.7 (SEER2/EER2) | 234 | Inverter |  | 2 | HEAT PUMP | Sky Air | 208/1 | 5 | Inverter | Variable Speed ECM | FTA24AAVJUD-RZA24AAVJU - 5 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA24AAVJU | FTA24AAVJUD | RZA24AAVJU | FTA24AAVJUD
AHU- | FTA24AAVJUD | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 24000 | 16900 | 27000 | 6 | 23.9475 | 208/1 | 32 | 35 | 115 | CU- | RZA24AAVJU | 47 | 27000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.0/11.7 (SEER2/EER2) | 234 | Inverter |  | 2 | HEAT PUMP | Sky Air | 208/1 | 6 | Inverter | Variable Speed ECM | FTA24AAVJUD-RZA24AAVJU - 6 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA24AAVJU | FTA24AAVJUD | RZA24AAVJU | FTA24AAVJUD
AHU- | FTA24AAVJUD | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 24000 | 16900 | 27000 | 8 | 31.93 | 208/1 | 41 | 45 | 115 | CU- | RZA24AAVJU | 47 | 27000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.0/11.7 (SEER2/EER2) | 234 | Inverter |  | 2 | HEAT PUMP | Sky Air | 208/1 | 8 | Inverter | Variable Speed ECM | FTA24AAVJUD-RZA24AAVJU - 8 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA24AAVJU | FTA24AAVJUD | RZA24AAVJU | FTA24AAVJUD
AHU- | FTA24AAVJUD | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 24000 | 16900 | 27000 | 10 | 39.9125 | 208/1 | 48.2 | 50 | 115 | CU- | RZA24AAVJU | 47 | 27000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.0/11.7 (SEER2/EER2) | 234 | Inverter |  | 2 | HEAT PUMP | Sky Air | 208/1 | 10 | Inverter | Variable Speed ECM | FTA24AAVJUD-RZA24AAVJU - 10 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA24AAVJU | FTA24AAVJUD | RZA24AAVJU | FTA24AAVJUD
AHU- | FTA30AAVJUD | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 29400 | 20900 | 35000 | - | - | 208/1 | 4.9 | 15 | 118 | CU- | RZA30AAVJU | 47 | 35000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/11.0 (SEER2/EER2) | 234 | Inverter |  | 2.5 | HEAT PUMP | Sky Air | 208/1 | - | Inverter | Variable Speed ECM | FTA30AAVJUD-RZA30AAVJU - 0 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA30AAVJU | FTA30AAVJUD | RZA30AAVJU | FTA30AAVJUD
AHU- | FTA30AAVJUD | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 29400 | 20900 | 35000 | 3 | 9.579 | 208/1 | 18.4 | 20 | 118 | CU- | RZA30AAVJU | 47 | 35000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/11.0 (SEER2/EER2) | 234 | Inverter |  | 2.5 | HEAT PUMP | Sky Air | 208/1 | 3 | Inverter | Variable Speed ECM | FTA30AAVJUD-RZA30AAVJU - 3 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA30AAVJU | FTA30AAVJUD | RZA30AAVJU | FTA30AAVJUD
AHU- | FTA30AAVJUD | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 29400 | 20900 | 35000 | 5 | 15.965 | 208/1 | 26.5 | 30 | 118 | CU- | RZA30AAVJU | 47 | 35000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/11.0 (SEER2/EER2) | 234 | Inverter |  | 2.5 | HEAT PUMP | Sky Air | 208/1 | 5 | Inverter | Variable Speed ECM | FTA30AAVJUD-RZA30AAVJU - 5 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA30AAVJU | FTA30AAVJUD | RZA30AAVJU | FTA30AAVJUD
AHU- | FTA30AAVJUD | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 29400 | 20900 | 35000 | 6 | 19.158 | 208/1 | 32 | 35 | 118 | CU- | RZA30AAVJU | 47 | 35000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/11.0 (SEER2/EER2) | 234 | Inverter |  | 2.5 | HEAT PUMP | Sky Air | 208/1 | 6 | Inverter | Variable Speed ECM | FTA30AAVJUD-RZA30AAVJU - 6 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA30AAVJU | FTA30AAVJUD | RZA30AAVJU | FTA30AAVJUD
AHU- | FTA30AAVJUD | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 29400 | 20900 | 35000 | 8 | 25.544 | 208/1 | 41 | 45 | 118 | CU- | RZA30AAVJU | 47 | 35000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/11.0 (SEER2/EER2) | 234 | Inverter |  | 2.5 | HEAT PUMP | Sky Air | 208/1 | 8 | Inverter | Variable Speed ECM | FTA30AAVJUD-RZA30AAVJU - 8 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA30AAVJU | FTA30AAVJUD | RZA30AAVJU | FTA30AAVJUD
AHU- | FTA30AAVJUD | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 29400 | 20900 | 35000 | 10 | 31.93 | 208/1 | 48.2 | 50 | 118 | CU- | RZA30AAVJU | 47 | 35000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/11.0 (SEER2/EER2) | 234 | Inverter |  | 2.5 | HEAT PUMP | Sky Air | 208/1 | 10 | Inverter | Variable Speed ECM | FTA30AAVJUD-RZA30AAVJU - 10 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA30AAVJU | FTA30AAVJUD | RZA30AAVJU | FTA30AAVJUD
AHU- | FTA36AAVJUD | 1050 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 35000 | 23700 | 40500 | - | - | 208/1 | 4.9 | 15 | 118 | CU- | RZA36AAVJU | 47 | 40500 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/10.0 (SEER2/EER2) | 234 | Inverter |  | 3 | HEAT PUMP | Sky Air | 208/1 | - | Inverter | Variable Speed ECM | FTA36AAVJUD-RZA36AAVJU - 0 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA36AAVJU | FTA36AAVJUD | RZA36AAVJU | FTA36AAVJUD
AHU- | FTA36AAVJUD | 1050 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 35000 | 23700 | 40500 | 3 | 9.1229 | 208/1 | 18.4 | 20 | 118 | CU- | RZA36AAVJU | 47 | 40500 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/10.0 (SEER2/EER2) | 234 | Inverter |  | 3 | HEAT PUMP | Sky Air | 208/1 | 3 | Inverter | Variable Speed ECM | FTA36AAVJUD-RZA36AAVJU - 3 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA36AAVJU | FTA36AAVJUD | RZA36AAVJU | FTA36AAVJUD
AHU- | FTA36AAVJUD | 1050 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 35000 | 23700 | 40500 | 5 | 15.2048 | 208/1 | 26.5 | 30 | 118 | CU- | RZA36AAVJU | 47 | 40500 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/10.0 (SEER2/EER2) | 234 | Inverter |  | 3 | HEAT PUMP | Sky Air | 208/1 | 5 | Inverter | Variable Speed ECM | FTA36AAVJUD-RZA36AAVJU - 5 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA36AAVJU | FTA36AAVJUD | RZA36AAVJU | FTA36AAVJUD
AHU- | FTA36AAVJUD | 1050 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 35000 | 23700 | 40500 | 6 | 18.2457 | 208/1 | 32 | 35 | 118 | CU- | RZA36AAVJU | 47 | 40500 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/10.0 (SEER2/EER2) | 234 | Inverter |  | 3 | HEAT PUMP | Sky Air | 208/1 | 6 | Inverter | Variable Speed ECM | FTA36AAVJUD-RZA36AAVJU - 6 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA36AAVJU | FTA36AAVJUD | RZA36AAVJU | FTA36AAVJUD
AHU- | FTA36AAVJUD | 1050 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 35000 | 23700 | 40500 | 8 | 24.3276 | 208/1 | 41 | 45 | 118 | CU- | RZA36AAVJU | 47 | 40500 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/10.0 (SEER2/EER2) | 234 | Inverter |  | 3 | HEAT PUMP | Sky Air | 208/1 | 8 | Inverter | Variable Speed ECM | FTA36AAVJUD-RZA36AAVJU - 8 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA36AAVJU | FTA36AAVJUD | RZA36AAVJU | FTA36AAVJUD
AHU- | FTA36AAVJUD | 1050 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 35000 | 23700 | 40500 | 10 | 30.4095 | 208/1 | 48.2 | 50 | 118 | CU- | RZA36AAVJU | 47 | 40500 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/10.0 (SEER2/EER2) | 234 | Inverter |  | 3 | HEAT PUMP | Sky Air | 208/1 | 10 | Inverter | Variable Speed ECM | FTA36AAVJUD-RZA36AAVJU - 10 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA36AAVJU | FTA36AAVJUD | RZA36AAVJU | FTA36AAVJUD
AHU- | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | - | - | 208/1 | 6.5 | 15 | 143 | CU- | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter |  | 3.5 | HEAT PUMP | Sky Air | 208/1 | - | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 0 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA42AAVJU | FTA42AAVJUD | RZA42AAVJU | FTA42AAVJUD
AHU- | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | 5 | 11.4036 | 208/1 | 28.2 | 30 | 143 | CU- | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter |  | 3.5 | HEAT PUMP | Sky Air | 208/1 | 5 | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 5 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA42AAVJU | FTA42AAVJUD | RZA42AAVJU | FTA42AAVJUD
AHU- | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | 6 | 13.6843 | 208/1 | 33.6 | 35 | 143 | CU- | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter |  | 3.5 | HEAT PUMP | Sky Air | 208/1 | 6 | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 6 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA42AAVJU | FTA42AAVJUD | RZA42AAVJU | FTA42AAVJUD
AHU- | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | 8 | 18.2457 | 208/1 | 42.6 | 45 | 143 | CU- | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter |  | 3.5 | HEAT PUMP | Sky Air | 208/1 | 8 | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 8 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA42AAVJU | FTA42AAVJUD | RZA42AAVJU | FTA42AAVJUD
AHU- | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | 10 | 22.8071 | 208/1 | 49.8 | 50 | 143 | CU- | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter |  | 3.5 | HEAT PUMP | Sky Air | 208/1 | 10 | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 10 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA42AAVJU | FTA42AAVJUD | RZA42AAVJU | FTA42AAVJUD
AHU- | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | 15 | 34.2107 | 208/1 | 71.5 | 80 | 143 | CU- | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter |  | 3.5 | HEAT PUMP | Sky Air | 208/1 | 15 | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 15 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA42AAVJU | FTA42AAVJUD | RZA42AAVJU | FTA42AAVJUD
AHU- | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | 19 | 43.3336 | 208/1 | 93.2 | 100 | 143 | CU- | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter |  | 3.5 | HEAT PUMP | Sky Air | 208/1 | 19 | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 19 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA42AAVJU | FTA42AAVJUD | RZA42AAVJU | FTA42AAVJUD
AHU- | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | - | - | 208/1 | 6.5 | 15 | 143 | CU- | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter |  | 4 | HEAT PUMP | Sky Air | 208/1 | - | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 0 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA48AAVJU | FTA48AAVJUD | RZA48AAVJU | FTA48AAVJUD
AHU- | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | 5 | 10.5033 | 208/1 | 28.2 | 30 | 143 | CU- | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter |  | 4 | HEAT PUMP | Sky Air | 208/1 | 5 | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 5 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA48AAVJU | FTA48AAVJUD | RZA48AAVJU | FTA48AAVJUD
AHU- | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | 6 | 12.6039 | 208/1 | 33.6 | 35 | 143 | CU- | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter |  | 4 | HEAT PUMP | Sky Air | 208/1 | 6 | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 6 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA48AAVJU | FTA48AAVJUD | RZA48AAVJU | FTA48AAVJUD
AHU- | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | 8 | 16.8053 | 208/1 | 42.6 | 45 | 143 | CU- | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter |  | 4 | HEAT PUMP | Sky Air | 208/1 | 8 | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 8 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA48AAVJU | FTA48AAVJUD | RZA48AAVJU | FTA48AAVJUD
AHU- | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | 10 | 21.0066 | 208/1 | 49.8 | 50 | 143 | CU- | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter |  | 4 | HEAT PUMP | Sky Air | 208/1 | 10 | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 10 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA48AAVJU | FTA48AAVJUD | RZA48AAVJU | FTA48AAVJUD
AHU- | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | 15 | 31.5099 | 208/1 | 71.5 | 80 | 143 | CU- | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter |  | 4 | HEAT PUMP | Sky Air | 208/1 | 15 | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 15 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA48AAVJU | FTA48AAVJUD | RZA48AAVJU | FTA48AAVJUD
AHU- | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | 19 | 39.9125 | 208/1 | 93.2 | 100 | 143 | CU- | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter |  | 4 | HEAT PUMP | Sky Air | 208/1 | 19 | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 19 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR |  |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA | RZA48AAVJU | FTA48AAVJUD | RZA48AAVJU | FTA48AAVJUD
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | - | - | 208/1 | 5.8 | 15 | 112 | CU- | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DH4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | 3 | 15.45 | 208/1 | 19 | 20 | 112 | CU- | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DH4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | 5 | 25.75 | 208/1 | 27 | 30 | 112 | CU- | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DH4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | 6 | 30.9 | 208/1 | 32.8 | 35 | 112 | CU- | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DH4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | 8 | 41.2 | 208/1 | 41.9 | 45 | 112 | CU- | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DH4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | 10 | 51.5 | 208/1 | 49.1 | 50 | 112 | CU- | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DH4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | 15 | 77.25 | 208/1 | 70.8 | 90 | 112 | CU- | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DH4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | - | - | 208/1 | 5.8 | 15 | 112 | CU- | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DH4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | 3 | 12.4403 | 208/1 | 19 | 20 | 112 | CU- | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DH4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | 5 | 20.7338 | 208/1 | 27 | 30 | 112 | CU- | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DH4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | 6 | 24.8805 | 208/1 | 32.8 | 35 | 112 | CU- | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DH4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | 8 | 33.174 | 208/1 | 41.9 | 45 | 112 | CU- | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DH4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | 10 | 41.4675 | 208/1 | 49.1 | 50 | 112 | CU- | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DH4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | 15 | 62.2013 | 208/1 | 70.8 | 90 | 112 | CU- | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 |  | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DH4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | - | - | 208/1 | 5.6 | 15 | 129 | CU- | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 |  | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DH4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | 3 | 9.0368 | 208/1 | 19 | 20 | 129 | CU- | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 |  | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DH4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | 5 | 15.0613 | 208/1 | 27 | 30 | 129 | CU- | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 |  | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DH4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | 6 | 18.0736 | 208/1 | 32.7 | 35 | 129 | CU- | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 |  | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DH4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | 8 | 24.0981 | 208/1 | 42 | 45 | 129 | CU- | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 |  | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DH4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | 10 | 30.1226 | 208/1 | 49 | 50 | 129 | CU- | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 |  | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DH4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | 15 | 45.184 | 208/1 | 49.1 | 80 | 129 | CU- | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 |  | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DH4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | - | - | 208/1 | 7.1 | 15 | 153 | CU- | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DH4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 3 | 8.0496 | 208/1 | 20.7 | 25 | 153 | CU- | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DH4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 5 | 13.416 | 208/1 | 29 | 35 | 153 | CU- | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DH4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 6 | 16.0992 | 208/1 | 34 | 40 | 153 | CU- | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DH4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 8 | 21.4655 | 208/1 | 43 | 50 | 153 | CU- | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DH4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 10 | 26.8319 | 208/1 | 50.5 | 60 | 153 | CU- | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DH4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 15 | 40.2479 | 208/1 | 72.1 | 80 | 153 | CU- | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DH4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 19 | 50.9807 | 208/1 | 93.9 | 100 | 153 | CU- | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 19 | 1 | ECM |  | DH4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | - | - | 208/1 | 5.9 | 15 | 153 | CU- | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 |  | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DH4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 3 | 7.1485 | 208/1 | 19 | 20 | 153 | CU- | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 |  | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DH4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 5 | 11.9142 | 208/1 | 28 | 30 | 153 | CU- | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 |  | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DH4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 6 | 14.297 | 208/1 | 33 | 35 | 153 | CU- | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 |  | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DH4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 8 | 19.0627 | 208/1 | 42 | 45 | 153 | CU- | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 |  | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DH4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 10 | 23.8284 | 208/1 | 49 | 50 | 153 | CU- | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 |  | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DH4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 15 | 35.7425 | 208/1 | 70.9 | 80 | 153 | CU- | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 |  | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DH4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 19 | 45.2739 | 208/1 | 92.5 | 100 | 153 | CU- | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 |  | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 19 | 1 | ECM |  | DH4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | - | - | 208/1 | 7.1 | 15 | 153 | CU- | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DH4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 3 | 5.9869 | 208/1 | 20.7 | 25 | 153 | CU- | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DH4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 5 | 9.9781 | 208/1 | 29 | 30 | 153 | CU- | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DH4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 6 | 11.9738 | 208/1 | 34 | 35 | 153 | CU- | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DH4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 8 | 15.965 | 208/1 | 43 | 45 | 153 | CU- | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DH4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 10 | 19.9563 | 208/1 | 50.5 | 60 | 153 | CU- | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DH4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 15 | 29.9344 | 208/1 | 72.1 | 80 | 153 | CU- | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DH4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 19 | 37.9169 | 208/1 | 93.9 | 100 | 153 | CU- | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 19 | 1 | ECM |  | DH4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DH4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 3 | 4.7895 | 208/1 | 22 | 25 | 167 | CU- | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DH4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 5 | 7.9825 | 208/1 | 30.3 | 35 | 167 | CU- | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DH4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 6 | 9.579 | 208/1 | 36 | 40 | 167 | CU- | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DH4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 8 | 12.772 | 208/1 | 45 | 45 | 167 | CU- | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DH4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 10 | 15.965 | 208/1 | 52 | 60 | 167 | CU- | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DH4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 15 | 23.9475 | 208/1 | 73.6 | 80 | 167 | CU- | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DH4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 20 | 31.93 | 208/1 | 95.3 | 100 | 167 | CU- | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 20 | 1 | ECM |  | DH4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 25 | 39.9125 | 208/1 | 117 | 125 | 167 | CU- | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 25 | 1 | ECM |  | DH4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | - | - | 208/1 | 5.8 | 15 | 112 | CU- | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM |  | DH5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | 3 | 15.085 | 208/1 | 19 | 20 | 112 | CU- | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM |  | DH5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | 5 | 25.1417 | 208/1 | 27 | 30 | 112 | CU- | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM |  | DH5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | 6 | 30.1701 | 208/1 | 32.8 | 35 | 112 | CU- | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM |  | DH5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | 8 | 40.2268 | 208/1 | 41.9 | 45 | 112 | CU- | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM |  | DH5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | 10 | 50.2835 | 208/1 | 49.1 | 50 | 112 | CU- | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM |  | DH5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | 15 | 75.4252 | 208/1 | 70.8 | 90 | 112 | CU- | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM |  | DH5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | - | - | 208/1 | 5.8 | 15 | 112 | CU- | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM |  | DH5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | 3 | 12.36 | 208/1 | 19 | 20 | 112 | CU- | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM |  | DH5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | 5 | 20.6 | 208/1 | 27 | 30 | 112 | CU- | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM |  | DH5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | 6 | 24.72 | 208/1 | 32.8 | 35 | 112 | CU- | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM |  | DH5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | 8 | 32.96 | 208/1 | 41.9 | 45 | 112 | CU- | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM |  | DH5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | 10 | 41.2 | 208/1 | 49.1 | 50 | 112 | CU- | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM |  | DH5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | 15 | 61.8 | 208/1 | 70.8 | 90 | 112 | CU- | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 |  | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM |  | DH5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | - | - | 208/1 | 5.6 | 15 | 129 | CU- | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 |  | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM |  | DH5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | 3 | 9.1229 | 208/1 | 19 | 20 | 129 | CU- | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 |  | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM |  | DH5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | 5 | 15.2048 | 208/1 | 27 | 30 | 129 | CU- | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 |  | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM |  | DH5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | 6 | 18.2457 | 208/1 | 32.7 | 35 | 129 | CU- | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 |  | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM |  | DH5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | 8 | 24.3276 | 208/1 | 42 | 45 | 129 | CU- | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 |  | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM |  | DH5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | 10 | 30.4095 | 208/1 | 49 | 50 | 129 | CU- | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 |  | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM |  | DH5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | 15 | 45.6143 | 208/1 | 49.1 | 80 | 129 | CU- | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 |  | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM |  | DH5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | - | - | 208/1 | 7.1 | 15 | 153 | CU- | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 |  | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM |  | DH5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 3 | 9.579 | 208/1 | 20.7 | 25 | 153 | CU- | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 |  | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM |  | DH5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 5 | 15.965 | 208/1 | 29 | 35 | 153 | CU- | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 |  | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM |  | DH5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 6 | 19.158 | 208/1 | 34 | 40 | 153 | CU- | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 |  | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM |  | DH5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 8 | 25.544 | 208/1 | 43 | 50 | 153 | CU- | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 |  | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM |  | DH5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 10 | 31.93 | 208/1 | 50.5 | 60 | 153 | CU- | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 |  | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM |  | DH5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 15 | 47.895 | 208/1 | 72.1 | 80 | 153 | CU- | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 |  | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM |  | DH5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 19 | 60.667 | 208/1 | 93.9 | 100 | 153 | CU- | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 |  | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 19 | 1 | ECM |  | DH5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | - | - | 208/1 | 5.9 | 15 | 153 | CU- | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 |  | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM |  | DH5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 3 | 7.0956 | 208/1 | 19 | 20 | 153 | CU- | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 |  | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM |  | DH5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 5 | 11.8259 | 208/1 | 28 | 30 | 153 | CU- | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 |  | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM |  | DH5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 6 | 14.1911 | 208/1 | 33 | 35 | 153 | CU- | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 |  | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM |  | DH5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 8 | 18.9215 | 208/1 | 42 | 45 | 153 | CU- | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 |  | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM |  | DH5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 10 | 23.6519 | 208/1 | 49 | 50 | 153 | CU- | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 |  | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM |  | DH5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 15 | 35.4778 | 208/1 | 70.9 | 80 | 153 | CU- | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 |  | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM |  | DH5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 19 | 44.9385 | 208/1 | 92.5 | 100 | 153 | CU- | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 |  | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 19 | 1 | ECM |  | DH5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | - | - | 208/1 | 7.1 | 15 | 153 | CU- | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 |  | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM |  | DH5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 3 | 5.9869 | 208/1 | 20.7 | 25 | 153 | CU- | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 |  | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM |  | DH5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 5 | 9.9781 | 208/1 | 29 | 30 | 153 | CU- | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 |  | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM |  | DH5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 6 | 11.9738 | 208/1 | 34 | 35 | 153 | CU- | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 |  | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM |  | DH5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 8 | 15.965 | 208/1 | 43 | 45 | 153 | CU- | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 |  | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM |  | DH5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 10 | 19.9563 | 208/1 | 50.5 | 60 | 153 | CU- | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 |  | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM |  | DH5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 15 | 29.9344 | 208/1 | 72.1 | 80 | 153 | CU- | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 |  | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM |  | DH5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 19 | 37.9169 | 208/1 | 93.9 | 100 | 153 | CU- | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 |  | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 19 | 1 | ECM |  | DH5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 |  | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM |  | DH5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 3 | 4.7895 | 208/1 | 22 | 25 | 167 | CU- | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 |  | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM |  | DH5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 5 | 7.9825 | 208/1 | 30.3 | 35 | 167 | CU- | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 |  | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM |  | DH5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 6 | 9.579 | 208/1 | 36 | 40 | 167 | CU- | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 |  | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM |  | DH5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 8 | 12.772 | 208/1 | 45 | 45 | 167 | CU- | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 |  | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM |  | DH5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 10 | 15.965 | 208/1 | 52 | 60 | 167 | CU- | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 |  | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM |  | DH5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 15 | 23.9475 | 208/1 | 73.6 | 80 | 167 | CU- | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 |  | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM |  | DH5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 20 | 31.93 | 208/1 | 95.3 | 100 | 167 | CU- | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 |  | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 20 | 1 | ECM |  | DH5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 25 | 39.9125 | 208/1 | 117 | 125 | 167 | CU- | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 |  | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 25 | 1 | ECM |  | DH5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | 17400 | - | - | 208/1 | 4.9 | 15 | 115 | CU- | DH6VSA1810 | 47 | 17400 | 8.8 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 19.0/12.0 (SEER2/EER2) | 122 | Inverter |  | 1.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH6VSA1810 | DFVE24BP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA1810 |  | DH6VSA1810
AHU- | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | 17400 | 3 | 15.7033 | 208/1 | 18.4 | 20 | 115 | CU- | DH6VSA1810 | 47 | 17400 | 8.8 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 19.0/12.0 (SEER2/EER2) | 122 | Inverter |  | 1.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 3 | Inverter | Variable Speed ECM |  | DH6VSA1810 | DFVE24BP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA1810 |  | DH6VSA1810
AHU- | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | 17400 | 5 | 26.1721 | 208/1 | 26.5 | 30 | 115 | CU- | DH6VSA1810 | 47 | 17400 | 8.8 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 19.0/12.0 (SEER2/EER2) | 122 | Inverter |  | 1.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DH6VSA1810 | DFVE24BP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA1810 |  | DH6VSA1810
AHU- | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | 17400 | 6 | 31.4066 | 208/1 | 32 | 35 | 115 | CU- | DH6VSA1810 | 47 | 17400 | 8.8 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 19.0/12.0 (SEER2/EER2) | 122 | Inverter |  | 1.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DH6VSA1810 | DFVE24BP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA1810 |  | DH6VSA1810
AHU- | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | 17400 | 8 | 41.8754 | 208/1 | 41 | 45 | 115 | CU- | DH6VSA1810 | 47 | 17400 | 8.8 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 19.0/12.0 (SEER2/EER2) | 122 | Inverter |  | 1.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DH6VSA1810 | DFVE24BP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA1810 |  | DH6VSA1810
AHU- | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | 17400 | 10 | 52.3443 | 208/1 | 48.5 | 50 | 115 | CU- | DH6VSA1810 | 47 | 17400 | 8.8 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 19.0/12.0 (SEER2/EER2) | 122 | Inverter |  | 1.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DH6VSA1810 | DFVE24BP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA1810 |  | DH6VSA1810
AHU- | DFVE24BP1300 | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | 23200 | - | - | 208/1 | 4.9 | 15 | 115 | CU- | DH6VSA2410 | 47 | 23200 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 122 | Inverter |  | 2 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH6VSA2410 | DFVE24BP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA2410 |  | DH6VSA2410
AHU- | DFVE24BP1300 | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | 23200 | 3 | 11.9738 | 208/1 | 18.4 | 20 | 115 | CU- | DH6VSA2410 | 47 | 23200 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 122 | Inverter |  | 2 | HEAT PUMP | 16.2 SEER2 | 208/1 | 3 | Inverter | Variable Speed ECM |  | DH6VSA2410 | DFVE24BP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA2410 |  | DH6VSA2410
AHU- | DFVE24BP1300 | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | 23200 | 5 | 19.9563 | 208/1 | 26.5 | 30 | 115 | CU- | DH6VSA2410 | 47 | 23200 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 122 | Inverter |  | 2 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DH6VSA2410 | DFVE24BP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA2410 |  | DH6VSA2410
AHU- | DFVE24BP1300 | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | 23200 | 6 | 23.9475 | 208/1 | 32 | 35 | 115 | CU- | DH6VSA2410 | 47 | 23200 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 122 | Inverter |  | 2 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DH6VSA2410 | DFVE24BP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA2410 |  | DH6VSA2410
AHU- | DFVE24BP1300 | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | 23200 | 8 | 31.93 | 208/1 | 41 | 45 | 115 | CU- | DH6VSA2410 | 47 | 23200 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 122 | Inverter |  | 2 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DH6VSA2410 | DFVE24BP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA2410 |  | DH6VSA2410
AHU- | DFVE24BP1300 | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | 23200 | 10 | 39.9125 | 208/1 | 48.5 | 50 | 115 | CU- | DH6VSA2410 | 47 | 23200 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 122 | Inverter |  | 2 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DH6VSA2410 | DFVE24BP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA2410 |  | DH6VSA2410
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | - | - | 208/1 | 6.5 | 15 | 140 | CU- | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter |  | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH6VSA3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3010 |  | DH6VSA3010
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | 5 | 15.8069 | 208/1 | 28.1 | 30 | 140 | CU- | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter |  | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DH6VSA3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3010 |  | DH6VSA3010
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | 6 | 18.9683 | 208/1 | 33.6 | 35 | 140 | CU- | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter |  | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DH6VSA3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3010 |  | DH6VSA3010
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | 8 | 25.2911 | 208/1 | 42.6 | 45 | 140 | CU- | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter |  | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DH6VSA3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3010 |  | DH6VSA3010
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | 10 | 31.6139 | 208/1 | 49.9 | 50 | 140 | CU- | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter |  | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DH6VSA3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3010 |  | DH6VSA3010
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | 15 | 47.4208 | 208/1 | 71.5 | 80 | 140 | CU- | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter |  | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DH6VSA3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3010 |  | DH6VSA3010
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | 19 | 60.0663 | 208/1 | 93.2 | 100 | 140 | CU- | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter |  | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 19 | Inverter | Variable Speed ECM |  | DH6VSA3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3010 |  | DH6VSA3010
AHU- | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | - | - | 208/1 | 6.5 | 15 | 140 | CU- | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter |  | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH6VSA3610 | DFVE42CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3610 |  | DH6VSA3610
AHU- | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | 5 | 12.6706 | 208/1 | 28.1 | 30 | 140 | CU- | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter |  | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DH6VSA3610 | DFVE42CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3610 |  | DH6VSA3610
AHU- | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | 6 | 15.2048 | 208/1 | 33.6 | 35 | 140 | CU- | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter |  | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DH6VSA3610 | DFVE42CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3610 |  | DH6VSA3610
AHU- | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | 8 | 20.273 | 208/1 | 42.6 | 45 | 140 | CU- | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter |  | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DH6VSA3610 | DFVE42CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3610 |  | DH6VSA3610
AHU- | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | 10 | 25.3413 | 208/1 | 49.9 | 50 | 140 | CU- | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter |  | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DH6VSA3610 | DFVE42CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3610 |  | DH6VSA3610
AHU- | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | 15 | 38.0119 | 208/1 | 71.5 | 80 | 140 | CU- | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter |  | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DH6VSA3610 | DFVE42CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3610 |  | DH6VSA3610
AHU- | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | 19 | 48.1484 | 208/1 | 93.2 | 100 | 140 | CU- | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter |  | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | 19 | Inverter | Variable Speed ECM |  | DH6VSA3610 | DFVE42CP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA3610 |  | DH6VSA3610
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | - | - | 208/1 | 6.5 | 15 | 150 | CU- | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH6VSA4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4210 |  | DH6VSA4210
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | 5 | 12.0947 | 208/1 | 28.1 | 30 | 150 | CU- | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DH6VSA4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4210 |  | DH6VSA4210
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | 6 | 14.5136 | 208/1 | 33.6 | 35 | 150 | CU- | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DH6VSA4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4210 |  | DH6VSA4210
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | 8 | 19.3515 | 208/1 | 42.6 | 45 | 150 | CU- | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DH6VSA4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4210 |  | DH6VSA4210
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | 10 | 24.1894 | 208/1 | 49.9 | 50 | 150 | CU- | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DH6VSA4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4210 |  | DH6VSA4210
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | 15 | 36.2841 | 208/1 | 71.5 | 80 | 150 | CU- | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DH6VSA4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4210 |  | DH6VSA4210
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | 20 | 48.3788 | 208/1 | 93.2 | 100 | 150 | CU- | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DH6VSA4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4210 |  | DH6VSA4210
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | - | - | 208/1 | 6.5 | 15 | 150 | CU- | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH6VSA4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4810 |  | DH6VSA4810
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | 5 | 11.5688 | 208/1 | 28.1 | 30 | 150 | CU- | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DH6VSA4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4810 |  | DH6VSA4810
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | 6 | 13.8826 | 208/1 | 33.6 | 35 | 150 | CU- | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DH6VSA4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4810 |  | DH6VSA4810
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | 8 | 18.5101 | 208/1 | 42.6 | 45 | 150 | CU- | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DH6VSA4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4810 |  | DH6VSA4810
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | 10 | 23.1377 | 208/1 | 49.9 | 50 | 150 | CU- | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DH6VSA4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4810 |  | DH6VSA4810
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | 15 | 34.7065 | 208/1 | 71.5 | 80 | 150 | CU- | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DH6VSA4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4810 |  | DH6VSA4810
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | 20 | 46.2754 | 208/1 | 93.2 | 100 | 150 | CU- | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter |  | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DH6VSA4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA4810 |  | DH6VSA4810
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter |  | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH6VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA6010 |  | DH6VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 5 | 9.7348 | 208/1 | 30.2 | 35 | 167 | CU- | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter |  | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DH6VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA6010 |  | DH6VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 6 | 11.6817 | 208/1 | 35.8 | 40 | 167 | CU- | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter |  | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DH6VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA6010 |  | DH6VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 8 | 15.5756 | 208/1 | 44.8 | 45 | 167 | CU- | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter |  | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DH6VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA6010 |  | DH6VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 10 | 19.4695 | 208/1 | 52 | 60 | 167 | CU- | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter |  | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DH6VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA6010 |  | DH6VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 15 | 29.2043 | 208/1 | 73.6 | 80 | 167 | CU- | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter |  | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DH6VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA6010 |  | DH6VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 20 | 38.939 | 208/1 | 95.3 | 100 | 167 | CU- | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter |  | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DH6VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA6010 |  | DH6VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 25 | 48.6738 | 208/1 | 117 | 125 | 167 | CU- | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter |  | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM |  | DH6VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE | DH6VSA6010 |  | DH6VSA6010
AHU- | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | - | - | 208/1 | 4.9 | 15 | 129 | CU- | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 |  | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM |  | DH7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | 3 | 12.2808 | 208/1 | 18.4 | 20 | 129 | CU- | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 |  | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | 3 | 2 | Variable Speed ECM |  | DH7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | 5 | 20.4679 | 208/1 | 26.5 | 30 | 129 | CU- | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 |  | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM |  | DH7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | 6 | 24.5615 | 208/1 | 32 | 35 | 129 | CU- | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 |  | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM |  | DH7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | 8 | 32.7487 | 208/1 | 41 | 45 | 129 | CU- | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 |  | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM |  | DH7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | 10 | 40.9359 | 208/1 | 48.2 | 50 | 129 | CU- | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 |  | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM |  | DH7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | 15 | 61.4038 | 208/1 | 69.9 | 70 | 129 | CU- | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 |  | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM |  | DH7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | - | - | 208/1 | 6.5 | 15 | 153 | CU- | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 |  | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM |  | DH7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | 5 | 13.416 | 208/1 | 28.2 | 35 | 153 | CU- | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 |  | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM |  | DH7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | 6 | 16.0992 | 208/1 | 33.6 | 40 | 153 | CU- | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 |  | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM |  | DH7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | 8 | 21.4655 | 208/1 | 42.6 | 50 | 153 | CU- | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 |  | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM |  | DH7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | 10 | 26.8319 | 208/1 | 49.8 | 60 | 153 | CU- | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 |  | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM |  | DH7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | 15 | 40.2479 | 208/1 | 71.5 | 80 | 153 | CU- | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 |  | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM |  | DH7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | 19 | 50.9807 | 208/1 | 93.2 | 100 | 153 | CU- | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 |  | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | 19 | 2 | Variable Speed ECM |  | DH7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 |  | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM |  | DH7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 5 | 10.4346 | 208/1 | 30.3 | 35 | 167 | CU- | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 |  | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM |  | DH7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 6 | 12.5216 | 208/1 | 35.7 | 40 | 167 | CU- | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 |  | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM |  | DH7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 8 | 16.6954 | 208/1 | 44.7 | 45 | 167 | CU- | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 |  | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM |  | DH7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 10 | 20.8693 | 208/1 | 52 | 60 | 167 | CU- | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 |  | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM |  | DH7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 15 | 31.3039 | 208/1 | 73.6 | 80 | 167 | CU- | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 |  | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM |  | DH7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 20 | 41.7386 | 208/1 | 95.3 | 100 | 167 | CU- | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 |  | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 20 | 2 | Variable Speed ECM |  | DH7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 25 | 52.1732 | 208/1 | 117 | 125 | 167 | CU- | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 |  | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 25 | 2 | Variable Speed ECM |  | DH7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 |  | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM |  | DH7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 5 | 8.4471 | 208/1 | 30.3 | 35 | 167 | CU- | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 |  | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM |  | DH7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 6 | 10.1365 | 208/1 | 35.7 | 40 | 167 | CU- | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 |  | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM |  | DH7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 8 | 13.5153 | 208/1 | 44.7 | 45 | 167 | CU- | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 |  | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM |  | DH7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 10 | 16.8942 | 208/1 | 52 | 60 | 167 | CU- | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 |  | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM |  | DH7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 15 | 25.3413 | 208/1 | 73.6 | 80 | 167 | CU- | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 |  | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM |  | DH7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 20 | 33.7884 | 208/1 | 95.3 | 100 | 167 | CU- | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 |  | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 20 | 2 | Variable Speed ECM |  | DH7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 25 | 42.2354 | 208/1 | 117 | 125 | 167 | CU- | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 |  | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 25 | 2 | Variable Speed ECM |  | DH7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | - | - | 208/1 | 6.5 | 15 | 140 | CU- | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter |  | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH7VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA2410 |  | DH7VSA2410
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | 5 | 15.8069 | 208/1 | 28.1 | 30 | 140 | CU- | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter |  | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DH7VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA2410 |  | DH7VSA2410
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | 6 | 18.9683 | 208/1 | 33.6 | 35 | 140 | CU- | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter |  | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DH7VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA2410 |  | DH7VSA2410
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | 8 | 25.2911 | 208/1 | 42.6 | 45 | 140 | CU- | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter |  | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DH7VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA2410 |  | DH7VSA2410
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | 10 | 31.6139 | 208/1 | 49.9 | 50 | 140 | CU- | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter |  | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DH7VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA2410 |  | DH7VSA2410
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | 15 | 47.4208 | 208/1 | 71.5 | 80 | 140 | CU- | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter |  | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DH7VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA2410 |  | DH7VSA2410
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | 19 | 60.0663 | 208/1 | 93.2 | 100 | 140 | CU- | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter |  | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | 19 | Inverter | Variable Speed ECM |  | DH7VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA2410 |  | DH7VSA2410
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | - | - | 208/1 | 6.5 | 15 | 150 | CU- | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter |  | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH7VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA3610 |  | DH7VSA3610
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | 5 | 12.0947 | 208/1 | 28.1 | 30 | 150 | CU- | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter |  | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DH7VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA3610 |  | DH7VSA3610
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | 6 | 14.5136 | 208/1 | 33.6 | 35 | 150 | CU- | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter |  | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DH7VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA3610 |  | DH7VSA3610
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | 8 | 19.3515 | 208/1 | 42.6 | 45 | 150 | CU- | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter |  | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DH7VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA3610 |  | DH7VSA3610
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | 10 | 24.1894 | 208/1 | 49.9 | 50 | 150 | CU- | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter |  | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DH7VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA3610 |  | DH7VSA3610
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | 15 | 36.2841 | 208/1 | 71.5 | 80 | 150 | CU- | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter |  | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DH7VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA3610 |  | DH7VSA3610
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | 20 | 48.3788 | 208/1 | 93.2 | 100 | 150 | CU- | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter |  | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DH7VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA3610 |  | DH7VSA3610
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH7VSA4210 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4210 |  | DH7VSA4210
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 5 | 11.5688 | 208/1 | 30.2 | 35 | 167 | CU- | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DH7VSA4210 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4210 |  | DH7VSA4210
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 6 | 13.8826 | 208/1 | 35.8 | 40 | 167 | CU- | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DH7VSA4210 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4210 |  | DH7VSA4210
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 8 | 18.5101 | 208/1 | 44.8 | 45 | 167 | CU- | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DH7VSA4210 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4210 |  | DH7VSA4210
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 10 | 23.1377 | 208/1 | 52 | 60 | 167 | CU- | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DH7VSA4210 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4210 |  | DH7VSA4210
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 15 | 34.7065 | 208/1 | 73.6 | 80 | 167 | CU- | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DH7VSA4210 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4210 |  | DH7VSA4210
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 20 | 46.2754 | 208/1 | 95.3 | 100 | 167 | CU- | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DH7VSA4210 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4210 |  | DH7VSA4210
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 25 | 57.8442 | 208/1 | 117 | 125 | 167 | CU- | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM |  | DH7VSA4210 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4210 |  | DH7VSA4210
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH7VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4810 |  | DH7VSA4810
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 5 | 9.7348 | 208/1 | 30.2 | 35 | 167 | CU- | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DH7VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4810 |  | DH7VSA4810
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 6 | 11.6817 | 208/1 | 35.8 | 40 | 167 | CU- | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DH7VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4810 |  | DH7VSA4810
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 8 | 15.5756 | 208/1 | 44.8 | 45 | 167 | CU- | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DH7VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4810 |  | DH7VSA4810
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 10 | 19.4695 | 208/1 | 52 | 60 | 167 | CU- | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DH7VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4810 |  | DH7VSA4810
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 15 | 29.2043 | 208/1 | 73.6 | 80 | 167 | CU- | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DH7VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4810 |  | DH7VSA4810
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 20 | 38.939 | 208/1 | 95.3 | 100 | 167 | CU- | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DH7VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4810 |  | DH7VSA4810
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 25 | 48.6738 | 208/1 | 117 | 125 | 167 | CU- | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter |  | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM |  | DH7VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA4810 |  | DH7VSA4810
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter |  | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH7VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA6010 |  | DH7VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 5 | 9.7348 | 208/1 | 30.2 | 35 | 167 | CU- | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter |  | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DH7VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA6010 |  | DH7VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 6 | 11.6817 | 208/1 | 35.8 | 40 | 167 | CU- | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter |  | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DH7VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA6010 |  | DH7VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 8 | 15.5756 | 208/1 | 44.8 | 45 | 167 | CU- | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter |  | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DH7VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA6010 |  | DH7VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 10 | 19.4695 | 208/1 | 52 | 60 | 167 | CU- | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter |  | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DH7VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA6010 |  | DH7VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 15 | 29.2043 | 208/1 | 73.6 | 80 | 167 | CU- | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter |  | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DH7VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA6010 |  | DH7VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 20 | 38.939 | 208/1 | 95.3 | 100 | 167 | CU- | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter |  | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DH7VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA6010 |  | DH7VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 25 | 48.6738 | 208/1 | 117 | 125 | 167 | CU- | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter |  | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM |  | DH7VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE | DH7VSA6010 |  | DH7VSA6010
AHU- | DFVE48CP0300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 58.4375 | 23000 | 18630 | 23000 | - | - | 115/1 | 6.5 | 15 | 155 | CU- | DH9VSA241C | 17 | 23000 | 9.2 HSPF2 | 208/1 | 17.4 | 20 | 95 | R32 | 19.2 / 11.7 (SEER2/EER2) | 230 | Inverter |  | 2 | HEAT PUMP | 19.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH9VSA241C | DFVE48CP0300 |  | ENGINEERING MANUAL - DH9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH9VS | INSTALLATION MANUAL - DFVE
AHU- | DFVE48CP0300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.3915 | 34200 | 28044 | 32000 | - | - | 115/1 | 6.5 | 15 | 155 | CU- | DH9VSA361C | 17 | 32000 | 9.2 HSPF2 | 208/1 | 21.8 | 25 | 95 | R32 | 19.0 / 11.7 (SEER2/EER2) | 230 | Inverter |  | 3 | HEAT PUMP | 19.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DH9VSA361C | DFVE48CP0300 |  | ENGINEERING MANUAL - DH9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH9VS | INSTALLATION MANUAL - DFVE
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | - | - | 208/1 | 7.1 | 15 | 153 | CU- | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | - | 1 | ECM |  | DH4SEA3630 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3630 |  | DH4SEA3630
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 3 | 8.0496 | 208/1 | 20.7 | 25 | 153 | CU- | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 3 | 1 | ECM |  | DH4SEA3630 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3630 |  | DH4SEA3630
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 5 | 13.416 | 208/1 | 29 | 35 | 153 | CU- | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 5 | 1 | ECM |  | DH4SEA3630 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3630 |  | DH4SEA3630
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 6 | 16.0992 | 208/1 | 34 | 40 | 153 | CU- | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 6 | 1 | ECM |  | DH4SEA3630 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3630 |  | DH4SEA3630
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 8 | 21.4655 | 208/1 | 43 | 50 | 153 | CU- | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 8 | 1 | ECM |  | DH4SEA3630 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3630 |  | DH4SEA3630
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 10 | 26.8319 | 208/1 | 50.5 | 60 | 153 | CU- | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 10 | 1 | ECM |  | DH4SEA3630 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3630 |  | DH4SEA3630
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 15 | 40.2479 | 208/1 | 72.1 | 80 | 153 | CU- | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 15 | 1 | ECM |  | DH4SEA3630 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3630 |  | DH4SEA3630
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 19 | 50.9807 | 208/1 | 93.9 | 100 | 153 | CU- | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 19 | 1 | ECM |  | DH4SEA3630 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3630 |  | DH4SEA3630
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | - | - | 208/1 | 7.1 | 15 | 153 | CU- | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | - | 1 | ECM |  | DH4SEA4830 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4830 |  | DH4SEA4830
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 3 | 5.9869 | 208/1 | 20.7 | 25 | 153 | CU- | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 3 | 1 | ECM |  | DH4SEA4830 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4830 |  | DH4SEA4830
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 5 | 9.9781 | 208/1 | 29 | 30 | 153 | CU- | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 5 | 1 | ECM |  | DH4SEA4830 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4830 |  | DH4SEA4830
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 6 | 11.9738 | 208/1 | 34 | 35 | 153 | CU- | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 6 | 1 | ECM |  | DH4SEA4830 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4830 |  | DH4SEA4830
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 8 | 15.965 | 208/1 | 43 | 45 | 153 | CU- | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 8 | 1 | ECM |  | DH4SEA4830 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4830 |  | DH4SEA4830
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 10 | 19.9563 | 208/1 | 50.5 | 60 | 153 | CU- | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 10 | 1 | ECM |  | DH4SEA4830 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4830 |  | DH4SEA4830
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 15 | 29.9344 | 208/1 | 72.1 | 80 | 153 | CU- | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 15 | 1 | ECM |  | DH4SEA4830 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4830 |  | DH4SEA4830
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 19 | 37.9169 | 208/1 | 93.9 | 100 | 153 | CU- | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 19 | 1 | ECM |  | DH4SEA4830 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4830 |  | DH4SEA4830
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | - | 1 | ECM |  | DH4SEA6030 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6030 |  | DH4SEA6030
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 3 | 4.7895 | 208/1 | 22 | 25 | 167 | CU- | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 3 | 1 | ECM |  | DH4SEA6030 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6030 |  | DH4SEA6030
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 5 | 7.9825 | 208/1 | 30.3 | 35 | 167 | CU- | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 5 | 1 | ECM |  | DH4SEA6030 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6030 |  | DH4SEA6030
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 6 | 9.579 | 208/1 | 36 | 40 | 167 | CU- | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 6 | 1 | ECM |  | DH4SEA6030 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6030 |  | DH4SEA6030
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 8 | 12.772 | 208/1 | 45 | 45 | 167 | CU- | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 8 | 1 | ECM |  | DH4SEA6030 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6030 |  | DH4SEA6030
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 10 | 15.965 | 208/1 | 52 | 60 | 167 | CU- | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 10 | 1 | ECM |  | DH4SEA6030 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6030 |  | DH4SEA6030
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 15 | 23.9475 | 208/1 | 73.6 | 80 | 167 | CU- | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 15 | 1 | ECM |  | DH4SEA6030 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6030 |  | DH4SEA6030
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 20 | 31.93 | 208/1 | 95.3 | 100 | 167 | CU- | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 20 | 1 | ECM |  | DH4SEA6030 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6030 |  | DH4SEA6030
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 25 | 39.9125 | 208/1 | 117 | 125 | 167 | CU- | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 25 | 1 | ECM |  | DH4SEA6030 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6030 |  | DH4SEA6030
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | - | - | 208/1 | 7.1 | 15 | 153 | CU- | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | - | 1 | ECM |  | DH4SEA3640 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3640 |  | DH4SEA3640
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 3 | 8.0496 | 208/1 | 20.7 | 25 | 153 | CU- | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 3 | 1 | ECM |  | DH4SEA3640 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3640 |  | DH4SEA3640
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 5 | 13.416 | 208/1 | 29 | 35 | 153 | CU- | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 5 | 1 | ECM |  | DH4SEA3640 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3640 |  | DH4SEA3640
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 6 | 16.0992 | 208/1 | 34 | 40 | 153 | CU- | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 6 | 1 | ECM |  | DH4SEA3640 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3640 |  | DH4SEA3640
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 8 | 21.4655 | 208/1 | 43 | 50 | 153 | CU- | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 8 | 1 | ECM |  | DH4SEA3640 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3640 |  | DH4SEA3640
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 10 | 26.8319 | 208/1 | 50.5 | 60 | 153 | CU- | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 10 | 1 | ECM |  | DH4SEA3640 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3640 |  | DH4SEA3640
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 15 | 40.2479 | 208/1 | 72.1 | 80 | 153 | CU- | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 15 | 1 | ECM |  | DH4SEA3640 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3640 |  | DH4SEA3640
AHU- | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 19 | 50.9807 | 208/1 | 93.9 | 100 | 153 | CU- | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 |  | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 19 | 1 | ECM |  | DH4SEA3640 | AMST36CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA3640 |  | DH4SEA3640
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | - | - | 208/1 | 7.1 | 15 | 153 | CU- | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | - | 1 | ECM |  | DH4SEA4840 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4840 |  | DH4SEA4840
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 3 | 5.9869 | 208/1 | 20.7 | 25 | 153 | CU- | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 3 | 1 | ECM |  | DH4SEA4840 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4840 |  | DH4SEA4840
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 5 | 9.9781 | 208/1 | 29 | 30 | 153 | CU- | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 5 | 1 | ECM |  | DH4SEA4840 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4840 |  | DH4SEA4840
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 6 | 11.9738 | 208/1 | 34 | 35 | 153 | CU- | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 6 | 1 | ECM |  | DH4SEA4840 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4840 |  | DH4SEA4840
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 8 | 15.965 | 208/1 | 43 | 45 | 153 | CU- | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 8 | 1 | ECM |  | DH4SEA4840 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4840 |  | DH4SEA4840
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 10 | 19.9563 | 208/1 | 50.5 | 60 | 153 | CU- | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 10 | 1 | ECM |  | DH4SEA4840 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4840 |  | DH4SEA4840
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 15 | 29.9344 | 208/1 | 72.1 | 80 | 153 | CU- | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 15 | 1 | ECM |  | DH4SEA4840 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4840 |  | DH4SEA4840
AHU- | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 19 | 37.9169 | 208/1 | 93.9 | 100 | 153 | CU- | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 |  | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 19 | 1 | ECM |  | DH4SEA4840 | AMST48CU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA4840 |  | DH4SEA4840
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | - | 1 | ECM |  | DH4SEA6040 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6040 |  | DH4SEA6040
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 3 | 4.7895 | 208/1 | 22 | 25 | 167 | CU- | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 3 | 1 | ECM |  | DH4SEA6040 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6040 |  | DH4SEA6040
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 5 | 7.9825 | 208/1 | 30.3 | 35 | 167 | CU- | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 5 | 1 | ECM |  | DH4SEA6040 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6040 |  | DH4SEA6040
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 6 | 9.579 | 208/1 | 36 | 40 | 167 | CU- | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 6 | 1 | ECM |  | DH4SEA6040 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6040 |  | DH4SEA6040
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 8 | 12.772 | 208/1 | 45 | 45 | 167 | CU- | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 8 | 1 | ECM |  | DH4SEA6040 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6040 |  | DH4SEA6040
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 10 | 15.965 | 208/1 | 52 | 60 | 167 | CU- | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 10 | 1 | ECM |  | DH4SEA6040 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6040 |  | DH4SEA6040
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 15 | 23.9475 | 208/1 | 73.6 | 80 | 167 | CU- | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 15 | 1 | ECM |  | DH4SEA6040 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6040 |  | DH4SEA6040
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 20 | 31.93 | 208/1 | 95.3 | 100 | 167 | CU- | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 20 | 1 | ECM |  | DH4SEA6040 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6040 |  | DH4SEA6040
AHU- | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 25 | 39.9125 | 208/1 | 117 | 125 | 167 | CU- | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 |  | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 25 | 1 | ECM |  | DH4SEA6040 | AMST60DU1300 |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST | DH4SEA6040 |  | DH4SEA6040
AHU- | DAQ09033 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | - | - | 208/3 | 15.5 | 20 | 430 | CU- | DH6TE09030 | 47 | 85000 | 2.25 COP | 208/3 | 38.7 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 7.5 | HEAT PUMP | 16.0 IEER | 208/3 | - | 2 | ECM |  | DH6TE09030 | DAQ09033 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE09030 |  | DH6TE09030
AHU- | DAQ09033 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | 15 | 17.1054 | 208/3 | 54.8 | 60 | 430 | CU- | DH6TE09030 | 47 | 85000 | 2.25 COP | 208/3 | 38.7 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 7.5 | HEAT PUMP | 16.0 IEER | 208/3 | 15 | 2 | ECM |  | DH6TE09030 | DAQ09033 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE09030 |  | DH6TE09030
AHU- | DAQ09033 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | 20 | 22.8071 | 208/3 | 67.3 | 70 | 430 | CU- | DH6TE09030 | 47 | 85000 | 2.25 COP | 208/3 | 38.7 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 7.5 | HEAT PUMP | 16.0 IEER | 208/3 | 20 | 2 | ECM |  | DH6TE09030 | DAQ09033 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE09030 |  | DH6TE09030
AHU- | DAQ09033 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | 30 | 34.2107 | 208/3 | 92.3 | 100 | 430 | CU- | DH6TE09030 | 47 | 85000 | 2.25 COP | 208/3 | 38.7 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 7.5 | HEAT PUMP | 16.0 IEER | 208/3 | 30 | 2 | ECM |  | DH6TE09030 | DAQ09033 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE09030 |  | DH6TE09030
AHU- | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | - | - | 208/3 | 15.5 | 20 | 430 | CU- | DH6TE12030 | 47 | 97000 | 2.25 COP | 208/3 | 41.6 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 10 | HEAT PUMP | 16.0 IEER | 208/3 | - | 2 | ECM |  | DH6TE12030 | DAQ12033 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE12030 |  | DH6TE12030
AHU- | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | 15 | 12.6539 | 208/3 | 54.8 | 60 | 430 | CU- | DH6TE12030 | 47 | 97000 | 2.25 COP | 208/3 | 41.6 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 10 | HEAT PUMP | 16.0 IEER | 208/3 | 15 | 2 | ECM |  | DH6TE12030 | DAQ12033 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE12030 |  | DH6TE12030
AHU- | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | 20 | 16.8719 | 208/3 | 67.3 | 70 | 430 | CU- | DH6TE12030 | 47 | 97000 | 2.25 COP | 208/3 | 41.6 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 10 | HEAT PUMP | 16.0 IEER | 208/3 | 20 | 2 | ECM |  | DH6TE12030 | DAQ12033 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE12030 |  | DH6TE12030
AHU- | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | 30 | 25.3078 | 208/3 | 92.3 | 100 | 430 | CU- | DH6TE12030 | 47 | 97000 | 2.25 COP | 208/3 | 41.6 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 10 | HEAT PUMP | 16.0 IEER | 208/3 | 30 | 2 | ECM |  | DH6TE12030 | DAQ12033 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE12030 |  | DH6TE12030
AHU- | DAQ09034 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | - | - | 460/3 | 5.2 | 15 | 430 | CU- | DH6TE09040 | 47 | 85000 | 2.25 COP | 460/3 | 17.9 | 20 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 7.5 | HEAT PUMP | 16.0 IEER | 460/3 | - | 2 | ECM |  | DH6TE09040 | DAQ09034 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE09040 |  | DH6TE09040
AHU- | DAQ09034 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | 15 | 17.1054 | 460/3 | 27.4 | 30 | 430 | CU- | DH6TE09040 | 47 | 85000 | 2.25 COP | 460/3 | 17.9 | 20 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 7.5 | HEAT PUMP | 16.0 IEER | 460/3 | 15 | 2 | ECM |  | DH6TE09040 | DAQ09034 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE09040 |  | DH6TE09040
AHU- | DAQ09034 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | 20 | 22.8071 | 460/3 | 34.6 | 35 | 430 | CU- | DH6TE09040 | 47 | 85000 | 2.25 COP | 460/3 | 17.9 | 20 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 7.5 | HEAT PUMP | 16.0 IEER | 460/3 | 20 | 2 | ECM |  | DH6TE09040 | DAQ09034 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE09040 |  | DH6TE09040
AHU- | DAQ09034 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | 30 | 34.2107 | 460/3 | 49.1 | 50 | 430 | CU- | DH6TE09040 | 47 | 85000 | 2.25 COP | 460/3 | 17.9 | 20 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 7.5 | HEAT PUMP | 16.0 IEER | 460/3 | 30 | 2 | ECM |  | DH6TE09040 | DAQ09034 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE09040 |  | DH6TE09040
AHU- | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | - | - | 460/3 | 5.2 | 15 | 430 | CU- | DH6TE12040 | 47 | 97000 | 2.25 COP | 460/3 | 20.8 | 25 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 10 | HEAT PUMP | 16.0 IEER | 460/3 | - | 2 | ECM |  | DH6TE12040 | DAQ12034 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE12040 |  | DH6TE12040
AHU- | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | 15 | 12.6539 | 460/3 | 27.4 | 30 | 430 | CU- | DH6TE12040 | 47 | 97000 | 2.25 COP | 460/3 | 20.8 | 25 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 10 | HEAT PUMP | 16.0 IEER | 460/3 | 15 | 2 | ECM |  | DH6TE12040 | DAQ12034 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE12040 |  | DH6TE12040
AHU- | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | 20 | 16.8719 | 460/3 | 34.6 | 35 | 430 | CU- | DH6TE12040 | 47 | 97000 | 2.25 COP | 460/3 | 20.8 | 25 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 10 | HEAT PUMP | 16.0 IEER | 460/3 | 20 | 2 | ECM |  | DH6TE12040 | DAQ12034 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE12040 |  | DH6TE12040
AHU- | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | 30 | 25.3078 | 460/3 | 49.1 | 50 | 430 | CU- | DH6TE12040 | 47 | 97000 | 2.25 COP | 460/3 | 20.8 | 25 | 95 | R32 | 16.0 IEER | 417 | 2 |  | 10 | HEAT PUMP | 16.0 IEER | 460/3 | 30 | 2 | ECM |  | DH6TE12040 | DAQ12034 |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ | DH6TE12040 |  | DH6TE12040
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | - | - | 208/1 | 5.8 | 15 | 112 | CU- | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 |  | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DC4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | 3 | 15.45 | 208/1 | 19 | 20 | 112 | CU- | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 |  | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DC4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | 5 | 25.75 | 208/1 | 27 | 30 | 112 | CU- | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 |  | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DC4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | 6 | 30.9 | 208/1 | 32.8 | 35 | 112 | CU- | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 |  | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DC4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | 8 | 41.2 | 208/1 | 41.9 | 45 | 112 | CU- | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 |  | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DC4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | 10 | 51.5 | 208/1 | 49.1 | 50 | 112 | CU- | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 |  | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DC4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | 15 | 77.25 | 208/1 | 70.8 | 90 | 112 | CU- | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 |  | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DC4SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | - | - | 208/1 | 5.8 | 15 | 112 | CU- | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 |  | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DC4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | 3 | 12.6039 | 208/1 | 19 | 20 | 112 | CU- | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 |  | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DC4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | 5 | 21.0066 | 208/1 | 27 | 30 | 112 | CU- | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 |  | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DC4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | 6 | 25.2079 | 208/1 | 32.8 | 35 | 112 | CU- | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 |  | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DC4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | 8 | 33.6105 | 208/1 | 41.9 | 45 | 112 | CU- | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 |  | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DC4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | 10 | 42.0132 | 208/1 | 49.1 | 50 | 112 | CU- | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 |  | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DC4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | 15 | 63.0197 | 208/1 | 70.8 | 90 | 112 | CU- | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 |  | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DC4SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | - | - | 208/1 | 5.6 | 15 | 129 | CU- | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 |  | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DC4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | 3 | 10.0832 | 208/1 | 19 | 20 | 129 | CU- | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 |  | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DC4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | 5 | 16.8053 | 208/1 | 27 | 30 | 129 | CU- | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 |  | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DC4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | 6 | 20.1663 | 208/1 | 32.7 | 35 | 129 | CU- | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 |  | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DC4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | 8 | 26.8884 | 208/1 | 42 | 45 | 129 | CU- | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 |  | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DC4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | 10 | 33.6105 | 208/1 | 49 | 50 | 129 | CU- | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 |  | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DC4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | 15 | 50.4158 | 208/1 | 49.1 | 80 | 129 | CU- | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 |  | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DC4SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | - | - | 208/1 | 7.1 | 15 | 153 | CU- | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 |  | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DC4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 3 | 8.1872 | 208/1 | 20.7 | 25 | 153 | CU- | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 |  | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DC4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 5 | 13.6453 | 208/1 | 29 | 35 | 153 | CU- | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 |  | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DC4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 6 | 16.3744 | 208/1 | 34 | 40 | 153 | CU- | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 |  | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DC4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 8 | 21.8325 | 208/1 | 43 | 50 | 153 | CU- | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 |  | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DC4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 10 | 27.2906 | 208/1 | 50.5 | 60 | 153 | CU- | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 |  | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DC4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 15 | 40.9359 | 208/1 | 72.1 | 80 | 153 | CU- | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 |  | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DC4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 19 | 51.8521 | 208/1 | 93.9 | 100 | 153 | CU- | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 |  | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 19 | 1 | ECM |  | DC4SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | - | - | 208/1 | 5.9 | 15 | 153 | CU- | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 |  | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DC4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 3 | 6.8914 | 208/1 | 19 | 20 | 153 | CU- | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 |  | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DC4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 5 | 11.4856 | 208/1 | 28 | 30 | 153 | CU- | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 |  | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DC4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 6 | 13.7827 | 208/1 | 33 | 35 | 153 | CU- | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 |  | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DC4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 8 | 18.377 | 208/1 | 42 | 45 | 153 | CU- | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 |  | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DC4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 10 | 22.9712 | 208/1 | 49 | 50 | 153 | CU- | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 |  | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DC4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 15 | 34.4568 | 208/1 | 70.9 | 80 | 153 | CU- | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 |  | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DC4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 19 | 43.6453 | 208/1 | 92.5 | 100 | 153 | CU- | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 |  | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 19 | 1 | ECM |  | DC4SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | - | - | 208/1 | 7.1 | 15 | 153 | CU- | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 |  | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DC4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 3 | 6.7458 | 208/1 | 20.7 | 25 | 153 | CU- | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 |  | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DC4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 5 | 11.243 | 208/1 | 29 | 30 | 153 | CU- | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 |  | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DC4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 6 | 13.4915 | 208/1 | 34 | 35 | 153 | CU- | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 |  | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DC4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 8 | 17.9887 | 208/1 | 43 | 45 | 153 | CU- | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 |  | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DC4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 10 | 22.4859 | 208/1 | 50.5 | 60 | 153 | CU- | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 |  | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DC4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 15 | 33.7289 | 208/1 | 72.1 | 80 | 153 | CU- | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 |  | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DC4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 19 | 42.7232 | 208/1 | 93.9 | 100 | 153 | CU- | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 |  | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 19 | 1 | ECM |  | DC4SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 |  | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM |  | DC4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 3 | 5.913 | 208/1 | 22 | 25 | 167 | CU- | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 |  | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM |  | DC4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 5 | 9.8549 | 208/1 | 30.3 | 35 | 167 | CU- | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 |  | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM |  | DC4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 6 | 11.8259 | 208/1 | 36 | 40 | 167 | CU- | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 |  | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM |  | DC4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 8 | 15.7679 | 208/1 | 45 | 45 | 167 | CU- | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 |  | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM |  | DC4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 10 | 19.7099 | 208/1 | 52 | 60 | 167 | CU- | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 |  | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM |  | DC4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 15 | 29.5648 | 208/1 | 73.6 | 80 | 167 | CU- | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 |  | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM |  | DC4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 20 | 39.4198 | 208/1 | 95.3 | 100 | 167 | CU- | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 |  | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 20 | 1 | ECM |  | DC4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 25 | 49.2747 | 208/1 | 117 | 125 | 167 | CU- | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 |  | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 25 | 1 | ECM |  | DC4SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | - | - | 208/1 | 5.8 | 15 | 112 | CU- | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 |  | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM |  | DC5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | 3 | 15.45 | 208/1 | 19 | 20 | 112 | CU- | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 |  | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM |  | DC5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | 5 | 25.75 | 208/1 | 27 | 30 | 112 | CU- | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 |  | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM |  | DC5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | 6 | 30.9 | 208/1 | 32.8 | 35 | 112 | CU- | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 |  | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM |  | DC5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | 8 | 41.2 | 208/1 | 41.9 | 45 | 112 | CU- | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 |  | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM |  | DC5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | 10 | 51.5 | 208/1 | 49.1 | 50 | 112 | CU- | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 |  | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM |  | DC5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | 15 | 77.25 | 208/1 | 70.8 | 90 | 112 | CU- | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 |  | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM |  | DC5SEA1810 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | - | - | 208/1 | 5.8 | 15 | 112 | CU- | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 |  | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM |  | DC5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | 3 | 12.6039 | 208/1 | 19 | 20 | 112 | CU- | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 |  | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM |  | DC5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | 5 | 21.0066 | 208/1 | 27 | 30 | 112 | CU- | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 |  | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM |  | DC5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | 6 | 25.2079 | 208/1 | 32.8 | 35 | 112 | CU- | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 |  | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM |  | DC5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | 8 | 33.6105 | 208/1 | 41.9 | 45 | 112 | CU- | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 |  | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM |  | DC5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | 10 | 42.0132 | 208/1 | 49.1 | 50 | 112 | CU- | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 |  | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM |  | DC5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | 15 | 63.0197 | 208/1 | 70.8 | 90 | 112 | CU- | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 |  | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM |  | DC5SEA2410 | AMST24BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | - | - | 208/1 | 5.6 | 15 | 129 | CU- | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 |  | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM |  | DC5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | 3 | 10.0832 | 208/1 | 19 | 20 | 129 | CU- | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 |  | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM |  | DC5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | 5 | 16.8053 | 208/1 | 27 | 30 | 129 | CU- | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 |  | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM |  | DC5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | 6 | 20.1663 | 208/1 | 32.7 | 35 | 129 | CU- | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 |  | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM |  | DC5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | 8 | 26.8884 | 208/1 | 42 | 45 | 129 | CU- | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 |  | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM |  | DC5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | 10 | 33.6105 | 208/1 | 49 | 50 | 129 | CU- | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 |  | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM |  | DC5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | 15 | 50.4158 | 208/1 | 49.1 | 80 | 129 | CU- | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 |  | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM |  | DC5SEA3010 | AMST30BU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | - | - | 208/1 | 7.1 | 15 | 153 | CU- | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 |  | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM |  | DC5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 3 | 8.1872 | 208/1 | 20.7 | 25 | 153 | CU- | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 |  | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM |  | DC5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 5 | 13.6453 | 208/1 | 29 | 35 | 153 | CU- | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 |  | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM |  | DC5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 6 | 16.3744 | 208/1 | 34 | 40 | 153 | CU- | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 |  | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM |  | DC5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 8 | 21.8325 | 208/1 | 43 | 50 | 153 | CU- | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 |  | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM |  | DC5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 10 | 27.2906 | 208/1 | 50.5 | 60 | 153 | CU- | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 |  | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM |  | DC5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 15 | 40.9359 | 208/1 | 72.1 | 80 | 153 | CU- | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 |  | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM |  | DC5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 19 | 51.8521 | 208/1 | 93.9 | 100 | 153 | CU- | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 |  | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 19 | 1 | ECM |  | DC5SEA3610 | AMST36CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | - | - | 208/1 | 5.9 | 15 | 153 | CU- | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 |  | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM |  | DC5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 3 | 7.2023 | 208/1 | 19 | 20 | 153 | CU- | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 |  | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM |  | DC5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 5 | 12.0038 | 208/1 | 28 | 30 | 153 | CU- | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 |  | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM |  | DC5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 6 | 14.4045 | 208/1 | 33 | 35 | 153 | CU- | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 |  | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM |  | DC5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 8 | 19.206 | 208/1 | 42 | 45 | 153 | CU- | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 |  | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM |  | DC5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 10 | 24.0075 | 208/1 | 49 | 50 | 153 | CU- | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 |  | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM |  | DC5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 15 | 36.0113 | 208/1 | 70.9 | 80 | 153 | CU- | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 |  | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM |  | DC5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 19 | 45.6143 | 208/1 | 92.5 | 100 | 153 | CU- | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 |  | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 19 | 1 | ECM |  | DC5SEA4210 | AMST42CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | - | - | 208/1 | 7.1 | 15 | 153 | CU- | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 |  | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM |  | DC5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 3 | 6.7458 | 208/1 | 20.7 | 25 | 153 | CU- | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 |  | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM |  | DC5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 5 | 11.243 | 208/1 | 29 | 30 | 153 | CU- | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 |  | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM |  | DC5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 6 | 13.4915 | 208/1 | 34 | 35 | 153 | CU- | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 |  | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM |  | DC5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 8 | 17.9887 | 208/1 | 43 | 45 | 153 | CU- | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 |  | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM |  | DC5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 10 | 22.4859 | 208/1 | 50.5 | 60 | 153 | CU- | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 |  | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM |  | DC5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 15 | 33.7289 | 208/1 | 72.1 | 80 | 153 | CU- | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 |  | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM |  | DC5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 19 | 42.7232 | 208/1 | 93.9 | 100 | 153 | CU- | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 |  | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 19 | 1 | ECM |  | DC5SEA4810 | AMST48CU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 |  | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM |  | DC5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 3 | 5.3217 | 208/1 | 22 | 25 | 167 | CU- | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 |  | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM |  | DC5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 5 | 8.8694 | 208/1 | 30.3 | 35 | 167 | CU- | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 |  | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM |  | DC5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 6 | 10.6433 | 208/1 | 36 | 40 | 167 | CU- | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 |  | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM |  | DC5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 8 | 14.1911 | 208/1 | 45 | 45 | 167 | CU- | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 |  | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM |  | DC5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 10 | 17.7389 | 208/1 | 52 | 60 | 167 | CU- | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 |  | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM |  | DC5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 15 | 26.6083 | 208/1 | 73.6 | 80 | 167 | CU- | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 |  | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM |  | DC5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 20 | 35.4778 | 208/1 | 95.3 | 100 | 167 | CU- | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 |  | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 20 | 1 | ECM |  | DC5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 25 | 44.3472 | 208/1 | 117 | 125 | 167 | CU- | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 |  | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 25 | 1 | ECM |  | DC5SEA6010 | AMST60DU1300 |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST
AHU- | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | - | - | - | 208/1 | 4.9 | 15 | 115 | CU- | DC6VSS1810 | - | - | - | 208/1 | 12.8 | 15 | 95 | R32 | 18.5/12.0 (SEER2/EER2) | 119 | Inverter |  | 1.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DC6VSS1810 | DFVE24BP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS1810 |  | DC6VSS1810
AHU- | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | - | 3 | 15.7033 | 208/1 | 18.4 | 20 | 115 | CU- | DC6VSS1810 | - | - | - | 208/1 | 12.8 | 15 | 95 | R32 | 18.5/12.0 (SEER2/EER2) | 119 | Inverter |  | 1.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 3 | Inverter | Variable Speed ECM |  | DC6VSS1810 | DFVE24BP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS1810 |  | DC6VSS1810
AHU- | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | - | 5 | 26.1721 | 208/1 | 26.5 | 30 | 115 | CU- | DC6VSS1810 | - | - | - | 208/1 | 12.8 | 15 | 95 | R32 | 18.5/12.0 (SEER2/EER2) | 119 | Inverter |  | 1.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DC6VSS1810 | DFVE24BP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS1810 |  | DC6VSS1810
AHU- | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | - | 6 | 31.4066 | 208/1 | 32 | 35 | 115 | CU- | DC6VSS1810 | - | - | - | 208/1 | 12.8 | 15 | 95 | R32 | 18.5/12.0 (SEER2/EER2) | 119 | Inverter |  | 1.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DC6VSS1810 | DFVE24BP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS1810 |  | DC6VSS1810
AHU- | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | - | 8 | 41.8754 | 208/1 | 41 | 45 | 115 | CU- | DC6VSS1810 | - | - | - | 208/1 | 12.8 | 15 | 95 | R32 | 18.5/12.0 (SEER2/EER2) | 119 | Inverter |  | 1.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DC6VSS1810 | DFVE24BP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS1810 |  | DC6VSS1810
AHU- | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | - | 10 | 52.3443 | 208/1 | 48.5 | 50 | 115 | CU- | DC6VSS1810 | - | - | - | 208/1 | 12.8 | 15 | 95 | R32 | 18.5/12.0 (SEER2/EER2) | 119 | Inverter |  | 1.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DC6VSS1810 | DFVE24BP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS1810 |  | DC6VSS1810
AHU- | DFVE24BP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | - | - | - | 208/1 | 4.9 | 15 | 115 | CU- | DC6VSS2410 | - | - | - | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 119 | Inverter |  | 2 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DC6VSS2410 | DFVE24BP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS2410 |  | DC6VSS2410
AHU- | DFVE24BP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | - | 3 | 11.9738 | 208/1 | 18.4 | 20 | 115 | CU- | DC6VSS2410 | - | - | - | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 119 | Inverter |  | 2 | COOLING ONLY | 16.2 SEER2 | 208/1 | 3 | Inverter | Variable Speed ECM |  | DC6VSS2410 | DFVE24BP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS2410 |  | DC6VSS2410
AHU- | DFVE24BP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | - | 5 | 19.9563 | 208/1 | 26.5 | 30 | 115 | CU- | DC6VSS2410 | - | - | - | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 119 | Inverter |  | 2 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DC6VSS2410 | DFVE24BP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS2410 |  | DC6VSS2410
AHU- | DFVE24BP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | - | 6 | 23.9475 | 208/1 | 32 | 35 | 115 | CU- | DC6VSS2410 | - | - | - | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 119 | Inverter |  | 2 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DC6VSS2410 | DFVE24BP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS2410 |  | DC6VSS2410
AHU- | DFVE24BP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | - | 8 | 31.93 | 208/1 | 41 | 45 | 115 | CU- | DC6VSS2410 | - | - | - | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 119 | Inverter |  | 2 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DC6VSS2410 | DFVE24BP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS2410 |  | DC6VSS2410
AHU- | DFVE24BP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | - | 10 | 39.9125 | 208/1 | 48.5 | 50 | 115 | CU- | DC6VSS2410 | - | - | - | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 119 | Inverter |  | 2 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DC6VSS2410 | DFVE24BP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS2410 |  | DC6VSS2410
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | - | - | 208/1 | 6.5 | 15 | 140 | CU- | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter |  | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DC6VSS3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3010 |  | DC6VSS3010
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | 5 | 15.8069 | 208/1 | 28.1 | 30 | 140 | CU- | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter |  | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DC6VSS3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3010 |  | DC6VSS3010
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | 6 | 18.9683 | 208/1 | 33.6 | 35 | 140 | CU- | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter |  | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DC6VSS3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3010 |  | DC6VSS3010
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | 8 | 25.2911 | 208/1 | 42.6 | 45 | 140 | CU- | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter |  | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DC6VSS3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3010 |  | DC6VSS3010
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | 10 | 31.6139 | 208/1 | 49.9 | 50 | 140 | CU- | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter |  | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DC6VSS3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3010 |  | DC6VSS3010
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | 15 | 47.4208 | 208/1 | 71.5 | 80 | 140 | CU- | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter |  | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DC6VSS3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3010 |  | DC6VSS3010
AHU- | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | 19 | 60.0663 | 208/1 | 93.2 | 100 | 140 | CU- | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter |  | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 19 | Inverter | Variable Speed ECM |  | DC6VSS3010 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3010 |  | DC6VSS3010
AHU- | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | - | - | 208/1 | 6.5 | 15 | 140 | CU- | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter |  | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DC6VSS3610 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3610 |  | DC6VSS3610
AHU- | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | 5 | 12.6706 | 208/1 | 28.1 | 30 | 140 | CU- | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter |  | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DC6VSS3610 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3610 |  | DC6VSS3610
AHU- | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | 6 | 15.2048 | 208/1 | 33.6 | 35 | 140 | CU- | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter |  | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DC6VSS3610 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3610 |  | DC6VSS3610
AHU- | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | 8 | 20.273 | 208/1 | 42.6 | 45 | 140 | CU- | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter |  | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DC6VSS3610 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3610 |  | DC6VSS3610
AHU- | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | 10 | 25.3413 | 208/1 | 49.9 | 50 | 140 | CU- | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter |  | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DC6VSS3610 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3610 |  | DC6VSS3610
AHU- | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | 15 | 38.0119 | 208/1 | 71.5 | 80 | 140 | CU- | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter |  | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DC6VSS3610 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3610 |  | DC6VSS3610
AHU- | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | 19 | 48.1484 | 208/1 | 93.2 | 100 | 140 | CU- | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter |  | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | 19 | Inverter | Variable Speed ECM |  | DC6VSS3610 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS3610 |  | DC6VSS3610
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | - | - | 208/1 | 6.5 | 15 | 150 | CU- | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DC6VSS4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4210 |  | DC6VSS4210
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | 5 | 12.0947 | 208/1 | 28.1 | 30 | 150 | CU- | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DC6VSS4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4210 |  | DC6VSS4210
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | 6 | 14.5136 | 208/1 | 33.6 | 35 | 150 | CU- | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DC6VSS4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4210 |  | DC6VSS4210
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | 8 | 19.3515 | 208/1 | 42.6 | 45 | 150 | CU- | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DC6VSS4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4210 |  | DC6VSS4210
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | 10 | 24.1894 | 208/1 | 49.9 | 50 | 150 | CU- | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DC6VSS4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4210 |  | DC6VSS4210
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | 15 | 36.2841 | 208/1 | 71.5 | 80 | 150 | CU- | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DC6VSS4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4210 |  | DC6VSS4210
AHU- | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | 20 | 48.3788 | 208/1 | 93.2 | 100 | 150 | CU- | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DC6VSS4210 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4210 |  | DC6VSS4210
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | - | - | 208/1 | 6.5 | 15 | 150 | CU- | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DC6VSS4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4810 |  | DC6VSS4810
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | 5 | 11.5688 | 208/1 | 28.1 | 30 | 150 | CU- | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DC6VSS4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4810 |  | DC6VSS4810
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | 6 | 13.8826 | 208/1 | 33.6 | 35 | 150 | CU- | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DC6VSS4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4810 |  | DC6VSS4810
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | 8 | 18.5101 | 208/1 | 42.6 | 45 | 150 | CU- | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DC6VSS4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4810 |  | DC6VSS4810
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | 10 | 23.1377 | 208/1 | 49.9 | 50 | 150 | CU- | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DC6VSS4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4810 |  | DC6VSS4810
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | 15 | 34.7065 | 208/1 | 71.5 | 80 | 150 | CU- | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DC6VSS4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4810 |  | DC6VSS4810
AHU- | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | 20 | 46.2754 | 208/1 | 93.2 | 100 | 150 | CU- | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter |  | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DC6VSS4810 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS4810 |  | DC6VSS4810
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter |  | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DC6VSS6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS6010 |  | DC6VSS6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 5 | 9.7348 | 208/1 | 30.2 | 35 | 167 | CU- | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter |  | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DC6VSS6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS6010 |  | DC6VSS6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 6 | 11.6817 | 208/1 | 35.8 | 40 | 167 | CU- | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter |  | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DC6VSS6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS6010 |  | DC6VSS6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 8 | 15.5756 | 208/1 | 44.8 | 45 | 167 | CU- | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter |  | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DC6VSS6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS6010 |  | DC6VSS6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 10 | 19.4695 | 208/1 | 52 | 60 | 167 | CU- | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter |  | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DC6VSS6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS6010 |  | DC6VSS6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 15 | 29.2043 | 208/1 | 73.6 | 80 | 167 | CU- | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter |  | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DC6VSS6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS6010 |  | DC6VSS6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 20 | 38.939 | 208/1 | 95.3 | 100 | 167 | CU- | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter |  | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DC6VSS6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS6010 |  | DC6VSS6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 25 | 48.6738 | 208/1 | 117 | 125 | 167 | CU- | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter |  | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM |  | DC6VSS6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE | DC6VSS6010 |  | DC6VSS6010
AHU- | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | - | - | 208/1 | 4.9 | 15 | 129 | CU- | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 |  | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM |  | DC7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | 3 | 11.4036 | 208/1 | 18.4 | 20 | 129 | CU- | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 |  | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | 3 | 2 | Variable Speed ECM |  | DC7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | 5 | 19.006 | 208/1 | 26.5 | 30 | 129 | CU- | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 |  | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM |  | DC7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | 6 | 22.8071 | 208/1 | 32 | 35 | 129 | CU- | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 |  | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM |  | DC7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | 8 | 30.4095 | 208/1 | 41 | 45 | 129 | CU- | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 |  | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM |  | DC7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | 10 | 38.0119 | 208/1 | 48.2 | 50 | 129 | CU- | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 |  | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM |  | DC7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | 15 | 57.0179 | 208/1 | 69.9 | 70 | 129 | CU- | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 |  | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM |  | DC7TCA2410 | DMVT30BP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | - | - | 208/1 | 6.5 | 15 | 153 | CU- | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 |  | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM |  | DC7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | 5 | 14.2545 | 208/1 | 28.2 | 35 | 153 | CU- | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 |  | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM |  | DC7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | 6 | 17.1054 | 208/1 | 33.6 | 40 | 153 | CU- | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 |  | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM |  | DC7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | 8 | 22.8071 | 208/1 | 42.6 | 50 | 153 | CU- | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 |  | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM |  | DC7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | 10 | 28.5089 | 208/1 | 49.8 | 60 | 153 | CU- | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 |  | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM |  | DC7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | 15 | 42.7634 | 208/1 | 71.5 | 80 | 153 | CU- | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 |  | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM |  | DC7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | 19 | 54.167 | 208/1 | 93.2 | 100 | 153 | CU- | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 |  | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | 19 | 2 | Variable Speed ECM |  | DC7TCA3610 | DMVT42CP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 |  | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM |  | DC7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 5 | 11.6533 | 208/1 | 30.3 | 35 | 167 | CU- | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 |  | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM |  | DC7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 6 | 13.9839 | 208/1 | 35.7 | 40 | 167 | CU- | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 |  | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM |  | DC7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 8 | 18.6453 | 208/1 | 44.7 | 45 | 167 | CU- | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 |  | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM |  | DC7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 10 | 23.3066 | 208/1 | 52 | 60 | 167 | CU- | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 |  | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM |  | DC7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 15 | 34.9599 | 208/1 | 73.6 | 80 | 167 | CU- | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 |  | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM |  | DC7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 20 | 46.6131 | 208/1 | 95.3 | 100 | 167 | CU- | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 |  | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 20 | 2 | Variable Speed ECM |  | DC7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 25 | 58.2664 | 208/1 | 117 | 125 | 167 | CU- | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 |  | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 25 | 2 | Variable Speed ECM |  | DC7TCA4810 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 |  | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM |  | DC7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 5 | 8.8694 | 208/1 | 30.3 | 35 | 167 | CU- | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 |  | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM |  | DC7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 6 | 10.6433 | 208/1 | 35.7 | 40 | 167 | CU- | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 |  | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM |  | DC7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 8 | 14.1911 | 208/1 | 44.7 | 45 | 167 | CU- | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 |  | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM |  | DC7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 10 | 17.7389 | 208/1 | 52 | 60 | 167 | CU- | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 |  | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM |  | DC7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 15 | 26.6083 | 208/1 | 73.6 | 80 | 167 | CU- | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 |  | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM |  | DC7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 20 | 35.4778 | 208/1 | 95.3 | 100 | 167 | CU- | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 |  | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 20 | 2 | Variable Speed ECM |  | DC7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 25 | 44.3472 | 208/1 | 117 | 125 | 167 | CU- | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 |  | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 25 | 2 | Variable Speed ECM |  | DC7TCA6010 | DMVT60DP1300 |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT
AHU- | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | - | - | 208/1 | 6.5 | 15 | 140 | CU- | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter |  | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DC9VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA2410 |  | DC9VSA2410
AHU- | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | 5 | 19.9563 | 208/1 | 28.1 | 30 | 140 | CU- | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter |  | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DC9VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA2410 |  | DC9VSA2410
AHU- | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | 6 | 23.9475 | 208/1 | 33.6 | 35 | 140 | CU- | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter |  | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DC9VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA2410 |  | DC9VSA2410
AHU- | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | 8 | 31.93 | 208/1 | 42.6 | 45 | 140 | CU- | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter |  | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DC9VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA2410 |  | DC9VSA2410
AHU- | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | 10 | 39.9125 | 208/1 | 49.9 | 50 | 140 | CU- | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter |  | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DC9VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA2410 |  | DC9VSA2410
AHU- | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | 15 | 59.8687 | 208/1 | 71.5 | 80 | 140 | CU- | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter |  | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DC9VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA2410 |  | DC9VSA2410
AHU- | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | 19 | 75.8337 | 208/1 | 93.2 | 100 | 140 | CU- | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter |  | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | 19 | Inverter | Variable Speed ECM |  | DC9VSA2410 | DFVE36CP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA2410 |  | DC9VSA2410
AHU- | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | - | - | 208/1 | 6.5 | 15 | 150 | CU- | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter |  | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DC9VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA3610 |  | DC9VSA3610
AHU- | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | 5 | 12.6706 | 208/1 | 28.1 | 30 | 150 | CU- | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter |  | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DC9VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA3610 |  | DC9VSA3610
AHU- | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | 6 | 15.2048 | 208/1 | 33.6 | 35 | 150 | CU- | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter |  | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DC9VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA3610 |  | DC9VSA3610
AHU- | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | 8 | 20.273 | 208/1 | 42.6 | 45 | 150 | CU- | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter |  | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DC9VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA3610 |  | DC9VSA3610
AHU- | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | 10 | 25.3413 | 208/1 | 49.9 | 50 | 150 | CU- | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter |  | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DC9VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA3610 |  | DC9VSA3610
AHU- | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | 15 | 38.0119 | 208/1 | 71.5 | 80 | 150 | CU- | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter |  | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DC9VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA3610 |  | DC9VSA3610
AHU- | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | 20 | 50.6825 | 208/1 | 93.2 | 100 | 150 | CU- | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter |  | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DC9VSA3610 | DFVE48DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA3610 |  | DC9VSA3610
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter |  | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DC9VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA4810 |  | DC9VSA4810
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 5 | 11.5688 | 208/1 | 30.2 | 35 | 167 | CU- | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter |  | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DC9VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA4810 |  | DC9VSA4810
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 6 | 13.8826 | 208/1 | 35.8 | 40 | 167 | CU- | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter |  | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DC9VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA4810 |  | DC9VSA4810
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 8 | 18.5101 | 208/1 | 44.8 | 45 | 167 | CU- | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter |  | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DC9VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA4810 |  | DC9VSA4810
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 10 | 23.1377 | 208/1 | 52 | 60 | 167 | CU- | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter |  | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DC9VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA4810 |  | DC9VSA4810
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 15 | 34.7065 | 208/1 | 73.6 | 80 | 167 | CU- | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter |  | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DC9VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA4810 |  | DC9VSA4810
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 20 | 46.2754 | 208/1 | 95.3 | 100 | 167 | CU- | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter |  | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DC9VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA4810 |  | DC9VSA4810
AHU- | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 25 | 57.8442 | 208/1 | 117 | 125 | 167 | CU- | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter |  | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM |  | DC9VSA4810 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA4810 |  | DC9VSA4810
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | - | - | 208/1 | 8.6 | 15 | 167 | CU- | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter |  | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | - | Inverter | Variable Speed ECM |  | DC9VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA6010 |  | DC9VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 5 | 9.7348 | 208/1 | 30.2 | 35 | 167 | CU- | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter |  | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM |  | DC9VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA6010 |  | DC9VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 6 | 11.6817 | 208/1 | 35.8 | 40 | 167 | CU- | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter |  | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM |  | DC9VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA6010 |  | DC9VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 8 | 15.5756 | 208/1 | 44.8 | 45 | 167 | CU- | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter |  | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM |  | DC9VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA6010 |  | DC9VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 10 | 19.4695 | 208/1 | 52 | 60 | 167 | CU- | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter |  | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM |  | DC9VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA6010 |  | DC9VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 15 | 29.2043 | 208/1 | 73.6 | 80 | 167 | CU- | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter |  | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM |  | DC9VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA6010 |  | DC9VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 20 | 38.939 | 208/1 | 95.3 | 100 | 167 | CU- | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter |  | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM |  | DC9VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA6010 |  | DC9VSA6010
AHU- | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 25 | 48.6738 | 208/1 | 117 | 125 | 167 | CU- | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter |  | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM |  | DC9VSA6010 | DFVE60DP1300 |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE | DC9VSA6010 |  | DC9VSA6010
AHU- | DAQ09033 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | - | - | 208/3 | 15.5 | 20 | 430 | CU- | DC6TE09030 | - | - | - | 208/3 | 38.7 | 50 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 7.5 | COOLING ONLY | 16.4 IEER | 208/3 | - | 2 | ECM |  | DC6TE09030 | DAQ09033 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ09033 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | 15 | 12.6539 | 208/3 | 54.8 | 60 | 430 | CU- | DC6TE09030 | - | - | - | 208/3 | 38.7 | 50 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 7.5 | COOLING ONLY | 16.4 IEER | 208/3 | 15 | 2 | ECM |  | DC6TE09030 | DAQ09033 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ09033 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | 20 | 16.8719 | 208/3 | 67.3 | 70 | 430 | CU- | DC6TE09030 | - | - | - | 208/3 | 38.7 | 50 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 7.5 | COOLING ONLY | 16.4 IEER | 208/3 | 20 | 2 | ECM |  | DC6TE09030 | DAQ09033 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ09033 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | 30 | 25.3078 | 208/3 | 92.3 | 100 | 430 | CU- | DC6TE09030 | - | - | - | 208/3 | 38.7 | 50 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 7.5 | COOLING ONLY | 16.4 IEER | 208/3 | 30 | 2 | ECM |  | DC6TE09030 | DAQ09033 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | - | - | 208/3 | 15.5 | 20 | 430 | CU- | DC6TE12030 | - | - | - | 208/3 | 45.9 | 60 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 10 | COOLING ONLY | 16.4 IEER | 208/3 | - | 2 | ECM |  | DC6TE12030 | DAQ12033 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | 15 | 12.6539 | 208/3 | 54.8 | 60 | 430 | CU- | DC6TE12030 | - | - | - | 208/3 | 45.9 | 60 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 10 | COOLING ONLY | 16.4 IEER | 208/3 | 15 | 2 | ECM |  | DC6TE12030 | DAQ12033 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | 20 | 16.8719 | 208/3 | 67.3 | 70 | 430 | CU- | DC6TE12030 | - | - | - | 208/3 | 45.9 | 60 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 10 | COOLING ONLY | 16.4 IEER | 208/3 | 20 | 2 | ECM |  | DC6TE12030 | DAQ12033 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | 30 | 25.3078 | 208/3 | 92.3 | 100 | 430 | CU- | DC6TE12030 | - | - | - | 208/3 | 45.9 | 60 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 10 | COOLING ONLY | 16.4 IEER | 208/3 | 30 | 2 | ECM |  | DC6TE12030 | DAQ12033 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ09034 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | - | - | 460/3 | 5.2 | 15 | 430 | CU- | DC6TE09040 | - | - | - | 460/3 | 17.9 | 20 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 7.5 | COOLING ONLY | 16.4 IEER | 460/3 | - | 2 | ECM |  | DC6TE09040 | DAQ09034 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ09034 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | 15 | 12.6539 | 460/3 | 27.4 | 30 | 430 | CU- | DC6TE09040 | - | - | - | 460/3 | 17.9 | 20 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 7.5 | COOLING ONLY | 16.4 IEER | 460/3 | 15 | 2 | ECM |  | DC6TE09040 | DAQ09034 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ09034 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | 20 | 16.8719 | 460/3 | 34.6 | 35 | 430 | CU- | DC6TE09040 | - | - | - | 460/3 | 17.9 | 20 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 7.5 | COOLING ONLY | 16.4 IEER | 460/3 | 20 | 2 | ECM |  | DC6TE09040 | DAQ09034 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ09034 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | 30 | 25.3078 | 460/3 | 49.1 | 50 | 430 | CU- | DC6TE09040 | - | - | - | 460/3 | 17.9 | 20 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 7.5 | COOLING ONLY | 16.4 IEER | 460/3 | 30 | 2 | ECM |  | DC6TE09040 | DAQ09034 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | - | - | 460/3 | 5.2 | 15 | 430 | CU- | DC6TE12040 | - | - | - | 460/3 | 20.8 | 25 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 10 | COOLING ONLY | 16.4 IEER | 460/3 | - | 2 | ECM |  | DC6TE12040 | DAQ12034 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | 15 | 12.6539 | 460/3 | 27.4 | 30 | 430 | CU- | DC6TE12040 | - | - | - | 460/3 | 20.8 | 25 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 10 | COOLING ONLY | 16.4 IEER | 460/3 | 15 | 2 | ECM |  | DC6TE12040 | DAQ12034 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | 20 | 16.8719 | 460/3 | 34.6 | 35 | 430 | CU- | DC6TE12040 | - | - | - | 460/3 | 20.8 | 25 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 10 | COOLING ONLY | 16.4 IEER | 460/3 | 20 | 2 | ECM |  | DC6TE12040 | DAQ12034 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ
AHU- | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | 30 | 25.3078 | 460/3 | 49.1 | 50 | 430 | CU- | DC6TE12040 | - | - | - | 460/3 | 20.8 | 25 | 95 | R32 | 16.4 IEER | 381 | 2 |  | 10 | COOLING ONLY | 16.4 IEER | 460/3 | 30 | 2 | ECM |  | DC6TE12040 | DAQ12034 |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ

## Schedule Notes
Provide with 7-day programmable thermostat
Provide with 7-day programmable BACnet thermostat
Provide with field installed disconnect. Disconnect shall be provided and installed by electrical contractor
Electric heat, if scheduled, shall be single point power. kW listed is at 240V & temperature rise has 0.75 multiplier applied for 230V