## SCHEDULE
SCHEDULE RANGE | [12 empty] | FILTERS |  |  |  | DOCUMENTATION
VFD Schedule | [12 empty] | HP | ELECTRICAL | ENCLOSURE | HARMONIC MITIGATION | SUBMITTAL (OUTDOOR UNIT) | SUBMITTAL (INDOOR UNIT) | SUBMITTAL (SYSTEM) | ENGINEERING MANUAL (SYSTEM) | ENGINEERING MANUAL (OUTDOOR UNIT) | ENGINEERING MANUAL (INDOOR UNIT) | CAPACITY TABLE | INSTALLATION MANUAL (OUTDOOR) | INSTALLATION MANUAL (INDOOR) | INSTALLATION MANUAL (SYSTEM) | REVIT (OUTDOOR) | REVIT (INDOOR) | REVIT (SYSTEM) | CAD (OUTDOOR) | CAD (INDOOR) | CAD (SYSTEM) | CONTROLS OPTIONS | OPERATION MANUAL
VFD Tag | Servicing | Motor Data |  |  | Enclosure Rating | Harmonic Mitigation | Disconnect | Bypass | Communications | VFD Min. SCCR | Basis of Design | Notes
|  | Qty | Voltage | HP (ea)
|  | 1 | 460V | 1 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-02A1-4 | 1, 2, 3, 4, 5, 6, 10 | 1 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 1.5 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-03A0-4 | 1, 2, 3, 4, 5, 6, 10 | 1.5 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 2 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-03A5-4 | 1, 2, 3, 4, 5, 6, 10 | 2 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 3 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-04A8-4 | 1, 2, 3, 4, 5, 6, 10 | 3 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 5 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-07A6-4 | 1, 2, 3, 4, 5, 6, 10 | 5 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 7.5 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-012A-4 | 1, 2, 3, 4, 5, 6, 10 | 7.5 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 10 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-014A-4 | 1, 2, 3, 4, 5, 6, 10 | 10 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 15 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-023A-4 | 1, 2, 3, 4, 5, 6, 10 | 15 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 20 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-027A-4 | 1, 2, 3, 4, 5, 6, 10 | 20 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 25 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-034A-4 | 1, 2, 3, 4, 5, 6, 10 | 25 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 30 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-044A-4 | 1, 2, 3, 4, 5, 6, 10 | 30 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 40 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-052A-4 | 1, 2, 3, 4, 5, 6, 10 | 40 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 50 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-065A-4 | 1, 2, 3, 4, 5, 6, 10 | 50 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 60 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-077A-4 | 1, 2, 3, 4, 5, 6, 10 | 60 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 75 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-096A-4 | 1, 2, 3, 4, 5, 6, 10 | 75 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 100 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-124A-4 | 1, 2, 3, 4, 5, 6, 10 | 100 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 125 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-156A-4 | 1, 2, 3, 4, 5, 6, 10 | 125 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 150 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-180A-4 | 1, 2, 3, 4, 5, 6, 10 | 150 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 200 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-240A-4 | 1, 2, 3, 4, 5, 6, 10 | 200 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 250 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-302A-4 | 1, 2, 3, 4, 5, 6, 10 | 250 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 300 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-361A-4 | 1, 2, 3, 4, 5, 6, 10 | 300 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 350 | UL Type 1 | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-414A-4 | 1, 2, 3, 4, 5, 6, 10 | 350 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 1 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-02A1-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 1 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 1.5 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-03A0-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 1.5 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 2 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-03A5-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 2 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 3 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-04A8-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 3 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 5 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-07A6-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 5 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 7.5 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-012A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 7.5 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 10 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-014A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 10 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 15 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-023A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 15 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 20 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-027A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 20 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 25 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-034A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 25 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 30 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-044A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 30 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 40 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-052A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 40 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 50 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-065A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 50 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 60 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-077A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 60 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 75 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-096A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 75 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 100 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-124A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 100 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 125 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-156A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 125 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 150 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-180A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 150 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 200 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-240A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 200 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 250 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-302A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 250 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 300 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-361A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 300 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 350 | UL Type 3R | 5% Impedance | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-414A-4+B058 | 1, 2, 3, 4, 5, 6, 10 | 350 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 1 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-02A1-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 1 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 1.5 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-03A0-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 1.5 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 2 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-03A5-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 2 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 3 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-04A8-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 3 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 5 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-07A6-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 5 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 7.5 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-012A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 7.5 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 10 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-014A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 10 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 15 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-023A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 15 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 20 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-027A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 20 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 25 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-034A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 25 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 30 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-044A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 30 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 40 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-052A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 40 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 50 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-065A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 50 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 60 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-077A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 60 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 75 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-096A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 75 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 100 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-124A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 100 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 125 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-156A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 125 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 150 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-180A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 150 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 200 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-240A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 200 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 250 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-302A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 250 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 300 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-361A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 300 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 350 | UL Type 1 | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-414A-4+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 350 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 1 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-02A1-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 1 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 1.5 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-03A0-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 1.5 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 2 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-03A5-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 2 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 3 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-04A8-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 3 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 5 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-07A6-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 5 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 7.5 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-012A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 7.5 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 10 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-014A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 10 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 15 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-023A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 15 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 20 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-027A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 20 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 25 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-034A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 25 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 30 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-044A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 30 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 40 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-052A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 40 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 50 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-065A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 50 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 60 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-077A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 60 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 75 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-096A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 75 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 100 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-124A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 100 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 125 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-156A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 125 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 150 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-180A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 150 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 200 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-240A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 200 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 250 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-302A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 250 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 300 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-361A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 300 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 350 | UL Type 3R | Passive Filter | Circuit Breaker | None | BACnet MS/TP | 100 KA | ABB ACH580-PCR-414A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 13, 14, 15, 16 | 350 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 1 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-02A1-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 1 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 1.5 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-03A0-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 1.5 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 2 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-03A5-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 2 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 3 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-04A8-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 3 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 5 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-07A6-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 5 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 7.5 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-012A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 7.5 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 10 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-014A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 10 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 15 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-023A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 15 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 20 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-027A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 20 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 25 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-034A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 25 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 30 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-044A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 30 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 40 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-052A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 40 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 50 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-065A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 50 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 60 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Vertical) | BACnet MS/TP | 100 KA | ABB ACH580-VCR-077A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 60 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 75 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-096A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 75 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 100 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-124A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 100 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 125 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-156A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 125 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 150 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-180A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 150 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 200 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-240A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 200 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 250 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-302A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 250 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 300 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-361A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 300 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 350 | UL Type 1 | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-414A-4 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 350 | 460V | UL Type 1 | 5% Impedance
|  | 1 | 460V | 1 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-02A1-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 1 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 1.5 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-03A0-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 1.5 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 2 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-03A5-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 2 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 3 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-04A8-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 3 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 5 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-07A6-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 5 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 7.5 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-012A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 7.5 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 10 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-014A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 10 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 15 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-023A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 15 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 20 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-027A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 20 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 25 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-034A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 25 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 30 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-044A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 30 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 40 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-052A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 40 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 50 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-065A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 50 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 60 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-077A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 60 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 75 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-096A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 75 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 100 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-124A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 100 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 125 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-156A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 125 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 150 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-180A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 150 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 200 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-240A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 200 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 250 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-302A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 250 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 300 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-361A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 300 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 350 | UL Type 1 | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-414A-4+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 350 | 460V | UL Type 1 | Passive Filter
|  | 1 | 460V | 1 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-02A1-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 1 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 1.5 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-03A0-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 1.5 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 2 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-03A5-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 2 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 3 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-04A8-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 3 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 5 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-07A6-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 5 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 7.5 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-012A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 7.5 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 10 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-014A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 10 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 15 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-023A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 15 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 20 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-027A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 20 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 25 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-034A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 25 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 30 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-044A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 30 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 40 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-052A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 40 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 50 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-065A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 50 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 60 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-077A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 60 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 75 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-096A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 75 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 100 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-124A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 100 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 125 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-156A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 125 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 150 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-180A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 150 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 200 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-240A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 200 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 250 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-302A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 250 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 300 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-361A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 300 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 350 | UL Type 3R | 5% Impedance | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-414A-4+B058 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 16 | 350 | 460V | UL Type 3R | 5% Impedance
|  | 1 | 460V | 1 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-02A1-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 1 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 1.5 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-03A0-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 1.5 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 2 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-03A5-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 2 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 3 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-04A8-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 3 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 5 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-07A6-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 5 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 7.5 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-012A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 7.5 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 10 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-014A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 10 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 15 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-023A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 15 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 20 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-027A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 20 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 25 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-034A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 25 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 30 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-044A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 30 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 40 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-052A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 40 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 50 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-065A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 50 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 60 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-077A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 60 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 75 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-096A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 75 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 100 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-124A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 100 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 125 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-156A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 125 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 150 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-180A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 150 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 200 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-240A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 200 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 250 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-302A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 250 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 300 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-361A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 300 | 460V | UL Type 3R | Passive Filter
|  | 1 | 460V | 350 | UL Type 3R | Passive Filter | Circuit Breaker | FVNR (Box Style) | BACnet MS/TP | 100 KA | ABB ACH580-BCR-414A-4+B058+E211 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16 | 350 | 460V | UL Type 3R | Passive Filter

## SCHEDULE NOTES
1. At minimum, VFD shall include 5% impedance via 5% AC line reactor or dual DC bus chokes sized to 5% equivalent impedance. VFD input Amps shall not exceed VFD output Amps.
2. Provide UL1449 surge suppression device.
3. VFD shall include alpha-numeric keypad interface, with display in plain English. (Displays relying solely on codes are not acceptable).
4. Provide internal EMI/RFI filter per IEC 61800-3.
5. VFD shall be BTL Listed for BACnet MS/TP, and also include Modbus and N2.
6. VFD shall include real time clock with battery backup (include 10 year battery).
7. Phase Loss Protection & Broken Belt (loss of load) indication while in Bypass.
8. Bypass Contactors shall be powered by Switch Mode Power supply, allowing +30% to -30% Input Voltage Tolerance. (120 V CPT not allowed).
9. VFD and Bypass shall both include BACnet MS/TP, Damper Control and Fireman’s override functionality.
10. Bypass operation to auto-reset after a brown out condition.
11. Include fast acting drive isolation fuses.
12. Bypass shall be fully functional in the event of a VFD failure. Bypass shall not relay on the VFD or the VFD’s control board/relays.
13. Passive harmonic filter shall be factory mounted in the same enclosure as the VFD.
14. Passive harmonic filter shall include capacitor drop-out contactor.
15. Passive harmonic filter shall reduce harmonics to 5% THiD, measured at the filter lugs, while operating at full load.
16. System to meet IEEE 519-2014 based on the harmonic mitigation method(s) identified in the above schedule