## SCHEDULE
SCHEDULE RANGE | [27 empty] | FILTERS | [13 empty] | DOCUMENTATION | [17 empty] | REFRIGERANT CALCULATIONS
SPLIT SYSTEM SCHEDULE | [27 empty] | SIZE (OUTDOOR UNIT) | COOLING ONLY OR HEAT PUMP | ELECTRICAL | NUMBER OF INDOOR UNITS | SIZE (INDOOR UNIT #1) | SIZE (INDOOR UNIT #2) | SIZE (INDOOR UNIT #3) | SIZE (INDOOR UNIT #4) | SIZE (INDOOR UNIT #5) | TYPE (INDOOR UNIT #1) | TYPE (INDOOR UNIT #2) | TYPE (INDOOR UNIT #3) | TYPE (INDOOR UNIT #4) | TYPE (INDOOR UNIT #5) | SUBMITTAL (OUTDOOR UNIT) | SUBMITTAL (INDOOR UNIT) | SUBMITTAL (SYSTEM) | ENGINEERING MANUAL (SYSTEM) | ENGINEERING MANUAL (OUTDOOR UNIT) | ENGINEERING MANUAL (INDOOR UNIT) | CAPACITY TABLE | INSTALLATION MANUAL (OUTDOOR) | INSTALLATION MANUAL (INDOOR) | INSTALLATION MANUAL (SYSTEM) | REVIT (OUTDOOR) | REVIT (INDOOR) | REVIT (SYSTEM) | CAD (OUTDOOR) | CAD (INDOOR) | CAD (SYSTEM) | CONTROLS OPTIONS | OPERATION MANUAL | REFRIGERANT | MAX VERTICAL SEPARATION (ODU TO IDU) (FT) | MAX VERTICAL SEPARATION (IDU TO IDU) (FT) | MAX TOTAL LINE SET (FT) | LIQUID LINE CONNECTION (IN) | SUCTION LINE CONNECTION (IN) | PRE-CHARGE PIPING LENGTH (FT) | FACTORY CHARGE (LBS) | FACTORY CHARGE (OZ) | ADDITIONAL CHARGE (OZ/FT)
INDOOR UNIT | [16 empty] | OUTDOOR UNIT | [8 empty] | Refrigerant | MAX ALLOWABLE LINE-SET LENGTHS
CFM | COOLING CAPACITY | [5 empty] | HEAT PUMP HEATING CAPACITY |  |  | OPERATING WEIGHT | INDOOR UNIT TYPE | ELECTRICAL |  |  | MAKE & MODEL |  | OA AMBIENT (COOLING) | OA AMBIENT (HEATING) | OPERATING WEIGHT | SEER2/EER2/HSPF2 | ELECTRICAL |  |  | MAKE & MODEL
| EDB | EWB | LDB | LWB | TOTAL CAPACITY | SENSIBLE CAPACITY | EDB | TEMP RISE | TOTAL CAPACITY |  |  | Voltage | MCA | MOP | MAKE | MODEL |  |  |  |  | Voltage | MCA | MOP | MAKE | MODEL
381 | 80 | 67 |  |  | 11200 | 8250 | 70 |  | 16000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXF09BVJU9 | 95 | 47 | 68 | 21.0 / 12.5 / 10.2 | 208/60/1 | 11.6 | 15 | DAIKIN | RXF09BVJU9 | R32 | 49' Vertical / 66' Total | 0.75 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTXF09BVJU9-RXF09BVJU9 | ENGINEERING MANUAL - OTERRA |  |  |  | IM - OTERRA OUTDOOR (09-12) | IM - OTERRA INDOOR (09-12) |  | RXF09BVJU9 | FTXF09BVJU9 |  | RXF09BVJU9 | FTXF09BVJU9 |  |  | OM - OTERRA INDOOR (09-12) | R-32 | 49 | - | 66 | 0.25 | 0.375 | 49 | 1.65 | 26.4 | 0.22
399 | 80 | 67 |  |  | 14600 | 9880 | 70 |  | 18000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXF12BVJU9 | 95 | 47 | 77 | 21.0 / 12.5 / 10.2 | 208/60/1 | 14.6 | 15 | DAIKIN | RXF12BVJU9 | R32 | 49' Vertical / 66' Total | 1 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTXF12BVJU9-RXF12BVJU9 | ENGINEERING MANUAL - OTERRA |  |  |  | IM - OTERRA OUTDOOR (09-12) | IM - OTERRA INDOOR (09-12) |  | RXF12BVJU9 | FTXF12BVJU9 |  | RXF12BVJU9 | FTXF12BVJU9 |  |  | OM - OTERRA INDOOR (09-12) | R-32 | 49 | - | 66 | 0.25 | 0.375 | 49 | 1.74 | 27.84 | 0.22
565 | 80 | 67 |  |  | 22000 | 14590 | 70 |  | 28000 | 37 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXF18BVJU9 | 95 | 47 | 121 | 21.0 / 12.0 / 9.6 | 208/60/1 | 21.4 | 25 | DAIKIN | RXF18BVJU9 | R32 | 66' Vertical / 99' Total | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTXF18BVJU9-RXF18BVJU9 | ENGINEERING MANUAL - OTERRA |  |  |  | IM - OTERRA OUTDOOR (18-24) | IM - OTERRA INDOOR (18-24) |  | RXF18BVJU9 | FTXF18BVJU9 |  | RXF18BVJU9 | FTXF18BVJU9 |  |  | OM - OTERRA INDOOR (18-24) | R-32 | 66 | - | 99 | 0.25 | 0.5 | 49 | 2.45 | 39.2 | 0.22
629 | 80 | 67 |  |  | 26400 | 16660 | 70 |  | 32000 | 37 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXF24BVJU9 | 95 | 47 | 121 | 21.0 / 12.0 / 9.5 | 208/60/1 | 21.6 | 25 | DAIKIN | RXF24BVJU9 | R32 | 66' Vertical / 99' Total | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTXF24BVJU9-RXF24BVJU9 | ENGINEERING MANUAL - OTERRA |  |  |  | IM - OTERRA OUTDOOR (18-24) | IM - OTERRA INDOOR (18-24) |  | RXF24BVJU9 | FTXF24BVJU9 |  | RXF24BVJU9 | FTXF24BVJU9 |  |  | OM - OTERRA INDOOR (18-24) | R-32 | 66 | - | 99 | 0.25 | 0.625 | 49 | 2.45 | 39.2 | 0.22
925 | 80 | 67 |  |  | 31400 | 20390 | 70 |  | 34800 | 42 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV30AVJU9 | 95 | 47 | 128 | 19.0 / 10.0 / 8.1 | 208/60/1 | 22 | 25 | DAIKIN | RXV30AVJU9 | R32 | 66' Vertical / 99' Total | 2.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 2.5 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTXV30AVJU9-RXV30AVJU9 | ENGINEERING MANUAL - POLARA |  |  |  | IM - POLARA OUTDOOR | IM - POLARA INDOOR (30-36) | [8 empty] | OM - POLARA INDOOR (30-36) | R-32 | 66 | - | 99 | 0.25 | 0.625 | 49 | 3.68 | 58.88 | 0.22
971 | 80 | 67 |  |  | 34400 | 21960 | 70 |  | 36000 | 42 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV36AVJU9 | 95 | 47 | 128 | 18.0 / 9.8 / 8.0 | 208/60/1 | 22 | 25 | DAIKIN | RXV36AVJU9 | R32 | 66' Vertical / 99' Total | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 3 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTXV36AVJU9-RXV36AVJU9 | ENGINEERING MANUAL - POLARA |  |  |  | IM - POLARA OUTDOOR | IM - POLARA INDOOR (30-36) | [8 empty] | OM - POLARA INDOOR (30-36) | R-32 | 66 | - | 99 | 0.25 | 0.625 | 49 | 3.68 | 58.88 | 0.22
322 | 80 | 67 |  |  | 11200 | 8250 | - |  | - | 25 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTKF09BVJU9 | 95 | - | 68 | 21.0 / 12.5 / - | 208/60/1 | 11.6 | 15 | DAIKIN | RKF09BVJU9 | R32 | 49' Vertical / 66' Total | 0.75 | COOLING ONLY | 208/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTKF09BVJU9-RKF09BVJU9 | ENGINEERING MANUAL - OTERRA |  |  |  | IM - OTERRA OUTDOOR (09-12) | IM - OTERRA INDOOR (09-12) |  | RKF09BVJU9 | FTXF09BVJU9 |  | RKF09BVJU9 | FTXF09BVJU9 |  |  | OM - OTERRA INDOOR (09-12) | R-32 | 49 | - | 66 | 0.25 | 0.625 | 49 | 1.65 | 26.4 | 0.22
399 | 80 | 67 |  |  | 14600 | 9880 | - |  | - | 25 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTKF12BVJU9 | 95 | - | 76 | 21.0 / 12.5 / - | 208/60/1 | 14.6 | 15 | DAIKIN | RKF12BVJU9 | R32 | 49' Vertical / 66' Total | 1 | COOLING ONLY | 208/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTKF12BVJU9-RKF12BVJU9 | ENGINEERING MANUAL - OTERRA |  |  |  | IM - OTERRA OUTDOOR (09-12) | IM - OTERRA INDOOR (09-12) |  | RKF12BVJU9 | FTXF12BVJU9 |  | RKF12BVJU9 | FTXF12BVJU9 |  |  | OM - OTERRA INDOOR (09-12) | R-32 | 49 | - | 66 | 0.25 | 0.375 | 49 | 1.74 | 27.84 | 0.22
565 | 80 | 67 |  |  | 22000 | 14590 | - |  | - | 37 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTKF18BVJU9 | 95 | - | 113 | 21.0 / 12.0 / - | 208/60/1 | 21.4 | 25 | DAIKIN | RKF18BVJU9 | R32 | 66' Vertical / 99' Total | 1.5 | COOLING ONLY | 208/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTKF18BVJU9-RKF18BVJU9 | ENGINEERING MANUAL - OTERRA |  |  |  | IM - OTERRA OUTDOOR (18-24) | IM - OTERRA INDOOR (18-24) |  | RKF18BVJU9 | FTXF18BVJU9 |  | RKF18BVJU9 | FTXF18BVJU9 |  |  | OM - OTERRA INDOOR (18-24) | R-32 | 66 | - | 99 | 0.25 | 0.5 | 49 | 2.45 | 39.2 | 0.22
629 | 80 | 67 |  |  | 26400 | 16660 | - |  | - | 37 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTKF24BVJU9 | 95 | - | 113 | 21.0 / 12.0 / - | 208/60/1 | 21.6 | 25 | DAIKIN | RKF24BVJU9 | R32 | 66' Vertical / 99' Total | 2 | COOLING ONLY | 208/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTKF24BVJU9-RKF24BVJU9 | ENGINEERING MANUAL - OTERRA |  |  |  | IM - OTERRA OUTDOOR (18-24) | IM - OTERRA INDOOR (18-24) |  | RKF24BVJU9 | FTXF24BVJU9 |  | RKF24BVJU9 | FTXF24BVJU9 |  |  | OM - OTERRA INDOOR (18-24) | R-32 | 66 | - | 99 | 0.25 | 0.625 | 49 | 2.45 | 39.2 | 0.22
925 | 80 | 67 |  |  | 31400 | 19980 | - |  | - | 42 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV30AVJU9 | 95 | - | 128 | 19.0 / 10.0 / - | 208/60/1 | 21.8 | 25 | DAIKIN | RKV30AVJU9 | R32 | 66' Vertical / 99' Total | 2.5 | COOLING ONLY | 208/60/1 (SINGLE POINT POWER) | 1 | 2.5 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTXV30AVJU9-RKV30AVJU9 | ENGINEERING MANUAL - POLARA |  |  |  | IM - POLARA OUTDOOR | IM - POLARA INDOOR (30-36) | [8 empty] | OM - POLARA INDOOR (30-36) | R-32 | 66 | - | 99 | 0.25 | 0.625 | 49 | 3.68 | 58.88 | 0.22
971 | 80 | 67 |  |  | 34400 | 21960 | - |  | - | 42 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV36AVJU9 | 95 | - | 128 | 18.0 / 9.8 / - | 208/60/1 | 21.9 | 25 | DAIKIN | RKV36AVJU9 | R32 | 66' Vertical / 99' Total | 3 | COOLING ONLY | 208/60/1 (SINGLE POINT POWER) | 1 | 3 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTXV36AVJU9-RKV36AVJU9 | ENGINEERING MANUAL - POLARA |  |  |  | IM - POLARA OUTDOOR | IM - POLARA INDOOR (30-36) | [8 empty] | OM - POLARA INDOOR (30-36) | R-32 | 66 | - | 99 | 0.25 | 0.625 | 49 | 3.68 | 58.88 | 0.22
424 | 80 | 67 |  |  | 10500 | 8140 | 70 |  | 12000 | 18 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXQ09ASBU9 | 95 | 47 | 59 | 20.0 / 12.0 / 9.0 | 115/60/1 | 14.9 | 15 | DAIKIN | RXQ09ASBU9 | R32 | 50' Vertical / 66' Total | 0.75 | HEAT PUMP | 115/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTXQ09ASBU9-RXQ09ASBU9 | ENGINEERING MANUAL - OTERRA 115V |  |  |  | IM - OTERRA 115V OUTDOOR | IM - OTERRA 115V INDOOR |  | RXQ09ASBU9 | FTXQ09ASBU9 |  | RXQ09ASBU9 | FTXQ09ASBU9 |  |  | OM - OTERRA 115V INDOOR (09-12) | R-32 | 50 | - | 66 | 0.25 | 0.375 | 50 | 1.15 | 18.4 | 0.22
413 | 80 | 67 |  |  | 12800 | 9310 | 70 |  | 14600 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXQ12ASBU9 | 95 | 47 | 64 | 20.0 / 12.0 / 9.0 | 115/60/1 | 15 | 15 | DAIKIN | RXQ12ASBU9 | R32 | 50' Vertical / 66' Total | 1 | HEAT PUMP | 115/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FTXQ12ASBU9-RXQ12ASBU9 | ENGINEERING MANUAL - OTERRA 115V |  |  |  | IM - OTERRA 115V OUTDOOR | IM - OTERRA 115V INDOOR |  | RXQ12ASBU9 | FTXQ12ASBU9 |  | RXQ12ASBU9 | FTXQ12ASBU9 |  |  | OM - OTERRA 115V INDOOR (09-12) | R-32 | 50 | - | 66 | 0.25 | 0.375 | 50 | 1.65 | 26.4 | 0.22
401 | 80 | 67 |  |  | 9400 | 6910 | 70 |  | 12800 | 64 | Ducted Concealed | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FDMA09AVJU9 | 95 | 47 | 72 | 16.0 / 11.1 / 9.0 | 208/60/1 | 11.6 | 15 | DAIKIN | RXP09AVJU9 | R32 | 49' Vertical / 66' Total | 0.75 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Ducted Concealed | - | - | - | - |  |  | FDMA09AVJU9-RXP09AVJU9 | ENGINEERING MANUAL - FDMA MINI SPLIT |  |  |  | IM - RXP OUTDOOR UNIT (09-12) | IM - FDMA INDOOR (09-24) |  | RXP09AVJU9 | FDMA09AVJU9 |  | RXP09AVJU9 | FDMA09AVJU9 |  |  | OM - FDMA INDOOR (09-24) | R-32 | 49 | - | 66 | 0.25 | 0.375 | 49 | 1.74 | 27.84 | 0.22
440 | 80 | 67 |  |  | 12400 | 8330 | 70 |  | 17000 | 64 | Ducted Concealed | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FDMA12AVJU9 | 95 | 47 | 72 | 16.0 / 10.0 / 9.0 | 208/60/1 | 14.6 | 15 | DAIKIN | RXP12AVJU9 | R32 | 49' Vertical / 66' Total | 1 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Ducted Concealed | - | - | - | - |  |  | FDMA12AVJU9-RXP12AVJU9 | ENGINEERING MANUAL - FDMA MINI SPLIT |  |  |  | IM - RXP OUTDOOR UNIT (09-12) | IM - FDMA INDOOR (09-24) |  | RXP12AVJU9 | FDMA12AVJU9 |  | RXP12AVJU9 | FDMA12AVJU9 |  |  | OM - FDMA INDOOR (09-24) | R-32 | 49 | - | 66 | 0.25 | 0.375 | 49 | 1.74 | 27.84 | 0.22
471 | 80 | 67 |  |  | 15700 | 11230 | 70 |  | 18500 | 82 | Ducted Concealed | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FDMA15AVJU9 | 95 | 47 | 127 | 18.0 / 11.8 / 9.2 | 208/60/1 | 16.1 | 20 | DAIKIN | RXP15AVJU9 | R32 | 66' Vertical / 99' Total | 1.25 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1.25 | - | - | - | - | Ducted Concealed | - | - | - | - |  |  | FDMA15AVJU9-RXP15AVJU9 | ENGINEERING MANUAL - FDMA MINI SPLIT |  |  |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FDMA INDOOR (09-24) |  | RXP15AVJU9 | FDMA15AVJU9 |  | RXP15AVJU9 | FDMA15AVJU9 |  |  | OM - FDMA INDOOR (09-24) | R-32 | 66 | - | 99 | 0.25 | 0.5 | 49 | 3.04 | 48.64 | 0.22
609 | 80 | 67 |  |  | 19600 | 14460 | 70 |  | 25000 | 82 | Ducted Concealed | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FDMA18AVJU9 | 95 | 47 | 127 | 18.0 / 11.6 / 9.2 | 208/60/1 | 21.4 | 25 | DAIKIN | RXP18AVJU9 | R32 | 66' Vertical / 99' Total | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Ducted Concealed | - | - | - | - |  |  | FDMA18AVJU9-RXP18AVJU9 | ENGINEERING MANUAL - FDMA MINI SPLIT |  |  |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FDMA INDOOR (09-24) |  | RXP18AVJU9 | FDMA18AVJU9 |  | RXP18AVJU9 | FDMA18AVJU9 |  |  | OM - FDMA INDOOR (09-24) | R-32 | 66 | - | 99 | 0.25 | 0.5 | 49 | 3.04 | 48.64 | 0.22
666 | 80 | 67 |  |  | 23000 | 15740 | 70 |  | 27600 | 88 | Ducted Concealed | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FDMA24AVJU9 | 95 | 47 | 127 | 18.0 / 10.3 / 9.2 | 208/60/1 | 21.6 | 25 | DAIKIN | RXP24AVJU9 | R32 | 66' Vertical / 99' Total | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Ducted Concealed | - | - | - | - |  |  | FDMA24AVJU9-RXP24AVJU9 | ENGINEERING MANUAL - FDMA MINI SPLIT |  |  |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FDMA INDOOR (09-24) |  | RXP24AVJU9 | FDMA24AVJU9 |  | RXP24AVJU9 | FDMA24AVJU9 |  |  | OM - FDMA INDOOR (09-24) | R-32 | 66 | - | 99 | 0.25 | 0.625 | 49 | 3.04 | 48.64 | 0.22
297 | 80 | 67 |  |  | 10900 | 7310 | 70 |  | 17100 | 40 | Floor Mounted (Black) | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FVXV09AVJUT9 | 95 | 47 | 72 | 19.5 / 12.0 / 9.7 | 208/60/1 | 11.6 | 15 | DAIKIN | RXP09AVJU9 | R32 | 49' Vertical / 66' Total | 0.75 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Floor Mounted (Black) | - | - | - | - |  |  | FVXV09AVJUT9-RXP09AVJU9 | ENGINEERING MANUAL - FVXV |  |  |  | IM - RXP OUTDOOR UNIT (09-12) | IM - FVXV INDOOR (09-18) |  | RXP09AVJU9 |  |  | RXP09AVJU9 |  |  |  | OM - FVXV INDOOR (09-18) | R-32 | 49 | - | 66 | 0.25 | 0.375 | 49 | 1.74 | 27.84 | 0.22
321 | 80 | 67 |  |  | 12600 | 8110 | 70 |  | 19900 | 40 | Floor Mounted (Black) | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FVXV12AVJUT9 | 95 | 47 | 72 | 19.5 / 10.5 / 9.5 | 208/60/1 | 14.6 | 15 | DAIKIN | RXP12AVJU9 | R32 | 49' Vertical / 66' Total | 1 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Floor Mounted (Black) | - | - | - | - |  |  | FVXV12AVJUT9-RXP12AVJU9 | ENGINEERING MANUAL - FVXV |  |  |  | IM - RXP OUTDOOR UNIT (09-12) | IM - FVXV INDOOR (09-18) |  | RXP12AVJU9 |  |  | RXP12AVJU9 |  |  |  | OM - FVXV INDOOR (09-18) | R-32 | 49 | - | 66 | 0.25 | 0.375 | 49 | 1.74 | 27.84 | 0.22
392 | 80 | 67 |  |  | 19100 | 11610 | 70 |  | 20400 | 40 | Floor Mounted (Black) | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FVXV15AVJUT9 | 95 | 47 | 127 | 19.5 / 12.0 / 9.6 | 208/60/1 | 16.1 | 20 | DAIKIN | RXP15AVJU9 | R32 | 66' Vertical / 99' Total | 1.25 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1.25 | - | - | - | - | Floor Mounted (Black) | - | - | - | - |  |  | FVXV15AVJUT9-RXP15AVJU9 | ENGINEERING MANUAL - FVXV |  |  |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FVXV INDOOR (09-18) |  | RXP15AVJU9 |  |  | RXP15AVJU9 |  |  |  | OM - FVXV INDOOR (09-18) | R-32 | 66 | - | 99 | 0.25 | 0.5 | 49 | 3.04 | 48.64 | 0.22
448 | 80 | 67 |  |  | 21400 | 13000 | 70 |  | 21800 | 40 | Floor Mounted (Black) | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FVXV18AVJUT9 | 95 | 47 | 127 | 19.5 / 12.0 / 9.5 | 208/60/1 | 21.4 | 25 | DAIKIN | RXP18AVJU9 | R32 | 66' Vertical / 99' Total | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Floor Mounted (Black) | - | - | - | - |  |  | FVXV18AVJUT9-RXP18AVJU9 | ENGINEERING MANUAL - FVXV |  |  |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FVXV INDOOR (09-18) |  | RXP18AVJU9 |  |  | RXP18AVJU9 |  |  |  | OM - FVXV INDOOR (09-18) | R-32 | 66 | - | 99 | 0.25 | 0.5 | 49 | 3.04 | 48.64 | 0.22
297 | 80 | 67 |  |  | 10900 | 7310 | 70 |  | 17100 | 40 | Floor Mounted (White) | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FVXV09AVJUW9 | 95 | 47 | 72 | 19.5 / 12.0 / 9.7 | 208/60/1 | 11.6 | 15 | DAIKIN | RXP09AVJU9 | R32 | 49' Vertical / 66' Total | 0.75 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Floor Mounted (White) | - | - | - | - |  |  | FVXV09AVJUW9-RXP09AVJU9 | ENGINEERING MANUAL - FVXV |  |  |  | IM - RXP OUTDOOR UNIT (09-12) | IM - FVXV INDOOR (09-18) |  | RXP09AVJU9 |  |  | RXP09AVJU9 |  |  |  | OM - FVXV INDOOR (09-18) | R-32 | 49 | - | 66 | 0.25 | 0.375 | 49 | 1.74 | 27.84 | 0.22
321 | 80 | 67 |  |  | 12600 | 8110 | 70 |  | 19900 | 40 | Floor Mounted (White) | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FVXV12AVJUW9 | 95 | 47 | 72 | 19.5 / 10.5 / 9.5 | 208/60/1 | 14.6 | 15 | DAIKIN | RXP12AVJU9 | R32 | 49' Vertical / 66' Total | 1 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Floor Mounted (White) | - | - | - | - |  |  | FVXV12AVJUW9-RXP12AVJU9 | ENGINEERING MANUAL - FVXV |  |  |  | IM - RXP OUTDOOR UNIT (09-12) | IM - FVXV INDOOR (09-18) |  | RXP12AVJU9 |  |  | RXP12AVJU9 |  |  |  | OM - FVXV INDOOR (09-18) | R-32 | 49 | - | 66 | 0.25 | 0.375 | 49 | 1.74 | 27.84 | 0.22
392 | 80 | 67 |  |  | 19100 | 11610 | 70 |  | 20400 | 40 | Floor Mounted (White) | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FVXV15AVJUW9 | 95 | 47 | 127 | 19.5 / 12.0 / 9.6 | 208/60/1 | 16.1 | 20 | DAIKIN | RXP15AVJU9 | R32 | 66' Vertical / 99' Total | 1.25 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1.25 | - | - | - | - | Floor Mounted (White) | - | - | - | - |  |  | FVXV15AVJUW9-RXP15AVJU9 | ENGINEERING MANUAL - FVXV |  |  |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FVXV INDOOR (09-18) |  | RXP15AVJU9 |  |  | RXP15AVJU9 |  |  |  | OM - FVXV INDOOR (09-18) | R-32 | 66 | - | 99 | 0.25 | 0.5 | 49 | 3.04 | 48.64 | 0.22
448 | 80 | 67 |  |  | 21400 | 13000 | 70 |  | 21800 | 40 | Floor Mounted (White) | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FVXV18AVJUW9 | 95 | 47 | 127 | 19.5 / 12.0 / 9.5 | 208/60/1 | 21.4 | 25 | DAIKIN | RXP18AVJU9 | R32 | 66' Vertical / 99' Total | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Floor Mounted (White) | - | - | - | - |  |  | FVXV18AVJUW9-RXP18AVJU9 | ENGINEERING MANUAL - FVXV |  |  |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FVXV INDOOR (09-18) |  | RXP18AVJU9 |  |  | RXP18AVJU9 |  |  |  | OM - FVXV INDOOR (09-18) | R-32 | 66 | - | 99 | 0.25 | 0.5 | 49 | 3.04 | 48.64 | 0.22
635 | 80 | 67 |  |  | 18000 | 14800 | 70 |  | 20000 | 82 | Ducted Concealed | 208/1 | 1.9 | 15 | DAIKIN | FBA18AAVJU | 95 | 47 | 234 | 16.3 / 13.5 / 8.5 | 208/60/1 | 19.8 | 20 | DAIKIN | RZA18AAVJU | R32 | 98' Vertical, 230' Total | 1.5 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 1.5 | - | - | - | - | Ducted Concealed | - | - | - | - |  |  | FBA18AAVJU-RZA18AAVJU | ENGINEERING MANUAL - FBA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FBA INDOOR (18-48) |  | RZA18AAVJU | FBA18AAVJU |  | RZA18AAVJU | FBA18AAVJU |  |  | OM - FBA INDOOR (18-48) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
742 | 80 | 67 |  |  | 24000 | 18700 | 70 |  | 27000 | 84 | Ducted Concealed | 208/1 | 1.9 | 15 | DAIKIN | FBA24AAVJU | 95 | 47 | 234 | 16.2 / 11.7 / 9.3 | 208/60/1 | 19.8 | 20 | DAIKIN | RZA24AAVJU | R32 | 98' Vertical, 230' Total | 2 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 2 | - | - | - | - | Ducted Concealed | - | - | - | - |  |  | FBA24AAVJU-RZA24AAVJU | ENGINEERING MANUAL - FBA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FBA INDOOR (18-48) |  | RZA24AAVJU | FBA24AAVJU |  | RZA24AAVJU | FBA24AAVJU |  |  | OM - FBA INDOOR (18-48) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
1094 | 80 | 67 |  |  | 30000 | 23400 | 70 |  | 34000 | 101 | Ducted Concealed | 208/1 | 3.1 | 15 | DAIKIN | FBA30AAVJU | 95 | 47 | 234 | 16.5 / 12.4 / 8.9 | 208/60/1 | 34.6 | 35 | DAIKIN | RZA30AAVJU | R32 | 98' Vertical, 230' Total | 2.5 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 2.5 | - | - | - | - | Ducted Concealed | - | - | - | - |  |  | FBA30AAVJU-RZA30AAVJU | ENGINEERING MANUAL - FBA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FBA INDOOR (18-48) |  | RZA30AAVJU | FBA30AAVJU |  | RZA30AAVJU | FBA30AAVJU |  |  | OM - FBA INDOOR (18-48) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
1130 | 80 | 67 |  |  | 36000 | 27200 | 70 |  | 40000 | 101 | Ducted Concealed | 208/1 | 3.1 | 15 | DAIKIN | FBA36AAVJU | 95 | 47 | 234 | 16.9 / 11.8 / 8.8 | 208/60/1 | 34.6 | 35 | DAIKIN | RZA36AAVJU | R32 | 98' Vertical, 230' Total | 3 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 3 | - | - | - | - | Ducted Concealed | - | - | - | - |  |  | FBA36AAVJU-RZA36AAVJU | ENGINEERING MANUAL - FBA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FBA INDOOR (18-48) |  | RZA36AAVJU | FBA36AAVJU |  | RZA36AAVJU | FBA36AAVJU |  |  | OM - FBA INDOOR (18-48) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
1377 | 80 | 67 |  |  | 40500 | 30500 | 70 |  | 47000 | 106 | Ducted Concealed | 208/1 | 3.6 | 15 | DAIKIN | FBA42AAVJU | 95 | 47 | 234 | 15.6 / 10.5 / 9.5 | 208/60/1 | 34.6 | 35 | DAIKIN | RZA42AAVJU | R32 | 98' Vertical, 230' Total | 3.5 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 3.5 | - | - | - | - | Ducted Concealed | - | - | - | - |  |  | FBA42AAVJU-RZA42AAVJU | ENGINEERING MANUAL - FBA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FBA INDOOR (18-48) |  | RZA42AAVJU | FBA42AAVJU |  | RZA42AAVJU | FBA42AAVJU |  |  | OM - FBA INDOOR (18-48) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
1377 | 80 | 67 |  |  | 48000 | 36100 | 70 |  | 54000 | 106 | Ducted Concealed | 208/1 | 3.6 | 15 | DAIKIN | FBA48AAVJU | 95 | 47 | 234 | 15.3 / 8.9 / 9.3 | 208/60/1 | 34.6 | 35 | DAIKIN | RZA48AAVJU | R32 | 98' Vertical, 230' Total | 4 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 4 | - | - | - | - | Ducted Concealed | - | - | - | - |  |  | FBA48AAVJU-RZA48AAVJU | ENGINEERING MANUAL - FBA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FBA INDOOR (18-48) |  | RZA48AAVJU | FBA48AAVJU |  | RZA48AAVJU | FBA48AAVJU |  |  | OM - FBA INDOOR (18-48) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
742 | 80 | 67 |  |  | 18000 | 16100 | 70 |  | 20000 | 51 | Cassette | 208/1 | 0.5 | 15 | DAIKIN | FCA18AAVJU | 95 | 47 | 234 | 19.5 / 14.0 / 9.2 | 208/60/1 | 19.8 | 20 | DAIKIN | RZA18AAVJU | R32 | 98' Vertical, 230' Total | 1.5 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 1.5 | - | - | - | - | Cassette | - | - | - | - |  |  | FCA18AAVJU-RZA18AAVJU | ENGINEERING MANUAL - FCA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FCA INDOOR (18-48) |  | RZA18AAVJU | FCA18AAVJU |  | RZA18AAVJU | FCA18AAVJU |  |  | OM - FCA INDOOR (18-48) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
777 | 80 | 67 |  |  | 24000 | 19900 | 70 |  | 27000 | 51 | Cassette | 208/1 | 0.5 | 15 | DAIKIN | FCA24AAVJU | 95 | 47 | 234 | 19.6 / 13.4 / 9.1 | 208/60/1 | 19.8 | 20 | DAIKIN | RZA24AAVJU | R32 | 98' Vertical, 230' Total | 2 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 2 | - | - | - | - | Cassette | - | - | - | - |  |  | FCA24AAVJU-RZA24AAVJU | ENGINEERING MANUAL - FCA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FCA INDOOR (18-48) |  | RZA24AAVJU | FCA24AAVJU |  | RZA24AAVJU | FCA24AAVJU |  |  | OM - FCA INDOOR (18-48) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
1059 | 80 | 67 |  |  | 30000 | 22300 | 70 |  | 34000 | 58 | Cassette | 208/1 | 1 | 15 | DAIKIN | FCA30AAVJU | 95 | 47 | 234 | 21.0 / 13.2 / 10.1 | 208/60/1 | 34.6 | 35 | DAIKIN | RZA30AAVJU | R32 | 98' Vertical, 230' Total | 2.5 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 2.5 | - | - | - | - | Cassette | - | - | - | - |  |  | FCA30AAVJU-RZA30AAVJU | ENGINEERING MANUAL - FCA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FCA INDOOR (18-48) |  | RZA30AAVJU | FCA30AAVJU |  | RZA30AAVJU | FCA30AAVJU |  |  | OM - FCA INDOOR (18-48) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
1253 | 80 | 67 |  |  | 36000 | 28300 | 70 |  | 40000 | 58 | Cassette | 208/1 | 1.6 | 15 | DAIKIN | FCA36AAVJU | 95 | 47 | 234 | 20.0 / 12.2 / 10.0 | 208/60/1 | 34.6 | 35 | DAIKIN | RZA36AAVJU | R32 | 98' Vertical, 230' Total | 3 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 3 | - | - | - | - | Cassette | - | - | - | - |  |  | FCA36AAVJU-RZA36AAVJU | ENGINEERING MANUAL - FCA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FCA INDOOR (18-48) |  | RZA36AAVJU | FCA36AAVJU |  | RZA36AAVJU | FCA36AAVJU |  |  | OM - FCA INDOOR (18-48) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
1253 | 80 | 67 |  |  | 42000 | 30600 | 70 |  | 47000 | 58 | Cassette | 208/1 | 1.6 | 15 | DAIKIN | FCA42AAVJU | 95 | 47 | 234 | 18.9 / 10.5 / 10.2 | 208/60/1 | 34.6 | 35 | DAIKIN | RZA42AAVJU | R32 | 98' Vertical, 230' Total | 3.5 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 3.5 | - | - | - | - | Cassette | - | - | - | - |  |  | FCA42AAVJU-RZA42AAVJU | ENGINEERING MANUAL - FCA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FCA INDOOR (18-48) |  | RZA42AAVJU | FCA42AAVJU |  | RZA42AAVJU | FCA42AAVJU |  |  | OM - FCA INDOOR (18-48) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
1253 | 80 | 67 |  |  | 48000 | 35000 | 70 |  | 54000 | 58 | Cassette | 208/1 | 1.6 | 15 | DAIKIN | FCA48AAVJU | 95 | 47 | 234 | 18.0 / 8.8 / 9.7 | 208/60/1 | 34.6 | 35 | DAIKIN | RZA48AAVJU | R32 | 98' Vertical, 230' Total | 4 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 4 | - | - | - | - | Cassette | - | - | - | - |  |  | FCA48AAVJU-RZA48AAVJU | ENGINEERING MANUAL - FCA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FCA INDOOR (18-48) |  | RZA48AAVJU | FCA48AAVJU |  | RZA48AAVJU | FCA48AAVJU |  |  | OM - FCA INDOOR (18-48) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
512 | 80 | 67 |  |  | 18000 | 13700 | 70 |  | 20000 | 35.3 | Wall Mounted | 208/1 | 0.5 | 15 | DAIKIN | FAA18AAVJU | 95 | 47 | 234 | 17.8 / 12.8 / 7.6 | 208/60/1 | 19.8 | 20 | DAIKIN | RZA18AAVJU | R32 | 98' Vertical, 230' Total | 1.5 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FAA18AAVJU-RZA18AAVJU | ENGINEERING MANUAL - FAA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FAA INDOOR (18-24) |  | RZA18AAVJU |  |  | RZA18AAVJU |  |  |  | OM - FAA INDOOR (18-24) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
670 | 80 | 67 |  |  | 24000 | 18000 | 70 |  | 27000 | 35.3 | Wall Mounted | 208/1 | 0.6 | 15 | DAIKIN | FAA24AAVJU | 95 | 47 | 234 | 18.2 / 11.4 / 7.8 | 208/60/1 | 19.8 | 20 | DAIKIN | RZA24AAVJU | R32 | 98' Vertical, 230' Total | 2 | HEAT PUMP | 208/60/1 (DUAL POINT POWER) | 1 | 2 | - | - | - | - | Wall Mounted | - | - | - | - |  |  | FAA24AAVJU-RZA24AAVJU | ENGINEERING MANUAL - FAA SKY AIR |  |  | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FAA INDOOR (18-24) |  | RZA24AAVJU |  |  | RZA24AAVJU |  |  |  | OM - FAA INDOOR (18-24) | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | DAIKIN | 2MXM18AVJU9 | R32 | 164' Max System Piping | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 0.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 2MXM18AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 2MXM18AVJU9 | CTXV07AVJU9 |  | 2MXM18AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 164 | 0.25 | 0.375 | 98.4 | 3.3 | 52.8 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6870 | - | 70 |  | 7440 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | DAIKIN | 2MXM18AVJU9 | R32 | 164' Max System Piping | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 2MXM18AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 2MXM18AVJU9 | CTXV07AVJU9 |  | 2MXM18AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 164 | 0.25 | 0.375 | 98.4 | 3.3 | 52.8 | 0.22
381 | 80 | 67 |  |  | 8830 | - | 70 |  | 9560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 6340 | - | 70 |  | 6820 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | DAIKIN | 2MXM18AVJU9 | R32 | 164' Max System Piping | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 2MXM18AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 2MXM18AVJU9 | CTXV07AVJU9 |  | 2MXM18AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 164 | 0.25 | 0.375 | 98.4 | 3.3 | 52.8 | 0.22
392 | 80 | 67 |  |  | 10860 | - | 70 |  | 11680 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 5470 | - | 70 |  | 5890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | DAIKIN | 2MXM18AVJU9 | R32 | 164' Max System Piping | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 2MXM18AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 2MXM18AVJU9 | CTXV07AVJU9 |  | 2MXM18AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 164 | 0.25 | 0.375 | 98.4 | 3.3 | 52.8 | 0.22
540 | 80 | 67 |  |  | 11730 | - | 70 |  | 12610 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 8600 | - | 70 |  | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | DAIKIN | 2MXM18AVJU9 | R32 | 164' Max System Piping | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 2MXM18AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 2MXM18AVJU9 | FTXV09AVJU9 |  | 2MXM18AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 164 | 0.25 | 0.375 | 98.4 | 3.3 | 52.8 | 0.22
381 | 80 | 67 |  |  | 8600 | - | 70 |  | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7370 | - | 70 |  | 7930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | DAIKIN | 2MXM18AVJU9 | R32 | 164' Max System Piping | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 2MXM18AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 2MXM18AVJU9 | FTXV09AVJU9 |  | 2MXM18AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 164 | 0.25 | 0.375 | 98.4 | 3.3 | 52.8 | 0.22
392 | 80 | 67 |  |  | 9830 | - | 70 |  | 10570 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 6450 | - | 70 |  | 6940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | DAIKIN | 2MXM18AVJU9 | R32 | 164' Max System Piping | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 2MXM18AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 2MXM18AVJU9 | FTXV09AVJU9 |  | 2MXM18AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 164 | 0.25 | 0.375 | 98.4 | 3.3 | 52.8 | 0.22
540 | 80 | 67 |  |  | 10750 | - | 70 |  | 11560 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
392 | 80 | 67 |  |  | 8600 | - | 70 |  | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | DAIKIN | 2MXM18AVJU9 | R32 | 164' Max System Piping | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 2MXM18AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 2MXM18AVJU9 | FTXV12AVJU9 |  | 2MXM18AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 164 | 0.25 | 0.375 | 98.4 | 3.3 | 52.8 | 0.22
392 | 80 | 67 |  |  | 8600 | - | 70 |  | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 0.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7570 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7440 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7350 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15750 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6440 | - | 70 |  | 6720 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 16560 | - | 70 |  | 17250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9470 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12630 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 8630 | - | 70 |  | 9000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 14380 | - | 70 |  | 15000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 15330 | - | 70 |  | 16000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 3MXM24AVJU9 | FTXV12AVJU9 |  | 3MXM24AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10670 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 3MXM24AVJU9 | FTXV12AVJU9 |  | 3MXM24AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 12780 | - | 70 |  | 13330 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
392 | 80 | 67 |  |  | 9200 | - | 70 |  | 9600 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 3MXM24AVJU9 | FTXV12AVJU9 |  | 3MXM24AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 13800 | - | 70 |  | 14400 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
540 | 80 | 67 |  |  | 11500 | - | 70 |  | 12000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.25 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 |  | 3MXM24AVJU9 | FTXV15AVJU9 |  | 3MXM24AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 11500 | - | 70 |  | 12000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 10450 | - | 70 |  | 10910 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.25 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 |  | 3MXM24AVJU9 | FTXV15AVJU9 |  | 3MXM24AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 12550 | - | 70 |  | 13090 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 11500 | - | 70 |  | 12000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.5 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 3MXM24AVJU9 | FTXV18AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV18AVJU9 |  | 3MXM24AVJU9 | FTXV18AVJU9 |  | 3MXM24AVJU9 | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 11500 | - | 70 |  | 12000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 0.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6460 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6460 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 10620 | - | 70 |  | 11080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 5550 | - | 70 |  | 5790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 5550 | - | 70 |  | 5790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 11900 | - | 70 |  | 12410 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5030 | - | 70 |  | 5250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 5030 | - | 70 |  | 5250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
565 | 80 | 67 |  |  | 12940 | - | 70 |  | 13500 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6440 | - | 70 |  | 6720 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 8280 | - | 70 |  | 8640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8280 | - | 70 |  | 8640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 5750 | - | 70 |  | 6000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 7390 | - | 70 |  | 7710 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 9860 | - | 70 |  | 10290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 5190 | - | 70 |  | 5420 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 6680 | - | 70 |  | 6970 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 11130 | - | 70 |  | 11610 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 4740 | - | 70 |  | 4940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 6090 | - | 70 |  | 6350 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 12180 | - | 70 |  | 12710 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5190 | - | 70 |  | 5420 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 8900 | - | 70 |  | 9290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 8900 | - | 70 |  | 9290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 4740 | - | 70 |  | 4940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 8120 | - | 70 |  | 8470 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 10150 | - | 70 |  | 10590 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 4350 | - | 70 |  | 4540 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 7460 | - | 70 |  | 7780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 11190 | - | 70 |  | 11680 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 4350 | - | 70 |  | 4540 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  | 3MXM24AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 9320 | - | 70 |  | 9730 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 9320 | - | 70 |  | 9730 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 6900 | - | 70 |  | 7200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 6900 | - | 70 |  | 7200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 9200 | - | 70 |  | 9600 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 6270 | - | 70 |  | 6550 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 6270 | - | 70 |  | 6550 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 10450 | - | 70 |  | 10910 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 5750 | - | 70 |  | 6000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 5750 | - | 70 |  | 6000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 11500 | - | 70 |  | 12000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 6270 | - | 70 |  | 6550 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 8360 | - | 70 |  | 8730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 8360 | - | 70 |  | 8730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 5750 | - | 70 |  | 6000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 7670 | - | 70 |  | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 9580 | - | 70 |  | 10000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 5310 | - | 70 |  | 5540 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 7080 | - | 70 |  | 7380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 10620 | - | 70 |  | 11080 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 5310 | - | 70 |  | 5540 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  | 3MXM24AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 8850 | - | 70 |  | 9230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 8850 | - | 70 |  | 9230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
392 | 80 | 67 |  |  | 7670 | - | 70 |  | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 3MXM24AVJU9 | FTXV12AVJU9 |  | 3MXM24AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 7670 | - | 70 |  | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 7670 | - | 70 |  | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 7080 | - | 70 |  | 7380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | DAIKIN | 3MXM24AVJU9 | R32 | 230' Max System Piping | 2 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 3MXM24AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 3MXM24AVJU9 | FTXV12AVJU9 |  | 3MXM24AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.625 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 7080 | - | 70 |  | 7380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 8850 | - | 70 |  | 9230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 0.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7570 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7480 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12820 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15890 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6970 | - | 70 |  | 7310 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 17930 | - | 70 |  | 18780 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6770 | - | 70 |  | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
629 | 80 | 67 |  |  | 23230 | - | 70 |  | 23770 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12740 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 8870 | - | 70 |  | 9200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 17730 | - | 70 |  | 18400 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 8650 | - | 70 |  | 8810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
629 | 80 | 67 |  |  | 23050 | - | 70 |  | 23490 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 11820 | - | 70 |  | 12270 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 14780 | - | 70 |  | 15330 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
392 | 80 | 67 |  |  | 11640 | - | 70 |  | 12000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 17460 | - | 70 |  | 18000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
392 | 80 | 67 |  |  | 11400 | - | 70 |  | 11530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
629 | 80 | 67 |  |  | 22800 | - | 70 |  | 23070 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
540 | 80 | 67 |  |  | 14550 | - | 70 |  | 15000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.25 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 |  | 4MXM36AVJU9 | FTXV15AVJU9 |  | 4MXM36AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 14550 | - | 70 |  | 15000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 14410 | - | 70 |  | 14680 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.25 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 |  | 4MXM36AVJU9 | FTXV15AVJU9 |  | 4MXM36AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 17290 | - | 70 |  | 17620 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
540 | 80 | 67 |  |  | 13150 | - | 70 |  | 13310 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.25 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 |  | 4MXM36AVJU9 | FTXV15AVJU9 |  | 4MXM36AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
629 | 80 | 67 |  |  | 21050 | - | 70 |  | 21290 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
565 | 80 | 67 |  |  | 17100 | - | 70 |  | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.5 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV18AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV18AVJU9 |  | 4MXM36AVJU9 | FTXV18AVJU9 |  | 4MXM36AVJU9 | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 17100 | - | 70 |  | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 14660 | - | 70 |  | 14830 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.5 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV18AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV18AVJU9 |  | 4MXM36AVJU9 | FTXV18AVJU9 |  | 4MXM36AVJU9 | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
629 | 80 | 67 |  |  | 19540 | - | 70 |  | 19770 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
629 | 80 | 67 |  |  | 17100 | - | 70 |  | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 2 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 4MXM36AVJU9 | FTXV24AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV24AVJU9 |  | 4MXM36AVJU9 | FTXV24AVJU9 |  | 4MXM36AVJU9 | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
629 | 80 | 67 |  |  | 17100 | - | 70 |  | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7430 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 0.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7430 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7430 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9510 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 6920 | - | 70 |  | 7240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6920 | - | 70 |  | 7240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 11860 | - | 70 |  | 12420 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 6830 | - | 70 |  | 7050 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6830 | - | 70 |  | 7050 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 14640 | - | 70 |  | 15100 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6740 | - | 70 |  | 6890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6740 | - | 70 |  | 6890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
565 | 80 | 67 |  |  | 17330 | - | 70 |  | 17720 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6300 | - | 70 |  | 6370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6300 | - | 70 |  | 6370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
629 | 80 | 67 |  |  | 21600 | - | 70 |  | 21850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 6970 | - | 70 |  | 9310 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 8960 | - | 70 |  | 9400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8960 | - | 70 |  | 9400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 8810 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 11740 | - | 70 |  | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 6770 | - | 70 |  | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 8710 | - | 70 |  | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 14520 | - | 70 |  | 14850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6690 | - | 70 |  | 6810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 8600 | - | 70 |  | 8760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 17210 | - | 70 |  | 17520 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5990 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 7700 | - | 70 |  | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
629 | 80 | 67 |  |  | 20520 | - | 70 |  | 20760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 6770 | - | 70 |  | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 11610 | - | 70 |  | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 11610 | - | 70 |  | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 6690 | - | 70 |  | 6810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 11470 | - | 70 |  | 11680 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 14340 | - | 70 |  | 14600 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6470 | - | 70 |  | 6880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 11090 | - | 70 |  | 11220 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 16640 | - | 70 |  | 16830 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5570 | - | 70 |  | 5630 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 9540 | - | 70 |  | 9660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
629 | 80 | 67 |  |  | 19090 | - | 70 |  | 19310 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 6470 | - | 70 |  | 6550 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 13860 | - | 70 |  | 14030 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 13860 | - | 70 |  | 14030 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5990 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 12830 | - | 70 |  | 12980 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 15390 | - | 70 |  | 15570 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5200 | - | 70 |  | 5270 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1.25 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 11150 | - | 70 |  | 11280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
629 | 80 | 67 |  |  | 17840 | - | 70 |  | 18050 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 5570 | - | 70 |  | 5630 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 14320 | - | 70 |  | 14480 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 14320 | - | 70 |  | 14480 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 8870 | - | 70 |  | 9200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 8870 | - | 70 |  | 9200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8870 | - | 70 |  | 9200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8730 | - | 70 |  | 9000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 8730 | - | 70 |  | 9000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 11640 | - | 70 |  | 12000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 8650 | - | 70 |  | 8810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 8650 | - | 70 |  | 8810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 14410 | - | 70 |  | 14680 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 17100 | - | 70 |  | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 7330 | - | 70 |  | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 7330 | - | 70 |  | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
629 | 80 | 67 |  |  | 19540 | - | 70 |  | 19770 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 8650 | - | 70 |  | 8810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 11530 | - | 70 |  | 11750 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 11530 | - | 70 |  | 11750 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 11400 | - | 70 |  | 11530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 14250 | - | 70 |  | 14420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 7890 | - | 70 |  | 7980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 10520 | - | 70 |  | 10650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 15780 | - | 70 |  | 15970 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 6840 | - | 70 |  | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 9120 | - | 70 |  | 9230 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
629 | 80 | 67 |  |  | 18240 | - | 70 |  | 18450 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 7890 | - | 70 |  | 7980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 13150 | - | 70 |  | 13310 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 13150 | - | 70 |  | 13310 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 7330 | - | 70 |  | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 12210 | - | 70 |  | 12360 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 14660 | - | 70 |  | 14830 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 6410 | - | 70 |  | 6490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1.25 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 10690 | - | 70 |  | 10810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
629 | 80 | 67 |  |  | 1710 | - | 70 |  | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 6840 | - | 70 |  | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 13680 | - | 70 |  | 13840 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 13680 | - | 70 |  | 13840 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
392 | 80 | 67 |  |  | 11400 | - | 70 |  | 11530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 11400 | - | 70 |  | 11530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 11400 | - | 70 |  | 11530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10520 | - | 70 |  | 10650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 10520 | - | 70 |  | 10650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 13150 | - | 70 |  | 13310 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
392 | 80 | 67 |  |  | 9770 | - | 70 |  | 9890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 9770 | - | 70 |  | 9890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 14660 | - | 70 |  | 14830 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
392 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
629 | 80 | 67 |  |  | 17100 | - | 70 |  | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
392 | 80 | 67 |  |  | 9770 | - | 70 |  | 9890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 12210 | - | 70 |  | 12360 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 12210 | - | 70 |  | 12650 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
392 | 80 | 67 |  |  | 9120 | - | 70 |  | 9230 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 11400 | - | 70 |  | 11530 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 13680 | - | 70 |  | 13840 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
392 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
565 | 80 | 67 |  |  | 12830 | - | 70 |  | 12980 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 12860 | - | 70 |  | 12980 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
540 | 80 | 67 |  |  | 11400 | - | 70 |  | 11530 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1.25 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 |  | 4MXM36AVJU9 | FTXV15AVJU9 |  | 4MXM36AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 11400 | - | 70 |  | 11530 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 11400 | - | 70 |  | 11530 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 10690 | - | 70 |  | 10810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1.25 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 4MXM36AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 |  | 4MXM36AVJU9 | FTXV15AVJU9 |  | 4MXM36AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
540 | 80 | 67 |  |  | 10690 | - | 70 |  | 10810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 12830 | - | 70 |  | 11530 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.5 | 0.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6790 | - | 70 |  | 7000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.5 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6790 | - | 70 |  | 7000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6790 | - | 70 |  | 7000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 8730 | - | 70 |  | 9000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 6720 | - | 70 |  | 6850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.5 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6720 | - | 70 |  | 6850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6720 | - | 70 |  | 6850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 11530 | - | 70 |  | 11750 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 6650 | - | 70 |  | 6730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.5 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6650 | - | 70 |  | 6730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6650 | - | 70 |  | 6760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 14250 | - | 70 |  | 14420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6140 | - | 70 |  | 6210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6140 | - | 70 |  | 6210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6140 | - | 70 |  | 6210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
565 | 80 | 67 |  |  | 15780 | - | 70 |  | 15970 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5320 | - | 70 |  | 5380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.5 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 5320 | - | 70 |  | 5380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 5320 | - | 70 |  | 5380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
629 | 80 | 67 |  |  | 18240 | - | 70 |  | 18450 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 6740 | - | 70 |  | 6890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.75 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6740 | - | 70 |  | 6890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 8660 | - | 70 |  | 8860 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8660 | - | 70 |  | 8860 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 6680 | - | 70 |  | 6760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.75 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6680 | - | 70 |  | 6760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 8590 | - | 70 |  | 8690 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 11450 | - | 70 |  | 11590 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 6300 | - | 70 |  | 6370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.75 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6300 | - | 70 |  | 6370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 8100 | - | 70 |  | 8190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 13500 | - | 70 |  | 13660 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5840 | - | 70 |  | 5910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.75 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 5840 | - | 70 |  | 5910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 7510 | - | 70 |  | 7600 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 15010 | - | 70 |  | 15190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5090 | - | 70 |  | 5150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.75 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 5090 | - | 70 |  | 5150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 6550 | - | 70 |  | 6630 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
629 | 80 | 67 |  |  | 17460 | - | 70 |  | 17670 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 6300 | - | 70 |  | 6370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 6300 | - | 70 |  | 6370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 10800 | - | 70 |  | 10930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10800 | - | 70 |  | 10930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 5840 | - | 70 |  | 5910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 5840 | - | 70 |  | 5910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 10010 | - | 70 |  | 10130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 12510 | - | 70 |  | 12660 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5440 | - | 70 |  | 5500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 5440 | - | 70 |  | 5500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 9330 | - | 70 |  | 9440 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 13990 | - | 70 |  | 14150 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5440 | - | 70 |  | 5500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 5440 | - | 70 |  | 5500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 11660 | - | 70 |  | 11800 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 11660 | - | 70 |  | 11800 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5090 | - | 70 |  | 5150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
332 | 80 | 67 |  |  | 5090 | - | 70 |  | 5150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 10910 | - | 70 |  | 11040 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 13100 | - | 70 |  | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6690 | - | 70 |  | 6810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 0.75 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 8600 | - | 70 |  | 8760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8600 | - | 70 |  | 8760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8600 | - | 70 |  | 8760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 6470 | - | 70 |  | 6550 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 0.75 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 8320 | - | 70 |  | 8420 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8320 | - | 70 |  | 8420 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 11090 | - | 70 |  | 11220 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 5990 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 0.75 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 7700 | - | 70 |  | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7700 | - | 70 |  | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 12830 | - | 70 |  | 12980 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5570 | - | 70 |  | 8630 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 0.75 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 7160 | - | 70 |  | 7240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7160 | - | 70 |  | 7240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 14320 | - | 70 |  | 14480 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5990 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 7700 | - | 70 |  | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 10260 | - | 70 |  | 10380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10260 | - | 70 |  | 10380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 5570 | - | 70 |  | 560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 7160 | - | 70 |  | 7240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 9540 | - | 70 |  | 9660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 11930 | - | 70 |  | 12070 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5200 | - | 70 |  | 5270 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 6690 | - | 70 |  | 6770 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 8920 | - | 70 |  | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 13380 | - | 70 |  | 13540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5200 | - | 70 |  | 5270 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 6690 | - | 70 |  | 6770 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 11150 | - | 70 |  | 11280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 11150 | - | 70 |  | 11280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5570 | - | 70 |  | 5630 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 9540 | - | 70 |  | 9660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9540 | - | 70 |  | 9660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9540 | - | 70 |  | 9660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 5200 | - | 70 |  | 5270 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  | 4MXM36AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 8920 | - | 70 |  | 9030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 8920 | - | 70 |  | 9030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 11150 | - | 70 |  | 11280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 0.75 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7890 | - | 70 |  | 7980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 0.75 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 7890 | - | 70 |  | 7980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7890 | - | 70 |  | 7980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 10520 | - | 70 |  | 10650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 7330 | - | 70 |  | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 0.75 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 7330 | - | 70 |  | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7330 | - | 70 |  | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 12210 | - | 70 |  | 12360 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 6840 | - | 70 |  | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 0.75 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 6840 | - | 70 |  | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 6840 | - | 70 |  | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 13680 | - | 70 |  | 13840 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 7330 | - | 70 |  | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 7330 | - | 70 |  | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 9770 | - | 70 |  | 9890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9770 | - | 70 |  | 9890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 6840 | - | 70 |  | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 6840 | - | 70 |  | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 9120 | - | 70 |  | 9230 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 11400 | - | 70 |  | 11530 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 6410 | - | 70 |  | 6490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 6410 | - | 70 |  | 6490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 12830 | - | 70 |  | 12980 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 6410 | - | 70 |  | 6490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
381 | 80 | 67 |  |  | 6410 | - | 70 |  | 6490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 10690 | - | 70 |  | 10810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 10690 | - | 70 |  | 10810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 6840 | - | 70 |  | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 1 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 9120 | - | 70 |  | 9230 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9120 | - | 70 |  | 9230 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9120 | - | 70 |  | 9230 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 6410 | - | 70 |  | 6490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 1 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  | 4MXM36AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 10690 | - | 70 |  | 10810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
392 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | DAIKIN | 4MXM36AVJU9 | R32 | 230' Max System Piping | 3 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 1 | 1 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 4MXM36AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  | 4MXM36AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 82 | 230 | 0.25 | 0.375 | 131.25 | 4.9 | 78.4 | 0.22
392 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 8550 | - | 70 |  | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 8950 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 0.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 8950 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 8930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 11480 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 8730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 14970 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 8240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 17660 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7870 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 20230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7320 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.5 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
629 | 80 | 67 |  |  | 24000 | - | 70 |  | 25080 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 11500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 11500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 10800 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 14400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 10280 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 17130 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9830 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 19670 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 0.75 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
629 | 80 | 67 |  |  | 24000 | - | 70 |  | 24650 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 13700 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 13700 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 13110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 16390 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12680 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 19020 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
629 | 80 | 67 |  |  | 24000 | - | 70 |  | 24400 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.25 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15410 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.25 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18490 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.25 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
629 | 80 | 67 |  |  | 24000 | - | 70 |  | 24370 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.5 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV18AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV18AVJU9 |  | 5MXM48AVJU9 | FTXV18AVJU9 |  | 5MXM48AVJU9 | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 1.5 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV18AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV18AVJU9 |  | 5MXM48AVJU9 | FTXV18AVJU9 |  | 5MXM48AVJU9 | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
629 | 80 | 67 |  |  | 24000 | - | 70 |  | 24340 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
629 | 80 | 67 |  |  | 23000 | - | 70 |  | 24250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 2 | 2 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - | 5MXM48AVJU9 | FTXV24AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV24AVJU9 |  | 5MXM48AVJU9 | FTXV24AVJU9 |  | 5MXM48AVJU9 | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
629 | 80 | 67 |  |  | 23000 | - | 70 |  | 24250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 8400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 0.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 8400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 8400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 8100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 8100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 10410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7750 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7750 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 13290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7480 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7480 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 16030 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7260 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7260 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18680 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.5 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
629 | 80 | 67 |  |  | 24000 | - | 70 |  | 24380 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7870 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 10120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 10120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9740 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12990 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7320 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15680 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9160 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 0.75 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
629 | 80 | 67 |  |  | 24000 | - | 70 |  | 24360 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7320 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12540 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12540 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18290 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
629 | 80 | 67 |  |  | 24000 | - | 70 |  | 24280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15240 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15240 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18270 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1.25 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
629 | 80 | 67 |  |  | 24000 | - | 70 |  | 24260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6570 | - | 70 |  | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 1.5 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 16900 | - | 70 |  | 17820 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
629 | 80 | 67 |  |  | 22530 | - | 70 |  | 23760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 5850 | - | 70 |  | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.5 | 2 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
629 | 80 | 67 |  |  | 20070 | - | 70 |  | 21160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
629 | 80 | 67 |  |  | 20070 | - | 70 |  | 21160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9830 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9830 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9830 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9510 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9510 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12680 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15410 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 0.75 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
629 | 80 | 67 |  |  | 24000 | - | 70 |  | 24340 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12330 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12330 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
629 | 80 | 67 |  |  | 24000 | - | 70 |  | 24270 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 8630 | - | 70 |  | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1.25 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 14380 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
629 | 80 | 67 |  |  | 23000 | - | 70 |  | 24250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 1.5 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 16240 | - | 70 |  | 17120 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
629 | 80 | 67 |  |  | 21650 | - | 70 |  | 22820 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 0.75 | 2 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
629 | 80 | 67 |  |  | 19370 | - | 70 |  | 20420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
629 | 80 | 67 |  |  | 19370 | - | 70 |  | 20420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
629 | 80 | 67 |  |  | 23000 | - | 70 |  | 24250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
392 | 80 | 67 |  |  | 10820 | - | 70 |  | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1.25 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 13530 | - | 70 |  | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
629 | 80 | 67 |  |  | 21650 | - | 70 |  | 22820 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 17250 | - | 70 |  | 18190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 17250 | - | 70 |  | 18190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1 | 1.5 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 15330 | - | 70 |  | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
629 | 80 | 67 |  |  | 20440 | - | 70 |  | 21560 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1.25 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 14380 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1.25 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 14380 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 17250 | - | 70 |  | 18190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
540 | 80 | 67 |  |  | 12780 | - | 70 |  | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1.25 | 1.25 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 12780 | - | 70 |  | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
629 | 80 | 67 |  |  | 20440 | - | 70 |  | 21560 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
540 | 80 | 67 |  |  | 13530 | - | 70 |  | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1.25 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 16240 | - | 70 |  | 17120 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 16240 | - | 70 |  | 17120 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
540 | 80 | 67 |  |  | 12110 | - | 70 |  | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1.25 | 1.5 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV15AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  | 5MXM48AVJU9 | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 14530 | - | 70 |  | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
629 | 80 | 67 |  |  | 19370 | - | 70 |  | 20420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
565 | 80 | 67 |  |  | 15330 | - | 70 |  | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 3 | 1.5 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - | 5MXM48AVJU9 | FTXV18AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV18AVJU9 |  | 5MXM48AVJU9 | FTXV18AVJU9 |  | 5MXM48AVJU9 | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
565 | 80 | 67 |  |  | 15330 | - | 70 |  | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 15330 | - | 70 |  | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.5 | 0.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.5 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9510 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.5 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12330 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.5 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.6 | 208/60/2 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.7 | 208/60/3 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.5 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
629 | 80 | 67 |  |  | 24000 | - | 70 |  | 24270 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7260 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.8 | 208/60/4 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.75 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7260 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9340 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9340 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.9 | 208/60/5 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.75 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.10 | 208/60/6 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.75 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15240 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.11 | 208/60/7 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.75 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.12 | 208/60/8 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 0.75 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 8810 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
629 | 80 | 67 |  |  | 23490 | - | 70 |  | 24260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.13 | 208/60/9 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.14 | 208/60/10 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15220 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.15 | 208/60/11 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6440 | - | 70 |  | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.16 | 208/60/12 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6440 | - | 70 |  | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 11040 | - | 70 |  | 11640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
629 | 80 | 67 |  |  | 22080 | - | 70 |  | 23280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.17 | 208/60/13 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.18 | 208/60/14 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 14680 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 17620 | - | 70 |  | 18190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6080 | - | 70 |  | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.19 | 208/60/15 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1.25 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6080 | - | 70 |  | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 13020 | - | 70 |  | 13730 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
629 | 80 | 67 |  |  | 20830 | - | 70 |  | 21960 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 6440 | - | 70 |  | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.20 | 208/60/16 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6440 | - | 70 |  | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
565 | 80 | 67 |  |  | 16560 | - | 70 |  | 17460 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 16560 | - | 70 |  | 17460 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5750 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.21 | 208/60/17 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.5 | 1.5 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 5750 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
565 | 80 | 67 |  |  | 14790 | - | 70 |  | 15590 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
629 | 80 | 67 |  |  | 19710 | - | 70 |  | 20790 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.22 | 208/60/18 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 0.75 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9160 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9160 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9160 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.23 | 208/60/19 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 0.75 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.24 | 208/60/20 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 0.75 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.25 | 208/60/21 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 0.75 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6570 | - | 70 |  | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.26 | 208/60/22 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 0.75 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 8450 | - | 70 |  | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8450 | - | 70 |  | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
629 | 80 | 67 |  |  | 22530 | - | 70 |  | 23760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.27 | 208/60/23 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.28 | 208/60/24 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.29 | 208/60/25 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.30 | 208/60/26 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7960 | - | 70 |  | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 10620 | - | 70 |  | 11190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
629 | 80 | 67 |  |  | 21230 | - | 70 |  | 22380 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.31 | 208/60/27 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6570 | - | 70 |  | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.32 | 208/60/28 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 8450 | - | 70 |  | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 14080 | - | 70 |  | 14850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 16900 | - | 70 |  | 17820 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5850 | - | 70 |  | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.33 | 208/60/29 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1.25 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7530 | - | 70 |  | 7940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 12550 | - | 70 |  | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
629 | 80 | 67 |  |  | 20070 | - | 70 |  | 21160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.34 | 208/60/30 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7960 | - | 70 |  | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 15920 | - | 70 |  | 16790 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 15920 | - | 70 |  | 16790 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5550 | - | 70 |  | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.35 | 208/60/31 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 0.75 | 1.5 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7140 | - | 70 |  | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 14280 | - | 70 |  | 15050 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
629 | 80 | 67 |  |  | 19030 | - | 70 |  | 20070 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.36 | 208/60/32 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.37 | 208/60/33 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6570 | - | 70 |  | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.38 | 208/60/34 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 11270 | - | 70 |  | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 11270 | - | 70 |  | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 16900 | - | 70 |  | 17820 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5850 | - | 70 |  | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.39 | 208/60/35 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1 | 1 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 10040 | - | 70 |  | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10040 | - | 70 |  | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
629 | 80 | 67 |  |  | 20070 | - | 70 |  | 21160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 6570 | - | 70 |  | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.40 | 208/60/36 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 11270 | - | 70 |  | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 14080 | - | 70 |  | 14850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 14080 | - | 70 |  | 14850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.41 | 208/60/37 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 10620 | - | 70 |  | 11190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 13270 | - | 70 |  | 13990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 15920 | - | 70 |  | 16790 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5550 | - | 70 |  | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.42 | 208/60/38 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1 | 1.25 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 9520 | - | 70 |  | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 11900 | - | 70 |  | 12540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
629 | 80 | 67 |  |  | 19030 | - | 70 |  | 20070 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 5850 | - | 70 |  | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.43 | 208/60/39 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1 | 1.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 10040 | - | 70 |  | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 15050 | - | 70 |  | 15870 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 15050 | - | 70 |  | 15870 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.44 | 208/60/40 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1.25 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 13270 | - | 70 |  | 13990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 13270 | - | 70 |  | 13990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 13270 | - | 70 |  | 13990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5850 | - | 70 |  | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.45 | 208/60/41 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1.25 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 12550 | - | 70 |  | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 12550 | - | 70 |  | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 15050 | - | 70 |  | 15870 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5550 | - | 70 |  | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.46 | 208/60/42 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.5 | 1.25 | 1.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 11900 | - | 70 |  | 12540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 14280 | - | 70 |  | 15050 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 14280 | - | 70 |  | 15050 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.47 | 208/60/43 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 0.75 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.48 | 208/60/44 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 0.75 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.49 | 208/60/45 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 0.75 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.50 | 208/60/46 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 0.75 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.51 | 208/60/47 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 0.75 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
629 | 80 | 67 |  |  | 21650 | - | 70 |  | 22820 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.52 | 208/60/48 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.53 | 208/60/49 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 8630 | - | 70 |  | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.54 | 208/60/50 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 8630 | - | 70 |  | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 17250 | - | 70 |  | 18190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.55 | 208/60/51 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 1 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
629 | 80 | 67 |  |  | 20440 | - | 70 |  | 21560 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 8630 | - | 70 |  | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.56 | 208/60/52 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 8630 | - | 70 |  | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 14380 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 14380 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.57 | 208/60/53 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 13530 | - | 70 |  | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 16240 | - | 70 |  | 17120 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.58 | 208/60/54 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 1.25 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 12110 | - | 70 |  | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
629 | 80 | 67 |  |  | 19370 | - | 70 |  | 20420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.59 | 208/60/55 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 0.75 | 1.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 15330 | - | 70 |  | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 15330 | - | 70 |  | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.60 | 208/60/56 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 1 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 8630 | - | 70 |  | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.61 | 208/60/57 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 1 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 14380 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.62 | 208/60/58 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 1 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 10820 | - | 70 |  | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10820 | - | 70 |  | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 16240 | - | 70 |  | 17120 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.63 | 208/60/59 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 1 | 1 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
629 | 80 | 67 |  |  | 19370 | - | 70 |  | 20420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.64 | 208/60/60 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 1 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 10820 | - | 70 |  | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 13530 | - | 70 |  | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 13530 | - | 70 |  | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.65 | 208/60/61 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 1 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 12780 | - | 70 |  | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 15330 | - | 70 |  | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.66 | 208/60/62 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 1 | 1.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 14530 | - | 70 |  | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 14530 | - | 70 |  | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.67 | 208/60/63 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 1.25 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 12780 | - | 70 |  | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 12780 | - | 70 |  | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 12780 | - | 70 |  | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.68 | 208/60/64 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 0.75 | 1.25 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 12110 | - | 70 |  | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 12110 | - | 70 |  | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 14530 | - | 70 |  | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.69 | 208/60/65 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 1 | 1 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10820 | - | 70 |  | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.70 | 208/60/66 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 1 | 1 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 10820 | - | 70 |  | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10820 | - | 70 |  | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 13530 | - | 70 |  | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.71 | 208/60/67 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 1 | 1 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 15330 | - | 70 |  | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.72 | 208/60/68 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 1 | 1 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 12780 | - | 70 |  | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 12780 | - | 70 |  | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.73 | 208/60/69 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 1 | 1 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 12110 | - | 70 |  | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 14530 | - | 70 |  | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/70 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 4 | 1 | 1.25 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - | 5MXM48AVJU9 | FTXV12AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  | 5MXM48AVJU9 | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
540 | 80 | 67 |  |  | 12110 | - | 70 |  | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 12110 | - | 70 |  | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 12110 | - | 70 |  | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.75 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
565 | 80 | 67 |  |  | 18000 | - | 70 |  | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 2 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
629 | 80 | 67 |  |  | 21230 | - | 70 |  | 22380 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 0.75 | 0.75 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 0.75 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 0.75 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 15000 | - | 70 |  | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6710 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 0.75 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6710 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6710 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 8630 | - | 70 |  | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 17250 | - | 70 |  | 18190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5960 | - | 70 |  | 6290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 0.75 | 2 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 5960 | - | 70 |  | 6290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 5960 | - | 70 |  | 6290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
629 | 80 | 67 |  |  | 20440 | - | 70 |  | 21560 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 6710 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6710 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6710 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 14380 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6310 | - | 70 |  | 6660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 1 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6310 | - | 70 |  | 6660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6310 | - | 70 |  | 6660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 10820 | - | 70 |  | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 16240 | - | 70 |  | 17120 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5650 | - | 70 |  | 5960 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 1 | 2 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 5650 | - | 70 |  | 5960 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 5650 | - | 70 |  | 5960 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
629 | 80 | 67 |  |  | 19370 | - | 70 |  | 20420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 6310 | - | 70 |  | 6660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 1.25 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6310 | - | 70 |  | 6660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 6310 | - | 70 |  | 6660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 13530 | - | 70 |  | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 13530 | - | 70 |  | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5960 | - | 70 |  | 6290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 1.25 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 5960 | - | 70 |  | 6290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 5960 | - | 70 |  | 6290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
540 | 80 | 67 |  |  | 12780 | - | 70 |  | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 15330 | - | 70 |  | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5650 | - | 70 |  | 5960 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.5 | 1.5 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 5650 | - | 70 |  | 5960 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
332 | 80 | 67 |  |  | 5650 | - | 70 |  | 5960 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
565 | 80 | 67 |  |  | 14530 | - | 70 |  | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
565 | 80 | 67 |  |  | 14530 | - | 70 |  | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.75 | 0.75 | 0.75 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.75 | 0.75 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.75 | 0.75 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 8810 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8810 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 14680 | - | 70 |  | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6440 | - | 70 |  | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.75 | 0.75 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6440 | - | 70 |  | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 8280 | - | 70 |  | 8730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8280 | - | 70 |  | 8730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 16560 | - | 70 |  | 17460 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5750 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.75 | 0.75 | 2 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 5750 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 7390 | - | 70 |  | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7390 | - | 70 |  | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
629 | 80 | 67 |  |  | 19710 | - | 70 |  | 20790 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.75 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6850 | - | 70 |  | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 8810 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 11740 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 11740 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 6440 | - | 70 |  | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.75 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6440 | - | 70 |  | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 8280 | - | 70 |  | 8730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 11040 | - | 70 |  | 11640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 13800 | - | 70 |  | 14550 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6080 | - | 70 |  | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.75 | 1 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6080 | - | 70 |  | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 7810 | - | 70 |  | 8240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 10420 | - | 70 |  | 10980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 15620 | - | 70 |  | 16470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6080 | - | 70 |  | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.75 | 1.25 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6080 | - | 70 |  | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 7810 | - | 70 |  | 8240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 13020 | - | 70 |  | 13730 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 13020 | - | 70 |  | 13730 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5750 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 0.75 | 1.25 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 5750 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
381 | 80 | 67 |  |  | 7390 | - | 70 |  | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 12320 | - | 70 |  | 12990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 14790 | - | 70 |  | 15590 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6440 | - | 70 |  | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 1 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6440 | - | 70 |  | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 11040 | - | 70 |  | 11640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 11040 | - | 70 |  | 11640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 11040 | - | 70 |  | 11640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 6080 | - | 70 |  | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 1 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 6080 | - | 70 |  | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 10420 | - | 70 |  | 10980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10420 | - | 70 |  | 10980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 13020 | - | 70 |  | 13730 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5750 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 1 | 1 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 5750 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 9860 | - | 70 |  | 10390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9860 | - | 70 |  | 10390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 14790 | - | 70 |  | 15590 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5750 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.5 | 1 | 1.25 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
332 | 80 | 67 |  |  | 5750 | - | 70 |  | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 | [6 empty] | IM - CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9
392 | 80 | 67 |  |  | 9860 | - | 70 |  | 10390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 12320 | - | 70 |  | 12990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 12320 | - | 70 |  | 12990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 0.75 | 0.75 | 0.75 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
332 | 80 | 67 |  |  | 7000 | - | 70 |  | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 0.75 | 0.75 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 12000 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 6570 | - | 70 |  | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 0.75 | 0.75 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 8450 | - | 70 |  | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8450 | - | 70 |  | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8450 | - | 70 |  | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 14080 | - | 70 |  | 14850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 0.75 | 0.75 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7960 | - | 70 |  | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7960 | - | 70 |  | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7960 | - | 70 |  | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 15920 | - | 70 |  | 16790 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5550 | - | 70 |  | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 0.75 | 0.75 | 2 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7140 | - | 70 |  | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7140 | - | 70 |  | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7140 | - | 70 |  | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
629 | 80 | 67 |  |  | 19030 | - | 70 |  | 20070 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 | [6 empty] | IM - FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | FTXV24AVJU9 |  |  | OM - FTXV24AVJU9
332 | 80 | 67 |  |  | 6570 | - | 70 |  | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 0.75 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 8450 | - | 70 |  | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8450 | - | 70 |  | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 11270 | - | 70 |  | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 11270 | - | 70 |  | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 0.75 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7960 | - | 70 |  | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7960 | - | 70 |  | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 10620 | - | 70 |  | 11190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 13270 | - | 70 |  | 13990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5850 | - | 70 |  | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 0.75 | 1 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7530 | - | 70 |  | 7940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7530 | - | 70 |  | 7940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 10040 | - | 70 |  | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 15050 | - | 70 |  | 15870 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5850 | - | 70 |  | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 0.75 | 1.25 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7530 | - | 70 |  | 7940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7530 | - | 70 |  | 7940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 12550 | - | 70 |  | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 12550 | - | 70 |  | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5550 | - | 70 |  | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 0.75 | 1.25 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7140 | - | 70 |  | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7140 | - | 70 |  | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 11900 | - | 70 |  | 12540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
565 | 80 | 67 |  |  | 14280 | - | 70 |  | 15050 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 6190 | - | 70 |  | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 1 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7960 | - | 70 |  | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 10620 | - | 70 |  | 11190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10620 | - | 70 |  | 11190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10620 | - | 70 |  | 11190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 5850 | - | 70 |  | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 1 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7530 | - | 70 |  | 7940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 10040 | - | 70 |  | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10040 | - | 70 |  | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 12550 | - | 70 |  | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5550 | - | 70 |  | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 1 | 1 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7140 | - | 70 |  | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 9520 | - | 70 |  | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9520 | - | 70 |  | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 14280 | - | 70 |  | 15050 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
332 | 80 | 67 |  |  | 5550 | - | 70 |  | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 0.75 | 1 | 1.25 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7140 | - | 70 |  | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 9520 | - | 70 |  | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 11900 | - | 70 |  | 12540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 11900 | - | 70 |  | 12540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
332 | 80 | 67 |  |  | 5850 | - | 70 |  | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 1 | 1 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 10040 | - | 70 |  | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10040 | - | 70 |  | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10040 | - | 70 |  | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10040 | - | 70 |  | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
332 | 80 | 67 |  |  | 5550 | - | 70 |  | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | CTXV07AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.5 | 1 | 1 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | CTXV07AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  | 5MXM48AVJU9 | CTXV07AVJU9 |  |  | OM - CTXV07AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 9520 | - | 70 |  | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9520 | - | 70 |  | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9520 | - | 70 |  | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 11900 | - | 70 |  | 12540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 9000 | - | 70 |  | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8630 | - | 70 |  | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.75 | 0.75 | 0.75 | 0.75 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 8630 | - | 70 |  | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8630 | - | 70 |  | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8630 | - | 70 |  | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 11500 | - | 70 |  | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.75 | 0.75 | 0.75 | 0.75 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 13530 | - | 70 |  | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.75 | 0.75 | 0.75 | 0.75 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
565 | 80 | 67 |  |  | 15330 | - | 70 |  | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.75 | 0.75 | 0.75 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 8120 | - | 70 |  | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 10820 | - | 70 |  | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10820 | - | 70 |  | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.75 | 0.75 | 0.75 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 12780 | - | 70 |  | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.75 | 0.75 | 0.75 | 1 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
565 | 80 | 67 |  |  | 14530 | - | 70 |  | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 | [6 empty] | IM - FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | FTXV18AVJU9 |  |  | OM - FTXV18AVJU9
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.75 | 0.75 | 0.75 | 1.25 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
540 | 80 | 67 |  |  | 12110 | - | 70 |  | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
540 | 80 | 67 |  |  | 12110 | - | 70 |  | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.75 | 0.75 | 1 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7670 | - | 70 |  | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 10220 | - | 70 |  | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.75 | 0.75 | 1 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 | [6 empty] | IM - FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
540 | 80 | 67 |  |  | 12110 | - | 70 |  | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 | [6 empty] | IM - FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | FTXV15AVJU9 |  |  | OM - FTXV15AVJU9
381 | 80 | 67 |  |  | 7260 | - | 70 |  | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV09AVJU9 | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | DAIKIN | 5MXM48AVJU9 | R32 | 262' Max System Piping | 4 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 5 | 0.75 | 1 | 1 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | 5MXM48AVJU9 | FTXV09AVJU9 |  | ENGINEERING MANUAL - MXM MULTI SPLIT |  |  | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  | 5MXM48AVJU9 | FTXV09AVJU9 |  |  | OM - FTXV09AVJU9 | R-32 | 49.25 | 24.6 | 262 | 0.25 | 0.375 | 131.25 | 6.94 | 111.04 | 0.22
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
392 | 80 | 67 |  |  | 9680 | - | 70 |  | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 | [6 empty] | IM - FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | FTXV12AVJU9 |  |  | OM - FTXV12AVJU9
378 | 80 | 67 |  |  | 9100 | 8250 | 70 |  | 10000 | 36 | Cassette | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FFA09AVJU9 | 95 | 47 | 63 | 19.8 / 12.0 / 9.4 | 208/60/1 | 11.6 | 15 | DAIKIN | RXV09AVJU9 | R32 | 49' Vertical / 66' Total | 0.75 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Cassette | - | - | - | - |  |  | FFA09AVJU9-RXV09AVJU9 | ENGINEERING MANUAL - VISTA CASSETTE |  |  |  | IM - VISTA CASSETTE OUTDOOR (09-12) | IM - VISTA CASSETTE IDU |  | RXV09AVJU9 | FFA09AVJU9 |  | RXV09AVJU9 | FFA09AVJU9 |  |  | OM - VISTA CASSETTE | R-32 | 49 | - | 66 | 0.25 | 0.375 | 49 | 1.65 | 26.4 | 0.22
406 | 80 | 67 |  |  | 10800 | 9730 | 70 |  | 13500 | 36 | Cassette | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FFA12AVJU9 | 95 | 47 | 63 | 19.5 / 11.5 / 9.0 | 208/60/1 | 14.6 | 15 | DAIKIN | RXV12AVJU9 | R32 | 49' Vertical / 66' Total | 1 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Cassette | - | - | - | - |  |  | FFA12AVJU9-RXV12AVJU9 | ENGINEERING MANUAL - VISTA CASSETTE |  |  |  | IM - VISTA CASSETTE OUTDOOR (09-12) | IM - VISTA CASSETTE IDU |  | RXV12AVJU9 | FFA12AVJU9 |  | RXV12AVJU9 | FFA12AVJU9 |  |  | OM - VISTA CASSETTE | R-32 | 49 | - | 66 | 0.25 | 0.375 | 49 | 1.65 | 26.4 | 0.22
420 | 80 | 67 |  |  | 14400 | 10540 | 70 |  | 16200 | 36 | Cassette | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FFA15AVJU9 | 95 | 47 | 113 | 19.6 / 11.5 / 8.8 | 208/60/1 | 16 | 20 | DAIKIN | RXV15AVJU9 | R32 | 66' Vertical / 99' Total | 1.25 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1.25 | - | - | - | - | Cassette | - | - | - | - |  |  | FFA15AVJU9-RXV15AVJU9 | ENGINEERING MANUAL - VISTA CASSETTE |  |  |  | IM - VISTA CASSETTE OUTDOOR (15-18) | IM - VISTA CASSETTE IDU |  | RXV15AVJU9 | FFA15AVJU9 |  | RXV15AVJU9 | FFA15AVJU9 |  |  | OM - VISTA CASSETTE | R-32 | 66 | - | 99 | 0.25 | 0.5 | 49 | 2.45 | 39.2 | 0.22
508 | 80 | 67 |  |  | 17400 | 12270 | 70 |  | 21600 | 36 | Cassette | Indoor Powered From Outdoor Unit |  |  | DAIKIN | FFA18AVJU9 | 95 | 47 | 113 | 18.2 / 11.5 / 8.5 | 208/60/1 | 17.9 | 20 | DAIKIN | RXV18AVJU9 | R32 | 66' Vertical / 99' Total | 1.5 | HEAT PUMP | 208/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Cassette | - | - | - | - |  |  | FFA18AVJU9-RXV18AVJU9 | ENGINEERING MANUAL - VISTA CASSETTE |  |  |  | IM - VISTA CASSETTE OUTDOOR (15-18) | IM - VISTA CASSETTE IDU |  | RXV18AVJU9 | FFA18AVJU9 |  | RXV18AVJU9 | FFA18AVJU9 |  |  | OM - VISTA CASSETTE | R-32 | 66 | - | 99 | 0.25 | 0.5 | 49 | 2.45 | 39.2 | 0.22

## SCHEDULE NOTES
Provide with 7-day programmable thermostat
Provide with 7-day programmable BACnet thermostat
Provide with low ambient wind baffle for cooling down to 0°F
Provide with field installed condensate pump
Provide with field installed disconnect. Disconnect shall be provided and installed by electrical contractor