## MULTI POSITION SPLIT
SPLIT SYSTEM HEAT PUMP SCHEDULE
TAG | DAIKIN AIR HANDLER MODEL NO. | NOMINAL TONS | LOCATION | TOTAL CFM | OA CFM | MAX FAN HP | ESP | MBH TOT. COOL | MBH SENS. COOL | EFFICIENCY | HEAT PUMP HEAT | HEAT KW | VOLTS/ PHASE | MCA | MOCP | TAG | DAIKIN HEAT PUMP MODEL NO. | VOLTS/ PHASE | MCA | MOCP | NOTES
NOTE:
1 | COOLING CAPACITIES ARE RATED IN ACCORDANCE WITH ARI STANDARD 210/290 AT 95°F AMBIENT OUTDOOR AIR TEMP., 80°F
DRY BULB, 67°F WET BULB ENTERING AIR TEMP., AND NOMINAL AIR QUANTITY LISTED.
2 | REFRIG. R-32 PIPING TO BE SIZED PER TOTAL INSTALL. EQUIV. LENGTH. LONG-LINE APP. TO BE PROVIDED WHENEVER MFG.
RECOMM. LENGTHS ARE EXCEEDED, INCL. LIQ. LINE SOLENOID VALVES, ACCUMULATOR, ETC. MAX T.E.L. IS 100'
3 | PROVIDE SINGLE POINT ELECTRICAL CONNECTION
4 | PROVIDE HONEYWELL "VISION-PRO 8000" THERMOSTAT/HUMIDISTAT
5 | PROVIDE NEW FILTERS IN UNIT WHEN BUILDING IS TURNED OVER TO OWNER/TENANT.
6 | SES HEAT PUMP DEHUMIDIFICATION CONTROL MODULE HPDM-MP AS WELL AS EQUIPMENT AND CONTROLS AS REQUIRED
FOR A COMPLETE WORKING SYSTEM
7 | HEAT PUMP TO BE INSTALLED LEVEL ON MANUFACTURERS PREFORMED PAD.
8 | PROVIDE LOW AMBIENT CONTROLS.
APPROVED EQUALS: TRANE, CARRIER, & LENNOX