## Mechanical Schedule
PACKAGED ROOFTOP UNITS
TAG | MAKE | MODEL NUMBER | NOM TONS | Fan Data |  |  | Cooling Performance | [6 empty] | Heating Performance |  |  |  | MODULATING HOT GAS REHEAT | COOLING STAGES | Electrical Data |  |  |  | NOTES | FILTERS | [5 empty] | DOCUMENTATION
|  |  |  | CFM | ESP (IWG) | TESP (IWG) | TOTAL CAPACITY (BTU/h) | SENSIBLE CAPACITY (BTU/h) | EFFICIENCY (AT AHRI) | EDB (°F) | EWB (°F) | LDB (°F) | LWB (°F) | INPUT (MBH) | OUTPUT (MBH) | EAT (°F) | LAT (°F) |  |  | VOLT/PH | INDOOR MOTOR HP | Unit MCA | Unit MOCP |  | SIZE | ELECTRICAL | EFFICIENCY | COOLING STAGES | HIGH/MEDIUM/LOW GAS HEAT | HGRH | SUBMITTAL (SYSTEM) | ENGINEERING MANUAL | INSTALLATION MANUAL | REVIT | CAD
RTU- | DAIKIN | DSG0363DM | 3 | 1265 | 0.5 | 0.5 | 35418 | 27395 | 14.0 SEER2/12.0 EER2 | 80 | 67 | 60.3 | 58.2 | 70 | 56.7 | 55 | 96 | NO | 1 | 208/3 | 0.75 | 19.9 | 30 |  | 3 | 208/3 | STANDARD | 1 | MEDIUM | NO | DSG0363DM | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0363DM | DSG0363DM
RTU- | DAIKIN | DSG0363DL | 3 | 1265 | 0.5 | 0.5 | 35418 | 27395 | 14.0 SEER2/12.0 EER2 | 80 | 67 | 60.3 | 58.2 | 45 | 36.45 | 55 | 81.4 | NO | 1 | 208/3 | 0.75 | 19.9 | 30 |  | 3 | 208/3 | STANDARD | 1 | LOW | NO | DSG0363DL | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0363DL | DSG0363DL
RTU- | DAIKIN | DSG0363DH | 3 | 1265 | 0.5 | 0.5 | 35418 | 27395 | 14.0 SEER2/12.0 EER2 | 80 | 67 | 60.3 | 58.2 | 90 | 72.9 | 55 | 107.7 | NO | 1 | 208/3 | 0.75 | 19.9 | 30 |  | 3 | 208/3 | STANDARD | 1 | HIGH | NO | DSG0363DH | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0363DH | DSG0363DH
RTU- | DAIKIN | DSG0364DL | 3 | 1265 | 0.5 | 0.5 | 35418 | 27395 | 14.0 SEER2/12.0 EER2 | 80 | 67 | 60.3 | 58.2 | 45 | 36.45 | 55 | 81.4 | NO | 1 | 460/3 | 1.2 | 9.1 | 15 |  | 3 | 460/3 | STANDARD | 1 | LOW | NO | DSG0364DL | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0364DL | DSG0364DL
RTU- | DAIKIN | DSG0364DM | 3 | 1265 | 0.5 | 0.5 | 35418 | 27395 | 14.0 SEER2/12.0 EER2 | 80 | 67 | 60.3 | 58.2 | 70 | 56.7 | 55 | 96 | NO | 1 | 460/3 | 1.2 | 9.1 | 15 |  | 3 | 460/3 | STANDARD | 1 | MEDIUM | NO | DSG0364DM | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0364DM | DSG0364DM
RTU- | DAIKIN | DSG0364DH | 3 | 1265 | 0.5 | 0.5 | 35418 | 27395 | 14.0 SEER2/12.0 EER2 | 80 | 67 | 60.3 | 58.2 | 90 | 72.9 | 55 | 107.7 | NO | 1 | 460/3 | 1.2 | 9.1 | 15 |  | 3 | 460/3 | STANDARD | 1 | HIGH | NO | DSG0364DH | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0364DH | DSG0364DH
RTU- | DAIKIN | DHG0363DL | 3 | 1267 | 0.5 | 0.5 | 35471 | 28816 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 59.3 | 58.2 | 45 | 36.45 | 55 | 81.3 | NO | 2 | 208/3 | 0.75 | 18.1 | 25 |  | 3 | 208/3 | HIGH | 2 | LOW | NO | DHG0363DL | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0363DL | DHG0363DL
RTU- | DAIKIN | DHG0363DM | 3 | 1267 | 0.5 | 0.5 | 35471 | 28816 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 59.3 | 58.2 | 70 | 56.7 | 55 | 95.9 | NO | 2 | 208/3 | 0.75 | 18.1 | 25 |  | 3 | 208/3 | HIGH | 2 | MEDIUM | NO | DHG0363DM | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0363DM | DHG0363DM
RTU- | DAIKIN | DHG0363DH | 3 | 1267 | 0.5 | 0.5 | 36499 | 32119 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 63.3 | 60.6 | 115 | 93.15 | 55 | 103.8 | NO | 2 | 208/3 | 0.75 | 18.1 | 25 |  | 3 | 208/3 | HIGH | 2 | HIGH | NO | DHG0363DH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0363DH | DHG0363DH
RTU- | DAIKIN | DHG0364DL | 3 | 1392 | 0.5 | 0.5 | 36022 | 30588 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 60 | 58.9 | 45 | 36.45 | 55 | 78.9 | NO | 2 | 460/3 | 1.2 | 8.2 | 15 |  | 3 | 460/3 | HIGH | 2 | LOW | NO | DHG0364DL | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0364DL | DHG0364DL
RTU- | DAIKIN | DHG0364DM | 3 | 1392 | 0.5 | 0.5 | 36022 | 30588 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 60 | 58.9 | 70 | 56.7 | 55 | 92.2 | NO | 2 | 460/3 | 1.2 | 8.2 | 15 |  | 3 | 460/3 | HIGH | 2 | MEDIUM | NO | DHG0364DM | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0364DM | DHG0364DM
RTU- | DAIKIN | DHG0364DH | 3 | 1392 | 0.5 | 0.5 | 36022 | 30588 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 60 | 58.9 | 115 | 93.15 | 55 | 116.2 | NO | 2 | 460/3 | 1.2 | 8.2 | 15 |  | 3 | 460/3 | HIGH | 2 | HIGH | NO | DHG0364DH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0364DH | DHG0364DH
RTU- | DAIKIN | DSG0483DL | 4 | 1655 | 0.5 | 0.5 | 46202 | 36218 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.1 | 58.2 | 70 | 56.7 | 55 | 86.3 | NO | 1 | 208/3 | 1 | 24.1 | 35 |  | 4 | 208/3 | STANDARD | 1 | LOW | NO | DSG0483DL | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0483DL | DSG0483DL
RTU- | DAIKIN | DSG0483DM | 4 | 1655 | 0.5 | 0.5 | 46202 | 36218 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.1 | 58.2 | 90 | 72.9 | 55 | 95.3 | NO | 1 | 208/3 | 1 | 24.1 | 35 |  | 4 | 208/3 | STANDARD | 1 | MEDIUM | NO | DSG0483DM | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0483DM | DSG0483DM
RTU- | DAIKIN | DSG0483DH | 4 | 1655 | 0.5 | 0.5 | 46202 | 36218 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.1 | 58.2 | 115 | 93.15 | 55 | 106.5 | NO | 1 | 208/3 | 1 | 24.1 | 35 |  | 4 | 208/3 | STANDARD | 1 | HIGH | NO | DSG0483DH | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0483DH | DSG0483DH
RTU- | DAIKIN | DSG0484DL | 4 | 1660 | 0.5 | 0.5 | 46221 | 36291 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.1 | 58.3 | 70 | 56.7 | 55 | 86.2 | NO | 1 | 460/3 | 1.2 | 10.6 | 15 |  | 4 | 460/3 | STANDARD | 1 | LOW | NO | DSG0484DL | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0484DL | DSG0484DL
RTU- | DAIKIN | DSG0484DM | 4 | 1660 | 0.5 | 0.5 | 46221 | 36291 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.1 | 58.3 | 90 | 72.9 | 55 | 95.2 | NO | 1 | 460/3 | 1.2 | 10.6 | 15 |  | 4 | 460/3 | STANDARD | 1 | MEDIUM | NO | DSG0484DM | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0484DM | DSG0484DM
RTU- | DAIKIN | DSG0484DH | 4 | 1660 | 0.5 | 0.5 | 46221 | 36291 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.1 | 58.3 | 115 | 93.15 | 55 | 106.3 | NO | 1 | 460/3 | 1.2 | 10.6 | 15 |  | 4 | 460/3 | STANDARD | 1 | HIGH | NO | DSG0484DH | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0484DH | DSG0484DH
RTU- | DAIKIN | DHG0483DL | 4 | 1672 | 0.5 | 0.5 | 47034 | 37846 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.4 | 58.2 | 70 | 56.7 | 55 | 86 | NO | 2 | 208/3 | 1 | 22.8 | 30 |  | 4 | 208/3 | HIGH | 2 | LOW | NO | DHG0483DL | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0483DL | DHG0483DL
RTU- | DAIKIN | DHG0483DM | 4 | 1660 | 0.5 | 0.5 | 46976 | 37683 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.4 | 58.1 | 115 | 93.15 | 55 | 106.3 | NO | 2 | 208/3 | 1 | 22.8 | 30 |  | 4 | 208/3 | HIGH | 2 | MEDIUM | NO | DHG0483DM | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0483DM | DHG0483DM
RTU- | DAIKIN | DHG0483DH | 4 | 1692 | 0.5 | 0.5 | 47132 | 38119 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.5 | 58.3 | 140 | 113.4 | 55 | 116.3 | NO | 2 | 208/3 | 1 | 22.8 | 30 |  | 4 | 208/3 | HIGH | 2 | HIGH | NO | DHG0483DH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0483DH | DHG0483DH
RTU- | DAIKIN | DHG0484DL | 4 | 1692 | 0.5 | 0.5 | 47132 | 38119 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.5 | 58.3 | 70 | 56.7 | 55 | 85.6 | NO | 2 | 460/3 | 1.2 | 10.7 | 15 |  | 4 | 460/3 | HIGH | 2 | LOW | NO | DHG0484DL | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0484DL | DHG0484DL
RTU- | DAIKIN | DHG0484DM | 4 | 1660 | 0.5 | 0.5 | 46976 | 37683 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.4 | 58.1 | 115 | 93.15 | 55 | 106.3 | NO | 2 | 460/3 | 1.2 | 10.7 | 15 |  | 4 | 460/3 | HIGH | 2 | MEDIUM | NO | DHG0484DM | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0484DM | DHG0484DM
RTU- | DAIKIN | DHG0484DH | 4 | 1692 | 0.5 | 0.5 | 47132 | 38119 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.5 | 58.3 | 140 | 113.4 | 55 | 116.3 | NO | 2 | 460/3 | 1.2 | 10.7 | 15 |  | 4 | 460/3 | HIGH | 2 | HIGH | NO | DHG0484DH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0484DH | DHG0484DH
RTU- | DAIKIN | DSG0603DL | 5 | 2090 | 0.5 | 0.5 | 58474 | 45127 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.4 | 58.2 | 90 | 72.9 | 55 | 86.9 | NO | 1 | 208/3 | 1 | 28.1 | 40 |  | 5 | 208/3 | STANDARD | 1 | LOW | NO | DSG0603DL | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0603DL | DSG0603DL
RTU- | DAIKIN | DSG0603DM | 5 | 2090 | 0.5 | 0.5 | 58474 | 45127 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.4 | 58.2 | 115 | 93.15 | 55 | 95.8 | NO | 1 | 208/3 | 1 | 28.1 | 40 |  | 5 | 208/3 | STANDARD | 1 | MEDIUM | NO | DSG0603DM | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0603DM | DSG0603DM
RTU- | DAIKIN | DSG0603DH | 5 | 2090 | 0.5 | 0.5 | 58474 | 45127 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.4 | 58.2 | 140 | 113.4 | 55 | 104.6 | NO | 1 | 208/3 | 1 | 28.1 | 40 |  | 5 | 208/3 | STANDARD | 1 | HIGH | NO | DSG0603DH | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0603DH | DSG0603DH
RTU- | DAIKIN | DSG0604DL | 5 | 2115 | 0.5 | 0.5 | 58580 | 45470 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.5 | 58.3 | 90 | 72.9 | 55 | 86.5 | NO | 1 | 460/3 | 1.2 | 13 | 20 |  | 5 | 460/3 | STANDARD | 1 | LOW | NO | DSG0604DL | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0604DL | DSG0604DL
RTU- | DAIKIN | DSG0604DM | 5 | 2115 | 0.5 | 0.5 | 58580 | 45470 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.5 | 58.3 | 115 | 93.15 | 55 | 95.3 | NO | 1 | 460/3 | 1.2 | 13 | 20 |  | 5 | 460/3 | STANDARD | 1 | MEDIUM | NO | DSG0604DM | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0604DM | DSG0604DM
RTU- | DAIKIN | DSG0604DH | 5 | 2115 | 0.5 | 0.5 | 58580 | 45470 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.5 | 58.3 | 140 | 113.4 | 55 | 104 | NO | 1 | 460/3 | 1.2 | 13 | 20 |  | 5 | 460/3 | STANDARD | 1 | HIGH | NO | DSG0604DH | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0604DH | DSG0604DH
RTU- | DAIKIN | DHG0603DL | 5 | 2022 | 0.5 | 0.5 | 59669 | 44976 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 59.8 | 57.7 | 70 | 56.7 | 55 | 80.6 | NO | 2 | 208/3 | 1 | 28.5 | 40 |  | 5 | 208/3 | HIGH | 2 | LOW | NO | DHG0603DL | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0603DL | DHG0603DL
RTU- | DAIKIN | DHG0603DM | 5 | 2022 | 0.5 | 0.5 | 59669 | 44976 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 59.8 | 57.7 | 115 | 93.15 | 55 | 97.1 | NO | 2 | 208/3 | 1 | 28.5 | 40 |  | 5 | 208/3 | HIGH | 2 | MEDIUM | NO | DHG0603DM | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0603DM | DHG0603DM
RTU- | DAIKIN | DHG0603DH | 5 | 2022 | 0.5 | 0.5 | 59669 | 44976 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 59.8 | 57.7 | 140 | 113.4 | 55 | 106.3 | NO | 2 | 208/3 | 1 | 28.5 | 40 |  | 5 | 208/3 | HIGH | 2 | HIGH | NO | DHG0603DH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0603DH | DHG0603DH
RTU- | DAIKIN | DHG0604DL | 5 | 2045 | 0.5 | 0.5 | 59777 | 45285 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 59.9 | 57.8 | 70 | 56.7 | 55 | 80.4 | NO | 2 | 460/3 | 1.2 | 13.3 | 20 |  | 5 | 460/3 | HIGH | 2 | LOW | NO | DHG0604DL | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0604DL | DHG0604DL
RTU- | DAIKIN | DHG0604DM | 5 | 2045 | 0.5 | 0.5 | 59777 | 45285 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 59.9 | 57.8 | 115 | 93.15 | 55 | 96.7 | NO | 2 | 460/3 | 1.2 | 13.3 | 20 |  | 5 | 460/3 | HIGH | 2 | MEDIUM | NO | DHG0604DM | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0604DM | DHG0604DM
RTU- | DAIKIN | DHG0604DH | 5 | 2045 | 0.5 | 0.5 | 59777 | 45285 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 59.9 | 57.8 | 140 | 113.4 | 55 | 105.7 | NO | 2 | 460/3 | 1.2 | 13.3 | 20 |  | 5 | 460/3 | HIGH | 2 | HIGH | NO | DHG0604DH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0604DH | DHG0604DH
RTU- | DAIKIN | DSG0723DL | 6 | 2235 | 0.5 | 0.5 | 69644 | 49347 | 16.7 IEER/11.8 EER | 80 | 67 | 59.9 | 57.1 | 90 | 72.9 | 55 | 84.8 | NO | 2 | 208/3 | 1.2 | 27.2 | 40 |  | 6 | 208/3 | STANDARD | 2 | LOW | NO | DSG0723DL | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0723DL | DSG0723DL
RTU- | DAIKIN | DSG0723DM | 6 | 2235 | 0.5 | 0.5 | 69644 | 49347 | 16.7 IEER/11.8 EER | 80 | 67 | 59.9 | 57.1 | 115 | 93.15 | 55 | 93.1 | NO | 2 | 208/3 | 1.2 | 27.2 | 40 |  | 6 | 208/3 | STANDARD | 2 | MEDIUM | NO | DSG0723DM | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0723DM | DSG0723DM
RTU- | DAIKIN | DSG0723DH | 6 | 2235 | 0.5 | 0.5 | 69644 | 49347 | 16.7 IEER/11.8 EER | 80 | 67 | 59.9 | 57.1 | 140 | 113.4 | 55 | 101.4 | NO | 2 | 208/3 | 1.2 | 27.2 | 40 |  | 6 | 208/3 | STANDARD | 2 | HIGH | NO | DSG0723DH | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0723DH | DSG0723DH
RTU- | DAIKIN | DSG0724DL | 6 | 2235 | 0.5 | 0.5 | 69644 | 49347 | 16.7 IEER/11.8 EER | 80 | 67 | 59.9 | 57.1 | 90 | 72.9 | 55 | 84.8 | NO | 2 | 460/3 | 1.2 | 12.2 | 15 |  | 6 | 460/3 | STANDARD | 2 | LOW | NO | DSG0724DL | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0724DL | DSG0724DL
RTU- | DAIKIN | DSG0724DM | 6 | 2235 | 0.5 | 0.5 | 69644 | 49347 | 16.7 IEER/11.8 EER | 80 | 67 | 59.9 | 57.1 | 115 | 93.15 | 55 | 93.1 | NO | 2 | 460/3 | 1.2 | 12.2 | 15 |  | 6 | 460/3 | STANDARD | 2 | MEDIUM | NO | DSG0724DM | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0724DM | DSG0724DM
RTU- | DAIKIN | DSG0724DH | 6 | 2235 | 0.5 | 0.5 | 69644 | 49347 | 16.7 IEER/11.8 EER | 80 | 67 | 59.9 | 57.1 | 140 | 113.4 | 55 | 101.4 | NO | 2 | 460/3 | 1.2 | 12.2 | 15 |  | 6 | 460/3 | STANDARD | 2 | HIGH | NO | DSG0724DH | ENGINEERING MANUAL - DSG (3-6) | INSTALLATION MANUAL - DSG (3-6) | DSG0724DH | DSG0724DH
RTU- | DAIKIN | DHG0723DL | 6 | 2250 | 0.5 | 0.5 | 69506 | 53078 | 18.6 IEER/12.5 EER | 80 | 67 | 58.5 | 57.2 | 70 | 56.7 | 55 | 78 | NO | 2 | 208/3 | 1.2 | 27.2 | 40 |  | 6 | 208/3 | HIGH | 2 | LOW | NO | DHG0723DL | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0723DL | DHG0723DL
RTU- | DAIKIN | DHG0723DM | 6 | 2250 | 0.5 | 0.5 | 69506 | 53078 | 18.6 IEER/12.5 EER | 80 | 67 | 58.5 | 57.2 | 125 | 101.25 | 55 | 96.2 | NO | 2 | 208/3 | 1.2 | 27.2 | 40 |  | 6 | 208/3 | HIGH | 2 | MEDIUM | NO | DHG0723DM | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0723DM | DHG0723DM
RTU- | DAIKIN | DHG0723DH | 6 | 2250 | 0.5 | 0.5 | 69506 | 53078 | 18.6 IEER/12.5 EER | 80 | 67 | 58.5 | 57.2 | 150 | 121.5 | 55 | 104.4 | NO | 2 | 208/3 | 1.2 | 27.2 | 40 |  | 6 | 208/3 | HIGH | 2 | HIGH | NO | DHG0723DH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0723DH | DHG0723DH
RTU- | DAIKIN | DHG0724DL | 6 | 2250 | 0.5 | 0.5 | 69506 | 53078 | 18.6 IEER/12.5 EER | 80 | 67 | 58.5 | 57.2 | 70 | 56.7 | 55 | 78 | NO | 2 | 460/3 | 1.2 | 12.2 | 15 |  | 6 | 460/3 | HIGH | 2 | LOW | NO | DHG0724DL | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0724DL | DHG0724DL
RTU- | DAIKIN | DHG0724DM | 6 | 2250 | 0.5 | 0.5 | 69506 | 53078 | 18.6 IEER/12.5 EER | 80 | 67 | 58.5 | 57.2 | 125 | 101.25 | 55 | 96.2 | NO | 2 | 460/3 | 1.2 | 12.2 | 15 |  | 6 | 460/3 | HIGH | 2 | MEDIUM | NO | DHG0724DM | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0724DM | DHG0724DM
RTU- | DAIKIN | DHG0724DH | 6 | 2250 | 0.5 | 0.5 | 69506 | 53078 | 18.6 IEER/12.5 EER | 80 | 67 | 58.5 | 57.2 | 150 | 121.5 | 55 | 104.4 | NO | 2 | 460/3 | 1.2 | 12.2 | 15 |  | 6 | 460/3 | HIGH | 2 | HIGH | NO | DHG0724DH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0724DH | DHG0724DH
RTU- | DAIKIN | DSG0903DL | 7.5 | 3082 | 0.5 | 0.5 | 90314 | 68535 | 16.0 IEER/12.0 EER | 80 | 67 | 59.8 | 57.8 | 130 | 105.3 | 55 | 86.2 | NO | 2 | 208/3 | 2.4 | 39.4 | 50 |  | 7.5 | 208/3 | STANDARD | 2 | LOW | NO | DSG0903DL | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG0903DL | DSG0903DL
RTU- | DAIKIN | DSG0903DM | 7.5 | 3101 | 0.5 | 0.5 | 90388 | 68775 | 16.0 IEER/12.0 EER | 80 | 67 | 59.8 | 57.8 | 180 | 145.8 | 55 | 98 | NO | 2 | 208/3 | 2.4 | 39.4 | 50 |  | 7.5 | 208/3 | STANDARD | 2 | MEDIUM | NO | DSG0903DM | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG0903DM | DSG0903DM
RTU- | DAIKIN | DSG0903DH | 7.5 | 3023 | 0.5 | 0.5 | 90087 | 67789 | 16.0 IEER/12.0 EER | 80 | 67 | 59.6 | 57.6 | 225 | 182.25 | 55 | 110.1 | NO | 2 | 208/3 | 2.4 | 39.4 | 50 |  | 7.5 | 208/3 | STANDARD | 2 | HIGH | NO | DSG0903DH | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG0903DH | DSG0903DH
RTU- | DAIKIN | DSG0904DL | 7.5 | 3082 | 0.5 | 0.5 | 90314 | 68535 | 16.0 IEER/12.0 EER | 80 | 67 | 59.8 | 57.8 | 130 | 105.3 | 55 | 86.2 | NO | 2 | 460/3 | 2.4 | 20.1 | 25 |  | 7.5 | 460/3 | STANDARD | 2 | LOW | NO | DSG0904DL | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG0904DL | DSG0904DL
RTU- | DAIKIN | DSG0904DM | 7.5 | 3101 | 0.5 | 0.5 | 90388 | 68775 | 16.0 IEER/12.0 EER | 80 | 67 | 59.8 | 57.8 | 180 | 145.8 | 55 | 98 | NO | 2 | 460/3 | 2.4 | 20.1 | 25 |  | 7.5 | 460/3 | STANDARD | 2 | MEDIUM | NO | DSG0904DM | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG0904DM | DSG0904DM
RTU- | DAIKIN | DSG0904DH | 7.5 | 3023 | 0.5 | 0.5 | 90087 | 67789 | 16.0 IEER/12.0 EER | 80 | 67 | 59.6 | 57.6 | 225 | 182.25 | 55 | 110.1 | NO | 2 | 460/3 | 2.4 | 20.1 | 25 |  | 7.5 | 460/3 | STANDARD | 2 | HIGH | NO | DSG0904DH | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG0904DH | DSG0904DH
RTU- | DAIKIN | DHG0903DL | 7.5 | 3146 | 0.5 | 0.5 | 90561 | 72417 | 17.5 IEER/12.5 EER | 80 | 67 | 59.1 | 57.9 | 130 | 105.3 | 55 | 85.6 | NO | 2 | 208/3 | 2.4 | 39.4 | 50 |  | 7.5 | 208/3 | HIGH | 2 | LOW | NO | DHG0903DL | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG0903DL | DHG0903DL
RTU- | DAIKIN | DHG0903DM | 7.5 | 3024 | 0.5 | 0.5 | 90091 | 70563 | 17.5 IEER/12.5 EER | 80 | 67 | 58.8 | 57.6 | 180 | 145.8 | 55 | 99.1 | NO | 2 | 208/3 | 2.4 | 39.4 | 50 |  | 7.5 | 208/3 | HIGH | 2 | MEDIUM | NO | DHG0903DM | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG0903DM | DHG0903DM
RTU- | DAIKIN | DHG0903DH | 7.5 | 3000 | 0.5 | 0.5 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 225 | 182.25 | 55 | 110.6 | NO | 2 | 208/3 | 2.4 | 39.4 | 50 |  | 7.5 | 208/3 | HIGH | 2 | HIGH | NO | DHG0903DH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG0903DH | DHG0903DH
RTU- | DAIKIN | DHG0904DL | 7.5 | 3146 | 0.5 | 0.5 | 90561 | 72417 | 17.5 IEER/12.5 EER | 80 | 67 | 59.1 | 57.9 | 130 | 105.3 | 55 | 85.6 | NO | 2 | 460/3 | 2.4 | 20.1 | 25 |  | 7.5 | 460/3 | HIGH | 2 | LOW | NO | DHG0904DL | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG0904DL | DHG0904DL
RTU- | DAIKIN | DHG0904DM | 7.5 | 3024 | 0.5 | 0.5 | 90091 | 70563 | 17.5 IEER/12.5 EER | 80 | 67 | 58.8 | 57.6 | 180 | 145.8 | 55 | 99.1 | NO | 2 | 460/3 | 2.4 | 20.1 | 25 |  | 7.5 | 460/3 | HIGH | 2 | MEDIUM | NO | DHG0904DM | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG0904DM | DHG0904DM
RTU- | DAIKIN | DHG0904DH | 7.5 | 3000 | 0.5 | 0.5 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 225 | 182.25 | 55 | 110.6 | NO | 2 | 460/3 | 2.4 | 20.1 | 25 |  | 7.5 | 460/3 | HIGH | 2 | HIGH | NO | DHG0904DH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG0904DH | DHG0904DH
RTU- | DAIKIN | DSG1023DL | 8.5 | 3459 | 0.5 | 0.5 | 98063 | 75041 | 15.5 IEER/11.4 EER | 80 | 67 | 60.3 | 58.1 | 130 | 105.3 | 55 | 82.8 | NO | 2 | 208/3 | 2.4 | 43.7 | 50 |  | 8.5 | 208/3 | STANDARD | 2 | LOW | NO | DSG1023DL | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1023DL | DSG1023DL
RTU- | DAIKIN | DSG1023DM | 8.5 | 3440 | 0.5 | 0.5 | 97985 | 74802 | 15.5 IEER/11.4 EER | 80 | 67 | 60.2 | 58 | 180 | 145.8 | 55 | 93.8 | NO | 2 | 208/3 | 2.4 | 43.7 | 50 |  | 8.5 | 208/3 | STANDARD | 2 | MEDIUM | NO | DSG1023DM | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1023DM | DSG1023DM
RTU- | DAIKIN | DSG1023DH | 8.5 | 3444 | 0.5 | 0.5 | 98001 | 74853 | 15.5 IEER/11.4 EER | 80 | 67 | 60.2 | 58 | 225 | 182.25 | 55 | 103.4 | NO | 2 | 208/3 | 2.4 | 43.7 | 50 |  | 8.5 | 208/3 | STANDARD | 2 | HIGH | NO | DSG1023DH | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1023DH | DSG1023DH
RTU- | DAIKIN | DSG1024DL | 8.5 | 3459 | 0.5 | 0.5 | 98063 | 75041 | 15.5 IEER/11.4 EER | 80 | 67 | 60.3 | 58.1 | 130 | 105.3 | 55 | 82.8 | NO | 2 | 460/3 | 2.4 | 21.5 | 25 |  | 8.5 | 460/3 | STANDARD | 2 | LOW | NO | DSG1024DL | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1024DL | DSG1024DL
RTU- | DAIKIN | DSG1024DM | 8.5 | 3440 | 0.5 | 0.5 | 97985 | 74802 | 15.5 IEER/11.4 EER | 80 | 67 | 60.2 | 58 | 180 | 145.8 | 55 | 93.8 | NO | 2 | 460/3 | 2.4 | 21.5 | 25 |  | 8.5 | 460/3 | STANDARD | 2 | MEDIUM | NO | DSG1024DM | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1024DM | DSG1024DM
RTU- | DAIKIN | DSG1024DH | 8.5 | 3444 | 0.5 | 0.5 | 98001 | 74853 | 15.5 IEER/11.4 EER | 80 | 67 | 60.2 | 58 | 225 | 182.25 | 55 | 103.4 | NO | 2 | 460/3 | 2.4 | 21.5 | 25 |  | 8.5 | 460/3 | STANDARD | 2 | HIGH | NO | DSG1024DH | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1024DH | DSG1024DH
RTU- | DAIKIN | DHG1023DL | 8.5 | 3632 | 0.5 | 0.5 | 104616 | 80554 | 17.5 IEER/12.5 EER | 80 | 67 | 59.8 | 57.9 | 130 | 105.3 | 55 | 81.5 | NO | 2 | 208/3 | 2.4 | 43.7 | 50 |  | 8.5 | 208/3 | HIGH | 2 | LOW | NO | DHG1023DL | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1023DL | DHG1023DL
RTU- | DAIKIN | DHG1023DM | 8.5 | 3632 | 0.5 | 0.5 | 104616 | 80554 | 17.5 IEER/12.5 EER | 80 | 67 | 59.8 | 57.9 | 180 | 145.8 | 55 | 91.7 | NO | 2 | 208/3 | 2.4 | 43.7 | 50 |  | 8.5 | 208/3 | HIGH | 2 | MEDIUM | NO | DHG1023DM | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1023DM | DHG1023DM
RTU- | DAIKIN | DHG1023DH | 8.5 | 3632 | 0.5 | 0.5 | 104616 | 80554 | 17.5 IEER/12.5 EER | 80 | 67 | 59.8 | 57.9 | 225 | 182.25 | 55 | 100.9 | NO | 2 | 208/3 | 2.4 | 43.7 | 50 |  | 8.5 | 208/3 | HIGH | 2 | HIGH | NO | DHG1023DH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1023DH | DHG1023DH
RTU- | DAIKIN | DHG1024DL | 8.5 | 3632 | 0.5 | 0.5 | 104616 | 80554 | 17.5 IEER/12.5 EER | 80 | 67 | 59.8 | 57.9 | 130 | 105.3 | 55 | 81.5 | NO | 2 | 460/3 | 2.4 | 21.5 | 25 |  | 8.5 | 460/3 | HIGH | 2 | LOW | NO | DHG1024DL | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1024DL | DHG1024DL
RTU- | DAIKIN | DHG1024DM | 8.5 | 3632 | 0.5 | 0.5 | 104616 | 80554 | 17.5 IEER/12.5 EER | 80 | 67 | 59.8 | 57.9 | 180 | 145.8 | 55 | 91.7 | NO | 2 | 460/3 | 2.4 | 21.5 | 25 |  | 8.5 | 460/3 | HIGH | 2 | MEDIUM | NO | DHG1024DM | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1024DM | DHG1024DM
RTU- | DAIKIN | DHG1024DH | 8.5 | 3632 | 0.5 | 0.5 | 104616 | 80554 | 17.5 IEER/12.5 EER | 80 | 67 | 59.8 | 57.9 | 225 | 182.25 | 55 | 100.9 | NO | 2 | 460/3 | 2.4 | 21.5 | 25 |  | 8.5 | 460/3 | HIGH | 2 | HIGH | NO | DHG1024DH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1024DH | DHG1024DH
RTU- | DAIKIN | DSG1203DL | 10 | 4060 | 0.5 | 0.5 | 119122 | 92915 | 15.2 IEER/11.4 EER | 80 | 67 | 59.2 | 57.7 | 130 | 105.3 | 55 | 78.7 | NO | 2 | 208/3 | 3.5 | 53.8 | 70 |  | 10 | 208/3 | STANDARD | 2 | LOW | NO | DSG1203DL | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1203DL | DSG1203DL
RTU- | DAIKIN | DSG1203DM | 10 | 4052 | 0.5 | 0.5 | 119122 | 92915 | 15.2 IEER/11.4 EER | 80 | 67 | 59.1 | 57.7 | 180 | 145.8 | 55 | 87.9 | NO | 2 | 208/3 | 3.5 | 53.8 | 70 |  | 10 | 208/3 | STANDARD | 2 | MEDIUM | NO | DSG1203DM | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1203DM | DSG1203DM
RTU- | DAIKIN | DSG1203DH | 10 | 4051 | 0.5 | 0.5 | 119122 | 92915 | 15.2 IEER/11.4 EER | 80 | 67 | 59.1 | 57.7 | 240 | 194.4 | 55 | 98.9 | NO | 2 | 208/3 | 3.5 | 53.8 | 70 |  | 10 | 208/3 | STANDARD | 2 | HIGH | NO | DSG1203DH | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1203DH | DSG1203DH
RTU- | DAIKIN | DSG1204DL | 10 | 4060 | 0.5 | 0.5 | 119122 | 92915 | 14.8 IEER/11.2 EER | 80 | 67 | 59.2 | 57.7 | 130 | 105.3 | 55 | 78.7 | NO | 2 | 460/3 | 3.5 | 26.2 | 30 |  | 10 | 460/3 | STANDARD | 2 | LOW | NO | DSG1204DL | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1204DL | DSG1204DL
RTU- | DAIKIN | DSG1204DM | 10 | 4052 | 0.5 | 0.5 | 119122 | 92915 | 14.8 IEER/11.2 EER | 80 | 67 | 59.1 | 57.7 | 180 | 145.8 | 55 | 87.9 | NO | 2 | 460/3 | 3.5 | 26.2 | 30 |  | 10 | 460/3 | STANDARD | 2 | MEDIUM | NO | DSG1204DM | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1204DM | DSG1204DM
RTU- | DAIKIN | DSG1204DH | 10 | 4051 | 0.5 | 0.5 | 119122 | 92915 | 14.8 IEER/11.2 EER | 80 | 67 | 59.1 | 57.7 | 240 | 194.4 | 55 | 98.9 | NO | 2 | 460/3 | 3.5 | 26.2 | 30 |  | 10 | 460/3 | STANDARD | 2 | HIGH | NO | DSG1204DH | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1204DH | DSG1204DH
RTU- | DAIKIN | DHG1203DL | 10 | 3955 | 0.5 | 0.5 | 118027 | 82891 | 17 IEER/12.5 EER | 80 | 67 | 60.9 | 57.6 | 130 | 105.3 | 55 | 79.3 | NO | 2 | 208/3 | 2.4 | 46.6 | 60 |  | 10 | 208/3 | HIGH | 2 | LOW | NO | DHG1203DL | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1203DL | DHG1203DL
RTU- | DAIKIN | DHG1203DM | 10 | 4018 | 0.5 | 0.5 | 118308 | 83767 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 180 | 145.8 | 55 | 88.2 | NO | 2 | 208/3 | 2.4 | 46.6 | 60 |  | 10 | 208/3 | HIGH | 2 | MEDIUM | NO | DHG1203DM | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1203DM | DHG1203DM
RTU- | DAIKIN | DHG1203DH | 10 | 4018 | 0.5 | 0.5 | 118308 | 83767 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 240 | 194.4 | 55 | 99.2 | NO | 2 | 208/3 | 2.4 | 46.6 | 60 |  | 10 | 208/3 | HIGH | 2 | HIGH | NO | DHG1203DH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1203DH | DHG1203DH
RTU- | DAIKIN | DHG1204DL | 10 | 3955 | 0.5 | 0.5 | 118027 | 82891 | 17 IEER/12.5 EER | 80 | 67 | 60.9 | 57.6 | 130 | 105.3 | 55 | 79.3 | NO | 2 | 460/3 | 2.4 | 24.4 | 30 |  | 10 | 460/3 | HIGH | 2 | LOW | NO | DHG1204DL | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1204DL | DHG1204DL
RTU- | DAIKIN | DHG1204DM | 10 | 4018 | 0.5 | 0.5 | 118308 | 83767 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 180 | 145.8 | 55 | 88.2 | NO | 2 | 460/3 | 2.4 | 24.4 | 30 |  | 10 | 460/3 | HIGH | 2 | MEDIUM | NO | DHG1204DM | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1204DM | DHG1204DM
RTU- | DAIKIN | DHG1204DH | 10 | 4018 | 0.5 | 0.5 | 118308 | 83767 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 240 | 194.4 | 55 | 99.2 | NO | 2 | 460/3 | 2.4 | 24.4 | 30 |  | 10 | 460/3 | HIGH | 2 | HIGH | NO | DHG1204DH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1204DH | DHG1204DH
RTU- | DAIKIN | DSG1503DL | 12.5 | 4549 | 0.5 | 0.5 | 141535 | 104491 | 15.2 IEER/11.4 EER | 80 | 67 | 59.1 | 57.1 | 130 | 105.3 | 55 | 76.2 | NO | 2 | 208/3 | 3.5 | 59.5 | 70 |  | 12.5 | 208/3 | STANDARD | 2 | LOW | NO | DSG1503DL | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1503DL | DSG1503DL
RTU- | DAIKIN | DSG1503DM | 12.5 | 4350 | 0.5 | 0.5 | 140660 | 101588 | 15.2 IEER/11.4 EER | 80 | 67 | 58.7 | 56.7 | 180 | 145.8 | 55 | 85.7 | NO | 2 | 208/3 | 3.5 | 59.5 | 70 |  | 12.5 | 208/3 | STANDARD | 2 | MEDIUM | NO | DSG1503DM | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1503DM | DSG1503DM
RTU- | DAIKIN | DSG1503DH | 12.5 | 4213 | 0.5 | 0.5 | 140057 | 99589 | 15.2 IEER/11.4 EER | 80 | 67 | 58.5 | 56.4 | 240 | 194.4 | 55 | 97.2 | NO | 2 | 208/3 | 3.5 | 59.5 | 70 |  | 12.5 | 208/3 | STANDARD | 2 | HIGH | NO | DSG1503DH | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1503DH | DSG1503DH
RTU- | DAIKIN | DSG1504DL | 12.5 | 4549 | 0.5 | 0.5 | 141535 | 104491 | 15.2 IEER/11.4 EER | 80 | 67 | 59.1 | 57.1 | 130 | 105.3 | 55 | 76.2 | NO | 2 | 460/3 | 3.5 | 30.2 | 35 |  | 12.5 | 460/3 | STANDARD | 2 | LOW | NO | DSG1504DL | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1504DL | DSG1504DL
RTU- | DAIKIN | DSG1504DM | 12.5 | 4350 | 0.5 | 0.5 | 140660 | 101588 | 15.2 IEER/11.4 EER | 80 | 67 | 58.7 | 56.7 | 180 | 145.8 | 55 | 85.7 | NO | 2 | 460/3 | 3.5 | 30.2 | 35 |  | 12.5 | 460/3 | STANDARD | 2 | MEDIUM | NO | DSG1504DM | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1504DM | DSG1504DM
RTU- | DAIKIN | DSG1504DH | 12.5 | 4213 | 0.5 | 0.5 | 140057 | 99589 | 15.2 IEER/11.4 EER | 80 | 67 | 58.5 | 56.4 | 240 | 194.4 | 55 | 97.2 | NO | 2 | 460/3 | 3.5 | 30.2 | 35 |  | 12.5 | 460/3 | STANDARD | 2 | HIGH | NO | DSG1504DH | ENGINEERING MANUAL - DSG (7.5-12.5) | INSTALLATION MANUAL - DSG (7.5-12.5) | DSG1504DH | DSG1504DH
RTU- | DAIKIN | DHG1503DL | 12.5 | 4522 | 0.5 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.1 | 57.1 | 130 | 105.3 | 55 | 76.3 | NO | 2 | 208/3 | 3.5 | 61.1 | 80 |  | 12.5 | 208/3 | HIGH | 2 | LOW | NO | DHG1503DL | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1503DL | DHG1503DL
RTU- | DAIKIN | DHG1503DM | 12.5 | 4522 | 0.5 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.1 | 57.1 | 180 | 145.8 | 55 | 84.5 | NO | 2 | 208/3 | 3.5 | 61.1 | 80 |  | 12.5 | 208/3 | HIGH | 2 | MEDIUM | NO | DHG1503DM | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1503DM | DHG1503DM
RTU- | DAIKIN | DHG1503DH | 12.5 | 4522 | 0.5 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.1 | 57.1 | 240 | 194.4 | 55 | 94.3 | NO | 2 | 208/3 | 3.5 | 61.1 | 80 |  | 12.5 | 208/3 | HIGH | 2 | HIGH | NO | DHG1503DH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1503DH | DHG1503DH
RTU- | DAIKIN | DHG1504DL | 12.5 | 4522 | 0.5 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.1 | 57.1 | 130 | 105.3 | 55 | 76.3 | NO | 2 | 460/3 | 3.5 | 30.6 | 35 |  | 12.5 | 460/3 | HIGH | 2 | LOW | NO | DHG1504DL | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1504DL | DHG1504DL
RTU- | DAIKIN | DHG1504DM | 12.5 | 4522 | 0.5 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.1 | 57.1 | 180 | 145.8 | 55 | 84.5 | NO | 2 | 460/3 | 3.5 | 30.6 | 35 |  | 12.5 | 460/3 | HIGH | 2 | MEDIUM | NO | DHG1504DM | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1504DM | DHG1504DM
RTU- | DAIKIN | DHG1504DH | 12.5 | 4522 | 0.5 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.1 | 57.1 | 240 | 194.4 | 55 | 94.3 | NO | 2 | 460/3 | 3.5 | 30.6 | 35 |  | 12.5 | 460/3 | HIGH | 2 | HIGH | NO | DHG1504DH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1504DH | DHG1504DH
RTU- | DAIKIN | DSG1803DL | 15 | 6338 | 0.5 | 0.67 | 176600 | 143046 | 14 IEER/10.8 EER | 80 | 67 | 59.5 | 58.3 | 260 | 210.6 | 55 | 85.4 | NO | 2 | 208/3 | 3.5 | 84.1 | 100 |  | 15 | 208/3 | STANDARD | 2 | LOW | NO | DSG1803DL | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG1803DL | DSG1803DL
RTU- | DAIKIN | DSG1803DM | 15 | 6328 | 0.5 | 0.67 | 176600 | 143046 | 14 IEER/10.8 EER | 80 | 67 | 59.5 | 58.2 | 360 | 291.6 | 55 | 97.1 | NO | 2 | 208/3 | 3.5 | 84.1 | 100 |  | 15 | 208/3 | STANDARD | 2 | MEDIUM | NO | DSG1803DM | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG1803DM | DSG1803DM
RTU- | DAIKIN | DSG1803DH | 15 | 6344 | 0.5 | 0.67 | 176600 | 143046 | 14 IEER/10.8 EER | 80 | 67 | 59.5 | 58.3 | 400 | 324 | 55 | 101.7 | NO | 2 | 208/3 | 3.5 | 84.1 | 100 |  | 15 | 208/3 | STANDARD | 2 | HIGH | NO | DSG1803DH | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG1803DH | DSG1803DH
RTU- | DAIKIN | DSG1804DL | 15 | 6338 | 0.5 | 0.67 | 176600 | 143046 | 14 IEER/10.8 EER | 80 | 67 | 59.5 | 58.3 | 260 | 210.6 | 55 | 85.4 | NO | 2 | 460/3 | 3.5 | 41.4 | 50 |  | 15 | 460/3 | STANDARD | 2 | LOW | NO | DSG1804DL | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG1804DL | DSG1804DL
RTU- | DAIKIN | DSG1804DM | 15 | 6328 | 0.5 | 0.67 | 176600 | 143046 | 14 IEER/10.8 EER | 80 | 67 | 59.5 | 58.2 | 360 | 291.6 | 55 | 97.1 | NO | 2 | 460/3 | 3.5 | 41.4 | 50 |  | 15 | 460/3 | STANDARD | 2 | MEDIUM | NO | DSG1804DM | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG1804DM | DSG1804DM
RTU- | DAIKIN | DSG1804DH | 15 | 6344 | 0.5 | 0.67 | 176600 | 143046 | 14 IEER/10.8 EER | 80 | 67 | 59.5 | 58.3 | 400 | 324 | 55 | 101.7 | NO | 2 | 460/3 | 3.5 | 41.4 | 50 |  | 15 | 460/3 | STANDARD | 2 | HIGH | NO | DSG1804DH | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG1804DH | DSG1804DH
RTU- | DAIKIN | DSG2403DL | 20 | 8177 | 0.5 | 0.77 | 238125 | 185737 | 14 IEER/10.8 EER | 80 | 67 | 59.3 | 57.8 | 260 | 210.6 | 55 | 78.6 | NO | 2 | 208/3 | 3.5 | 98.7 | 125 |  | 20 | 208/3 | STANDARD | 2 | LOW | NO | DSG2403DL | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG2403DL | DSG2403DL
RTU- | DAIKIN | DSG2403DM | 20 | 8272 | 0.5 | 0.77 | 238125 | 185737 | 14 IEER/10.8 EER | 80 | 67 | 59.6 | 57.9 | 360 | 291.6 | 55 | 87.2 | NO | 2 | 208/3 | 3.5 | 98.7 | 125 |  | 20 | 208/3 | STANDARD | 2 | MEDIUM | NO | DSG2403DM | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG2403DM | DSG2403DM
RTU- | DAIKIN | DSG2403DH | 20 | 8035 | 0.5 | 0.77 | 238125 | 185737 | 14 IEER/10.8 EER | 80 | 67 | 59 | 57.6 | 400 | 324 | 55 | 91.9 | NO | 2 | 208/3 | 3.5 | 98.7 | 125 |  | 20 | 208/3 | STANDARD | 2 | HIGH | NO | DSG2403DH | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG2403DH | DSG2403DH
RTU- | DAIKIN | DSG2404DL | 20 | 8177 | 0.5 | 0.77 | 238125 | 185737 | 14 IEER/10.8 EER | 80 | 67 | 59.3 | 57.8 | 260 | 210.6 | 55 | 78.6 | NO | 2 | 460/3 | 3.5 | 50.8 | 60 |  | 20 | 460/3 | STANDARD | 2 | LOW | NO | DSG2404DL | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG2404DL | DSG2404DL
RTU- | DAIKIN | DSG2404DM | 20 | 8272 | 0.5 | 0.77 | 238125 | 185737 | 14 IEER/10.8 EER | 80 | 67 | 59.6 | 57.9 | 360 | 291.6 | 55 | 87.2 | NO | 2 | 460/3 | 3.5 | 50.8 | 60 |  | 20 | 460/3 | STANDARD | 2 | MEDIUM | NO | DSG2404DM | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG2404DM | DSG2404DM
RTU- | DAIKIN | DSG2404DH | 20 | 8035 | 0.5 | 0.77 | 238125 | 185737 | 14 IEER/10.8 EER | 80 | 67 | 59 | 57.6 | 400 | 324 | 55 | 91.9 | NO | 2 | 460/3 | 3.5 | 50.8 | 60 |  | 20 | 460/3 | STANDARD | 2 | HIGH | NO | DSG2404DH | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG2404DH | DSG2404DH
RTU- | DAIKIN | DSG3003DL | 25 | 10056 | 0.5 | 0.93 | 303155 | 227366 | 13 IEER/9.8 EER | 80 | 67 | 59.4 | 57.5 | 260 | 210.6 | 55 | 74.2 | NO | 2 | 208/3 | 5 | 151 | 175 |  | 25 | 208/3 | STANDARD | 2 | LOW | NO | DSG3003DL | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG3003DL | DSG3003DL
RTU- | DAIKIN | DSG3003DM | 25 | 10056 | 0.5 | 0.93 | 303155 | 227366 | 13 IEER/9.8 EER | 80 | 67 | 59.4 | 57.5 | 360 | 291.6 | 55 | 81.5 | NO | 2 | 208/3 | 5 | 151 | 175 |  | 25 | 208/3 | STANDARD | 2 | MEDIUM | NO | DSG3003DM | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG3003DM | DSG3003DM
RTU- | DAIKIN | DSG3003DH | 25 | 10056 | 0.5 | 0.93 | 303155 | 227366 | 13 IEER/9.8 EER | 80 | 67 | 59.4 | 57.5 | 400 | 324 | 55 | 84.5 | NO | 2 | 208/3 | 5 | 151 | 175 |  | 25 | 208/3 | STANDARD | 2 | HIGH | NO | DSG3003DH | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG3003DH | DSG3003DH
RTU- | DAIKIN | DSG3004DL | 25 | 10056 | 0.5 | 0.93 | 303155 | 227366 | 13 IEER/9.8 EER | 80 | 67 | 59.4 | 57.5 | 260 | 210.6 | 55 | 74.2 | NO | 2 | 460/3 | 5 | 74.3 | 90 |  | 25 | 460/3 | STANDARD | 2 | LOW | NO | DSG3004DL | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG3004DL | DSG3004DL
RTU- | DAIKIN | DSG3004DM | 25 | 10056 | 0.5 | 0.93 | 303155 | 227366 | 13 IEER/9.8 EER | 80 | 67 | 59.4 | 57.5 | 360 | 291.6 | 55 | 81.5 | NO | 2 | 460/3 | 5 | 74.3 | 90 |  | 25 | 460/3 | STANDARD | 2 | MEDIUM | NO | DSG3004DM | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG3004DM | DSG3004DM
RTU- | DAIKIN | DSG3004DH | 25 | 10056 | 0.5 | 0.93 | 303155 | 227366 | 13 IEER/9.8 EER | 80 | 67 | 59.4 | 57.5 | 400 | 324 | 55 | 84.5 | NO | 2 | 460/3 | 5 | 74.3 | 90 |  | 25 | 460/3 | STANDARD | 2 | HIGH | NO | DSG3004DH | ENGINEERING MANUAL - DSG (15-25) | INSTALLATION MANUAL - DSG (15-25) | DSG3004DH | DSG3004DH
RTU- | DAIKIN | DHG0363DL | 3 | 1200 | 0.5 | 0.59 | 35176 | 27866 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 58.9 | 57.8 | 45 | 36.45 | 55 | 82.8 | YES | 2 | 208/3 | 0.75 | 18.1 | 25 |  | 3 | 208/3 | HIGH | 2 | LOW | YES | DHG0363DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0363DL | DHG0363DL
RTU- | DAIKIN | DHG0363DM | 3 | 1200 | 0.5 | 0.59 | 35176 | 27866 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 58.9 | 57.8 | 70 | 56.7 | 55 | 98.2 | YES | 2 | 208/3 | 0.75 | 18.1 | 25 |  | 3 | 208/3 | HIGH | 2 | MEDIUM | YES | DHG0363DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0363DM | DHG0363DM
RTU- | DAIKIN | DHG0363DH | 3 | 1200 | 0.5 | 0.59 | 35176 | 27866 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 58.9 | 57.8 | 115 | 93.15 | 55 | 126 | YES | 2 | 208/3 | 0.75 | 18.1 | 25 |  | 3 | 208/3 | HIGH | 2 | HIGH | YES | DHG0363DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0363DH | DHG0363DH
RTU- | DAIKIN | DHG0364DL | 3 | 1200 | 0.5 | 0.59 | 35176 | 27866 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 58.9 | 57.8 | 45 | 36.45 | 55 | 82.8 | YES | 2 | 460/3 | 1.2 | 8.2 | 15 |  | 3 | 460/3 | HIGH | 2 | LOW | YES | DHG0364DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0364DL | DHG0364DL
RTU- | DAIKIN | DHG0364DM | 3 | 1200 | 0.5 | 0.59 | 35176 | 27866 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 58.9 | 57.8 | 70 | 56.7 | 55 | 98.2 | YES | 2 | 460/3 | 1.2 | 8.2 | 15 |  | 3 | 460/3 | HIGH | 2 | MEDIUM | YES | DHG0364DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0364DM | DHG0364DM
RTU- | DAIKIN | DHG0364DH | 3 | 1200 | 0.5 | 0.59 | 35176 | 27866 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 58.9 | 57.8 | 115 | 93.15 | 55 | 126 | YES | 2 | 460/3 | 1.2 | 8.2 | 15 |  | 3 | 460/3 | HIGH | 2 | HIGH | YES | DHG0364DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0364DH | DHG0364DH
RTU- | DAIKIN | DHG0483DL | 4 | 1600 | 0.5 | 0.61 | 46683 | 36866 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.1 | 57.8 | 70 | 56.7 | 55 | 87.4 | YES | 2 | 208/3 | 1 | 22.8 | 30 |  | 4 | 208/3 | HIGH | 2 | LOW | YES | DHG0483DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0483DL | DHG0483DL
RTU- | DAIKIN | DHG0483DM | 4 | 1600 | 0.5 | 0.61 | 46683 | 36866 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.1 | 57.8 | 115 | 93.15 | 55 | 108.2 | YES | 2 | 208/3 | 1 | 22.8 | 30 |  | 4 | 208/3 | HIGH | 2 | MEDIUM | YES | DHG0483DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0483DM | DHG0483DM
RTU- | DAIKIN | DHG0483DH | 4 | 1600 | 0.5 | 0.61 | 46683 | 36866 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.1 | 57.8 | 140 | 113.4 | 55 | 119.8 | YES | 2 | 208/3 | 1 | 22.8 | 30 |  | 4 | 208/3 | HIGH | 2 | HIGH | YES | DHG0483DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0483DH | DHG0483DH
RTU- | DAIKIN | DHG0484DL | 4 | 1600 | 0.5 | 0.61 | 46683 | 36866 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.1 | 57.8 | 70 | 56.7 | 55 | 87.4 | YES | 2 | 460/3 | 1.2 | 10.7 | 15 |  | 4 | 460/3 | HIGH | 2 | LOW | YES | DHG0484DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0484DL | DHG0484DL
RTU- | DAIKIN | DHG0484DM | 4 | 1600 | 0.5 | 0.61 | 46683 | 36866 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.1 | 57.8 | 115 | 93.15 | 55 | 108.2 | YES | 2 | 460/3 | 1.2 | 10.7 | 15 |  | 4 | 460/3 | HIGH | 2 | MEDIUM | YES | DHG0484DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0484DM | DHG0484DM
RTU- | DAIKIN | DHG0484DH | 4 | 1600 | 0.5 | 0.61 | 46683 | 36866 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.1 | 57.8 | 140 | 113.4 | 55 | 119.8 | YES | 2 | 460/3 | 1.2 | 10.7 | 15 |  | 4 | 460/3 | HIGH | 2 | HIGH | YES | DHG0484DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0484DH | DHG0484DH
RTU- | DAIKIN | DHG0603DL | 5 | 2100 | 0.5 | 0.64 | 60037 | 46024 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 60.1 | 58 | 70 | 56.7 | 55 | 79.7 | YES | 2 | 208/3 | 1 | 28.5 | 40 |  | 5 | 208/3 | HIGH | 2 | LOW | YES | DHG0603DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0603DL | DHG0603DL
RTU- | DAIKIN | DHG0603DM | 5 | 2100 | 0.5 | 0.64 | 60037 | 46024 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 60.1 | 58 | 115 | 93.15 | 55 | 95.6 | YES | 2 | 208/3 | 1 | 28.5 | 40 |  | 5 | 208/3 | HIGH | 2 | MEDIUM | YES | DHG0603DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0603DM | DHG0603DM
RTU- | DAIKIN | DHG0603DH | 5 | 2100 | 0.5 | 0.64 | 60037 | 46024 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 60.1 | 58 | 140 | 113.4 | 55 | 104.4 | YES | 2 | 208/3 | 1 | 28.5 | 40 |  | 5 | 208/3 | HIGH | 2 | HIGH | YES | DHG0603DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0603DH | DHG0603DH
RTU- | DAIKIN | DHG0604DL | 5 | 2100 | 0.5 | 0.64 | 60037 | 46024 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 60.1 | 58 | 70 | 56.7 | 55 | 79.7 | YES | 2 | 460/3 | 1.2 | 13.3 | 20 |  | 5 | 460/3 | HIGH | 2 | LOW | YES | DHG0604DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0604DL | DHG0604DL
RTU- | DAIKIN | DHG0604DM | 5 | 2100 | 0.5 | 0.64 | 60037 | 46024 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 60.1 | 58 | 115 | 93.15 | 55 | 95.6 | YES | 2 | 460/3 | 1.2 | 13.3 | 20 |  | 5 | 460/3 | HIGH | 2 | MEDIUM | YES | DHG0604DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0604DM | DHG0604DM
RTU- | DAIKIN | DHG0604DH | 5 | 2100 | 0.5 | 0.64 | 60037 | 46024 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 60.1 | 58 | 140 | 113.4 | 55 | 104.4 | YES | 2 | 460/3 | 1.2 | 13.3 | 20 |  | 5 | 460/3 | HIGH | 2 | HIGH | YES | DHG0604DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0604DH | DHG0604DH
RTU- | DAIKIN | DHG0723DL | 6 | 2200 | 0.5 | 0.61 | 69253 | 52414 | 18.6 IEER/12.5 EER | 80 | 67 | 58.3 | 57 | 70 | 56.7 | 55 | 78.6 | YES | 2 | 208/3 | 1.2 | 27.2 | 40 |  | 6 | 208/3 | HIGH | 2 | LOW | YES | DHG0723DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0723DL | DHG0723DL
RTU- | DAIKIN | DHG0723DM | 6 | 2200 | 0.5 | 0.61 | 69253 | 52414 | 18.6 IEER/12.5 EER | 80 | 67 | 58.3 | 57 | 125 | 101.25 | 55 | 97.1 | YES | 2 | 208/3 | 1.2 | 27.2 | 40 |  | 6 | 208/3 | HIGH | 2 | MEDIUM | YES | DHG0723DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0723DM | DHG0723DM
RTU- | DAIKIN | DHG0723DH | 6 | 2200 | 0.5 | 0.61 | 69253 | 52414 | 18.6 IEER/12.5 EER | 80 | 67 | 58.3 | 57 | 150 | 121.5 | 55 | 105.5 | YES | 2 | 208/3 | 1.2 | 27.2 | 40 |  | 6 | 208/3 | HIGH | 2 | HIGH | YES | DHG0723DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0723DH | DHG0723DH
RTU- | DAIKIN | DHG0724DL | 6 | 2200 | 0.5 | 0.61 | 69253 | 52414 | 18.6 IEER/12.5 EER | 80 | 67 | 58.3 | 57 | 70 | 56.7 | 55 | 78.6 | YES | 2 | 460/3 | 1.2 | 12.2 | 15 |  | 6 | 460/3 | HIGH | 2 | LOW | YES | DHG0724DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0724DL | DHG0724DL
RTU- | DAIKIN | DHG0724DM | 6 | 2200 | 0.5 | 0.61 | 69253 | 52414 | 18.6 IEER/12.5 EER | 80 | 67 | 58.3 | 57 | 125 | 101.25 | 55 | 97.1 | YES | 2 | 460/3 | 1.2 | 12.2 | 15 |  | 6 | 460/3 | HIGH | 2 | MEDIUM | YES | DHG0724DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0724DM | DHG0724DM
RTU- | DAIKIN | DHG0724DH | 6 | 2200 | 0.5 | 0.61 | 69253 | 52414 | 18.6 IEER/12.5 EER | 80 | 67 | 58.3 | 57 | 150 | 121.5 | 55 | 105.5 | YES | 2 | 460/3 | 1.2 | 12.2 | 15 |  | 6 | 460/3 | HIGH | 2 | HIGH | YES | DHG0724DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | INSTALLATION MANUAL - DHG (3-6) | DHG0724DH | DHG0724DH
RTU- | DAIKIN | DHG0903DL | 7.5 | 3000 | 0.5 | 0.67 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 130 | 105.3 | 55 | 87.1 | YES | 2 | 208/3 | 2.4 | 39.4 | 50 |  | 7.5 | 208/3 | HIGH | 2 | LOW | YES | DHG0903DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG0903DL | DHG0903DL
RTU- | DAIKIN | DHG0903DM | 7.5 | 3000 | 0.5 | 0.67 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 180 | 145.8 | 55 | 99.4 | YES | 2 | 208/3 | 2.4 | 39.4 | 50 |  | 7.5 | 208/3 | HIGH | 2 | MEDIUM | YES | DHG0903DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG0903DM | DHG0903DM
RTU- | DAIKIN | DHG0903DH | 7.5 | 3000 | 0.5 | 0.67 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 225 | 182.25 | 55 | 110.6 | YES | 2 | 208/3 | 2.4 | 39.4 | 50 |  | 7.5 | 208/3 | HIGH | 2 | HIGH | YES | DHG0903DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG0903DH | DHG0903DH
RTU- | DAIKIN | DHG0904DL | 7.5 | 3000 | 0.5 | 0.67 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 130 | 105.3 | 55 | 87.1 | YES | 2 | 460/3 | 2.4 | 20.1 | 25 |  | 7.5 | 460/3 | HIGH | 2 | LOW | YES | DHG0904DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG0904DL | DHG0904DL
RTU- | DAIKIN | DHG0904DM | 7.5 | 3000 | 0.5 | 0.67 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 180 | 145.8 | 55 | 99.4 | YES | 2 | 460/3 | 2.4 | 20.1 | 25 |  | 7.5 | 460/3 | HIGH | 2 | MEDIUM | YES | DHG0904DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG0904DM | DHG0904DM
RTU- | DAIKIN | DHG0904DH | 7.5 | 3000 | 0.5 | 0.67 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 225 | 182.25 | 55 | 110.6 | YES | 2 | 460/3 | 2.4 | 20.1 | 25 |  | 7.5 | 460/3 | HIGH | 2 | HIGH | YES | DHG0904DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG0904DH | DHG0904DH
RTU- | DAIKIN | DHG1023DL | 8.5 | 3400 | 0.5 | 0.66 | 103705 | 77724 | 17.5 IEER/12.5 EER | 80 | 67 | 59.2 | 57.3 | 130 | 105.3 | 55 | 83.3 | YES | 2 | 208/3 | 2.4 | 43.7 | 50 |  | 8.5 | 208/3 | HIGH | 2 | LOW | YES | DHG1023DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1023DL | DHG1023DL
RTU- | DAIKIN | DHG1023DM | 8.5 | 3400 | 0.5 | 0.66 | 103705 | 77724 | 17.5 IEER/12.5 EER | 80 | 67 | 59.2 | 57.3 | 180 | 145.8 | 55 | 94.2 | YES | 2 | 208/3 | 2.4 | 43.7 | 50 |  | 8.5 | 208/3 | HIGH | 2 | MEDIUM | YES | DHG1023DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1023DM | DHG1023DM
RTU- | DAIKIN | DHG1023DH | 8.5 | 3400 | 0.5 | 0.66 | 103705 | 77724 | 17.5 IEER/12.5 EER | 80 | 67 | 59.2 | 57.3 | 225 | 182.25 | 55 | 104 | YES | 2 | 208/3 | 2.4 | 43.7 | 50 |  | 8.5 | 208/3 | HIGH | 2 | HIGH | YES | DHG1023DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1023DH | DHG1023DH
RTU- | DAIKIN | DHG1024DL | 8.5 | 3400 | 0.5 | 0.66 | 103705 | 77724 | 17.5 IEER/12.5 EER | 80 | 67 | 59.2 | 57.3 | 130 | 105.3 | 55 | 83.3 | YES | 2 | 460/3 | 2.4 | 21.5 | 25 |  | 8.5 | 460/3 | HIGH | 2 | LOW | YES | DHG1024DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1024DL | DHG1024DL
RTU- | DAIKIN | DHG1024DM | 8.5 | 3400 | 0.5 | 0.66 | 103705 | 77724 | 17.5 IEER/12.5 EER | 80 | 67 | 59.2 | 57.3 | 180 | 145.8 | 55 | 94.2 | YES | 2 | 460/3 | 2.4 | 21.5 | 25 |  | 8.5 | 460/3 | HIGH | 2 | MEDIUM | YES | DHG1024DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1024DM | DHG1024DM
RTU- | DAIKIN | DHG1024DH | 8.5 | 3400 | 0.5 | 0.66 | 103705 | 77724 | 17.5 IEER/12.5 EER | 80 | 67 | 59.2 | 57.3 | 225 | 182.25 | 55 | 104 | YES | 2 | 460/3 | 2.4 | 21.5 | 25 |  | 8.5 | 460/3 | HIGH | 2 | HIGH | YES | DHG1024DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1024DH | DHG1024DH
RTU- | DAIKIN | DHG1203DL | 10 | 4000 | 0.5 | 0.65 | 118228 | 83517 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 130 | 105.3 | 55 | 79.1 | YES | 2 | 208/3 | 2.4 | 46.6 | 60 |  | 10 | 208/3 | HIGH | 2 | LOW | YES | DHG1203DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1203DL | DHG1203DL
RTU- | DAIKIN | DHG1203DM | 10 | 4000 | 0.5 | 0.65 | 118228 | 83517 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 180 | 145.8 | 55 | 88.3 | YES | 2 | 208/3 | 2.4 | 46.6 | 60 |  | 10 | 208/3 | HIGH | 2 | MEDIUM | YES | DHG1203DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1203DM | DHG1203DM
RTU- | DAIKIN | DHG1203DH | 10 | 4000 | 0.5 | 0.65 | 118228 | 83517 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 240 | 194.4 | 55 | 99.4 | YES | 2 | 208/3 | 2.4 | 46.6 | 60 |  | 10 | 208/3 | HIGH | 2 | HIGH | YES | DHG1203DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1203DH | DHG1203DH
RTU- | DAIKIN | DHG1204DL | 10 | 4000 | 0.5 | 0.65 | 118228 | 83517 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 130 | 105.3 | 55 | 79.1 | YES | 2 | 460/3 | 2.4 | 24.4 | 30 |  | 10 | 460/3 | HIGH | 2 | LOW | YES | DHG1204DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1204DL | DHG1204DL
RTU- | DAIKIN | DHG1204DM | 10 | 4000 | 0.5 | 0.65 | 118228 | 83517 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 180 | 145.8 | 55 | 88.3 | YES | 2 | 460/3 | 2.4 | 24.4 | 30 |  | 10 | 460/3 | HIGH | 2 | MEDIUM | YES | DHG1204DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1204DM | DHG1204DM
RTU- | DAIKIN | DHG1204DH | 10 | 4000 | 0.5 | 0.65 | 118228 | 83517 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 240 | 194.4 | 55 | 99.4 | YES | 2 | 460/3 | 2.4 | 24.4 | 30 |  | 10 | 460/3 | HIGH | 2 | HIGH | YES | DHG1204DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1204DH | DHG1204DH
RTU- | DAIKIN | DHG1503DL | 12.5 | 4600 | 0.5 | 0.65 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.5 | 57.3 | 130 | 105.3 | 55 | 75.9 | YES | 2 | 208/3 | 3.5 | 61.1 | 80 |  | 12.5 | 208/3 | HIGH | 2 | LOW | YES | DHG1503DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1503DL | DHG1503DL
RTU- | DAIKIN | DHG1503DM | 12.5 | 4600 | 0.5 | 0.65 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.5 | 57.3 | 180 | 145.8 | 55 | 84 | YES | 2 | 208/3 | 3.5 | 61.1 | 80 |  | 12.5 | 208/3 | HIGH | 2 | MEDIUM | YES | DHG1503DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1503DM | DHG1503DM
RTU- | DAIKIN | DHG1503DH | 12.5 | 4600 | 0.5 | 0.65 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.5 | 57.3 | 240 | 194.4 | 55 | 93.6 | YES | 2 | 208/3 | 3.5 | 61.1 | 80 |  | 12.5 | 208/3 | HIGH | 2 | HIGH | YES | DHG1503DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1503DH | DHG1503DH
RTU- | DAIKIN | DHG1504DL | 12.5 | 4600 | 0.5 | 0.65 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.5 | 57.3 | 130 | 105.3 | 55 | 75.9 | YES | 2 | 460/3 | 3.5 | 30.6 | 35 |  | 12.5 | 460/3 | HIGH | 2 | LOW | YES | DHG1504DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1504DL | DHG1504DL
RTU- | DAIKIN | DHG1504DM | 12.5 | 4600 | 0.5 | 0.65 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.5 | 57.3 | 180 | 145.8 | 55 | 84 | YES | 2 | 460/3 | 3.5 | 30.6 | 35 |  | 12.5 | 460/3 | HIGH | 2 | MEDIUM | YES | DHG1504DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1504DM | DHG1504DM
RTU- | DAIKIN | DHG1504DH | 12.5 | 4600 | 0.5 | 0.65 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.5 | 57.3 | 240 | 194.4 | 55 | 93.6 | YES | 2 | 460/3 | 3.5 | 30.6 | 35 |  | 12.5 | 460/3 | HIGH | 2 | HIGH | YES | DHG1504DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | INSTALLATION MANUAL - DHG (7.5-12.5) | DHG1504DH | DHG1504DH