## Mini Splits
SPLIT SYSTEM SCHEDULE
INDOOR UNIT | [13 empty] | OUTDOOR UNIT | [8 empty] | Refrigerant | MAX ALLOWABLE LINE-SET LENGTHS | ACCESSORIES
SYMBOL | CFM | COOLING CAPACITY |  |  |  | HEAT PUMP HEATING CAPACITY |  | OPERATING WEIGHT | INDOOR UNIT TYPE | ELECTRICAL |  |  | MANUFACTURER | SYMBOL | OA AMBIENT (COOLING) | OA AMBIENT (HEATING) | OPERATING WEIGHT | SEER2/EER2/HSPF2 | ELECTRICAL |  |  | MANUFACTURER
|  | EDB | EWB | TOTAL CAPACITY | SENSIBLE CAPACITY | EDB | TOTAL CAPACITY |  |  | Voltage | MCA | MOP | DAIKIN | [5 empty] | Voltage | MCA | MOP | DAIKIN |  |  |  | FILTERS | [11 empty] | DOCUMENTATION
[26 empty] | SIZE (OUTDOOR UNIT) | COOLING ONLY OR HEAT PUMP | SIZE (INDOOR UNIT #1) | SIZE (INDOOR UNIT #2) | SIZE (INDOOR UNIT #3) | SIZE (INDOOR UNIT #4) | SIZE (INDOOR UNIT #5) | TYPE (INDOOR UNIT #1) | TYPE (INDOOR UNIT #2) | TYPE (INDOOR UNIT #3) | TYPE (INDOOR UNIT #4) | TYPE (INDOOR UNIT #5) | SUBMITTAL (SYSTEM) | SUBMITTAL (MULTI SPLIT OUTDOOR UNIT) | SUBMITTAL (MULTI SPLIT INDOOR UNITS) | ENGINEERING MANUAL | CAPACITY TABLE | INSTALLATION MANUAL (OUTDOOR) | INSTALLATION MANUAL (INDOOR) | OPERATION MANUAL | REVIT (OUTDOOR) | REVIT (INDOOR) | CAD (OUTDOOR) | CAD (INDOOR)
IDU- | 381 | 80 | 67 | 11200 | 8250 | 70 | 16000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXF09BVJU9 | ODU- | 95 | 47 | 68 | 21.0 / 12.5 / 10.2 | 208/60/1 | 11.6 | 15 | RXF09BVJU9 | R32 | 49' Vertical / 66' Total |  | 0.75 | HEAT PUMP | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - | FTXF09BVJU9-RXF09BVJU9 |  |  | ENGINEERING MANUAL - OTERRA |  | IM - OTERRA OUTDOOR (09-12) | IM - OTERRA INDOOR (09-12) | OM - OTERRA INDOOR (09-12) | RXF09BVJU9 | FTXF09BVJU9 | RXF09BVJU9 | FTXF09BVJU9
IDU- | 399 | 80 | 67 | 14600 | 9880 | 70 | 18000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXF12BVJU9 | ODU- | 95 | 47 | 77 | 21.0 / 12.5 / 10.2 | 208/60/1 | 14.6 | 15 | RXF12BVJU9 | R32 | 49' Vertical / 66' Total |  | 1 | HEAT PUMP | 1 | - | - | - | - | Wall Mounted | - | - | - | - | FTXF12BVJU9-RXF12BVJU9 |  |  | ENGINEERING MANUAL - OTERRA |  | IM - OTERRA OUTDOOR (09-12) | IM - OTERRA INDOOR (09-12) | OM - OTERRA INDOOR (09-12) | RXF12BVJU9 | FTXF12BVJU9 | RXF12BVJU9 | FTXF12BVJU9
IDU- | 565 | 80 | 67 | 22000 | 14590 | 70 | 28000 | 37 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXF18BVJU9 | ODU- | 95 | 47 | 121 | 21.0 / 12.0 / 9.6 | 208/60/1 | 21.4 | 25 | RXF18BVJU9 | R32 | 66' Vertical / 99' Total |  | 1.5 | HEAT PUMP | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - | FTXF18BVJU9-RXF18BVJU9 |  |  | ENGINEERING MANUAL - OTERRA |  | IM - OTERRA OUTDOOR (18-24) | IM - OTERRA INDOOR (18-24) | OM - OTERRA INDOOR (18-24) | RXF18BVJU9 | FTXF18BVJU9 | RXF18BVJU9 | FTXF18BVJU9
IDU- | 629 | 80 | 67 | 26400 | 16660 | 70 | 32000 | 37 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXF24BVJU9 | ODU- | 95 | 47 | 121 | 21.0 / 12.0 / 9.5 | 208/60/1 | 21.6 | 25 | RXF24BVJU9 | R32 | 66' Vertical / 99' Total |  | 2 | HEAT PUMP | 2 | - | - | - | - | Wall Mounted | - | - | - | - | FTXF24BVJU9-RXF24BVJU9 |  |  | ENGINEERING MANUAL - OTERRA |  | IM - OTERRA OUTDOOR (18-24) | IM - OTERRA INDOOR (18-24) | OM - OTERRA INDOOR (18-24) | RXF24BVJU9 | FTXF24BVJU9 | RXF24BVJU9 | FTXF24BVJU9
IDU- | 925 | 80 | 67 | 31400 | 20390 | 70 | 34800 | 42 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV30AVJU9 | ODU- | 95 | 47 | 128 | 19.0 / 10.0 / 8.1 | 208/60/1 | 22 | 25 | RXV30AVJU9 | R32 | 66' Vertical / 99' Total |  | 2.5 | HEAT PUMP | 2.5 | - | - | - | - | Wall Mounted | - | - | - | - | FTXV30AVJU9-RXV30AVJU9 |  |  | ENGINEERING MANUAL - POLARA |  | IM - POLARA OUTDOOR | IM - POLARA INDOOR (30-36) | OM - POLARA INDOOR (30-36)
IDU- | 971 | 80 | 67 | 34400 | 21960 | 70 | 36000 | 42 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV36AVJU9 | ODU- | 95 | 47 | 128 | 18.0 / 9.8 / 8.0 | 208/60/1 | 22 | 25 | RXV36AVJU9 | R32 | 66' Vertical / 99' Total |  | 3 | HEAT PUMP | 3 | - | - | - | - | Wall Mounted | - | - | - | - | FTXV36AVJU9-RXV36AVJU9 |  |  | ENGINEERING MANUAL - POLARA |  | IM - POLARA OUTDOOR | IM - POLARA INDOOR (30-36) | OM - POLARA INDOOR (30-36)
IDU- | 322 | 80 | 67 | 11200 | 8250 | - | - | 25 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTKF09BVJU9 | ODU- | 95 | - | 68 | 21.0 / 12.5 / - | 208/60/1 | 11.6 | 15 | RKF09BVJU9 | R32 | 49' Vertical / 66' Total |  | 0.75 | COOLING ONLY | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - | FTKF09BVJU9-RKF09BVJU9 |  |  | ENGINEERING MANUAL - OTERRA |  | IM - OTERRA OUTDOOR (09-12) | IM - OTERRA INDOOR (09-12) | OM - OTERRA INDOOR (09-12) | RKF09BVJU9 | FTXF09BVJU9 | RKF09BVJU9 | FTXF09BVJU9
IDU- | 399 | 80 | 67 | 14600 | 9880 | - | - | 25 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTKF12BVJU9 | ODU- | 95 | - | 76 | 21.0 / 12.5 / - | 208/60/1 | 14.6 | 15 | RKF12BVJU9 | R32 | 49' Vertical / 66' Total |  | 1 | COOLING ONLY | 1 | - | - | - | - | Wall Mounted | - | - | - | - | FTKF12BVJU9-RKF12BVJU9 |  |  | ENGINEERING MANUAL - OTERRA |  | IM - OTERRA OUTDOOR (09-12) | IM - OTERRA INDOOR (09-12) | OM - OTERRA INDOOR (09-12) | RKF12BVJU9 | FTXF12BVJU9 | RKF12BVJU9 | FTXF12BVJU9
IDU- | 565 | 80 | 67 | 22000 | 14590 | - | - | 37 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTKF18BVJU9 | ODU- | 95 | - | 113 | 21.0 / 12.0 / - | 208/60/1 | 21.4 | 25 | RKF18BVJU9 | R32 | 66' Vertical / 99' Total |  | 1.5 | COOLING ONLY | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - | FTKF18BVJU9-RKF18BVJU9 |  |  | ENGINEERING MANUAL - OTERRA |  | IM - OTERRA OUTDOOR (18-24) | IM - OTERRA INDOOR (18-24) | OM - OTERRA INDOOR (18-24) | RKF18BVJU9 | FTXF18BVJU9 | RKF18BVJU9 | FTXF18BVJU9
IDU- | 629 | 80 | 67 | 26400 | 16660 | - | - | 37 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTKF24BVJU9 | ODU- | 95 | - | 113 | 21.0 / 12.0 / - | 208/60/1 | 21.6 | 25 | RKF24BVJU9 | R32 | 66' Vertical / 99' Total |  | 2 | COOLING ONLY | 2 | - | - | - | - | Wall Mounted | - | - | - | - | FTKF24BVJU9-RKF24BVJU9 |  |  | ENGINEERING MANUAL - OTERRA |  | IM - OTERRA OUTDOOR (18-24) | IM - OTERRA INDOOR (18-24) | OM - OTERRA INDOOR (18-24) | RKF24BVJU9 | FTXF24BVJU9 | RKF24BVJU9 | FTXF24BVJU9
IDU- | 925 | 80 | 67 | 31400 | 19980 | - | - | 42 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV30AVJU9 | ODU- | 95 | - | 128 | 19.0 / 10.0 / - | 208/60/1 | 21.8 | 25 | RKV30AVJU9 | R32 | 66' Vertical / 99' Total |  | 2.5 | COOLING ONLY | 2.5 | - | - | - | - | Wall Mounted | - | - | - | - | FTXV30AVJU9-RKV30AVJU9 |  |  | ENGINEERING MANUAL - POLARA |  | IM - POLARA OUTDOOR | IM - POLARA INDOOR (30-36) | OM - POLARA INDOOR (30-36)
IDU- | 971 | 80 | 67 | 34400 | 21960 | - | - | 42 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV36AVJU9 | ODU- | 95 | - | 128 | 18.0 / 9.8 / - | 208/60/1 | 21.9 | 25 | RKV36AVJU9 | R32 | 66' Vertical / 99' Total |  | 3 | COOLING ONLY | 3 | - | - | - | - | Wall Mounted | - | - | - | - | FTXV36AVJU9-RKV36AVJU9 |  |  | ENGINEERING MANUAL - POLARA |  | IM - POLARA OUTDOOR | IM - POLARA INDOOR (30-36) | OM - POLARA INDOOR (30-36)
IDU- | 424 | 80 | 67 | 10500 | 8140 | 70 | 12000 | 18 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXQ09ASBU9 | ODU- | 95 | 47 | 59 | 20.0 / 12.0 / 9.0 | 115/60/1 | 14.9 | 15 | RXQ09ASBU9 | R32 | 50' Vertical / 66' Total |  | 0.75 | HEAT PUMP | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - | FTXQ09ASBU9-RXQ09ASBU9 |  |  | ENGINEERING MANUAL - OTERRA 115V |  | IM - OTERRA 115V OUTDOOR | IM - OTERRA 115V INDOOR | OM - OTERRA 115V INDOOR (09-12) | RXQ09ASBU9 | FTXQ09ASBU9 | RXQ09ASBU9 | FTXQ09ASBU9
IDU- | 413 | 80 | 67 | 12800 | 9310 | 70 | 14600 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXQ12ASBU9 | ODU- | 95 | 47 | 64 | 20.0 / 12.0 / 9.0 | 115/60/1 | 15 | 15 | RXQ12ASBU9 | R32 | 50' Vertical / 66' Total |  | 1 | HEAT PUMP | 1 | - | - | - | - | Wall Mounted | - | - | - | - | FTXQ12ASBU9-RXQ12ASBU9 |  |  | ENGINEERING MANUAL - OTERRA 115V |  | IM - OTERRA 115V OUTDOOR | IM - OTERRA 115V INDOOR | OM - OTERRA 115V INDOOR (09-12) | RXQ12ASBU9 | FTXQ12ASBU9 | RXQ12ASBU9 | FTXQ12ASBU9
IDU- | 401 | 80 | 67 | 9400 | 6910 | 70 | 12800 | 64 | Ducted Concealed | Indoor Powered From Outdoor Unit |  |  | FDMA09AVJU9 | ODU- | 95 | 47 | 72 | 16.0 / 11.1 / 9.0 | 208/60/1 | 11.6 | 15 | RXP09AVJU9 | R32 | 49' Vertical / 66' Total |  | 0.75 | HEAT PUMP | 0.75 | - | - | - | - | Ducted Concealed | - | - | - | - | FDMA09AVJU9-RXP09AVJU9 |  |  | ENGINEERING MANUAL - FDMA MINI SPLIT |  | IM - RXP OUTDOOR UNIT (09-12) | IM - FDMA INDOOR (09-24) | OM - FDMA INDOOR (09-24) | RXP09AVJU9 | FDMA09AVJU9 | RXP09AVJU9 | FDMA09AVJU9
IDU- | 440 | 80 | 67 | 12400 | 8330 | 70 | 17000 | 64 | Ducted Concealed | Indoor Powered From Outdoor Unit |  |  | FDMA12AVJU9 | ODU- | 95 | 47 | 72 | 16.0 / 10.0 / 9.0 | 208/60/1 | 14.6 | 15 | RXP12AVJU9 | R32 | 49' Vertical / 66' Total |  | 1 | HEAT PUMP | 1 | - | - | - | - | Ducted Concealed | - | - | - | - | FDMA12AVJU9-RXP12AVJU9 |  |  | ENGINEERING MANUAL - FDMA MINI SPLIT |  | IM - RXP OUTDOOR UNIT (09-12) | IM - FDMA INDOOR (09-24) | OM - FDMA INDOOR (09-24) | RXP12AVJU9 | FDMA12AVJU9 | RXP12AVJU9 | FDMA12AVJU9
IDU- | 471 | 80 | 67 | 15700 | 11230 | 70 | 18500 | 82 | Ducted Concealed | Indoor Powered From Outdoor Unit |  |  | FDMA15AVJU9 | ODU- | 95 | 47 | 127 | 18.0 / 11.8 / 9.2 | 208/60/1 | 16.1 | 20 | RXP15AVJU9 | R32 | 66' Vertical / 99' Total |  | 1.25 | HEAT PUMP | 1.25 | - | - | - | - | Ducted Concealed | - | - | - | - | FDMA15AVJU9-RXP15AVJU9 |  |  | ENGINEERING MANUAL - FDMA MINI SPLIT |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FDMA INDOOR (09-24) | OM - FDMA INDOOR (09-24) | RXP15AVJU9 | FDMA15AVJU9 | RXP15AVJU9 | FDMA15AVJU9
IDU- | 609 | 80 | 67 | 19600 | 14460 | 70 | 25000 | 82 | Ducted Concealed | Indoor Powered From Outdoor Unit |  |  | FDMA18AVJU9 | ODU- | 95 | 47 | 127 | 18.0 / 11.6 / 9.2 | 208/60/1 | 21.4 | 25 | RXP18AVJU9 | R32 | 66' Vertical / 99' Total |  | 1.5 | HEAT PUMP | 1.5 | - | - | - | - | Ducted Concealed | - | - | - | - | FDMA18AVJU9-RXP18AVJU9 |  |  | ENGINEERING MANUAL - FDMA MINI SPLIT |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FDMA INDOOR (09-24) | OM - FDMA INDOOR (09-24) | RXP18AVJU9 | FDMA18AVJU9 | RXP18AVJU9 | FDMA18AVJU9
IDU- | 666 | 80 | 67 | 23000 | 15740 | 70 | 27600 | 88 | Ducted Concealed | Indoor Powered From Outdoor Unit |  |  | FDMA24AVJU9 | ODU- | 95 | 47 | 127 | 18.0 / 10.3 / 9.2 | 208/60/1 | 21.6 | 25 | RXP24AVJU9 | R32 | 66' Vertical / 99' Total |  | 2 | HEAT PUMP | 2 | - | - | - | - | Ducted Concealed | - | - | - | - | FDMA24AVJU9-RXP24AVJU9 |  |  | ENGINEERING MANUAL - FDMA MINI SPLIT |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FDMA INDOOR (09-24) | OM - FDMA INDOOR (09-24) | RXP24AVJU9 | FDMA24AVJU9 | RXP24AVJU9 | FDMA24AVJU9
IDU- | 297 | 80 | 67 | 10900 | 7310 | 70 | 17100 | 40 | Floor Mounted (Black) | Indoor Powered From Outdoor Unit |  |  | FVXV09AVJUT9 | ODU- | 95 | 47 | 72 | 19.5 / 12.0 / 9.7 | 208/60/1 | 11.6 | 15 | RXP09AVJU9 | R32 | 49' Vertical / 66' Total |  | 0.75 | HEAT PUMP | 0.75 | - | - | - | - | Floor Mounted (Black) | - | - | - | - | FVXV09AVJUT9-RXP09AVJU9 |  |  | ENGINEERING MANUAL - FVXV |  | IM - RXP OUTDOOR UNIT (09-12) | IM - FVXV INDOOR (09-18) | OM - FVXV INDOOR (09-18) | RXP09AVJU9 |  | RXP09AVJU9
IDU- | 321 | 80 | 67 | 12600 | 8110 | 70 | 19900 | 40 | Floor Mounted (Black) | Indoor Powered From Outdoor Unit |  |  | FVXV12AVJUT9 | ODU- | 95 | 47 | 72 | 19.5 / 10.5 / 9.5 | 208/60/1 | 14.6 | 15 | RXP12AVJU9 | R32 | 49' Vertical / 66' Total |  | 1 | HEAT PUMP | 1 | - | - | - | - | Floor Mounted (Black) | - | - | - | - | FVXV12AVJUT9-RXP12AVJU9 |  |  | ENGINEERING MANUAL - FVXV |  | IM - RXP OUTDOOR UNIT (09-12) | IM - FVXV INDOOR (09-18) | OM - FVXV INDOOR (09-18) | RXP12AVJU9 |  | RXP12AVJU9
IDU- | 392 | 80 | 67 | 19100 | 11610 | 70 | 20400 | 40 | Floor Mounted (Black) | Indoor Powered From Outdoor Unit |  |  | FVXV15AVJUT9 | ODU- | 95 | 47 | 127 | 19.5 / 12.0 / 9.6 | 208/60/1 | 16.1 | 20 | RXP15AVJU9 | R32 | 66' Vertical / 99' Total |  | 1.25 | HEAT PUMP | 1.25 | - | - | - | - | Floor Mounted (Black) | - | - | - | - | FVXV15AVJUT9-RXP15AVJU9 |  |  | ENGINEERING MANUAL - FVXV |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FVXV INDOOR (09-18) | OM - FVXV INDOOR (09-18) | RXP15AVJU9 |  | RXP15AVJU9
IDU- | 448 | 80 | 67 | 21400 | 13000 | 70 | 21800 | 40 | Floor Mounted (Black) | Indoor Powered From Outdoor Unit |  |  | FVXV18AVJUT9 | ODU- | 95 | 47 | 127 | 19.5 / 12.0 / 9.5 | 208/60/1 | 21.4 | 25 | RXP18AVJU9 | R32 | 66' Vertical / 99' Total |  | 1.5 | HEAT PUMP | 1.5 | - | - | - | - | Floor Mounted (Black) | - | - | - | - | FVXV18AVJUT9-RXP18AVJU9 |  |  | ENGINEERING MANUAL - FVXV |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FVXV INDOOR (09-18) | OM - FVXV INDOOR (09-18) | RXP18AVJU9 |  | RXP18AVJU9
IDU- | 297 | 80 | 67 | 10900 | 7310 | 70 | 17100 | 40 | Floor Mounted (White) | Indoor Powered From Outdoor Unit |  |  | FVXV09AVJUW9 | ODU- | 95 | 47 | 72 | 19.5 / 12.0 / 9.7 | 208/60/1 | 11.6 | 15 | RXP09AVJU9 | R32 | 49' Vertical / 66' Total |  | 0.75 | HEAT PUMP | 0.75 | - | - | - | - | Floor Mounted (White) | - | - | - | - | FVXV09AVJUW9-RXP09AVJU9 |  |  | ENGINEERING MANUAL - FVXV |  | IM - RXP OUTDOOR UNIT (09-12) | IM - FVXV INDOOR (09-18) | OM - FVXV INDOOR (09-18) | RXP09AVJU9 |  | RXP09AVJU9
IDU- | 321 | 80 | 67 | 12600 | 8110 | 70 | 19900 | 40 | Floor Mounted (White) | Indoor Powered From Outdoor Unit |  |  | FVXV12AVJUW9 | ODU- | 95 | 47 | 72 | 19.5 / 10.5 / 9.5 | 208/60/1 | 14.6 | 15 | RXP12AVJU9 | R32 | 49' Vertical / 66' Total |  | 1 | HEAT PUMP | 1 | - | - | - | - | Floor Mounted (White) | - | - | - | - | FVXV12AVJUW9-RXP12AVJU9 |  |  | ENGINEERING MANUAL - FVXV |  | IM - RXP OUTDOOR UNIT (09-12) | IM - FVXV INDOOR (09-18) | OM - FVXV INDOOR (09-18) | RXP12AVJU9 |  | RXP12AVJU9
IDU- | 392 | 80 | 67 | 19100 | 11610 | 70 | 20400 | 40 | Floor Mounted (White) | Indoor Powered From Outdoor Unit |  |  | FVXV15AVJUW9 | ODU- | 95 | 47 | 127 | 19.5 / 12.0 / 9.6 | 208/60/1 | 16.1 | 20 | RXP15AVJU9 | R32 | 66' Vertical / 99' Total |  | 1.25 | HEAT PUMP | 1.25 | - | - | - | - | Floor Mounted (White) | - | - | - | - | FVXV15AVJUW9-RXP15AVJU9 |  |  | ENGINEERING MANUAL - FVXV |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FVXV INDOOR (09-18) | OM - FVXV INDOOR (09-18) | RXP15AVJU9 |  | RXP15AVJU9
IDU- | 448 | 80 | 67 | 21400 | 13000 | 70 | 21800 | 40 | Floor Mounted (White) | Indoor Powered From Outdoor Unit |  |  | FVXV18AVJUW9 | ODU- | 95 | 47 | 127 | 19.5 / 12.0 / 9.5 | 208/60/1 | 21.4 | 25 | RXP18AVJU9 | R32 | 66' Vertical / 99' Total |  | 1.5 | HEAT PUMP | 1.5 | - | - | - | - | Floor Mounted (White) | - | - | - | - | FVXV18AVJUW9-RXP18AVJU9 |  |  | ENGINEERING MANUAL - FVXV |  | IM - RXP OUTDOOR UNIT (15-24) | IM - FVXV INDOOR (09-18) | OM - FVXV INDOOR (09-18) | RXP18AVJU9 |  | RXP18AVJU9
IDU- | 635 | 80 | 67 | 18000 | 14800 | 70 | 20000 | 82 | Ducted Concealed | 208/1 | 1.9 | 15 | FBA18AAVJU | ODU- | 95 | 47 | 234 | 16.3 / 13.5 / 8.5 | 208/60/1 | 19.8 | 20 | RZA18AAVJU | R32 | 98' Vertical, 230' Total |  | 1.5 | HEAT PUMP | 1.5 | - | - | - | - | Ducted Concealed | - | - | - | - | FBA18AAVJU-RZA18AAVJU |  |  | ENGINEERING MANUAL - FBA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FBA INDOOR (18-48) | OM - FBA INDOOR (18-48) | RZA18AAVJU | FBA18AAVJU | RZA18AAVJU | FBA18AAVJU
IDU- | 742 | 80 | 67 | 24000 | 18700 | 70 | 27000 | 84 | Ducted Concealed | 208/1 | 1.9 | 15 | FBA24AAVJU | ODU- | 95 | 47 | 234 | 16.2 / 11.7 / 9.3 | 208/60/1 | 19.8 | 20 | RZA24AAVJU | R32 | 98' Vertical, 230' Total |  | 2 | HEAT PUMP | 2 | - | - | - | - | Ducted Concealed | - | - | - | - | FBA24AAVJU-RZA24AAVJU |  |  | ENGINEERING MANUAL - FBA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FBA INDOOR (18-48) | OM - FBA INDOOR (18-48) | RZA24AAVJU | FBA24AAVJU | RZA24AAVJU | FBA24AAVJU
IDU- | 1094 | 80 | 67 | 30000 | 23400 | 70 | 34000 | 101 | Ducted Concealed | 208/1 | 3.1 | 15 | FBA30AAVJU | ODU- | 95 | 47 | 234 | 16.5 / 12.4 / 8.9 | 208/60/1 | 34.6 | 35 | RZA30AAVJU | R32 | 98' Vertical, 230' Total |  | 2.5 | HEAT PUMP | 2.5 | - | - | - | - | Ducted Concealed | - | - | - | - | FBA30AAVJU-RZA30AAVJU |  |  | ENGINEERING MANUAL - FBA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FBA INDOOR (18-48) | OM - FBA INDOOR (18-48) | RZA30AAVJU | FBA30AAVJU | RZA30AAVJU | FBA30AAVJU
IDU- | 1130 | 80 | 67 | 36000 | 27200 | 70 | 40000 | 101 | Ducted Concealed | 208/1 | 3.1 | 15 | FBA36AAVJU | ODU- | 95 | 47 | 234 | 16.9 / 11.8 / 8.8 | 208/60/1 | 34.6 | 35 | RZA36AAVJU | R32 | 98' Vertical, 230' Total |  | 3 | HEAT PUMP | 3 | - | - | - | - | Ducted Concealed | - | - | - | - | FBA36AAVJU-RZA36AAVJU |  |  | ENGINEERING MANUAL - FBA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FBA INDOOR (18-48) | OM - FBA INDOOR (18-48) | RZA36AAVJU | FBA36AAVJU | RZA36AAVJU | FBA36AAVJU
IDU- | 1377 | 80 | 67 | 40500 | 30500 | 70 | 47000 | 106 | Ducted Concealed | 208/1 | 3.6 | 15 | FBA42AAVJU | ODU- | 95 | 47 | 234 | 15.6 / 10.5 / 9.5 | 208/60/1 | 34.6 | 35 | RZA42AAVJU | R32 | 98' Vertical, 230' Total |  | 3.5 | HEAT PUMP | 3.5 | - | - | - | - | Ducted Concealed | - | - | - | - | FBA42AAVJU-RZA42AAVJU |  |  | ENGINEERING MANUAL - FBA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FBA INDOOR (18-48) | OM - FBA INDOOR (18-48) | RZA42AAVJU | FBA42AAVJU | RZA42AAVJU | FBA42AAVJU
IDU- | 1377 | 80 | 67 | 48000 | 36100 | 70 | 54000 | 106 | Ducted Concealed | 208/1 | 3.6 | 15 | FBA48AAVJU | ODU- | 95 | 47 | 234 | 15.3 / 8.9 / 9.3 | 208/60/1 | 34.6 | 35 | RZA48AAVJU | R32 | 98' Vertical, 230' Total |  | 4 | HEAT PUMP | 4 | - | - | - | - | Ducted Concealed | - | - | - | - | FBA48AAVJU-RZA48AAVJU |  |  | ENGINEERING MANUAL - FBA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FBA INDOOR (18-48) | OM - FBA INDOOR (18-48) | RZA48AAVJU | FBA48AAVJU | RZA48AAVJU | FBA48AAVJU
IDU- | 742 | 80 | 67 | 18000 | 16100 | 70 | 20000 | 51 | Cassette | 208/1 | 0.5 | 15 | FCA18AAVJU | ODU- | 95 | 47 | 234 | 19.5 / 14.0 / 9.2 | 208/60/1 | 19.8 | 20 | RZA18AAVJU | R32 | 98' Vertical, 230' Total |  | 1.5 | HEAT PUMP | 1.5 | - | - | - | - | Cassette | - | - | - | - | FCA18AAVJU-RZA18AAVJU |  |  | ENGINEERING MANUAL - FCA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FCA INDOOR (18-48) | OM - FCA INDOOR (18-48) | RZA18AAVJU | FCA18AAVJU | RZA18AAVJU | FCA18AAVJU
IDU- | 777 | 80 | 67 | 24000 | 19900 | 70 | 27000 | 51 | Cassette | 208/1 | 0.5 | 15 | FCA24AAVJU | ODU- | 95 | 47 | 234 | 19.6 / 13.4 / 9.1 | 208/60/1 | 19.8 | 20 | RZA24AAVJU | R32 | 98' Vertical, 230' Total |  | 2 | HEAT PUMP | 2 | - | - | - | - | Cassette | - | - | - | - | FCA24AAVJU-RZA24AAVJU |  |  | ENGINEERING MANUAL - FCA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FCA INDOOR (18-48) | OM - FCA INDOOR (18-48) | RZA24AAVJU | FCA24AAVJU | RZA24AAVJU | FCA24AAVJU
IDU- | 1059 | 80 | 67 | 30000 | 22300 | 70 | 34000 | 58 | Cassette | 208/1 | 1 | 15 | FCA30AAVJU | ODU- | 95 | 47 | 234 | 21.0 / 13.2 / 10.1 | 208/60/1 | 34.6 | 35 | RZA30AAVJU | R32 | 98' Vertical, 230' Total |  | 2.5 | HEAT PUMP | 2.5 | - | - | - | - | Cassette | - | - | - | - | FCA30AAVJU-RZA30AAVJU |  |  | ENGINEERING MANUAL - FCA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FCA INDOOR (18-48) | OM - FCA INDOOR (18-48) | RZA30AAVJU | FCA30AAVJU | RZA30AAVJU | FCA30AAVJU
IDU- | 1253 | 80 | 67 | 36000 | 28300 | 70 | 40000 | 58 | Cassette | 208/1 | 1.6 | 15 | FCA36AAVJU | ODU- | 95 | 47 | 234 | 20.0 / 12.2 / 10.0 | 208/60/1 | 34.6 | 35 | RZA36AAVJU | R32 | 98' Vertical, 230' Total |  | 3 | HEAT PUMP | 3 | - | - | - | - | Cassette | - | - | - | - | FCA36AAVJU-RZA36AAVJU |  |  | ENGINEERING MANUAL - FCA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FCA INDOOR (18-48) | OM - FCA INDOOR (18-48) | RZA36AAVJU | FCA36AAVJU | RZA36AAVJU | FCA36AAVJU
IDU- | 1253 | 80 | 67 | 42000 | 30600 | 70 | 47000 | 58 | Cassette | 208/1 | 1.6 | 15 | FCA42AAVJU | ODU- | 95 | 47 | 234 | 18.9 / 10.5 / 10.2 | 208/60/1 | 34.6 | 35 | RZA42AAVJU | R32 | 98' Vertical, 230' Total |  | 3.5 | HEAT PUMP | 3.5 | - | - | - | - | Cassette | - | - | - | - | FCA42AAVJU-RZA42AAVJU |  |  | ENGINEERING MANUAL - FCA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FCA INDOOR (18-48) | OM - FCA INDOOR (18-48) | RZA42AAVJU | FCA42AAVJU | RZA42AAVJU | FCA42AAVJU
IDU- | 1253 | 80 | 67 | 48000 | 35000 | 70 | 54000 | 58 | Cassette | 208/1 | 1.6 | 15 | FCA48AAVJU | ODU- | 95 | 47 | 234 | 18.0 / 8.8 / 9.7 | 208/60/1 | 34.6 | 35 | RZA48AAVJU | R32 | 98' Vertical, 230' Total |  | 4 | HEAT PUMP | 4 | - | - | - | - | Cassette | - | - | - | - | FCA48AAVJU-RZA48AAVJU |  |  | ENGINEERING MANUAL - FCA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FCA INDOOR (18-48) | OM - FCA INDOOR (18-48) | RZA48AAVJU | FCA48AAVJU | RZA48AAVJU | FCA48AAVJU
IDU- | 512 | 80 | 67 | 18000 | 13700 | 70 | 20000 | 35.3 | Wall Mounted | 208/1 | 0.5 | 15 | FAA18AAVJU | ODU- | 95 | 47 | 234 | 17.8 / 12.8 / 7.6 | 208/60/1 | 19.8 | 20 | RZA18AAVJU | R32 | 98' Vertical, 230' Total |  | 1.5 | HEAT PUMP | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - | FAA18AAVJU-RZA18AAVJU |  |  | ENGINEERING MANUAL - FAA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FAA INDOOR (18-24) | OM - FAA INDOOR (18-24) | RZA18AAVJU |  | RZA18AAVJU
IDU- | 670 | 80 | 67 | 24000 | 18000 | 70 | 27000 | 35.3 | Wall Mounted | 208/1 | 0.6 | 15 | FAA24AAVJU | ODU- | 95 | 47 | 234 | 18.2 / 11.4 / 7.8 | 208/60/1 | 19.8 | 20 | RZA24AAVJU | R32 | 98' Vertical, 230' Total |  | 2 | HEAT PUMP | 2 | - | - | - | - | Wall Mounted | - | - | - | - | FAA24AAVJU-RZA24AAVJU |  |  | ENGINEERING MANUAL - FAA SKY AIR | CAPACITY TABLE - SKY AIR | IM - RZA OUTDOOR UNIT (18-48) | IM - FAA INDOOR (18-24) | OM - FAA INDOOR (18-24) | RZA24AAVJU |  | RZA24AAVJU
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | 2MXM18AVJU9 | R32 | 164' Max System Piping |  | 1.5 | HEAT PUMP | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - |  | 2MXM18AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 2MXM18AVJU9 | CTXV07AVJU9 | 2MXM18AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 10300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | 2MXM18AVJU9 | R32 | 164' Max System Piping |  | 1.5 | HEAT PUMP | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - |  | 2MXM18AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 2MXM18AVJU9 | FTXV09AVJU9 | 2MXM18AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 13300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | 2MXM18AVJU9 | R32 | 164' Max System Piping |  | 1.5 | HEAT PUMP | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - |  | 2MXM18AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 2MXM18AVJU9 | FTXV12AVJU9 | 2MXM18AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 16300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | 2MXM18AVJU9 | R32 | 164' Max System Piping |  | 1.5 | HEAT PUMP | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - |  | 2MXM18AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 2MXM18AVJU9 | FTXV15AVJU9 | 2MXM18AVJU9 | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | 2MXM18AVJU9 | R32 | 164' Max System Piping |  | 1.5 | HEAT PUMP | 0.5 | 0.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 2MXM18AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 2MXM18AVJU9 | CTXV07AVJU9 | 2MXM18AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6870 | - | 70 | 7440 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | 2MXM18AVJU9 | R32 | 164' Max System Piping |  | 1.5 | HEAT PUMP | 0.5 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 2MXM18AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 2MXM18AVJU9 | CTXV07AVJU9 | 2MXM18AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8830 | - | 70 | 9560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 6340 | - | 70 | 6820 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | 2MXM18AVJU9 | R32 | 164' Max System Piping |  | 1.5 | HEAT PUMP | 0.5 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 2MXM18AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 2MXM18AVJU9 | CTXV07AVJU9 | 2MXM18AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 10860 | - | 70 | 11680 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 5470 | - | 70 | 5890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | 2MXM18AVJU9 | R32 | 164' Max System Piping |  | 1.5 | HEAT PUMP | 0.5 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 2MXM18AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 2MXM18AVJU9 | CTXV07AVJU9 | 2MXM18AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 11730 | - | 70 | 12610 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 8600 | - | 70 | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | 2MXM18AVJU9 | R32 | 164' Max System Piping |  | 1.5 | HEAT PUMP | 0.75 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 2MXM18AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 2MXM18AVJU9 | FTXV09AVJU9 | 2MXM18AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8600 | - | 70 | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7370 | - | 70 | 7930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | 2MXM18AVJU9 | R32 | 164' Max System Piping |  | 1.5 | HEAT PUMP | 0.75 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 2MXM18AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 2MXM18AVJU9 | FTXV09AVJU9 | 2MXM18AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9830 | - | 70 | 10570 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 6450 | - | 70 | 6940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | 2MXM18AVJU9 | R32 | 164' Max System Piping |  | 1.5 | HEAT PUMP | 0.75 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 2MXM18AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 2MXM18AVJU9 | FTXV09AVJU9 | 2MXM18AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 10750 | - | 70 | 11560 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 392 | 80 | 67 | 8600 | - | 70 | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 127 | 21.0 / 12.0 / 10.0 | 208/60/1 | 15.6 | 20 | 2MXM18AVJU9 | R32 | 164' Max System Piping |  | 1.5 | HEAT PUMP | 1 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 2MXM18AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 2MXM18AVJU9 | FTXV12AVJU9 | 2MXM18AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 8600 | - | 70 | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | - | - | - | - | Wall Mounted | - | - | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 10300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 13300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 1 | - | - | - | - | Wall Mounted | - | - | - | - |  | 3MXM24AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 3MXM24AVJU9 | FTXV12AVJU9 | 3MXM24AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 16600 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 1.25 | - | - | - | - | Wall Mounted | - | - | - | - |  | 3MXM24AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 3MXM24AVJU9 | FTXV15AVJU9 | 3MXM24AVJU9 | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 19300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - |  | 3MXM24AVJU9 | FTXV18AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 | 3MXM24AVJU9 | FTXV18AVJU9 | 3MXM24AVJU9 | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 0.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7570 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7440 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7350 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15750 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6440 | - | 70 | 6720 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 16560 | - | 70 | 17250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9470 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12630 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 8630 | - | 70 | 9000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 14380 | - | 70 | 15000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 15330 | - | 70 | 16000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 1 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 3MXM24AVJU9 | FTXV12AVJU9 | 3MXM24AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10670 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 1 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 3MXM24AVJU9 | FTXV12AVJU9 | 3MXM24AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 12780 | - | 70 | 13330 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 392 | 80 | 67 | 9200 | - | 70 | 9600 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 1 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 3MXM24AVJU9 | FTXV12AVJU9 | 3MXM24AVJU9 | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 13800 | - | 70 | 14400 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 540 | 80 | 67 | 11500 | - | 70 | 12000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 1.25 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 3MXM24AVJU9 | FTXV15AVJU9 | 3MXM24AVJU9 | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 11500 | - | 70 | 12000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 10450 | - | 70 | 10910 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 1.25 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 3MXM24AVJU9 | FTXV15AVJU9 | 3MXM24AVJU9 | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 12550 | - | 70 | 13090 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 11500 | - | 70 | 12000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 1.5 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 3MXM24AVJU9 | FTXV18AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 | 3MXM24AVJU9 | FTXV18AVJU9 | 3MXM24AVJU9 | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 11500 | - | 70 | 12000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 0.5 | 0.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 0.5 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6460 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 0.5 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6460 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 10620 | - | 70 | 11080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 5550 | - | 70 | 5790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 0.5 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5550 | - | 70 | 5790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 11900 | - | 70 | 12410 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5030 | - | 70 | 5250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 0.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5030 | - | 70 | 5250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 12940 | - | 70 | 13500 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6440 | - | 70 | 6720 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 0.75 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8280 | - | 70 | 8640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8280 | - | 70 | 8640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 5750 | - | 70 | 6000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 0.75 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7390 | - | 70 | 7710 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9860 | - | 70 | 10290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 5190 | - | 70 | 5420 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 0.75 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 6680 | - | 70 | 6970 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 11130 | - | 70 | 11610 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 4740 | - | 70 | 4940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 0.75 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 6090 | - | 70 | 6350 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 12180 | - | 70 | 12710 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5190 | - | 70 | 5420 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 8900 | - | 70 | 9290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 8900 | - | 70 | 9290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 4740 | - | 70 | 4940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 8120 | - | 70 | 8470 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 10150 | - | 70 | 10590 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 4350 | - | 70 | 4540 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 7460 | - | 70 | 7780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 11190 | - | 70 | 11680 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 4350 | - | 70 | 4540 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.5 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9 | 3MXM24AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 9320 | - | 70 | 9730 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 9320 | - | 70 | 9730 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | 0.75 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 6900 | - | 70 | 7200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | 0.75 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 6900 | - | 70 | 7200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9200 | - | 70 | 9600 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 6270 | - | 70 | 6550 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | 0.75 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 6270 | - | 70 | 6550 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 10450 | - | 70 | 10910 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 5750 | - | 70 | 6000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | 0.75 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 5750 | - | 70 | 6000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 11500 | - | 70 | 12000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 6270 | - | 70 | 6550 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 8360 | - | 70 | 8730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 8360 | - | 70 | 8730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 5750 | - | 70 | 6000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 7670 | - | 70 | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 9580 | - | 70 | 10000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 5310 | - | 70 | 5540 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 7080 | - | 70 | 7380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 10620 | - | 70 | 11080 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 5310 | - | 70 | 5540 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 0.75 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9 | 3MXM24AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 8850 | - | 70 | 9230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 8850 | - | 70 | 9230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 392 | 80 | 67 | 7670 | - | 70 | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 1 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 3MXM24AVJU9 | FTXV12AVJU9 | 3MXM24AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 7670 | - | 70 | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 7670 | - | 70 | 8000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 7080 | - | 70 | 7380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 140 | 21.0 / 12.0 / 10.0 | 208/60/1 | 19.9 | 25 | 3MXM24AVJU9 | R32 | 230' Max System Piping |  | 2 | HEAT PUMP | 1 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 3MXM24AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT |  | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 3MXM24AVJU9 | FTXV12AVJU9 | 3MXM24AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 7080 | - | 70 | 7380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 8850 | - | 70 | 9230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | - | - | - | - | Wall Mounted | - | - | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 10300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 13300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | - | - | - | - | Wall Mounted | - | - | - | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 16600 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1.25 | - | - | - | - | Wall Mounted | - | - | - | - |  | 4MXM36AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 4MXM36AVJU9 | FTXV15AVJU9 | 4MXM36AVJU9 | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 19300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - |  | 4MXM36AVJU9 | FTXV18AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 | 4MXM36AVJU9 | FTXV18AVJU9 | 4MXM36AVJU9 | FTXV18AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 25300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 2 | - | - | - | - | Wall Mounted | - | - | - | - |  | 4MXM36AVJU9 | FTXV24AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 | 4MXM36AVJU9 | FTXV24AVJU9 | 4MXM36AVJU9 | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7570 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7480 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12820 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15890 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6970 | - | 70 | 7310 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 17930 | - | 70 | 18780 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6770 | - | 70 | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 629 | 80 | 67 | 23230 | - | 70 | 23770 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12740 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 8870 | - | 70 | 9200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 17730 | - | 70 | 18400 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 8650 | - | 70 | 8810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 23050 | - | 70 | 23490 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11820 | - | 70 | 12270 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 14780 | - | 70 | 15330 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 392 | 80 | 67 | 11640 | - | 70 | 12000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 17460 | - | 70 | 18000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 392 | 80 | 67 | 11400 | - | 70 | 11530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 22800 | - | 70 | 23070 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 540 | 80 | 67 | 14550 | - | 70 | 15000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1.25 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 4MXM36AVJU9 | FTXV15AVJU9 | 4MXM36AVJU9 | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 14550 | - | 70 | 15000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 14410 | - | 70 | 14680 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1.25 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 4MXM36AVJU9 | FTXV15AVJU9 | 4MXM36AVJU9 | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 17290 | - | 70 | 17620 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 540 | 80 | 67 | 13150 | - | 70 | 13310 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1.25 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 4MXM36AVJU9 | FTXV15AVJU9 | 4MXM36AVJU9 | FTXV15AVJU9
IDU- | 629 | 80 | 67 | 21050 | - | 70 | 21290 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 565 | 80 | 67 | 17100 | - | 70 | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1.5 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV18AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 | 4MXM36AVJU9 | FTXV18AVJU9 | 4MXM36AVJU9 | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 17100 | - | 70 | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 14660 | - | 70 | 14830 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1.5 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV18AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 | 4MXM36AVJU9 | FTXV18AVJU9 | 4MXM36AVJU9 | FTXV18AVJU9
IDU- | 629 | 80 | 67 | 19540 | - | 70 | 19770 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 629 | 80 | 67 | 17100 | - | 70 | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 2 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 4MXM36AVJU9 | FTXV24AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 | 4MXM36AVJU9 | FTXV24AVJU9 | 4MXM36AVJU9 | FTXV24AVJU9
IDU- | 629 | 80 | 67 | 17100 | - | 70 | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7430 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7430 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7430 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9510 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 6920 | - | 70 | 7240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6920 | - | 70 | 7240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 11860 | - | 70 | 12420 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 6830 | - | 70 | 7050 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6830 | - | 70 | 7050 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 14640 | - | 70 | 15100 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6740 | - | 70 | 6890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6740 | - | 70 | 6890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 17330 | - | 70 | 17720 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6300 | - | 70 | 6370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6300 | - | 70 | 6370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 629 | 80 | 67 | 21600 | - | 70 | 21850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 6970 | - | 70 | 9310 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8960 | - | 70 | 9400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8960 | - | 70 | 9400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8810 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 11740 | - | 70 | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 6770 | - | 70 | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8710 | - | 70 | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 14520 | - | 70 | 14850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6690 | - | 70 | 6810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8600 | - | 70 | 8760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 17210 | - | 70 | 17520 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5990 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7700 | - | 70 | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 20520 | - | 70 | 20760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 6770 | - | 70 | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 11610 | - | 70 | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11610 | - | 70 | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 6690 | - | 70 | 6810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 11470 | - | 70 | 11680 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 14340 | - | 70 | 14600 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6470 | - | 70 | 6880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 11090 | - | 70 | 11220 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 16640 | - | 70 | 16830 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5570 | - | 70 | 5630 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 9540 | - | 70 | 9660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 19090 | - | 70 | 19310 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 6470 | - | 70 | 6550 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 13860 | - | 70 | 14030 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 13860 | - | 70 | 14030 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5990 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 12830 | - | 70 | 12980 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 15390 | - | 70 | 15570 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5200 | - | 70 | 5270 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1.25 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 11150 | - | 70 | 11280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 629 | 80 | 67 | 17840 | - | 70 | 18050 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 5570 | - | 70 | 5630 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 14320 | - | 70 | 14480 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 14320 | - | 70 | 14480 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 8870 | - | 70 | 9200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8870 | - | 70 | 9200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8870 | - | 70 | 9200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8730 | - | 70 | 9000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8730 | - | 70 | 9000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 11640 | - | 70 | 12000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 8650 | - | 70 | 8810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8650 | - | 70 | 8810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 14410 | - | 70 | 14680 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 17100 | - | 70 | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 7330 | - | 70 | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7330 | - | 70 | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 19540 | - | 70 | 19770 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 8650 | - | 70 | 8810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 11530 | - | 70 | 11750 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11530 | - | 70 | 11750 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 11400 | - | 70 | 11530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 14250 | - | 70 | 14420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 7890 | - | 70 | 7980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10520 | - | 70 | 10650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 15780 | - | 70 | 15970 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 6840 | - | 70 | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9120 | - | 70 | 9230 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 18240 | - | 70 | 18450 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 7890 | - | 70 | 7980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 13150 | - | 70 | 13310 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 13150 | - | 70 | 13310 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 7330 | - | 70 | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 12210 | - | 70 | 12360 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 14660 | - | 70 | 14830 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 6410 | - | 70 | 6490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1.25 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 10690 | - | 70 | 10810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 629 | 80 | 67 | 1710 | - | 70 | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 6840 | - | 70 | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 13680 | - | 70 | 13840 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 13680 | - | 70 | 13840 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 392 | 80 | 67 | 11400 | - | 70 | 11530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11400 | - | 70 | 11530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11400 | - | 70 | 11530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10520 | - | 70 | 10650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10520 | - | 70 | 10650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 13150 | - | 70 | 13310 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 392 | 80 | 67 | 9770 | - | 70 | 9890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9770 | - | 70 | 9890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 14660 | - | 70 | 14830 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 392 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | 1 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 17100 | - | 70 | 17300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 392 | 80 | 67 | 9770 | - | 70 | 9890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 12210 | - | 70 | 12360 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 12210 | - | 70 | 12650 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 392 | 80 | 67 | 9120 | - | 70 | 9230 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 11400 | - | 70 | 11530 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 13680 | - | 70 | 13840 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 392 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 12830 | - | 70 | 12980 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 12860 | - | 70 | 12980 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 540 | 80 | 67 | 11400 | - | 70 | 11530 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1.25 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 4MXM36AVJU9 | FTXV15AVJU9 | 4MXM36AVJU9 | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 11400 | - | 70 | 11530 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 11400 | - | 70 | 11530 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 10690 | - | 70 | 10810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1.25 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 4MXM36AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 4MXM36AVJU9 | FTXV15AVJU9 | 4MXM36AVJU9 | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 10690 | - | 70 | 10810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 12830 | - | 70 | 11530 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6790 | - | 70 | 7000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6790 | - | 70 | 7000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6790 | - | 70 | 7000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8730 | - | 70 | 9000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 6720 | - | 70 | 6850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6720 | - | 70 | 6850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6720 | - | 70 | 6850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 11530 | - | 70 | 11750 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 6650 | - | 70 | 6730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6650 | - | 70 | 6730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6650 | - | 70 | 6760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 14250 | - | 70 | 14420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6140 | - | 70 | 6210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6140 | - | 70 | 6210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6140 | - | 70 | 6210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 15780 | - | 70 | 15970 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5320 | - | 70 | 5380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5320 | - | 70 | 5380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5320 | - | 70 | 5380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 629 | 80 | 67 | 18240 | - | 70 | 18450 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 6740 | - | 70 | 6890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6740 | - | 70 | 6890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8660 | - | 70 | 8860 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8660 | - | 70 | 8860 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 6680 | - | 70 | 6760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6680 | - | 70 | 6760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8590 | - | 70 | 8690 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 11450 | - | 70 | 11590 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 6300 | - | 70 | 6370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6300 | - | 70 | 6370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8100 | - | 70 | 8190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 13500 | - | 70 | 13660 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5840 | - | 70 | 5910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5840 | - | 70 | 5910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7510 | - | 70 | 7600 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 15010 | - | 70 | 15190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5090 | - | 70 | 5150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5090 | - | 70 | 5150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 6550 | - | 70 | 6630 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 17460 | - | 70 | 17670 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 6300 | - | 70 | 6370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6300 | - | 70 | 6370 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 10800 | - | 70 | 10930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10800 | - | 70 | 10930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 5840 | - | 70 | 5910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5840 | - | 70 | 5910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 10010 | - | 70 | 10130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 12510 | - | 70 | 12660 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5440 | - | 70 | 5500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5440 | - | 70 | 5500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 9330 | - | 70 | 9440 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 13990 | - | 70 | 14150 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5440 | - | 70 | 5500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5440 | - | 70 | 5500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 11660 | - | 70 | 11800 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 11660 | - | 70 | 11800 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5090 | - | 70 | 5150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.5 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5090 | - | 70 | 5150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 10910 | - | 70 | 11040 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 13100 | - | 70 | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6690 | - | 70 | 6810 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8600 | - | 70 | 8760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8600 | - | 70 | 8760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8600 | - | 70 | 8760 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 6470 | - | 70 | 6550 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8320 | - | 70 | 8420 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8320 | - | 70 | 8420 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 11090 | - | 70 | 11220 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 5990 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7700 | - | 70 | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7700 | - | 70 | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 12830 | - | 70 | 12980 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5570 | - | 70 | 8630 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7160 | - | 70 | 7240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7160 | - | 70 | 7240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 14320 | - | 70 | 14480 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5990 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7700 | - | 70 | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10260 | - | 70 | 10380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10260 | - | 70 | 10380 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 5570 | - | 70 | 560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7160 | - | 70 | 7240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9540 | - | 70 | 9660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 11930 | - | 70 | 12070 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5200 | - | 70 | 5270 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 6690 | - | 70 | 6770 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 8920 | - | 70 | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 13380 | - | 70 | 13540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5200 | - | 70 | 5270 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 0.75 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 6690 | - | 70 | 6770 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 11150 | - | 70 | 11280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 11150 | - | 70 | 11280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5570 | - | 70 | 5630 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 9540 | - | 70 | 9660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9540 | - | 70 | 9660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9540 | - | 70 | 9660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 5200 | - | 70 | 5270 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.5 | 1 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9 | 4MXM36AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 8920 | - | 70 | 9030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 8920 | - | 70 | 9030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 11150 | - | 70 | 11280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7890 | - | 70 | 7980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7890 | - | 70 | 7980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7890 | - | 70 | 7980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10520 | - | 70 | 10650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 7330 | - | 70 | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7330 | - | 70 | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7330 | - | 70 | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 12210 | - | 70 | 12360 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 6840 | - | 70 | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 6840 | - | 70 | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 6840 | - | 70 | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 13680 | - | 70 | 13840 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 7330 | - | 70 | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7330 | - | 70 | 7410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9770 | - | 70 | 9890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9770 | - | 70 | 9890 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 6840 | - | 70 | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 6840 | - | 70 | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9120 | - | 70 | 9230 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 11400 | - | 70 | 11530 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 6410 | - | 70 | 6490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 6410 | - | 70 | 6490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 12830 | - | 70 | 12980 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 6410 | - | 70 | 6490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 0.75 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 6410 | - | 70 | 6490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 10690 | - | 70 | 10810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 10690 | - | 70 | 10810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 6840 | - | 70 | 6920 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9120 | - | 70 | 9230 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9120 | - | 70 | 9230 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9120 | - | 70 | 9230 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 6410 | - | 70 | 6490 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 0.75 | 1 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9 | 4MXM36AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 10690 | - | 70 | 10810 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 392 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 142 | 20.0 / 10.0 / 9.5 | 208/60/1 | 24.1 | 25 | 4MXM36AVJU9 | R32 | 230' Max System Piping |  | 3 | HEAT PUMP | 1 | 1 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 4MXM36AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 2MXM 3MXM 4MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9 | 4MXM36AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 8550 | - | 70 | 8650 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8900 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | - | - | - | - | Wall Mounted | - | - | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 11500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 15300 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | - | - | - | - | Wall Mounted | - | - | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 19200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.25 | - | - | - | - | Wall Mounted | - | - | - | - |  | 5MXM48AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 23000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - |  | 5MXM48AVJU9 | FTXV18AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 | 5MXM48AVJU9 | FTXV18AVJU9 | 5MXM48AVJU9 | FTXV18AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 27400 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 2 | - | - | - | - | Wall Mounted | - | - | - | - |  | 5MXM48AVJU9 | FTXV24AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 | 5MXM48AVJU9 | FTXV24AVJU9 | 5MXM48AVJU9 | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8950 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8950 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 11480 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 14970 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 17660 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7870 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 20230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7320 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 25080 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 11500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 11500 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 10800 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 14400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 10280 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 17130 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9830 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 19670 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 24650 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 13700 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 13700 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 13110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 16390 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12680 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 19020 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 24400 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.25 | 1.25 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15410 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.25 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18490 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.25 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 24370 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.5 | 1.5 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV18AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 | 5MXM48AVJU9 | FTXV18AVJU9 | 5MXM48AVJU9 | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.5 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV18AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 | 5MXM48AVJU9 | FTXV18AVJU9 | 5MXM48AVJU9 | FTXV18AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 24340 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 629 | 80 | 67 | 23000 | - | 70 | 24250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 2 | 2 | - | - | - | Wall Mounted | Wall Mounted | - | - | - |  | 5MXM48AVJU9 | FTXV24AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 | 5MXM48AVJU9 | FTXV24AVJU9 | 5MXM48AVJU9 | FTXV24AVJU9
IDU- | 629 | 80 | 67 | 23000 | - | 70 | 24250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 8100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 10410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7750 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7750 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 13290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7480 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7480 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 16030 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7260 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7260 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18680 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 24380 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7870 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 10120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 10120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9740 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12990 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7320 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15680 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9160 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 24360 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7320 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12540 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12540 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18290 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 24280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15240 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15240 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18270 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1.25 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 24260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6570 | - | 70 | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1.5 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 16900 | - | 70 | 17820 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 629 | 80 | 67 | 22530 | - | 70 | 23760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 5850 | - | 70 | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 2 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 629 | 80 | 67 | 20070 | - | 70 | 21160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 629 | 80 | 67 | 20070 | - | 70 | 21160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9830 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9830 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9830 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9510 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9510 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12680 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15410 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18300 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 24340 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9250 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12330 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12330 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 24270 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 8630 | - | 70 | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1.25 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 14380 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 629 | 80 | 67 | 23000 | - | 70 | 24250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1.5 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 16240 | - | 70 | 17120 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 629 | 80 | 67 | 21650 | - | 70 | 22820 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 2 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 19370 | - | 70 | 20420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 629 | 80 | 67 | 19370 | - | 70 | 20420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1 | 1 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12200 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 23000 | - | 70 | 24250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 392 | 80 | 67 | 10820 | - | 70 | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1.25 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 13530 | - | 70 | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 629 | 80 | 67 | 21650 | - | 70 | 22820 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 17250 | - | 70 | 18190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 17250 | - | 70 | 18190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1.5 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 15330 | - | 70 | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 629 | 80 | 67 | 20440 | - | 70 | 21560 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.25 | 1.25 | 1.25 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 14380 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.25 | 1.25 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 14380 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 17250 | - | 70 | 18190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 540 | 80 | 67 | 12780 | - | 70 | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.25 | 1.25 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 12780 | - | 70 | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 629 | 80 | 67 | 20440 | - | 70 | 21560 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 540 | 80 | 67 | 13530 | - | 70 | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.25 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 16240 | - | 70 | 17120 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 16240 | - | 70 | 17120 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 540 | 80 | 67 | 12110 | - | 70 | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.25 | 1.5 | 2 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV15AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9 | 5MXM48AVJU9 | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 14530 | - | 70 | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 629 | 80 | 67 | 19370 | - | 70 | 20420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 565 | 80 | 67 | 15330 | - | 70 | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1.5 | 1.5 | 1.5 | - | - | Wall Mounted | Wall Mounted | Wall Mounted | - | - |  | 5MXM48AVJU9 | FTXV18AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 | 5MXM48AVJU9 | FTXV18AVJU9 | 5MXM48AVJU9 | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 15330 | - | 70 | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 15330 | - | 70 | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7400 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9510 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12330 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.5 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15250 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.6 | 208/60/2 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.7 | 208/60/3 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 629 | 80 | 67 | 24000 | - | 70 | 24270 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7260 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.8 | 208/60/4 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7260 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9340 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9340 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.9 | 208/60/5 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.10 | 208/60/6 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15240 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.11 | 208/60/7 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.12 | 208/60/8 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8810 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 23490 | - | 70 | 24260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.13 | 208/60/9 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.14 | 208/60/10 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15220 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.15 | 208/60/11 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6440 | - | 70 | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.16 | 208/60/12 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6440 | - | 70 | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 11040 | - | 70 | 11640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 22080 | - | 70 | 23280 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.17 | 208/60/13 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.18 | 208/60/14 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 14680 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 17620 | - | 70 | 18190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6080 | - | 70 | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.19 | 208/60/15 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1.25 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6080 | - | 70 | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 13020 | - | 70 | 13730 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 629 | 80 | 67 | 20830 | - | 70 | 21960 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 6440 | - | 70 | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.20 | 208/60/16 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6440 | - | 70 | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 16560 | - | 70 | 17460 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 16560 | - | 70 | 17460 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5750 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.21 | 208/60/17 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1.5 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5750 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 14790 | - | 70 | 15590 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 629 | 80 | 67 | 19710 | - | 70 | 20790 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.22 | 208/60/18 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9160 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9160 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9160 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.23 | 208/60/19 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.24 | 208/60/20 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.25 | 208/60/21 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6570 | - | 70 | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.26 | 208/60/22 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8450 | - | 70 | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8450 | - | 70 | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 22530 | - | 70 | 23760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.27 | 208/60/23 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.28 | 208/60/24 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.29 | 208/60/25 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.30 | 208/60/26 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7960 | - | 70 | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10620 | - | 70 | 11190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 21230 | - | 70 | 22380 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.31 | 208/60/27 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6570 | - | 70 | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.32 | 208/60/28 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8450 | - | 70 | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 14080 | - | 70 | 14850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 16900 | - | 70 | 17820 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5850 | - | 70 | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.33 | 208/60/29 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1.25 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7530 | - | 70 | 7940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 12550 | - | 70 | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 629 | 80 | 67 | 20070 | - | 70 | 21160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.34 | 208/60/30 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7960 | - | 70 | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 15920 | - | 70 | 16790 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 15920 | - | 70 | 16790 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5550 | - | 70 | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.35 | 208/60/31 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1.5 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7140 | - | 70 | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 14280 | - | 70 | 15050 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 629 | 80 | 67 | 19030 | - | 70 | 20070 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.36 | 208/60/32 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.37 | 208/60/33 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6570 | - | 70 | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.38 | 208/60/34 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 11270 | - | 70 | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11270 | - | 70 | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 16900 | - | 70 | 17820 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5850 | - | 70 | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.39 | 208/60/35 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 10040 | - | 70 | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10040 | - | 70 | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 20070 | - | 70 | 21160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 6570 | - | 70 | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.40 | 208/60/36 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 11270 | - | 70 | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 14080 | - | 70 | 14850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 14080 | - | 70 | 14850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.41 | 208/60/37 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 10620 | - | 70 | 11190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 13270 | - | 70 | 13990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 15920 | - | 70 | 16790 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5550 | - | 70 | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.42 | 208/60/38 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1.25 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 9520 | - | 70 | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 11900 | - | 70 | 12540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 629 | 80 | 67 | 19030 | - | 70 | 20070 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 5850 | - | 70 | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.43 | 208/60/39 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 10040 | - | 70 | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 15050 | - | 70 | 15870 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 15050 | - | 70 | 15870 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.44 | 208/60/40 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1.25 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 13270 | - | 70 | 13990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 13270 | - | 70 | 13990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 13270 | - | 70 | 13990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5850 | - | 70 | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.45 | 208/60/41 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1.25 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 12550 | - | 70 | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 12550 | - | 70 | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 15050 | - | 70 | 15870 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5550 | - | 70 | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.46 | 208/60/42 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1.25 | 1.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 11900 | - | 70 | 12540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 14280 | - | 70 | 15050 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 14280 | - | 70 | 15050 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.47 | 208/60/43 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 0.75 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.48 | 208/60/44 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.49 | 208/60/45 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15210 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.50 | 208/60/46 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.51 | 208/60/47 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 21650 | - | 70 | 22820 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.52 | 208/60/48 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.53 | 208/60/49 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 8630 | - | 70 | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.54 | 208/60/50 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8630 | - | 70 | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 17250 | - | 70 | 18190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.55 | 208/60/51 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 20440 | - | 70 | 21560 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 8630 | - | 70 | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.56 | 208/60/52 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8630 | - | 70 | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 14380 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 14380 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.57 | 208/60/53 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 13530 | - | 70 | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 16240 | - | 70 | 17120 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.58 | 208/60/54 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1.25 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 12110 | - | 70 | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 629 | 80 | 67 | 19370 | - | 70 | 20420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.59 | 208/60/55 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 15330 | - | 70 | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 15330 | - | 70 | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.60 | 208/60/56 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 8630 | - | 70 | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.61 | 208/60/57 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 14380 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.62 | 208/60/58 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10820 | - | 70 | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10820 | - | 70 | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 16240 | - | 70 | 17120 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.63 | 208/60/59 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | 1 | 2 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 19370 | - | 70 | 20420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.64 | 208/60/60 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10820 | - | 70 | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 13530 | - | 70 | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 13530 | - | 70 | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.65 | 208/60/61 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 12780 | - | 70 | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 15330 | - | 70 | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.66 | 208/60/62 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | 1.5 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 14530 | - | 70 | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 14530 | - | 70 | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.67 | 208/60/63 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1.25 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 12780 | - | 70 | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 12780 | - | 70 | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 12780 | - | 70 | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.68 | 208/60/64 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1.25 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 12110 | - | 70 | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 12110 | - | 70 | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 14530 | - | 70 | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.69 | 208/60/65 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1 | 1 | 1 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10820 | - | 70 | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.70 | 208/60/66 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1 | 1 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10820 | - | 70 | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10820 | - | 70 | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 13530 | - | 70 | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.71 | 208/60/67 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1 | 1 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 15330 | - | 70 | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.72 | 208/60/68 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 12780 | - | 70 | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 12780 | - | 70 | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.73 | 208/60/69 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1 | 1.25 | 1.5 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 12110 | - | 70 | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 14530 | - | 70 | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/70 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 1 | 1.25 | 1.25 | 1.25 | - | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | - |  | 5MXM48AVJU9 | FTXV12AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9 | 5MXM48AVJU9 | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 12110 | - | 70 | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 12110 | - | 70 | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 12110 | - | 70 | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7120 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.5 | 0.75 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9150 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.5 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12180 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.5 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.5 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 18000 | - | 70 | 18200 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.5 | 2 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 629 | 80 | 67 | 21230 | - | 70 | 22380 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.75 | 0.75 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7110 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.75 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.75 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 15000 | - | 70 | 15170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6710 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.75 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6710 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6710 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8630 | - | 70 | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 17250 | - | 70 | 18190 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5960 | - | 70 | 6290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 0.75 | 2 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5960 | - | 70 | 6290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5960 | - | 70 | 6290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 20440 | - | 70 | 21560 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 6710 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6710 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6710 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 14380 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6310 | - | 70 | 6660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6310 | - | 70 | 6660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6310 | - | 70 | 6660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 10820 | - | 70 | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 16240 | - | 70 | 17120 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5650 | - | 70 | 5960 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1 | 2 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5650 | - | 70 | 5960 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5650 | - | 70 | 5960 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 629 | 80 | 67 | 19370 | - | 70 | 20420 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 6310 | - | 70 | 6660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1.25 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6310 | - | 70 | 6660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6310 | - | 70 | 6660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 13530 | - | 70 | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 13530 | - | 70 | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5960 | - | 70 | 6290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1.25 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5960 | - | 70 | 6290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5960 | - | 70 | 6290 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 540 | 80 | 67 | 12780 | - | 70 | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 15330 | - | 70 | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5650 | - | 70 | 5960 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.5 | 1.5 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5650 | - | 70 | 5960 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5650 | - | 70 | 5960 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 565 | 80 | 67 | 14530 | - | 70 | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 565 | 80 | 67 | 14530 | - | 70 | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 0.75 | 0.75 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 0.75 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12140 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 0.75 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8810 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8810 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 14680 | - | 70 | 15160 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6440 | - | 70 | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 0.75 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6440 | - | 70 | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8280 | - | 70 | 8730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8280 | - | 70 | 8730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 16560 | - | 70 | 17460 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5750 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 0.75 | 2 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5750 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7390 | - | 70 | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7390 | - | 70 | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 19710 | - | 70 | 20790 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6850 | - | 70 | 7070 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8810 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 11740 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11740 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 6440 | - | 70 | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6440 | - | 70 | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8280 | - | 70 | 8730 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 11040 | - | 70 | 11640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 13800 | - | 70 | 14550 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6080 | - | 70 | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 1 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6080 | - | 70 | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7810 | - | 70 | 8240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10420 | - | 70 | 10980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 15620 | - | 70 | 16470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6080 | - | 70 | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 1.25 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6080 | - | 70 | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7810 | - | 70 | 8240 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 13020 | - | 70 | 13730 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 13020 | - | 70 | 13730 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5750 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 0.75 | 1.25 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5750 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7390 | - | 70 | 7790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 12320 | - | 70 | 12990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 14790 | - | 70 | 15590 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6440 | - | 70 | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6440 | - | 70 | 6790 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 11040 | - | 70 | 11640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11040 | - | 70 | 11640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11040 | - | 70 | 11640 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 6080 | - | 70 | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 6080 | - | 70 | 6410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 10420 | - | 70 | 10980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10420 | - | 70 | 10980 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 13020 | - | 70 | 13730 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5750 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1 | 1 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5750 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 9860 | - | 70 | 10390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9860 | - | 70 | 10390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 14790 | - | 70 | 15590 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5750 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.5 | 1 | 1.25 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 332 | 80 | 67 | 5750 | - | 70 | 6060 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | [26 empty] | CTXV07AVJU9 |  |  |  | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 |  | CTXV07AVJU9 |  | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 9860 | - | 70 | 10390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 12320 | - | 70 | 12990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 12320 | - | 70 | 12990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 0.75 | 0.75 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 332 | 80 | 67 | 7000 | - | 70 | 7080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 0.75 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 12000 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 6570 | - | 70 | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 0.75 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8450 | - | 70 | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8450 | - | 70 | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8450 | - | 70 | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 14080 | - | 70 | 14850 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 0.75 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7960 | - | 70 | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7960 | - | 70 | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7960 | - | 70 | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 15920 | - | 70 | 16790 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5550 | - | 70 | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 0.75 | 2 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7140 | - | 70 | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7140 | - | 70 | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7140 | - | 70 | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 629 | 80 | 67 | 19030 | - | 70 | 20070 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV24AVJU9 | [26 empty] | FTXV24AVJU9 |  |  |  | IM - FTXV24AVJU9 | OM - FTXV24AVJU9 |  | FTXV24AVJU9 |  | FTXV24AVJU9
IDU- | 332 | 80 | 67 | 6570 | - | 70 | 6930 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 8450 | - | 70 | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8450 | - | 70 | 8910 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 11270 | - | 70 | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 11270 | - | 70 | 11880 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7960 | - | 70 | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7960 | - | 70 | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10620 | - | 70 | 11190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 13270 | - | 70 | 13990 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5850 | - | 70 | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 1 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7530 | - | 70 | 7940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7530 | - | 70 | 7940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10040 | - | 70 | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 15050 | - | 70 | 15870 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5850 | - | 70 | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 1.25 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7530 | - | 70 | 7940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7530 | - | 70 | 7940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 12550 | - | 70 | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 12550 | - | 70 | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5550 | - | 70 | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 0.75 | 1.25 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7140 | - | 70 | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7140 | - | 70 | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 11900 | - | 70 | 12540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 565 | 80 | 67 | 14280 | - | 70 | 15050 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 6190 | - | 70 | 6530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7960 | - | 70 | 8390 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10620 | - | 70 | 11190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10620 | - | 70 | 11190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10620 | - | 70 | 11190 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 5850 | - | 70 | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7530 | - | 70 | 7940 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10040 | - | 70 | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10040 | - | 70 | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 12550 | - | 70 | 13230 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5550 | - | 70 | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1 | 1 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7140 | - | 70 | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9520 | - | 70 | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9520 | - | 70 | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 14280 | - | 70 | 15050 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 332 | 80 | 67 | 5550 | - | 70 | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 0.75 | 1 | 1.25 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 381 | 80 | 67 | 7140 | - | 70 | 7530 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9520 | - | 70 | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 11900 | - | 70 | 12540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 11900 | - | 70 | 12540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 332 | 80 | 67 | 5850 | - | 70 | 6170 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 10040 | - | 70 | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10040 | - | 70 | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10040 | - | 70 | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10040 | - | 70 | 10580 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 332 | 80 | 67 | 5550 | - | 70 | 5850 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | CTXV07AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.5 | 1 | 1 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | CTXV07AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - CTXV07AVJU9 | OM - CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9 | 5MXM48AVJU9 | CTXV07AVJU9
IDU- | 392 | 80 | 67 | 9520 | - | 70 | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9520 | - | 70 | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9520 | - | 70 | 10030 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 11900 | - | 70 | 12540 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 9000 | - | 70 | 9100 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8630 | - | 70 | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 0.75 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8630 | - | 70 | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8630 | - | 70 | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8630 | - | 70 | 9090 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 11500 | - | 70 | 12130 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 0.75 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 13530 | - | 70 | 14260 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 0.75 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 565 | 80 | 67 | 15330 | - | 70 | 16170 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 8120 | - | 70 | 8560 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10820 | - | 70 | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10820 | - | 70 | 11410 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 12780 | - | 70 | 13470 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 1 | 1.5 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 565 | 80 | 67 | 14530 | - | 70 | 15320 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV18AVJU9 | [26 empty] | FTXV18AVJU9 |  |  |  | IM - FTXV18AVJU9 | OM - FTXV18AVJU9 |  | FTXV18AVJU9 |  | FTXV18AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 0.75 | 1.25 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 540 | 80 | 67 | 12110 | - | 70 | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 540 | 80 | 67 | 12110 | - | 70 | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7670 | - | 70 | 8080 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 10220 | - | 70 | 10780 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 0.75 | 1 | 1 | 1.25 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | [26 empty] | FTXV09AVJU9 |  |  |  | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 |  | FTXV09AVJU9 |  | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 540 | 80 | 67 | 12110 | - | 70 | 12760 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV15AVJU9 | [26 empty] | FTXV15AVJU9 |  |  |  | IM - FTXV15AVJU9 | OM - FTXV15AVJU9 |  | FTXV15AVJU9 |  | FTXV15AVJU9
IDU- | 381 | 80 | 67 | 7260 | - | 70 | 7660 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV09AVJU9 | ODU- | 95 | 47 | 219 | 20.0 / 10.0 / 9.74 | 208/60/1 | 38.1 | 40 | 5MXM48AVJU9 | R32 | 262' Max System Piping |  | 4 | HEAT PUMP | 0.75 | 1 | 1 | 1 | 1 | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted | Wall Mounted |  | 5MXM48AVJU9 | FTXV09AVJU9 | ENGINEERING MANUAL - MXM MULTI SPLIT | CAPACITY TABLE - MXM MULTI SPLIT | IM - 5MXM | IM - FTXV09AVJU9 | OM - FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9 | 5MXM48AVJU9 | FTXV09AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
IDU- | 392 | 80 | 67 | 9680 | - | 70 | 10210 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | FTXV12AVJU9 | [26 empty] | FTXV12AVJU9 |  |  |  | IM - FTXV12AVJU9 | OM - FTXV12AVJU9 |  | FTXV12AVJU9 |  | FTXV12AVJU9
ACCESSORIES:
A
B
C
D
E
F
G
H
I
J
K
L
M
N
O
P
Q
R
S
T
U
V
W
X
Y
Z