## MINI SPLIT
SPLIT SYSTEM UNIT
AIR HANDLING UNIT | [12 empty] | OUTDOOR CONDENSING UNIT |  |  | SINGLE POINT POWER (TO OUTDOOR UNIT*)
UNIT NO. | MANUFACTURER & MODEL # | SERVES | SUPPLY - FAN DATA |  | COOLING CAPACITY |  |  | HEATING CAPACITY |  | EFFICIENCY | INDOOR UNIT ELECTRICAL DATA* |  | GENERAL DATA |  |  | ELECTRICAL DATA
|  |  | TOTAL CFM | MIN O.A CFM | TOTAL (btuh) | E. DB (F) | E. WB (F) | TOTAL (btuh) | AMBIENT (F) | SEER | V0LT/PH | MCA/MOCP | UNIT NO. | MANUFACTURER & M0DEL | WEIGHT (LBS) | VOLT/PH | MCA/MOP
AHU-1 | DAIKIN FTKF09BVJU9 | IT ROOM | 322 | 0 | 11200 | 80 | 67 | N/A | N/A | 21 | 208/1 | 11.6/15 | CU-1 | DAIKIN RKF09BVJU9 | 68 | 208/1 | 21.4/25
AHU-2 | DAIKIN FTXF09BVJU9 | IT ROOM | 381 | 0 | 11200 | 80 | 67 | 16000 | 47 | 21 | 208/1 | 11.6/15 | CU-2 | DAIKIN RXF09BVJU9 | 68 | 208/1 | 11.6/15
* POWER IS SINGLE POINT CONNECTION TO BE MADE TO OUTDOOR CONDENSING UNIT. POWER FROM CONDENSING UNIT SHALL BE PROVIDED TO INDOOR UNIT. FOLLOW MANUFACTURER'S INSTALLATION INSTRUCTIONS. PROVIDE DISCONNECT AT INDOOR AND OUTDOOR LOCATION. UNIT SHALL BE SUPPLIED WITH ALL PROVISIONS NECESARY FOR LOW AMBIENT COOLING. PROVIDE INTEGRAL CONDENSATE PUMP.

## RTU
ROOFTOP PACKAGED AR HANDING UNTS
TAG: |  | RTU-1 | RTU-2
MANUFACTURER: |  | DAIKIN | DAIKIN
UNIT MODEL NUMBER: |  | DHG0484DM | DHG0604DM
WEIGHT: |  | LBS | LBS
| NOTES | 1,2,3,4,5,6,8 | 1,2,3,4,5,6
| SUPPLY CFM | 1600 | 2100
| SUPPLY FAN HP | 1.2 | 1.2
| EXTERNAL STATIC PRESSURE (IN. OF WATER) | 0.5 | 0.5
| NOMINAL CAPACITY (TONS) | 4 | 5
| GROSS TOT COOLING CAP. (BTU/h) | 46683 | 60037
| EFFICIENCY | 16.4 SEER2/12.2 EER2 | 16.2 SEER2/12.2 EER2
| COOLING STAGES | 2 | 2
| INPUT HEA1NG CAP. (MBH) - NAT. GAS | 115 | 115
| OUTPUT HEATINC CAP. (MBH) | 93.15 | 93.15
HEATING STAGES
| VOLTAGE/PHASE | 460/3 | 460/3
| SINGLE POINT ELEC. CONN. MCA(A)/M0P(A) | 10.7/15 | 13.3/20
| SEISMIC IMPORTANCE FACTOR (IP) | 1.5 | 1.5
NOTES-
1. PROVIDE FACTORY ROOF CURB.
2. R-32 REFRIGERANT
3. PROVIDE TWO POSITION OUTSIDE AIR DAMPER, POWERED CLOSED WHEN UNIT IS OFF
4. PROVIDE 2" PLEATED FILTERS
5. PROVIDE PROGRAMMABLE THERMOSTAT
6. PROVIDE A WATER LEVEL DETECTION DEVICE CONFORMING TO UL508 TO SHUT OFF
THE EQUIPMENT IN THE EVENT THAT THE PRIMARY DRAIN IS BLOCKED
7. PROVIDE DRY BULB ECONOMIZER, POWERED CLOSED WHEN UNIT IS OFF.
8. PROVIDE HOT GAS REHEAT DEHUMIDIFICATION
ACCEPTABLE MANUFACTURERS: 1. TRANE 4. DAIKIN 2. CARRIER 5. TEMPMASTER