## RTU
PACKAGED ROOFTOP UNIT SCHEDULE
I.D. | SUPPLY | EXT. SP | MOTOR | BOD TOTAL | BOD SENSIBLE | AMBIENT | COIL EAT |  | HEATING |  |  |  |  | EER | SEER2/ | COP (47°F)/(17°F) | VOLTS/ | MCA | MOCP | BASIS OF DESIGN | APPROX. | REMARKS
TAG | AIRFLOW (CFM) | (IN. WC) (1) | HP | CAPACITY (MBH) | CAPACITY (MBH) | TEMP (°F) | °F db | °F wb | TYPE | GAS INPUT | GAS OUTPUT | HEAT PUMP BTU/h (47°F, 70°F Indoor DB) | HEAT PUMP BTU/h (17°F, 70°F Indoor DB) |  | IEER |  | PHASE |  |  |  | WEIGHT (LBS)
RTU-1 | 1655 | 0.5 | 1 | 46.202 | 36.218 | 95 | 80 | 67 | GAS | 70 | 56 | - | - | 11.8 | 13.7 | - | 208/3 | 24.1 | 35 | DAIKIN DSG0483DL | 548
RTU-2 | 2090 | 0.5 | 1 | 58.474 | 45.127 | 95 | 80 | 67 | GAS | 90 | 72 | - | - | 11.8 | 13.7 | - | 208/3 | 28.1 | 40 | DAIKIN DSG0603DL | 537
RTU-3 | 2400 | 0.5 | 1.2 | 69.967 | 55.179 | 95 | 80 | 67 | HEAT PUMP | - | - | 62000 | - | 12 | 17.2 | 3.5/2.4 | 460/3 | 12.2 | 15 | DAIKIN DHH0724 | 708
RTU-4 | 8401 | 0.5 | 3.5 | 230.2 | 177.254 | 95 | 80 | 67 | HEAT PUMP | - | - | 220000 | 122000 | 10.6 | 14.35 | 3.3/2.05 | 208/3 | 98.7 | 125 | DAIKIN DSH2403 | 2354
(1) THIS IS THE SP EXTERNAL TO THE ENTIRE UNIT ASSEMBLY (WET COIL, CASING, CLEAN FILTERS, AND FURNACE LOSSES ARE NOT INCLUDED IN THIS EXTERNAL SP).
(2) HEAT PUMP CAPACITY RATED AT 17°F.
(3) PROVIDE WITH POWERED GFI OUTLET. COORD. WITH DIV. 26.
(4) PROVIDE WITH INTEGRAL DISCONNECT. COORD. WITH DIV. 26.
(5) PROVIDE SMOKE DETECTORS RETURN DUCTWORK FOR AUTOMATIC SHUTDOWN IN COMPLIANCE WITH NFPA 72. DETECTORS SHALL BE SUPPLIED BY DIV. 26 AND INSTALLED BY DIV. 23.
(6) PROVIDE WITH 7-DAY PROGRAMMABLE TSTAT OR INTERLOCK TO BAS.
(7) PROVIDE UNIT WITH DIFFERENTIAL-ENTHALPY ECONOMIZER AND BAROMETRIC RELIEF.
(8) PROVIDE UNIT WITH DIFFERENTIAL-ENTHALPY ECONOMIZER AND POWERED EXHAUST
(9) PROVIDE WITH HOT GAS REHEAT AND SPACE-MOUNTED TEMPERATURE/HUMIDITY SENSOR.
(10) PROVIDE UNIT WITH PLENUM RETURN CURB.
(11) PROVIDE WITH ECM SUPPLY FAN
(12) PROVIDE WITH MODULATING OUTSIDE AIR DAMPER, INTERLOCKED TO SPACE-MOUNTED CO2 SENSOR FOR DEMAND CONTROL VENTILATION SEQUENCE.
(13) FOR ALL HEALTHCARE APPLICATIONS OUTSIDE AIR INTAKE SHALL BE A MINIMUM OF 36" ABOVE THE ADJACENT ROOF. PROVIDE WITH EXTENDED HEIGHT CURB AS REQUIRED.

## MULTI POSITION SPLIT
SPLIT SYSTEM SCHEDULE
|  |  | FAN COIL UNIT DATA | [8 empty] | HEATING SECTION |  |  |  | CONDENSING UNIT DATA
I.D. TAG | MINIMUM TOTAL CAP. (BTUH) | MINIMUM SENSIBLE CAP. (BTUH) | AIRFLOW (CFM) | OUTSIDE AIR (CFM) | EXT. S.P. (IN. W.C.) ① | MAX H.P. | COIL | EAT | VOLTS/ PHASE | DRIVE ② | TYPE OF UNIT | PRIMARY HEATING |  | SECONDARY HEATING |  | AMBIENT TEMP.(F) | VOLTS/ PHASE | STAGES | EFFICIENCY | BASIS OF DESIGN | REMARKS
[7 empty] | ° F db | °F wb |  |  |  | TYPE | CAPACITY③ | TYPE | CAPACITY③
AHU-1/CU-1 | 18000 | 14040 | 620 | - | 0.5 | 0.75 | 80 | 67 | 208/1 | D | MULTI-POSITION AHU | HP | 17.3 MBH | ELEC | 5 | 95 | 208/1 | 1 | 15.2/12.5 (SEER2/EER2) | DAIKIN DH4SEA1810/AMST24BU1300 | ① ② ③ ④ ⑤ ⑥ ⑦
AHU-2/CU-2 | 34400 | 26144 | 1170 | - | 0.5 | 0.75 | 80 | 67 | 208/1 | D | MULTI-POSITION AHU | - | - | ELEC | 8 | 95 | 208/1 | 1 | 14.5/12.0 (SEER2/EER2) | DAIKIN DC4SEA3610/AMST36CU1300 | ① ② ③ ④ ⑤ ⑥ ⑦
① THIS IS THE SP EXTERNAL TO THE ENTIRE FAN COIL UNIT ASSEMBLY (WET COIL, CASING, CLEAN FILTERS, AND FURNACE LOSSES ARE NOT INCLUDED IN THIS EXT. SP.)
② B = BELT DRIVE, D = DIRECT
③ HP STANDS FOR HEAT PUMP AND CAPACITY IS GIVEN IN MBH, ELEC STANDS FOR ELECTRIC HEAT AND VALUES ARE GIVEN IN kW.
④ PROVIDE WITH REMOTE WALL MOUNTED THERMOSTAT LOCATED AS SHOWN ON PLANS.
⑤ PROVIDE AIR HANDLER WITH VARIABLE SPEED ECM FAN.
⑥ CONDENSATE IS TO BE CONNECTED INTO EXISTING CONDENSATE DRAIN FROM EXISTING UNITS BEING REPLACED.
⑦ BLOWER COIL UNIT SHALL BE ENCOMPASSED BY A DRAIN PAN AND ALSO CONSIST OF A FLOAT SWITCH LOCATED IN DRAIN PAN TO DISABLE UNIT UNDER WATER DETECTION.