## SCHEDULE
SCHEDULE RANGE | [31 empty] | FILTERS | [6 empty] | DOCUMENTATION
PACKAGED ROOFTOP UNITS | [31 empty] | SIZE | ELECTRICAL | TYPE | EFFICIENCY | COOLING STAGES | HIGH/MEDIUM/LOW GAS HEAT | HGRH | SUBMITTAL (OUTDOOR UNIT) | SUBMITTAL (INDOOR UNIT) | SUBMITTAL (SYSTEM) | ENGINEERING MANUAL (SYSTEM) | ENGINEERING MANUAL (OUTDOOR UNIT) | ENGINEERING MANUAL (INDOOR UNIT) | CAPACITY TABLE | INSTALLATION MANUAL (OUTDOOR) | INSTALLATION MANUAL (INDOOR) | INSTALLATION MANUAL (SYSTEM) | REVIT (OUTDOOR) | REVIT (INDOOR) | REVIT (SYSTEM) | CAD (OUTDOOR) | CAD (INDOOR) | CAD (SYSTEM) | CONTROLS OPTIONS | OPERATION MANUAL
Make | Model Number | Nominal Tons | Fan Data |  | Cooling Performance | [6 empty] | Gas Heating Performance |  |  |  |  | Heat Pump Heating Performance | [5 empty] | Aux. Electric Heat |  | Modulating Hot Gas Reheat | Cooling Stages | Electrical Data |  |  |  | Weight (lbs)
|  |  | CFM | ESP (IWG) | Total Capacity (BTU/h) | Sensible Capacity (BTU/h) | Efficiency (At AHRI) | EDB (°F) | EWB (°F) | LDB (°F) | LWB (°F) | Input (MBH) | Output (MBH) | Stages | EAT (°F) | LAT (°F) | BTU/h (47°F, 70°F Indoor DB) | BTU/h (17°F, 70°F Indoor DB) | BTU/h (70°F Indoor DB) | Temperature Rise (°F) | COP (47°F) | COP (17°F) | kW | Temperature Rise (°F) |  |  | VOLT/PH | Indoor Motor HP | Unit MCA | Unit MOCP
DAIKIN | DSG0363DM | 3 | 1265 | 0.5 | 35418 | 27395 | 14.0 SEER2/12.0 EER2 | 80 | 67 | 60.3 | 58.2 | 70 | 56 | 2 | 55 | 96 | - | - | - |  | - | - | - | - | NO | 1 | 208/3 | 0.75 | 19.9 | 30 | 517 | 3 | 208/3 | GAS | STANDARD | 1 | MEDIUM | NO |  |  | DSG0363DM | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0363DM |  |  | DSG0363DM
DAIKIN | DSG0363DL | 3 | 1265 | 0.5 | 35418 | 27395 | 14.0 SEER2/12.0 EER2 | 80 | 67 | 60.3 | 58.2 | 45 | 36 | 2 | 55 | 81.4 | - | - | - |  | - | - | - | - | NO | 1 | 208/3 | 0.75 | 19.9 | 30 | 517 | 3 | 208/3 | GAS | STANDARD | 1 | LOW | NO |  |  | DSG0363DL | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0363DL |  |  | DSG0363DL
DAIKIN | DSG0363DH | 3 | 1265 | 0.5 | 35418 | 27395 | 14.0 SEER2/12.0 EER2 | 80 | 67 | 60.3 | 58.2 | 90 | 72 | 2 | 55 | 107.7 | - | - | - |  | - | - | - | - | NO | 1 | 208/3 | 0.75 | 19.9 | 30 | 517 | 3 | 208/3 | GAS | STANDARD | 1 | HIGH | NO |  |  | DSG0363DH | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0363DH |  |  | DSG0363DH
DAIKIN | DSG0364DL | 3 | 1265 | 0.5 | 35418 | 27395 | 14.0 SEER2/12.0 EER2 | 80 | 67 | 60.3 | 58.2 | 45 | 36 | 2 | 55 | 81.4 | - | - | - |  | - | - | - | - | NO | 1 | 460/3 | 1.2 | 9.1 | 15 | 520 | 3 | 460/3 | GAS | STANDARD | 1 | LOW | NO |  |  | DSG0364DL | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0364DL |  |  | DSG0364DL
DAIKIN | DSG0364DM | 3 | 1265 | 0.5 | 35418 | 27395 | 14.0 SEER2/12.0 EER2 | 80 | 67 | 60.3 | 58.2 | 70 | 56 | 2 | 55 | 96 | - | - | - |  | - | - | - | - | NO | 1 | 460/3 | 1.2 | 9.1 | 15 | 520 | 3 | 460/3 | GAS | STANDARD | 1 | MEDIUM | NO |  |  | DSG0364DM | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0364DM |  |  | DSG0364DM
DAIKIN | DSG0364DH | 3 | 1265 | 0.5 | 35418 | 27395 | 14.0 SEER2/12.0 EER2 | 80 | 67 | 60.3 | 58.2 | 90 | 72 | 2 | 55 | 107.7 | - | - | - |  | - | - | - | - | NO | 1 | 460/3 | 1.2 | 9.1 | 15 | 520 | 3 | 460/3 | GAS | STANDARD | 1 | HIGH | NO |  |  | DSG0364DH | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0364DH |  |  | DSG0364DH
DAIKIN | DHG0363DL | 3 | 1267 | 0.5 | 35471 | 28816 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 59.3 | 58.2 | 45 | 36.45 | 2 | 55 | 81.3 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 0.75 | 18.1 | 25 | 572 | 3 | 208/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG0363DL | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0363DL |  |  | DHG0363DL
DAIKIN | DHG0363DM | 3 | 1267 | 0.5 | 35471 | 28816 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 59.3 | 58.2 | 70 | 56.7 | 2 | 55 | 95.9 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 0.75 | 18.1 | 25 | 572 | 3 | 208/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG0363DM | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0363DM |  |  | DHG0363DM
DAIKIN | DHG0363DH | 3 | 1747 | 0.5 | 36499 | 32119 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 63.3 | 60.6 | 115 | 93.15 | 2 | 55 | 103.8 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 0.75 | 18.1 | 25 | 572 | 3 | 208/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG0363DH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0363DH |  |  | DHG0363DH
DAIKIN | DHG0364DL | 3 | 1392 | 0.5 | 36022 | 30588 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 60 | 58.9 | 45 | 36.45 | 2 | 55 | 78.9 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 8.2 | 15 | 572 | 3 | 460/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG0364DL | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0364DL |  |  | DHG0364DL
DAIKIN | DHG0364DM | 3 | 1392 | 0.5 | 36022 | 30588 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 60 | 58.9 | 70 | 56.7 | 2 | 55 | 92.2 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 8.2 | 15 | 572 | 3 | 460/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG0364DM | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0364DM |  |  | DHG0364DM
DAIKIN | DHG0364DH | 3 | 1392 | 0.5 | 36022 | 30588 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 60 | 58.9 | 115 | 93.15 | 2 | 55 | 116.2 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 8.2 | 15 | 572 | 3 | 460/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG0364DH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0364DH |  |  | DHG0364DH
DAIKIN | DSG0483DL | 4 | 1655 | 0.5 | 46202 | 36218 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.1 | 58.2 | 70 | 56 | 2 | 55 | 86.3 | - | - | - |  | - | - | - | - | NO | 1 | 208/3 | 1 | 24.1 | 35 | 548 | 4 | 208/3 | GAS | STANDARD | 1 | LOW | NO |  |  | DSG0483DL | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0483DL |  |  | DSG0483DL
DAIKIN | DSG0483DM | 4 | 1655 | 0.5 | 46202 | 36218 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.1 | 58.2 | 90 | 72 | 2 | 55 | 95.3 | - | - | - |  | - | - | - | - | NO | 1 | 208/3 | 1 | 24.1 | 35 | 548 | 4 | 208/3 | GAS | STANDARD | 1 | MEDIUM | NO |  |  | DSG0483DM | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0483DM |  |  | DSG0483DM
DAIKIN | DSG0483DH | 4 | 1655 | 0.5 | 46202 | 36218 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.1 | 58.2 | 115 | 92 | 2 | 55 | 106.5 | - | - | - |  | - | - | - | - | NO | 1 | 208/3 | 1 | 24.1 | 35 | 548 | 4 | 208/3 | GAS | STANDARD | 1 | HIGH | NO |  |  | DSG0483DH | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0483DH |  |  | DSG0483DH
DAIKIN | DSG0484DL | 4 | 1660 | 0.5 | 46221 | 36291 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.1 | 58.3 | 70 | 56 | 2 | 55 | 86.2 | - | - | - |  | - | - | - | - | NO | 1 | 460/3 | 1.2 | 10.6 | 15 | 552 | 4 | 460/3 | GAS | STANDARD | 1 | LOW | NO |  |  | DSG0484DL | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0484DL |  |  | DSG0484DL
DAIKIN | DSG0484DM | 4 | 1660 | 0.5 | 46221 | 36291 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.1 | 58.3 | 90 | 72 | 2 | 55 | 95.2 | - | - | - |  | - | - | - | - | NO | 1 | 460/3 | 1.2 | 10.6 | 15 | 552 | 4 | 460/3 | GAS | STANDARD | 1 | MEDIUM | NO |  |  | DSG0484DM | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0484DM |  |  | DSG0484DM
DAIKIN | DSG0484DH | 4 | 1660 | 0.5 | 46221 | 36291 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.1 | 58.3 | 115 | 92 | 2 | 55 | 106.3 | - | - | - |  | - | - | - | - | NO | 1 | 460/3 | 1.2 | 10.6 | 15 | 552 | 4 | 460/3 | GAS | STANDARD | 1 | HIGH | NO |  |  | DSG0484DH | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0484DH |  |  | DSG0484DH
DAIKIN | DHG0483DL | 4 | 1672 | 0.5 | 47034 | 37846 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.4 | 58.2 | 70 | 56.7 | 2 | 55 | 86 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 1 | 22.8 | 30 | 647 | 4 | 208/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG0483DL | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0483DL |  |  | DHG0483DL
DAIKIN | DHG0483DM | 4 | 1660 | 0.5 | 46976 | 37683 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.4 | 58.1 | 115 | 93.15 | 2 | 55 | 106.3 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 1 | 22.8 | 30 | 647 | 4 | 208/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG0483DM | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0483DM |  |  | DHG0483DM
DAIKIN | DHG0483DH | 4 | 1692 | 0.5 | 47132 | 38119 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.5 | 58.3 | 140 | 113.4 | 2 | 55 | 116.3 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 1 | 22.8 | 30 | 647 | 4 | 208/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG0483DH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0483DH |  |  | DHG0483DH
DAIKIN | DHG0484DL | 4 | 1692 | 0.5 | 47132 | 38119 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.5 | 58.3 | 70 | 56.7 | 2 | 55 | 85.6 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 10.7 | 15 | 647 | 4 | 460/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG0484DL | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0484DL |  |  | DHG0484DL
DAIKIN | DHG0484DM | 4 | 1660 | 0.5 | 46976 | 37683 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.4 | 58.1 | 115 | 93.15 | 2 | 55 | 106.3 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 10.7 | 15 | 647 | 4 | 460/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG0484DM | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0484DM |  |  | DHG0484DM
DAIKIN | DHG0484DH | 4 | 1692 | 0.5 | 47132 | 38119 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.5 | 58.3 | 140 | 113.4 | 2 | 55 | 116.3 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 10.7 | 15 | 647 | 4 | 460/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG0484DH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0484DH |  |  | DHG0484DH
DAIKIN | DSG0603DL | 5 | 2090 | 0.5 | 58474 | 45127 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.4 | 58.2 | 90 | 72 | 2 | 55 | 86.9 | - | - | - |  | - | - | - | - | NO | 1 | 208/3 | 1 | 28.1 | 40 | 537 | 5 | 208/3 | GAS | STANDARD | 1 | LOW | NO |  |  | DSG0603DL | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0603DL |  |  | DSG0603DL
DAIKIN | DSG0603DM | 5 | 2090 | 0.5 | 58474 | 45127 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.4 | 58.2 | 115 | 92 | 2 | 55 | 95.8 | - | - | - |  | - | - | - | - | NO | 1 | 208/3 | 1 | 28.1 | 40 | 537 | 5 | 208/3 | GAS | STANDARD | 1 | MEDIUM | NO |  |  | DSG0603DM | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0603DM |  |  | DSG0603DM
DAIKIN | DSG0603DH | 5 | 2090 | 0.5 | 58474 | 45127 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.4 | 58.2 | 140 | 112 | 2 | 55 | 104.6 | - | - | - |  | - | - | - | - | NO | 1 | 208/3 | 1 | 28.1 | 40 | 537 | 5 | 208/3 | GAS | STANDARD | 1 | HIGH | NO |  |  | DSG0603DH | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0603DH |  |  | DSG0603DH
DAIKIN | DSG0604DL | 5 | 2115 | 0.5 | 58580 | 45470 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.5 | 58.3 | 90 | 72 | 2 | 55 | 86.5 | - | - | - |  | - | - | - | - | NO | 1 | 460/3 | 1.2 | 13 | 20 | 541 | 5 | 460/3 | GAS | STANDARD | 1 | LOW | NO |  |  | DSG0604DL | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0604DL |  |  | DSG0604DL
DAIKIN | DSG0604DM | 5 | 2115 | 0.5 | 58580 | 45470 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.5 | 58.3 | 115 | 92 | 2 | 55 | 95.3 | - | - | - |  | - | - | - | - | NO | 1 | 460/3 | 1.2 | 13 | 20 | 541 | 5 | 460/3 | GAS | STANDARD | 1 | MEDIUM | NO |  |  | DSG0604DM | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0604DM |  |  | DSG0604DM
DAIKIN | DSG0604DH | 5 | 2115 | 0.5 | 58580 | 45470 | 13.7 SEER2/11.8 EER2 | 80 | 67 | 60.5 | 58.3 | 140 | 112 | 2 | 55 | 104 | - | - | - |  | - | - | - | - | NO | 1 | 460/3 | 1.2 | 13 | 20 | 541 | 5 | 460/3 | GAS | STANDARD | 1 | HIGH | NO |  |  | DSG0604DH | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0604DH |  |  | DSG0604DH
DAIKIN | DHG0603DL | 5 | 2022 | 0.5 | 59669 | 44976 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 59.8 | 57.7 | 70 | 56.7 | 2 | 55 | 80.6 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 1 | 28.5 | 40 | 655 | 5 | 208/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG0603DL | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0603DL |  |  | DHG0603DL
DAIKIN | DHG0603DM | 5 | 2022 | 0.5 | 59669 | 44976 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 59.8 | 57.7 | 115 | 93.15 | 2 | 55 | 97.1 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 1 | 28.5 | 40 | 655 | 5 | 208/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG0603DM | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0603DM |  |  | DHG0603DM
DAIKIN | DHG0603DH | 5 | 2022 | 0.5 | 59669 | 44976 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 59.8 | 57.7 | 140 | 113.4 | 2 | 55 | 106.3 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 1 | 28.5 | 40 | 655 | 5 | 208/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG0603DH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0603DH |  |  | DHG0603DH
DAIKIN | DHG0604DL | 5 | 2045 | 0.5 | 59777 | 45285 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 59.9 | 57.8 | 70 | 56.7 | 2 | 55 | 80.4 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 13.3 | 20 | 655 | 5 | 460/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG0604DL | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0604DL |  |  | DHG0604DL
DAIKIN | DHG0604DM | 5 | 2045 | 0.5 | 59777 | 45285 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 59.9 | 57.8 | 115 | 93.15 | 2 | 55 | 96.7 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 13.3 | 20 | 655 | 5 | 460/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG0604DM | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0604DM |  |  | DHG0604DM
DAIKIN | DHG0604DH | 5 | 2045 | 0.5 | 59777 | 45285 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 59.9 | 57.8 | 140 | 113.4 | 2 | 55 | 105.7 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 13.3 | 20 | 655 | 5 | 460/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG0604DH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0604DH |  |  | DHG0604DH
DAIKIN | DSG0723DL | 6 | 2235 | 0.5 | 69644 | 49347 | 16.7 IEER/11.8 EER | 80 | 67 | 59.9 | 57.1 | 90 | 72 | 2 | 55 | 84.8 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 1.2 | 27.2 | 40 | 626 | 6 | 208/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG0723DL | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0723DL |  |  | DSG0723DL
DAIKIN | DSG0723DM | 6 | 2235 | 0.5 | 69644 | 49347 | 16.7 IEER/11.8 EER | 80 | 67 | 59.9 | 57.1 | 115 | 92 | 2 | 55 | 93.1 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 1.2 | 27.2 | 40 | 626 | 6 | 208/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG0723DM | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0723DM |  |  | DSG0723DM
DAIKIN | DSG0723DH | 6 | 2235 | 0.5 | 69644 | 49347 | 16.7 IEER/11.8 EER | 80 | 67 | 59.9 | 57.1 | 140 | 112 | 2 | 55 | 101.4 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 1.2 | 27.2 | 40 | 626 | 6 | 208/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG0723DH | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0723DH |  |  | DSG0723DH
DAIKIN | DSG0724DL | 6 | 2235 | 0.5 | 69644 | 49347 | 16.7 IEER/11.8 EER | 80 | 67 | 59.9 | 57.1 | 90 | 72 | 2 | 55 | 84.8 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 12.2 | 15 | 626 | 6 | 460/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG0724DL | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0724DL |  |  | DSG0724DL
DAIKIN | DSG0724DM | 6 | 2235 | 0.5 | 69644 | 49347 | 16.7 IEER/11.8 EER | 80 | 67 | 59.9 | 57.1 | 115 | 92 | 2 | 55 | 93.1 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 12.2 | 15 | 626 | 6 | 460/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG0724DM | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0724DM |  |  | DSG0724DM
DAIKIN | DSG0724DH | 6 | 2235 | 0.5 | 69644 | 49347 | 16.7 IEER/11.8 EER | 80 | 67 | 59.9 | 57.1 | 140 | 112 | 2 | 55 | 101.4 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 12.2 | 15 | 626 | 6 | 460/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG0724DH | ENGINEERING MANUAL - DSG (3-6) | [5 empty] | INSTALLATION MANUAL - DSG (3-6) |  |  | DSG0724DH |  |  | DSG0724DH
DAIKIN | DHG0723DL | 6 | 2250 | 0.5 | 69506 | 53078 | 18.6 IEER/12.5 EER | 80 | 67 | 58.5 | 57.2 | 70 | 56.7 | 2 | 55 | 78 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 1.2 | 27.2 | 40 | 705 | 6 | 208/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG0723DL | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0723DL |  |  | DHG0723DL
DAIKIN | DHG0723DM | 6 | 2250 | 0.5 | 69506 | 53078 | 18.6 IEER/12.5 EER | 80 | 67 | 58.5 | 57.2 | 125 | 101.25 | 2 | 55 | 96.2 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 1.2 | 27.2 | 40 | 705 | 6 | 208/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG0723DM | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0723DM |  |  | DHG0723DM
DAIKIN | DHG0723DH | 6 | 2250 | 0.5 | 69506 | 53078 | 18.6 IEER/12.5 EER | 80 | 67 | 58.5 | 57.2 | 150 | 121.5 | 2 | 55 | 104.4 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 1.2 | 27.2 | 40 | 705 | 6 | 208/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG0723DH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0723DH |  |  | DHG0723DH
DAIKIN | DHG0724DL | 6 | 2250 | 0.5 | 69506 | 53078 | 18.6 IEER/12.5 EER | 80 | 67 | 58.5 | 57.2 | 70 | 56.7 | 2 | 55 | 78 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 12.2 | 15 | 705 | 6 | 460/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG0724DL | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0724DL |  |  | DHG0724DL
DAIKIN | DHG0724DM | 6 | 2250 | 0.5 | 69506 | 53078 | 18.6 IEER/12.5 EER | 80 | 67 | 58.5 | 57.2 | 125 | 101.25 | 2 | 55 | 96.2 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 12.2 | 15 | 705 | 6 | 460/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG0724DM | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0724DM |  |  | DHG0724DM
DAIKIN | DHG0724DH | 6 | 2250 | 0.5 | 69506 | 53078 | 18.6 IEER/12.5 EER | 80 | 67 | 58.5 | 57.2 | 150 | 121.5 | 2 | 55 | 104.4 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 12.2 | 15 | 705 | 6 | 460/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG0724DH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0724DH |  |  | DHG0724DH
DAIKIN | DSG0903DL | 7.5 | 3082 | 0.5 | 90314 | 68535 | 16.0 IEER/12.0 EER | 80 | 67 | 59.8 | 57.8 | 130 | 105.3 | 2 | 55 | 86.2 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 39.4 | 50 | 1106 | 7.5 | 208/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG0903DL | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG0903DL |  |  | DSG0903DL
DAIKIN | DSG0903DM | 7.5 | 3101 | 0.5 | 90388 | 68775 | 16.0 IEER/12.0 EER | 80 | 67 | 59.8 | 57.8 | 180 | 145.8 | 2 | 55 | 98 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 39.4 | 50 | 1106 | 7.5 | 208/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG0903DM | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG0903DM |  |  | DSG0903DM
DAIKIN | DSG0903DH | 7.5 | 3023 | 0.5 | 90087 | 67789 | 16.0 IEER/12.0 EER | 80 | 67 | 59.6 | 57.6 | 225 | 182.25 | 2 | 55 | 110.1 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 39.4 | 50 | 1106 | 7.5 | 208/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG0903DH | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG0903DH |  |  | DSG0903DH
DAIKIN | DSG0904DL | 7.5 | 3082 | 0.5 | 90314 | 68535 | 16.0 IEER/12.0 EER | 80 | 67 | 59.8 | 57.8 | 130 | 105.3 | 2 | 55 | 86.2 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 20.1 | 25 | 1106 | 7.5 | 460/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG0904DL | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG0904DL |  |  | DSG0904DL
DAIKIN | DSG0904DM | 7.5 | 3101 | 0.5 | 90388 | 68775 | 16.0 IEER/12.0 EER | 80 | 67 | 59.8 | 57.8 | 180 | 145.8 | 2 | 55 | 98 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 20.1 | 25 | 1106 | 7.5 | 460/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG0904DM | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG0904DM |  |  | DSG0904DM
DAIKIN | DSG0904DH | 7.5 | 3023 | 0.5 | 90087 | 67789 | 16.0 IEER/12.0 EER | 80 | 67 | 59.6 | 57.6 | 225 | 182.25 | 2 | 55 | 110.1 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 20.1 | 25 | 1106 | 7.5 | 460/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG0904DH | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG0904DH |  |  | DSG0904DH
DAIKIN | DHG0903DL | 7.5 | 3146 | 0.5 | 90561 | 72417 | 17.5 IEER/12.5 EER | 80 | 67 | 59.1 | 57.9 | 130 | 105.3 | 2 | 55 | 85.6 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 39.4 | 50 | 1253 | 7.5 | 208/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG0903DL | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG0903DL |  |  | DHG0903DL
DAIKIN | DHG0903DM | 7.5 | 3024 | 0.5 | 90091 | 70563 | 17.5 IEER/12.5 EER | 80 | 67 | 58.8 | 57.6 | 180 | 145.8 | 2 | 55 | 99.1 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 39.4 | 50 | 1253 | 7.5 | 208/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG0903DM | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG0903DM |  |  | DHG0903DM
DAIKIN | DHG0903DH | 7.5 | 3000 | 0.5 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 225 | 182.25 | 2 | 55 | 110.6 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 39.4 | 50 | 1253 | 7.5 | 208/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG0903DH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG0903DH |  |  | DHG0903DH
DAIKIN | DHG0904DL | 7.5 | 3146 | 0.5 | 90561 | 72417 | 17.5 IEER/12.5 EER | 80 | 67 | 59.1 | 57.9 | 130 | 105.3 | 2 | 55 | 85.6 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 20.1 | 25 | 1253 | 7.5 | 460/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG0904DL | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG0904DL |  |  | DHG0904DL
DAIKIN | DHG0904DM | 7.5 | 3024 | 0.5 | 90091 | 70563 | 17.5 IEER/12.5 EER | 80 | 67 | 58.8 | 57.6 | 180 | 145.8 | 2 | 55 | 99.1 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 20.1 | 25 | 1253 | 7.5 | 460/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG0904DM | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG0904DM |  |  | DHG0904DM
DAIKIN | DHG0904DH | 7.5 | 3000 | 0.5 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 225 | 182.25 | 2 | 55 | 110.6 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 20.1 | 25 | 1253 | 7.5 | 460/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG0904DH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG0904DH |  |  | DHG0904DH
DAIKIN | DSG1023DL | 8.5 | 3459 | 0.5 | 98063 | 75041 | 15.5 IEER/11.4 EER | 80 | 67 | 60.3 | 58.1 | 130 | 105.3 | 2 | 55 | 82.8 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 43.7 | 50 | 1118 | 8.5 | 208/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG1023DL | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1023DL |  |  | DSG1023DL
DAIKIN | DSG1023DM | 8.5 | 3440 | 0.5 | 97985 | 74802 | 15.5 IEER/11.4 EER | 80 | 67 | 60.2 | 58 | 180 | 145.8 | 2 | 55 | 93.8 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 43.7 | 50 | 1118 | 8.5 | 208/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG1023DM | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1023DM |  |  | DSG1023DM
DAIKIN | DSG1023DH | 8.5 | 3444 | 0.5 | 98001 | 74853 | 15.5 IEER/11.4 EER | 80 | 67 | 60.2 | 58 | 225 | 182.25 | 2 | 55 | 103.4 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 43.7 | 50 | 1118 | 8.5 | 208/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG1023DH | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1023DH |  |  | DSG1023DH
DAIKIN | DSG1024DL | 8.5 | 3459 | 0.5 | 98063 | 75041 | 15.5 IEER/11.4 EER | 80 | 67 | 60.3 | 58.1 | 130 | 105.3 | 2 | 55 | 82.8 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 21.5 | 25 | 1118 | 8.5 | 460/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG1024DL | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1024DL |  |  | DSG1024DL
DAIKIN | DSG1024DM | 8.5 | 3440 | 0.5 | 97985 | 74802 | 15.5 IEER/11.4 EER | 80 | 67 | 60.2 | 58 | 180 | 145.8 | 2 | 55 | 93.8 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 21.5 | 25 | 1118 | 8.5 | 460/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG1024DM | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1024DM |  |  | DSG1024DM
DAIKIN | DSG1024DH | 8.5 | 3444 | 0.5 | 98001 | 74853 | 15.5 IEER/11.4 EER | 80 | 67 | 60.2 | 58 | 225 | 182.25 | 2 | 55 | 103.4 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 21.5 | 25 | 1118 | 8.5 | 460/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG1024DH | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1024DH |  |  | DSG1024DH
DAIKIN | DHG1023DL | 8.5 | 3632 | 0.5 | 104616 | 80554 | 17.5 IEER/12.5 EER | 80 | 67 | 59.8 | 57.9 | 130 | 105.3 | 2 | 55 | 81.5 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 43.7 | 50 | 1268 | 8.5 | 208/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG1023DL | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1023DL |  |  | DHG1023DL
DAIKIN | DHG1023DM | 8.5 | 3632 | 0.5 | 104616 | 80554 | 17.5 IEER/12.5 EER | 80 | 67 | 59.8 | 57.9 | 180 | 145.8 | 2 | 55 | 91.7 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 43.7 | 50 | 1268 | 8.5 | 208/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG1023DM | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1023DM |  |  | DHG1023DM
DAIKIN | DHG1023DH | 8.5 | 3632 | 0.5 | 104616 | 80554 | 17.5 IEER/12.5 EER | 80 | 67 | 59.8 | 57.9 | 225 | 182.25 | 2 | 55 | 100.9 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 43.7 | 50 | 1268 | 8.5 | 208/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG1023DH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1023DH |  |  | DHG1023DH
DAIKIN | DHG1024DL | 8.5 | 3632 | 0.5 | 104616 | 80554 | 17.5 IEER/12.5 EER | 80 | 67 | 59.8 | 57.9 | 130 | 105.3 | 2 | 55 | 81.5 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 21.5 | 25 | 1268 | 8.5 | 460/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG1024DL | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1024DL |  |  | DHG1024DL
DAIKIN | DHG1024DM | 8.5 | 3632 | 0.5 | 104616 | 80554 | 17.5 IEER/12.5 EER | 80 | 67 | 59.8 | 57.9 | 180 | 145.8 | 2 | 55 | 91.7 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 21.5 | 25 | 1268 | 8.5 | 460/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG1024DM | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1024DM |  |  | DHG1024DM
DAIKIN | DHG1024DH | 8.5 | 3632 | 0.5 | 104616 | 80554 | 17.5 IEER/12.5 EER | 80 | 67 | 59.8 | 57.9 | 225 | 182.25 | 2 | 55 | 100.9 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 21.5 | 25 | 1268 | 8.5 | 460/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG1024DH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1024DH |  |  | DHG1024DH
DAIKIN | DSG1203DL | 10 | 4060 | 0.5 | 119122 | 92915 | 15.2 IEER/11.4 EER | 80 | 67 | 59.2 | 57.7 | 130 | 105.3 | 2 | 55 | 78.7 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 53.8 | 70 | 1161 | 10 | 208/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG1203DL | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1203DL |  |  | DSG1203DL
DAIKIN | DSG1203DM | 10 | 4052 | 0.5 | 119122 | 92915 | 15.2 IEER/11.4 EER | 80 | 67 | 59.1 | 57.7 | 180 | 145.8 | 2 | 55 | 87.9 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 53.8 | 70 | 1161 | 10 | 208/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG1203DM | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1203DM |  |  | DSG1203DM
DAIKIN | DSG1203DH | 10 | 4051 | 0.5 | 119122 | 92915 | 15.2 IEER/11.4 EER | 80 | 67 | 59.1 | 57.7 | 240 | 194.4 | 2 | 55 | 98.9 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 53.8 | 70 | 1161 | 10 | 208/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG1203DH | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1203DH |  |  | DSG1203DH
DAIKIN | DSG1204DL | 10 | 4060 | 0.5 | 119122 | 92915 | 14.8 IEER/11.2 EER | 80 | 67 | 59.2 | 57.7 | 130 | 105.3 | 2 | 55 | 78.7 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 26.2 | 30 | 1161 | 10 | 460/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG1204DL | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1204DL |  |  | DSG1204DL
DAIKIN | DSG1204DM | 10 | 4052 | 0.5 | 119122 | 92915 | 14.8 IEER/11.2 EER | 80 | 67 | 59.1 | 57.7 | 180 | 145.8 | 2 | 55 | 87.9 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 26.2 | 30 | 1161 | 10 | 460/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG1204DM | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1204DM |  |  | DSG1204DM
DAIKIN | DSG1204DH | 10 | 4051 | 0.5 | 119122 | 92915 | 14.8 IEER/11.2 EER | 80 | 67 | 59.1 | 57.7 | 240 | 194.4 | 2 | 55 | 98.9 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 26.2 | 30 | 1161 | 10 | 460/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG1204DH | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1204DH |  |  | DSG1204DH
DAIKIN | DHG1203DL | 10 | 3955 | 0.5 | 118027 | 82891 | 17 IEER/12.5 EER | 80 | 67 | 60.9 | 57.6 | 130 | 105.3 | 2 | 55 | 79.3 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 46.6 | 60 | 1296 | 10 | 208/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG1203DL | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1203DL |  |  | DHG1203DL
DAIKIN | DHG1203DM | 10 | 4018 | 0.5 | 118308 | 83767 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 180 | 145.8 | 2 | 55 | 88.2 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 46.6 | 60 | 1296 | 10 | 208/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG1203DM | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1203DM |  |  | DHG1203DM
DAIKIN | DHG1203DH | 10 | 4018 | 0.5 | 118308 | 83767 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 240 | 194.4 | 2 | 55 | 99.2 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 2.4 | 46.6 | 60 | 1296 | 10 | 208/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG1203DH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1203DH |  |  | DHG1203DH
DAIKIN | DHG1204DL | 10 | 3955 | 0.5 | 118027 | 82891 | 17 IEER/12.5 EER | 80 | 67 | 60.9 | 57.6 | 130 | 105.3 | 2 | 55 | 79.3 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 24.4 | 30 | 1296 | 10 | 460/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG1204DL | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1204DL |  |  | DHG1204DL
DAIKIN | DHG1204DM | 10 | 4018 | 0.5 | 118308 | 83767 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 180 | 145.8 | 2 | 55 | 88.2 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 24.4 | 30 | 1296 | 10 | 460/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG1204DM | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1204DM |  |  | DHG1204DM
DAIKIN | DHG1204DH | 10 | 4018 | 0.5 | 118308 | 83767 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 240 | 194.4 | 2 | 55 | 99.2 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 2.4 | 24.4 | 30 | 1296 | 10 | 460/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG1204DH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1204DH |  |  | DHG1204DH
DAIKIN | DSG1503DL | 12.5 | 4549 | 0.5 | 141535 | 104491 | 15.2 IEER/11.4 EER | 80 | 67 | 59.1 | 57.1 | 130 | 105.3 | 2 | 55 | 76.2 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 59.5 | 70 | 1244 | 12.5 | 208/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG1503DL | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1503DL |  |  | DSG1503DL
DAIKIN | DSG1503DM | 12.5 | 4350 | 0.5 | 140660 | 101588 | 15.2 IEER/11.4 EER | 80 | 67 | 58.7 | 56.7 | 180 | 145.8 | 2 | 55 | 85.7 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 59.5 | 70 | 1244 | 12.5 | 208/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG1503DM | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1503DM |  |  | DSG1503DM
DAIKIN | DSG1503DH | 12.5 | 4213 | 0.5 | 140057 | 99589 | 15.2 IEER/11.4 EER | 80 | 67 | 58.5 | 56.4 | 240 | 194.4 | 2 | 55 | 97.2 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 59.5 | 70 | 1244 | 12.5 | 208/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG1503DH | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1503DH |  |  | DSG1503DH
DAIKIN | DSG1504DL | 12.5 | 4549 | 0.5 | 141535 | 104491 | 15.2 IEER/11.4 EER | 80 | 67 | 59.1 | 57.1 | 130 | 105.3 | 2 | 55 | 76.2 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 30.2 | 35 | 1244 | 12.5 | 460/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG1504DL | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1504DL |  |  | DSG1504DL
DAIKIN | DSG1504DM | 12.5 | 4350 | 0.5 | 140660 | 101588 | 15.2 IEER/11.4 EER | 80 | 67 | 58.7 | 56.7 | 180 | 145.8 | 2 | 55 | 85.7 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 30.2 | 35 | 1244 | 12.5 | 460/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG1504DM | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1504DM |  |  | DSG1504DM
DAIKIN | DSG1504DH | 12.5 | 4213 | 0.5 | 140057 | 99589 | 15.2 IEER/11.4 EER | 80 | 67 | 58.5 | 56.4 | 240 | 194.4 | 2 | 55 | 97.2 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 30.2 | 35 | 1244 | 12.5 | 460/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG1504DH | ENGINEERING MANUAL - DSG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSG (7.5-12.5) |  |  | DSG1504DH |  |  | DSG1504DH
DAIKIN | DHG1503DL | 12.5 | 4522 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.1 | 57.1 | 130 | 105.3 | 2 | 55 | 76.3 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 61.1 | 80 | 1310 | 12.5 | 208/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG1503DL | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1503DL |  |  | DHG1503DL
DAIKIN | DHG1503DM | 12.5 | 4522 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.1 | 57.1 | 180 | 145.8 | 2 | 55 | 84.5 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 61.1 | 80 | 1310 | 12.5 | 208/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG1503DM | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1503DM |  |  | DHG1503DM
DAIKIN | DHG1503DH | 12.5 | 4522 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.1 | 57.1 | 240 | 194.4 | 2 | 55 | 94.3 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 61.1 | 80 | 1310 | 12.5 | 208/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG1503DH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1503DH |  |  | DHG1503DH
DAIKIN | DHG1504DL | 12.5 | 4522 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.1 | 57.1 | 130 | 105.3 | 2 | 55 | 76.3 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 30.6 | 35 | 1310 | 12.5 | 460/3 | GAS | HIGH | 2 | LOW | NO |  |  | DHG1504DL | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1504DL |  |  | DHG1504DL
DAIKIN | DHG1504DM | 12.5 | 4522 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.1 | 57.1 | 180 | 145.8 | 2 | 55 | 84.5 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 30.6 | 35 | 1310 | 12.5 | 460/3 | GAS | HIGH | 2 | MEDIUM | NO |  |  | DHG1504DM | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1504DM |  |  | DHG1504DM
DAIKIN | DHG1504DH | 12.5 | 4522 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.1 | 57.1 | 240 | 194.4 | 2 | 55 | 94.3 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 30.6 | 35 | 1310 | 12.5 | 460/3 | GAS | HIGH | 2 | HIGH | NO |  |  | DHG1504DH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1504DH |  |  | DHG1504DH
DAIKIN | DSG1803DL | 15 | 6338 | 0.5 | 176600 | 143046 | 14 IEER/10.8 EER | 80 | 67 | 59.5 | 58.3 | 260 | 210.6 | 2 | 55 | 85.4 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 84.1 | 100 | 1922 | 15 | 208/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG1803DL | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG1803DL |  |  | DSG1803DL
DAIKIN | DSG1803DM | 15 | 6328 | 0.5 | 176600 | 143046 | 14 IEER/10.8 EER | 80 | 67 | 59.5 | 58.2 | 360 | 291.6 | 2 | 55 | 97.1 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 84.1 | 100 | 1922 | 15 | 208/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG1803DM | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG1803DM |  |  | DSG1803DM
DAIKIN | DSG1803DH | 15 | 6344 | 0.5 | 176600 | 143046 | 14 IEER/10.8 EER | 80 | 67 | 59.5 | 58.3 | 400 | 324 | 2 | 55 | 101.7 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 84.1 | 100 | 1922 | 15 | 208/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG1803DH | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG1803DH |  |  | DSG1803DH
DAIKIN | DSG1804DL | 15 | 6338 | 0.5 | 176600 | 143046 | 14 IEER/10.8 EER | 80 | 67 | 59.5 | 58.3 | 260 | 210.6 | 2 | 55 | 85.4 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 41.4 | 50 | 1922 | 15 | 460/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG1804DL | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG1804DL |  |  | DSG1804DL
DAIKIN | DSG1804DM | 15 | 6328 | 0.5 | 176600 | 143046 | 14 IEER/10.8 EER | 80 | 67 | 59.5 | 58.2 | 360 | 291.6 | 2 | 55 | 97.1 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 41.4 | 50 | 1922 | 15 | 460/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG1804DM | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG1804DM |  |  | DSG1804DM
DAIKIN | DSG1804DH | 15 | 6344 | 0.5 | 176600 | 143046 | 14 IEER/10.8 EER | 80 | 67 | 59.5 | 58.3 | 400 | 324 | 2 | 55 | 101.7 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 41.4 | 50 | 1922 | 15 | 460/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG1804DH | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG1804DH |  |  | DSG1804DH
DAIKIN | DSG2403DL | 20 | 8177 | 0.5 | 238125 | 185737 | 14 IEER/10.8 EER | 80 | 67 | 59.3 | 57.8 | 260 | 210.6 | 2 | 55 | 78.6 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 98.7 | 125 | 2175 | 20 | 208/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG2403DL | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG2403DL |  |  | DSG2403DL
DAIKIN | DSG2403DM | 20 | 8272 | 0.5 | 238125 | 185737 | 14 IEER/10.8 EER | 80 | 67 | 59.6 | 57.9 | 360 | 291.6 | 2 | 55 | 87.2 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 98.7 | 125 | 2175 | 20 | 208/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG2403DM | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG2403DM |  |  | DSG2403DM
DAIKIN | DSG2403DH | 20 | 8035 | 0.5 | 238125 | 185737 | 14 IEER/10.8 EER | 80 | 67 | 59 | 57.6 | 400 | 324 | 2 | 55 | 91.9 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 3.5 | 98.7 | 125 | 2175 | 20 | 208/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG2403DH | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG2403DH |  |  | DSG2403DH
DAIKIN | DSG2404DL | 20 | 8177 | 0.5 | 238125 | 185737 | 14 IEER/10.8 EER | 80 | 67 | 59.3 | 57.8 | 260 | 210.6 | 2 | 55 | 78.6 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 50.8 | 60 | 2175 | 20 | 460/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG2404DL | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG2404DL |  |  | DSG2404DL
DAIKIN | DSG2404DM | 20 | 8272 | 0.5 | 238125 | 185737 | 14 IEER/10.8 EER | 80 | 67 | 59.6 | 57.9 | 360 | 291.6 | 2 | 55 | 87.2 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 50.8 | 60 | 2175 | 20 | 460/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG2404DM | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG2404DM |  |  | DSG2404DM
DAIKIN | DSG2404DH | 20 | 8035 | 0.5 | 238125 | 185737 | 14 IEER/10.8 EER | 80 | 67 | 59 | 57.6 | 400 | 324 | 2 | 55 | 91.9 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 3.5 | 50.8 | 60 | 2175 | 20 | 460/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG2404DH | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG2404DH |  |  | DSG2404DH
DAIKIN | DSG3003DL | 25 | 10056 | 0.5 | 303155 | 227366 | 13 IEER/9.8 EER | 80 | 67 | 59.4 | 57.5 | 260 | 210.6 | 2 | 55 | 74.2 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 5 | 151 | 175 | 2316 | 25 | 208/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG3003DL | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG3003DL |  |  | DSG3003DL
DAIKIN | DSG3003DM | 25 | 10056 | 0.5 | 303155 | 227366 | 13 IEER/9.8 EER | 80 | 67 | 59.4 | 57.5 | 360 | 291.6 | 2 | 55 | 81.5 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 5 | 151 | 175 | 2316 | 25 | 208/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG3003DM | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG3003DM |  |  | DSG3003DM
DAIKIN | DSG3003DH | 25 | 10056 | 0.5 | 303155 | 227366 | 13 IEER/9.8 EER | 80 | 67 | 59.4 | 57.5 | 400 | 324 | 2 | 55 | 84.5 | - | - | - |  | - | - | - | - | NO | 2 | 208/3 | 5 | 151 | 175 | 2316 | 25 | 208/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG3003DH | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG3003DH |  |  | DSG3003DH
DAIKIN | DSG3004DL | 25 | 10056 | 0.5 | 303155 | 227366 | 13 IEER/9.8 EER | 80 | 67 | 59.4 | 57.5 | 260 | 210.6 | 2 | 55 | 74.2 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 5 | 74.3 | 90 | 2316 | 25 | 460/3 | GAS | STANDARD | 2 | LOW | NO |  |  | DSG3004DL | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG3004DL |  |  | DSG3004DL
DAIKIN | DSG3004DM | 25 | 10056 | 0.5 | 303155 | 227366 | 13 IEER/9.8 EER | 80 | 67 | 59.4 | 57.5 | 360 | 291.6 | 2 | 55 | 81.5 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 5 | 74.3 | 90 | 2316 | 25 | 460/3 | GAS | STANDARD | 2 | MEDIUM | NO |  |  | DSG3004DM | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG3004DM |  |  | DSG3004DM
DAIKIN | DSG3004DH | 25 | 10056 | 0.5 | 303155 | 227366 | 13 IEER/9.8 EER | 80 | 67 | 59.4 | 57.5 | 400 | 324 | 2 | 55 | 84.5 | - | - | - |  | - | - | - | - | NO | 2 | 460/3 | 5 | 74.3 | 90 | 2316 | 25 | 460/3 | GAS | STANDARD | 2 | HIGH | NO |  |  | DSG3004DH | ENGINEERING MANUAL - DSG (15-25) | [5 empty] | INSTALLATION MANUAL - DSG (15-25) |  |  | DSG3004DH |  |  | DSG3004DH
DAIKIN | DHG0363DL | 3 | 1200 | 0.5 | 35176 | 27866 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 58.9 | 57.8 | 45 | 36.45 | 2 | 55 | 82.8 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 0.75 | 18.1 | 25 | 572 | 3 | 208/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG0363DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0363DL |  |  | DHG0363DL
DAIKIN | DHG0363DM | 3 | 1200 | 0.5 | 35176 | 27866 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 58.9 | 57.8 | 70 | 56.7 | 2 | 55 | 98.2 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 0.75 | 18.1 | 25 | 572 | 3 | 208/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG0363DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0363DM |  |  | DHG0363DM
DAIKIN | DHG0363DH | 3 | 1200 | 0.5 | 35176 | 27866 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 58.9 | 57.8 | 115 | 93.15 | 2 | 55 | 126 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 0.75 | 18.1 | 25 | 572 | 3 | 208/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG0363DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0363DH |  |  | DHG0363DH
DAIKIN | DHG0364DL | 3 | 1200 | 0.5 | 35176 | 27866 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 58.9 | 57.8 | 45 | 36.45 | 2 | 55 | 82.8 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 1.2 | 8.2 | 15 | 572 | 3 | 460/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG0364DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0364DL |  |  | DHG0364DL
DAIKIN | DHG0364DM | 3 | 1200 | 0.5 | 35176 | 27866 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 58.9 | 57.8 | 70 | 56.7 | 2 | 55 | 98.2 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 1.2 | 8.2 | 15 | 572 | 3 | 460/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG0364DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0364DM |  |  | DHG0364DM
DAIKIN | DHG0364DH | 3 | 1200 | 0.5 | 35176 | 27866 | 16.6 SEER2/12.5 EER2 | 80 | 67 | 58.9 | 57.8 | 115 | 93.15 | 2 | 55 | 126 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 1.2 | 8.2 | 15 | 572 | 3 | 460/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG0364DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0364DH |  |  | DHG0364DH
DAIKIN | DHG0483DL | 4 | 1600 | 0.5 | 46683 | 36866 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.1 | 57.8 | 70 | 56.7 | 2 | 55 | 87.4 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 1 | 22.8 | 30 | 647 | 4 | 208/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG0483DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0483DL |  |  | DHG0483DL
DAIKIN | DHG0483DM | 4 | 1600 | 0.5 | 46683 | 36866 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.1 | 57.8 | 115 | 93.15 | 2 | 55 | 108.2 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 1 | 22.8 | 30 | 647 | 4 | 208/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG0483DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0483DM |  |  | DHG0483DM
DAIKIN | DHG0483DH | 4 | 1600 | 0.5 | 46683 | 36866 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.1 | 57.8 | 140 | 113.4 | 2 | 55 | 119.8 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 1 | 22.8 | 30 | 647 | 4 | 208/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG0483DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0483DH |  |  | DHG0483DH
DAIKIN | DHG0484DL | 4 | 1600 | 0.5 | 46683 | 36866 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.1 | 57.8 | 70 | 56.7 | 2 | 55 | 87.4 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 1.2 | 10.7 | 15 | 647 | 4 | 460/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG0484DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0484DL |  |  | DHG0484DL
DAIKIN | DHG0484DM | 4 | 1600 | 0.5 | 46683 | 36866 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.1 | 57.8 | 115 | 93.15 | 2 | 55 | 108.2 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 1.2 | 10.7 | 15 | 647 | 4 | 460/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG0484DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0484DM |  |  | DHG0484DM
DAIKIN | DHG0484DH | 4 | 1600 | 0.5 | 46683 | 36866 | 16.4 SEER2/12.2 EER2 | 80 | 67 | 59.1 | 57.8 | 140 | 113.4 | 2 | 55 | 119.8 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 1.2 | 10.7 | 15 | 647 | 4 | 460/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG0484DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0484DH |  |  | DHG0484DH
DAIKIN | DHG0603DL | 5 | 2100 | 0.5 | 60037 | 46024 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 60.1 | 58 | 70 | 56.7 | 2 | 55 | 79.7 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 1 | 28.5 | 40 | 655 | 5 | 208/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG0603DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0603DL |  |  | DHG0603DL
DAIKIN | DHG0603DM | 5 | 2100 | 0.5 | 60037 | 46024 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 60.1 | 58 | 115 | 93.15 | 2 | 55 | 95.6 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 1 | 28.5 | 40 | 655 | 5 | 208/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG0603DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0603DM |  |  | DHG0603DM
DAIKIN | DHG0603DH | 5 | 2100 | 0.5 | 60037 | 46024 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 60.1 | 58 | 140 | 113.4 | 2 | 55 | 104.4 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 1 | 28.5 | 40 | 655 | 5 | 208/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG0603DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0603DH |  |  | DHG0603DH
DAIKIN | DHG0604DL | 5 | 2100 | 0.5 | 60037 | 46024 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 60.1 | 58 | 70 | 56.7 | 2 | 55 | 79.7 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 1.2 | 13.3 | 20 | 655 | 5 | 460/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG0604DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0604DL |  |  | DHG0604DL
DAIKIN | DHG0604DM | 5 | 2100 | 0.5 | 60037 | 46024 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 60.1 | 58 | 115 | 93.15 | 2 | 55 | 95.6 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 1.2 | 13.3 | 20 | 655 | 5 | 460/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG0604DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0604DM |  |  | DHG0604DM
DAIKIN | DHG0604DH | 5 | 2100 | 0.5 | 60037 | 46024 | 16.2 SEER2/12.2 EER2 | 80 | 67 | 60.1 | 58 | 140 | 113.4 | 2 | 55 | 104.4 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 1.2 | 13.3 | 20 | 655 | 5 | 460/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG0604DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0604DH |  |  | DHG0604DH
DAIKIN | DHG0723DL | 6 | 2200 | 0.5 | 69253 | 52414 | 18.6 IEER/12.5 EER | 80 | 67 | 58.3 | 57 | 70 | 56.7 | 2 | 55 | 78.6 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 1.2 | 27.2 | 40 | 705 | 6 | 208/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG0723DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0723DL |  |  | DHG0723DL
DAIKIN | DHG0723DM | 6 | 2200 | 0.5 | 69253 | 52414 | 18.6 IEER/12.5 EER | 80 | 67 | 58.3 | 57 | 125 | 101.25 | 2 | 55 | 97.1 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 1.2 | 27.2 | 40 | 705 | 6 | 208/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG0723DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0723DM |  |  | DHG0723DM
DAIKIN | DHG0723DH | 6 | 2200 | 0.5 | 69253 | 52414 | 18.6 IEER/12.5 EER | 80 | 67 | 58.3 | 57 | 150 | 121.5 | 2 | 55 | 105.5 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 1.2 | 27.2 | 40 | 705 | 6 | 208/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG0723DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0723DH |  |  | DHG0723DH
DAIKIN | DHG0724DL | 6 | 2200 | 0.5 | 69253 | 52414 | 18.6 IEER/12.5 EER | 80 | 67 | 58.3 | 57 | 70 | 56.7 | 2 | 55 | 78.6 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 1.2 | 12.2 | 15 | 705 | 6 | 460/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG0724DL - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0724DL |  |  | DHG0724DL
DAIKIN | DHG0724DM | 6 | 2200 | 0.5 | 69253 | 52414 | 18.6 IEER/12.5 EER | 80 | 67 | 58.3 | 57 | 125 | 101.25 | 2 | 55 | 97.1 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 1.2 | 12.2 | 15 | 705 | 6 | 460/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG0724DM - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0724DM |  |  | DHG0724DM
DAIKIN | DHG0724DH | 6 | 2200 | 0.5 | 69253 | 52414 | 18.6 IEER/12.5 EER | 80 | 67 | 58.3 | 57 | 150 | 121.5 | 2 | 55 | 105.5 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 1.2 | 12.2 | 15 | 705 | 6 | 460/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG0724DH - HGRH | ENGINEERING MANUAL - DHG (3-6) | [5 empty] | INSTALLATION MANUAL - DHG (3-6) |  |  | DHG0724DH |  |  | DHG0724DH
DAIKIN | DHG0903DL | 7.5 | 3000 | 0.5 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 130 | 105.3 | 2 | 55 | 87.1 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 2.4 | 39.4 | 50 | 1253 | 7.5 | 208/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG0903DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG0903DL |  |  | DHG0903DL
DAIKIN | DHG0903DM | 7.5 | 3000 | 0.5 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 180 | 145.8 | 2 | 55 | 99.4 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 2.4 | 39.4 | 50 | 1253 | 7.5 | 208/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG0903DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG0903DM |  |  | DHG0903DM
DAIKIN | DHG0903DH | 7.5 | 3000 | 0.5 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 225 | 182.25 | 2 | 55 | 110.6 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 2.4 | 39.4 | 50 | 1253 | 7.5 | 208/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG0903DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG0903DH |  |  | DHG0903DH
DAIKIN | DHG0904DL | 7.5 | 3000 | 0.5 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 130 | 105.3 | 2 | 55 | 87.1 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 2.4 | 20.1 | 25 | 1253 | 7.5 | 460/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG0904DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG0904DL |  |  | DHG0904DL
DAIKIN | DHG0904DM | 7.5 | 3000 | 0.5 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 180 | 145.8 | 2 | 55 | 99.4 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 2.4 | 20.1 | 25 | 1253 | 7.5 | 460/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG0904DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG0904DM |  |  | DHG0904DM
DAIKIN | DHG0904DH | 7.5 | 3000 | 0.5 | 89999 | 70199 | 17.5 IEER/12.5 EER | 80 | 67 | 58.7 | 57.5 | 225 | 182.25 | 2 | 55 | 110.6 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 2.4 | 20.1 | 25 | 1253 | 7.5 | 460/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG0904DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG0904DH |  |  | DHG0904DH
DAIKIN | DHG1023DL | 8.5 | 3400 | 0.5 | 103705 | 77724 | 17.5 IEER/12.5 EER | 80 | 67 | 59.2 | 57.3 | 130 | 105.3 | 2 | 55 | 83.3 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 2.4 | 43.7 | 50 | 1268 | 8.5 | 208/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG1023DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1023DL |  |  | DHG1023DL
DAIKIN | DHG1023DM | 8.5 | 3400 | 0.5 | 103705 | 77724 | 17.5 IEER/12.5 EER | 80 | 67 | 59.2 | 57.3 | 180 | 145.8 | 2 | 55 | 94.2 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 2.4 | 43.7 | 50 | 1268 | 8.5 | 208/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG1023DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1023DM |  |  | DHG1023DM
DAIKIN | DHG1023DH | 8.5 | 3400 | 0.5 | 103705 | 77724 | 17.5 IEER/12.5 EER | 80 | 67 | 59.2 | 57.3 | 225 | 182.25 | 2 | 55 | 104 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 2.4 | 43.7 | 50 | 1268 | 8.5 | 208/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG1023DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1023DH |  |  | DHG1023DH
DAIKIN | DHG1024DL | 8.5 | 3400 | 0.5 | 103705 | 77724 | 17.5 IEER/12.5 EER | 80 | 67 | 59.2 | 57.3 | 130 | 105.3 | 2 | 55 | 83.3 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 2.4 | 21.5 | 25 | 1268 | 8.5 | 460/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG1024DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1024DL |  |  | DHG1024DL
DAIKIN | DHG1024DM | 8.5 | 3400 | 0.5 | 103705 | 77724 | 17.5 IEER/12.5 EER | 80 | 67 | 59.2 | 57.3 | 180 | 145.8 | 2 | 55 | 94.2 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 2.4 | 21.5 | 25 | 1268 | 8.5 | 460/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG1024DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1024DM |  |  | DHG1024DM
DAIKIN | DHG1024DH | 8.5 | 3400 | 0.5 | 103705 | 77724 | 17.5 IEER/12.5 EER | 80 | 67 | 59.2 | 57.3 | 225 | 182.25 | 2 | 55 | 104 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 2.4 | 21.5 | 25 | 1268 | 8.5 | 460/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG1024DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1024DH |  |  | DHG1024DH
DAIKIN | DHG1203DL | 10 | 4000 | 0.5 | 118228 | 83517 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 130 | 105.3 | 2 | 55 | 79.1 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 2.4 | 46.6 | 60 | 1296 | 10 | 208/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG1203DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1203DL |  |  | DHG1203DL
DAIKIN | DHG1203DM | 10 | 4000 | 0.5 | 118228 | 83517 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 180 | 145.8 | 2 | 55 | 88.3 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 2.4 | 46.6 | 60 | 1296 | 10 | 208/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG1203DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1203DM |  |  | DHG1203DM
DAIKIN | DHG1203DH | 10 | 4000 | 0.5 | 118228 | 83517 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 240 | 194.4 | 2 | 55 | 99.4 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 2.4 | 46.6 | 60 | 1296 | 10 | 208/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG1203DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1203DH |  |  | DHG1203DH
DAIKIN | DHG1204DL | 10 | 4000 | 0.5 | 118228 | 83517 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 130 | 105.3 | 2 | 55 | 79.1 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 2.4 | 24.4 | 30 | 1296 | 10 | 460/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG1204DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1204DL |  |  | DHG1204DL
DAIKIN | DHG1204DM | 10 | 4000 | 0.5 | 118228 | 83517 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 180 | 145.8 | 2 | 55 | 88.3 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 2.4 | 24.4 | 30 | 1296 | 10 | 460/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG1204DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1204DM |  |  | DHG1204DM
DAIKIN | DHG1204DH | 10 | 4000 | 0.5 | 118228 | 83517 | 17 IEER/12.5 EER | 80 | 67 | 61 | 57.7 | 240 | 194.4 | 2 | 55 | 99.4 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 2.4 | 24.4 | 30 | 1296 | 10 | 460/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG1204DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1204DH |  |  | DHG1204DH
DAIKIN | DHG1503DL | 12.5 | 4600 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.5 | 57.3 | 130 | 105.3 | 2 | 55 | 75.9 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 3.5 | 61.1 | 80 | 1310 | 12.5 | 208/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG1503DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1503DL |  |  | DHG1503DL
DAIKIN | DHG1503DM | 12.5 | 4600 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.5 | 57.3 | 180 | 145.8 | 2 | 55 | 84 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 3.5 | 61.1 | 80 | 1310 | 12.5 | 208/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG1503DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1503DM |  |  | DHG1503DM
DAIKIN | DHG1503DH | 12.5 | 4600 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.5 | 57.3 | 240 | 194.4 | 2 | 55 | 93.6 | - | - | - |  | - | - | - | - | YES | 2 | 208/3 | 3.5 | 61.1 | 80 | 1310 | 12.5 | 208/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG1503DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1503DH |  |  | DHG1503DH
DAIKIN | DHG1504DL | 12.5 | 4600 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.5 | 57.3 | 130 | 105.3 | 2 | 55 | 75.9 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 3.5 | 30.6 | 35 | 1310 | 12.5 | 460/3 | GAS | HIGH | 2 | LOW | YES |  |  | DHG1504DL - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1504DL |  |  | DHG1504DL
DAIKIN | DHG1504DM | 12.5 | 4600 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.5 | 57.3 | 180 | 145.8 | 2 | 55 | 84 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 3.5 | 30.6 | 35 | 1310 | 12.5 | 460/3 | GAS | HIGH | 2 | MEDIUM | YES |  |  | DHG1504DM - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1504DM |  |  | DHG1504DM
DAIKIN | DHG1504DH | 12.5 | 4600 | 0.5 | 141415 | 108889 | 16 IEER/12 EER | 80 | 67 | 58.5 | 57.3 | 240 | 194.4 | 2 | 55 | 93.6 | - | - | - |  | - | - | - | - | YES | 2 | 460/3 | 3.5 | 30.6 | 35 | 1310 | 12.5 | 460/3 | GAS | HIGH | 2 | HIGH | YES |  |  | DHG1504DH - HGRH | ENGINEERING MANUAL - DHG (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DHG (7.5-12.5) |  |  | DHG1504DH |  |  | DHG1504DH
DAIKIN | DSH0724 | 6 | 2183 | 0.5 | 67442 | 50799 | 16.70 IEER/11.30 EER | 80 | 67 | 58.8 | 57.2 | - | - | - | - | - | 67000 | - |  |  | 3.4 | 2.25 | 5 |  | NO | 2 | 460/3 | 1.2 | 20.2 | 25 | 645 | 6 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 6-Ton - SE - 460/3 - 5kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0724 |  |  | DSH0724
DAIKIN | DSH1504 | 12.5 | 4706 | 0.5 | 144859 | 109043 | 14.20 IEER/10.60 EER | 80 | 67 | 58.9 | 57.2 | - | - | - | - | - | 143000 | 85500 |  |  | 3.4 | 2.05 | 45 |  | NO | 2 | 460/3 | 3.5 | 99.3 | 100 | 1364 | 12.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 12.5-Ton - SE - 460/3 - 45kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1504 |  |  | DSH1504
DAIKIN | DSH1804 | 15 | 6411 | 0.5 | 176881 | 129333 | 14.5 IEER/10.6 EER | 80 | 67 | 61.6 | 58.3 | - | - | - | - | - | 172000 | 100000 |  |  | 3.3 | 2.05 | 30 |  | NO | 2 | 460/3 | 3.5 | 87.8 | 90 | 2273 | 15 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 15.0-Ton - SE - 460/3 - 30kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH1804 |  |  | DSH1804
DAIKIN | DSH0724 | 6 | 2183 | 0.5 | 67442 | 50799 | 16.70 IEER/11.30 EER | 80 | 67 | 58.8 | 57.2 | - | - | - | - | - | 67000 | - |  |  | 3.4 | 2.25 | 20 |  | NO | 2 | 460/3 | 1.2 | 42.8 | 45 | 645 | 6 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 6-Ton - SE - 460/3 - 20kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0724 |  |  | DSH0724
DAIKIN | DSH1504 | 12.5 | 4706 | 0.5 | 144859 | 109043 | 14.20 IEER/10.60 EER | 80 | 67 | 58.9 | 57.2 | - | - | - | - | - | 143000 | 85500 |  |  | 3.4 | 2.05 | 60 |  | NO | 2 | 460/3 | 3.5 | 101 | 110 | 1364 | 12.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 12.5-Ton - SE - 460/3 - 60kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1504 |  |  | DSH1504
DAIKIN | DSH1804 | 15 | 6411 | 0.5 | 176881 | 129333 | 14.5 IEER/10.6 EER | 80 | 67 | 61.6 | 58.3 | - | - | - | - | - | 172000 | 100000 |  |  | 3.3 | 2.05 | 45 |  | NO | 2 | 460/3 | 3.5 | 109 | 110 | 2273 | 15 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 15.0-Ton - SE - 460/3 - 45kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH1804 |  |  | DSH1804
DAIKIN | DHH0604 | 5 | 2100 | 0.5 | 60668 | 48247 | 16.4 SEER2/12.20 EER2 | 80 | 67 | 59.1 | 57.9 | - | - | - | - | - | 59000 | - |  |  | - | - | 15 |  | NO | 2 | 460/3 | 1.2 | 35.9 | 40 | 630 | 5 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 5-Ton - HE - 460/3 - 15kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0604 |  |  | DHH0604
DAIKIN | DHH0604 | 5 | 2100 | 0.5 | 60668 | 48247 | 16.4 SEER2/12.20 EER2 | 80 | 67 | 59.1 | 57.9 | - | - | - | - | - | 59000 | - |  |  | - | - | 10 |  | NO | 2 | 460/3 | 1.2 | 28.3 | 30 | 630 | 5 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 5-Ton - HE - 460/3 - 10kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0604 |  |  | DHH0604
DAIKIN | DHH0724 | 6 | 2400 | 0.5 | 69967 | 55179 | 17.20 IEER/12.0 EER | 80 | 67 | 59.1 | 57.8 | - | - | - | - | - | 62000 | - |  |  | 3.5 | 2.4 | 30 |  | NO | 2 | 460/3 | 1.2 | 57.3 | 60 | 708 | 6 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 6-Ton - HE - 460/3 - 30kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0724 |  |  | DHH0724
DAIKIN | DHH0724 | 6 | 2400 | 0.5 | 69967 | 55179 | 17.20 IEER/12.0 EER | 80 | 67 | 59.1 | 57.8 | - | - | - | - | - | 62000 | - |  |  | 3.5 | 2.4 | 20 |  | NO | 2 | 460/3 | 1.2 | 42.2 | 45 | 708 | 6 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 6-Ton - HE - 460/3 - 20kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0724 |  |  | DHH0724
DAIKIN | DHH0724 | 6 | 2400 | 0.5 | 69967 | 55179 | 17.20 IEER/12.0 EER | 80 | 67 | 59.1 | 57.8 | - | - | - | - | - | 62000 | - |  |  | 3.5 | 2.4 | - | - | NO | 2 | 460/3 | 1.2 | 12.2 | 15 | 708 | 6 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 6-Ton - HE - 460/3 - 0kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0724 |  |  | DHH0724
DAIKIN | DVH1204 | 10 | 4270 | 1 | 128803 | 94756 | 20.0 IEER/12.1 EER | 80 | 67 | 59.8 | 57.4 | - | - | - | - | - | 114000 | 80000 |  |  | 3.74 | 2.5 | - | - | NO | Variable | 460/3 | 3.5 | 26.5 | 35 | 1293 | 10 | 460/3 | HEAT PUMP | MZVAV | Variable | - | NO |  |  | 10.0-Ton - MZVAV - 460/3 - 0kW | ENGINEERING MANUAL - DVH (7.5-10) | [5 empty] | INSTALLATION MANUAL - DVH (7.5-10) |  |  | DVH1204 |  |  | DVH1204
DAIKIN | DVH1203 | 10 | 4270 | 1 | 128803 | 94756 | 20.0 IEER/12.1 EER | 80 | 67 | 59.8 | 57.4 | - | - | - | - | - | 114000 | 80000 |  |  | 3.74 | 2.5 | - | - | NO | Variable | 208/3 | 3.5 | 54 | 70 | 1293 | 10 | 208/3 | HEAT PUMP | MZVAV | Variable | - | NO |  |  | 10.0-Ton - MZVAV - 208/3 - 0kW | ENGINEERING MANUAL - DVH (7.5-10) | [5 empty] | INSTALLATION MANUAL - DVH (7.5-10) |  |  | DVH1203 |  |  | DVH1203
DAIKIN | DVH1024 | 8.5 | 3800 | 1 | 111575 | 84874 | 20.0 IEER/12.3 EER | 80 | 67 | 59.7 | 57.7 | - | - | - | - | - | 102000 | 72000 |  |  | 3.85 | 2.5 | - | - | NO | Variable | 460/3 | 3.5 | 26 | 30 | 1293 | 8.5 | 460/3 | HEAT PUMP | MZVAV | Variable | - | NO |  |  | 8.5-Ton - MZVAV - 460/3 - 0kW | ENGINEERING MANUAL - DVH (7.5-10) | [5 empty] | INSTALLATION MANUAL - DVH (7.5-10) |  |  | DVH1024 |  |  | DVH1024
DAIKIN | DVH1023 | 8.5 | 3800 | 1 | 111575 | 84874 | 20.0 IEER/12.3 EER | 80 | 67 | 59.7 | 57.7 | - | - | - | - | - | 102000 | 72000 |  |  | 3.85 | 2.5 | - | - | NO | Variable | 208/3 | 3.5 | 52.7 | 60 | 1293 | 8.5 | 208/3 | HEAT PUMP | MZVAV | Variable | - | NO |  |  | 8.5-Ton - MZVAV - 208/3 - 0kW | ENGINEERING MANUAL - DVH (7.5-10) | [5 empty] | INSTALLATION MANUAL - DVH (7.5-10) |  |  | DVH1023 |  |  | DVH1023
DAIKIN | DVH0904 | 7.5 | 3600 | 1 | 102928 | 79341 | 20.0 IEER/12.4 EER | 80 | 67 | 60 | 58 | - | - | - | - | - | 90000 | 63000 |  |  | 3.85 | 2.5 | - | - | NO | Variable | 460/3 | 3.5 | 24.8 | 30 | 1293 | 7.5 | 460/3 | HEAT PUMP | MZVAV | Variable | - | NO |  |  | 7.5-Ton - MZVAV - 460/3 - 0kW | ENGINEERING MANUAL - DVH (7.5-10) | [5 empty] | INSTALLATION MANUAL - DVH (7.5-10) |  |  | DVH0904 |  |  | DVH0904
DAIKIN | DVH0903 | 7.5 | 3600 | 1 | 102928 | 79341 | 20.0 IEER/12.4 EER | 80 | 67 | 60 | 58 | - | - | - | - | - | 90000 | 63000 |  |  | 3.85 | 2.5 | - | - | NO | Variable | 208/3 | 3.5 | 49.9 | 60 | 1293 | 7.5 | 208/3 | HEAT PUMP | MZVAV | Variable | - | NO |  |  | 7.5-Ton - MZVAV - 208/3 - 0kW | ENGINEERING MANUAL - DVH (7.5-10) | [5 empty] | INSTALLATION MANUAL - DVH (7.5-10) |  |  | DVH0903 |  |  | DVH0903
DAIKIN | DHH0724 | 6 | 2400 | 0.5 | 69967 | 55179 | 17.20 IEER/12.0 EER | 80 | 67 | 59.1 | 57.8 | - | - | - | - | - | 62000 | - |  |  | 3.5 | 2.4 | 15 |  | NO | 2 | 460/3 | 1.2 | 34.7 | 35 | 708 | 6 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 6-Ton - HE - 460/3 - 15kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0724 |  |  | DHH0724
DAIKIN | DHH0724 | 6 | 2400 | 0.5 | 69967 | 55179 | 17.20 IEER/12.0 EER | 80 | 67 | 59.1 | 57.8 | - | - | - | - | - | 62000 | - |  |  | 3.5 | 2.4 | 10 |  | NO | 2 | 460/3 | 1.2 | 27.2 | 30 | 708 | 6 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 6-Ton - HE - 460/3 - 10kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0724 |  |  | DHH0724
DAIKIN | DHH0724 | 6 | 2400 | 0.5 | 69967 | 55179 | 17.20 IEER/12.0 EER | 80 | 67 | 59.1 | 57.8 | - | - | - | - | - | 62000 | - |  |  | 3.5 | 2.4 | 5 |  | NO | 2 | 460/3 | 1.2 | 19.7 | 25 | 708 | 6 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 6-Ton - HE - 460/3 - 5kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0724 |  |  | DHH0724
DAIKIN | DHH0723 | 6 | 2400 | 0.5 | 69967 | 55179 | 17.20 IEER/12.0 EER | 80 | 67 | 59.1 | 57.8 | - | - | - | - | - | 62000 | - |  |  | 3.5 | 2.4 | 30 |  | NO | 2 | 208/3 | 1.2 | 105 | 110 | 708 | 6 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 6-Ton - HE - 208/3 - 30kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0723 |  |  | DHH0723
DAIKIN | DHH0723 | 6 | 2400 | 0.5 | 69967 | 55179 | 17.20 IEER/12.0 EER | 80 | 67 | 59.1 | 57.8 | - | - | - | - | - | 62000 | - |  |  | 3.5 | 2.4 | 20 |  | NO | 2 | 208/3 | 1.2 | 79 | 80 | 708 | 6 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 6-Ton - HE - 208/3 - 20kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0723 |  |  | DHH0723
DAIKIN | DHH0723 | 6 | 2400 | 0.5 | 69967 | 55179 | 17.20 IEER/12.0 EER | 80 | 67 | 59.1 | 57.8 | - | - | - | - | - | 62000 | - |  |  | 3.5 | 2.4 | 15 |  | NO | 2 | 208/3 | 1.2 | 66.3 | 70 | 708 | 6 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 6-Ton - HE - 208/3 - 15kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0723 |  |  | DHH0723
DAIKIN | DHH0603 | 5 | 2100 | 0.5 | 60668 | 48247 | 16.4 SEER2/12.20 EER2 | 80 | 67 | 59.1 | 57.9 | - | - | - | - | - | 59000 | - |  |  | - | - | 10 |  | NO | 2 | 208/3 | 1 | 55.3 | 60 | 630 | 5 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 5-Ton - HE - 208/3 - 10kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0603 |  |  | DHH0603
DAIKIN | DHH0723 | 6 | 2400 | 0.5 | 69967 | 55179 | 17.20 IEER/12.0 EER | 80 | 67 | 59.1 | 57.8 | - | - | - | - | - | 62000 | - |  |  | 3.5 | 2.4 | 10 |  | NO | 2 | 208/3 | 1.2 | 53.1 | 60 | 708 | 6 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 6-Ton - HE - 208/3 - 10kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0723 |  |  | DHH0723
DAIKIN | DHH0723 | 6 | 2400 | 0.5 | 69967 | 55179 | 17.20 IEER/12.0 EER | 80 | 67 | 59.1 | 57.8 | - | - | - | - | - | 62000 | - |  |  | 3.5 | 2.4 | 5 |  | NO | 2 | 208/3 | 1.2 | 40.2 | 50 | 708 | 6 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 6-Ton - HE - 208/3 - 5kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0723 |  |  | DHH0723
DAIKIN | DHH0724 | 6 | 2400 | 0.5 | 69967 | 55179 | 17.20 IEER/12.0 EER | 80 | 67 | 59.1 | 57.8 | - | - | - | - | - | 62000 | - |  |  | 3.5 | 2.4 | - | - | NO | 2 | 460/3 | 1.2 | 12.2 | 15 | 708 | 6 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 6-Ton - HE - 460/3 - 0kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0724 |  |  | DHH0724
DAIKIN | DHH0604 | 5 | 2100 | 0.5 | 60668 | 48247 | 16.4 SEER2/12.20 EER2 | 80 | 67 | 59.1 | 57.9 | - | - | - | - | - | 59000 | - |  |  | - | - | 20 |  | NO | 2 | 460/3 | 1.2 | 43.4 | 45 | 630 | 5 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 5-Ton - HE - 460/3 - 20kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0604 |  |  | DHH0604
DAIKIN | DHH0604 | 5 | 2100 | 0.5 | 60668 | 48247 | 16.4 SEER2/12.20 EER2 | 80 | 67 | 59.1 | 57.9 | - | - | - | - | - | 59000 | - |  |  | - | - | 5 |  | NO | 2 | 460/3 | 1.2 | 20.8 | 25 | 630 | 5 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 5-Ton - HE - 460/3 - 5kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0604 |  |  | DHH0604
DAIKIN | DHH0603 | 5 | 2100 | 0.5 | 60668 | 48247 | 16.4 SEER2/12.20 EER2 | 80 | 67 | 59.1 | 57.9 | - | - | - | - | - | 59000 | - |  |  | - | - | 15 |  | NO | 2 | 208/3 | 1 | 68.5 | 70 | 630 | 5 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 5-Ton - HE - 208/3 - 15kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0603 |  |  | DHH0603
DAIKIN | DHH0604 | 5 | 2100 | 0.5 | 60668 | 48247 | 16.4 SEER2/12.20 EER2 | 80 | 67 | 59.1 | 57.9 | - | - | - | - | - | 59000 | - |  |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 13.3 | 20 | 630 | 5 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 5-Ton - HE - 460/3 - 0kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0604 |  |  | DHH0604
DAIKIN | DHH0603 | 5 | 2100 | 0.5 | 60668 | 48247 | 16.4 SEER2/12.20 EER2 | 80 | 67 | 59.1 | 57.9 | - | - | - | - | - | 59000 | - |  |  | - | - | 5 |  | NO | 2 | 208/3 | 1 | 42.4 | 50 | 630 | 5 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 5-Ton - HE - 208/3 - 5kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0603 |  |  | DHH0603
DAIKIN | DHH0483 | 4 | 1600 | 0.5 | 48225 | 38116 | 16.8 SEER2/13.0 EER2 | 80 | 67 | 58.3 | 57.5 | - | - | - | - | - | 46000 | - |  |  | - | - | 20 |  | NO | 2 | 208/3 | 1 | 77.2 | 80 | 621 | 4 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 4-Ton - HE - 208/3 - 20kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0483 |  |  | DHH0483
DAIKIN | DHH0483 | 4 | 1600 | 0.5 | 48225 | 38116 | 16.8 SEER2/13.0 EER2 | 80 | 67 | 58.3 | 57.5 | - | - | - | - | - | 46000 | - |  |  | - | - | 10 |  | NO | 2 | 208/3 | 1 | 51.3 | 60 | 621 | 4 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 4-Ton - HE - 208/3 - 10kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0483 |  |  | DHH0483
DAIKIN | DHH0483 | 4 | 1600 | 0.5 | 48225 | 38116 | 16.8 SEER2/13.0 EER2 | 80 | 67 | 58.3 | 57.5 | - | - | - | - | - | 46000 | - |  |  | - | - | - | - | NO | 2 | 208/3 | 1 | 25.4 | 35 | 621 | 4 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 4-Ton - HE - 208/3 - 0kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0483 |  |  | DHH0483
DAIKIN | DHH0363 | 3 | 1200 | 0.5 | 35224 | 27292 | 16.4 SEER2/13.0 EER2 | 80 | 67 | 59.3 | 57.7 | - | - | - | - | - | 33200 | - |  |  | - | - | 10 |  | NO | 2 | 208/3 | 0.75 | 44 | 45 | 595 | 3 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 3-Ton - HE - 208/3 - 10kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0363 |  |  | DHH0363
DAIKIN | DHH0603 | 5 | 2100 | 0.5 | 60668 | 48247 | 16.4 SEER2/12.20 EER2 | 80 | 67 | 59.1 | 57.9 | - | - | - | - | - | 59000 | - |  |  | - | - | - | - | NO | 2 | 208/3 | 1 | 29.4 | 40 | 630 | 5 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 5-Ton - HE - 208/3 - 0kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0603 |  |  | DHH0603
DAIKIN | DHH0484 | 4 | 1600 | 0.5 | 48225 | 38116 | 16.8 SEER2/13.0 EER2 | 80 | 67 | 58.3 | 57.5 | - | - | - | - | - | 46000 | - |  |  | - | - | 10 |  | NO | 2 | 460/3 | 1.2 | 26.9 | 30 | 621 | 4 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 4-Ton - HE - 460/3 - 10kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0484 |  |  | DHH0484
DAIKIN | DHH0484 | 4 | 1600 | 0.5 | 48225 | 38116 | 16.8 SEER2/13.0 EER2 | 80 | 67 | 58.3 | 57.5 | - | - | - | - | - | 46000 | - |  |  | - | - | 5 |  | NO | 2 | 460/3 | 1.2 | 19.4 | 20 | 621 | 4 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 4-Ton - HE - 460/3 - 5kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0484 |  |  | DHH0484
DAIKIN | DHH0484 | 4 | 1600 | 0.5 | 48225 | 38116 | 16.8 SEER2/13.0 EER2 | 80 | 67 | 58.3 | 57.5 | - | - | - | - | - | 46000 | - |  |  | - | - | 15 |  | NO | 2 | 460/3 | 1.2 | 34.4 | 35 | 621 | 4 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 4-Ton - HE - 460/3 - 15kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0484 |  |  | DHH0484
DAIKIN | DHH0484 | 4 | 1600 | 0.5 | 48225 | 38116 | 16.8 SEER2/13.0 EER2 | 80 | 67 | 58.3 | 57.5 | - | - | - | - | - | 46000 | - |  |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 11.9 | 15 | 621 | 4 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 4-Ton - HE - 460/3 - 0kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0484 |  |  | DHH0484
DAIKIN | DHH0484 | 4 | 1600 | 0.5 | 48225 | 38116 | 16.8 SEER2/13.0 EER2 | 80 | 67 | 58.3 | 57.5 | - | - | - | - | - | 46000 | - |  |  | - | - | 20 |  | NO | 2 | 460/3 | 1.2 | 41.9 | 45 | 621 | 4 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 4-Ton - HE - 460/3 - 20kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0484 |  |  | DHH0484
DAIKIN | DHH0483 | 4 | 1600 | 0.5 | 48225 | 38116 | 16.8 SEER2/13.0 EER2 | 80 | 67 | 58.3 | 57.5 | - | - | - | - | - | 46000 | - |  |  | - | - | 15 |  | NO | 2 | 208/3 | 1 | 64.5 | 70 | 621 | 4 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 4-Ton - HE - 208/3 - 15kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0483 |  |  | DHH0483
DAIKIN | DHH0483 | 4 | 1600 | 0.5 | 48225 | 38116 | 16.8 SEER2/13.0 EER2 | 80 | 67 | 58.3 | 57.5 | - | - | - | - | - | 46000 | - |  |  | - | - | 5 |  | NO | 2 | 208/3 | 1 | 38.4 | 45 | 621 | 4 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 4-Ton - HE - 208/3 - 5kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0483 |  |  | DHH0483
DAIKIN | DHH0364 | 3 | 1200 | 0.5 | 35224 | 27292 | 16.4 SEER2/13.0 EER2 | 80 | 67 | 59.3 | 57.7 | - | - | - | - | - | 33200 | - |  |  | - | - | 10 |  | NO | 2 | 460/3 | 1.2 | 23.2 | 25 | 595 | 3 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 3-Ton - HE - 460/3 - 10kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0364 |  |  | DHH0364
DAIKIN | DHH0364 | 3 | 1200 | 0.5 | 35224 | 27292 | 16.4 SEER2/13.0 EER2 | 80 | 67 | 59.3 | 57.7 | - | - | - | - | - | 33200 | - |  |  | - | - | 5 |  | NO | 2 | 460/3 | 1.2 | 15.7 | 20 | 595 | 3 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 3-Ton - HE - 460/3 - 5kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0364 |  |  | DHH0364
DAIKIN | DHH0364 | 3 | 1200 | 0.5 | 35224 | 27292 | 16.4 SEER2/13.0 EER2 | 80 | 67 | 59.3 | 57.7 | - | - | - | - | - | 33200 | - |  |  | - | - | - | - | NO | 2 | 460/3 | 1.2 | 8.2 | 15 | 595 | 3 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 3-Ton - HE - 460/3 - 0kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0364 |  |  | DHH0364
DAIKIN | DHH0364 | 3 | 1200 | 0.5 | 35224 | 27292 | 16.4 SEER2/13.0 EER2 | 80 | 67 | 59.3 | 57.7 | - | - | - | - | - | 33200 | - |  |  | - | - | 15 |  | NO | 2 | 460/3 | 1.2 | 30.7 | 35 | 595 | 3 | 460/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 3-Ton - HE - 460/3 - 15kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0364 |  |  | DHH0364
DAIKIN | DHH0363 | 3 | 1200 | 0.5 | 35224 | 27292 | 16.4 SEER2/13.0 EER2 | 80 | 67 | 59.3 | 57.7 | - | - | - | - | - | 33200 | - |  |  | - | - | 15 |  | NO | 2 | 208/3 | 0.75 | 57.2 | 60 | 595 | 3 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 3-Ton - HE - 208/3 - 15kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0363 |  |  | DHH0363
DAIKIN | DHH0363 | 3 | 1200 | 0.5 | 35224 | 27292 | 16.4 SEER2/13.0 EER2 | 80 | 67 | 59.3 | 57.7 | - | - | - | - | - | 33200 | - |  |  | - | - | 5 |  | NO | 2 | 208/3 | 0.75 | 31.1 | 35 | 595 | 3 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 3-Ton - HE - 208/3 - 5kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0363 |  |  | DHH0363
DAIKIN | DHH0363 | 3 | 1200 | 0.5 | 35224 | 27292 | 16.4 SEER2/13.0 EER2 | 80 | 67 | 59.3 | 57.7 | - | - | - | - | - | 33200 | - |  |  | - | - | - | - | NO | 2 | 208/3 | 0.75 | 18.1 | 25 | 595 | 3 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 3-Ton - HE - 208/3 - 0kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0363 |  |  | DHH0363
DAIKIN | DHH0603 | 5 | 2100 | 0.5 | 60668 | 48247 | 16.4 SEER2/12.20 EER2 | 80 | 67 | 59.1 | 57.9 | - | - | - | - | - | 59000 | - |  |  | - | - | 20 |  | NO | 2 | 208/3 | 1 | 81.2 | 90 | 630 | 5 | 208/3 | HEAT PUMP | HIGH | 2 | - | NO |  |  | 5-Ton - HE - 208/3 - 20kW | ENGINEERING MANUAL - DHH (3-6) | [5 empty] | INSTALLATION MANUAL - DHH (3-6) |  |  | DHH0603 |  |  | DHH0603
DAIKIN | DSH1504 | 12.5 | 4706 | 0.5 | 144859 | 109043 | 14.20 IEER/10.60 EER | 80 | 67 | 58.9 | 57.2 | - | - | - | - | - | 143000 | 85500 |  |  | 3.4 | 2.05 | 15 |  | NO | 2 | 460/3 | 3.5 | 54.2 | 60 | 1364 | 12.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 12.5-Ton - SE - 460/3 - 15kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1504 |  |  | DSH1504
DAIKIN | DSH1804 | 15 | 6411 | 0.5 | 176881 | 129333 | 14.5 IEER/10.6 EER | 80 | 67 | 61.6 | 58.3 | - | - | - | - | - | 172000 | 100000 |  |  | 3.3 | 2.05 | 60 |  | NO | 2 | 460/3 | 3.5 | 114 | 125 | 2273 | 15 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 15.0-Ton - SE - 460/3 - 60kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH1804 |  |  | DSH1804
DAIKIN | DSH2404 | 20 | 8000 | 0.5 | 230200 | 177254 | 14.35 IEER/10.6 EER | 80 | 67 | 59.9 | 57.9 | - | - | - | - | - | 220000 | 122000 |  |  | 3.3 | 2.05 | 60 |  | NO | 2 | 460/3 | 3.5 | 120 | 125 | 2354 | 20 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 20-Ton - SE - 460/3 - 60kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH2404 |  |  | DSH2404
DAIKIN | DSH2404 | 20 | 8000 | 0.5 | 230200 | 177254 | 14.35 IEER/10.6 EER | 80 | 67 | 59.9 | 57.9 | - | - | - | - | - | 220000 | 122000 |  |  | 3.3 | 2.05 | - | - | NO | 2 | 460/3 | 3.5 | 50.8 | 60 | 2354 | 20 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 20-Ton - SE - 460/3 - 0kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH2404 |  |  | DSH2404
DAIKIN | DSH2404 | 20 | 8000 | 0.5 | 230200 | 177254 | 14.35 IEER/10.6 EER | 80 | 67 | 59.9 | 57.9 | - | - | - | - | - | 220000 | 122000 |  |  | 3.3 | 2.05 | 45 |  | NO | 2 | 460/3 | 3.5 | 116 | 125 | 2354 | 20 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 20-Ton - SE - 460/3 - 45kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH2404 |  |  | DSH2404
DAIKIN | DSH2404 | 20 | 8000 | 0.5 | 230200 | 177254 | 14.35 IEER/10.6 EER | 80 | 67 | 59.9 | 57.9 | - | - | - | - | - | 220000 | 122000 |  |  | 3.3 | 2.05 | 75 |  | NO | 2 | 460/3 | 3.5 | 137 | 150 | 2354 | 20 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 20-Ton - SE - 460/3 - 75kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH2404 |  |  | DSH2404
DAIKIN | DSH2404 | 20 | 8000 | 0.5 | 230200 | 177254 | 14.35 IEER/10.6 EER | 80 | 67 | 59.9 | 57.9 | - | - | - | - | - | 220000 | 122000 |  |  | 3.3 | 2.05 | 30 |  | NO | 2 | 460/3 | 3.5 | 94.1 | 100 | 2354 | 20 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 20-Ton - SE - 460/3 - 30kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH2404 |  |  | DSH2404
DAIKIN | DSH2403 | 20 | 8401 | 0.5 | 230200 | 177254 | 14.35 IEER/10.6 EER | 80 | 67 | 60.8 | 58.4 | - | - | - | - | - | 220000 | 122000 |  |  | 3.3 | 2.05 | 75 |  | NO | 2 | 208/3 | 3.5 | 249 | 250 | 2354 | 20 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 20-Ton - SE - 208/3 - 75kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH2403 |  |  | DSH2403
DAIKIN | DSH2403 | 20 | 8401 | 0.5 | 230200 | 177254 | 14.35 IEER/10.6 EER | 80 | 67 | 60.8 | 58.4 | - | - | - | - | - | 220000 | 122000 |  |  | 3.3 | 2.05 | 60 |  | NO | 2 | 208/3 | 3.5 | 249 | 250 | 2354 | 20 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 20-Ton - SE - 208/3 - 60kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH2403 |  |  | DSH2403
DAIKIN | DSH2403 | 20 | 8401 | 0.5 | 230200 | 177254 | 14.35 IEER/10.6 EER | 80 | 67 | 60.8 | 58.4 | - | - | - | - | - | 220000 | 122000 |  |  | 3.3 | 2.05 | 45 |  | NO | 2 | 208/3 | 3.5 | 211 | 225 | 2354 | 20 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 20-Ton - SE - 208/3 - 45kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH2403 |  |  | DSH2403
DAIKIN | DSH2403 | 20 | 8401 | 0.5 | 230200 | 177254 | 14.35 IEER/10.6 EER | 80 | 67 | 60.8 | 58.4 | - | - | - | - | - | 220000 | 122000 |  |  | 3.3 | 2.05 | 30 |  | NO | 2 | 208/3 | 3.5 | 174 | 175 | 2354 | 20 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 20-Ton - SE - 208/3 - 30kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH2403 |  |  | DSH2403
DAIKIN | DSH2403 | 20 | 8401 | 0.5 | 230200 | 177254 | 14.35 IEER/10.6 EER | 80 | 67 | 60.8 | 58.4 | - | - | - | - | - | 220000 | 122000 |  |  | 3.3 | 2.05 | - | - | NO | 2 | 208/3 | 3.5 | 98.7 | 125 | 2354 | 20 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 20-Ton - SE - 208/3 - 0kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH2403 |  |  | DSH2403
DAIKIN | DSH1804 | 15 | 6411 | 0.5 | 176881 | 129333 | 14.5 IEER/10.6 EER | 80 | 67 | 61.6 | 58.3 | - | - | - | - | - | 172000 | 100000 |  |  | 3.3 | 2.05 | - | - | NO | 2 | 460/3 | 3.5 | 44.5 | 50 | 2273 | 15 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 15.0-Ton - SE - 460/3 - 0kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH1804 |  |  | DSH1804
DAIKIN | DSH1803 | 15 | 6411 | 0.5 | 176881 | 129333 | 14.5 IEER/10.6 EER | 80 | 67 | 61.6 | 58.3 | - | - | - | - | - | 172000 | 100000 |  |  | 3.3 | 2.05 | 60 |  | NO | 2 | 208/3 | 3.5 | 239 | 250 | 2273 | 15 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 15.0-Ton - SE - 208/3 - 60kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH1803 |  |  | DSH1803
DAIKIN | DSH1803 | 15 | 6411 | 0.5 | 176881 | 129333 | 14.5 IEER/10.6 EER | 80 | 67 | 61.6 | 58.3 | - | - | - | - | - | 172000 | 100000 |  |  | 3.3 | 2.05 | 45 |  | NO | 2 | 208/3 | 3.5 | 201 | 225 | 2273 | 15 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 15.0-Ton - SE - 208/3 - 45kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH1803 |  |  | DSH1803
DAIKIN | DSH1803 | 15 | 6411 | 0.5 | 176881 | 129333 | 14.5 IEER/10.6 EER | 80 | 67 | 61.6 | 58.3 | - | - | - | - | - | 172000 | 100000 |  |  | 3.3 | 2.05 | 30 |  | NO | 2 | 208/3 | 3.5 | 164 | 175 | 2273 | 15 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 15.0-Ton - SE - 208/3 - 30kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH1803 |  |  | DSH1803
DAIKIN | DSH1803 | 15 | 6411 | 0.5 | 176881 | 129333 | 14.5 IEER/10.6 EER | 80 | 67 | 61.6 | 58.3 | - | - | - | - | - | 172000 | 100000 |  |  | 3.3 | 2.05 | - | - | NO | 2 | 208/3 | 3.5 | 88.9 | 110 | 2273 | 15 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 15.0-Ton - SE - 208/3 - 0kW | ENGINEERING MANUAL - DSH (15-20) | [5 empty] | INSTALLATION MANUAL - DSH (15-25) |  |  | DSH1803 |  |  | DSH1803
DAIKIN | DSH1504 | 12.5 | 4706 | 0.5 | 144859 | 109043 | 14.20 IEER/10.60 EER | 80 | 67 | 58.9 | 57.2 | - | - | - | - | - | 143000 | 85500 |  |  | 3.4 | 2.05 | 30 |  | NO | 2 | 460/3 | 3.5 | 74.9 | 80 | 1364 | 12.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 12.5-Ton - SE - 460/3 - 30kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1504 |  |  | DSH1504
DAIKIN | DSH1504 | 12.5 | 4706 | 0.5 | 144859 | 109043 | 14.20 IEER/10.60 EER | 80 | 67 | 58.9 | 57.2 | - | - | - | - | - | 143000 | 85500 |  |  | 3.4 | 2.05 | - | - | NO | 2 | 460/3 | 3.5 | 31.6 | 40 | 1364 | 12.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 12.5-Ton - SE - 460/3 - 0kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1504 |  |  | DSH1504
DAIKIN | DSH1503 | 12.5 | 4706 | 0.5 | 144859 | 109043 | 14.20 IEER/10.60 EER | 80 | 67 | 58.9 | 57.2 | - | - | - | - | - | 143000 | 85500 |  |  | 3.4 | 2.05 | 60 |  | NO | 2 | 208/3 | 3.5 | 215 | 225 | 1364 | 12.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 12.5-Ton - SE - 208/3 - 60kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1503 |  |  | DSH1503
DAIKIN | DSH1204 | 10 | 4153 | 0.5 | 117158 | 94737 | 15.2 IEER/11.4 EER | 80 | 67 | 59.3 | 58.1 | - | - | - | - | - | 116000 | 66000 |  |  | 3.4 | 2.25 | 30 |  | NO | 2 | 460/3 | 3.5 | 72.4 | 80 | 1169 | 10 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 10-Ton - SE - 460/3 - 30kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1204 |  |  | DSH1204
DAIKIN | DSH1503 | 12.5 | 4706 | 0.5 | 144859 | 109043 | 14.20 IEER/10.60 EER | 80 | 67 | 58.9 | 57.2 | - | - | - | - | - | 143000 | 85500 |  |  | 3.4 | 2.05 | 45 |  | NO | 2 | 208/3 | 3.5 | 182 | 200 | 1364 | 12.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 12.5-Ton - SE - 208/3 - 45kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1503 |  |  | DSH1503
DAIKIN | DSH1503 | 12.5 | 4706 | 0.5 | 144859 | 109043 | 14.20 IEER/10.60 EER | 80 | 67 | 58.9 | 57.2 | - | - | - | - | - | 143000 | 85500 |  |  | 3.4 | 2.05 | 30 |  | NO | 2 | 208/3 | 3.5 | 140 | 150 | 1364 | 12.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 12.5-Ton - SE - 208/3 - 30kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1503 |  |  | DSH1503
DAIKIN | DSH1503 | 12.5 | 4706 | 0.5 | 144859 | 109043 | 14.20 IEER/10.60 EER | 80 | 67 | 58.9 | 57.2 | - | - | - | - | - | 143000 | 85500 |  |  | 3.4 | 2.05 | 15 |  | NO | 2 | 208/3 | 3.5 | 104 | 110 | 1364 | 12.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 12.5-Ton - SE - 208/3 - 15kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1503 |  |  | DSH1503
DAIKIN | DSH1503 | 12.5 | 4706 | 0.5 | 144859 | 109043 | 14.20 IEER/10.60 EER | 80 | 67 | 58.9 | 57.2 | - | - | - | - | - | 143000 | 85500 |  |  | 3.4 | 2.05 | - | - | NO | 2 | 208/3 | 3.5 | 65.1 | 80 | 1364 | 12.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 12.5-Ton - SE - 208/3 - 0kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1503 |  |  | DSH1503
DAIKIN | DSH1204 | 10 | 4153 | 0.5 | 117158 | 94737 | 15.2 IEER/11.4 EER | 80 | 67 | 59.3 | 58.1 | - | - | - | - | - | 116000 | 66000 |  |  | 3.4 | 2.25 | 45 |  | NO | 2 | 460/3 | 3.5 | 94.9 | 100 | 1169 | 10 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 10-Ton - SE - 460/3 - 45kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1204 |  |  | DSH1204
DAIKIN | DSH1023 | 8.5 | 3438 | 0.5 | 99572 | 80653 | 15.5 IEER/11.4 EER | 80 | 67 | 58.7 | 57.9 | - | - | - | - | - | 97000 | 56000 |  |  | 3.4 | 2.25 | - | - | NO | 2 | 208/3 | 2.4 | 43.7 | 50 | 1157 | 8.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 8.5-Ton - SE - 208/3 - 0kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1023 |  |  | DSH1023
DAIKIN | DSH1203 | 10 | 4153 | 0.5 | 117158 | 94737 | 15.2 IEER/11.4 EER | 80 | 67 | 59.3 | 58.1 | - | - | - | - | - | 116000 | 66000 |  |  | 3.4 | 2.25 | 45 |  | NO | 2 | 208/3 | 3.5 | 172 | 175 | 1169 | 10 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 10-Ton - SE - 208/3 - 45kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1203 |  |  | DSH1203
DAIKIN | DSH1203 | 10 | 4153 | 0.5 | 117158 | 94737 | 15.2 IEER/11.4 EER | 80 | 67 | 59.3 | 58.1 | - | - | - | - | - | 116000 | 66000 |  |  | 3.4 | 2.25 | 30 |  | NO | 2 | 208/3 | 3.5 | 133 | 150 | 1169 | 10 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 10-Ton - SE - 208/3 - 30kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1203 |  |  | DSH1203
DAIKIN | DSH1204 | 10 | 4153 | 0.5 | 117158 | 94737 | 15.2 IEER/11.4 EER | 80 | 67 | 59.3 | 58.1 | - | - | - | - | - | 116000 | 66000 |  |  | 3.4 | 2.25 | 15 |  | NO | 2 | 460/3 | 3.5 | 49.8 | 50 | 1169 | 10 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 10-Ton - SE - 460/3 - 15kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1204 |  |  | DSH1204
DAIKIN | DSH1204 | 10 | 4153 | 0.5 | 117158 | 94737 | 15.2 IEER/11.4 EER | 80 | 67 | 59.3 | 58.1 | - | - | - | - | - | 116000 | 66000 |  |  | 3.4 | 2.25 | - | - | NO | 2 | 460/3 | 3.5 | 27.3 | 30 | 1169 | 10 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 10-Ton - SE - 460/3 - 0kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1204 |  |  | DSH1204
DAIKIN | DSH1203 | 10 | 4153 | 0.5 | 117158 | 94737 | 15.2 IEER/11.4 EER | 80 | 67 | 59.3 | 58.1 | - | - | - | - | - | 116000 | 66000 |  |  | 3.4 | 2.25 | 15 |  | NO | 2 | 208/3 | 3.5 | 94.3 | 100 | 1169 | 10 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 10-Ton - SE - 208/3 - 15kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1203 |  |  | DSH1203
DAIKIN | DSH1203 | 10 | 4153 | 0.5 | 117158 | 94737 | 15.2 IEER/11.4 EER | 80 | 67 | 59.3 | 58.1 | - | - | - | - | - | 116000 | 66000 |  |  | 3.4 | 2.25 | - | - | NO | 2 | 208/3 | 3.5 | 55.2 | 70 | 1169 | 10 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 10-Ton - SE - 208/3 - 0kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1203 |  |  | DSH1203
DAIKIN | DSH1024 | 8.5 | 3438 | 0.5 | 99572 | 80653 | 15.5 IEER/11.4 EER | 80 | 67 | 58.7 | 57.9 | - | - | - | - | - | 97000 | 56000 |  |  | 3.4 | 2.25 | 45 |  | NO | 2 | 460/3 | 2.4 | 89.2 | 90 | 1157 | 8.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 8.5-Ton - SE - 460/3 - 45kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1024 |  |  | DSH1024
DAIKIN | DSH1024 | 8.5 | 3438 | 0.5 | 99572 | 80653 | 15.5 IEER/11.4 EER | 80 | 67 | 58.7 | 57.9 | - | - | - | - | - | 97000 | 56000 |  |  | 3.4 | 2.25 | 30 |  | NO | 2 | 460/3 | 2.4 | 66.6 | 70 | 1157 | 8.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 8.5-Ton - SE - 460/3 - 30kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1024 |  |  | DSH1024
DAIKIN | DSH1024 | 8.5 | 3438 | 0.5 | 99572 | 80653 | 15.5 IEER/11.4 EER | 80 | 67 | 58.7 | 57.9 | - | - | - | - | - | 97000 | 56000 |  |  | 3.4 | 2.25 | 15 |  | NO | 2 | 460/3 | 2.4 | 44.1 | 45 | 1157 | 8.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 8.5-Ton - SE - 460/3 - 15kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1024 |  |  | DSH1024
DAIKIN | DSH1024 | 8.5 | 3438 | 0.5 | 99572 | 80653 | 15.5 IEER/11.4 EER | 80 | 67 | 58.7 | 57.9 | - | - | - | - | - | 97000 | 56000 |  |  | 3.4 | 2.25 | - | - | NO | 2 | 460/3 | 2.4 | 21.5 | 25 | 1157 | 8.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 8.5-Ton - SE - 460/3 - 0kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1024 |  |  | DSH1024
DAIKIN | DSH1023 | 8.5 | 3438 | 0.5 | 99572 | 80653 | 15.5 IEER/11.4 EER | 80 | 67 | 58.7 | 57.9 | - | - | - | - | - | 97000 | 56000 |  |  | 3.4 | 2.25 | 45 |  | NO | 2 | 208/3 | 2.4 | 161 | 175 | 1157 | 8.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 8.5-Ton - SE - 208/3 - 45kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1023 |  |  | DSH1023
DAIKIN | DSH1023 | 8.5 | 3438 | 0.5 | 99572 | 80653 | 15.5 IEER/11.4 EER | 80 | 67 | 58.7 | 57.9 | - | - | - | - | - | 97000 | 56000 |  |  | 3.4 | 2.25 | 30 |  | NO | 2 | 208/3 | 2.4 | 122 | 125 | 1157 | 8.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 8.5-Ton - SE - 208/3 - 30kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1023 |  |  | DSH1023
DAIKIN | DSH1023 | 8.5 | 3438 | 0.5 | 99572 | 80653 | 15.5 IEER/11.4 EER | 80 | 67 | 58.7 | 57.9 | - | - | - | - | - | 97000 | 56000 |  |  | 3.4 | 2.25 | 15 |  | NO | 2 | 208/3 | 2.4 | 82.8 | 90 | 1157 | 8.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 8.5-Ton - SE - 208/3 - 15kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH1023 |  |  | DSH1023
DAIKIN | DSH0904 | 7.5 | 3133 | 0.5 | 86489 | 69011 | 16 IEER/11.4 EER | 80 | 67 | 60 | 58.3 | - | - | - | - | - | 86000 | 50000 |  |  | 3.4 | 2.25 | 45 |  | NO | 2 | 460/3 | 2.4 | 87.7 | 90 | 1157 | 7.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 7.5-Ton - SE - 460/3 - 45kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH0904 |  |  | DSH0904
DAIKIN | DSH0904 | 7.5 | 3133 | 0.5 | 86489 | 69011 | 16 IEER/11.4 EER | 80 | 67 | 60 | 58.3 | - | - | - | - | - | 86000 | 50000 |  |  | 3.4 | 2.25 | 30 |  | NO | 2 | 460/3 | 2.4 | 65.2 | 70 | 1157 | 7.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 7.5-Ton - SE - 460/3 - 30kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH0904 |  |  | DSH0904
DAIKIN | DSH0904 | 7.5 | 3133 | 0.5 | 86489 | 69011 | 16 IEER/11.4 EER | 80 | 67 | 60 | 58.3 | - | - | - | - | - | 86000 | 50000 |  |  | 3.4 | 2.25 | 15 |  | NO | 2 | 460/3 | 2.4 | 42.6 | 45 | 1157 | 7.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 7.5-Ton - SE - 460/3 - 15kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH0904 |  |  | DSH0904
DAIKIN | DSH0904 | 7.5 | 3133 | 0.5 | 86489 | 69011 | 16 IEER/11.4 EER | 80 | 67 | 60 | 58.3 | - | - | - | - | - | 86000 | 50000 |  |  | 3.4 | 2.25 | - | - | NO | 2 | 460/3 | 2.4 | 20.1 | 25 | 1157 | 7.5 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 7.5-Ton - SE - 460/3 - 0kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH0904 |  |  | DSH0904
DAIKIN | DSH0903 | 7.5 | 3133 | 0.5 | 86489 | 69011 | 16 IEER/11.4 EER | 80 | 67 | 60 | 58.3 | - | - | - | - | - | 86000 | 50000 |  |  | 3.4 | 2.25 | 45 |  | NO | 2 | 208/3 | 2.4 | 157 | 175 | 1157 | 7.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 7.5-Ton - SE - 208/3 - 45kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH0903 |  |  | DSH0903
DAIKIN | DSH0903 | 7.5 | 3133 | 0.5 | 86489 | 69011 | 16 IEER/11.4 EER | 80 | 67 | 60 | 58.3 | - | - | - | - | - | 86000 | 50000 |  |  | 3.4 | 2.25 | 30 |  | NO | 2 | 208/3 | 2.4 | 118 | 125 | 1157 | 7.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 7.5-Ton - SE - 208/3 - 30kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH0903 |  |  | DSH0903
DAIKIN | DSH0903 | 7.5 | 3133 | 0.5 | 86489 | 69011 | 16 IEER/11.4 EER | 80 | 67 | 60 | 58.3 | - | - | - | - | - | 86000 | 50000 |  |  | 3.4 | 2.25 | 15 |  | NO | 2 | 208/3 | 2.4 | 78.5 | 80 | 1157 | 7.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 7.5-Ton - SE - 208/3 - 15kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH0903 |  |  | DSH0903
DAIKIN | DSH0903 | 7.5 | 3133 | 0.5 | 86489 | 69011 | 16 IEER/11.4 EER | 80 | 67 | 60 | 58.3 | - | - | - | - | - | 86000 | 50000 |  |  | 3.4 | 2.25 | - | - | NO | 2 | 208/3 | 2.4 | 39.4 | 50 | 1157 | 7.5 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 7.5-Ton - SE - 208/3 - 0kW | ENGINEERING MANUAL - DSH (7.5-12.5) | [5 empty] | INSTALLATION MANUAL - DSH (7.5-12.5) |  |  | DSH0903 |  |  | DSH0903
DAIKIN | DSH0723 | 6 | 2183 | 0.5 | 67442 | 50799 | 16.70 IEER/11.30 EER | 80 | 67 | 58.8 | 57.2 | - | - | - | - | - | 67000 | - |  |  | 3.4 | 2.25 | 5 |  | NO | 2 | 208/3 | 1.2 | 40.9 | 50 | 645 | 6 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 6-Ton - SE - 208/3 - 5kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0723 |  |  | DSH0723
DAIKIN | DSH0724 | 6 | 2183 | 0.5 | 67442 | 50799 | 16.70 IEER/11.30 EER | 80 | 67 | 58.8 | 57.2 | - | - | - | - | - | 67000 | - |  |  | 3.4 | 2.25 | 30 |  | NO | 2 | 460/3 | 1.2 | 57.8 | 60 | 645 | 6 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 6-Ton - SE - 460/3 - 30kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0724 |  |  | DSH0724
DAIKIN | DSH0724 | 6 | 2183 | 0.5 | 67442 | 50799 | 16.70 IEER/11.30 EER | 80 | 67 | 58.8 | 57.2 | - | - | - | - | - | 67000 | - |  |  | 3.4 | 2.25 | 15 |  | NO | 2 | 460/3 | 1.2 | 35.3 | 40 | 645 | 6 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 6-Ton - SE - 460/3 - 15kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0724 |  |  | DSH0724
DAIKIN | DSH0724 | 6 | 2183 | 0.5 | 67442 | 50799 | 16.70 IEER/11.30 EER | 80 | 67 | 58.8 | 57.2 | - | - | - | - | - | 67000 | - |  |  | 3.4 | 2.25 | 10 |  | NO | 2 | 460/3 | 1.2 | 27.7 | 30 | 645 | 6 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 6-Ton - SE - 460/3 - 10kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0724 |  |  | DSH0724
DAIKIN | DSH0724 | 6 | 2183 | 0.5 | 67442 | 50799 | 16.70 IEER/11.30 EER | 80 | 67 | 58.8 | 57.2 | - | - | - | - | - | 67000 | - |  |  | 3.4 | 2.25 | - | - | NO | 2 | 460/3 | 1.2 | 12.7 | 15 | 645 | 6 | 460/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 6-Ton - SE - 460/3 - 0kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0724 |  |  | DSH0724
DAIKIN | DSH0723 | 6 | 2183 | 0.5 | 67442 | 50799 | 16.70 IEER/11.30 EER | 80 | 67 | 58.8 | 57.2 | - | - | - | - | - | 67000 | - |  |  | 3.4 | 2.25 | 30 |  | NO | 2 | 208/3 | 1.2 | 106 | 110 | 645 | 6 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 6-Ton - SE - 208/3 - 30kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0723 |  |  | DSH0723
DAIKIN | DSH0723 | 6 | 2183 | 0.5 | 67442 | 50799 | 16.70 IEER/11.30 EER | 80 | 67 | 58.8 | 57.2 | - | - | - | - | - | 67000 | - |  |  | 3.4 | 2.25 | 20 |  | NO | 2 | 208/3 | 1.2 | 79.7 | 80 | 645 | 6 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 6-Ton - SE - 208/3 - 20kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0723 |  |  | DSH0723
DAIKIN | DSH0723 | 6 | 2183 | 0.5 | 67442 | 50799 | 16.70 IEER/11.30 EER | 80 | 67 | 58.8 | 57.2 | - | - | - | - | - | 67000 | - |  |  | 3.4 | 2.25 | 15 |  | NO | 2 | 208/3 | 1.2 | 67 | 70 | 645 | 6 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 6-Ton - SE - 208/3 - 15kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0723 |  |  | DSH0723
DAIKIN | DSH0723 | 6 | 2183 | 0.5 | 67442 | 50799 | 16.70 IEER/11.30 EER | 80 | 67 | 58.8 | 57.2 | - | - | - | - | - | 67000 | - |  |  | 3.4 | 2.25 | 10 |  | NO | 2 | 208/3 | 1.2 | 53.8 | 60 | 645 | 6 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 6-Ton - SE - 208/3 - 10kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0723 |  |  | DSH0723
DAIKIN | DSH0723 | 6 | 2183 | 0.5 | 67442 | 50799 | 16.70 IEER/11.30 EER | 80 | 67 | 58.8 | 57.2 | - | - | - | - | - | 67000 | - |  |  | 3.4 | 2.25 | - | - | NO | 2 | 208/3 | 1.2 | 27.9 | 40 | 645 | 6 | 208/3 | HEAT PUMP | STANDARD | 2 | - | NO |  |  | 6-Ton - SE - 208/3 - 0kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0723 |  |  | DSH0723
DAIKIN | DSH0604 | 5 | 2071 | 0.5 | 58342 | 47695 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.1 | 58.1 | - | - | - | - | - | 55000 | - |  |  | - | - | 15 |  | NO | 1 | 460/3 | 1.2 | 35.5 | 40 | 600 | 5 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 5-Ton - SE - 460/3 - 15kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0604 |  |  | DSH0604
DAIKIN | DSH0604 | 5 | 2071 | 0.5 | 58342 | 47695 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.1 | 58.1 | - | - | - | - | - | 55000 | - |  |  | - | - | 10 |  | NO | 1 | 460/3 | 1.2 | 28 | 30 | 600 | 5 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 5-Ton - SE - 460/3 - 10kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0604 |  |  | DSH0604
DAIKIN | DSH0604 | 5 | 2071 | 0.5 | 58342 | 47695 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.1 | 58.1 | - | - | - | - | - | 55000 | - |  |  | - | - | 5 |  | NO | 1 | 460/3 | 1.2 | 20.5 | 25 | 600 | 5 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 5-Ton - SE - 460/3 - 5kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0604 |  |  | DSH0604
DAIKIN | DSH0604 | 5 | 2071 | 0.5 | 58342 | 47695 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.1 | 58.1 | - | - | - | - | - | 55000 | - |  |  | - | - | - | - | NO | 1 | 460/3 | 1.2 | 13 | 20 | 600 | 5 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 5-Ton - SE - 460/3 - 0kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0604 |  |  | DSH0604
DAIKIN | DSH0603 | 5 | 2060 | 0.5 | 58296 | 47539 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59 | 58.1 | - | - | - | - | - | 55000 | - |  |  | - | - | 20 |  | NO | 1 | 208/3 | 1 | 82.4 | 90 | 596 | 5 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 5-Ton - SE - 208/3 - 20kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0603 |  |  | DSH0603
DAIKIN | DSH0603 | 5 | 2060 | 0.5 | 58296 | 47539 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59 | 58.1 | - | - | - | - | - | 55000 | - |  |  | - | - | 15 |  | NO | 1 | 208/3 | 1 | 69.6 | 70 | 596 | 5 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 5-Ton - SE - 208/3 - 15kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0603 |  |  | DSH0603
DAIKIN | DSH0603 | 5 | 2060 | 0.5 | 58296 | 47539 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59 | 58.1 | - | - | - | - | - | 55000 | - |  |  | - | - | 5 |  | NO | 1 | 208/3 | 1 | 43.5 | 50 | 596 | 5 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 5-Ton - SE - 208/3 - 5kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0603 |  |  | DSH0603
DAIKIN | DSH0603 | 5 | 2060 | 0.5 | 58296 | 47539 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59 | 58.1 | - | - | - | - | - | 55000 | - |  |  | - | - | - | - | NO | 1 | 208/3 | 1 | 30.5 | 45 | 596 | 5 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 5-Ton - SE - 208/3 - 0kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0603 |  |  | DSH0603
DAIKIN | DSH0484 | 4 | 1604 | 0.5 | 46090 | 36667 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.2 | 58 | - | - | - | - | - | 45000 | - |  |  | - | - | 20 |  | NO | 1 | 460/3 | 1.2 | 40.5 | 45 | 586 | 4 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 4-Ton - SE - 460/3 - 20kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0484 |  |  | DSH0484
DAIKIN | DSH0484 | 4 | 1604 | 0.5 | 46090 | 36667 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.2 | 58 | - | - | - | - | - | 45000 | - |  |  | - | - | 15 |  | NO | 1 | 460/3 | 1.2 | 33 | 35 | 586 | 4 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 4-Ton - SE - 460/3 - 15kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0484 |  |  | DSH0484
DAIKIN | DSH0484 | 4 | 1604 | 0.5 | 46090 | 36667 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.2 | 58 | - | - | - | - | - | 45000 | - |  |  | - | - | 10 |  | NO | 1 | 460/3 | 1.2 | 25.4 | 30 | 586 | 4 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 4-Ton - SE - 460/3 - 10kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0484 |  |  | DSH0484
DAIKIN | DSH0484 | 4 | 1604 | 0.5 | 46090 | 36667 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.2 | 58 | - | - | - | - | - | 45000 | - |  |  | - | - | 5 |  | NO | 1 | 460/3 | 1.2 | 17.9 | 20 | 586 | 4 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 4-Ton - SE - 460/3 - 5kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0484 |  |  | DSH0484
DAIKIN | DSH0484 | 4 | 1604 | 0.5 | 46090 | 36667 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.2 | 58 | - | - | - | - | - | 45000 | - |  |  | - | - | - | - | NO | 1 | 460/3 | 1.2 | 10.4 | 15 | 586 | 4 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 4-Ton - SE - 460/3 - 0kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0484 |  |  | DSH0484
DAIKIN | DSH0483 | 4 | 1604 | 0.5 | 46090 | 36667 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.2 | 58 | - | - | - | - | - | 45000 | - |  |  | - | - | 20 |  | NO | 1 | 208/3 | 1 | 75.4 | 80 | 582 | 4 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 4-Ton - SE - 208/3 - 20kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0483 |  |  | DSH0483
DAIKIN | DSH0483 | 4 | 1604 | 0.5 | 46090 | 36667 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.2 | 58 | - | - | - | - | - | 45000 | - |  |  | - | - | 15 |  | NO | 1 | 208/3 | 1 | 62.6 | 70 | 582 | 4 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 4-Ton - SE - 208/3 - 15kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0483 |  |  | DSH0483
DAIKIN | DSH0483 | 4 | 1604 | 0.5 | 46090 | 36667 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.2 | 58 | - | - | - | - | - | 45000 | - |  |  | - | - | 10 |  | NO | 1 | 208/3 | 1 | 49.5 | 50 | 582 | 4 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 4-Ton - SE - 208/3 - 10kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0483 |  |  | DSH0483
DAIKIN | DSH0483 | 4 | 1604 | 0.5 | 46090 | 36667 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.2 | 58 | - | - | - | - | - | 45000 | - |  |  | - | - | 5 |  | NO | 1 | 208/3 | 1 | 36.5 | 45 | 582 | 4 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 4-Ton - SE - 208/3 - 5kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0483 |  |  | DSH0483
DAIKIN | DSH0483 | 4 | 1604 | 0.5 | 46090 | 36667 | 13.70 SEER2/11.80 EER2 | 80 | 67 | 59.2 | 58 | - | - | - | - | - | 45000 | - |  |  | - | - | - | - | NO | 1 | 208/3 | 1 | 23.5 | 35 | 582 | 4 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 4-Ton - SE - 208/3 - 0kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0483 |  |  | DSH0483
DAIKIN | DSH0364 | 3 | 1272 | 0.5 | 35188 | 27662 | 14.0 SEER2/12.00 EER2 | 80 | 67 | 60.2 | 58.3 | - | - | - | - | - | 33600 | - |  |  | - | - | 15 |  | NO | 1 | 460/3 | 1.2 | 31.6 | 35 | 543 | 3 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 3-Ton - SE - 460/3 - 15kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0364 |  |  | DSH0364
DAIKIN | DSH0364 | 3 | 1272 | 0.5 | 35188 | 27662 | 14.0 SEER2/12.00 EER2 | 80 | 67 | 60.2 | 58.3 | - | - | - | - | - | 33600 | - |  |  | - | - | 10 |  | NO | 1 | 460/3 | 1.2 | 24.1 | 25 | 543 | 3 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 3-Ton - SE - 460/3 - 10kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0364 |  |  | DSH0364
DAIKIN | DSH0364 | 3 | 1272 | 0.5 | 35188 | 27662 | 14.0 SEER2/12.00 EER2 | 80 | 67 | 60.2 | 58.3 | - | - | - | - | - | 33600 | - |  |  | - | - | 5 |  | NO | 1 | 460/3 | 1.2 | 16.6 | 20 | 543 | 3 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 3-Ton - SE - 460/3 - 5kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0364 |  |  | DSH0364
DAIKIN | DSH0364 | 3 | 1272 | 0.5 | 35188 | 27662 | 14.0 SEER2/12.00 EER2 | 80 | 67 | 60.2 | 58.3 | - | - | - | - | - | 33600 | - |  |  | - | - | - | - | NO | 1 | 460/3 | 1.2 | 9.1 | 15 | 543 | 3 | 460/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 3-Ton - SE - 460/3 - 0kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0364 |  |  | DSH0364
DAIKIN | DSH0363 | 3 | 1303 | 0.5 | 35301 | 28087 | 14.0 SEER2/12.00 EER2 | 80 | 67 | 60.4 | 58.5 | - | - | - | - | - | 33600 | - |  |  | - | - | 15 |  | NO | 1 | 208/3 | 0.75 | 58.9 | 60 | 535 | 3 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 3-Ton - SE - 208/3 - 15kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0363 |  |  | DSH0363
DAIKIN | DSH0363 | 3 | 1303 | 0.5 | 35301 | 28087 | 14.0 SEER2/12.00 EER2 | 80 | 67 | 60.4 | 58.5 | - | - | - | - | - | 33600 | - |  |  | - | - | 10 |  | NO | 1 | 208/3 | 0.75 | 45.8 | 50 | 535 | 3 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 3-Ton - SE - 208/3 - 10kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0363 |  |  | DSH0363
DAIKIN | DSH0363 | 3 | 1303 | 0.5 | 35301 | 28087 | 14.0 SEER2/12.00 EER2 | 80 | 67 | 60.4 | 58.5 | - | - | - | - | - | 33600 | - |  |  | - | - | 5 |  | NO | 1 | 208/3 | 0.75 | 32.9 | 40 | 535 | 3 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 3-Ton - SE - 208/3 - 5kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0363 |  |  | DSH0363
DAIKIN | DSH0363 | 3 | 1303 | 0.5 | 35301 | 28087 | 14.0 SEER2/12.00 EER2 | 80 | 67 | 60.4 | 58.5 | - | - | - | - | - | 33600 | - |  |  | - | - | - | - | NO | 1 | 208/3 | 0.75 | 19.9 | 30 | 535 | 3 | 208/3 | HEAT PUMP | STANDARD | 1 | - | NO |  |  | 3-Ton - SE - 208/3 - 0kW | ENGINEERING MANUAL - DSH (3-6) | [5 empty] | INSTALLATION MANUAL - DSH (3-6) |  |  | DSH0363 |  |  | DSH0363
DAIKIN | DVH1204 | 10 | 4120 | 1 | 128803 | 94756 | 20.0 IEER/12.1 EER | 80 | 67 | 59.1 | 57.1 | - | - | - | - | - | 114000 | 80000 |  |  | 3.74 | 2.5 | - | - | YES | Variable | 460/3 | 3.5 | 26.5 | 35 | 1293 | 10 | 460/3 | HEAT PUMP | MZVAV | Variable | - | YES |  |  | 10-Ton - MZVAV - HGRH - 460-3 - 0kW | ENGINEERING MANUAL - DVH (7.5-10) | [5 empty] | INSTALLATION MANUAL - DVH (7.5-10) |  |  | DVH1204 |  |  | DVH1204
DAIKIN | DVH1203 | 10 | 4120 | 1 | 128803 | 94756 | 20.0 IEER/12.1 EER | 80 | 67 | 59.1 | 57.1 | - | - | - | - | - | 114000 | 80000 |  |  | 3.74 | 2.5 | - | - | YES | Variable | 208/3 | 3.5 | 54 | 70 | 1293 | 10 | 208/3 | HEAT PUMP | MZVAV | Variable | - | YES |  |  | 10-Ton - MZVAV - HGRH - 208-3 - 0kW | ENGINEERING MANUAL - DVH (7.5-10) | [5 empty] | INSTALLATION MANUAL - DVH (7.5-10) |  |  | DVH1203 |  |  | DVH1203
DAIKIN | DVH1024 | 8.5 | 3800 | 1 | 111575 | 84874 | 20.0 IEER/12.3 EER | 80 | 67 | 59.7 | 57.7 | - | - | - | - | - | 102000 | 72000 |  |  | 3.85 | 2.5 | - | - | YES | Variable | 460/3 | 3.5 | 26 | 30 | 1293 | 8.5 | 460/3 | HEAT PUMP | MZVAV | Variable | - | YES |  |  | 8.5-Ton - MZVAV - HGRH - 460-3 - 0kW | ENGINEERING MANUAL - DVH (7.5-10) | [5 empty] | INSTALLATION MANUAL - DVH (7.5-10) |  |  | DVH1024 |  |  | DVH1024
DAIKIN | DVH1023 | 8.5 | 3800 | 1 | 111575 | 84874 | 20.0 IEER/12.3 EER | 80 | 67 | 59.7 | 57.7 | - | - | - | - | - | 102000 | 72000 |  |  | 3.85 | 2.5 | - | - | YES | Variable | 208/3 | 3.5 | 52.7 | 60 | 1293 | 8.5 | 208/3 | HEAT PUMP | MZVAV | Variable | - | YES |  |  | 8.5-Ton - MZVAV - HGRH - 208-3 - 0kW | ENGINEERING MANUAL - DVH (7.5-10) | [5 empty] | INSTALLATION MANUAL - DVH (7.5-10) |  |  | DVH1023 |  |  | DVH1023
DAIKIN | DVH0904 | 7.5 | 3600 | 1 | 102928 | 79341 | 20.0 IEER/12.4 EER | 80 | 67 | 60 | 58 | - | - | - | - | - | 90000 | 63000 |  |  | 3.85 | 2.5 | - | - | YES | Variable | 460/3 | 3.5 | 24.8 | 30 | 1293 | 7.5 | 460/3 | HEAT PUMP | MZVAV | Variable | - | YES |  |  | 7.5-Ton - MZVAV - HGRH - 460-3 - 0kW | ENGINEERING MANUAL - DVH (7.5-10) | [5 empty] | INSTALLATION MANUAL - DVH (7.5-10) |  |  | DVH0904 |  |  | DVH0904
DAIKIN | DVH0903 | 7.5 | 3600 | 1 | 102928 | 79341 | 20.0 IEER/12.4 EER | 80 | 67 | 60 | 58 | - | - | - | - | - | 90000 | 63000 |  |  | 3.85 | 2.5 | - | - | YES | Variable | 208/3 | 3.5 | 49.9 | 60 | 1293 | 7.5 | 208/3 | HEAT PUMP | MZVAV | Variable | - | YES |  |  | 7.5-Ton - MZVAV - HGRH - 208-3 - 0kW | ENGINEERING MANUAL - DVH (7.5-10) | [5 empty] | INSTALLATION MANUAL - DVH (7.5-10) |  |  | DVH0903 |  |  | DVH0903

## SCHEDULE NOTES
Provide with economizer with enthalpy sensor
Provide with factory installed disconnect
Provide with factory installed, field powered 115V GFCI outlet
Provide with 7-day programmable thermostat
Provide with 7-day programmable BACnet thermostat
Provide with factory installed DDC controller with BAS input and 7-day programmable thermostat
Provide with 24" factory roofcurb