## SCHEDULE
SCHEDULE RANGE | [26 empty] | FILTERS | [7 empty] | DOCUMENTATION | [20 empty] | REFRIGERANT CALCULATIONS
SPLIT SYSTEM SCHEDULE | [26 empty] | SIZE | NOMINAL EFFICIENCY | COMPRESSOR STAGES | COIL ORIENTATION | GAS STAGES | GAS INPUT | GAS OUTPUT | AFUE (%) | SUBMITTAL (OUTDOOR UNIT) | SUBMITTAL (COIL) | SUBMITTAL (FURNACE) | SUBMITTAL (SYSTEM) | ENGINEERING MANUAL (SYSTEM) | ENGINEERING MANUAL (OUTDOOR UNIT) | ENGINEERING MANUAL (COIL) | ENGINEERING MANUAL (FURNACE) | INSTALLATION MANUAL (OUTDOOR) | INSTALLATION MANUAL (FURNACE) | INSTALLATION MANUAL (COIL) | REVIT (OUTDOOR) | REVIT (FURNACE) | REVIT (COIL) | REVIT (SYSTEM) | CAD (OUTDOOR) | CAD (FURNACE) | CAD (COIL) | CAD (SYSTEM) | CONTROLS OPTIONS | OPERATION MANUAL | REFRIGERANT | MAX VERTICAL SEPARATION (ODU TO IDU) (FT) | MAX VERTICAL SEPARATION (IDU TO IDU) (FT) | MAX TOTAL LINE SET (FT) | LIQUID LINE CONNECTION (IN) | SUCTION LINE CONNECTION (IN) | PRE-CHARGE PIPING LENGTH (FT) | FACTORY CHARGE (LBS) | FACTORY CHARGE (OZ) | ADDITIONAL CHARGE (OZ/FT)
INDOOR AIR HANDLING UNIT | [16 empty] | OUTDOOR CONDENSING UNIT
MAKE | MODEL (COIL / FURNACE) | SUPPLY FAN |  |  | COOLING |  |  | GAS HEATING |  |  |  |  | ELECTRICAL DATA |  |  | WEIGHT (COIL & FURNACE) | MAKE | MODEL | ELECTRICAL DATA |  |  | OUTDOOR AMBIENT (COOLING) | REFRIGERANT | EFFICIENCY (SEER2 / EER2) | WEIGHT | COMPRESSOR STAGES
|  | AIRFLOW (CFM) | MOTOR (HP) | MOTOR TYPE | EAT (DB) | EAT (WB) | TOTAL CAPACITY | GAS INPUT | GAS OUTPUT | TEMP RISE | STAGES | AFUE (%) | VOLTAGE / PHASE | MCA | MOP |  |  |  | VOLTAGE / PHASE | MCA | MOP
DAIKIN | CAPEA2418B3 / DR80TC0603BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 156 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 18 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC6VSS2410 | CAPEA2418B3 | DR80TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR80TC0603BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 163 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC6VSS3010 | CAPEA3022B3 | DR80TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR80TC0603BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 163 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC6VSS1810 | CAPEA3022B3 | DR80TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626B3 / DR80TC0603BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 168 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC6VSS3610 | CAPEA3626B3 | DR80TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80TC0603BN | 840 | 0.5 | ECM | 80 | 67 | 24000 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 158 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 18 / 13 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC7TCA2410 | CAPTA2422B3 | DR80TC0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80TC0603BN | 1120 | 0.5 | ECM | 80 | 67 | 35000 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 165 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17 / 13 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC7TCA3610 | CAPTA3626B3 | DR80TC0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR80TC0603BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 168 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 17.5 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 60000 | 48000 | 80 | DC6VSS2410 | CHPEA2422B3 | DR80TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR80TC0603BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 168 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 60000 | 48000 | 80 | DC6VSS1810 | CHPEA2422B3 | DR80TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026B3 / DR80TC0603BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 176 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 60000 | 48000 | 80 | DC6VSS3010 | CHPEA3026B3 | DR80TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626B3 / DR80TC0603BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 178 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 60000 | 48000 | 80 | DC6VSS3610 | CHPEA3626B3 | DR80TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80TC0603BN | 840 | 0.5 | ECM | 80 | 67 | 23600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 170 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 18 / 13 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 60000 | 48000 | 80 | DC7TCA2410 | CHPTA2426B3 | DR80TC0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80TC0603BN | 1120 | 0.5 | ECM | 80 | 67 | 34600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 180 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 60000 | 48000 | 80 | DC7TCA3610 | CHPTA3630B3 | DR80TC0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA2418B3 / DR80TC0604BN | 800 | 0.75 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 157 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 18 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC6VSS2410 | CAPEA2418B3 | DR80TC0604BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR80TC0604BN | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 164 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC6VSS3010 | CAPEA3022B3 | DR80TC0604BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR80TC0604BN | 610 | 0.75 | ECM | 80 | 67 | 17100 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 164 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC6VSS1810 | CAPEA3022B3 | DR80TC0604BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626B3 / DR80TC0604BN | 1260 | 0.75 | ECM | 80 | 67 | 33600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 169 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC6VSS3610 | CAPEA3626B3 | DR80TC0604BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80TC0604BN | 840 | 0.75 | ECM | 80 | 67 | 24000 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 159 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 18 / 13 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC7TCA2410 | CAPTA2422B3 | DR80TC0604BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80TC0604BN | 1120 | 0.75 | ECM | 80 | 67 | 35000 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 166 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17 / 13 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC7TCA3610 | CAPTA3626B3 | DR80TC0604BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR80TC0604BN | 800 | 0.75 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 169 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 17.5 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 60000 | 48000 | 80 | DC6VSS2410 | CHPEA2422B3 | DR80TC0604BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR80TC0604BN | 610 | 0.75 | ECM | 80 | 67 | 17100 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 169 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 60000 | 48000 | 80 | DC6VSS1810 | CHPEA2422B3 | DR80TC0604BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026B3 / DR80TC0604BN | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 177 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 60000 | 48000 | 80 | DC6VSS3010 | CHPEA3026B3 | DR80TC0604BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626B3 / DR80TC0604BN | 1260 | 0.75 | ECM | 80 | 67 | 33600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 179 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 60000 | 48000 | 80 | DC6VSS3610 | CHPEA3626B3 | DR80TC0604BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80TC0604BN | 840 | 0.75 | ECM | 80 | 67 | 23600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 171 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 18 / 13 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 60000 | 48000 | 80 | DC7TCA2410 | CHPTA2426B3 | DR80TC0604BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80TC0604BN | 1120 | 0.75 | ECM | 80 | 67 | 35000 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 181 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 60000 | 48000 | 80 | DC7TCA3610 | CHPTA3630B3 | DR80TC0604BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA2418B3 / DR80TC0803BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 158 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 18 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS2410 | CAPEA2418B3 | DR80TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR80TC0803BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 165 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS3010 | CAPEA3022B3 | DR80TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR80TC0803BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 165 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS1810 | CAPEA3022B3 | DR80TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626B3 / DR80TC0803BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 170 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS3610 | CAPEA3626B3 | DR80TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80TC0803BN | 840 | 0.5 | ECM | 80 | 67 | 24000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 160 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 18 / 13 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC7TCA2410 | CAPTA2422B3 | DR80TC0803BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80TC0803BN | 1120 | 0.5 | ECM | 80 | 67 | 35000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 167 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17 / 13 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC7TCA3610 | CAPTA3626B3 | DR80TC0803BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR80TC0803BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 170 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 17.5 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS2410 | CHPEA2422B3 | DR80TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR80TC0803BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 170 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS1810 | CHPEA2422B3 | DR80TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026B3 / DR80TC0803BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 178 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS3010 | CHPEA3026B3 | DR80TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626B3 / DR80TC0803BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 180 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS3610 | CHPEA3626B3 | DR80TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80TC0803BN | 840 | 0.5 | ECM | 80 | 67 | 23600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 172 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 18 / 13 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 64000 | 80 | DC7TCA2410 | CHPTA2426B3 | DR80TC0803BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80TC0803BN | 1120 | 0.5 | ECM | 80 | 67 | 35000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 182 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 64000 | 80 | DC7TCA3610 | CHPTA3630B3 | DR80TC0803BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA2418C3 / DR80TC0804CN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 175 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 18 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS2410 | CAPEA2418C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022C3 / DR80TC0804CN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 182 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS3010 | CAPEA3022C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022C3 / DR80TC0804CN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 182 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS1810 | CAPEA3022C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626C3 / DR80TC0804CN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 185 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16.6 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS3610 | CAPEA3626C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR80TC0804CN | 1380 | 0.5 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 194 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.2 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS4810 | CAPEA4830C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR80TC0804CN | 1320 | 0.5 | ECM | 80 | 67 | 41000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 194 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS4210 | CAPEA4830C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA6030C3 / DR80TC0804CN | 1640 | 0.5 | ECM | 80 | 67 | 52000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 196 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.5 / 8.5 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS6010 | CAPEA6030C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80TC0804CN | 840 | 0.5 | ECM | 80 | 67 | 24000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 176 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 18.2 / 13 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC7TCA2410 | CAPTA2422C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80TC0804CN | 1150 | 0.5 | ECM | 80 | 67 | 35400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 186 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17.2 / 13 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC7TCA3610 | CAPTA3626C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TC0804CN | 1380 | 0.5 | ECM | 80 | 67 | 46000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 197 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.5 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC7TCA4810 | CAPTA6030C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026C3 / DR80TC0804CN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 193 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS3010 | CHPEA3026C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626C3 / DR80TC0804CN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 197 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16.6 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS3610 | CHPEA3626C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR80TC0804CN | 1380 | 0.5 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 204 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.2 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS4810 | CHPEA4830C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR80TC0804CN | 1320 | 0.5 | ECM | 80 | 67 | 41000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 204 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS4210 | CHPEA4830C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA6030C3 / DR80TC0804CN | 1640 | 0.5 | ECM | 80 | 67 | 52000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 204 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.2 / 8.2 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS6010 | CHPEA6030C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR80TC0804CN | 840 | 0.5 | ECM | 80 | 67 | 23600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 188 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 18 / 13 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 64000 | 80 | DC7TCA2410 | CHPTA2426C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80TC0804CN | 1150 | 0.5 | ECM | 80 | 67 | 35000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 198 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17.2 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 64000 | 80 | DC7TCA3610 | CHPTA3630C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR80TC0804CN | 1380 | 0.5 | ECM | 80 | 67 | 45000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 7.75 | 15 | 202 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.2 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 64000 | 80 | DC7TCA4810 | CHPTA4830C3 | DR80TC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA2418C3 / DR80TC0805CN | 800 | 0.75 | ECM | 80 | 67 | 23200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 175 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 18 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS2410 | CAPEA2418C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022C3 / DR80TC0805CN | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 182 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS3010 | CAPEA3022C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022C3 / DR80TC0805CN | 610 | 0.75 | ECM | 80 | 67 | 17100 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 182 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS1810 | CAPEA3022C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626C3 / DR80TC0805CN | 1260 | 0.75 | ECM | 80 | 67 | 33600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 185 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16.6 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS3610 | CAPEA3626C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR80TC0805CN | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 194 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.2 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS4810 | CAPEA4830C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR80TC0805CN | 1320 | 0.75 | ECM | 80 | 67 | 41000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 194 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS4210 | CAPEA4830C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA6030C3 / DR80TC0805CN | 1640 | 0.75 | ECM | 80 | 67 | 52000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 196 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.5 / 8.5 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS6010 | CAPEA6030C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80TC0805CN | 1120 | 0.75 | ECM | 80 | 67 | 35400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 186 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17.2 / 13 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC7TCA3610 | CAPTA3626C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TC0805CN | 1480 | 0.75 | ECM | 80 | 67 | 57000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 197 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 16.2 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC7TCA6010 | CAPTA6030C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TC0805CN | 1380 | 0.75 | ECM | 80 | 67 | 47000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 197 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.5 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC7TCA4810 | CAPTA6030C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026C3 / DR80TC0805CN | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 193 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS3010 | CHPEA3026C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626C3 / DR80TC0805CN | 1260 | 0.75 | ECM | 80 | 67 | 33600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 197 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16.6 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS3610 | CHPEA3626C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR80TC0805CN | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 204 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.2 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS4810 | CHPEA4830C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR80TC0805CN | 1320 | 0.75 | ECM | 80 | 67 | 41000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 204 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS4210 | CHPEA4830C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA6030C3 / DR80TC0805CN | 1640 | 0.75 | ECM | 80 | 67 | 52000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 204 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.2 / 8.2 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS6010 | CHPEA6030C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR80TC0805CN | 1380 | 0.75 | ECM | 80 | 67 | 46000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 202 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.2 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 64000 | 80 | DC7TCA4810 | CHPTA4830C3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80TC0805CN | 1480 | 0.75 | ECM | 80 | 67 | 56000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 206 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 64000 | 80 | DC7TCA6010 | CHPTA6030D3 | DR80TC0805CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626D3 / DR80TC0805DN | 1260 | 0.75 | ECM | 80 | 67 | 33600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 195 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16.6 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS3610 | CAPEA3626D3 | DR80TC0805DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830D3 / DR80TC0805DN | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 202 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.6 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS4810 | CAPEA4830D3 | DR80TC0805DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830D3 / DR80TC0805DN | 1320 | 0.75 | ECM | 80 | 67 | 41000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 202 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS4210 | CAPEA4830D3 | DR80TC0805DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA6030D3 / DR80TC0805DN | 1640 | 0.75 | ECM | 80 | 67 | 52500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 206 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.5 / 8.5 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC6VSS6010 | CAPEA6030D3 | DR80TC0805DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TC0805DN | 1480 | 0.75 | ECM | 80 | 67 | 57000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 202 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 16.2 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC7TCA6010 | CAPTA6030C3 | DR80TC0805DN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TC0805DN | 1380 | 0.75 | ECM | 80 | 67 | 46000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 202 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.5 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC7TCA4810 | CAPTA6030C3 | DR80TC0805DN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830D3 / DR80TC0805DN | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 212 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.6 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS4810 | CHPEA4830D3 | DR80TC0805DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830D3 / DR80TC0805DN | 1320 | 0.75 | ECM | 80 | 67 | 41000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 212 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS4210 | CHPEA4830D3 | DR80TC0805DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA6030D3 / DR80TC0805DN | 1640 | 0.75 | ECM | 80 | 67 | 52500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 209 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.5 / 8.4 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 64000 | 80 | DC6VSS6010 | CHPEA6030D3 | DR80TC0805DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80TC0805DN | 1480 | 0.75 | ECM | 80 | 67 | 56000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 211 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 64000 | 80 | DC7TCA6010 | CHPTA6030D3 | DR80TC0805DN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022C3 / DR80TC1005CN | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 188 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC6VSS3010 | CAPEA3022C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626C3 / DR80TC1005CN | 1260 | 0.75 | ECM | 80 | 67 | 33600 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 191 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16.6 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC6VSS3610 | CAPEA3626C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR80TC1005CN | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 200 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.2 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC6VSS4810 | CAPEA4830C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR80TC1005CN | 1320 | 0.75 | ECM | 80 | 67 | 41000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 200 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC6VSS4210 | CAPEA4830C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA6030C3 / DR80TC1005CN | 1640 | 0.75 | ECM | 80 | 67 | 52000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 202 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.5 / 8.5 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC6VSS6010 | CAPEA6030C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80TC1005CN | 1120 | 0.75 | ECM | 80 | 67 | 35400 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 192 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17.2 / 13 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC7TCA3610 | CAPTA3626C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TC1005CN | 1480 | 0.75 | ECM | 80 | 67 | 57500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 203 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 16.2 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC7TCA6010 | CAPTA6030C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TC1005CN | 1380 | 0.75 | ECM | 80 | 67 | 46000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 203 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.5 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC7TCA4810 | CAPTA6030C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026C3 / DR80TC1005CN | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 199 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 80000 | 80 | DC6VSS3010 | CHPEA3026C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626C3 / DR80TC1005CN | 1260 | 0.75 | ECM | 80 | 67 | 33600 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 203 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16.6 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 80000 | 80 | DC6VSS3610 | CHPEA3626C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR80TC1005CN | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 210 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.2 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 80000 | 80 | DC6VSS4810 | CHPEA4830C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR80TC1005CN | 1320 | 0.75 | ECM | 80 | 67 | 41000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 210 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 80000 | 80 | DC6VSS4210 | CHPEA4830C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA6030C3 / DR80TC1005CN | 1640 | 0.75 | ECM | 80 | 67 | 52000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 210 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.2 / 8.2 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 80000 | 80 | DC6VSS6010 | CHPEA6030C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS |  | IM - DC6VS | IM - DR80TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR80TC1005CN | 1380 | 0.75 | ECM | 80 | 67 | 45000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 208 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.2 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 100000 | 80000 | 80 | DC7TCA4810 | CHPTA4830C3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80TC1005CN | 1480 | 0.75 | ECM | 80 | 67 | 56000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 12.1 | 15 | 212 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 100000 | 80000 | 80 | DC7TCA6010 | CHPTA6030D3 | DR80TC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS |  | IM - DC7TCA | IM - DR80TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80TN0403AN | 860 | 0.5 | ECM | 80 | 67 | 23600 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 138 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC5SEA2410 | CAPTA2422A3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422A3 / DR80TN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17600 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 138 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC5SEA1810 | CAPTA2422A3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422A3 / DR80TN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17800 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 138 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC4SEA1810 | CAPTA2422A3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3022A3 / DR80TN0403AN | 900 | 0.5 | ECM | 80 | 67 | 28400 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 136 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC5SEA3010 | CAPTA3022A3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA2426B3 / DR80TN0403AN | 860 | 0.5 | ECM | 80 | 67 | 23400 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 154 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 40000 | 32000 | 80 | DC5SEA2410 | CHPTA2426B3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR80TN0403AN | 640 | 0.5 | ECM | 80 | 67 | 17600 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 154 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 40000 | 32000 | 80 | DC5SEA1810 | CHPTA2426B3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR80TN0403AN | 910 | 0.5 | ECM | 80 | 67 | 28400 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 157 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 40000 | 32000 | 80 | DC5SEA3010 | CHPTA3026B3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422B3 / DR80TN0603BN | 850 | 0.5 | ECM | 80 | 67 | 23600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 156 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC5SEA2410 | CAPTA2422B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422B3 / DR80TN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 156 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 16 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC5SEA1810 | CAPTA2422B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR80TN0603BN | 850 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 156 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA2422B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422B3 / DR80TN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17800 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 156 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA1810 | CAPTA2422B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3026B3 / DR80TN0603BN | 950 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 161 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA3010 | CAPTA3026B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626B3 / DR80TN0603BN | 1060 | 0.5 | ECM | 80 | 67 | 34400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 163 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC5SEA3610 | CAPTA3626B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626B3 / DR80TN0603BN | 1060 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 163 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA3610 | CAPTA3626B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA2426B3 / DR80TN0603BN | 840 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 168 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC5SEA2410 | CHPTA2426B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR80TN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 168 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 16 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC5SEA1810 | CHPTA2426B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR80TN0603BN | 840 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 168 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA2426B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA2426B3 / DR80TN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 168 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA1810 | CHPTA2426B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR80TN0603BN | 940 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 171 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA3010 | CHPTA3026B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630B3 / DR80TN0603BN | 1050 | 0.5 | ECM | 80 | 67 | 34600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 178 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC5SEA3610 | CHPTA3630B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630B3 / DR80TN0603BN | 1050 | 0.5 | ECM | 80 | 67 | 34400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 178 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA3610 | CHPTA3630B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA3026B3 / DR80TN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 166 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC5SEA3010 | CAPTA3026B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422B3 / DR80TN0803BN | 720 | 0.5 | ECM | 80 | 67 | 23600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 161 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC5SEA2410 | CAPTA2422B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422B3 / DR80TN0803BN | 650 | 0.5 | ECM | 80 | 67 | 17400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 161 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 16 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC5SEA1810 | CAPTA2422B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR80TN0803BN | 720 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 161 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA2422B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422B3 / DR80TN0803BN | 650 | 0.5 | ECM | 80 | 67 | 17800 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 161 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA1810 | CAPTA2422B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3026B3 / DR80TN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 166 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3026B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626B3 / DR80TN0803BN | 1100 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 168 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC5SEA3610 | CAPTA3626B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626B3 / DR80TN0803BN | 1100 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 168 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA3626B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA2426B3 / DR80TN0803BN | 720 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 173 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC5SEA2410 | CHPTA2426B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR80TN0803BN | 720 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 173 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA2426B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA3026B3 / DR80TN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 176 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC5SEA3010 | CHPTA3026B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026B3 / DR80TN0803BN | 910 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 176 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3026B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630B3 / DR80TN0803BN | 1090 | 0.5 | ECM | 80 | 67 | 34600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 183 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC5SEA3610 | CHPTA3630B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630B3 / DR80TN0803BN | 1090 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 183 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA3630B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA3026C3 / DR80TN0805CN | 1030 | 1 | ECM | 80 | 67 | 28600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 184 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.5 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC5SEA3010 | CAPTA3026C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3022C3 / DR80TN0805CN | 1020 | 1 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 177 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC5SEA3010 | CAPTA3022C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3626C3 / DR80TN0805CN | 1050 | 1 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 187 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.5 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC5SEA3610 | CAPTA3626C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626C3 / DR80TN0805CN | 1050 | 1 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 187 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA3626C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA4230C3 / DR80TN0805CN | 1260 | 1 | ECM | 80 | 67 | 40000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 191 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12.5 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC5SEA4210 | CAPTA4230C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR80TN0805CN | 1260 | 1 | ECM | 80 | 67 | 39500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 191 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4210 | CAPTA4230C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR80TN0805CN | 1830 | 1 | ECM | 80 | 67 | 56500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 198 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 16 / 11.7 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC5SEA6010 | CAPTA6030C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA6030C3 / DR80TN0805CN | 1370 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 198 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12.5 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC5SEA4810 | CAPTA6030C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR80TN0805CN | 1380 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 198 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6030C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA3026C3 / DR80TN0805CN | 1030 | 1 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 191 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC5SEA3010 | CHPTA3026C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3630C3 / DR80TN0805CN | 1040 | 1 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 199 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 16 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC5SEA3610 | CHPTA3630C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR80TN0805CN | 1040 | 1 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 199 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA3630C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4230C3 / DR80TN0805CN | 1240 | 1 | ECM | 80 | 67 | 39500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 199 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC5SEA4210 | CHPTA4230C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CHPTA4230C3 / DR80TN0805CN | 1240 | 1 | ECM | 80 | 67 | 39000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 199 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA4210 | CHPTA4230C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CHPTA4830C3 / DR80TN0805CN | 1330 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 203 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12.5 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC5SEA4810 | CHPTA4830C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR80TN0805CN | 1330 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 203 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CHPTA4830C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA6030D3 / DR80TN0805CN | 1830 | 1 | ECM | 80 | 67 | 56000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 207 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 11.7 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC5SEA6010 | CHPTA6030D3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA3626C3 / DR80TN1005CN | 1230 | 1 | ECM | 80 | 67 | 34400 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 190 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.5 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC5SEA3610 | CAPTA3626C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA4230C3 / DR80TN1005CN | 1250 | 1 | ECM | 80 | 67 | 40000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 194 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12.5 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC5SEA4210 | CAPTA4230C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR80TN1005CN | 1250 | 1 | ECM | 80 | 67 | 39500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 194 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA4210 | CAPTA4230C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR80TN1005CN | 1390 | 1 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 201 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12.5 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC5SEA4810 | CAPTA6030C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR80TN1005CN | 1390 | 1 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 201 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA4810 | CAPTA6030C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CAPTA6030C3 / DR80TN1005CN | 1550 | 1 | ECM | 80 | 67 | 56000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 201 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA6010 | CAPTA6030C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | CHPTA4230C3 / DR80TN1005CN | 1220 | 1 | ECM | 80 | 67 | 39500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 202 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 80000 | 80 | DC5SEA4210 | CHPTA4230C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CHPTA4230C3 / DR80TN1005CN | 1220 | 1 | ECM | 80 | 67 | 39000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 202 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 80000 | 80 | DC4SEA4210 | CHPTA4230C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CHPTA4830C3 / DR80TN1005CN | 1330 | 1 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 206 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12.5 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 80000 | 80 | DC5SEA4810 | CHPTA4830C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC5SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR80TN1005CN | 1330 | 1 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 206 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 80000 | 80 | DC4SEA4810 | CHPTA4830C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA6030D3 / DR80TN1005CN | 1550 | 1 | ECM | 80 | 67 | 55500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 210 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 13.8 / 11.2 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 80000 | 80 | DC4SEA6010 | CHPTA6030D3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | CAPTA2422A3 / DR92SN0403AN | 810 | 0.5 | ECM | 80 | 67 | 23400 | 40000 | 36840 |  | 1 | 92 | 115/60/1 | 9.7 | 15 | 146 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 36840 | 92 | DC5SEA2410 | CAPTA2422A3 | DR92SN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422A3 / DR92SN0403AN | 550 | 0.5 | ECM | 80 | 67 | 17600 | 40000 | 36840 |  | 1 | 92 | 115/60/1 | 9.7 | 15 | 146 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 36840 | 92 | DC5SEA1810 | CAPTA2422A3 | DR92SN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422A3 / DR92SN0403AN | 810 | 0.5 | ECM | 80 | 67 | 23200 | 40000 | 36840 |  | 1 | 92 | 115/60/1 | 9.7 | 15 | 146 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 36840 | 92 | DC4SEA2410 | CAPTA2422A3 | DR92SN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422A3 / DR92SN0403AN | 620 | 0.5 | ECM | 80 | 67 | 17800 | 40000 | 36840 |  | 1 | 92 | 115/60/1 | 9.7 | 15 | 146 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 36840 | 92 | DC4SEA1810 | CAPTA2422A3 | DR92SN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR92SN0403AN | 710 | 0.5 | ECM | 80 | 67 | 23400 | 40000 | 36840 |  | 1 | 92 | 115/60/1 | 9.7 | 15 | 162 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 40000 | 36840 | 92 | DC5SEA2410 | CHPTA2426B3 | DR92SN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR92SN0403AN | 570 | 0.5 | ECM | 80 | 67 | 17600 | 40000 | 36840 |  | 1 | 92 | 115/60/1 | 9.7 | 15 | 162 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 40000 | 36840 | 92 | DC5SEA1810 | CHPTA2426B3 | DR92SN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3026B3 / DR92SN0603BN | 940 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 168 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 55260 | 92 | DC5SEA3010 | CAPTA3026B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422B3 / DR92SN0603BN | 750 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 163 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 55260 | 92 | DC5SEA2410 | CAPTA2422B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422B3 / DR92SN0603BN | 600 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 163 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 55260 | 92 | DC5SEA1810 | CAPTA2422B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR92SN0603BN | 750 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 163 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 55260 | 92 | DC4SEA2410 | CAPTA2422B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422B3 / DR92SN0603BN | 630 | 0.5 | ECM | 80 | 67 | 17800 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 163 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 55260 | 92 | DC4SEA1810 | CAPTA2422B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3022B3 / DR92SN0603BN | 930 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 162 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 55260 | 92 | DC5SEA3010 | CAPTA3022B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3026B3 / DR92SN0603BN | 940 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 168 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 55260 | 92 | DC4SEA3010 | CAPTA3026B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626B3 / DR92SN0603BN | 1090 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 170 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 55260 | 92 | DC5SEA3610 | CAPTA3626B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626B3 / DR92SN0603BN | 1090 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 170 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 55260 | 92 | DC4SEA3610 | CAPTA3626B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA2426B3 / DR92SN0603BN | 740 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 175 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 55260 | 92 | DC5SEA2410 | CHPTA2426B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR92SN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 175 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 55260 | 92 | DC5SEA1810 | CHPTA2426B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR92SN0603BN | 740 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 175 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 55260 | 92 | DC4SEA2410 | CHPTA2426B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA2426B3 / DR92SN0603BN | 640 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 175 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 55260 | 92 | DC4SEA1810 | CHPTA2426B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR92SN0603BN | 940 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 55260 | 92 | DC5SEA3010 | CHPTA3026B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026B3 / DR92SN0603BN | 940 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 55260 | 92 | DC4SEA3010 | CHPTA3026B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630B3 / DR92SN0603BN | 1080 | 0.5 | ECM | 80 | 67 | 34400 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 185 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 55260 | 92 | DC5SEA3610 | CHPTA3630B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630B3 / DR92SN0603BN | 1080 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 55260 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 185 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 55260 | 92 | DC4SEA3610 | CHPTA3630B3 | DR92SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA3026B3 / DR92SN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 172 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA3010 | CAPTA3026B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422B3 / DR92SN0803BN | 830 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 167 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA2410 | CAPTA2422B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422B3 / DR92SN0803BN | 590 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 167 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA1810 | CAPTA2422B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR92SN0803BN | 830 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 167 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC4SEA2410 | CAPTA2422B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422B3 / DR92SN0803BN | 590 | 0.5 | ECM | 80 | 67 | 17800 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 167 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC4SEA1810 | CAPTA2422B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3022B3 / DR92SN0803BN | 910 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA3010 | CAPTA3022B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3026B3 / DR92SN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 172 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC4SEA3010 | CAPTA3026B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626B3 / DR92SN0803BN | 1050 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 174 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA3610 | CAPTA3626B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626B3 / DR92SN0803BN | 1050 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 174 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC4SEA3610 | CAPTA3626B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA2426B3 / DR92SN0803BN | 820 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 179 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA2410 | CHPTA2426B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR92SN0803BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 179 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA1810 | CHPTA2426B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR92SN0803BN | 820 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 179 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC4SEA2410 | CHPTA2426B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA2426B3 / DR92SN0803BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 179 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC4SEA1810 | CHPTA2426B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR92SN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 182 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA3010 | CHPTA3026B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026B3 / DR92SN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 182 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC4SEA3010 | CHPTA3026B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630B3 / DR92SN0803BN | 1040 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 189 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA3610 | CHPTA3630B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630B3 / DR92SN0803BN | 1040 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 9.8 | 15 | 189 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC4SEA3610 | CHPTA3630B3 | DR92SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA3026C3 / DR92SN0804CN | 1020 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 189 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA3010 | CAPTA3026C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3022C3 / DR92SN0804CN | 990 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 182 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA3010 | CAPTA3022C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3026C3 / DR92SN0804CN | 1020 | 0.75 | ECM | 80 | 67 | 28200 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 189 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC4SEA3010 | CAPTA3026C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626C3 / DR92SN0804CN | 1100 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 192 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA3610 | CAPTA3626C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA4230C3 / DR92SN0804CN | 1260 | 0.75 | ECM | 80 | 67 | 40000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 196 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA4210 | CAPTA4230C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR92SN0804CN | 1260 | 0.75 | ECM | 80 | 67 | 39000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 196 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC4SEA4210 | CAPTA4230C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR92SN0804CN | 1370 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 203 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA4810 | CAPTA6030C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR92SN0804CN | 1370 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 203 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC4SEA4810 | CAPTA6030C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA3026C3 / DR92SN0804CN | 1000 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 196 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA3010 | CHPTA3026C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026C3 / DR92SN0804CN | 1000 | 0.75 | ECM | 80 | 67 | 28600 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 196 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC4SEA3010 | CHPTA3026C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630C3 / DR92SN0804CN | 1090 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 204 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 16 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA3610 | CHPTA3630C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR92SN0804CN | 1090 | 0.75 | ECM | 80 | 67 | 34200 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 204 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC4SEA3610 | CHPTA3630C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4230C3 / DR92SN0804CN | 1330 | 0.75 | ECM | 80 | 67 | 39000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 204 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 14.5 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA4210 | CHPTA4230C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CHPTA4230C3 / DR92SN0804CN | 1330 | 0.75 | ECM | 80 | 67 | 39000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 204 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC4SEA4210 | CHPTA4230C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CHPTA4830C3 / DR92SN0804CN | 1330 | 0.75 | ECM | 80 | 67 | 45000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 208 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA4810 | CHPTA4830C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR92SN0804CN | 1330 | 0.75 | ECM | 80 | 67 | 45000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 208 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC4SEA4810 | CHPTA4830C3 | DR92SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CAPTA3026C3 / DR92SN0805CN | 1060 | 1 | ECM | 80 | 67 | 28400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 193 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA3010 | CAPTA3026C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3022C3 / DR92SN0805CN | 1040 | 1 | ECM | 80 | 67 | 28400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 186 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA3010 | CAPTA3022C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3626C3 / DR92SN0805CN | 1090 | 1 | ECM | 80 | 67 | 34400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 196 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA3610 | CAPTA3626C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA4230C3 / DR92SN0805CN | 1250 | 1 | ECM | 80 | 67 | 40000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 200 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA4210 | CAPTA4230C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR92SN0805CN | 1250 | 1 | ECM | 80 | 67 | 39000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 200 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC4SEA4210 | CAPTA4230C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR92SN0805CN | 1830 | 1 | ECM | 80 | 67 | 56500 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 207 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 11.5 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA6010 | CAPTA6030C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA6030C3 / DR92SN0805CN | 1340 | 1 | ECM | 80 | 67 | 45500 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 207 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC5SEA4810 | CAPTA6030C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR92SN0805CN | 1400 | 1 | ECM | 80 | 67 | 45500 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 207 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC4SEA4810 | CAPTA6030C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CAPTA6030C3 / DR92SN0805CN | 1550 | 1 | ECM | 80 | 67 | 56000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 207 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 73680 | 92 | DC4SEA6010 | CAPTA6030C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | CHPTA3026C3 / DR92SN0805CN | 1060 | 1 | ECM | 80 | 67 | 28400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 200 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA3010 | CHPTA3026C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3630C3 / DR92SN0805CN | 1070 | 1 | ECM | 80 | 67 | 34400 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 208 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 16 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA3610 | CHPTA3630C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR92SN0805CN | 1070 | 1 | ECM | 80 | 67 | 34200 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 208 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC4SEA3610 | CHPTA3630C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4230C3 / DR92SN0805CN | 1280 | 1 | ECM | 80 | 67 | 39000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 208 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 14.5 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA4210 | CHPTA4230C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CHPTA4230C3 / DR92SN0805CN | 1280 | 1 | ECM | 80 | 67 | 39000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 208 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC4SEA4210 | CHPTA4230C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CHPTA4830C3 / DR92SN0805CN | 1380 | 1 | ECM | 80 | 67 | 45000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 212 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA4810 | CHPTA4830C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR92SN0805CN | 1350 | 1 | ECM | 80 | 67 | 45000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 212 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC4SEA4810 | CHPTA4830C3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA6030D3 / DR92SN0805CN | 1830 | 1 | ECM | 80 | 67 | 56000 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 216 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 11.7 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC5SEA6010 | CHPTA6030D3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CHPTA6030D3 / DR92SN0805CN | 1550 | 1 | ECM | 80 | 67 | 55500 | 80000 | 73680 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 216 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 13.8 / 11.2 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 73680 | 92 | DC4SEA6010 | CHPTA6030D3 | DR92SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | CAPTA3026C3 / DR92SN1004CN | 1000 | 0.75 | ECM | 80 | 67 | 28200 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 193 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC4SEA3010 | CAPTA3026C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626C3 / DR92SN1004CN | 1100 | 0.75 | ECM | 80 | 67 | 34400 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 196 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC5SEA3610 | CAPTA3626C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626C3 / DR92SN1004CN | 1100 | 0.75 | ECM | 80 | 67 | 34200 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 196 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC4SEA3610 | CAPTA3626C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA4230C3 / DR92SN1004CN | 1260 | 0.75 | ECM | 80 | 67 | 40000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 200 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC5SEA4210 | CAPTA4230C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR92SN1004CN | 1260 | 0.75 | ECM | 80 | 67 | 39000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 200 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC4SEA4210 | CAPTA4230C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR92SN1004CN | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 207 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC5SEA4810 | CAPTA6030C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR92SN1004CN | 1370 | 0.75 | ECM | 80 | 67 | 45500 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 207 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC4SEA4810 | CAPTA6030C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA3026C3 / DR92SN1004CN | 990 | 0.75 | ECM | 80 | 67 | 28200 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 200 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC4SEA3010 | CHPTA3026C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630C3 / DR92SN1004CN | 1090 | 0.75 | ECM | 80 | 67 | 34400 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 208 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 16 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC5SEA3610 | CHPTA3630C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR92SN1004CN | 1090 | 0.75 | ECM | 80 | 67 | 34200 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 208 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC4SEA3610 | CHPTA3630C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4230C3 / DR92SN1004CN | 1360 | 0.75 | ECM | 80 | 67 | 39000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 208 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 14.5 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC5SEA4210 | CHPTA4230C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CHPTA4230C3 / DR92SN1004CN | 1360 | 0.75 | ECM | 80 | 67 | 39000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 208 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC4SEA4210 | CHPTA4230C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CHPTA4830C3 / DR92SN1004CN | 1350 | 0.75 | ECM | 80 | 67 | 45000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 212 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC5SEA4810 | CHPTA4830C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR92SN1004CN | 1350 | 0.75 | ECM | 80 | 67 | 45000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 13.4 | 20 | 212 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC4SEA4810 | CHPTA4830C3 | DR92SN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CAPTA3626C3 / DR92SN1005CN | 1070 | 1 | ECM | 80 | 67 | 34200 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 199 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC5SEA3610 | CAPTA3626C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626C3 / DR92SN1005CN | 1070 | 1 | ECM | 80 | 67 | 34200 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 199 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC4SEA3610 | CAPTA3626C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA4230C3 / DR92SN1005CN | 1230 | 1 | ECM | 80 | 67 | 40000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 203 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC5SEA4210 | CAPTA4230C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR92SN1005CN | 1230 | 1 | ECM | 80 | 67 | 39000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 203 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC4SEA4210 | CAPTA4230C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR92SN1005CN | 1800 | 1 | ECM | 80 | 67 | 56500 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 210 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 11.7 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC5SEA6010 | CAPTA6030C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA6030C3 / DR92SN1005CN | 1410 | 1 | ECM | 80 | 67 | 45500 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 210 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC5SEA4810 | CAPTA6030C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR92SN1005CN | 1410 | 1 | ECM | 80 | 67 | 45500 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 210 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC4SEA4810 | CAPTA6030C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CAPTA6030C3 / DR92SN1005CN | 1570 | 1 | ECM | 80 | 67 | 56000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 210 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 92100 | 92 | DC4SEA6010 | CAPTA6030C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | CHPTA3630C3 / DR92SN1005CN | 1040 | 1 | ECM | 80 | 67 | 34400 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 211 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 16 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC5SEA3610 | CHPTA3630C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR92SN1005CN | 1040 | 1 | ECM | 80 | 67 | 34200 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 211 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC4SEA3610 | CHPTA3630C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4230C3 / DR92SN1005CN | 1360 | 1 | ECM | 80 | 67 | 39000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 211 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 14.5 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC5SEA4210 | CHPTA4230C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CHPTA4230C3 / DR92SN1005CN | 1360 | 1 | ECM | 80 | 67 | 39000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 211 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC4SEA4210 | CHPTA4230C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CHPTA4830C3 / DR92SN1005CN | 1350 | 1 | ECM | 80 | 67 | 45000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 215 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC5SEA4810 | CHPTA4830C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR92SN1005CN | 1350 | 1 | ECM | 80 | 67 | 45000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 215 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC4SEA4810 | CHPTA4830C3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA6030D3 / DR92SN1005CN | 1800 | 1 | ECM | 80 | 67 | 56000 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 219 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 11.7 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC5SEA6010 | CHPTA6030D3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CHPTA6030D3 / DR92SN1005CN | 1570 | 1 | ECM | 80 | 67 | 55500 | 100000 | 92100 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 219 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 13.8 / 11.2 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 92100 | 92 | DC4SEA6010 | CHPTA6030D3 | DR92SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | CAPTA4230D3 / DR92SN1205DN | 1260 | 1 | ECM | 80 | 67 | 40000 | 120000 | 110520 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 222 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 110520 | 92 | DC5SEA4210 | CAPTA4230D3 | DR92SN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230D3 / DR92SN1205DN | 1260 | 1 | ECM | 80 | 67 | 39500 | 120000 | 110520 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 222 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 110520 | 92 | DC4SEA4210 | CAPTA4230D3 | DR92SN1205DN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030D3 / DR92SN1205DN | 1780 | 1 | ECM | 80 | 67 | 56500 | 120000 | 110520 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 227 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 11.7 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 110520 | 92 | DC5SEA6010 | CAPTA6030D3 | DR92SN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA6030D3 / DR92SN1205DN | 1400 | 1 | ECM | 80 | 67 | 45500 | 120000 | 110520 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 227 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 110520 | 92 | DC5SEA4810 | CAPTA6030D3 | DR92SN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030D3 / DR92SN1205DN | 1410 | 1 | ECM | 80 | 67 | 45000 | 120000 | 110520 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 227 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15.2 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 110520 | 92 | DC4SEA4810 | CAPTA6030D3 | DR92SN1205DN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CAPTA6030D3 / DR92SN1205DN | 1500 | 1 | ECM | 80 | 67 | 56500 | 120000 | 110520 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 227 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 110520 | 92 | DC4SEA6010 | CAPTA6030D3 | DR92SN1205DN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | CHPTA6030D3 / DR92SN1205DN | 1780 | 1 | ECM | 80 | 67 | 56000 | 120000 | 110520 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 232 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 11.7 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 120000 | 110520 | 92 | DC5SEA6010 | CHPTA6030D3 | DR92SN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS |  | IM - DC5SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CHPTA6030D3 / DR92SN1205DN | 1500 | 1 | ECM | 80 | 67 | 56000 | 120000 | 110520 |  | 1 | 92 | 115/60/1 | 16.4 | 25 | 232 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.2 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 120000 | 110520 | 92 | DC4SEA6010 | CHPTA6030D3 | DR92SN1205DN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS |  | IM - DC4SEA | IM - DR92SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | CAPTA2422A3 / DR96SN0403AN | 840 | 0.5 | ECM | 80 | 67 | 23400 | 40000 | 38800 |  | 1 | 96 | 115/60/1 | 9.7 | 15 | 148 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 38800 | 96 | DC5SEA2410 | CAPTA2422A3 | DR96SN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422A3 / DR96SN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17600 | 40000 | 38800 |  | 1 | 96 | 115/60/1 | 9.7 | 15 | 148 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 38800 | 96 | DC5SEA1810 | CAPTA2422A3 | DR96SN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422A3 / DR96SN0403AN | 840 | 0.5 | ECM | 80 | 67 | 23200 | 40000 | 38800 |  | 1 | 96 | 115/60/1 | 9.7 | 15 | 148 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.3 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 38800 | 96 | DC4SEA2410 | CAPTA2422A3 | DR96SN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422A3 / DR96SN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17800 | 40000 | 38800 |  | 1 | 96 | 115/60/1 | 9.7 | 15 | 148 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 38800 | 96 | DC4SEA1810 | CAPTA2422A3 | DR96SN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0403AN | 840 | 0.5 | ECM | 80 | 67 | 23400 | 40000 | 38800 |  | 1 | 96 | 115/60/1 | 9.7 | 15 | 164 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 40000 | 38800 | 96 | DC5SEA2410 | CHPTA2426B3 | DR96SN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0403AN | 650 | 0.5 | ECM | 80 | 67 | 17600 | 40000 | 38800 |  | 1 | 96 | 115/60/1 | 9.7 | 15 | 164 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 40000 | 38800 | 96 | DC5SEA1810 | CHPTA2426B3 | DR96SN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR96SN0403AN | 920 | 0.5 | ECM | 80 | 67 | 28200 | 40000 | 38800 |  | 1 | 96 | 115/60/1 | 9.7 | 15 | 167 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 40000 | 38800 | 96 | DC5SEA3010 | CHPTA3026B3 | DR96SN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3026B3 / DR96SN0603BN | 940 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 171 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA3010 | CAPTA3026B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3026B3 / DR96SN0603BN | 960 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 171 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA3010 | CAPTA3026B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0603BN | 820 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA2410 | CAPTA2422B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0603BN | 590 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA1810 | CAPTA2422B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0603BN | 820 | 0.5 | ECM | 80 | 67 | 23600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC4SEA2410 | CAPTA2422B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0603BN | 590 | 0.5 | ECM | 80 | 67 | 17800 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC4SEA1810 | CAPTA2422B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0603BN | 840 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA2410 | CAPTA2422B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA1810 | CAPTA2422B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0603BN | 840 | 0.5 | ECM | 80 | 67 | 23600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC4SEA2410 | CAPTA2422B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0603BN | 620 | 0.5 | ECM | 80 | 67 | 17800 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC4SEA1810 | CAPTA2422B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3022B3 / DR96SN0603BN | 930 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 165 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA3010 | CAPTA3022B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3022B3 / DR96SN0603BN | 950 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 165 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA3010 | CAPTA3022B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3026B3 / DR96SN0603BN | 940 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 171 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC4SEA3010 | CAPTA3026B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3026B3 / DR96SN0603BN | 960 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 171 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC4SEA3010 | CAPTA3026B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626B3 / DR96SN0603BN | 1070 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 173 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA3610 | CAPTA3626B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626B3 / DR96SN0603BN | 1070 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 173 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC4SEA3610 | CAPTA3626B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA3626B3 / DR96SN0603BN | 1070 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 173 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 14.5 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA3610 | CAPTA3626B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626B3 / DR96SN0603BN | 1070 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 173 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC4SEA3610 | CAPTA3626B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA2426B3 / DR96SN0603BN | 810 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC5SEA2410 | CHPTA2426B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0603BN | 590 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC5SEA1810 | CHPTA2426B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0603BN | 810 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC4SEA2410 | CHPTA2426B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0603BN | 590 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC4SEA1810 | CHPTA2426B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0603BN | 830 | 0.5 | ECM | 80 | 67 | 23600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC5SEA2410 | CHPTA2426B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC5SEA1810 | CHPTA2426B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0603BN | 840 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC4SEA2410 | CHPTA2426B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0603BN | 620 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC4SEA1810 | CHPTA2426B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR96SN0603BN | 930 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 181 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC5SEA3010 | CHPTA3026B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026B3 / DR96SN0603BN | 930 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 181 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC4SEA3010 | CHPTA3026B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3026B3 / DR96SN0603BN | 960 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 181 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC5SEA3010 | CHPTA3026B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026B3 / DR96SN0603BN | 960 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 181 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC4SEA3010 | CHPTA3026B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630B3 / DR96SN0603BN | 1060 | 0.5 | ECM | 80 | 67 | 34400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 188 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC5SEA3610 | CHPTA3630B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630B3 / DR96SN0603BN | 1060 | 0.5 | ECM | 80 | 67 | 34600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 188 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC4SEA3610 | CHPTA3630B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA3630B3 / DR96SN0603BN | 1060 | 0.5 | ECM | 80 | 67 | 34400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 188 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC5SEA3610 | CHPTA3630B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630B3 / DR96SN0603BN | 1060 | 0.5 | ECM | 80 | 67 | 34600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 188 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC4SEA3610 | CHPTA3630B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA3026B3 / DR96SN0603BN | 990 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 171 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA3010 | CAPTA3026B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0603BN | 800 | 0.5 | ECM | 80 | 67 | 23600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA2410 | CAPTA2422B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0603BN | 600 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA1810 | CAPTA2422B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0603BN | 800 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC4SEA2410 | CAPTA2422B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0603BN | 600 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 166 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC4SEA1810 | CAPTA2422B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3022B3 / DR96SN0603BN | 980 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 165 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA3010 | CAPTA3022B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3026B3 / DR96SN0603BN | 990 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 171 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.3 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC4SEA3010 | CAPTA3026B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626B3 / DR96SN0603BN | 1070 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 173 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 14.5 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC5SEA3610 | CAPTA3626B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626B3 / DR96SN0603BN | 1060 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 173 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 58200 | 96 | DC4SEA3610 | CAPTA3626B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA2426B3 / DR96SN0603BN | 800 | 0.5 | ECM | 80 | 67 | 23600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC5SEA2410 | CHPTA2426B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC5SEA1810 | CHPTA2426B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0603BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC4SEA2410 | CHPTA2426B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0603BN | 630 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 178 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC4SEA1810 | CHPTA2426B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR96SN0603BN | 990 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 181 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC5SEA3010 | CHPTA3026B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026B3 / DR96SN0603BN | 990 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 181 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC4SEA3010 | CHPTA3026B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630B3 / DR96SN0603BN | 1060 | 0.5 | ECM | 80 | 67 | 34400 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 188 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 14.5 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC5SEA3610 | CHPTA3630B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630B3 / DR96SN0603BN | 1050 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 58200 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 188 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 58200 | 96 | DC4SEA3610 | CHPTA3630B3 | DR96SN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA2422B3 / DR96SN0803BN | 820 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 76000 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 172 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 76000 | 96 | DC5SEA2410 | CAPTA2422B3 | DR96SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0803BN | 600 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 76000 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 172 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 76000 | 96 | DC5SEA1810 | CAPTA2422B3 | DR96SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0803BN | 820 | 0.5 | ECM | 80 | 67 | 23600 | 80000 | 76000 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 172 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 76000 | 96 | DC4SEA2410 | CAPTA2422B3 | DR96SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422B3 / DR96SN0803BN | 600 | 0.5 | ECM | 80 | 67 | 17800 | 80000 | 76000 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 172 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 76000 | 96 | DC4SEA1810 | CAPTA2422B3 | DR96SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3026B3 / DR96SN0803BN | 910 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 76000 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 177 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 76000 | 96 | DC4SEA3010 | CAPTA3026B3 | DR96SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626B3 / DR96SN0803BN | 1030 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 76000 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 179 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 76000 | 96 | DC4SEA3610 | CAPTA3626B3 | DR96SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA2426B3 / DR96SN0803BN | 810 | 0.5 | ECM | 80 | 67 | 23600 | 80000 | 76000 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 184 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 76000 | 96 | DC5SEA2410 | CHPTA2426B3 | DR96SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0803BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 76000 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 184 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 76000 | 96 | DC5SEA1810 | CHPTA2426B3 | DR96SN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0803BN | 810 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 76000 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 184 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 76000 | 96 | DC4SEA2410 | CHPTA2426B3 | DR96SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA2426B3 / DR96SN0803BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 76000 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 184 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 76000 | 96 | DC4SEA1810 | CHPTA2426B3 | DR96SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR96SN0803BN | 910 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 76000 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 187 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 76000 | 96 | DC4SEA3010 | CHPTA3026B3 | DR96SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630B3 / DR96SN0803BN | 1020 | 0.5 | ECM | 80 | 67 | 34600 | 80000 | 76000 |  | 1 | 96 | 115/60/1 | 9.8 | 15 | 194 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 76000 | 96 | DC4SEA3610 | CHPTA3630B3 | DR96SN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA3026C3 / DR96SN0804CN | 890 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 194 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA3010 | CAPTA3026C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422C3 / DR96SN0804CN | 850 | 0.75 | ECM | 80 | 67 | 23600 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 187 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA2410 | CAPTA2422C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422C3 / DR96SN0804CN | 850 | 0.75 | ECM | 80 | 67 | 23200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 187 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC4SEA2410 | CAPTA2422C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA3026C3 / DR96SN0804CN | 1030 | 0.75 | ECM | 80 | 67 | 28200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 194 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC4SEA3010 | CAPTA3026C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626C3 / DR96SN0804CN | 1060 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 197 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA3610 | CAPTA3626C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626C3 / DR96SN0804CN | 1060 | 0.75 | ECM | 80 | 67 | 34200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 197 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC4SEA3610 | CAPTA3626C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA4230C3 / DR96SN0804CN | 1250 | 0.75 | ECM | 80 | 67 | 40000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 201 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA4210 | CAPTA4230C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR96SN0804CN | 1250 | 0.75 | ECM | 80 | 67 | 39000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 201 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC4SEA4210 | CAPTA4230C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR96SN0804CN | 1420 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 208 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA4810 | CAPTA6030C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR96SN0804CN | 1430 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 208 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC4SEA4810 | CAPTA6030C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA2426C3 / DR96SN0804CN | 850 | 0.75 | ECM | 80 | 67 | 23400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 199 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA2410 | CHPTA2426C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426C3 / DR96SN0804CN | 840 | 0.75 | ECM | 80 | 67 | 23200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 199 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA2410 | CHPTA2426C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA3026C3 / DR96SN0804CN | 890 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 201 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA3010 | CHPTA3026C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026C3 / DR96SN0804CN | 1030 | 0.75 | ECM | 80 | 67 | 28600 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 201 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA3010 | CHPTA3026C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630C3 / DR96SN0804CN | 1030 | 0.75 | ECM | 80 | 67 | 34600 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 209 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA3610 | CHPTA3630C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR96SN0804CN | 1030 | 0.75 | ECM | 80 | 67 | 34200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 209 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA3610 | CHPTA3630C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4230C3 / DR96SN0804CN | 1220 | 0.75 | ECM | 80 | 67 | 39000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 209 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 14.5 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA4210 | CHPTA4230C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CHPTA4230C3 / DR96SN0804CN | 1220 | 0.75 | ECM | 80 | 67 | 39000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 209 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA4210 | CHPTA4230C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CHPTA4830C3 / DR96SN0804CN | 1380 | 0.75 | ECM | 80 | 67 | 45000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 213 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA4810 | CHPTA4830C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR96SN0804CN | 1380 | 0.75 | ECM | 80 | 67 | 45000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 213 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA4810 | CHPTA4830C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CAPTA3026C3 / DR96SN0804CN | 900 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 194 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA3010 | CAPTA3026C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422C3 / DR96SN0804CN | 860 | 0.75 | ECM | 80 | 67 | 23400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 187 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA2410 | CAPTA2422C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA3026C3 / DR96SN0804CN | 1050 | 0.75 | ECM | 80 | 67 | 28200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 194 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC4SEA3010 | CAPTA3026C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626C3 / DR96SN0804CN | 1070 | 0.75 | ECM | 80 | 67 | 34200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 197 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 14.5 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA3610 | CAPTA3626C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA4230C3 / DR96SN0804CN | 1260 | 0.75 | ECM | 80 | 67 | 39500 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 201 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA4210 | CAPTA4230C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR96SN0804CN | 1260 | 0.75 | ECM | 80 | 67 | 39000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 201 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC4SEA4210 | CAPTA4230C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR96SN0804CN | 1360 | 0.75 | ECM | 80 | 67 | 45000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 208 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA4810 | CAPTA6030C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA2426C3 / DR96SN0804CN | 850 | 0.75 | ECM | 80 | 67 | 23400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 199 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA2410 | CHPTA2426C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA3026C3 / DR96SN0804CN | 890 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 201 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA3010 | CHPTA3026C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026C3 / DR96SN0804CN | 1040 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 201 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA3010 | CHPTA3026C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630C3 / DR96SN0804CN | 1040 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 209 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA3610 | CHPTA3630C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR96SN0804CN | 1040 | 0.75 | ECM | 80 | 67 | 34200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 209 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA3610 | CHPTA3630C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4830C3 / DR96SN0804CN | 1330 | 0.75 | ECM | 80 | 67 | 44500 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 13.4 | 20 | 213 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA4810 | CHPTA4830C3 | DR96SN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA3026C3 / DR96SN0805CN | 1030 | 1 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 197 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA3010 | CAPTA3026C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3026C3 / DR96SN0805CN | 940 | 1 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 197 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA3010 | CAPTA3026C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3022C3 / DR96SN0805CN | 1020 | 1 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 190 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA3010 | CAPTA3022C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3022C3 / DR96SN0805CN | 930 | 1 | ECM | 80 | 67 | 28200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 190 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA3010 | CAPTA3022C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3026C3 / DR96SN0805CN | 950 | 1 | ECM | 80 | 67 | 28200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 197 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC4SEA3010 | CAPTA3026C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626C3 / DR96SN0805CN | 1060 | 1 | ECM | 80 | 67 | 34400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 200 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA3610 | CAPTA3626C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626C3 / DR96SN0805CN | 1070 | 1 | ECM | 80 | 67 | 34400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 200 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA3610 | CAPTA3626C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA4230C3 / DR96SN0805CN | 1240 | 1 | ECM | 80 | 67 | 40000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 204 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA4210 | CAPTA4230C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR96SN0805CN | 1240 | 1 | ECM | 80 | 67 | 39000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 204 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC4SEA4210 | CAPTA4230C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA4230C3 / DR96SN0805CN | 1320 | 1 | ECM | 80 | 67 | 39500 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 204 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA4210 | CAPTA4230C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR96SN0805CN | 1320 | 1 | ECM | 80 | 67 | 39000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 204 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC4SEA4210 | CAPTA4230C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR96SN0805CN | 1550 | 1 | ECM | 80 | 67 | 56500 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 211 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 11.5 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA6010 | CAPTA6030C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA6030C3 / DR96SN0805CN | 1370 | 1 | ECM | 80 | 67 | 45500 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 211 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA4810 | CAPTA6030C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR96SN0805CN | 1370 | 1 | ECM | 80 | 67 | 45500 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 211 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC4SEA4810 | CAPTA6030C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CAPTA6030C3 / DR96SN0805CN | 1600 | 1 | ECM | 80 | 67 | 56500 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 211 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 11.8 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA6010 | CAPTA6030C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA6030C3 / DR96SN0805CN | 1370 | 1 | ECM | 80 | 67 | 45500 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 211 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC5SEA4810 | CAPTA6030C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR96SN0805CN | 1370 | 1 | ECM | 80 | 67 | 45500 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 211 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 77600 | 96 | DC4SEA4810 | CAPTA6030C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA3026C3 / DR96SN0805CN | 1030 | 1 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 204 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA3010 | CHPTA3026C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026C3 / DR96SN0805CN | 940 | 1 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 204 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA3010 | CHPTA3026C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026C3 / DR96SN0805CN | 940 | 1 | ECM | 80 | 67 | 28200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 204 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA3010 | CHPTA3026C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630C3 / DR96SN0805CN | 1040 | 1 | ECM | 80 | 67 | 34600 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 212 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA3610 | CHPTA3630C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR96SN0805CN | 1040 | 1 | ECM | 80 | 67 | 34200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 212 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA3610 | CHPTA3630C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA3630C3 / DR96SN0805CN | 1060 | 1 | ECM | 80 | 67 | 34600 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 212 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA3610 | CHPTA3630C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR96SN0805CN | 1060 | 1 | ECM | 80 | 67 | 34200 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 212 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA3610 | CHPTA3630C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4230C3 / DR96SN0805CN | 1330 | 1 | ECM | 80 | 67 | 39000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 212 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 14.5 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA4210 | CHPTA4230C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CHPTA4230C3 / DR96SN0805CN | 1330 | 1 | ECM | 80 | 67 | 39000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 212 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA4210 | CHPTA4230C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CHPTA4230C3 / DR96SN0805CN | 1290 | 1 | ECM | 80 | 67 | 39000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 212 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 14.5 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA4210 | CHPTA4230C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CHPTA4230C3 / DR96SN0805CN | 1290 | 1 | ECM | 80 | 67 | 39000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 212 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA4210 | CHPTA4230C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CHPTA4830C3 / DR96SN0805CN | 1330 | 1 | ECM | 80 | 67 | 45000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 216 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA4810 | CHPTA4830C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR96SN0805CN | 1330 | 1 | ECM | 80 | 67 | 45000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 216 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA4810 | CHPTA4830C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA4830C3 / DR96SN0805CN | 1350 | 1 | ECM | 80 | 67 | 45000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 216 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA4810 | CHPTA4830C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR96SN0805CN | 1350 | 1 | ECM | 80 | 67 | 45000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 216 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC4SEA4810 | CHPTA4830C3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA6030D3 / DR96SN0805CN | 1550 | 1 | ECM | 80 | 67 | 56000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 220 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.2 / 11.8 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA6010 | CHPTA6030D3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CHPTA6030D3 / DR96SN0805CN | 1600 | 1 | ECM | 80 | 67 | 56000 | 80000 | 77600 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 220 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 11.8 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 77600 | 96 | DC5SEA6010 | CHPTA6030D3 | DR96SN0805CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA3626C3 / DR96SN1005CN | 1100 | 1 | ECM | 80 | 67 | 34400 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 204 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 96100 | 96 | DC5SEA3610 | CAPTA3626C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA4230C3 / DR96SN1005CN | 1260 | 1 | ECM | 80 | 67 | 40000 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 208 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 96100 | 96 | DC5SEA4210 | CAPTA4230C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR96SN1005CN | 1260 | 1 | ECM | 80 | 67 | 39000 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 208 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 96100 | 96 | DC4SEA4210 | CAPTA4230C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR96SN1005CN | 1810 | 1 | ECM | 80 | 67 | 56500 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 215 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 11.5 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 96100 | 96 | DC5SEA6010 | CAPTA6030C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA6030C3 / DR96SN1005CN | 1380 | 1 | ECM | 80 | 67 | 45500 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 215 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 96100 | 96 | DC5SEA4810 | CAPTA6030C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR96SN1005CN | 1390 | 1 | ECM | 80 | 67 | 45500 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 215 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 96100 | 96 | DC4SEA4810 | CAPTA6030C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA3630C3 / DR96SN1005CN | 1070 | 1 | ECM | 80 | 67 | 34600 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 216 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 96100 | 96 | DC5SEA3610 | CHPTA3630C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR96SN1005CN | 1070 | 1 | ECM | 80 | 67 | 34200 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 216 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 96100 | 96 | DC4SEA3610 | CHPTA3630C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4230C3 / DR96SN1005CN | 1270 | 1 | ECM | 80 | 67 | 39000 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 216 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 14.5 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 96100 | 96 | DC5SEA4210 | CHPTA4230C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CHPTA4230C3 / DR96SN1005CN | 1260 | 1 | ECM | 80 | 67 | 39000 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 216 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 96100 | 96 | DC4SEA4210 | CHPTA4230C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CHPTA4830C3 / DR96SN1005CN | 1340 | 1 | ECM | 80 | 67 | 45000 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 220 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 96100 | 96 | DC5SEA4810 | CHPTA4830C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR96SN1005CN | 1340 | 1 | ECM | 80 | 67 | 45000 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 220 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 96100 | 96 | DC4SEA4810 | CHPTA4830C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA6030D3 / DR96SN1005CN | 1810 | 1 | ECM | 80 | 67 | 56000 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 224 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.2 / 11.5 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 96100 | 96 | DC5SEA6010 | CHPTA6030D3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA3626C3 / DR96SN1005CN | 1080 | 1 | ECM | 80 | 67 | 34200 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 204 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 14.5 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 96100 | 96 | DC5SEA3610 | CAPTA3626C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA4230C3 / DR96SN1005CN | 1260 | 1 | ECM | 80 | 67 | 39500 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 208 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 96100 | 96 | DC5SEA4210 | CAPTA4230C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR96SN1005CN | 1260 | 1 | ECM | 80 | 67 | 39000 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 208 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 96100 | 96 | DC4SEA4210 | CAPTA4230C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR96SN1005CN | 1370 | 1 | ECM | 80 | 67 | 45000 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 215 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 96100 | 96 | DC5SEA4810 | CAPTA6030C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA3630C3 / DR96SN1005CN | 1040 | 1 | ECM | 80 | 67 | 34400 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 216 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 96100 | 96 | DC5SEA3610 | CHPTA3630C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR96SN1005CN | 1040 | 1 | ECM | 80 | 67 | 34200 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 216 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 96100 | 96 | DC4SEA3610 | CHPTA3630C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4830C3 / DR96SN1005CN | 1330 | 1 | ECM | 80 | 67 | 44500 | 100000 | 96100 |  | 1 | 96 | 115/60/1 | 16.4 | 25 | 220 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 96100 | 96 | DC5SEA4810 | CHPTA4830C3 | DR96SN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA4230C3 / DR96SN1205DN | 1240 | 1 | ECM | 80 | 67 | 40000 | 120000 | 115320 |  | 1 | 96 | 115/60/1 | 16.7 | 25 | 220 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 115320 | 96 | DC5SEA4210 | CAPTA4230C3 | DR96SN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230D3 / DR96SN1205DN | 1240 | 1 | ECM | 80 | 67 | 39500 | 120000 | 115320 |  | 1 | 96 | 115/60/1 | 16.7 | 25 | 226 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 115320 | 96 | DC4SEA4210 | CAPTA4230D3 | DR96SN1205DN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030D3 / DR96SN1205DN | 1350 | 1 | ECM | 80 | 67 | 45500 | 120000 | 115320 |  | 1 | 96 | 115/60/1 | 16.7 | 25 | 231 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12.5 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 115320 | 96 | DC5SEA4810 | CAPTA6030D3 | DR96SN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030D3 / DR96SN1205DN | 1380 | 1 | ECM | 80 | 67 | 45500 | 120000 | 115320 |  | 1 | 96 | 115/60/1 | 16.7 | 25 | 231 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 115320 | 96 | DC4SEA4810 | CAPTA6030D3 | DR96SN1205DN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CAPTA6030D3 / DR96SN1205DN | 1500 | 1 | ECM | 80 | 67 | 56500 | 120000 | 115320 |  | 1 | 96 | 115/60/1 | 16.7 | 25 | 231 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 115320 | 96 | DC4SEA6010 | CAPTA6030D3 | DR96SN1205DN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | CHPTA6030D3 / DR96SN1205DN | 1500 | 1 | ECM | 80 | 67 | 56000 | 120000 | 115320 |  | 1 | 96 | 115/60/1 | 16.7 | 25 | 236 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.2 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 120000 | 115320 | 96 | DC4SEA6010 | CHPTA6030D3 | DR96SN1205DN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC4SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | CAPTA6030D3 / DR96SN1205DN | 1790 | 1 | ECM | 80 | 67 | 56500 | 120000 | 115320 |  | 1 | 96 | 115/60/1 | 16.7 | 25 | 231 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.2 / 11.7 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 115320 | 96 | DC5SEA6010 | CAPTA6030D3 | DR96SN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA6030D3 / DR96SN1205DN | 1380 | 1 | ECM | 80 | 67 | 45500 | 120000 | 115320 |  | 1 | 96 | 115/60/1 | 16.7 | 25 | 231 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 115320 | 96 | DC5SEA4810 | CAPTA6030D3 | DR96SN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA6030D3 / DR96SN1205DN | 1790 | 1 | ECM | 80 | 67 | 56000 | 120000 | 115320 |  | 1 | 96 | 115/60/1 | 16.7 | 25 | 236 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.2 / 11.5 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 1 | 120000 | 115320 | 96 | DC5SEA6010 | CHPTA6030D3 | DR96SN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96SN | IM - DC5SEA | IM - DR96SN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPEA2418B3 / DR96TC0403BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 40000 | 39000 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 160 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 18 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 40000 | 39000 | 96 | DC6VSS2410 | CAPEA2418B3 | DR96TC0403BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR96TC0403BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 40000 | 39000 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 167 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 9.8 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 40000 | 39000 | 96 | DC6VSS3010 | CAPEA3022B3 | DR96TC0403BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR96TC0403BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 40000 | 39000 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 167 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 40000 | 39000 | 96 | DC6VSS1810 | CAPEA3022B3 | DR96TC0403BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626B3 / DR96TC0403BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 40000 | 39000 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 172 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 40000 | 39000 | 96 | DC6VSS3610 | CAPEA3626B3 | DR96TC0403BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR96TC0403BN | 840 | 0.5 | ECM | 80 | 67 | 24000 | 40000 | 39000 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 162 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.5 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 40000 | 39000 | 96 | DC7TCA2410 | CAPTA2422B3 | DR96TC0403BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR96TC0403BN | 1130 | 0.5 | ECM | 80 | 67 | 35000 | 40000 | 39000 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 169 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 16.7 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 40000 | 39000 | 96 | DC7TCA3610 | CAPTA3626B3 | DR96TC0403BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR96TC0403BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 40000 | 39000 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 172 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 17.5 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 40000 | 39000 | 96 | DC6VSS2410 | CHPEA2422B3 | DR96TC0403BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR96TC0403BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 40000 | 39000 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 172 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 40000 | 39000 | 96 | DC6VSS1810 | CHPEA2422B3 | DR96TC0403BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026B3 / DR96TC0403BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 40000 | 39000 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 180 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 40000 | 39000 | 96 | DC6VSS3010 | CHPEA3026B3 | DR96TC0403BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626B3 / DR96TC0403BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 40000 | 39000 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 182 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 40000 | 39000 | 96 | DC6VSS3610 | CHPEA3626B3 | DR96TC0403BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR96TC0403BN | 840 | 0.5 | ECM | 80 | 67 | 23600 | 40000 | 39000 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 174 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.2 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 40000 | 39000 | 96 | DC7TCA2410 | CHPTA2426B3 | DR96TC0403BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR96TC0403BN | 1130 | 0.5 | ECM | 80 | 67 | 34600 | 40000 | 39000 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 184 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 16.5 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 40000 | 39000 | 96 | DC7TCA3610 | CHPTA3630B3 | DR96TC0403BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA2418B3 / DR96TC0603BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 167 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 18 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC6VSS2410 | CAPEA2418B3 | DR96TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR96TC0603BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 174 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 9.8 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC6VSS3010 | CAPEA3022B3 | DR96TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR96TC0603BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 174 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC6VSS1810 | CAPEA3022B3 | DR96TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626B3 / DR96TC0603BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 179 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC6VSS3610 | CAPEA3626B3 | DR96TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR96TC0603BN | 840 | 0.5 | ECM | 80 | 67 | 24000 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 169 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.5 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC7TCA2410 | CAPTA2422B3 | DR96TC0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR96TC0603BN | 1120 | 0.5 | ECM | 80 | 67 | 35000 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 176 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 16.7 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC7TCA3610 | CAPTA3626B3 | DR96TC0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR96TC0603BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 179 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 17.5 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 60000 | 58200 | 96 | DC6VSS2410 | CHPEA2422B3 | DR96TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR96TC0603BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 179 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 60000 | 58200 | 96 | DC6VSS1810 | CHPEA2422B3 | DR96TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026B3 / DR96TC0603BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 187 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 60000 | 58200 | 96 | DC6VSS3010 | CHPEA3026B3 | DR96TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626B3 / DR96TC0603BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 189 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 60000 | 58200 | 96 | DC6VSS3610 | CHPEA3626B3 | DR96TC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR96TC0603BN | 840 | 0.5 | ECM | 80 | 67 | 23600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 181 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.2 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 60000 | 58200 | 96 | DC7TCA2410 | CHPTA2426B3 | DR96TC0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR96TC0603BN | 1140 | 0.5 | ECM | 80 | 67 | 34600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 191 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 16.5 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 60000 | 58200 | 96 | DC7TCA3610 | CHPTA3630B3 | DR96TC0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA2418B3 / DR96TC0803BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 170 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 18 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC6VSS2410 | CAPEA2418B3 | DR96TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR96TC0803BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 177 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 9.8 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC6VSS3010 | CAPEA3022B3 | DR96TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR96TC0803BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 177 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC6VSS1810 | CAPEA3022B3 | DR96TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626B3 / DR96TC0803BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 182 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC6VSS3610 | CAPEA3626B3 | DR96TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR96TC0803BN | 840 | 0.5 | ECM | 80 | 67 | 24000 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 172 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.5 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC7TCA2410 | CAPTA2422B3 | DR96TC0803BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR96TC0803BN | 1120 | 0.5 | ECM | 80 | 67 | 35000 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 179 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 16.7 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC7TCA3610 | CAPTA3626B3 | DR96TC0803BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR96TC0803BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 182 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 17.5 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 76880 | 96 | DC6VSS2410 | CHPEA2422B3 | DR96TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR96TC0803BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 182 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 76880 | 96 | DC6VSS1810 | CHPEA2422B3 | DR96TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026B3 / DR96TC0803BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 190 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 76880 | 96 | DC6VSS3010 | CHPEA3026B3 | DR96TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626B3 / DR96TC0803BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 192 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 76880 | 96 | DC6VSS3610 | CHPEA3626B3 | DR96TC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR96TC0803BN | 840 | 0.5 | ECM | 80 | 67 | 23600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 184 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.2 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 76880 | 96 | DC7TCA2410 | CHPTA2426B3 | DR96TC0803BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR96TC0803BN | 1120 | 0.5 | ECM | 80 | 67 | 34600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.5 | 15 | 194 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 16.5 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 76880 | 96 | DC7TCA3610 | CHPTA3630B3 | DR96TC0803BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA2418C3 / DR96TC0804CN | 800 | 0.75 | ECM | 80 | 67 | 23200 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 189 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 18 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC6VSS2410 | CAPEA2418C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022C3 / DR96TC0804CN | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 196 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC6VSS3010 | CAPEA3022C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022C3 / DR96TC0804CN | 610 | 0.75 | ECM | 80 | 67 | 17100 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 196 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC6VSS1810 | CAPEA3022C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626C3 / DR96TC0804CN | 1260 | 0.75 | ECM | 80 | 67 | 33600 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 199 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC6VSS3610 | CAPEA3626C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR96TC0804CN | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 208 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16 / 8.6 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC6VSS4810 | CAPEA4830C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR96TC0804CN | 1320 | 0.75 | ECM | 80 | 67 | 41000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 208 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC6VSS4210 | CAPEA4830C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA6030C3 / DR96TC0804CN | 1640 | 0.75 | ECM | 80 | 67 | 52000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 210 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.5 / 8.4 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC6VSS6010 | CAPEA6030C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR96TC0804CN | 840 | 0.75 | ECM | 80 | 67 | 24000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 190 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.5 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC7TCA2410 | CAPTA2422C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR96TC0804CN | 1150 | 0.75 | ECM | 80 | 67 | 35000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 200 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17.2 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC7TCA3610 | CAPTA3626C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR96TC0804CN | 1380 | 0.75 | ECM | 80 | 67 | 46000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 211 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.2 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC7TCA4810 | CAPTA6030C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026C3 / DR96TC0804CN | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 207 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 77600 | 96 | DC6VSS3010 | CHPEA3026C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626C3 / DR96TC0804CN | 1260 | 0.75 | ECM | 80 | 67 | 33600 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 211 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 77600 | 96 | DC6VSS3610 | CHPEA3626C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR96TC0804CN | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 218 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16 / 8.6 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 77600 | 96 | DC6VSS4810 | CHPEA4830C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR96TC0804CN | 1320 | 0.75 | ECM | 80 | 67 | 41000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 218 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.5 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 77600 | 96 | DC6VSS4210 | CHPEA4830C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA6030C3 / DR96TC0804CN | 1640 | 0.75 | ECM | 80 | 67 | 52000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 218 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.2 / 8.2 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 80000 | 77600 | 96 | DC6VSS6010 | CHPEA6030C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR96TC0804CN | 840 | 0.75 | ECM | 80 | 67 | 23600 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 202 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.5 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 77600 | 96 | DC7TCA2410 | CHPTA2426C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR96TC0804CN | 1150 | 0.75 | ECM | 80 | 67 | 34600 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 212 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 77600 | 96 | DC7TCA3610 | CHPTA3630C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR96TC0804CN | 1380 | 0.75 | ECM | 80 | 67 | 45000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 10.8 | 15 | 216 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 16.7 / 12 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 80000 | 77600 | 96 | DC7TCA4810 | CHPTA4830C3 | DR96TC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022C3 / DR96TC1005CN | 1010 | 1 | ECM | 80 | 67 | 28400 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 202 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 96100 | 96 | DC6VSS3010 | CAPEA3022C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626C3 / DR96TC1005CN | 1260 | 1 | ECM | 80 | 67 | 33600 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 205 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 96100 | 96 | DC6VSS3610 | CAPEA3626C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR96TC1005CN | 1380 | 1 | ECM | 80 | 67 | 45500 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 214 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16 / 8.6 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 96100 | 96 | DC6VSS4810 | CAPEA4830C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR96TC1005CN | 1320 | 1 | ECM | 80 | 67 | 41000 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 214 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 96100 | 96 | DC6VSS4210 | CAPEA4830C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA6030C3 / DR96TC1005CN | 1640 | 1 | ECM | 80 | 67 | 52000 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 216 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.5 / 8.4 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 96100 | 96 | DC6VSS6010 | CAPEA6030C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR96TC1005CN | 1120 | 1 | ECM | 80 | 67 | 35000 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 206 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17.2 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 100000 | 96100 | 96 | DC7TCA3610 | CAPTA3626C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR96TC1005CN | 1480 | 1 | ECM | 80 | 67 | 56500 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 217 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 16 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 100000 | 96100 | 96 | DC7TCA6010 | CAPTA6030C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR96TC1005CN | 1380 | 1 | ECM | 80 | 67 | 46500 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 217 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.2 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 100000 | 96100 | 96 | DC7TCA4810 | CAPTA6030C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026C3 / DR96TC1005CN | 1010 | 1 | ECM | 80 | 67 | 28400 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 213 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 96100 | 96 | DC6VSS3010 | CHPEA3026C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626C3 / DR96TC1005CN | 1260 | 1 | ECM | 80 | 67 | 33600 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 217 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 96100 | 96 | DC6VSS3610 | CHPEA3626C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR96TC1005CN | 1380 | 1 | ECM | 80 | 67 | 45500 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 224 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16 / 8.6 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 96100 | 96 | DC6VSS4810 | CHPEA4830C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR96TC1005CN | 1320 | 1 | ECM | 80 | 67 | 41000 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 224 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.5 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 96100 | 96 | DC6VSS4210 | CHPEA4830C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA6030C3 / DR96TC1005CN | 1640 | 1 | ECM | 80 | 67 | 52000 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 224 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.2 / 8.2 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 96100 | 96 | DC6VSS6010 | CHPEA6030C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR96TC1005CN | 1380 | 1 | ECM | 80 | 67 | 45500 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 222 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 16.7 / 12 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 100000 | 96100 | 96 | DC7TCA4810 | CHPTA4830C3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR96TC1005CN | 1480 | 1 | ECM | 80 | 67 | 56000 | 100000 | 96100 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 226 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 100000 | 96100 | 96 | DC7TCA6010 | CHPTA6030D3 | DR96TC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626D3 / DR96TC1005DN | 1260 | 1 | ECM | 80 | 67 | 33600 | 100000 | 97500 |  | 2 | 96 | 115/60/1 | 13.9 | 20 | 220 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16.6 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 97500 | 96 | DC6VSS3610 | CAPEA3626D3 | DR96TC1005DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830D3 / DR96TC1005DN | 1380 | 1 | ECM | 80 | 67 | 45500 | 100000 | 97500 |  | 2 | 96 | 115/60/1 | 13.9 | 20 | 227 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.2 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 97500 | 96 | DC6VSS4810 | CAPEA4830D3 | DR96TC1005DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830D3 / DR96TC1005DN | 1320 | 1 | ECM | 80 | 67 | 41000 | 100000 | 97500 |  | 2 | 96 | 115/60/1 | 13.9 | 20 | 227 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 97500 | 96 | DC6VSS4210 | CAPEA4830D3 | DR96TC1005DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA6030D3 / DR96TC1005DN | 1640 | 1 | ECM | 80 | 67 | 52500 | 100000 | 97500 |  | 2 | 96 | 115/60/1 | 13.9 | 20 | 231 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.5 / 8.5 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 100000 | 97500 | 96 | DC6VSS6010 | CAPEA6030D3 | DR96TC1005DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830D3 / DR96TC1005DN | 1380 | 1 | ECM | 80 | 67 | 45500 | 100000 | 97500 |  | 2 | 96 | 115/60/1 | 13.9 | 20 | 237 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.2 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 97500 | 96 | DC6VSS4810 | CHPEA4830D3 | DR96TC1005DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830D3 / DR96TC1005DN | 1320 | 1 | ECM | 80 | 67 | 41000 | 100000 | 97500 |  | 2 | 96 | 115/60/1 | 13.9 | 20 | 237 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.5 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 97500 | 96 | DC6VSS4210 | CHPEA4830D3 | DR96TC1005DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA6030D3 / DR96TC1005DN | 1640 | 1 | ECM | 80 | 67 | 52500 | 100000 | 97500 |  | 2 | 96 | 115/60/1 | 13.9 | 20 | 234 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.2 / 8.4 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 100000 | 97500 | 96 | DC6VSS6010 | CHPEA6030D3 | DR96TC1005DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR96TC1005DN | 1480 | 1 | ECM | 80 | 67 | 56000 | 100000 | 97500 |  | 2 | 96 | 115/60/1 | 13.9 | 20 | 236 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 100000 | 97500 | 96 | DC7TCA6010 | CHPTA6030D3 | DR96TC1005DN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626D3 / DR96TC1205DN | 1260 | 1 | ECM | 80 | 67 | 33600 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 223 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16.6 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 120000 | 115320 | 96 | DC6VSS3610 | CAPEA3626D3 | DR96TC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830D3 / DR96TC1205DN | 1380 | 1 | ECM | 80 | 67 | 45500 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 230 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.2 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 120000 | 115320 | 96 | DC6VSS4810 | CAPEA4830D3 | DR96TC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830D3 / DR96TC1205DN | 1320 | 1 | ECM | 80 | 67 | 41000 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 230 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 120000 | 115320 | 96 | DC6VSS4210 | CAPEA4830D3 | DR96TC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA6030D3 / DR96TC1205DN | 1640 | 1 | ECM | 80 | 67 | 52500 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 234 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.5 / 8.5 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | 2 | 120000 | 115320 | 96 | DC6VSS6010 | CAPEA6030D3 | DR96TC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR96TC1205DN | 1480 | 1 | ECM | 80 | 67 | 57500 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 230 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 16 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 120000 | 115320 | 96 | DC7TCA6010 | CAPTA6030C3 | DR96TC1205DN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR96TC1205DN | 1380 | 1 | ECM | 80 | 67 | 46000 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 230 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.2 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 120000 | 115320 | 96 | DC7TCA4810 | CAPTA6030C3 | DR96TC1205DN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830D3 / DR96TC1205DN | 1380 | 1 | ECM | 80 | 67 | 45500 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 240 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.2 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 120000 | 115320 | 96 | DC6VSS4810 | CHPEA4830D3 | DR96TC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830D3 / DR96TC1205DN | 1320 | 1 | ECM | 80 | 67 | 41000 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 240 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.5 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 120000 | 115320 | 96 | DC6VSS4210 | CHPEA4830D3 | DR96TC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA6030D3 / DR96TC1205DN | 1640 | 1 | ECM | 80 | 67 | 52500 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 237 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.2 / 8.4 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | 2 | 120000 | 115320 | 96 | DC6VSS6010 | CHPEA6030D3 | DR96TC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC6VS | IM - DR96TC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR96TC1205DN | 1480 | 1 | ECM | 80 | 67 | 56000 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 13.8 | 20 | 239 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 16 / 11.8 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | 2 | 120000 | 115320 | 96 | DC7TCA6010 | CHPTA6030D3 | DR96TC1205DN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TC | IM - DC7TCA | IM - DR96TC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR96TN0303AN | 810 | 0.5 | ECM | 80 | 67 | 23400 | 30000 | 29100 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 149 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 30000 | 29100 | 96 | DC5SEA2410 | CAPTA2422A3 | DR96TN0303AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422A3 / DR96TN0303AN | 620 | 0.5 | ECM | 80 | 67 | 17600 | 30000 | 29100 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 149 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 30000 | 29100 | 96 | DC5SEA1810 | CAPTA2422A3 | DR96TN0303AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422A3 / DR96TN0303AN | 810 | 0.5 | ECM | 80 | 67 | 23000 | 30000 | 29100 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 149 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.3 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 30000 | 29100 | 96 | DC4SEA2410 | CAPTA2422A3 | DR96TN0303AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422A3 / DR96TN0303AN | 620 | 0.5 | ECM | 80 | 67 | 17600 | 30000 | 29100 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 149 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 30000 | 29100 | 96 | DC4SEA1810 | CAPTA2422A3 | DR96TN0303AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0303AN | 810 | 0.5 | ECM | 80 | 67 | 23400 | 30000 | 29100 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 165 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 30000 | 29100 | 96 | DC5SEA2410 | CHPTA2426B3 | DR96TN0303AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0303AN | 620 | 0.5 | ECM | 80 | 67 | 17600 | 30000 | 29100 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 165 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 30000 | 29100 | 96 | DC5SEA1810 | CHPTA2426B3 | DR96TN0303AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422A3 / DR96TN0403AN | 820 | 0.5 | ECM | 80 | 67 | 23400 | 40000 | 38800 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 149 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 38800 | 96 | DC5SEA2410 | CAPTA2422A3 | DR96TN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422A3 / DR96TN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17600 | 40000 | 38800 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 149 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 38800 | 96 | DC5SEA1810 | CAPTA2422A3 | DR96TN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422A3 / DR96TN0403AN | 820 | 0.5 | ECM | 80 | 67 | 23000 | 40000 | 38800 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 149 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.3 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 38800 | 96 | DC4SEA2410 | CAPTA2422A3 | DR96TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422A3 / DR96TN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17800 | 40000 | 38800 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 149 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 38800 | 96 | DC4SEA1810 | CAPTA2422A3 | DR96TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0403AN | 810 | 0.5 | ECM | 80 | 67 | 23400 | 40000 | 38800 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 165 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 40000 | 38800 | 96 | DC5SEA2410 | CHPTA2426B3 | DR96TN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0403AN | 640 | 0.5 | ECM | 80 | 67 | 17600 | 40000 | 38800 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 165 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 40000 | 38800 | 96 | DC5SEA1810 | CHPTA2426B3 | DR96TN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR96TN0403AN | 930 | 0.5 | ECM | 80 | 67 | 28200 | 40000 | 38800 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 168 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 40000 | 38800 | 96 | DC5SEA3010 | CHPTA3026B3 | DR96TN0403AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422A3 / DR96TN0603AN | 810 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 57660 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 154 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 57660 | 96 | DC5SEA2410 | CAPTA2422A3 | DR96TN0603AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422A3 / DR96TN0603AN | 620 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 57660 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 154 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 57660 | 96 | DC5SEA1810 | CAPTA2422A3 | DR96TN0603AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422A3 / DR96TN0603AN | 810 | 0.5 | ECM | 80 | 67 | 22800 | 60000 | 57660 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 154 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.3 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 57660 | 96 | DC4SEA2410 | CAPTA2422A3 | DR96TN0603AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422A3 / DR96TN0603AN | 620 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 57660 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 154 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 57660 | 96 | DC4SEA1810 | CAPTA2422A3 | DR96TN0603AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0603AN | 810 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 57660 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 170 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 57660 | 96 | DC5SEA2410 | CHPTA2426B3 | DR96TN0603AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0603AN | 620 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 57660 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 170 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 57660 | 96 | DC5SEA1810 | CHPTA2426B3 | DR96TN0603AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR96TN0603AN | 920 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 57660 |  | 2 | 96 | 115/60/1 | 7.8 | 15 | 173 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 57660 | 96 | DC5SEA3010 | CHPTA3026B3 | DR96TN0603AN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0603BN | 850 | 0.5 | ECM | 80 | 67 | 24000 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 168 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC7TCA2410 | CAPTA2422B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC7TCA | IM - DR96TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026B3 / DR96TN0603BN | 940 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 173 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC5SEA3010 | CAPTA3026B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0603BN | 820 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 168 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC5SEA2410 | CAPTA2422B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0603BN | 600 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 168 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC5SEA1810 | CAPTA2422B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0603BN | 820 | 0.5 | ECM | 80 | 67 | 23600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 168 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC4SEA2410 | CAPTA2422B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0603BN | 600 | 0.5 | ECM | 80 | 67 | 17800 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 168 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC4SEA1810 | CAPTA2422B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3022B3 / DR96TN0603BN | 930 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 167 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC5SEA3010 | CAPTA3022B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3026B3 / DR96TN0603BN | 940 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 173 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC4SEA3010 | CAPTA3026B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626B3 / DR96TN0603BN | 1040 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 175 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC5SEA3610 | CAPTA3626B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626B3 / DR96TN0603BN | 1040 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 175 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC4SEA3610 | CAPTA3626B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA2426B3 / DR96TN0603BN | 810 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 180 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC5SEA2410 | CHPTA2426B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 180 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC5SEA1810 | CHPTA2426B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0603BN | 810 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 180 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC4SEA2410 | CHPTA2426B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 180 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC4SEA1810 | CHPTA2426B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR96TN0603BN | 930 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 183 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC5SEA3010 | CHPTA3026B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026B3 / DR96TN0603BN | 930 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 183 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC4SEA3010 | CHPTA3026B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630B3 / DR96TN0603BN | 1030 | 0.5 | ECM | 80 | 67 | 34400 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 190 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC5SEA3610 | CHPTA3630B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630B3 / DR96TN0603BN | 1030 | 0.5 | ECM | 80 | 67 | 34600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 190 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC4SEA3610 | CHPTA3630B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA3026B3 / DR96TN0603BN | 930 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 173 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC5SEA3010 | CAPTA3026B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0603BN | 830 | 0.5 | ECM | 80 | 67 | 23600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 168 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC5SEA2410 | CAPTA2422B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0603BN | 550 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 168 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC5SEA1810 | CAPTA2422B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0603BN | 830 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 168 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC4SEA2410 | CAPTA2422B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0603BN | 630 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 168 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC4SEA1810 | CAPTA2422B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3022B3 / DR96TN0603BN | 920 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 167 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC5SEA3010 | CAPTA3022B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3026B3 / DR96TN0603BN | 930 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 173 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.3 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC4SEA3010 | CAPTA3026B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626B3 / DR96TN0603BN | 1090 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 175 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 14.5 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC5SEA3610 | CAPTA3626B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626B3 / DR96TN0603BN | 1090 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 175 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 58200 | 96 | DC4SEA3610 | CAPTA3626B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA2426B3 / DR96TN0603BN | 820 | 0.5 | ECM | 80 | 67 | 23600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 180 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC5SEA2410 | CHPTA2426B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0603BN | 560 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 180 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC5SEA1810 | CHPTA2426B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0603BN | 820 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 180 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC4SEA2410 | CHPTA2426B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0603BN | 630 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 180 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC4SEA1810 | CHPTA2426B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR96TN0603BN | 930 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 183 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC5SEA3010 | CHPTA3026B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026B3 / DR96TN0603BN | 930 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 183 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC4SEA3010 | CHPTA3026B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630B3 / DR96TN0603BN | 1090 | 0.5 | ECM | 80 | 67 | 34400 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 190 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 14.5 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC5SEA3610 | CHPTA3630B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630B3 / DR96TN0603BN | 1080 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 58200 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 190 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 58200 | 96 | DC4SEA3610 | CHPTA3630B3 | DR96TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA3026B3 / DR96TN0803BN | 930 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 178 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC5SEA3010 | CAPTA3026B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0803BN | 810 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 173 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC5SEA2410 | CAPTA2422B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0803BN | 580 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 173 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC5SEA1810 | CAPTA2422B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0803BN | 810 | 0.5 | ECM | 80 | 67 | 23600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 173 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC4SEA2410 | CAPTA2422B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0803BN | 580 | 0.5 | ECM | 80 | 67 | 17800 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 173 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC4SEA1810 | CAPTA2422B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3022B3 / DR96TN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 172 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC5SEA3010 | CAPTA3022B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3026B3 / DR96TN0803BN | 930 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 178 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC4SEA3010 | CAPTA3026B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626B3 / DR96TN0803BN | 1060 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 180 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC5SEA3610 | CAPTA3626B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626B3 / DR96TN0803BN | 1060 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 180 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC4SEA3610 | CAPTA3626B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA2426B3 / DR96TN0803BN | 800 | 0.5 | ECM | 80 | 67 | 23600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 185 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC5SEA2410 | CHPTA2426B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0803BN | 600 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 185 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC5SEA1810 | CHPTA2426B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0803BN | 800 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 185 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC4SEA2410 | CHPTA2426B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0803BN | 600 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 185 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC4SEA1810 | CHPTA2426B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR96TN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 188 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC5SEA3010 | CHPTA3026B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026B3 / DR96TN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 188 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC4SEA3010 | CHPTA3026B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630B3 / DR96TN0803BN | 1050 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 195 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC5SEA3610 | CHPTA3630B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630B3 / DR96TN0803BN | 1050 | 0.5 | ECM | 80 | 67 | 34600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 195 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC4SEA3610 | CHPTA3630B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA2422B3 / DR96TN0803BN | 820 | 0.5 | ECM | 80 | 67 | 23600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 173 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC5SEA2410 | CAPTA2422B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0803BN | 600 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 173 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC5SEA1810 | CAPTA2422B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0803BN | 820 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 173 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC4SEA2410 | CAPTA2422B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA2422B3 / DR96TN0803BN | 600 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 173 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC4SEA1810 | CAPTA2422B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CAPTA3026B3 / DR96TN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 178 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.3 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC4SEA3010 | CAPTA3026B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626B3 / DR96TN0803BN | 1150 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 180 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 14.5 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC5SEA3610 | CAPTA3626B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626B3 / DR96TN0803BN | 1040 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 180 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 76880 | 96 | DC4SEA3610 | CAPTA3626B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA2426B3 / DR96TN0803BN | 810 | 0.5 | ECM | 80 | 67 | 23600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 185 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 14.5 / 12 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC5SEA2410 | CHPTA2426B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0803BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 185 | DAIKIN | DC5SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 142 | 1 | 1.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC5SEA1810 | CHPTA2426B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0803BN | 810 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 185 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC4SEA2410 | CHPTA2426B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA2426B3 / DR96TN0803BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 185 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 11.7 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC4SEA1810 | CHPTA2426B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | CHPTA3026B3 / DR96TN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 188 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC4SEA3010 | CHPTA3026B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630B3 / DR96TN0803BN | 1080 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 195 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 14.5 / 12 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC5SEA3610 | CHPTA3630B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630B3 / DR96TN0803BN | 1030 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 76880 |  | 2 | 96 | 115/60/1 | 7.7 | 15 | 195 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 14.5 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 76880 | 96 | DC4SEA3610 | CHPTA3630B3 | DR96TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA3026C3 / DR96TN0804CN | 900 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 193 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC5SEA3010 | CAPTA3026C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA6030C3 / DR96TN0804CN | 1490 | 0.75 | ECM | 80 | 67 | 47000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 207 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17 / 12 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC7TCA4810 | CAPTA6030C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC7TCA | IM - DR96TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR96TN0804CN | 760 | 0.75 | ECM | 80 | 67 | 23600 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 186 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC5SEA2410 | CAPTA2422C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CAPTA2422C3 / DR96TN0804CN | 760 | 0.75 | ECM | 80 | 67 | 23200 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 186 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC4SEA2410 | CAPTA2422C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CAPTA3026C3 / DR96TN0804CN | 900 | 0.75 | ECM | 80 | 67 | 28200 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 193 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC4SEA3010 | CAPTA3026C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CAPTA3626C3 / DR96TN0804CN | 1080 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 196 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC5SEA3610 | CAPTA3626C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626C3 / DR96TN0804CN | 1080 | 0.75 | ECM | 80 | 67 | 34200 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 196 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC4SEA3610 | CAPTA3626C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA4230C3 / DR96TN0804CN | 1230 | 0.75 | ECM | 80 | 67 | 39000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 200 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC4SEA4210 | CAPTA4230C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR96TN0804CN | 1370 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 207 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC5SEA4810 | CAPTA6030C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR96TN0804CN | 1340 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 207 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 77600 | 96 | DC4SEA4810 | CAPTA6030C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA2426C3 / DR96TN0804CN | 750 | 0.75 | ECM | 80 | 67 | 23400 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 198 | DAIKIN | DC5SEA2410 | 208/60/1 | 13.8 | 20 | 95 | R-32 | 15.2 / 12.5 | 168 | 1 | 2 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 77600 | 96 | DC5SEA2410 | CHPTA2426C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | CHPTA2426C3 / DR96TN0804CN | 750 | 0.75 | ECM | 80 | 67 | 23200 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 198 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 77600 | 96 | DC4SEA2410 | CHPTA2426C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | CHPTA3026C3 / DR96TN0804CN | 900 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 200 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 77600 | 96 | DC5SEA3010 | CHPTA3026C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3026C3 / DR96TN0804CN | 900 | 0.75 | ECM | 80 | 67 | 28600 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 200 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 77600 | 96 | DC4SEA3010 | CHPTA3026C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | CHPTA3630C3 / DR96TN0804CN | 1050 | 0.75 | ECM | 80 | 67 | 34600 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 208 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 77600 | 96 | DC5SEA3610 | CHPTA3630C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR96TN0804CN | 1050 | 0.75 | ECM | 80 | 67 | 34200 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 208 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 77600 | 96 | DC4SEA3610 | CHPTA3630C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4230C3 / DR96TN0804CN | 1280 | 0.75 | ECM | 80 | 67 | 39000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 208 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 77600 | 96 | DC4SEA4210 | CHPTA4230C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CHPTA4830C3 / DR96TN0804CN | 1330 | 0.75 | ECM | 80 | 67 | 45000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 212 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 77600 | 96 | DC5SEA4810 | CHPTA4830C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR96TN0804CN | 1330 | 0.75 | ECM | 80 | 67 | 45000 | 80000 | 77600 |  | 2 | 96 | 115/60/1 | 11.3 | 15 | 212 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 77600 | 96 | DC4SEA4810 | CHPTA4830C3 | DR96TN0804CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CAPTA3026C3 / DR96TN1004CN | 860 | 1 | ECM | 80 | 67 | 28400 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 201 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC5SEA3010 | CAPTA3026C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA6030C3 / DR96TN1004CN | 1550 | 1 | ECM | 80 | 67 | 47000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 215 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 16.5 / 12 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC7TCA4810 | CAPTA6030C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC7TCA | IM - DR96TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR96TN1004CN | 1100 | 1 | ECM | 80 | 67 | 34400 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 204 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC5SEA3610 | CAPTA3626C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA4230C3 / DR96TN1004CN | 1250 | 1 | ECM | 80 | 67 | 40000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 208 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC5SEA4210 | CAPTA4230C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230C3 / DR96TN1004CN | 1250 | 1 | ECM | 80 | 67 | 39000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 208 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC4SEA4210 | CAPTA4230C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR96TN1004CN | 1330 | 1 | ECM | 80 | 67 | 45500 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 215 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC5SEA4810 | CAPTA6030C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR96TN1004CN | 1340 | 1 | ECM | 80 | 67 | 45500 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 215 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC4SEA4810 | CAPTA6030C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA3026C3 / DR96TN1004CN | 860 | 1 | ECM | 80 | 67 | 28400 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 208 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC5SEA3010 | CHPTA3026C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3630C3 / DR96TN1004CN | 1070 | 1 | ECM | 80 | 67 | 34600 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 216 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC5SEA3610 | CHPTA3630C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR96TN1004CN | 1070 | 1 | ECM | 80 | 67 | 34200 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 216 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC4SEA3610 | CHPTA3630C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4230C3 / DR96TN1004CN | 1300 | 1 | ECM | 80 | 67 | 39000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 216 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 14.5 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC5SEA4210 | CHPTA4230C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CHPTA4230C3 / DR96TN1004CN | 1300 | 1 | ECM | 80 | 67 | 39000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 216 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC4SEA4210 | CHPTA4230C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CHPTA4830C3 / DR96TN1004CN | 1370 | 1 | ECM | 80 | 67 | 45000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 220 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC5SEA4810 | CHPTA4830C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR96TN1004CN | 1300 | 1 | ECM | 80 | 67 | 45000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 220 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC4SEA4810 | CHPTA4830C3 | DR96TN1004CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CAPTA3026C3 / DR96TN1005CN | 940 | 1 | ECM | 80 | 67 | 28400 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 202 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC5SEA3010 | CAPTA3026C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3022C3 / DR96TN1005CN | 930 | 1 | ECM | 80 | 67 | 28400 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 195 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC5SEA3010 | CAPTA3022C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CAPTA3626C3 / DR96TN1005CN | 1080 | 1 | ECM | 80 | 67 | 34400 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 205 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC5SEA3610 | CAPTA3626C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CAPTA3626C3 / DR96TN1005CN | 1080 | 1 | ECM | 80 | 67 | 34200 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 205 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC4SEA3610 | CAPTA3626C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CAPTA6030C3 / DR96TN1005CN | 1650 | 1 | ECM | 80 | 67 | 56500 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 216 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 11.5 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC5SEA6010 | CAPTA6030C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA6030C3 / DR96TN1005CN | 1420 | 1 | ECM | 80 | 67 | 45500 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 216 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC5SEA4810 | CAPTA6030C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030C3 / DR96TN1005CN | 1420 | 1 | ECM | 80 | 67 | 45500 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 216 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC4SEA4810 | CAPTA6030C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA3026C3 / DR96TN1005CN | 930 | 1 | ECM | 80 | 67 | 28400 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 209 | DAIKIN | DC5SEA3010 | 208/60/1 | 15.4 | 25 | 95 | R-32 | 15.2 / 12.5 | 222 | 1 | 2.5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC5SEA3010 | CHPTA3026C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | CHPTA3630C3 / DR96TN1005CN | 1040 | 1 | ECM | 80 | 67 | 34600 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 217 | DAIKIN | DC5SEA3610 | 208/60/1 | 17.8 | 30 | 95 | R-32 | 15.2 / 12.5 | 226 | 1 | 3 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC5SEA3610 | CHPTA3630C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | CHPTA3630C3 / DR96TN1005CN | 1070 | 1 | ECM | 80 | 67 | 34200 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 217 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC4SEA3610 | CHPTA3630C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | CHPTA4830C3 / DR96TN1005CN | 1350 | 1 | ECM | 80 | 67 | 45000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 221 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC5SEA4810 | CHPTA4830C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR96TN1005CN | 1350 | 1 | ECM | 80 | 67 | 45000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 221 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC4SEA4810 | CHPTA4830C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CHPTA6030D3 / DR96TN1005CN | 1650 | 1 | ECM | 80 | 67 | 56000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 225 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.2 / 11.5 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC5SEA6010 | CHPTA6030D3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA4230C3 / DR96TN1005CN | 1250 | 1 | ECM | 80 | 67 | 39000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 209 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC4SEA4210 | CAPTA4230C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030C3 / DR96TN1005CN | 1650 | 1 | ECM | 80 | 67 | 56000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 216 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.2 / 11.5 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC5SEA6010 | CAPTA6030C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA6030C3 / DR96TN1005CN | 1370 | 1 | ECM | 80 | 67 | 45000 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 216 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 97000 | 96 | DC5SEA4810 | CAPTA6030C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA4830C3 / DR96TN1005CN | 1330 | 1 | ECM | 80 | 67 | 44500 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 221 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 14.5 / 12 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC5SEA4810 | CHPTA4830C3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CHPTA6030D3 / DR96TN1005CN | 1650 | 1 | ECM | 80 | 67 | 55500 | 100000 | 97000 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 225 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.2 / 11.5 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 97000 | 96 | DC5SEA6010 | CHPTA6030D3 | DR96TN1005CN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA4230D3 / DR96TN1205DN | 1250 | 1 | ECM | 80 | 67 | 40000 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 225 | DAIKIN | DC5SEA4210 | 208/60/1 | 19.3 | 30 | 95 | R-32 | 15.2 / 12 | 282 | 1 | 3.5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 115320 | 96 | DC5SEA4210 | CAPTA4230D3 | DR96TN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | CAPTA4230D3 / DR96TN1205DN | 1250 | 1 | ECM | 80 | 67 | 39500 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 225 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 115320 | 96 | DC4SEA4210 | CAPTA4230D3 | DR96TN1205DN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | CAPTA6030D3 / DR96TN1205DN | 1620 | 1 | ECM | 80 | 67 | 56500 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 230 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 12 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 115320 | 96 | DC5SEA6010 | CAPTA6030D3 | DR96TN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CAPTA6030D3 / DR96TN1205DN | 1360 | 1 | ECM | 80 | 67 | 45500 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 230 | DAIKIN | DC5SEA4810 | 208/60/1 | 25.5 | 40 | 95 | R-32 | 15.2 / 12.5 | 280 | 1 | 4 | 15.2 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 115320 | 96 | DC5SEA4810 | CAPTA6030D3 | DR96TN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | CAPTA6030D3 / DR96TN1205DN | 1390 | 1 | ECM | 80 | 67 | 45500 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 230 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 115320 | 96 | DC4SEA4810 | CAPTA6030D3 | DR96TN1205DN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | CAPTA6030D3 / DR96TN1205DN | 1500 | 1 | ECM | 80 | 67 | 56500 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 230 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 115320 | 96 | DC4SEA6010 | CAPTA6030D3 | DR96TN1205DN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CAPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | CHPTA6030D3 / DR96TN1205DN | 1620 | 1 | ECM | 80 | 67 | 56000 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 235 | DAIKIN | DC5SEA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.2 / 12 | 300 | 1 | 5 | 15.2 SEER2 (Single Stage) | 1 | Horizontal | 2 | 120000 | 115320 | 96 | DC5SEA6010 | CHPTA6030D3 | DR96TN1205DN |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC5SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | CHPTA6030D3 / DR96TN1205DN | 1500 | 1 | ECM | 80 | 67 | 56000 | 120000 | 115320 |  | 2 | 96 | 115/60/1 | 14.3 | 25 | 235 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.2 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 120000 | 115320 | 96 | DC4SEA6010 | CHPTA6030D3 | DR96TN1205DN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR96TN | IM - DC4SEA | IM - DR96TN | IM - CHPTA | [10 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | CAPEA2418B3 / DR97MC0603BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 58200 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 166 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 18 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 60000 | 58200 | 97 | DC6VSS2410 | CAPEA2418B3 | DR97MC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR97MC0603BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 173 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 9.8 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 60000 | 58200 | 97 | DC6VSS3010 | CAPEA3022B3 | DR97MC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR97MC0603BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 60000 | 58200 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 173 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 60000 | 58200 | 97 | DC6VSS1810 | CAPEA3022B3 | DR97MC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626B3 / DR97MC0603BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 60000 | 58200 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 178 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 60000 | 58200 | 97 | DC6VSS3610 | CAPEA3626B3 | DR97MC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR97MC0603BN | 840 | 0.5 | ECM | 80 | 67 | 24000 | 60000 | 58200 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 168 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.5 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | Modulating | 60000 | 58200 | 97 | DC7TCA2410 | CAPTA2422B3 | DR97MC0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR97MC0603BN | 1140 | 0.5 | ECM | 80 | 67 | 35000 | 60000 | 58200 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 175 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 16.7 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | Modulating | 60000 | 58200 | 97 | DC7TCA3610 | CAPTA3626B3 | DR97MC0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR97MC0603BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 58200 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 178 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 17.5 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 60000 | 58200 | 97 | DC6VSS2410 | CHPEA2422B3 | DR97MC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR97MC0603BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 60000 | 58200 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 178 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 60000 | 58200 | 97 | DC6VSS1810 | CHPEA2422B3 | DR97MC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026B3 / DR97MC0603BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 58200 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 186 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 60000 | 58200 | 97 | DC6VSS3010 | CHPEA3026B3 | DR97MC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626B3 / DR97MC0603BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 60000 | 58200 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 188 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 60000 | 58200 | 97 | DC6VSS3610 | CHPEA3626B3 | DR97MC0603BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR97MC0603BN | 840 | 0.5 | ECM | 80 | 67 | 23600 | 60000 | 58200 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 180 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.2 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | Modulating | 60000 | 58200 | 97 | DC7TCA2410 | CHPTA2426B3 | DR97MC0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR97MC0603BN | 1140 | 0.5 | ECM | 80 | 67 | 34600 | 60000 | 58200 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 190 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 16.5 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | Modulating | 60000 | 58200 | 97 | DC7TCA3610 | CHPTA3630B3 | DR97MC0603BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA2418B3 / DR97MC0803BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 171 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 18 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC6VSS2410 | CAPEA2418B3 | DR97MC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR97MC0803BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 178 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 9.8 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC6VSS3010 | CAPEA3022B3 | DR97MC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022B3 / DR97MC0803BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 178 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC6VSS1810 | CAPEA3022B3 | DR97MC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626B3 / DR97MC0803BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 183 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC6VSS3610 | CAPEA3626B3 | DR97MC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR97MC0803BN | 840 | 0.5 | ECM | 80 | 67 | 24000 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 173 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.5 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC7TCA2410 | CAPTA2422B3 | DR97MC0803BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR97MC0803BN | 1120 | 0.5 | ECM | 80 | 67 | 35000 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 180 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 16.7 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC7TCA3610 | CAPTA3626B3 | DR97MC0803BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR97MC0803BN | 800 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 183 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 17.5 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 80000 | 77600 | 97 | DC6VSS2410 | CHPEA2422B3 | DR97MC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA2422B3 / DR97MC0803BN | 610 | 0.5 | ECM | 80 | 67 | 17100 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 183 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 80000 | 77600 | 97 | DC6VSS1810 | CHPEA2422B3 | DR97MC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026B3 / DR97MC0803BN | 1010 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 191 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 80000 | 77600 | 97 | DC6VSS3010 | CHPEA3026B3 | DR97MC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626B3 / DR97MC0803BN | 1260 | 0.5 | ECM | 80 | 67 | 33600 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 193 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 80000 | 77600 | 97 | DC6VSS3610 | CHPEA3626B3 | DR97MC0803BN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR97MC0803BN | 840 | 0.5 | ECM | 80 | 67 | 23600 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 185 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.2 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | Modulating | 80000 | 77600 | 97 | DC7TCA2410 | CHPTA2426B3 | DR97MC0803BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR97MC0803BN | 1120 | 0.5 | ECM | 80 | 67 | 34600 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 8.1 | 15 | 195 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 16.5 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | Modulating | 80000 | 77600 | 97 | DC7TCA3610 | CHPTA3630B3 | DR97MC0803BN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA2418C3 / DR97MC0804CN | 800 | 0.75 | ECM | 80 | 67 | 23200 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 189 | DAIKIN | DC6VSS2410 | 208/60/1 | 16.8 | 20 | 95 | R-32 | 18 / 10.2 | 136 | Inverter | 2 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC6VSS2410 | CAPEA2418C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022C3 / DR97MC0804CN | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 196 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC6VSS3010 | CAPEA3022C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022C3 / DR97MC0804CN | 610 | 0.75 | ECM | 80 | 67 | 17100 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 196 | DAIKIN | DC6VSS1810 | 208/60/1 | 12.8 | 15 | 95 | R-32 | 18.5 / 12 | 136 | Inverter | 1.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC6VSS1810 | CAPEA3022C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626C3 / DR97MC0804CN | 1260 | 0.75 | ECM | 80 | 67 | 33600 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 199 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC6VSS3610 | CAPEA3626C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR97MC0804CN | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 208 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16 / 8.6 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC6VSS4810 | CAPEA4830C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR97MC0804CN | 1320 | 0.75 | ECM | 80 | 67 | 41000 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 208 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC6VSS4210 | CAPEA4830C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA6030C3 / DR97MC0804CN | 1640 | 0.75 | ECM | 80 | 67 | 52000 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 210 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.5 / 8.4 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC6VSS6010 | CAPEA6030C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR97MC0804CN | 840 | 0.75 | ECM | 80 | 67 | 24000 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 190 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.5 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC7TCA2410 | CAPTA2422C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR97MC0804CN | 1150 | 0.75 | ECM | 80 | 67 | 35000 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 200 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17.2 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC7TCA3610 | CAPTA3626C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR97MC0804CN | 1380 | 0.75 | ECM | 80 | 67 | 46000 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 211 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.2 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | Modulating | 80000 | 77600 | 97 | DC7TCA4810 | CAPTA6030C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026C3 / DR97MC0804CN | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 207 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 80000 | 77600 | 97 | DC6VSS3010 | CHPEA3026C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626C3 / DR97MC0804CN | 1260 | 0.75 | ECM | 80 | 67 | 33600 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 211 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 80000 | 77600 | 97 | DC6VSS3610 | CHPEA3626C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR97MC0804CN | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 218 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16 / 8.6 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 80000 | 77600 | 97 | DC6VSS4810 | CHPEA4830C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR97MC0804CN | 1320 | 0.75 | ECM | 80 | 67 | 41000 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 218 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.5 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 80000 | 77600 | 97 | DC6VSS4210 | CHPEA4830C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA6030C3 / DR97MC0804CN | 1640 | 0.75 | ECM | 80 | 67 | 52000 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 218 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.2 / 8.2 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 80000 | 77600 | 97 | DC6VSS6010 | CHPEA6030C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR97MC0804CN | 840 | 0.75 | ECM | 80 | 67 | 23600 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 202 | DAIKIN | DC7TCA2410 | 208/60/1 | 15 | 20 | 95 | R-32 | 17.5 / 12.5 | 227 | 2 | 2 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | Modulating | 80000 | 77600 | 97 | DC7TCA2410 | CHPTA2426C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR97MC0804CN | 1150 | 0.75 | ECM | 80 | 67 | 34600 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 212 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | Modulating | 80000 | 77600 | 97 | DC7TCA3610 | CHPTA3630C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR97MC0804CN | 1380 | 0.75 | ECM | 80 | 67 | 45000 | 80000 | 77600 |  | Modulating | 97 | 115/60/1 | 11.4 | 15 | 216 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 16.7 / 12 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | Modulating | 80000 | 77600 | 97 | DC7TCA4810 | CHPTA4830C3 | DR97MC0804CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3022C3 / DR97MC1005CN | 1010 | 1 | ECM | 80 | 67 | 28400 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 203 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 100000 | 97000 | 97 | DC6VSS3010 | CAPEA3022C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626C3 / DR97MC1005CN | 1260 | 1 | ECM | 80 | 67 | 33600 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 206 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 100000 | 97000 | 97 | DC6VSS3610 | CAPEA3626C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR97MC1005CN | 1380 | 1 | ECM | 80 | 67 | 45500 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 215 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16 / 8.6 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 100000 | 97000 | 97 | DC6VSS4810 | CAPEA4830C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830C3 / DR97MC1005CN | 1320 | 1 | ECM | 80 | 67 | 41000 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 215 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 100000 | 97000 | 97 | DC6VSS4210 | CAPEA4830C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA6030C3 / DR97MC1005CN | 1640 | 1 | ECM | 80 | 67 | 52000 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 217 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.5 / 8.4 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 100000 | 97000 | 97 | DC6VSS6010 | CAPEA6030C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR97MC1005CN | 1120 | 1 | ECM | 80 | 67 | 35000 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 207 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17.2 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | Modulating | 100000 | 97000 | 97 | DC7TCA3610 | CAPTA3626C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR97MC1005CN | 1480 | 1 | ECM | 80 | 67 | 56500 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 218 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 16 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | Modulating | 100000 | 97000 | 97 | DC7TCA6010 | CAPTA6030C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR97MC1005CN | 1380 | 1 | ECM | 80 | 67 | 46000 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 218 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.2 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | Modulating | 100000 | 97000 | 97 | DC7TCA4810 | CAPTA6030C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3026C3 / DR97MC1005CN | 1010 | 1 | ECM | 80 | 67 | 28400 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 214 | DAIKIN | DC6VSS3010 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 17.5 / 10 | 136 | Inverter | 2.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 100000 | 97000 | 97 | DC6VSS3010 | CHPEA3026C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA3626C3 / DR97MC1005CN | 1260 | 1 | ECM | 80 | 67 | 33600 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 218 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 100000 | 97000 | 97 | DC6VSS3610 | CHPEA3626C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR97MC1005CN | 1380 | 1 | ECM | 80 | 67 | 45500 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 225 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16 / 8.6 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 100000 | 97000 | 97 | DC6VSS4810 | CHPEA4830C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830C3 / DR97MC1005CN | 1320 | 1 | ECM | 80 | 67 | 41000 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 225 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.5 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 100000 | 97000 | 97 | DC6VSS4210 | CHPEA4830C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA6030C3 / DR97MC1005CN | 1640 | 1 | ECM | 80 | 67 | 52000 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 225 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.2 / 8.2 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 100000 | 97000 | 97 | DC6VSS6010 | CHPEA6030C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR97MC1005CN | 1150 | 1 | ECM | 80 | 67 | 34600 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 219 | DAIKIN | DC7TCA3610 | 208/60/1 | 20.8 | 35 | 95 | R-32 | 17 / 12.5 | 229 | 2 | 3 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | Modulating | 100000 | 97000 | 97 | DC7TCA3610 | CHPTA3630C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR97MC1005CN | 1380 | 1 | ECM | 80 | 67 | 45000 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 223 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 16.7 / 12 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | Modulating | 100000 | 97000 | 97 | DC7TCA4810 | CHPTA4830C3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR97MC1005CN | 1480 | 1 | ECM | 80 | 67 | 56000 | 100000 | 97000 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 227 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | Modulating | 100000 | 97000 | 97 | DC7TCA6010 | CHPTA6030D3 | DR97MC1005CN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA3626D3 / DR97MC1205DN | 1260 | 1 | ECM | 80 | 67 | 33600 | 120000 | 116400 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 224 | DAIKIN | DC6VSS3610 | 208/60/1 | 22.4 | 25 | 95 | R-32 | 16.6 / 9 | 136 | Inverter | 3 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 120000 | 116400 | 97 | DC6VSS3610 | CAPEA3626D3 | DR97MC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830D3 / DR97MC1205DN | 1380 | 1 | ECM | 80 | 67 | 45500 | 120000 | 116400 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 231 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.2 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 120000 | 116400 | 97 | DC6VSS4810 | CAPEA4830D3 | DR97MC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA4830D3 / DR97MC1205DN | 1320 | 1 | ECM | 80 | 67 | 41000 | 120000 | 116400 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 231 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 17 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 120000 | 116400 | 97 | DC6VSS4210 | CAPEA4830D3 | DR97MC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPEA6030D3 / DR97MC1205DN | 1640 | 1 | ECM | 80 | 67 | 52500 | 120000 | 116400 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 235 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.5 / 8.5 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Upflow/Downflow | Modulating | 120000 | 116400 | 97 | DC6VSS6010 | CAPEA6030D3 | DR97MC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CAPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR97MC1205DN | 1480 | 1 | ECM | 80 | 67 | 56500 | 120000 | 116400 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 231 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 16 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | Modulating | 120000 | 116400 | 97 | DC7TCA6010 | CAPTA6030C3 | DR97MC1205DN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR97MC1205DN | 1380 | 1 | ECM | 80 | 67 | 46000 | 120000 | 116400 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 231 | DAIKIN | DC7TCA4810 | 208/60/1 | 31.6 | 50 | 95 | R-32 | 17.2 / 12.5 | 301 | 2 | 4 | 17.2 SEER2 (Two Stage) | 2 | Upflow/Downflow | Modulating | 120000 | 116400 | 97 | DC7TCA4810 | CAPTA6030C3 | DR97MC1205DN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830D3 / DR97MC1205DN | 1380 | 1 | ECM | 80 | 67 | 45500 | 120000 | 116400 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 241 | DAIKIN | DC6VSS4810 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.2 / 9 | 194 | Inverter | 4 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 120000 | 116400 | 97 | DC6VSS4810 | CHPEA4830D3 | DR97MC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA4830D3 / DR97MC1205DN | 1320 | 1 | ECM | 80 | 67 | 41000 | 120000 | 116400 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 241 | DAIKIN | DC6VSS4210 | 208/60/1 | 31.8 | 35 | 95 | R-32 | 16.5 / 9 | 194 | Inverter | 3.5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 120000 | 116400 | 97 | DC6VSS4210 | CHPEA4830D3 | DR97MC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPEA6030D3 / DR97MC1205DN | 1640 | 1 | ECM | 80 | 67 | 52500 | 120000 | 116400 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 238 | DAIKIN | DC6VSS6010 | 208/60/1 | 37.5 | 40 | 95 | R-32 | 15.2 / 8.4 | 194 | Inverter | 5 | 16.2 SEER2 (Inverter) | Inverter | Horizontal | Modulating | 120000 | 116400 | 97 | DC6VSS6010 | CHPEA6030D3 | DR97MC1205DN |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC6VS | IM - DR97MC | IM - CHPEA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR97MC1205DN | 1480 | 1 | ECM | 80 | 67 | 56000 | 120000 | 116400 |  | Modulating | 97 | 115/60/1 | 14.4 | 25 | 240 | DAIKIN | DC7TCA6010 | 208/60/1 | 36.4 | 60 | 95 | R-32 | 15.5 / 12 | 299 | 2 | 5 | 17.2 SEER2 (Two Stage) | 2 | Horizontal | Modulating | 120000 | 116400 | 97 | DC7TCA6010 | CHPTA6030D3 | DR97MC1205DN |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR97MC | IM - DC7TCA | IM - DR97MC | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA1818A3 / DR80SN0403AX | 610 | 0.5 | ECM | 80 | 67 | 17600 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 131 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 32000 | 80 | DC4SEA1810 | CAPTA1818A3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA1818B3 / DR80SN0403AX | 610 | 0.5 | ECM | 80 | 67 | 17600 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 135 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 32000 | 80 | DC4SEA1810 | CAPTA1818B3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA1822A3 / DR80SN0403AX | 600 | 0.5 | ECM | 80 | 67 | 17200 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 143 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 32000 | 80 | DC4SEA1810 | CHPTA1822A3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA1822B3 / DR80SN0403AX | 600 | 0.5 | ECM | 80 | 67 | 17200 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 147 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 32000 | 80 | DC4SEA1810 | CHPTA1822B3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80SN0403AX | 630 | 0.5 | ECM | 80 | 67 | 17800 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 138 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 32000 | 80 | DC4SEA1810 | CAPTA2422A3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80SN0403AX | 630 | 0.5 | ECM | 80 | 67 | 17800 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 142 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 32000 | 80 | DC4SEA1810 | CAPTA2422B3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80SN0403AX | 630 | 0.5 | ECM | 80 | 67 | 17800 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 145 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 32000 | 80 | DC4SEA1810 | CAPTA2422C3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80SN0403AX | 640 | 0.5 | ECM | 80 | 67 | 17400 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 154 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 40000 | 32000 | 80 | DC4SEA1810 | CHPTA2426B3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR80SN0403AX | 640 | 0.5 | ECM | 80 | 67 | 17400 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 157 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 40000 | 32000 | 80 | DC4SEA1810 | CHPTA2426C3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026B3 / DR80SN0403AX | 930 | 0.5 | ECM | 80 | 67 | 28200 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 147 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 32000 | 80 | DC4SEA3010 | CAPTA3026B3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026C3 / DR80SN0403AX | 930 | 0.5 | ECM | 80 | 67 | 28200 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 152 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 32000 | 80 | DC4SEA3010 | CAPTA3026C3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80SN0403AX | 950 | 0.5 | ECM | 80 | 67 | 28400 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 149 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 32000 | 80 | DC4SEA3010 | CAPTA3626B3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80SN0403AX | 950 | 0.5 | ECM | 80 | 67 | 28400 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 155 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 40000 | 32000 | 80 | DC4SEA3010 | CAPTA3626C3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80SN0403AX | 940 | 0.5 | ECM | 80 | 67 | 28600 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 164 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 40000 | 32000 | 80 | DC4SEA3010 | CHPTA3630B3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80SN0403AX | 940 | 0.5 | ECM | 80 | 67 | 28600 | 40000 | 32000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 167 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 40000 | 32000 | 80 | DC4SEA3010 | CHPTA3630C3 | DR80SN0403AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA1818A3 / DR80SN0603AX | 590 | 0.5 | ECM | 80 | 67 | 17400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 136 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA1810 | CAPTA1818A3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA1818B3 / DR80SN0603AX | 590 | 0.5 | ECM | 80 | 67 | 17400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 140 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA1810 | CAPTA1818B3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA1822A3 / DR80SN0603AX | 580 | 0.5 | ECM | 80 | 67 | 17200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 148 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA1810 | CHPTA1822A3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA1822B3 / DR80SN0603AX | 580 | 0.5 | ECM | 80 | 67 | 17200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 152 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA1810 | CHPTA1822B3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80SN0603AX | 820 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 143 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA2422A3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80SN0603AX | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 143 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA1810 | CAPTA2422A3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80SN0603AX | 820 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 147 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA2422B3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80SN0603AX | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 147 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA1810 | CAPTA2422B3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80SN0603AX | 820 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 150 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA2422C3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80SN0603AX | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 150 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA1810 | CAPTA2422C3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80SN0603AX | 810 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 159 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA2426B3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80SN0603AX | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 159 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA1810 | CHPTA2426B3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR80SN0603AX | 810 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 162 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA2426C3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR80SN0603AX | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 162 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA1810 | CHPTA2426C3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022A3 / DR80SN0603AX | 820 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 141 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA3022A3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022B3 / DR80SN0603AX | 820 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 146 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA3022B3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022C3 / DR80SN0603AX | 820 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 150 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA3022C3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026B3 / DR80SN0603AX | 830 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 162 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA3026B3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026C3 / DR80SN0603AX | 830 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 164 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 14.5 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA3026C3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80SN0603AX | 1020 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 154 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA3010 | CAPTA3626B3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80SN0603AX | 1020 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 160 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA3010 | CAPTA3626C3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80SN0603AX | 1010 | 0.5 | ECM | 80 | 67 | 28600 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 169 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA3010 | CHPTA3630B3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80SN0603AX | 1010 | 0.5 | ECM | 80 | 67 | 28600 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 8.7 | 15 | 172 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA3010 | CHPTA3630C3 | DR80SN0603AX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80SN0604BX | 840 | 0.75 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 152 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA2422A3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80SN0604BX | 840 | 0.75 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 156 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA2422B3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80SN0604BX | 840 | 0.75 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 159 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA2422C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80SN0604BX | 830 | 0.75 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 168 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA2426B3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR80SN0604BX | 830 | 0.75 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 171 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA2426C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022A3 / DR80SN0604BX | 840 | 0.75 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 150 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA3022A3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022B3 / DR80SN0604BX | 840 | 0.75 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 155 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA3022B3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022C3 / DR80SN0604BX | 840 | 0.75 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 159 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA3022C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026B3 / DR80SN0604BX | 960 | 0.75 | ECM | 80 | 67 | 28200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 161 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA3010 | CAPTA3026B3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026C3 / DR80SN0604BX | 960 | 0.75 | ECM | 80 | 67 | 28200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 166 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA3010 | CAPTA3026C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026B3 / DR80SN0604BX | 960 | 0.75 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 171 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA3010 | CHPTA3026B3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026B3 / DR80SN0604BX | 850 | 0.75 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 171 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA3026B3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026C3 / DR80SN0604BX | 960 | 0.75 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 173 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA3010 | CHPTA3026C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026C3 / DR80SN0604BX | 850 | 0.75 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 173 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA3026C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80SN0604BX | 970 | 0.75 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 163 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA3010 | CAPTA3626B3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80SN0604BX | 1040 | 0.75 | ECM | 80 | 67 | 34200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 163 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA3610 | CAPTA3626B3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80SN0604BX | 970 | 0.75 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 169 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA3010 | CAPTA3626C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80SN0604BX | 1040 | 0.75 | ECM | 80 | 67 | 34200 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 169 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA3610 | CAPTA3626C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80SN0604BX | 970 | 0.75 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 178 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA3010 | CHPTA3630B3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80SN0604BX | 1030 | 0.75 | ECM | 80 | 67 | 34400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 178 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA3610 | CHPTA3630B3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80SN0604BX | 970 | 0.75 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 181 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA3010 | CHPTA3630C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80SN0604BX | 1030 | 0.75 | ECM | 80 | 67 | 34400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 181 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA3610 | CHPTA3630C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80SN0604BX | 1060 | 0.75 | ECM | 80 | 67 | 34800 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 173 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA3610 | CAPTA4230C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN0604BX | 1060 | 0.75 | ECM | 80 | 67 | 34800 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 179 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN0604BX | 1030 | 0.75 | ECM | 80 | 67 | 34400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 181 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN0604BX | 1060 | 0.75 | ECM | 80 | 67 | 34800 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 179 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 60000 | 48000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN0604BX | 1030 | 0.75 | ECM | 80 | 67 | 34400 | 60000 | 48000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 181 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 60000 | 48000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80SN0604BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA1818A3 / DR80SN0803BX | 630 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 148 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.7 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA1810 | CAPTA1818A3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA1818B3 / DR80SN0803BX | 630 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 152 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.7 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA1810 | CAPTA1818B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA1822A3 / DR80SN0803BX | 630 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 160 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA1810 | CHPTA1822A3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA1822B3 / DR80SN0803BX | 630 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 164 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA1810 | CHPTA1822B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80SN0803BX | 730 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 155 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA2422A3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80SN0803BX | 650 | 0.5 | ECM | 80 | 67 | 17800 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 155 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA1810 | CAPTA2422A3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80SN0803BX | 730 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 159 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA2422B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80SN0803BX | 650 | 0.5 | ECM | 80 | 67 | 17800 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 159 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA1810 | CAPTA2422B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80SN0803BX | 730 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 162 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA2422C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80SN0803BX | 650 | 0.5 | ECM | 80 | 67 | 17800 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 162 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA1810 | CAPTA2422C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80SN0803BX | 720 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 171 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA2426B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR80SN0803BX | 720 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 174 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA2426C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022A3 / DR80SN0803BX | 730 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 153 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA3022A3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022B3 / DR80SN0803BX | 730 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 158 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA3022B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022C3 / DR80SN0803BX | 730 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 162 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA3022C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026B3 / DR80SN0803BX | 920 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 164 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3026B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026C3 / DR80SN0803BX | 920 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 169 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3026C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026B3 / DR80SN0803BX | 910 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 174 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3026B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026B3 / DR80SN0803BX | 730 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 174 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA3026B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026C3 / DR80SN0803BX | 910 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 176 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3026C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026C3 / DR80SN0803BX | 730 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 176 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA3026C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80SN0803BX | 940 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 166 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3626B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80SN0803BX | 1100 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 166 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA3626B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80SN0803BX | 940 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 172 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3626C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80SN0803BX | 1100 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 172 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA3626C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80SN0803BX | 930 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 181 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3630B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80SN0803BX | 1100 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 181 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA3630B3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80SN0803BX | 930 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 184 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3630C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80SN0803BX | 1100 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 184 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA3630C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80SN0803BX | 1050 | 0.5 | ECM | 80 | 67 | 34800 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 176 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN0803BX | 1050 | 0.5 | ECM | 80 | 67 | 34800 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 182 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN0803BX | 1100 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 184 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN0803BX | 1050 | 0.5 | ECM | 80 | 67 | 34800 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 182 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN0803BX | 1100 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 7.7 | 15 | 184 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80SN0803BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80SN0804BX | 820 | 0.75 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 157 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA2422A3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80SN0804BX | 820 | 0.75 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 161 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA2422B3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80SN0804BX | 820 | 0.75 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 164 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA2422C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80SN0804BX | 810 | 0.75 | ECM | 80 | 67 | 23200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 173 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA2426B3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR80SN0804BX | 810 | 0.75 | ECM | 80 | 67 | 23200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 176 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA2426C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022A3 / DR80SN0804BX | 820 | 0.75 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 155 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA3022A3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022B3 / DR80SN0804BX | 820 | 0.75 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 160 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA3022B3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022C3 / DR80SN0804BX | 820 | 0.75 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 164 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA3022C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026B3 / DR80SN0804BX | 1000 | 0.75 | ECM | 80 | 67 | 28200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 166 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3026B3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026C3 / DR80SN0804BX | 1000 | 0.75 | ECM | 80 | 67 | 28200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 171 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3026C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026B3 / DR80SN0804BX | 990 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 176 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3026B3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026B3 / DR80SN0804BX | 820 | 0.75 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 176 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA3026B3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026C3 / DR80SN0804BX | 990 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 178 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3026C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026C3 / DR80SN0804BX | 820 | 0.75 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 178 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA3026C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80SN0804BX | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 168 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3626B3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80SN0804BX | 1090 | 0.75 | ECM | 80 | 67 | 34200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 168 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA3626B3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80SN0804BX | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 174 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3626C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80SN0804BX | 1090 | 0.75 | ECM | 80 | 67 | 34200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 174 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA3626C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80SN0804BX | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 183 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3630B3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80SN0804BX | 1090 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 183 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA3630B3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80SN0804BX | 1010 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 186 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3630C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80SN0804BX | 1090 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 186 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA3630C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80SN0804BX | 1120 | 0.75 | ECM | 80 | 67 | 34800 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 178 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN0804BX | 1120 | 0.75 | ECM | 80 | 67 | 34800 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 184 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN0804BX | 1090 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 186 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN0804BX | 1120 | 0.75 | ECM | 80 | 67 | 34800 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 184 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN0804BX | 1090 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 186 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80SN0804BX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026B3 / DR80SN0805CX | 970 | 0.75 | ECM | 80 | 67 | 28200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 173 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3026B3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026C3 / DR80SN0805CX | 970 | 0.75 | ECM | 80 | 67 | 28200 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 178 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3026C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026B3 / DR80SN0805CX | 960 | 0.75 | ECM | 80 | 67 | 28600 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 183 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3026B3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026C3 / DR80SN0805CX | 960 | 0.75 | ECM | 80 | 67 | 28600 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 185 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3026C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80SN0805CX | 980 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 175 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3626B3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80SN0805CX | 1050 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 175 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA3626B3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80SN0805CX | 980 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 181 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3626C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80SN0805CX | 1050 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 181 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA3626C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80SN0805CX | 970 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 190 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3630B3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80SN0805CX | 1030 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 190 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA3630B3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80SN0805CX | 970 | 0.75 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 193 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3630C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80SN0805CX | 1030 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 193 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA3630C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80SN0805CX | 1260 | 0.75 | ECM | 80 | 67 | 39500 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 185 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA4210 | CAPTA4230C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80SN0805CX | 1070 | 0.75 | ECM | 80 | 67 | 35000 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 185 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12.5 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN0805CX | 1260 | 0.75 | ECM | 80 | 67 | 39500 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 191 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA4210 | CAPTA4230D3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN0805CX | 1070 | 0.75 | ECM | 80 | 67 | 35000 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 191 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12.5 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN0805CX | 1350 | 0.75 | ECM | 80 | 67 | 39000 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 193 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA4210 | CHPTA4230C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN0805CX | 1030 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 193 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN0805CX | 1260 | 0.75 | ECM | 80 | 67 | 39500 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 191 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA4210 | CAPTA4230D3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN0805CX | 1070 | 0.75 | ECM | 80 | 67 | 35000 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 191 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12.5 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN0805CX | 1350 | 0.75 | ECM | 80 | 67 | 39000 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 193 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA4210 | CHPTA4230C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN0805CX | 1030 | 0.75 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 193 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR80SN0805CX | 1330 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 197 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA4810 | CHPTA4830C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR80SN0805CX | 1230 | 0.75 | ECM | 80 | 67 | 39000 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 197 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA4210 | CHPTA4830C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80SN0805CX | 1500 | 0.75 | ECM | 80 | 67 | 56000 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 192 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA6010 | CAPTA6030C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80SN0805CX | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 192 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6030C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80SN0805CX | 1260 | 0.75 | ECM | 80 | 67 | 40000 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 192 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA4210 | CAPTA6030C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80SN0805CX | 1500 | 0.75 | ECM | 80 | 67 | 56000 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 196 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA6010 | CAPTA6030D3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80SN0805CX | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 196 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6030D3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80SN0805CX | 1260 | 0.75 | ECM | 80 | 67 | 40000 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 196 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA4210 | CAPTA6030D3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80SN0805CX | 1520 | 0.75 | ECM | 80 | 67 | 57000 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 196 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 15 / 12 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA6010 | CAPTA6034C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80SN0805CX | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 196 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6034C3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80SN0805CX | 1520 | 0.75 | ECM | 80 | 67 | 57000 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 199 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 15 / 12 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA6010 | CAPTA6034D3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80SN0805CX | 1380 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 199 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6034D3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80SN0805CX | 1500 | 0.75 | ECM | 80 | 67 | 55500 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 201 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 13.8 / 11.2 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA6010 | CHPTA6030D3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80SN0805CX | 1370 | 0.75 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 201 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 80000 | 64000 | 80 | DC4SEA4810 | CHPTA6030D3 | DR80SN0805CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80SN1005CX | 1060 | 0.75 | ECM | 80 | 67 | 34400 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 181 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA3610 | CAPTA3626B3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80SN1005CX | 1060 | 0.75 | ECM | 80 | 67 | 34400 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 187 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA3610 | CAPTA3626C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80SN1005CX | 1040 | 0.75 | ECM | 80 | 67 | 34400 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 196 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 80000 | 80 | DC4SEA3610 | CHPTA3630B3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80SN1005CX | 1040 | 0.75 | ECM | 80 | 67 | 34400 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 199 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 80000 | 80 | DC4SEA3610 | CHPTA3630C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80SN1005CX | 1290 | 0.75 | ECM | 80 | 67 | 39500 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 191 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA4210 | CAPTA4230C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80SN1005CX | 1080 | 0.75 | ECM | 80 | 67 | 35000 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 191 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12.5 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA3610 | CAPTA4230C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN1005CX | 1290 | 0.75 | ECM | 80 | 67 | 39500 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 197 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA4210 | CAPTA4230D3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN1005CX | 1080 | 0.75 | ECM | 80 | 67 | 35000 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 197 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12.5 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN1005CX | 1260 | 0.75 | ECM | 80 | 67 | 39000 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 199 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 80000 | 80 | DC4SEA4210 | CHPTA4230C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN1005CX | 1040 | 0.75 | ECM | 80 | 67 | 34400 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 199 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 80000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN1005CX | 1290 | 0.75 | ECM | 80 | 67 | 39500 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 197 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA4210 | CAPTA4230D3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80SN1005CX | 1080 | 0.75 | ECM | 80 | 67 | 35000 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 197 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12.5 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN1005CX | 1260 | 0.75 | ECM | 80 | 67 | 39000 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 199 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 80000 | 80 | DC4SEA4210 | CHPTA4230C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80SN1005CX | 1040 | 0.75 | ECM | 80 | 67 | 34400 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 199 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 80000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR80SN1005CX | 1320 | 0.75 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 203 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 80000 | 80 | DC4SEA4810 | CHPTA4830C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR80SN1005CX | 1260 | 0.75 | ECM | 80 | 67 | 39000 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 203 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 80000 | 80 | DC4SEA4210 | CHPTA4830C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80SN1005CX | 1520 | 0.75 | ECM | 80 | 67 | 56000 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 198 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA6010 | CAPTA6030C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80SN1005CX | 1340 | 0.75 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 198 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA4810 | CAPTA6030C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80SN1005CX | 1290 | 0.75 | ECM | 80 | 67 | 40000 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 198 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA4210 | CAPTA6030C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80SN1005CX | 1520 | 0.75 | ECM | 80 | 67 | 56000 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 202 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA6010 | CAPTA6030D3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80SN1005CX | 1340 | 0.75 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 202 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA4810 | CAPTA6030D3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80SN1005CX | 1290 | 0.75 | ECM | 80 | 67 | 40000 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 202 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA4210 | CAPTA6030D3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80SN1005CX | 1530 | 0.75 | ECM | 80 | 67 | 57000 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 202 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 15 / 12 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA6010 | CAPTA6034C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80SN1005CX | 1350 | 0.75 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 202 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA4810 | CAPTA6034C3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80SN1005CX | 1530 | 0.75 | ECM | 80 | 67 | 57000 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 205 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 15 / 12 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA6010 | CAPTA6034D3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80SN1005CX | 1350 | 0.75 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 205 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 100000 | 80000 | 80 | DC4SEA4810 | CAPTA6034D3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80SN1005CX | 1520 | 0.75 | ECM | 80 | 67 | 55500 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 207 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 13.8 / 11.2 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 80000 | 80 | DC4SEA6010 | CHPTA6030D3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80SN1005CX | 1340 | 0.75 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 1 | 80 | 115/60/1 | 12.5 | 15 | 207 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 100000 | 80000 | 80 | DC4SEA4810 | CHPTA6030D3 | DR80SN1005CX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80SN1205DX | 1480 | 1 | ECM | 80 | 67 | 56500 | 120000 | 96000 |  | 1 | 80 | 115/60/1 | 15.3 | 20 | 211 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 96000 | 80 | DC4SEA6010 | CAPTA6030C3 | DR80SN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80SN1205DX | 1330 | 1 | ECM | 80 | 67 | 45500 | 120000 | 96000 |  | 1 | 80 | 115/60/1 | 15.3 | 20 | 211 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 96000 | 80 | DC4SEA4810 | CAPTA6030C3 | DR80SN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80SN1205DX | 1480 | 1 | ECM | 80 | 67 | 56500 | 120000 | 96000 |  | 1 | 80 | 115/60/1 | 15.3 | 20 | 215 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 96000 | 80 | DC4SEA6010 | CAPTA6030D3 | DR80SN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80SN1205DX | 1330 | 1 | ECM | 80 | 67 | 45500 | 120000 | 96000 |  | 1 | 80 | 115/60/1 | 15.3 | 20 | 215 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 96000 | 80 | DC4SEA4810 | CAPTA6030D3 | DR80SN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80SN1205DX | 1500 | 1 | ECM | 80 | 67 | 57000 | 120000 | 96000 |  | 1 | 80 | 115/60/1 | 15.3 | 20 | 215 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 15 / 12 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 96000 | 80 | DC4SEA6010 | CAPTA6034C3 | DR80SN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80SN1205DX | 1340 | 1 | ECM | 80 | 67 | 45500 | 120000 | 96000 |  | 1 | 80 | 115/60/1 | 15.3 | 20 | 215 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 96000 | 80 | DC4SEA4810 | CAPTA6034C3 | DR80SN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80SN1205DX | 1500 | 1 | ECM | 80 | 67 | 57000 | 120000 | 96000 |  | 1 | 80 | 115/60/1 | 15.3 | 20 | 218 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 15 / 12 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 96000 | 80 | DC4SEA6010 | CAPTA6034D3 | DR80SN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80SN1205DX | 1340 | 1 | ECM | 80 | 67 | 45500 | 120000 | 96000 |  | 1 | 80 | 115/60/1 | 15.3 | 20 | 218 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 1 | 120000 | 96000 | 80 | DC4SEA4810 | CAPTA6034D3 | DR80SN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80SN1205DX | 1480 | 1 | ECM | 80 | 67 | 56000 | 120000 | 96000 |  | 1 | 80 | 115/60/1 | 15.3 | 20 | 220 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.2 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 120000 | 96000 | 80 | DC4SEA6010 | CHPTA6030D3 | DR80SN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80SN1205DX | 1320 | 1 | ECM | 80 | 67 | 45500 | 120000 | 96000 |  | 1 | 80 | 115/60/1 | 15.3 | 20 | 220 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 1 | 120000 | 96000 | 80 | DC4SEA4810 | CHPTA6030D3 | DR80SN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80SN | IM - DC4SEA | IM - DR80SN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA1818A3 / DR80TN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17600 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 131 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC4SEA1810 | CAPTA1818A3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA1818B3 / DR80TN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17600 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 135 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC4SEA1810 | CAPTA1818B3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA1822A3 / DR80TN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17200 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 143 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC4SEA1810 | CHPTA1822A3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA1822B3 / DR80TN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17200 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 147 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC4SEA1810 | CHPTA1822B3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80TN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17800 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 138 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC4SEA1810 | CAPTA2422A3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80TN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17800 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 142 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC4SEA1810 | CAPTA2422B3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80TN0403AN | 630 | 0.5 | ECM | 80 | 67 | 17800 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 145 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC4SEA1810 | CAPTA2422C3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80TN0403AN | 640 | 0.5 | ECM | 80 | 67 | 17400 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 154 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 40000 | 32000 | 80 | DC4SEA1810 | CHPTA2426B3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR80TN0403AN | 640 | 0.5 | ECM | 80 | 67 | 17400 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 157 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 40000 | 32000 | 80 | DC4SEA1810 | CHPTA2426C3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026B3 / DR80TN0403AN | 930 | 0.5 | ECM | 80 | 67 | 28200 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 147 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC4SEA3010 | CAPTA3026B3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026C3 / DR80TN0403AN | 930 | 0.5 | ECM | 80 | 67 | 28200 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 152 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC4SEA3010 | CAPTA3026C3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80TN0403AN | 950 | 0.5 | ECM | 80 | 67 | 28400 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 149 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC4SEA3010 | CAPTA3626B3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80TN0403AN | 950 | 0.5 | ECM | 80 | 67 | 28400 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 155 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 40000 | 32000 | 80 | DC4SEA3010 | CAPTA3626C3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80TN0403AN | 930 | 0.5 | ECM | 80 | 67 | 28600 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 164 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 40000 | 32000 | 80 | DC4SEA3010 | CHPTA3630B3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80TN0403AN | 930 | 0.5 | ECM | 80 | 67 | 28600 | 40000 | 32000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 167 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 14.5 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 40000 | 32000 | 80 | DC4SEA3010 | CHPTA3630C3 | DR80TN0403AN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA1818A3 / DR80TN0603BN | 600 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 145 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA1810 | CAPTA1818A3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA1818B3 / DR80TN0603BN | 600 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 149 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA1810 | CAPTA1818B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA1822A3 / DR80TN0603BN | 590 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 157 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA1810 | CHPTA1822A3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA1822B3 / DR80TN0603BN | 590 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 161 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA1810 | CHPTA1822B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80TN0603BN | 850 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 152 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA2422A3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80TN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17800 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 152 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA1810 | CAPTA2422A3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80TN0603BN | 850 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 156 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA2422B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80TN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17800 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 156 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA1810 | CAPTA2422B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80TN0603BN | 850 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 159 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA2422C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80TN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17800 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 159 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA1810 | CAPTA2422C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80TN0603BN | 840 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 168 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA2426B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80TN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 168 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA1810 | CHPTA2426B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR80TN0603BN | 840 | 0.5 | ECM | 80 | 67 | 23200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 171 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA2426C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR80TN0603BN | 610 | 0.5 | ECM | 80 | 67 | 17600 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 171 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA1810 | CHPTA2426C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022A3 / DR80TN0603BN | 850 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 150 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA3022A3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022B3 / DR80TN0603BN | 850 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 155 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA3022B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022C3 / DR80TN0603BN | 850 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 159 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA2410 | CAPTA3022C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026B3 / DR80TN0603BN | 950 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 161 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA3010 | CAPTA3026B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026C3 / DR80TN0603BN | 950 | 0.5 | ECM | 80 | 67 | 28200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 166 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA3010 | CAPTA3026C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026B3 / DR80TN0603BN | 940 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 171 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA3010 | CHPTA3026B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026B3 / DR80TN0603BN | 860 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 171 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA3026B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026C3 / DR80TN0603BN | 940 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 173 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA3010 | CHPTA3026C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026C3 / DR80TN0603BN | 860 | 0.5 | ECM | 80 | 67 | 23400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 173 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA2410 | CHPTA3026C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80TN0603BN | 960 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 163 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA3010 | CAPTA3626B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80TN0603BN | 1060 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 163 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA3610 | CAPTA3626B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80TN0603BN | 960 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 169 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA3010 | CAPTA3626C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80TN0603BN | 1060 | 0.5 | ECM | 80 | 67 | 34200 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 169 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA3610 | CAPTA3626C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80TN0603BN | 950 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 178 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA3010 | CHPTA3630B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80TN0603BN | 1050 | 0.5 | ECM | 80 | 67 | 34400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 178 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA3610 | CHPTA3630B3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80TN0603BN | 950 | 0.5 | ECM | 80 | 67 | 28400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 181 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA3010 | CHPTA3630C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80TN0603BN | 1050 | 0.5 | ECM | 80 | 67 | 34400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 181 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA3610 | CHPTA3630C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80TN0603BN | 1080 | 0.5 | ECM | 80 | 67 | 34800 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 173 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA3610 | CAPTA4230C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN0603BN | 1080 | 0.5 | ECM | 80 | 67 | 34800 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 179 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80TN0603BN | 1050 | 0.5 | ECM | 80 | 67 | 34400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 181 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN0603BN | 1080 | 0.5 | ECM | 80 | 67 | 34800 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 179 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 60000 | 48000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80TN0603BN | 1050 | 0.5 | ECM | 80 | 67 | 34400 | 60000 | 48000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 181 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 60000 | 48000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80TN0603BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA1818A3 / DR80TN0803BN | 630 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 150 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.7 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA1810 | CAPTA1818A3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA1818B3 / DR80TN0803BN | 630 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 154 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.7 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA1810 | CAPTA1818B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA1822A3 / DR80TN0803BN | 630 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 162 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA1810 | CHPTA1822A3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA1822B3 / DR80TN0803BN | 630 | 0.5 | ECM | 80 | 67 | 17600 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 166 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 14.5 / 12 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA1810 | CHPTA1822B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80TN0803BN | 720 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 157 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA2422A3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422A3 / DR80TN0803BN | 650 | 0.5 | ECM | 80 | 67 | 17800 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 157 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA1810 | CAPTA2422A3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80TN0803BN | 720 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 161 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA2422B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422B3 / DR80TN0803BN | 650 | 0.5 | ECM | 80 | 67 | 17800 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 161 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA1810 | CAPTA2422B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80TN0803BN | 720 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 164 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA2422C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA2422C3 / DR80TN0803BN | 650 | 0.5 | ECM | 80 | 67 | 17800 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 164 | DAIKIN | DC4SEA1810 | 208/60/1 | 11.1 | 15 | 95 | R-32 | 15.2 / 12.5 | 141 | 1 | 1.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA1810 | CAPTA2422C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426B3 / DR80TN0803BN | 720 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 173 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA2426B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA2426C3 / DR80TN0803BN | 720 | 0.5 | ECM | 80 | 67 | 23200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 176 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA2426C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022A3 / DR80TN0803BN | 720 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 155 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA3022A3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022B3 / DR80TN0803BN | 720 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 160 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA3022B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3022C3 / DR80TN0803BN | 720 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 164 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA2410 | CAPTA3022C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026B3 / DR80TN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 166 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3026B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3026C3 / DR80TN0803BN | 920 | 0.5 | ECM | 80 | 67 | 28200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 171 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3026C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026B3 / DR80TN0803BN | 910 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 176 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3026B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026B3 / DR80TN0803BN | 730 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 176 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA3026B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026C3 / DR80TN0803BN | 910 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 178 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3026C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3026C3 / DR80TN0803BN | 730 | 0.5 | ECM | 80 | 67 | 23400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 178 | DAIKIN | DC4SEA2410 | 208/60/1 | 13.5 | 20 | 95 | R-32 | 15.2 / 12.5 | 149 | 1 | 2 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA2410 | CHPTA3026C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80TN0803BN | 940 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 168 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3626B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80TN0803BN | 1100 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 168 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA3626B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80TN0803BN | 940 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 174 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3010 | CAPTA3626C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80TN0803BN | 1100 | 0.5 | ECM | 80 | 67 | 34200 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 174 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA3626C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80TN0803BN | 930 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 183 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3630B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80TN0803BN | 1090 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 183 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA3630B3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80TN0803BN | 930 | 0.5 | ECM | 80 | 67 | 28400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 186 | DAIKIN | DC4SEA3010 | 208/60/1 | 15.35 | 25 | 95 | R-32 | 15.2 / 12.5 | 174 | 1 | 2.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3010 | CHPTA3630C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80TN0803BN | 1090 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 186 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA3630C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80TN0803BN | 1120 | 0.5 | ECM | 80 | 67 | 34800 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 178 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN0803BN | 1120 | 0.5 | ECM | 80 | 67 | 34800 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 184 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80TN0803BN | 1090 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 186 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN0803BN | 1120 | 0.5 | ECM | 80 | 67 | 34800 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 184 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80TN0803BN | 1090 | 0.5 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 8.7 | 15 | 186 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80TN0803BN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626B3 / DR80TN0805CN | 1050 | 1 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 181 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA3626B3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA3626C3 / DR80TN0805CN | 1050 | 1 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 187 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA3626C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630B3 / DR80TN0805CN | 1040 | 1 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 196 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA3630B3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA3630C3 / DR80TN0805CN | 1040 | 1 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 199 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA3630C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80TN0805CN | 1260 | 1 | ECM | 80 | 67 | 39500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 191 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4210 | CAPTA4230C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80TN0805CN | 1070 | 1 | ECM | 80 | 67 | 35000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 191 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12.5 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN0805CN | 1260 | 1 | ECM | 80 | 67 | 39500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 197 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4210 | CAPTA4230D3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN0805CN | 1070 | 1 | ECM | 80 | 67 | 35000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 197 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12.5 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80TN0805CN | 1240 | 1 | ECM | 80 | 67 | 39000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 199 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA4210 | CHPTA4230C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80TN0805CN | 1040 | 1 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 199 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN0805CN | 1260 | 1 | ECM | 80 | 67 | 39500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 197 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4210 | CAPTA4230D3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN0805CN | 1070 | 1 | ECM | 80 | 67 | 35000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 197 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12.5 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80TN0805CN | 1240 | 1 | ECM | 80 | 67 | 39000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 199 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA4210 | CHPTA4230C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80TN0805CN | 1040 | 1 | ECM | 80 | 67 | 34400 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 199 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CHPTA4230C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR80TN0805CN | 1330 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 203 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CHPTA4830C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR80TN0805CN | 1240 | 1 | ECM | 80 | 67 | 39000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 203 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA4210 | CHPTA4830C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TN0805CN | 1370 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 198 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6030C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TN0805CN | 1260 | 1 | ECM | 80 | 67 | 40000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 198 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4210 | CAPTA6030C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80TN0805CN | 1370 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 202 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6030D3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80TN0805CN | 1260 | 1 | ECM | 80 | 67 | 40000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 202 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4210 | CAPTA6030D3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80TN0805CN | 1380 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 202 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6034C3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80TN0805CN | 1380 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 205 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6034D3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80TN0805CN | 1370 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 207 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.3 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CHPTA6030D3 | DR80TN0805CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80TN0805DX | 1050 | 1 | ECM | 80 | 67 | 35000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 196 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12.5 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230C3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN0805DX | 1050 | 1 | ECM | 80 | 67 | 35000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 202 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12.5 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN0805DX | 1050 | 1 | ECM | 80 | 67 | 35000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 202 | DAIKIN | DC4SEA3610 | 208/60/1 | 17.75 | 30 | 95 | R-32 | 15.2 / 12.5 | 178 | 1 | 3 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA3610 | CAPTA4230D3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TN0805DX | 1500 | 1 | ECM | 80 | 67 | 57000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 203 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14.5 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA6010 | CAPTA6030C3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TN0805DX | 1450 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 203 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6030C3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80TN0805DX | 1500 | 1 | ECM | 80 | 67 | 57000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 207 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14.5 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA6010 | CAPTA6030D3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80TN0805DX | 1450 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 207 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6030D3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80TN0805DX | 1520 | 1 | ECM | 80 | 67 | 57000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 207 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 15.2 / 12 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA6010 | CAPTA6034C3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80TN0805DX | 1480 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 207 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15.2 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6034C3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80TN0805DX | 1520 | 1 | ECM | 80 | 67 | 57000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 210 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 15.2 / 12 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA6010 | CAPTA6034D3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80TN0805DX | 1480 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 210 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15.2 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CAPTA6034D3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80TN0805DX | 1500 | 1 | ECM | 80 | 67 | 56000 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 212 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.2 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA6010 | CHPTA6030D3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80TN0805DX | 1450 | 1 | ECM | 80 | 67 | 45500 | 80000 | 64000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 212 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.3 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 80000 | 64000 | 80 | DC4SEA4810 | CHPTA6030D3 | DR80TN0805DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80TN1005CN | 1250 | 1 | ECM | 80 | 67 | 39500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 194 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA4210 | CAPTA4230C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN1005CN | 1250 | 1 | ECM | 80 | 67 | 39500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 200 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA4210 | CAPTA4230D3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80TN1005CN | 1220 | 1 | ECM | 80 | 67 | 39000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 202 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 80000 | 80 | DC4SEA4210 | CHPTA4230C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN1005CN | 1250 | 1 | ECM | 80 | 67 | 39500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 200 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA4210 | CAPTA4230D3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4230C3 / DR80TN1005CN | 1220 | 1 | ECM | 80 | 67 | 39000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 202 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 14.5 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 80000 | 80 | DC4SEA4210 | CHPTA4230C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR80TN1005CN | 1330 | 1 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 206 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 80000 | 80 | DC4SEA4810 | CHPTA4830C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA4830C3 / DR80TN1005CN | 1220 | 1 | ECM | 80 | 67 | 39000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 206 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 80000 | 80 | DC4SEA4210 | CHPTA4830C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TN1005CN | 1550 | 1 | ECM | 80 | 67 | 56000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 201 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA6010 | CAPTA6030C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TN1005CN | 1380 | 1 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 201 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA4810 | CAPTA6030C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80TN1005CN | 1550 | 1 | ECM | 80 | 67 | 56000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 205 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA6010 | CAPTA6030D3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80TN1005CN | 1380 | 1 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 205 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA4810 | CAPTA6030D3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80TN1005CN | 1550 | 1 | ECM | 80 | 67 | 57000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 205 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14.5 / 12 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA6010 | CAPTA6034C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80TN1005CN | 1390 | 1 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 205 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA4810 | CAPTA6034C3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80TN1005CN | 1550 | 1 | ECM | 80 | 67 | 57000 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 208 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14.5 / 12 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA6010 | CAPTA6034D3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80TN1005CN | 1390 | 1 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 208 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 100000 | 80000 | 80 | DC4SEA4810 | CAPTA6034D3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80TN1005CN | 1550 | 1 | ECM | 80 | 67 | 55500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 210 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 13.8 / 11.2 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 80000 | 80 | DC4SEA6010 | CHPTA6030D3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80TN1005CN | 1380 | 1 | ECM | 80 | 67 | 45500 | 100000 | 80000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 210 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.3 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 100000 | 80000 | 80 | DC4SEA4810 | CHPTA6030D3 | DR80TN1005CN |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230C3 / DR80TN1205DX | 1290 | 1 | ECM | 80 | 67 | 39500 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 207 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA4210 | CAPTA4230C3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN1205DX | 1290 | 1 | ECM | 80 | 67 | 39500 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 213 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA4210 | CAPTA4230D3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA4230D3 / DR80TN1205DX | 1290 | 1 | ECM | 80 | 67 | 39500 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 213 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA4210 | CAPTA4230D3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TN1205DX | 1480 | 1 | ECM | 80 | 67 | 56500 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 214 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA6010 | CAPTA6030C3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TN1205DX | 1370 | 1 | ECM | 80 | 67 | 45500 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 214 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA4810 | CAPTA6030C3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030C3 / DR80TN1205DX | 1290 | 1 | ECM | 80 | 67 | 40000 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 214 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA4210 | CAPTA6030C3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80TN1205DX | 1480 | 1 | ECM | 80 | 67 | 56500 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 218 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.5 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA6010 | CAPTA6030D3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80TN1205DX | 1370 | 1 | ECM | 80 | 67 | 45500 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 218 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.5 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA4810 | CAPTA6030D3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6030D3 / DR80TN1205DX | 1290 | 1 | ECM | 80 | 67 | 40000 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 218 | DAIKIN | DC4SEA4210 | 208/60/1 | 18.95 | 30 | 95 | R-32 | 15.2 / 12 | 239 | 1 | 3.5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA4210 | CAPTA6030D3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80TN1205DX | 1500 | 1 | ECM | 80 | 67 | 57000 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 218 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 15 / 12 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA6010 | CAPTA6034C3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034C3 / DR80TN1205DX | 1400 | 1 | ECM | 80 | 67 | 45500 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 218 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15.2 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA4810 | CAPTA6034C3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80TN1205DX | 1500 | 1 | ECM | 80 | 67 | 57000 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 221 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 15 / 12 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA6010 | CAPTA6034D3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CAPTA6034D3 / DR80TN1205DX | 1400 | 1 | ECM | 80 | 67 | 45500 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 221 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 15.2 / 12 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Upflow/Downflow | 2 | 120000 | 96000 | 80 | DC4SEA4810 | CAPTA6034D3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CAPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80TN1205DX | 1480 | 1 | ECM | 80 | 67 | 56000 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 223 | DAIKIN | DC4SEA6010 | 208/60/1 | 32.44 | 50 | 95 | R-32 | 14 / 11.2 | 244 | 1 | 5 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 120000 | 96000 | 80 | DC4SEA6010 | CHPTA6030D3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | CHPTA6030D3 / DR80TN1205DX | 1360 | 1 | ECM | 80 | 67 | 45500 | 120000 | 96000 |  | 2 | 80 | 115/60/1 | 15.32 | 20 | 223 | DAIKIN | DC4SEA4810 | 208/60/1 | 25.19 | 40 | 95 | R-32 | 14.3 / 11.7 | 241 | 1 | 4 | 14.3 SEER2 (Single Stage) | 1 | Horizontal | 2 | 120000 | 96000 | 80 | DC4SEA4810 | CHPTA6030D3 | DR80TN1205DX |  |  | ENGINEERING MANUAL - DC4SEA | ENGINEERING MANUAL - COILS | ENGINEERING MANUAL - DR80TN | IM - DC4SEA | IM - DR80TN | IM - CHPTA | [10 empty] | - | - | - | - | - | - | - | - | - | -

## Sheet1
0 | 15.2 SEER2
14.3 SEER2
16.2 SEER2
17.2 SEER2

## SCHEDULE NOTES
Provide with 7-day programmable thermostat
Provide with 7-day programmable BACnet thermostat
Provide with field installed disconnect. Disconnect shall be provided and installed by electrical contractor