## SCHEDULE
SCHEDULE RANGE | [16 empty] | FILTERS |  |  | DOCUMENTATION
VAV SCHEDULE | [16 empty] | SIZE | COOLING CFM | INSULATION | SUBMITTAL (OUTDOOR UNIT) | SUBMITTAL (INDOOR UNIT) | SUBMITTAL (SYSTEM) | ENGINEERING MANUAL (SYSTEM) | ENGINEERING MANUAL (OUTDOOR UNIT) | ENGINEERING MANUAL (INDOOR UNIT) | CAPACITY TABLE | INSTALLATION MANUAL (OUTDOOR) | INSTALLATION MANUAL (INDOOR) | INSTALLATION MANUAL (SYSTEM) | REVIT (OUTDOOR) | REVIT (INDOOR) | REVIT (SYSTEM) | CAD (OUTDOOR) | CAD (INDOOR) | CAD (SYSTEM) | CONTROLS OPTIONS | OPERATION MANUAL
MAKE | MODEL | SIZE | MAX PRIMARY CFM | MIN PRIMARY CFM | MAX HEATING CFM | INLET SP (IN. W.G.) | DOWNSTREAM SP (IN. W.G.) | DIFFERENTIAL PD (IN. W.G.) | MIN OPERATING SP (IN. W.G.) | MAX DISCHARGE NC | MAX DISCHARGE SOUND POWER | MAX RADIATED NC | MAX RADIATED SOUND POWER | SUPPLY AIR TEMP (°F) | RETURN AIR TEMP (°F) | INSULATION
PRICE | SDV | 4 | 75 | 45 | 75 | 1 | 0.25 | 0.75 | 0.01 | 15 | 60,53,42,39,37,34 | 3 | 45,37,27,24,21,22 | 55 | 75 | 0.5" Fiberglass | 4 | 75 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 80 | 45 | 80 | 1 | 0.25 | 0.75 | 0.01 | 16 | 61,54,43,40,38,34 | 4 | 46,38,28,24,22,22 | 55 | 75 | 0.5" Fiberglass | 4 | 80 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 85 | 45 | 85 | 1 | 0.25 | 0.75 | 0.01 | 17 | 62,55,44,41,39,35 | 6 | 47,39,29,25,23,23 | 55 | 75 | 0.5" Fiberglass | 4 | 85 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 90 | 45 | 90 | 1 | 0.25 | 0.75 | 0.01 | 19 | 63,56,45,42,39,36 | 7 | 48,40,30,26,23,23 | 55 | 75 | 0.5" Fiberglass | 4 | 90 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 95 | 45 | 95 | 1 | 0.25 | 0.75 | 0.01 | 20 | 64,57,46,43,40,36 | 7 | 48,41,31,27,24,23 | 55 | 75 | 0.5" Fiberglass | 4 | 95 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 100 | 45 | 100 | 1 | 0.25 | 0.75 | 0.01 | 20 | 64,58,47,43,41,37 | 8 | 49,41,31,27,24,24 | 55 | 75 | 0.5" Fiberglass | 4 | 100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 105 | 45 | 105 | 1 | 0.25 | 0.75 | 0.01 | 21 | 65,59,47,44,41,38 | 10 | 50,42,32,28,25,24 | 55 | 75 | 0.5" Fiberglass | 4 | 105 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 110 | 45 | 110 | 1 | 0.25 | 0.75 | 0.01 | 22 | 66,60,48,45,42,38 | 11 | 51,43,33,28,25,25 | 55 | 75 | 0.5" Fiberglass | 4 | 110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 115 | 45 | 115 | 1 | 0.25 | 0.75 | 0.01 | 24 | 67,61,49,45,42,39 | 11 | 51,44,33,29,26,25 | 55 | 75 | 0.5" Fiberglass | 4 | 115 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 120 | 45 | 120 | 1 | 0.25 | 0.75 | 0.01 | 24 | 67,62,49,46,43,39 | 12 | 52,45,34,29,26,25 | 55 | 75 | 0.5" Fiberglass | 4 | 120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 125 | 45 | 125 | 1 | 0.25 | 0.75 | 0.01 | 25 | 68,62,50,47,44,39 | 12 | 52,45,35,30,27,25 | 55 | 75 | 0.5" Fiberglass | 4 | 125 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 130 | 45 | 130 | 1 | 0.25 | 0.75 | 0.01 | 26 | 69,63,51,47,44,40 | 13 | 53,46,35,30,27,26 | 55 | 75 | 0.5" Fiberglass | 4 | 130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 135 | 45 | 135 | 1 | 0.25 | 0.75 | 0.01 | 26 | 69,64,51,48,44,40 | 13 | 53,46,36,31,27,26 | 55 | 75 | 0.5" Fiberglass | 4 | 135 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 140 | 45 | 140 | 1 | 0.25 | 0.75 | 0.01 | 28 | 70,64,52,48,45,41 | 15 | 54,47,36,31,28,26 | 55 | 75 | 0.5" Fiberglass | 4 | 140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 145 | 45 | 145 | 1 | 0.25 | 0.75 | 0.01 | 28 | 70,65,52,49,45,41 | 15 | 54,48,37,32,28,27 | 55 | 75 | 0.5" Fiberglass | 4 | 145 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 150 | 45 | 150 | 1 | 0.25 | 0.75 | 0.01 | 29 | 71,66,53,49,46,42 | 16 | 55,48,37,32,28,27 | 55 | 75 | 0.5" Fiberglass | 4 | 150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 155 | 45 | 155 | 1 | 0.25 | 0.75 | 0.01 | 30 | 72,66,53,50,46,42 | 17 | 55,49,38,33,29,27 | 55 | 75 | 0.5" Fiberglass | 4 | 155 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 160 | 45 | 160 | 1 | 0.25 | 0.75 | 0.01 | 30 | 72,67,54,50,47,42 | 17 | 56,49,38,33,29,27 | 55 | 75 | 0.5" Fiberglass | 4 | 160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 165 | 45 | 165 | 1 | 0.25 | 0.75 | 0.01 | 31 | 73,67,54,51,47,43 | 18 | 56,50,39,33,29,28 | 55 | 75 | 0.5" Fiberglass | 4 | 165 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 170 | 45 | 170 | 1 | 0.25 | 0.75 | 0.01 | 31 | 73,68,55,51,47,43 | 19 | 57,50,39,34,30,28 | 55 | 75 | 0.5" Fiberglass | 4 | 170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 175 | 45 | 175 | 1 | 0.25 | 0.75 | 0.01 | 33 | 74,68,55,52,48,43 | 19 | 57,51,40,34,30,28 | 55 | 75 | 0.5" Fiberglass | 4 | 175 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 180 | 45 | 180 | 1 | 0.25 | 0.75 | 0.01 | 33 | 74,69,56,52,48,44 | 19 | 57,51,40,34,30,28 | 55 | 75 | 0.5" Fiberglass | 4 | 180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 185 | 45 | 185 | 1 | 0.25 | 0.75 | 0.01 | 33 | 74,69,56,52,48,44 | 20 | 58,52,40,35,30,28 | 55 | 75 | 0.5" Fiberglass | 4 | 185 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 190 | 45 | 190 | 1 | 0.25 | 0.75 | 0.01 | 34 | 75,70,56,53,49,44 | 20 | 58,52,41,35,31,29 | 55 | 75 | 0.5" Fiberglass | 4 | 190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 195 | 45 | 195 | 1 | 0.25 | 0.75 | 0.01 | 34 | 75,70,57,53,49,45 | 21 | 59,53,41,35,31,29 | 55 | 75 | 0.5" Fiberglass | 4 | 195 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 200 | 45 | 200 | 1 | 0.25 | 0.75 | 0.01 | 35 | 76,71,57,53,49,45 | 21 | 59,53,41,36,31,29 | 55 | 75 | 0.5" Fiberglass | 4 | 200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 205 | 45 | 205 | 1 | 0.25 | 0.75 | 0.01 | 35 | 76,71,58,54,50,45 | 23 | 59,54,42,36,32,29 | 55 | 75 | 0.5" Fiberglass | 4 | 205 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 210 | 45 | 210 | 1 | 0.25 | 0.75 | 0.01 | 36 | 77,72,58,54,50,45 | 23 | 60,54,42,36,32,29 | 55 | 75 | 0.5" Fiberglass | 4 | 210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 215 | 45 | 215 | 1 | 0.25 | 0.75 | 0.01 | 36 | 77,72,58,55,50,46 | 23 | 60,54,42,36,32,29 | 55 | 75 | 0.5" Fiberglass | 4 | 215 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 220 | 45 | 220 | 1 | 0.25 | 0.75 | 0.01 | 36 | 77,73,59,55,51,46 | 24 | 60,55,43,37,32,30 | 55 | 75 | 0.5" Fiberglass | 4 | 220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 225 | 45 | 225 | 1 | 0.25 | 0.75 | 0.01 | 38 | 78,73,59,55,51,46 | 24 | 61,55,43,37,32,30 | 55 | 75 | 0.5" Fiberglass | 4 | 225 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 230 | 45 | 230 | 1 | 0.25 | 0.75 | 0.01 | 38 | 78,73,59,55,51,46 | 24 | 61,55,43,37,33,30 | 55 | 75 | 0.5" Fiberglass | 4 | 230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 235 | 45 | 235 | 1 | 0.25 | 0.75 | 0.01 | 38 | 78,74,60,56,51,47 | 25 | 61,56,44,38,33,30 | 55 | 75 | 0.5" Fiberglass | 4 | 235 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 240 | 45 | 240 | 1 | 0.25 | 0.75 | 0.01 | 39 | 79,74,60,56,52,47 | 25 | 62,56,44,38,33,30 | 55 | 75 | 0.5" Fiberglass | 4 | 240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 245 | 45 | 245 | 1 | 0.25 | 0.75 | 0.01 | 39 | 79,75,60,56,52,47 | 26 | 62,57,44,38,33,30 | 55 | 75 | 0.5" Fiberglass | 4 | 245 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 250 | 45 | 250 | 1 | 0.25 | 0.75 | 0.01 | 39 | 79,75,61,57,52,47 | 26 | 62,57,45,38,34,31 | 55 | 75 | 0.5" Fiberglass | 4 | 250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 255 | 45 | 255 | 1 | 0.25 | 0.75 | 0.01 | 40 | 80,75,61,57,52,48 | 26 | 62,57,45,39,34,31 | 55 | 75 | 0.5" Fiberglass | 4 | 255 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 260 | 45 | 260 | 1 | 0.25 | 0.75 | 0.01 | 40 | 80,76,61,57,53,48 | 27 | 63,58,45,39,34,31 | 55 | 75 | 0.5" Fiberglass | 4 | 260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 265 | 45 | 265 | 1 | 0.25 | 0.75 | 0.01 | 40 | 80,76,62,58,53,48 | 27 | 63,58,46,39,34,31 | 55 | 75 | 0.5" Fiberglass | 4 | 265 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 270 | 45 | 270 | 1 | 0.25 | 0.75 | 0.01 | 42 | 81,76,62,58,53,48 | 27 | 63,58,46,39,34,31 | 55 | 75 | 0.5" Fiberglass | 4 | 270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 275 | 45 | 275 | 1 | 0.25 | 0.75 | 0.01 | 42 | 81,77,62,58,53,48 | 27 | 63,58,46,39,34,31 | 55 | 75 | 0.5" Fiberglass | 4 | 275 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 280 | 45 | 280 | 1 | 0.25 | 0.75 | 0.01 | 42 | 81,77,62,58,54,49 | 28 | 64,59,46,40,35,31 | 55 | 75 | 0.5" Fiberglass | 4 | 280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 285 | 45 | 285 | 1 | 0.25 | 0.75 | 0.01 | 43 | 82,77,63,59,54,49 | 28 | 64,59,47,40,35,32 | 55 | 75 | 0.5" Fiberglass | 4 | 285 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 290 | 45 | 290 | 1 | 0.25 | 0.75 | 0.01 | 43 | 82,78,63,59,54,49 | 28 | 64,59,47,40,35,32 | 55 | 75 | 0.5" Fiberglass | 4 | 290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 295 | 45 | 295 | 1 | 0.25 | 0.75 | 0.01 | 43 | 82,78,63,59,54,49 | 30 | 64,60,47,40,35,32 | 55 | 75 | 0.5" Fiberglass | 4 | 295 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 300 | 45 | 300 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,78,63,59,54,49 | 30 | 65,60,47,41,35,32 | 55 | 75 | 0.5" Fiberglass | 4 | 300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 305 | 45 | 305 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,79,64,60,55,50 | 30 | 65,60,48,41,36,32 | 55 | 75 | 0.5" Fiberglass | 4 | 305 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 310 | 45 | 310 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,79,64,60,55,50 | 31 | 65,61,48,41,36,32 | 55 | 75 | 0.5" Fiberglass | 4 | 310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 315 | 45 | 315 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,79,64,60,55,50 | 31 | 65,61,48,41,36,32 | 55 | 75 | 0.5" Fiberglass | 4 | 315 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 320 | 45 | 320 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,79,64,60,55,50 | 31 | 66,61,48,41,36,32 | 55 | 75 | 0.5" Fiberglass | 4 | 320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 325 | 45 | 325 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,80,65,61,55,50 | 31 | 66,61,48,42,36,33 | 55 | 75 | 0.5" Fiberglass | 4 | 325 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 330 | 45 | 330 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,80,65,61,56,51 | 32 | 66,62,49,42,36,33 | 55 | 75 | 0.5" Fiberglass | 4 | 330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 335 | 45 | 335 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,80,65,61,56,51 | 32 | 66,62,49,42,36,33 | 55 | 75 | 0.5" Fiberglass | 4 | 335 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 340 | 45 | 340 | 1 | 0.25 | 0.75 | 0.01 | 43 | 84,81,65,61,56,51 | 32 | 66,62,49,42,37,33 | 55 | 75 | 0.5" Fiberglass | 4 | 340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 345 | 45 | 345 | 1 | 0.25 | 0.75 | 0.01 | 43 | 85,81,66,61,56,51 | 32 | 67,62,49,42,37,33 | 55 | 75 | 0.5" Fiberglass | 4 | 345 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 350 | 45 | 350 | 1 | 0.25 | 0.75 | 0.01 | 43 | 85,81,66,62,56,51 | 33 | 67,63,50,42,37,33 | 55 | 75 | 0.5" Fiberglass | 4 | 350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 355 | 45 | 355 | 1 | 0.25 | 0.75 | 0.01 | 43 | 85,81,66,62,57,51 | 33 | 67,63,50,43,37,33 | 55 | 75 | 0.5" Fiberglass | 4 | 355 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 360 | 45 | 360 | 1 | 0.25 | 0.75 | 0.01 | 44 | 85,82,66,62,57,51 | 33 | 67,63,50,43,37,33 | 55 | 75 | 0.5" Fiberglass | 4 | 360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 365 | 45 | 365 | 1 | 0.25 | 0.75 | 0.01 | 44 | 86,82,66,62,57,52 | 33 | 67,63,50,43,37,33 | 55 | 75 | 0.5" Fiberglass | 4 | 365 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 370 | 45 | 370 | 1 | 0.25 | 0.75 | 0.01 | 44 | 86,82,67,62,57,52 | 33 | 68,63,50,43,37,33 | 55 | 75 | 0.5" Fiberglass | 4 | 370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 375 | 45 | 375 | 1 | 0.25 | 0.75 | 0.01 | 44 | 86,82,67,63,57,52 | 34 | 68,64,51,43,38,34 | 55 | 75 | 0.5" Fiberglass | 4 | 375 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 380 | 45 | 380 | 1 | 0.25 | 0.75 | 0.01 | 45 | 86,83,67,63,57,52 | 34 | 68,64,51,43,38,34 | 55 | 75 | 0.5" Fiberglass | 4 | 380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 385 | 45 | 385 | 1 | 0.25 | 0.75 | 0.01 | 45 | 86,83,67,63,58,52 | 34 | 68,64,51,44,38,34 | 55 | 75 | 0.5" Fiberglass | 4 | 385 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 390 | 45 | 390 | 1 | 0.25 | 0.75 | 0.01 | 45 | 87,83,67,63,58,52 | 34 | 68,64,51,44,38,34 | 55 | 75 | 0.5" Fiberglass | 4 | 390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 395 | 45 | 395 | 1 | 0.25 | 0.75 | 0.01 | 45 | 87,83,68,63,58,53 | 36 | 69,65,51,44,38,34 | 55 | 75 | 0.5" Fiberglass | 4 | 395 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 400 | 45 | 400 | 1 | 0.25 | 0.75 | 0.01 | 46 | 87,84,68,64,58,53 | 36 | 69,65,51,44,38,34 | 55 | 75 | 0.5" Fiberglass | 4 | 400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 150 | 65 | 150 | 1 | 0.25 | 0.75 | 0.02 | 16 | 61,53,46,41,38,36 | 7 | 48,41,31,28,26,24 | 55 | 75 | 0.5" Fiberglass | 6 | 150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 155 | 65 | 155 | 1 | 0.25 | 0.75 | 0.02 | 17 | 62,54,46,42,38,37 | 8 | 49,41,32,28,26,24 | 55 | 75 | 0.5" Fiberglass | 6 | 155 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 160 | 65 | 160 | 1 | 0.25 | 0.75 | 0.02 | 17 | 62,54,46,42,38,37 | 8 | 49,42,32,29,27,24 | 55 | 75 | 0.5" Fiberglass | 6 | 160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 165 | 65 | 165 | 1 | 0.25 | 0.75 | 0.02 | 17 | 62,55,47,42,39,37 | 8 | 49,42,33,29,27,25 | 55 | 75 | 0.5" Fiberglass | 6 | 165 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 170 | 65 | 170 | 1 | 0.25 | 0.75 | 0.03 | 19 | 63,55,47,43,39,37 | 10 | 50,42,33,29,27,25 | 55 | 75 | 0.5" Fiberglass | 6 | 170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 175 | 65 | 175 | 1 | 0.25 | 0.75 | 0.03 | 19 | 63,56,48,43,39,37 | 10 | 50,43,33,30,27,25 | 55 | 75 | 0.5" Fiberglass | 6 | 175 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 180 | 65 | 180 | 1 | 0.25 | 0.75 | 0.03 | 19 | 63,56,48,43,39,38 | 10 | 50,43,34,30,27,25 | 55 | 75 | 0.5" Fiberglass | 6 | 180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 185 | 65 | 185 | 1 | 0.25 | 0.75 | 0.03 | 20 | 64,56,48,44,39,38 | 11 | 51,44,34,30,28,25 | 55 | 75 | 0.5" Fiberglass | 6 | 185 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 190 | 65 | 190 | 1 | 0.25 | 0.75 | 0.03 | 20 | 64,57,49,44,40,38 | 11 | 51,44,34,31,28,25 | 55 | 75 | 0.5" Fiberglass | 6 | 190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 195 | 65 | 195 | 1 | 0.25 | 0.75 | 0.03 | 20 | 64,57,49,44,40,38 | 11 | 51,44,35,31,28,25 | 55 | 75 | 0.5" Fiberglass | 6 | 195 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 200 | 65 | 200 | 1 | 0.25 | 0.75 | 0.04 | 21 | 65,58,49,45,40,38 | 12 | 51,45,35,31,28,25 | 55 | 75 | 0.5" Fiberglass | 6 | 200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 205 | 65 | 205 | 1 | 0.25 | 0.75 | 0.04 | 21 | 65,58,50,45,40,38 | 12 | 52,45,35,31,28,25 | 55 | 75 | 0.5" Fiberglass | 6 | 205 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 210 | 65 | 210 | 1 | 0.25 | 0.75 | 0.04 | 21 | 65,58,50,45,41,39 | 12 | 52,45,36,32,29,26 | 55 | 75 | 0.5" Fiberglass | 6 | 210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 215 | 65 | 215 | 1 | 0.25 | 0.75 | 0.04 | 22 | 66,59,50,45,41,39 | 13 | 52,46,36,32,29,26 | 55 | 75 | 0.5" Fiberglass | 6 | 215 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 220 | 65 | 220 | 1 | 0.25 | 0.75 | 0.04 | 22 | 66,59,51,46,41,39 | 13 | 53,46,36,32,29,26 | 55 | 75 | 0.5" Fiberglass | 6 | 220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 225 | 65 | 225 | 1 | 0.25 | 0.75 | 0.05 | 22 | 66,59,51,46,41,39 | 13 | 53,46,37,32,29,26 | 55 | 75 | 0.5" Fiberglass | 6 | 225 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 230 | 65 | 230 | 1 | 0.25 | 0.75 | 0.05 | 22 | 66,60,51,46,41,39 | 13 | 53,46,37,33,29,26 | 55 | 75 | 0.5" Fiberglass | 6 | 230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 235 | 65 | 235 | 1 | 0.25 | 0.75 | 0.05 | 24 | 67,60,52,47,41,39 | 14 | 53,47,37,33,29,26 | 55 | 75 | 0.5" Fiberglass | 6 | 235 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 240 | 65 | 240 | 1 | 0.25 | 0.75 | 0.05 | 24 | 67,60,52,47,42,39 | 15 | 54,47,38,33,30,26 | 55 | 75 | 0.5" Fiberglass | 6 | 240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 245 | 65 | 245 | 1 | 0.25 | 0.75 | 0.05 | 24 | 67,61,52,47,42,40 | 15 | 54,47,38,33,30,26 | 55 | 75 | 0.5" Fiberglass | 6 | 245 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 250 | 65 | 250 | 1 | 0.25 | 0.75 | 0.06 | 24 | 67,61,52,47,42,40 | 15 | 54,48,38,34,30,26 | 55 | 75 | 0.5" Fiberglass | 6 | 250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 255 | 65 | 255 | 1 | 0.25 | 0.75 | 0.06 | 25 | 68,61,53,47,42,40 | 15 | 54,48,38,34,30,26 | 55 | 75 | 0.5" Fiberglass | 6 | 255 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 260 | 65 | 260 | 1 | 0.25 | 0.75 | 0.06 | 25 | 68,61,53,48,42,40 | 15 | 54,48,39,34,30,26 | 55 | 75 | 0.5" Fiberglass | 6 | 260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 265 | 65 | 265 | 1 | 0.25 | 0.75 | 0.06 | 25 | 68,62,53,48,42,40 | 16 | 55,48,39,34,30,26 | 55 | 75 | 0.5" Fiberglass | 6 | 265 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 270 | 65 | 270 | 1 | 0.25 | 0.75 | 0.07 | 25 | 68,62,53,48,43,40 | 17 | 55,49,39,34,30,26 | 55 | 75 | 0.5" Fiberglass | 6 | 270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 275 | 65 | 275 | 1 | 0.25 | 0.75 | 0.07 | 26 | 69,62,54,48,43,40 | 17 | 55,49,39,35,31,27 | 55 | 75 | 0.5" Fiberglass | 6 | 275 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 280 | 65 | 280 | 1 | 0.25 | 0.75 | 0.07 | 26 | 69,62,54,49,43,40 | 17 | 55,49,40,35,31,27 | 55 | 75 | 0.5" Fiberglass | 6 | 280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 285 | 65 | 285 | 1 | 0.25 | 0.75 | 0.07 | 26 | 69,63,54,49,43,41 | 17 | 56,49,40,35,31,27 | 55 | 75 | 0.5" Fiberglass | 6 | 285 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 290 | 65 | 290 | 1 | 0.25 | 0.75 | 0.08 | 26 | 69,63,54,49,43,41 | 18 | 56,50,40,35,31,27 | 55 | 75 | 0.5" Fiberglass | 6 | 290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 295 | 65 | 295 | 1 | 0.25 | 0.75 | 0.08 | 26 | 69,63,55,49,43,41 | 18 | 56,50,40,35,31,27 | 55 | 75 | 0.5" Fiberglass | 6 | 295 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 300 | 65 | 300 | 1 | 0.25 | 0.75 | 0.08 | 24 | 70,63,55,49,44,41 | 18 | 56,50,40,36,31,27 | 55 | 75 | 0.5" Fiberglass | 6 | 300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 305 | 65 | 305 | 1 | 0.25 | 0.75 | 0.08 | 24 | 70,64,55,50,44,41 | 18 | 56,50,41,36,31,27 | 55 | 75 | 0.5" Fiberglass | 6 | 305 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 310 | 65 | 310 | 1 | 0.25 | 0.75 | 0.09 | 24 | 70,64,55,50,44,41 | 19 | 57,50,41,36,31,27 | 55 | 75 | 0.5" Fiberglass | 6 | 310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 315 | 65 | 315 | 1 | 0.25 | 0.75 | 0.09 | 24 | 70,64,56,50,44,41 | 19 | 57,51,41,36,32,27 | 55 | 75 | 0.5" Fiberglass | 6 | 315 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 320 | 65 | 320 | 1 | 0.25 | 0.75 | 0.09 | 24 | 70,64,56,50,44,41 | 19 | 57,51,41,36,32,27 | 55 | 75 | 0.5" Fiberglass | 6 | 320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 325 | 65 | 325 | 1 | 0.25 | 0.75 | 0.1 | 25 | 71,65,56,50,44,41 | 19 | 57,51,42,36,32,27 | 55 | 75 | 0.5" Fiberglass | 6 | 325 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 330 | 65 | 330 | 1 | 0.25 | 0.75 | 0.1 | 25 | 71,65,56,51,44,41 | 19 | 57,51,42,37,32,27 | 55 | 75 | 0.5" Fiberglass | 6 | 330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 335 | 65 | 335 | 1 | 0.25 | 0.75 | 0.1 | 25 | 71,65,56,51,44,42 | 20 | 57,52,42,37,32,27 | 55 | 75 | 0.5" Fiberglass | 6 | 335 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 340 | 65 | 340 | 1 | 0.25 | 0.75 | 0.1 | 25 | 71,65,57,51,45,42 | 20 | 58,52,42,37,32,27 | 55 | 75 | 0.5" Fiberglass | 6 | 340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 345 | 65 | 345 | 1 | 0.25 | 0.75 | 0.11 | 25 | 71,66,57,51,45,42 | 20 | 58,52,42,37,32,27 | 55 | 75 | 0.5" Fiberglass | 6 | 345 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 350 | 65 | 350 | 1 | 0.25 | 0.75 | 0.11 | 26 | 72,66,57,51,45,42 | 20 | 58,52,43,37,32,27 | 55 | 75 | 0.5" Fiberglass | 6 | 350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 355 | 65 | 355 | 1 | 0.25 | 0.75 | 0.11 | 26 | 72,66,57,51,45,42 | 20 | 58,52,43,37,32,28 | 55 | 75 | 0.5" Fiberglass | 6 | 355 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 360 | 65 | 360 | 1 | 0.25 | 0.75 | 0.12 | 26 | 72,66,57,52,45,42 | 20 | 58,52,43,38,32,28 | 55 | 75 | 0.5" Fiberglass | 6 | 360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 365 | 65 | 365 | 1 | 0.25 | 0.75 | 0.12 | 26 | 72,66,58,52,45,42 | 21 | 58,53,43,38,33,28 | 55 | 75 | 0.5" Fiberglass | 6 | 365 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 370 | 65 | 370 | 1 | 0.25 | 0.75 | 0.12 | 26 | 72,67,58,52,45,42 | 21 | 59,53,43,38,33,28 | 55 | 75 | 0.5" Fiberglass | 6 | 370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 375 | 65 | 375 | 1 | 0.25 | 0.75 | 0.13 | 26 | 72,67,58,52,45,42 | 21 | 59,53,43,38,33,28 | 55 | 75 | 0.5" Fiberglass | 6 | 375 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 380 | 65 | 380 | 1 | 0.25 | 0.75 | 0.13 | 28 | 73,67,58,52,46,42 | 21 | 59,53,44,38,33,28 | 55 | 75 | 0.5" Fiberglass | 6 | 380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 385 | 65 | 385 | 1 | 0.25 | 0.75 | 0.13 | 28 | 73,67,58,52,46,43 | 21 | 59,53,44,38,33,28 | 55 | 75 | 0.5" Fiberglass | 6 | 385 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 390 | 65 | 390 | 1 | 0.25 | 0.75 | 0.14 | 28 | 73,67,58,53,46,43 | 23 | 59,54,44,38,33,28 | 55 | 75 | 0.5" Fiberglass | 6 | 390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 395 | 65 | 395 | 1 | 0.25 | 0.75 | 0.14 | 28 | 73,67,59,53,46,43 | 23 | 59,54,44,39,33,28 | 55 | 75 | 0.5" Fiberglass | 6 | 395 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 400 | 65 | 400 | 1 | 0.25 | 0.75 | 0.14 | 28 | 73,68,59,53,46,43 | 23 | 59,54,44,39,33,28 | 55 | 75 | 0.5" Fiberglass | 6 | 400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 405 | 65 | 405 | 1 | 0.25 | 0.75 | 0.15 | 28 | 73,68,59,53,46,43 | 23 | 60,54,44,39,33,28 | 55 | 75 | 0.5" Fiberglass | 6 | 405 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 410 | 65 | 410 | 1 | 0.25 | 0.75 | 0.15 | 28 | 73,68,59,53,46,43 | 23 | 60,54,45,39,33,28 | 55 | 75 | 0.5" Fiberglass | 6 | 410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 415 | 65 | 415 | 1 | 0.25 | 0.75 | 0.15 | 29 | 74,68,59,53,46,43 | 23 | 60,54,45,39,34,28 | 55 | 75 | 0.5" Fiberglass | 6 | 415 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 420 | 65 | 420 | 1 | 0.25 | 0.75 | 0.16 | 29 | 74,68,59,53,46,43 | 24 | 60,55,45,39,34,28 | 55 | 75 | 0.5" Fiberglass | 6 | 420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 425 | 65 | 425 | 1 | 0.25 | 0.75 | 0.16 | 29 | 74,69,60,54,46,43 | 24 | 60,55,45,39,34,28 | 55 | 75 | 0.5" Fiberglass | 6 | 425 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 430 | 65 | 430 | 1 | 0.25 | 0.75 | 0.17 | 29 | 74,69,60,54,47,43 | 24 | 60,55,45,39,34,28 | 55 | 75 | 0.5" Fiberglass | 6 | 430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 435 | 65 | 435 | 1 | 0.25 | 0.75 | 0.17 | 29 | 74,69,60,54,47,43 | 24 | 60,55,45,40,34,28 | 55 | 75 | 0.5" Fiberglass | 6 | 435 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 440 | 65 | 440 | 1 | 0.25 | 0.75 | 0.17 | 29 | 74,69,60,54,47,43 | 24 | 61,55,46,40,34,28 | 55 | 75 | 0.5" Fiberglass | 6 | 440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 445 | 65 | 445 | 1 | 0.25 | 0.75 | 0.18 | 29 | 74,69,60,54,47,43 | 24 | 61,55,46,40,34,28 | 55 | 75 | 0.5" Fiberglass | 6 | 445 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 450 | 65 | 450 | 1 | 0.25 | 0.75 | 0.18 | 30 | 75,69,60,54,47,44 | 24 | 61,55,46,40,34,28 | 55 | 75 | 0.5" Fiberglass | 6 | 450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 455 | 65 | 455 | 1 | 0.25 | 0.75 | 0.19 | 30 | 75,70,61,54,47,44 | 25 | 61,56,46,40,34,28 | 55 | 75 | 0.5" Fiberglass | 6 | 455 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 460 | 65 | 460 | 1 | 0.25 | 0.75 | 0.19 | 30 | 75,70,61,55,47,44 | 25 | 61,56,46,40,34,29 | 55 | 75 | 0.5" Fiberglass | 6 | 460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 465 | 65 | 465 | 1 | 0.25 | 0.75 | 0.19 | 30 | 75,70,61,55,47,44 | 25 | 61,56,46,40,34,29 | 55 | 75 | 0.5" Fiberglass | 6 | 465 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 470 | 65 | 470 | 1 | 0.25 | 0.75 | 0.2 | 30 | 75,70,61,55,47,44 | 25 | 61,56,46,40,34,29 | 55 | 75 | 0.5" Fiberglass | 6 | 470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 475 | 65 | 475 | 1 | 0.25 | 0.75 | 0.2 | 30 | 75,70,61,55,47,44 | 25 | 61,56,47,41,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 475 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 480 | 65 | 480 | 1 | 0.25 | 0.75 | 0.21 | 30 | 75,70,61,55,47,44 | 25 | 62,56,47,41,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 485 | 65 | 485 | 1 | 0.25 | 0.75 | 0.21 | 31 | 76,70,61,55,48,44 | 25 | 62,56,47,41,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 485 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 490 | 65 | 490 | 1 | 0.25 | 0.75 | 0.22 | 31 | 76,71,62,55,48,44 | 26 | 62,57,47,41,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 495 | 65 | 495 | 1 | 0.25 | 0.75 | 0.22 | 31 | 76,71,62,55,48,44 | 26 | 62,57,47,41,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 495 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 500 | 65 | 500 | 1 | 0.25 | 0.75 | 0.22 | 31 | 76,71,62,56,48,44 | 26 | 62,57,47,41,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 505 | 65 | 505 | 1 | 0.25 | 0.75 | 0.23 | 31 | 76,71,62,56,48,44 | 26 | 62,57,47,41,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 505 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 510 | 65 | 510 | 1 | 0.25 | 0.75 | 0.23 | 31 | 76,71,62,56,48,44 | 26 | 62,57,47,41,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 515 | 65 | 515 | 1 | 0.25 | 0.75 | 0.24 | 31 | 76,71,62,56,48,44 | 26 | 62,57,48,41,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 515 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 520 | 65 | 520 | 1 | 0.25 | 0.75 | 0.24 | 31 | 76,71,62,56,48,44 | 26 | 62,57,48,41,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 525 | 65 | 525 | 1 | 0.25 | 0.75 | 0.25 | 32 | 76,72,62,56,48,45 | 27 | 63,58,48,42,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 525 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 530 | 65 | 530 | 1 | 0.25 | 0.75 | 0.25 | 33 | 77,72,63,56,48,45 | 27 | 63,58,48,42,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 535 | 65 | 535 | 1 | 0.25 | 0.75 | 0.26 | 33 | 77,72,63,56,48,45 | 27 | 63,58,48,42,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 535 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 540 | 65 | 540 | 1 | 0.25 | 0.75 | 0.26 | 33 | 77,72,63,56,48,45 | 27 | 63,58,48,42,35,29 | 55 | 75 | 0.5" Fiberglass | 6 | 540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 545 | 65 | 545 | 1 | 0.25 | 0.75 | 0.27 | 33 | 77,72,63,57,49,45 | 27 | 63,58,48,42,36,29 | 55 | 75 | 0.5" Fiberglass | 6 | 545 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 550 | 65 | 550 | 1 | 0.25 | 0.75 | 0.27 | 33 | 77,72,63,57,49,45 | 27 | 63,58,48,42,36,29 | 55 | 75 | 0.5" Fiberglass | 6 | 550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 550 | 65 | 550 | 1 | 0.25 | 0.75 | 0.27 | 33 | 77,72,63,57,49,45 | 27 | 63,58,48,42,36,29 | 55 | 75 | 0.5" Fiberglass | 6 | 550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 400 | 125 | 400 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,57,48,46,43,40 | 11 | 51,44,35,30,26,22 | 55 | 75 | 0.5" Fiberglass | 8 | 400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 405 | 125 | 405 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,57,48,46,44,40 | 11 | 51,44,35,30,26,22 | 55 | 75 | 0.5" Fiberglass | 8 | 405 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 410 | 125 | 410 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,57,49,46,44,40 | 11 | 51,44,35,30,26,22 | 55 | 75 | 0.5" Fiberglass | 8 | 410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 415 | 125 | 415 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,58,49,46,44,40 | 12 | 51,45,35,30,26,22 | 55 | 75 | 0.5" Fiberglass | 8 | 415 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 420 | 125 | 420 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,58,49,46,44,40 | 12 | 52,45,36,31,26,22 | 55 | 75 | 0.5" Fiberglass | 8 | 420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 425 | 125 | 425 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,58,49,46,44,40 | 12 | 52,45,36,31,26,22 | 55 | 75 | 0.5" Fiberglass | 8 | 425 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 430 | 125 | 430 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,58,49,47,44,41 | 12 | 52,45,36,31,26,22 | 55 | 75 | 0.5" Fiberglass | 8 | 430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 435 | 125 | 435 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,58,49,47,44,41 | 12 | 52,45,36,31,26,22 | 55 | 75 | 0.5" Fiberglass | 8 | 435 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 440 | 125 | 440 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,58,50,47,44,41 | 12 | 52,45,36,31,26,22 | 55 | 75 | 0.5" Fiberglass | 8 | 440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 445 | 125 | 445 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,59,50,47,44,41 | 12 | 52,45,36,31,26,22 | 55 | 75 | 0.5" Fiberglass | 8 | 445 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 450 | 125 | 450 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,59,50,47,45,41 | 13 | 53,46,36,31,27,22 | 55 | 75 | 0.5" Fiberglass | 8 | 450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 455 | 125 | 455 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,59,50,47,45,41 | 13 | 53,46,36,31,27,22 | 55 | 75 | 0.5" Fiberglass | 8 | 455 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 460 | 125 | 460 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,59,50,48,45,41 | 13 | 53,46,37,32,27,23 | 55 | 75 | 0.5" Fiberglass | 8 | 460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 465 | 125 | 465 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,59,50,48,45,41 | 13 | 53,46,37,32,27,23 | 55 | 75 | 0.5" Fiberglass | 8 | 465 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 470 | 125 | 470 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,59,51,48,45,41 | 13 | 53,46,37,32,27,23 | 55 | 75 | 0.5" Fiberglass | 8 | 470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 475 | 125 | 475 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,60,51,48,45,41 | 13 | 53,46,37,32,27,23 | 55 | 75 | 0.5" Fiberglass | 8 | 475 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 480 | 125 | 480 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,60,51,48,45,42 | 13 | 53,46,37,32,27,23 | 55 | 75 | 0.5" Fiberglass | 8 | 480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 485 | 125 | 485 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,60,51,48,45,42 | 15 | 54,46,37,32,27,23 | 55 | 75 | 0.5" Fiberglass | 8 | 485 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 490 | 125 | 490 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,60,51,49,45,42 | 15 | 54,47,37,32,27,23 | 55 | 75 | 0.5" Fiberglass | 8 | 490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 495 | 125 | 495 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,60,51,49,46,42 | 15 | 54,47,37,32,27,23 | 55 | 75 | 0.5" Fiberglass | 8 | 495 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 500 | 125 | 500 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,60,52,49,46,42 | 15 | 54,47,38,32,27,23 | 55 | 75 | 0.5" Fiberglass | 8 | 500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 505 | 125 | 505 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,60,52,49,46,42 | 15 | 54,47,38,33,27,23 | 55 | 75 | 0.5" Fiberglass | 8 | 505 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 510 | 125 | 510 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,61,52,49,46,42 | 15 | 54,47,38,33,28,23 | 55 | 75 | 0.5" Fiberglass | 8 | 510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 515 | 125 | 515 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,61,52,49,46,42 | 15 | 54,47,38,33,28,23 | 55 | 75 | 0.5" Fiberglass | 8 | 515 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 520 | 125 | 520 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,61,52,49,46,42 | 15 | 54,47,38,33,28,23 | 55 | 75 | 0.5" Fiberglass | 8 | 520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 525 | 125 | 525 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,61,52,50,46,42 | 16 | 55,47,38,33,28,23 | 55 | 75 | 0.5" Fiberglass | 8 | 525 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 530 | 125 | 530 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,61,52,50,46,42 | 16 | 55,48,38,33,28,23 | 55 | 75 | 0.5" Fiberglass | 8 | 530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 535 | 125 | 535 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,61,53,50,46,42 | 16 | 55,48,38,33,28,23 | 55 | 75 | 0.5" Fiberglass | 8 | 535 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 540 | 125 | 540 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,61,53,50,46,43 | 16 | 55,48,38,33,28,23 | 55 | 75 | 0.5" Fiberglass | 8 | 540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 545 | 125 | 545 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,62,53,50,46,43 | 16 | 55,48,38,33,28,23 | 55 | 75 | 0.5" Fiberglass | 8 | 545 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 550 | 125 | 550 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,62,53,50,47,43 | 16 | 55,48,39,34,28,23 | 55 | 75 | 0.5" Fiberglass | 8 | 550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 555 | 125 | 555 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,62,53,50,47,43 | 16 | 55,48,39,34,28,24 | 55 | 75 | 0.5" Fiberglass | 8 | 555 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 560 | 125 | 560 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,62,53,51,47,43 | 16 | 55,48,39,34,28,24 | 55 | 75 | 0.5" Fiberglass | 8 | 560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 565 | 125 | 565 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,62,53,51,47,43 | 17 | 56,48,39,34,28,24 | 55 | 75 | 0.5" Fiberglass | 8 | 565 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 570 | 125 | 570 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,62,53,51,47,43 | 17 | 56,49,39,34,28,24 | 55 | 75 | 0.5" Fiberglass | 8 | 570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 575 | 125 | 575 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,62,54,51,47,43 | 17 | 56,49,39,34,28,24 | 55 | 75 | 0.5" Fiberglass | 8 | 575 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 580 | 125 | 580 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,62,54,51,47,43 | 17 | 56,49,39,34,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 585 | 125 | 585 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,63,54,51,47,43 | 17 | 56,49,39,34,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 585 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 590 | 125 | 590 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,63,54,51,47,43 | 17 | 56,49,39,34,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 595 | 125 | 595 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,63,54,51,47,43 | 17 | 56,49,39,34,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 595 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 600 | 125 | 600 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,63,54,52,47,43 | 17 | 56,49,40,35,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 605 | 125 | 605 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,63,54,52,48,44 | 17 | 56,49,40,35,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 605 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 610 | 125 | 610 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,63,54,52,48,44 | 19 | 57,49,40,35,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 615 | 125 | 615 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,63,55,52,48,44 | 19 | 57,49,40,35,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 615 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 620 | 125 | 620 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,63,55,52,48,44 | 19 | 57,50,40,35,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 625 | 125 | 625 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,64,55,52,48,44 | 19 | 57,50,40,35,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 625 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 630 | 125 | 630 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,64,55,52,48,44 | 19 | 57,50,40,35,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 635 | 125 | 635 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,64,55,52,48,44 | 19 | 57,50,40,35,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 635 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 640 | 125 | 640 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,64,55,53,48,44 | 19 | 57,50,40,35,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 645 | 125 | 645 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,64,55,53,48,44 | 19 | 57,50,40,35,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 645 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 650 | 125 | 650 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,64,55,53,48,44 | 19 | 57,50,40,35,29,24 | 55 | 75 | 0.5" Fiberglass | 8 | 650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 655 | 125 | 655 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,64,56,53,48,44 | 19 | 57,50,41,35,30,24 | 55 | 75 | 0.5" Fiberglass | 8 | 655 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 660 | 125 | 660 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,64,56,53,48,44 | 20 | 58,50,41,36,30,24 | 55 | 75 | 0.5" Fiberglass | 8 | 660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 665 | 125 | 665 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,65,56,53,48,44 | 20 | 58,50,41,36,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 665 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 670 | 125 | 670 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,65,56,53,49,44 | 20 | 58,51,41,36,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 675 | 125 | 675 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,65,56,53,49,44 | 20 | 58,51,41,36,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 675 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 680 | 125 | 680 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,65,56,53,49,45 | 20 | 58,51,41,36,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 685 | 125 | 685 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,65,56,54,49,45 | 20 | 58,51,41,36,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 685 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 690 | 125 | 690 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,65,56,54,49,45 | 20 | 58,51,41,36,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 695 | 125 | 695 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,65,56,54,49,45 | 20 | 58,51,41,36,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 695 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 700 | 125 | 700 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,65,57,54,49,45 | 20 | 58,51,41,36,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 705 | 125 | 705 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,57,54,49,45 | 20 | 58,51,41,36,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 705 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 710 | 125 | 710 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,65,57,54,49,45 | 21 | 59,51,41,36,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 715 | 125 | 715 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,57,54,49,45 | 21 | 59,51,41,36,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 715 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 720 | 125 | 720 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,57,54,49,45 | 21 | 59,51,42,37,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 725 | 125 | 725 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,57,54,49,45 | 21 | 59,52,42,37,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 725 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 730 | 125 | 730 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,57,55,49,45 | 21 | 59,52,42,37,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 735 | 125 | 735 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,57,55,49,45 | 21 | 59,52,42,37,30,25 | 55 | 75 | 0.5" Fiberglass | 8 | 735 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 740 | 125 | 740 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,57,55,50,45 | 21 | 59,52,42,37,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 745 | 125 | 745 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,57,55,50,45 | 21 | 59,52,42,37,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 745 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 750 | 125 | 750 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,58,55,50,45 | 21 | 59,52,42,37,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 755 | 125 | 755 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,58,55,50,45 | 21 | 59,52,42,37,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 755 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 760 | 125 | 760 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,58,55,50,45 | 21 | 59,52,42,37,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 765 | 125 | 765 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,58,55,50,46 | 21 | 59,52,42,37,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 765 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 770 | 125 | 770 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,58,55,50,46 | 22 | 60,52,42,37,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 775 | 125 | 775 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,58,55,50,46 | 22 | 60,52,42,37,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 775 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 780 | 125 | 780 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,58,56,50,46 | 22 | 60,52,42,37,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 785 | 125 | 785 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,58,56,50,46 | 22 | 60,53,43,38,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 785 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 790 | 125 | 790 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,58,56,50,46 | 22 | 60,53,43,38,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 795 | 125 | 795 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,58,56,50,46 | 22 | 60,53,43,38,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 795 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 800 | 125 | 800 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,58,56,50,46 | 22 | 60,53,43,38,31,25 | 55 | 75 | 0.5" Fiberglass | 8 | 800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 805 | 125 | 805 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,59,56,50,46 | 22 | 60,53,43,38,31,26 | 55 | 75 | 0.5" Fiberglass | 8 | 805 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 810 | 125 | 810 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,59,56,50,46 | 22 | 60,53,43,38,31,26 | 55 | 75 | 0.5" Fiberglass | 8 | 810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 815 | 125 | 815 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,59,56,51,46 | 22 | 60,53,43,38,31,26 | 55 | 75 | 0.5" Fiberglass | 8 | 815 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 820 | 125 | 820 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,59,56,51,46 | 22 | 60,53,43,38,31,26 | 55 | 75 | 0.5" Fiberglass | 8 | 820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 825 | 125 | 825 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,59,56,51,46 | 22 | 60,53,43,38,31,26 | 55 | 75 | 0.5" Fiberglass | 8 | 825 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 830 | 125 | 830 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,59,56,51,46 | 24 | 61,53,43,38,31,26 | 55 | 75 | 0.5" Fiberglass | 8 | 830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 835 | 125 | 835 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,59,57,51,46 | 24 | 61,53,43,38,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 835 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 840 | 125 | 840 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,59,57,51,46 | 24 | 61,53,43,38,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 845 | 125 | 845 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,59,57,51,46 | 24 | 61,53,43,38,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 845 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 850 | 125 | 850 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,59,57,51,46 | 24 | 61,53,43,38,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 855 | 125 | 855 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,59,57,51,46 | 24 | 61,54,43,38,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 855 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 860 | 125 | 860 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,60,57,51,47 | 24 | 61,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 865 | 125 | 865 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,60,57,51,47 | 24 | 61,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 865 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 870 | 125 | 870 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,60,57,51,47 | 24 | 61,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 875 | 125 | 875 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,60,57,51,47 | 24 | 61,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 875 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 880 | 125 | 880 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,60,57,51,47 | 24 | 61,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 885 | 125 | 885 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,60,57,51,47 | 24 | 61,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 885 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 890 | 125 | 890 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,60,58,51,47 | 24 | 61,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 895 | 125 | 895 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,60,58,51,47 | 25 | 62,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 895 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 900 | 125 | 900 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,60,58,52,47 | 25 | 62,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 905 | 125 | 905 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,60,58,52,47 | 25 | 62,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 905 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 910 | 125 | 910 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,60,58,52,47 | 25 | 62,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 915 | 125 | 915 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,60,58,52,47 | 25 | 62,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 915 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 920 | 125 | 920 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,61,58,52,47 | 25 | 62,54,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 925 | 125 | 925 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,61,58,52,47 | 25 | 62,55,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 925 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 930 | 125 | 930 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,61,58,52,47 | 25 | 62,55,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 935 | 125 | 935 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,61,58,52,47 | 25 | 62,55,44,39,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 935 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 940 | 125 | 940 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,61,58,52,47 | 25 | 62,55,45,40,32,26 | 55 | 75 | 0.5" Fiberglass | 8 | 940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 945 | 125 | 945 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,61,58,52,47 | 25 | 62,55,45,40,33,26 | 55 | 75 | 0.5" Fiberglass | 8 | 945 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 950 | 125 | 950 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,61,59,52,47 | 25 | 62,55,45,40,33,26 | 55 | 75 | 0.5" Fiberglass | 8 | 950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 955 | 125 | 955 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,61,59,52,47 | 25 | 62,55,45,40,33,26 | 55 | 75 | 0.5" Fiberglass | 8 | 955 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 960 | 125 | 960 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,61,59,52,47 | 25 | 62,55,45,40,33,26 | 55 | 75 | 0.5" Fiberglass | 8 | 960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 965 | 125 | 965 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,61,59,52,48 | 26 | 63,55,45,40,33,26 | 55 | 75 | 0.5" Fiberglass | 8 | 965 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 970 | 125 | 970 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,61,59,52,48 | 26 | 63,55,45,40,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 975 | 125 | 975 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,61,59,52,48 | 26 | 63,55,45,40,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 975 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 980 | 125 | 980 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,61,59,52,48 | 26 | 63,55,45,40,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 985 | 125 | 985 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,62,59,52,48 | 26 | 63,55,45,40,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 985 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 990 | 125 | 990 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,62,59,52,48 | 26 | 63,55,45,40,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 995 | 125 | 995 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,62,59,53,48 | 26 | 63,55,45,40,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 995 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1000 | 125 | 1000 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,62,59,53,48 | 26 | 63,56,45,40,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1005 | 125 | 1005 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,62,59,53,48 | 26 | 63,56,45,40,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1005 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1010 | 125 | 1010 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,62,59,53,48 | 26 | 63,56,45,40,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1015 | 125 | 1015 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,62,59,53,48 | 26 | 63,56,45,40,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1015 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1020 | 125 | 1020 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,62,60,53,48 | 26 | 63,56,45,40,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1025 | 125 | 1025 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,62,60,53,48 | 26 | 63,56,45,40,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1025 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1030 | 125 | 1030 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,62,60,53,48 | 26 | 63,56,46,41,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1035 | 125 | 1035 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,71,62,60,53,48 | 26 | 63,56,46,41,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1035 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1040 | 125 | 1040 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,71,62,60,53,48 | 28 | 64,56,46,41,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1045 | 125 | 1045 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,71,62,60,53,48 | 28 | 64,56,46,41,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1045 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1050 | 125 | 1050 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,71,63,60,53,48 | 28 | 64,56,46,41,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1055 | 125 | 1055 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,71,63,60,53,48 | 28 | 64,56,46,41,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1055 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1060 | 125 | 1060 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,71,63,60,53,48 | 28 | 64,56,46,41,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1065 | 125 | 1065 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,71,63,60,53,48 | 28 | 64,56,46,41,33,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1065 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1070 | 125 | 1070 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,72,63,60,53,48 | 28 | 64,56,46,41,34,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1075 | 125 | 1075 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,72,63,60,53,48 | 28 | 64,56,46,41,34,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1075 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1080 | 125 | 1080 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,72,63,60,53,48 | 28 | 64,56,46,41,34,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1085 | 125 | 1085 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,72,63,60,53,49 | 28 | 64,57,46,41,34,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1085 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1090 | 125 | 1090 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,72,63,61,53,49 | 28 | 64,57,46,41,34,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1095 | 125 | 1095 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,72,63,61,53,49 | 28 | 64,57,46,41,34,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1095 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1100 | 125 | 1100 | 1 | 0.25 | 0.75 | 0.01 | 33 | 79,72,63,61,54,49 | 28 | 64,57,46,41,34,27 | 55 | 75 | 0.5" Fiberglass | 8 | 1100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 550 | 210 | 550 | 1 | 0.25 | 0.75 | 0.01 | 16 | 64,58,46,45,44,42 | 11 | 51,44,37,28,23,24 | 55 | 75 | 0.5" Fiberglass | 10 | 550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 555 | 210 | 555 | 1 | 0.25 | 0.75 | 0.01 | 16 | 64,58,47,45,44,42 | 11 | 51,44,37,28,23,24 | 55 | 75 | 0.5" Fiberglass | 10 | 555 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 560 | 210 | 560 | 1 | 0.25 | 0.75 | 0.01 | 16 | 64,58,47,46,45,42 | 11 | 51,44,37,28,23,24 | 55 | 75 | 0.5" Fiberglass | 10 | 560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 565 | 210 | 565 | 1 | 0.25 | 0.75 | 0.01 | 16 | 64,58,47,46,45,42 | 11 | 51,44,37,28,23,24 | 55 | 75 | 0.5" Fiberglass | 10 | 565 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 570 | 210 | 570 | 1 | 0.25 | 0.75 | 0.01 | 16 | 64,58,47,46,45,42 | 12 | 51,45,37,29,23,24 | 55 | 75 | 0.5" Fiberglass | 10 | 570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 575 | 210 | 575 | 1 | 0.25 | 0.75 | 0.01 | 16 | 64,58,47,46,45,42 | 12 | 51,45,37,29,23,24 | 55 | 75 | 0.5" Fiberglass | 10 | 575 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 580 | 210 | 580 | 1 | 0.25 | 0.75 | 0.01 | 16 | 64,58,47,46,45,42 | 12 | 51,45,37,29,23,24 | 55 | 75 | 0.5" Fiberglass | 10 | 580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 585 | 210 | 585 | 1 | 0.25 | 0.75 | 0.01 | 16 | 64,58,47,46,45,42 | 12 | 52,45,37,29,23,24 | 55 | 75 | 0.5" Fiberglass | 10 | 585 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 590 | 210 | 590 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,58,47,46,45,42 | 12 | 52,45,37,29,23,24 | 55 | 75 | 0.5" Fiberglass | 10 | 590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 595 | 210 | 595 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,58,47,46,45,42 | 12 | 52,45,37,29,23,24 | 55 | 75 | 0.5" Fiberglass | 10 | 595 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 600 | 210 | 600 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,58,48,46,45,42 | 12 | 52,45,38,29,23,24 | 55 | 75 | 0.5" Fiberglass | 10 | 600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 605 | 210 | 605 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,58,48,47,45,42 | 12 | 52,45,38,29,24,24 | 55 | 75 | 0.5" Fiberglass | 10 | 605 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 610 | 210 | 610 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,59,48,47,45,42 | 12 | 52,45,38,29,24,24 | 55 | 75 | 0.5" Fiberglass | 10 | 610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 615 | 210 | 615 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,59,48,47,45,42 | 12 | 52,45,38,29,24,24 | 55 | 75 | 0.5" Fiberglass | 10 | 615 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 620 | 210 | 620 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,59,48,47,45,43 | 12 | 52,45,38,29,24,24 | 55 | 75 | 0.5" Fiberglass | 10 | 620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 625 | 210 | 625 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,59,48,47,45,43 | 12 | 52,45,38,30,24,24 | 55 | 75 | 0.5" Fiberglass | 10 | 625 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 630 | 210 | 630 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,59,48,47,46,43 | 12 | 52,45,38,30,24,25 | 55 | 75 | 0.5" Fiberglass | 10 | 630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 635 | 210 | 635 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,59,48,47,46,43 | 13 | 52,46,38,30,24,25 | 55 | 75 | 0.5" Fiberglass | 10 | 635 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 640 | 210 | 640 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,59,48,47,46,43 | 13 | 52,46,38,30,24,25 | 55 | 75 | 0.5" Fiberglass | 10 | 640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 645 | 210 | 645 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,59,48,47,46,43 | 13 | 52,46,38,30,24,25 | 55 | 75 | 0.5" Fiberglass | 10 | 645 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 650 | 210 | 650 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,59,49,47,46,43 | 13 | 53,46,38,30,24,25 | 55 | 75 | 0.5" Fiberglass | 10 | 650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 655 | 210 | 655 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,49,48,46,43 | 13 | 53,46,38,30,24,25 | 55 | 75 | 0.5" Fiberglass | 10 | 655 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 660 | 210 | 660 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,49,48,46,43 | 13 | 53,46,38,30,24,25 | 55 | 75 | 0.5" Fiberglass | 10 | 660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 665 | 210 | 665 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,49,48,46,43 | 13 | 53,46,38,30,24,25 | 55 | 75 | 0.5" Fiberglass | 10 | 665 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 670 | 210 | 670 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,49,48,46,43 | 13 | 53,46,39,30,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 675 | 210 | 675 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,49,48,46,43 | 13 | 53,46,39,30,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 675 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 680 | 210 | 680 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,60,49,48,46,43 | 13 | 53,46,39,30,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 685 | 210 | 685 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,60,49,48,46,43 | 13 | 53,46,39,31,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 685 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 690 | 210 | 690 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,60,49,48,46,43 | 13 | 53,46,39,31,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 695 | 210 | 695 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,60,49,48,46,43 | 13 | 53,46,39,31,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 695 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 700 | 210 | 700 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,60,49,48,46,44 | 13 | 53,46,39,31,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 705 | 210 | 705 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,50,49,46,44 | 13 | 53,46,39,31,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 705 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 710 | 210 | 710 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,50,49,47,44 | 14 | 53,47,39,31,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 715 | 210 | 715 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,50,49,47,44 | 14 | 53,47,39,31,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 715 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 720 | 210 | 720 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,50,49,47,44 | 15 | 54,47,39,31,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 725 | 210 | 725 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,50,49,47,44 | 15 | 54,47,39,31,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 725 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 730 | 210 | 730 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,50,49,47,44 | 15 | 54,47,39,31,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 735 | 210 | 735 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,50,49,47,44 | 15 | 54,47,39,31,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 735 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 740 | 210 | 740 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,50,49,47,44 | 15 | 54,47,39,31,25,25 | 55 | 75 | 0.5" Fiberglass | 10 | 740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 745 | 210 | 745 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,50,49,47,44 | 15 | 54,47,39,31,26,25 | 55 | 75 | 0.5" Fiberglass | 10 | 745 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 750 | 210 | 750 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,50,49,47,44 | 15 | 54,47,40,31,26,25 | 55 | 75 | 0.5" Fiberglass | 10 | 750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 755 | 210 | 755 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,50,49,47,44 | 15 | 54,47,40,32,26,25 | 55 | 75 | 0.5" Fiberglass | 10 | 755 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 760 | 210 | 760 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,50,49,47,44 | 15 | 54,47,40,32,26,25 | 55 | 75 | 0.5" Fiberglass | 10 | 760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 765 | 210 | 765 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,51,50,47,44 | 15 | 54,47,40,32,26,25 | 55 | 75 | 0.5" Fiberglass | 10 | 765 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 770 | 210 | 770 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,51,50,47,44 | 15 | 54,47,40,32,26,26 | 55 | 75 | 0.5" Fiberglass | 10 | 770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 775 | 210 | 775 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,51,50,47,44 | 15 | 54,47,40,32,26,26 | 55 | 75 | 0.5" Fiberglass | 10 | 775 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 780 | 210 | 780 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,51,50,47,44 | 15 | 54,47,40,32,26,26 | 55 | 75 | 0.5" Fiberglass | 10 | 780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 785 | 210 | 785 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,51,50,47,44 | 15 | 54,47,40,32,26,26 | 55 | 75 | 0.5" Fiberglass | 10 | 785 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 790 | 210 | 790 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,51,50,47,45 | 15 | 54,48,40,32,26,26 | 55 | 75 | 0.5" Fiberglass | 10 | 790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 795 | 210 | 795 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,51,50,47,45 | 16 | 55,48,40,32,26,26 | 55 | 75 | 0.5" Fiberglass | 10 | 795 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 800 | 210 | 800 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,51,50,48,45 | 16 | 55,48,40,32,26,26 | 55 | 75 | 0.5" Fiberglass | 10 | 800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 805 | 210 | 805 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,51,50,48,45 | 16 | 55,48,40,32,26,26 | 55 | 75 | 0.5" Fiberglass | 10 | 805 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 810 | 210 | 810 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,51,50,48,45 | 16 | 55,48,40,32,26,26 | 55 | 75 | 0.5" Fiberglass | 10 | 810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 815 | 210 | 815 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,51,50,48,45 | 16 | 55,48,40,32,26,26 | 55 | 75 | 0.5" Fiberglass | 10 | 815 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 820 | 210 | 820 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,51,50,48,45 | 16 | 55,48,40,32,26,26 | 55 | 75 | 0.5" Fiberglass | 10 | 820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 825 | 210 | 825 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,51,51,48,45 | 16 | 55,48,40,32,26,26 | 55 | 75 | 0.5" Fiberglass | 10 | 825 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 830 | 210 | 830 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,52,51,48,45 | 16 | 55,48,40,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 835 | 210 | 835 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,52,51,48,45 | 16 | 55,48,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 835 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 840 | 210 | 840 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,52,51,48,45 | 16 | 55,48,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 845 | 210 | 845 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,52,51,48,45 | 16 | 55,48,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 845 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 850 | 210 | 850 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,52,51,48,45 | 16 | 55,48,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 855 | 210 | 855 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,52,51,48,45 | 16 | 55,48,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 855 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 860 | 210 | 860 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,52,51,48,45 | 16 | 55,48,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 865 | 210 | 865 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,52,51,48,45 | 16 | 55,48,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 865 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 870 | 210 | 870 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,52,51,48,45 | 16 | 55,48,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 875 | 210 | 875 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,52,51,48,45 | 16 | 55,48,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 875 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 880 | 210 | 880 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,52,51,48,45 | 17 | 56,49,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 885 | 210 | 885 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,52,51,48,45 | 17 | 56,49,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 885 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 890 | 210 | 890 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,52,52,48,46 | 17 | 56,49,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 895 | 210 | 895 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,52,52,48,46 | 17 | 56,49,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 895 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 900 | 210 | 900 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,53,52,48,46 | 17 | 56,49,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 905 | 210 | 905 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,53,52,49,46 | 17 | 56,49,41,33,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 905 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 910 | 210 | 910 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,53,52,49,46 | 17 | 56,49,41,34,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 915 | 210 | 915 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,53,52,49,46 | 17 | 56,49,41,34,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 915 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 920 | 210 | 920 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,53,52,49,46 | 17 | 56,49,41,34,27,26 | 55 | 75 | 0.5" Fiberglass | 10 | 920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 925 | 210 | 925 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,53,52,49,46 | 17 | 56,49,41,34,28,26 | 55 | 75 | 0.5" Fiberglass | 10 | 925 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 930 | 210 | 930 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,53,52,49,46 | 17 | 56,49,41,34,28,26 | 55 | 75 | 0.5" Fiberglass | 10 | 930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 935 | 210 | 935 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,53,52,49,46 | 17 | 56,49,42,34,28,26 | 55 | 75 | 0.5" Fiberglass | 10 | 935 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 940 | 210 | 940 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,53,52,49,46 | 17 | 56,49,42,34,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 945 | 210 | 945 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,53,52,49,46 | 17 | 56,49,42,34,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 945 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 950 | 210 | 950 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,53,52,49,46 | 17 | 56,49,42,34,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 955 | 210 | 955 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,53,52,49,46 | 17 | 56,49,42,34,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 955 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 960 | 210 | 960 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,53,53,49,46 | 17 | 56,49,42,34,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 965 | 210 | 965 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,53,53,49,46 | 17 | 56,49,42,34,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 965 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 970 | 210 | 970 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,53,53,49,46 | 19 | 57,49,42,34,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 975 | 210 | 975 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,53,53,49,46 | 19 | 57,49,42,34,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 975 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 980 | 210 | 980 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,54,53,49,46 | 19 | 57,49,42,34,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 985 | 210 | 985 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,54,53,49,46 | 19 | 57,50,42,34,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 985 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 990 | 210 | 990 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,54,53,49,46 | 19 | 57,50,42,34,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 995 | 210 | 995 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,54,53,49,46 | 19 | 57,50,42,35,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 995 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1000 | 210 | 1000 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,54,53,49,46 | 19 | 57,50,42,35,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1005 | 210 | 1005 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,54,53,49,47 | 19 | 57,50,42,35,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1005 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1010 | 210 | 1010 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,54,53,49,47 | 19 | 57,50,42,35,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1015 | 210 | 1015 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,54,53,49,47 | 19 | 57,50,42,35,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1015 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1020 | 210 | 1020 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,54,53,50,47 | 19 | 57,50,42,35,28,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1025 | 210 | 1025 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,54,53,50,47 | 19 | 57,50,42,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1025 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1030 | 210 | 1030 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,54,53,50,47 | 19 | 57,50,42,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1035 | 210 | 1035 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,54,53,50,47 | 19 | 57,50,42,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1035 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1040 | 210 | 1040 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,54,54,50,47 | 19 | 57,50,42,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1045 | 210 | 1045 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,54,54,50,47 | 19 | 57,50,43,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1045 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1050 | 210 | 1050 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,54,54,50,47 | 19 | 57,50,43,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1055 | 210 | 1055 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,54,54,50,47 | 19 | 57,50,43,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1055 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1060 | 210 | 1060 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,55,54,50,47 | 19 | 57,50,43,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1065 | 210 | 1065 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,55,54,50,47 | 19 | 57,50,43,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1065 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1070 | 210 | 1070 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,55,54,50,47 | 19 | 57,50,43,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1075 | 210 | 1075 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,55,54,50,47 | 20 | 58,50,43,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1075 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1080 | 210 | 1080 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,55,54,50,47 | 20 | 58,50,43,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1085 | 210 | 1085 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,54,50,47 | 20 | 58,50,43,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1085 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1090 | 210 | 1090 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,54,50,47 | 20 | 58,50,43,35,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1095 | 210 | 1095 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,54,50,47 | 20 | 58,51,43,36,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1095 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1100 | 210 | 1100 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,54,50,47 | 20 | 58,51,43,36,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1105 | 210 | 1105 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,54,50,47 | 20 | 58,51,43,36,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1105 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1110 | 210 | 1110 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,54,50,47 | 20 | 58,51,43,36,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1115 | 210 | 1115 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,54,50,47 | 20 | 58,51,43,36,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1115 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1120 | 210 | 1120 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,54,50,47 | 20 | 58,51,43,36,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1125 | 210 | 1125 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,55,50,47 | 20 | 58,51,43,36,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1125 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1130 | 210 | 1130 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,55,50,47 | 20 | 58,51,43,36,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1135 | 210 | 1135 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,55,50,48 | 20 | 58,51,43,36,29,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1135 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1140 | 210 | 1140 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,55,50,48 | 20 | 58,51,43,36,30,27 | 55 | 75 | 0.5" Fiberglass | 10 | 1140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1145 | 210 | 1145 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,55,50,48 | 20 | 58,51,43,36,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1145 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1150 | 210 | 1150 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,55,55,51,48 | 20 | 58,51,43,36,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1155 | 210 | 1155 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,56,55,51,48 | 20 | 58,51,43,36,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1155 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1160 | 210 | 1160 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,56,55,51,48 | 20 | 58,51,43,36,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1165 | 210 | 1165 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,56,55,51,48 | 20 | 58,51,44,36,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1165 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1170 | 210 | 1170 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,56,55,51,48 | 20 | 58,51,44,36,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1175 | 210 | 1175 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,56,55,51,48 | 20 | 58,51,44,36,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1175 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1180 | 210 | 1180 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,56,55,51,48 | 20 | 58,51,44,36,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1185 | 210 | 1185 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,56,55,51,48 | 20 | 58,51,44,36,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1185 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1190 | 210 | 1190 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,56,55,51,48 | 21 | 59,51,44,36,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1195 | 210 | 1195 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,56,55,51,48 | 21 | 59,51,44,36,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1195 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1200 | 210 | 1200 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,56,55,51,48 | 21 | 59,51,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1205 | 210 | 1205 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,56,55,51,48 | 21 | 59,51,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1205 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1210 | 210 | 1210 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,56,55,51,48 | 21 | 59,51,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1215 | 210 | 1215 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,56,56,51,48 | 21 | 59,51,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1215 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1220 | 210 | 1220 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,56,56,51,48 | 21 | 59,52,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1225 | 210 | 1225 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,56,56,51,48 | 21 | 59,52,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1225 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1230 | 210 | 1230 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,56,56,51,48 | 21 | 59,52,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1235 | 210 | 1235 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,56,56,51,48 | 21 | 59,52,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1235 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1240 | 210 | 1240 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,56,56,51,48 | 21 | 59,52,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1245 | 210 | 1245 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,56,56,51,48 | 21 | 59,52,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1245 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1250 | 210 | 1250 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,57,56,51,48 | 21 | 59,52,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1255 | 210 | 1255 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,57,56,51,48 | 21 | 59,52,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1255 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1260 | 210 | 1260 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,57,56,51,48 | 21 | 59,52,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1265 | 210 | 1265 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,57,56,51,48 | 21 | 59,52,44,37,30,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1265 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1270 | 210 | 1270 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,57,56,51,48 | 21 | 59,52,44,37,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1275 | 210 | 1275 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,57,56,51,48 | 21 | 59,52,44,37,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1275 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1280 | 210 | 1280 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,57,56,51,49 | 21 | 59,52,44,37,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1285 | 210 | 1285 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,57,56,51,49 | 21 | 59,52,44,37,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1285 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1290 | 210 | 1290 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,57,56,51,49 | 21 | 59,52,44,37,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1295 | 210 | 1295 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,57,56,52,49 | 21 | 59,52,44,37,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1295 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1300 | 210 | 1300 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,57,56,52,49 | 21 | 59,52,45,37,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1305 | 210 | 1305 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,57,56,52,49 | 21 | 59,52,45,37,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1305 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1310 | 210 | 1310 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,57,57,52,49 | 21 | 59,52,45,37,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1315 | 210 | 1315 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,57,57,52,49 | 21 | 59,52,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1315 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1320 | 210 | 1320 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,57,57,52,49 | 22 | 60,52,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1325 | 210 | 1325 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,57,57,52,49 | 22 | 60,52,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1325 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1330 | 210 | 1330 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,57,57,52,49 | 22 | 60,52,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1335 | 210 | 1335 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,57,57,52,49 | 22 | 60,52,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1335 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1340 | 210 | 1340 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,57,57,52,49 | 22 | 60,52,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1345 | 210 | 1345 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,57,57,52,49 | 22 | 60,52,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1345 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1350 | 210 | 1350 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,57,57,52,49 | 22 | 60,52,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1355 | 210 | 1355 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,57,52,49 | 22 | 60,52,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1355 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1360 | 210 | 1360 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,57,52,49 | 22 | 60,53,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1365 | 210 | 1365 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,57,52,49 | 22 | 60,53,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1365 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1370 | 210 | 1370 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,57,52,49 | 22 | 60,53,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1375 | 210 | 1375 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,57,52,49 | 22 | 60,53,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1375 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1380 | 210 | 1380 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,57,52,49 | 22 | 60,53,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1385 | 210 | 1385 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,57,52,49 | 22 | 60,53,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1385 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1390 | 210 | 1390 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,57,52,49 | 22 | 60,53,45,38,31,28 | 55 | 75 | 0.5" Fiberglass | 10 | 1390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1395 | 210 | 1395 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,57,52,49 | 22 | 60,53,45,38,31,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1395 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1400 | 210 | 1400 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,57,52,49 | 22 | 60,53,45,38,31,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1405 | 210 | 1405 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,57,52,49 | 22 | 60,53,45,38,31,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1405 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1410 | 210 | 1410 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,57,52,49 | 22 | 60,53,45,38,31,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1415 | 210 | 1415 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,58,52,49 | 22 | 60,53,45,38,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1415 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1420 | 210 | 1420 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,58,52,49 | 22 | 60,53,45,38,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1425 | 210 | 1425 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,58,52,49 | 22 | 60,53,45,38,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1425 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1430 | 210 | 1430 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,58,58,52,49 | 22 | 60,53,45,38,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1435 | 210 | 1435 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,58,58,52,49 | 22 | 60,53,45,38,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1435 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1440 | 210 | 1440 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,58,58,52,49 | 22 | 60,53,45,38,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1445 | 210 | 1445 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,58,58,52,50 | 22 | 60,53,45,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1445 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1450 | 210 | 1450 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,58,58,52,50 | 22 | 60,53,45,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1455 | 210 | 1455 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,58,58,52,50 | 22 | 60,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1455 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1460 | 210 | 1460 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,58,58,53,50 | 24 | 61,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1465 | 210 | 1465 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,58,58,53,50 | 24 | 61,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1465 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1470 | 210 | 1470 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,58,58,53,50 | 24 | 61,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1475 | 210 | 1475 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,58,53,50 | 24 | 61,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1475 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1480 | 210 | 1480 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,58,53,50 | 24 | 61,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1485 | 210 | 1485 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,58,53,50 | 24 | 61,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1485 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1490 | 210 | 1490 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,58,53,50 | 24 | 61,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1495 | 210 | 1495 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,58,53,50 | 24 | 61,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1495 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1500 | 210 | 1500 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,58,53,50 | 24 | 61,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1505 | 210 | 1505 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,58,53,50 | 24 | 61,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1505 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1510 | 210 | 1510 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,58,53,50 | 24 | 61,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1515 | 210 | 1515 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,58,53,50 | 24 | 61,53,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1515 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1520 | 210 | 1520 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,58,53,50 | 24 | 61,54,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1525 | 210 | 1525 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,58,53,50 | 24 | 61,54,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1525 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1530 | 210 | 1530 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1535 | 210 | 1535 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1535 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1540 | 210 | 1540 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1545 | 210 | 1545 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1545 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1550 | 210 | 1550 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1555 | 210 | 1555 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1555 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1560 | 210 | 1560 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1565 | 210 | 1565 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1565 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1570 | 210 | 1570 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,39,32,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1575 | 210 | 1575 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,39,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1575 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1580 | 210 | 1580 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,39,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1585 | 210 | 1585 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1585 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1590 | 210 | 1590 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,59,53,50 | 24 | 61,54,46,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1595 | 210 | 1595 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,68,59,59,53,50 | 24 | 61,54,46,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1595 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1600 | 210 | 1600 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,68,60,59,53,50 | 24 | 61,54,46,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1605 | 210 | 1605 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,68,60,59,53,50 | 24 | 61,54,46,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1605 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1610 | 210 | 1610 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,68,60,59,53,50 | 24 | 61,54,46,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1615 | 210 | 1615 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,68,60,59,53,50 | 25 | 62,54,46,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1615 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1620 | 210 | 1620 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,68,60,59,53,50 | 25 | 62,54,46,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1625 | 210 | 1625 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,68,60,59,53,50 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1625 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1630 | 210 | 1630 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,68,60,59,53,50 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1635 | 210 | 1635 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,59,53,51 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1635 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1640 | 210 | 1640 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,59,53,51 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1645 | 210 | 1645 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,59,53,51 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1645 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1650 | 210 | 1650 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1655 | 210 | 1655 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1655 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1660 | 210 | 1660 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1665 | 210 | 1665 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1665 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1670 | 210 | 1670 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1675 | 210 | 1675 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1675 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1680 | 210 | 1680 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1685 | 210 | 1685 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,54,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1685 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1690 | 210 | 1690 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,55,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1695 | 210 | 1695 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,55,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1695 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1700 | 210 | 1700 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,55,47,40,33,29 | 55 | 75 | 0.5" Fiberglass | 10 | 1700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1705 | 210 | 1705 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,55,47,40,33,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1705 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1710 | 210 | 1710 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,55,47,40,33,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1715 | 210 | 1715 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,55,47,40,33,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1715 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1720 | 210 | 1720 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,55,47,40,33,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1725 | 210 | 1725 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,55,47,40,33,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1725 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1730 | 210 | 1730 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,60,54,51 | 25 | 62,55,47,40,33,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1735 | 210 | 1735 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,61,60,54,51 | 25 | 62,55,47,40,33,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1735 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1740 | 210 | 1740 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,61,60,54,51 | 25 | 62,55,47,41,33,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1745 | 210 | 1745 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,61,60,54,51 | 25 | 62,55,47,41,33,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1745 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1750 | 210 | 1750 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,61,60,54,51 | 25 | 62,55,47,41,34,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1755 | 210 | 1755 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,61,60,54,51 | 25 | 62,55,47,41,34,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1755 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1760 | 210 | 1760 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,61,60,54,51 | 25 | 62,55,47,41,34,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1765 | 210 | 1765 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,61,60,54,51 | 25 | 62,55,47,41,34,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1765 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1770 | 210 | 1770 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,61,60,54,51 | 25 | 62,55,47,41,34,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1775 | 210 | 1775 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,69,61,60,54,51 | 25 | 62,55,47,41,34,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1775 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1780 | 210 | 1780 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,69,61,60,54,51 | 25 | 62,55,47,41,34,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1785 | 210 | 1785 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,69,61,61,54,51 | 26 | 63,55,47,41,34,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1785 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1790 | 210 | 1790 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,69,61,61,54,51 | 26 | 63,55,47,41,34,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1795 | 210 | 1795 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,69,61,61,54,51 | 26 | 63,55,47,41,34,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1795 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1800 | 210 | 1800 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,69,61,61,54,51 | 26 | 63,55,47,41,34,30 | 55 | 75 | 0.5" Fiberglass | 10 | 1800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 900 | 300 | 900 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,52,49,47,45 | 15 | 52,45,42,35,27,26 | 55 | 75 | 0.5" Fiberglass | 12 | 900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 905 | 300 | 905 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,52,49,47,45 | 15 | 52,45,42,35,27,26 | 55 | 75 | 0.5" Fiberglass | 12 | 905 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 910 | 300 | 910 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,52,49,47,45 | 15 | 52,45,42,35,27,26 | 55 | 75 | 0.5" Fiberglass | 12 | 910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 915 | 300 | 915 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,52,49,47,45 | 15 | 52,45,42,35,27,26 | 55 | 75 | 0.5" Fiberglass | 12 | 915 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 920 | 300 | 920 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,52,49,47,45 | 15 | 52,45,42,35,27,26 | 55 | 75 | 0.5" Fiberglass | 12 | 920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 925 | 300 | 925 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,52,49,47,45 | 15 | 53,45,42,35,27,26 | 55 | 75 | 0.5" Fiberglass | 12 | 925 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 930 | 300 | 930 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,52,49,47,45 | 15 | 53,45,42,35,27,26 | 55 | 75 | 0.5" Fiberglass | 12 | 930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 935 | 300 | 935 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,52,49,47,45 | 15 | 53,45,42,35,27,27 | 55 | 75 | 0.5" Fiberglass | 12 | 935 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 940 | 300 | 940 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,52,50,47,45 | 15 | 53,45,42,35,27,27 | 55 | 75 | 0.5" Fiberglass | 12 | 940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 945 | 300 | 945 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,52,50,48,46 | 15 | 53,45,42,35,27,27 | 55 | 75 | 0.5" Fiberglass | 12 | 945 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 950 | 300 | 950 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,52,50,48,46 | 15 | 53,45,42,35,27,27 | 55 | 75 | 0.5" Fiberglass | 12 | 950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 955 | 300 | 955 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,52,50,48,46 | 15 | 53,45,42,35,27,27 | 55 | 75 | 0.5" Fiberglass | 12 | 955 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 960 | 300 | 960 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,52,50,48,46 | 15 | 53,45,42,35,27,27 | 55 | 75 | 0.5" Fiberglass | 12 | 960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 965 | 300 | 965 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,52,50,48,46 | 15 | 53,46,42,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 965 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 970 | 300 | 970 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,53,50,48,46 | 15 | 53,46,42,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 975 | 300 | 975 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,53,50,48,46 | 15 | 53,46,42,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 975 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 980 | 300 | 980 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,53,50,48,46 | 15 | 53,46,42,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 985 | 300 | 985 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,53,50,48,46 | 15 | 53,46,42,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 985 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 990 | 300 | 990 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,53,50,48,46 | 15 | 53,46,42,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 995 | 300 | 995 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,53,50,48,46 | 16 | 53,46,43,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 995 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1000 | 300 | 1000 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,53,50,48,46 | 16 | 53,46,43,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 1000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1005 | 300 | 1005 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,53,50,48,46 | 16 | 53,46,43,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 1005 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1010 | 300 | 1010 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,53,50,48,46 | 16 | 53,46,43,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 1010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1015 | 300 | 1015 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,53,50,48,46 | 16 | 53,46,43,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 1015 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1020 | 300 | 1020 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,53,50,48,46 | 16 | 53,46,43,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 1020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1025 | 300 | 1025 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,53,50,48,46 | 16 | 54,46,43,36,28,27 | 55 | 75 | 0.5" Fiberglass | 12 | 1025 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1030 | 300 | 1030 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,53,50,48,46 | 16 | 54,46,43,36,28,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1035 | 300 | 1035 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,53,51,48,46 | 16 | 54,46,43,36,28,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1035 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1040 | 300 | 1040 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,53,51,48,46 | 16 | 54,46,43,36,28,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1045 | 300 | 1045 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,53,51,48,46 | 16 | 54,46,43,36,28,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1045 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1050 | 300 | 1050 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,53,51,48,46 | 16 | 54,46,43,36,28,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1055 | 300 | 1055 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,53,51,48,46 | 16 | 54,46,43,36,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1055 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1060 | 300 | 1060 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,54,51,48,46 | 16 | 54,46,43,36,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1065 | 300 | 1065 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,54,51,48,46 | 16 | 54,46,43,36,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1065 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1070 | 300 | 1070 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,54,51,48,46 | 16 | 54,46,43,36,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1075 | 300 | 1075 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,54,51,49,46 | 16 | 54,46,43,36,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1075 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1080 | 300 | 1080 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 16 | 54,46,43,37,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1085 | 300 | 1085 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 16 | 54,46,43,37,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1085 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1090 | 300 | 1090 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 16 | 54,46,43,37,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1095 | 300 | 1095 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 18 | 54,46,44,37,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1095 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1100 | 300 | 1100 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 18 | 54,47,44,37,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1105 | 300 | 1105 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 18 | 54,47,44,37,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1105 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1110 | 300 | 1110 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 18 | 54,47,44,37,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1115 | 300 | 1115 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 18 | 54,47,44,37,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1115 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1120 | 300 | 1120 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 18 | 54,47,44,37,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1125 | 300 | 1125 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 18 | 54,47,44,37,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1125 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1130 | 300 | 1130 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 18 | 54,47,44,37,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1135 | 300 | 1135 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 18 | 54,47,44,37,29,28 | 55 | 75 | 0.5" Fiberglass | 12 | 1135 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1140 | 300 | 1140 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,51,49,47 | 18 | 55,47,44,37,29,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1145 | 300 | 1145 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,52,49,47 | 18 | 55,47,44,37,29,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1145 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1150 | 300 | 1150 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,52,49,47 | 18 | 55,47,44,37,29,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1155 | 300 | 1155 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,54,52,49,47 | 18 | 55,47,44,37,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1155 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1160 | 300 | 1160 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,55,52,49,47 | 18 | 55,47,44,37,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1165 | 300 | 1165 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,55,52,49,47 | 18 | 55,47,44,37,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1165 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1170 | 300 | 1170 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,55,52,49,47 | 18 | 55,47,44,37,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1175 | 300 | 1175 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,55,52,49,47 | 18 | 55,47,44,37,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1175 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1180 | 300 | 1180 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,55,52,49,47 | 18 | 55,47,44,37,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1185 | 300 | 1185 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,55,52,49,47 | 18 | 55,47,44,37,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1185 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1190 | 300 | 1190 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,55,52,49,47 | 18 | 55,47,44,37,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1195 | 300 | 1195 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,55,52,49,47 | 18 | 55,47,44,37,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1195 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1200 | 300 | 1200 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,55,52,49,47 | 18 | 55,47,44,37,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1205 | 300 | 1205 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,55,52,49,47 | 18 | 55,47,44,37,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1205 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1210 | 300 | 1210 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,55,52,49,47 | 19 | 55,47,45,38,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1215 | 300 | 1215 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,55,52,49,47 | 19 | 55,47,45,38,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1215 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1220 | 300 | 1220 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,55,52,50,47 | 19 | 55,47,45,38,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1225 | 300 | 1225 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,55,52,50,47 | 19 | 55,47,45,38,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1225 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1230 | 300 | 1230 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,55,52,50,47 | 19 | 55,47,45,38,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1235 | 300 | 1235 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,55,52,50,48 | 19 | 55,47,45,38,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1235 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1240 | 300 | 1240 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,55,52,50,48 | 19 | 55,47,45,38,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1245 | 300 | 1245 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,55,52,50,48 | 19 | 55,48,45,38,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1245 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1250 | 300 | 1250 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,55,52,50,48 | 19 | 55,48,45,38,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1255 | 300 | 1255 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,55,52,50,48 | 19 | 55,48,45,38,30,29 | 55 | 75 | 0.5" Fiberglass | 12 | 1255 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1260 | 300 | 1260 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,55,53,50,48 | 19 | 55,48,45,38,30,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1265 | 300 | 1265 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1265 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1270 | 300 | 1270 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1275 | 300 | 1275 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1275 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1280 | 300 | 1280 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1285 | 300 | 1285 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1285 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1290 | 300 | 1290 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1295 | 300 | 1295 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1295 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1300 | 300 | 1300 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1305 | 300 | 1305 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1305 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1310 | 300 | 1310 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1315 | 300 | 1315 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1315 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1320 | 300 | 1320 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1325 | 300 | 1325 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 19 | 56,48,45,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1325 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1330 | 300 | 1330 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 20 | 56,48,46,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1335 | 300 | 1335 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 20 | 56,48,46,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1335 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1340 | 300 | 1340 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 20 | 56,48,46,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1345 | 300 | 1345 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 20 | 56,48,46,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1345 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1350 | 300 | 1350 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 20 | 56,48,46,38,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1355 | 300 | 1355 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 20 | 56,48,46,39,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1355 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1360 | 300 | 1360 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 20 | 56,48,46,39,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1365 | 300 | 1365 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,56,53,50,48 | 20 | 56,48,46,39,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1365 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1370 | 300 | 1370 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,56,53,50,48 | 20 | 56,48,46,39,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1375 | 300 | 1375 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,56,53,50,48 | 20 | 56,48,46,39,31,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1375 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1380 | 300 | 1380 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,57,53,50,48 | 20 | 56,48,46,39,32,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1385 | 300 | 1385 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,53,51,48 | 20 | 56,48,46,39,32,30 | 55 | 75 | 0.5" Fiberglass | 12 | 1385 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1390 | 300 | 1390 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,48 | 20 | 56,48,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1395 | 300 | 1395 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,48 | 20 | 56,48,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1395 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1400 | 300 | 1400 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,48 | 20 | 56,48,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1405 | 300 | 1405 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,48 | 20 | 57,48,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1405 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1410 | 300 | 1410 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,48 | 20 | 57,48,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1415 | 300 | 1415 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 20 | 57,49,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1415 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1420 | 300 | 1420 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 20 | 57,49,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1425 | 300 | 1425 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 20 | 57,49,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1425 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1430 | 300 | 1430 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 20 | 57,49,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1435 | 300 | 1435 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 20 | 57,49,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1435 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1440 | 300 | 1440 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 20 | 57,49,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1445 | 300 | 1445 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 20 | 57,49,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1445 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1450 | 300 | 1450 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 20 | 57,49,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1455 | 300 | 1455 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 20 | 57,49,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1455 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1460 | 300 | 1460 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 20 | 57,49,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1465 | 300 | 1465 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 20 | 57,49,46,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1465 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1470 | 300 | 1470 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 21 | 57,49,47,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1475 | 300 | 1475 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 21 | 57,49,47,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1475 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1480 | 300 | 1480 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 21 | 57,49,47,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1485 | 300 | 1485 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 21 | 57,49,47,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1485 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1490 | 300 | 1490 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 21 | 57,49,47,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1495 | 300 | 1495 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 21 | 57,49,47,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1495 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1500 | 300 | 1500 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 21 | 57,49,47,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1505 | 300 | 1505 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,57,54,51,49 | 21 | 57,49,47,39,32,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1505 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1510 | 300 | 1510 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,58,54,51,49 | 21 | 57,49,47,39,33,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1515 | 300 | 1515 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,58,54,51,49 | 21 | 57,49,47,40,33,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1515 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1520 | 300 | 1520 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,58,54,51,49 | 21 | 57,49,47,40,33,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1525 | 300 | 1525 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,58,54,51,49 | 21 | 57,49,47,40,33,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1525 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1530 | 300 | 1530 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,58,54,51,49 | 21 | 57,49,47,40,33,31 | 55 | 75 | 0.5" Fiberglass | 12 | 1530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1535 | 300 | 1535 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,58,55,51,49 | 21 | 57,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1535 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1540 | 300 | 1540 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,51,49 | 21 | 57,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1545 | 300 | 1545 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,51,49 | 21 | 57,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1545 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1550 | 300 | 1550 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,51,49 | 21 | 57,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1555 | 300 | 1555 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,51,49 | 21 | 57,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1555 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1560 | 300 | 1560 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,51,49 | 21 | 58,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1565 | 300 | 1565 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,51,49 | 21 | 58,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1565 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1570 | 300 | 1570 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,51,49 | 21 | 58,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1575 | 300 | 1575 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,52,49 | 21 | 58,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1575 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1580 | 300 | 1580 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,52,49 | 21 | 58,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1585 | 300 | 1585 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,52,49 | 21 | 58,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1585 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1590 | 300 | 1590 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,52,49 | 21 | 58,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1595 | 300 | 1595 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,52,49 | 21 | 58,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1595 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1600 | 300 | 1600 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,58,55,52,49 | 21 | 58,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1605 | 300 | 1605 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,58,55,52,49 | 21 | 58,49,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1605 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1610 | 300 | 1610 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,58,55,52,49 | 21 | 58,50,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1615 | 300 | 1615 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,58,55,52,49 | 21 | 58,50,47,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1615 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1620 | 300 | 1620 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,58,55,52,50 | 22 | 58,50,48,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1625 | 300 | 1625 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,58,55,52,50 | 22 | 58,50,48,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1625 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1630 | 300 | 1630 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,58,55,52,50 | 22 | 58,50,48,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1635 | 300 | 1635 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,58,55,52,50 | 22 | 58,50,48,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1635 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1640 | 300 | 1640 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,58,55,52,50 | 22 | 58,50,48,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1645 | 300 | 1645 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,58,55,52,50 | 22 | 58,50,48,40,33,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1645 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1650 | 300 | 1650 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,55,52,50 | 22 | 58,50,48,40,34,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1655 | 300 | 1655 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,55,52,50 | 22 | 58,50,48,40,34,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1655 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1660 | 300 | 1660 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,55,52,50 | 22 | 58,50,48,40,34,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1665 | 300 | 1665 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,55,52,50 | 22 | 58,50,48,40,34,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1665 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1670 | 300 | 1670 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,55,52,50 | 22 | 58,50,48,40,34,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1675 | 300 | 1675 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,55,52,50 | 22 | 58,50,48,40,34,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1675 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1680 | 300 | 1680 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,55,52,50 | 22 | 58,50,48,40,34,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1685 | 300 | 1685 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,55,52,50 | 22 | 58,50,48,40,34,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1685 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1690 | 300 | 1690 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,56,52,50 | 22 | 58,50,48,40,34,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1695 | 300 | 1695 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,56,52,50 | 22 | 58,50,48,41,34,32 | 55 | 75 | 0.5" Fiberglass | 12 | 1695 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1700 | 300 | 1700 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,56,52,50 | 22 | 58,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1705 | 300 | 1705 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,56,52,50 | 22 | 58,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1705 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1710 | 300 | 1710 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,56,52,50 | 22 | 58,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1715 | 300 | 1715 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,56,52,50 | 22 | 58,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1715 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1720 | 300 | 1720 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,56,52,50 | 22 | 58,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1725 | 300 | 1725 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,56,52,50 | 22 | 58,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1725 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1730 | 300 | 1730 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,59,56,52,50 | 22 | 58,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1735 | 300 | 1735 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,52,50 | 22 | 59,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1735 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1740 | 300 | 1740 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,52,50 | 22 | 59,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1745 | 300 | 1745 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,52,50 | 22 | 59,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1745 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1750 | 300 | 1750 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,52,50 | 22 | 59,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1755 | 300 | 1755 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,52,50 | 22 | 59,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1755 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1760 | 300 | 1760 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,52,50 | 22 | 59,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1765 | 300 | 1765 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,52,50 | 22 | 59,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1765 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1770 | 300 | 1770 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,52,50 | 22 | 59,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1775 | 300 | 1775 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,52,50 | 22 | 59,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1775 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1780 | 300 | 1780 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,52,50 | 22 | 59,50,48,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1785 | 300 | 1785 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,52,50 | 23 | 59,50,49,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1785 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1790 | 300 | 1790 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,53,50 | 23 | 59,50,49,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1795 | 300 | 1795 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,59,56,53,50 | 23 | 59,50,49,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1795 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1800 | 300 | 1800 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,50 | 23 | 59,50,49,41,34,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1805 | 300 | 1805 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,50 | 23 | 59,50,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1805 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1810 | 300 | 1810 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,50 | 23 | 59,50,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1815 | 300 | 1815 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,50 | 23 | 59,50,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1815 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1820 | 300 | 1820 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,50 | 23 | 59,50,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1825 | 300 | 1825 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,50 | 23 | 59,50,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1825 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1830 | 300 | 1830 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,50 | 23 | 59,51,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1835 | 300 | 1835 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,50 | 23 | 59,51,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1835 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1840 | 300 | 1840 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,50 | 23 | 59,51,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1845 | 300 | 1845 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,50 | 23 | 59,51,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1845 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1850 | 300 | 1850 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,50 | 23 | 59,51,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1855 | 300 | 1855 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,51 | 23 | 59,51,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1855 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1860 | 300 | 1860 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,60,56,53,51 | 23 | 59,51,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1865 | 300 | 1865 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 59,51,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1865 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1870 | 300 | 1870 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 59,51,49,41,35,33 | 55 | 75 | 0.5" Fiberglass | 12 | 1870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1875 | 300 | 1875 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 59,51,49,41,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1875 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1880 | 300 | 1880 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 59,51,49,41,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1885 | 300 | 1885 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 59,51,49,41,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1885 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1890 | 300 | 1890 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 59,51,49,41,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1895 | 300 | 1895 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 59,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1895 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1900 | 300 | 1900 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 59,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1905 | 300 | 1905 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 59,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1905 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1910 | 300 | 1910 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 59,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1915 | 300 | 1915 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 59,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1915 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1920 | 576 | 1920 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 59,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1925 | 300 | 1925 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 60,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1925 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1930 | 300 | 1930 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 60,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1935 | 300 | 1935 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 60,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1935 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1940 | 300 | 1940 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 60,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1945 | 300 | 1945 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 60,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1945 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1950 | 300 | 1950 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,60,57,53,51 | 23 | 60,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1955 | 300 | 1955 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,60,57,53,51 | 23 | 60,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1955 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1960 | 300 | 1960 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,60,57,53,51 | 23 | 60,51,49,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1965 | 590 | 1965 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,60,57,53,51 | 24 | 60,51,50,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1965 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1970 | 300 | 1970 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,57,53,51 | 24 | 60,51,50,42,35,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1975 | 300 | 1975 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,57,53,51 | 24 | 60,51,50,42,36,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1975 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1980 | 300 | 1980 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,57,53,51 | 24 | 60,51,50,42,36,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1990 | 300 | 1990 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,57,53,51 | 24 | 60,51,50,42,36,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1995 | 300 | 1995 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,57,53,51 | 24 | 60,51,50,42,36,34 | 55 | 75 | 0.5" Fiberglass | 12 | 1995 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2000 | 300 | 2000 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,57,53,51 | 24 | 60,51,50,42,36,34 | 55 | 75 | 0.5" Fiberglass | 12 | 2000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2010 | 300 | 2010 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,57,53,51 | 24 | 60,51,50,42,36,34 | 55 | 75 | 0.5" Fiberglass | 12 | 2010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2020 | 300 | 2020 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,57,53,51 | 24 | 60,51,50,42,36,34 | 55 | 75 | 0.5" Fiberglass | 12 | 2020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2030 | 300 | 2030 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,57,54,51 | 24 | 60,51,50,42,36,34 | 55 | 75 | 0.5" Fiberglass | 12 | 2030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2040 | 300 | 2040 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,57,54,51 | 24 | 60,51,50,42,36,34 | 55 | 75 | 0.5" Fiberglass | 12 | 2040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2050 | 300 | 2050 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,57,54,51 | 24 | 60,51,50,42,36,34 | 55 | 75 | 0.5" Fiberglass | 12 | 2050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2060 | 300 | 2060 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,58,54,51 | 24 | 60,51,50,42,36,34 | 55 | 75 | 0.5" Fiberglass | 12 | 2060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2070 | 300 | 2070 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,58,54,51 | 24 | 60,51,50,42,36,34 | 55 | 75 | 0.5" Fiberglass | 12 | 2070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2080 | 300 | 2080 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,58,54,51 | 24 | 60,52,50,42,36,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2090 | 300 | 2090 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,58,54,51 | 24 | 60,52,50,42,36,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2100 | 300 | 2100 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,58,54,51 | 24 | 60,52,50,42,36,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2110 | 300 | 2110 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,58,54,51 | 24 | 60,52,50,42,36,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2120 | 300 | 2120 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,58,54,51 | 24 | 60,52,50,43,36,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2130 | 300 | 2130 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,58,54,52 | 24 | 60,52,50,43,36,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2140 | 300 | 2140 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,58,54,52 | 24 | 61,52,50,43,36,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2150 | 300 | 2150 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,62,58,54,52 | 24 | 61,52,50,43,36,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2160 | 300 | 2160 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,62,58,54,52 | 24 | 61,52,50,43,37,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2170 | 300 | 2170 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,62,58,54,52 | 25 | 61,52,51,43,37,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2180 | 300 | 2180 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,62,58,54,52 | 25 | 61,52,51,43,37,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2190 | 300 | 2190 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,62,58,54,52 | 25 | 61,52,51,43,37,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2200 | 300 | 2200 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,58,54,52 | 25 | 61,52,51,43,37,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2120 | 300 | 2210 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,61,58,54,51 | 24 | 60,52,50,43,36,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2220 | 666 | 2220 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,58,54,52 | 25 | 61,52,51,43,37,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2230 | 300 | 2230 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,58,54,52 | 25 | 61,52,51,43,37,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2240 | 300 | 2240 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,58,54,52 | 25 | 61,52,51,43,37,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2250 | 300 | 2250 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,58,54,52 | 25 | 61,52,51,43,37,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2260 | 300 | 2260 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,58,54,52 | 25 | 61,52,51,43,37,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2270 | 300 | 2270 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,59,54,52 | 25 | 61,52,51,43,37,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2280 | 300 | 2280 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,59,54,52 | 25 | 61,52,51,43,37,35 | 55 | 75 | 0.5" Fiberglass | 12 | 2280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2290 | 300 | 2290 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,59,54,52 | 25 | 61,52,51,43,37,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2300 | 300 | 2300 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,59,54,52 | 25 | 61,52,51,43,37,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2310 | 300 | 2310 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,59,55,52 | 25 | 61,52,51,43,37,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2320 | 300 | 2320 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,59,55,52 | 25 | 61,52,51,43,37,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2330 | 300 | 2330 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,59,55,52 | 25 | 61,52,51,43,37,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2340 | 300 | 2340 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,62,59,55,52 | 25 | 61,52,51,43,37,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2350 | 300 | 2350 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,52 | 25 | 61,52,51,43,37,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2360 | 300 | 2360 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,52 | 25 | 61,53,51,43,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2370 | 300 | 2370 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,52 | 25 | 61,53,51,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2380 | 300 | 2380 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,52 | 25 | 62,53,51,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2390 | 300 | 2390 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,52 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2400 | 300 | 2400 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,52 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2410 | 300 | 2410 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,52 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2420 | 300 | 2420 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,52 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2430 | 300 | 2430 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,53 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2440 | 300 | 2440 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,53 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2450 | 300 | 2450 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,53 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2460 | 300 | 2460 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,53 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2470 | 300 | 2470 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,63,59,55,53 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2480 | 300 | 2480 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,63,59,55,53 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2490 | 300 | 2490 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,63,59,55,53 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2500 | 300 | 2500 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,63,60,55,53 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2510 | 300 | 2510 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,63,60,55,53 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2520 | 756 | 2520 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,63,60,55,53 | 26 | 62,53,52,44,38,36 | 55 | 75 | 0.5" Fiberglass | 12 | 2520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2530 | 300 | 2530 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,63,60,55,53 | 26 | 62,53,52,44,38,37 | 55 | 75 | 0.5" Fiberglass | 12 | 2530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2540 | 300 | 2540 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,63,60,55,53 | 26 | 62,53,52,44,38,37 | 55 | 75 | 0.5" Fiberglass | 12 | 2540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2550 | 300 | 2550 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,63,60,55,53 | 26 | 62,53,52,44,38,37 | 55 | 75 | 0.5" Fiberglass | 12 | 2550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2560 | 300 | 2560 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,63,60,55,53 | 26 | 62,53,52,44,38,37 | 55 | 75 | 0.5" Fiberglass | 12 | 2560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2570 | 300 | 2570 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,64,60,55,53 | 26 | 62,53,52,44,38,37 | 55 | 75 | 0.5" Fiberglass | 12 | 2570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2580 | 300 | 2580 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,64,60,55,53 | 26 | 62,53,52,44,39,37 | 55 | 75 | 0.5" Fiberglass | 12 | 2580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2590 | 300 | 2590 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,64,60,55,53 | 26 | 62,53,52,44,39,37 | 55 | 75 | 0.5" Fiberglass | 12 | 2590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2600 | 300 | 2600 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,64,60,55,53 | 26 | 62,53,52,44,39,37 | 55 | 75 | 0.5" Fiberglass | 12 | 2600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1000 | 430 | 1000 | 1 | 0.25 | 0.75 | 0.01 | 11 | 62,55,50,48,47,45 | 12 | 51,45,37,30,25,25 | 55 | 75 | 0.5" Fiberglass | 14 | 1000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1005 | 430 | 1005 | 1 | 0.25 | 0.75 | 0.01 | 11 | 62,55,50,48,47,45 | 12 | 51,45,37,30,25,25 | 55 | 75 | 0.5" Fiberglass | 14 | 1005 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1010 | 430 | 1010 | 1 | 0.25 | 0.75 | 0.01 | 11 | 62,55,50,48,47,45 | 12 | 51,45,37,30,25,25 | 55 | 75 | 0.5" Fiberglass | 14 | 1010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1015 | 430 | 1015 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,50,48,47,45 | 12 | 51,45,37,30,25,25 | 55 | 75 | 0.5" Fiberglass | 14 | 1015 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1020 | 430 | 1020 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,50,48,47,45 | 12 | 51,45,37,30,25,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1025 | 430 | 1025 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,50,48,47,45 | 12 | 51,45,37,30,25,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1025 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1030 | 430 | 1030 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,50,48,47,45 | 12 | 51,45,37,30,25,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1035 | 430 | 1035 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,50,48,47,45 | 12 | 51,45,37,30,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1035 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1040 | 430 | 1040 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,50,48,47,45 | 12 | 51,45,37,30,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1045 | 430 | 1045 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,50,48,47,45 | 12 | 51,45,37,30,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1045 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1050 | 430 | 1050 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,50,48,47,45 | 12 | 51,45,37,30,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1055 | 430 | 1055 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,50,49,47,45 | 12 | 51,45,37,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1055 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1060 | 430 | 1060 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,50,49,47,45 | 12 | 51,45,37,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1065 | 430 | 1065 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,50,49,47,45 | 12 | 51,45,37,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1065 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1070 | 430 | 1070 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,47,45 | 12 | 51,45,38,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1075 | 430 | 1075 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,47,45 | 12 | 51,45,38,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1075 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1080 | 430 | 1080 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,47,45 | 12 | 51,45,38,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1085 | 430 | 1085 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,47,45 | 12 | 51,45,38,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1085 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1090 | 430 | 1090 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,47,45 | 12 | 51,45,38,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1095 | 430 | 1095 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,48,45 | 13 | 51,46,38,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1095 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1100 | 430 | 1100 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,48,46 | 13 | 52,46,38,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1105 | 430 | 1105 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,48,46 | 13 | 52,46,38,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1105 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1110 | 430 | 1110 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,48,46 | 13 | 52,46,38,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1115 | 430 | 1115 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,48,46 | 13 | 52,46,38,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1115 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1120 | 430 | 1120 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,48,46 | 13 | 52,46,38,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1125 | 430 | 1125 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,48,46 | 13 | 52,46,38,31,26,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1125 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1130 | 430 | 1130 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,48,46 | 13 | 52,46,38,31,27,26 | 55 | 75 | 0.5" Fiberglass | 14 | 1130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1135 | 430 | 1135 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,48,46 | 13 | 52,46,38,31,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1135 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1140 | 430 | 1140 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,49,48,46 | 13 | 52,46,38,31,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1145 | 430 | 1145 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,49,48,46 | 13 | 52,46,38,31,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1145 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1150 | 430 | 1150 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,49,48,46 | 13 | 52,46,38,31,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1155 | 430 | 1155 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,56,52,49,48,46 | 13 | 52,46,38,31,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1155 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1160 | 430 | 1160 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,56,52,49,48,46 | 13 | 52,46,38,31,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1165 | 430 | 1165 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,56,52,49,48,46 | 13 | 52,46,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1165 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1170 | 430 | 1170 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,56,52,49,48,46 | 13 | 52,46,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1175 | 430 | 1175 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,52,49,48,46 | 13 | 52,46,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1175 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1180 | 430 | 1180 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,52,50,48,46 | 13 | 52,46,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1185 | 430 | 1185 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,52,50,48,46 | 13 | 52,46,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1185 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1190 | 430 | 1190 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,52,50,48,46 | 13 | 52,46,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1195 | 430 | 1195 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,52,50,48,46 | 13 | 52,46,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1195 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1200 | 430 | 1200 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,52,50,48,46 | 13 | 52,46,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1205 | 430 | 1205 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,52,50,48,46 | 13 | 52,46,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1205 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1210 | 430 | 1210 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,52,50,48,46 | 13 | 52,46,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1215 | 430 | 1215 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,52,50,48,46 | 13 | 52,46,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1215 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1220 | 430 | 1220 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,52,50,48,46 | 14 | 52,47,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1225 | 430 | 1225 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,52,50,48,46 | 14 | 52,47,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1225 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1230 | 430 | 1230 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,48,46 | 14 | 53,47,39,32,27,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1235 | 430 | 1235 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,48,46 | 14 | 53,47,39,32,28,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1235 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1240 | 430 | 1240 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,48,46 | 14 | 53,47,39,32,28,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1245 | 430 | 1245 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,48,46 | 14 | 53,47,39,32,28,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1245 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1250 | 430 | 1250 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,46 | 14 | 53,47,39,32,28,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1255 | 430 | 1255 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,46 | 14 | 53,47,39,32,28,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1255 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1260 | 430 | 1260 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,46 | 14 | 53,47,39,32,28,27 | 55 | 75 | 0.5" Fiberglass | 14 | 1260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1265 | 430 | 1265 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,46 | 14 | 53,47,40,32,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1265 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1270 | 430 | 1270 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,46 | 14 | 53,47,40,32,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1275 | 430 | 1275 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,46 | 14 | 53,47,40,32,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1275 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1280 | 430 | 1280 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,46 | 14 | 53,47,40,32,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1285 | 430 | 1285 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,46 | 14 | 53,47,40,33,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1285 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1290 | 430 | 1290 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,47 | 14 | 53,47,40,33,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1295 | 430 | 1295 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,47 | 14 | 53,47,40,33,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1295 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1300 | 430 | 1300 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,47 | 14 | 53,47,40,33,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1305 | 430 | 1305 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,47 | 14 | 53,47,40,33,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1305 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1310 | 430 | 1310 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,50,49,47 | 14 | 53,47,40,33,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1315 | 430 | 1315 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,53,50,49,47 | 14 | 53,47,40,33,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1315 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1320 | 430 | 1320 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,50,49,47 | 14 | 53,47,40,33,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1325 | 430 | 1325 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,51,49,47 | 14 | 53,47,40,33,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1325 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1330 | 430 | 1330 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,51,49,47 | 14 | 53,47,40,33,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1335 | 430 | 1335 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,51,49,47 | 14 | 53,47,40,33,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1335 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1340 | 430 | 1340 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,51,49,47 | 14 | 53,47,40,33,28,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1345 | 430 | 1345 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,51,49,47 | 14 | 53,47,40,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1345 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1350 | 430 | 1350 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,51,49,47 | 14 | 53,47,40,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1355 | 430 | 1355 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,51,49,47 | 14 | 53,47,40,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1355 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1360 | 430 | 1360 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,51,49,47 | 14 | 53,47,40,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1365 | 430 | 1365 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,51,49,47 | 15 | 53,48,40,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1365 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1370 | 430 | 1370 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,51,49,47 | 15 | 54,48,40,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1375 | 430 | 1375 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,51,49,47 | 15 | 54,48,41,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1375 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1380 | 430 | 1380 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,51,49,47 | 15 | 54,48,41,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1385 | 430 | 1385 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,51,49,47 | 15 | 54,48,41,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1385 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1390 | 430 | 1390 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,51,49,47 | 15 | 54,48,41,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1395 | 430 | 1395 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,51,49,47 | 15 | 54,48,41,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1395 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1400 | 430 | 1400 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,51,49,47 | 15 | 54,48,41,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1405 | 430 | 1405 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,51,49,47 | 15 | 54,48,41,33,29,28 | 55 | 75 | 0.5" Fiberglass | 14 | 1405 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1410 | 430 | 1410 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,49,47 | 15 | 54,48,41,33,29,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1415 | 430 | 1415 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,49,47 | 15 | 54,48,41,33,29,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1415 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1420 | 430 | 1420 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,50,47 | 15 | 54,48,41,34,29,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1425 | 430 | 1425 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,50,47 | 15 | 54,48,41,34,29,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1425 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1430 | 430 | 1430 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,50,47 | 15 | 54,48,41,34,29,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1435 | 430 | 1435 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,50,47 | 15 | 54,48,41,34,29,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1435 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1440 | 430 | 1440 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,50,47 | 15 | 54,48,41,34,29,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1445 | 430 | 1445 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,50,47 | 15 | 54,48,41,34,29,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1445 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1450 | 430 | 1450 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,50,47 | 15 | 54,48,41,34,29,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1455 | 430 | 1455 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,50,47 | 15 | 54,48,41,34,29,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1455 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1460 | 430 | 1460 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,50,47 | 15 | 54,48,41,34,29,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1465 | 430 | 1465 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,50,47 | 15 | 54,48,41,34,29,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1465 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1470 | 430 | 1470 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,50,47 | 15 | 54,48,41,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1475 | 430 | 1475 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,51,50,47 | 15 | 54,48,41,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1475 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1480 | 430 | 1480 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,52,50,47 | 15 | 54,48,41,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1485 | 430 | 1485 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,52,50,47 | 15 | 54,48,41,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1485 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1490 | 430 | 1490 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,52,50,47 | 15 | 54,48,41,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1495 | 430 | 1495 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,52,50,47 | 15 | 54,48,41,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1495 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1500 | 430 | 1500 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,52,50,47 | 15 | 54,48,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1505 | 430 | 1505 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,52,50,47 | 15 | 54,48,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1505 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1510 | 430 | 1510 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,52,50,48 | 15 | 54,48,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1515 | 430 | 1515 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 15 | 54,48,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1515 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1520 | 430 | 1520 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 54,49,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1525 | 430 | 1525 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 55,49,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1525 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1530 | 430 | 1530 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 55,49,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1535 | 430 | 1535 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 55,49,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1535 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1540 | 430 | 1540 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 55,49,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1545 | 430 | 1545 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 55,49,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1545 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1550 | 430 | 1550 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 55,49,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1555 | 430 | 1555 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 55,49,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1555 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1560 | 430 | 1560 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 55,49,42,34,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1565 | 430 | 1565 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 55,49,42,35,30,29 | 55 | 75 | 0.5" Fiberglass | 14 | 1565 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1570 | 430 | 1570 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 55,49,42,35,30,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1575 | 430 | 1575 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 55,49,42,35,30,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1575 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1580 | 430 | 1580 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,52,50,48 | 17 | 55,49,42,35,30,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1585 | 430 | 1585 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,52,50,48 | 17 | 55,49,42,35,30,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1585 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1590 | 430 | 1590 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,52,50,48 | 17 | 55,49,42,35,30,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1595 | 430 | 1595 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,52,50,48 | 17 | 55,49,42,35,30,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1595 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1600 | 430 | 1600 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,52,50,48 | 17 | 55,49,42,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1605 | 430 | 1605 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,52,50,48 | 17 | 55,49,42,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1605 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1610 | 430 | 1610 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,52,50,48 | 17 | 55,49,42,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1615 | 430 | 1615 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,52,51,48 | 17 | 55,49,42,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1615 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1620 | 430 | 1620 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,52,51,48 | 17 | 55,49,42,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1625 | 430 | 1625 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,52,51,48 | 17 | 55,49,42,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1625 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1630 | 430 | 1630 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,52,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1635 | 430 | 1635 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,52,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1635 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1640 | 430 | 1640 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,52,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1645 | 430 | 1645 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,52,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1645 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1650 | 430 | 1650 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,52,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1655 | 430 | 1655 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,52,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1655 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1660 | 430 | 1660 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,53,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1665 | 430 | 1665 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,53,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1665 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1670 | 430 | 1670 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,53,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1675 | 430 | 1675 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,53,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1675 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1680 | 430 | 1680 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,53,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1685 | 430 | 1685 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,53,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1685 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1690 | 430 | 1690 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,53,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1695 | 430 | 1695 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,53,51,48 | 17 | 55,49,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1695 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1700 | 430 | 1700 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,53,51,48 | 18 | 56,50,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1705 | 430 | 1705 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,53,51,48 | 18 | 56,50,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1705 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1710 | 430 | 1710 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,53,51,48 | 18 | 56,50,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1715 | 430 | 1715 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,53,51,48 | 18 | 56,50,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1715 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1720 | 430 | 1720 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,53,51,48 | 18 | 56,50,43,35,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1725 | 430 | 1725 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,53,51,48 | 18 | 56,50,43,36,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1725 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1730 | 430 | 1730 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,53,51,48 | 18 | 56,50,43,36,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1735 | 430 | 1735 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,53,51,48 | 18 | 56,50,43,36,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1735 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1740 | 430 | 1740 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,48 | 18 | 56,50,43,36,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1745 | 430 | 1745 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,48 | 18 | 56,50,43,36,31,30 | 55 | 75 | 0.5" Fiberglass | 14 | 1745 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1750 | 430 | 1750 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,48 | 18 | 56,50,43,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1755 | 430 | 1755 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,48 | 18 | 56,50,43,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1755 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1760 | 430 | 1760 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,48 | 18 | 56,50,43,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1765 | 430 | 1765 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,48 | 18 | 56,50,43,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1765 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1770 | 430 | 1770 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1775 | 430 | 1775 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1775 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1780 | 430 | 1780 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1785 | 430 | 1785 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1785 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1790 | 430 | 1790 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1795 | 430 | 1795 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1795 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1800 | 430 | 1800 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1805 | 430 | 1805 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1805 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1810 | 430 | 1810 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1815 | 430 | 1815 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1815 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1820 | 430 | 1820 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1825 | 430 | 1825 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1825 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1830 | 430 | 1830 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1835 | 430 | 1835 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,51,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1835 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1840 | 430 | 1840 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,58,53,52,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1845 | 430 | 1845 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,53,52,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1845 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1850 | 430 | 1850 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,53,52,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1855 | 430 | 1855 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,54,52,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1855 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1860 | 430 | 1860 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,54,52,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1865 | 430 | 1865 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1865 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1870 | 430 | 1870 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1875 | 430 | 1875 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1875 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1880 | 430 | 1880 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1885 | 430 | 1885 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1885 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1890 | 430 | 1890 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 18 | 56,50,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1895 | 430 | 1895 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 19 | 56,51,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1895 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1900 | 430 | 1900 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 19 | 57,51,44,36,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1905 | 430 | 1905 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 19 | 57,51,44,37,32,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1905 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1910 | 430 | 1910 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 19 | 57,51,44,37,33,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1915 | 430 | 1915 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 19 | 57,51,44,37,33,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1915 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1920 | 576 | 1920 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 19 | 57,51,44,37,33,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1925 | 430 | 1925 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,54,52,49 | 19 | 57,51,44,37,33,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1925 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1930 | 430 | 1930 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,54,52,49 | 19 | 57,51,45,37,33,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1935 | 430 | 1935 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,54,52,49 | 19 | 57,51,45,37,33,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1935 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1940 | 430 | 1940 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,54,52,49 | 19 | 57,51,45,37,33,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1945 | 430 | 1945 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,54,52,49 | 19 | 57,51,45,37,33,31 | 55 | 75 | 0.5" Fiberglass | 14 | 1945 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1950 | 430 | 1950 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 1950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1955 | 430 | 1955 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 1955 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1960 | 430 | 1960 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 1960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1965 | 590 | 1965 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 1965 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1970 | 430 | 1970 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 1970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1975 | 430 | 1975 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 1975 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1980 | 430 | 1980 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 1980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1990 | 430 | 1990 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 1990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1995 | 430 | 1995 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 1995 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2000 | 430 | 2000 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2010 | 430 | 2010 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2020 | 430 | 2020 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2030 | 430 | 2030 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2040 | 430 | 2040 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2050 | 430 | 2050 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2060 | 430 | 2060 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2070 | 430 | 2070 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,54,52,49 | 19 | 57,51,45,37,33,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2080 | 430 | 2080 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,55,52,50 | 19 | 57,51,45,37,34,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2090 | 430 | 2090 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,55,52,50 | 19 | 57,51,45,37,34,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2100 | 430 | 2100 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,55,53,50 | 20 | 57,51,46,38,34,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2110 | 430 | 2110 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,55,53,50 | 20 | 57,51,46,38,34,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2120 | 430 | 2120 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,55,53,50 | 20 | 58,52,46,38,34,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2130 | 430 | 2130 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,55,53,50 | 20 | 58,52,46,38,34,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2140 | 430 | 2140 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,61,55,53,50 | 20 | 58,52,46,38,34,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2150 | 430 | 2150 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,61,55,53,50 | 20 | 58,52,46,38,34,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2160 | 430 | 2160 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,61,55,53,50 | 20 | 58,52,46,38,34,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2170 | 430 | 2170 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,61,55,53,50 | 20 | 58,52,46,38,34,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2180 | 430 | 2180 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,61,55,53,50 | 20 | 58,52,46,38,34,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2190 | 430 | 2190 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,61,55,53,50 | 20 | 58,52,46,38,34,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2200 | 430 | 2200 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,55,53,50 | 20 | 58,52,46,38,34,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2120 | 430 | 2210 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,60,55,53,50 | 20 | 58,52,46,38,34,32 | 55 | 75 | 0.5" Fiberglass | 14 | 2120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2220 | 666 | 2220 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,55,53,50 | 20 | 58,52,46,38,34,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2230 | 430 | 2230 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,55,53,50 | 20 | 58,52,46,38,34,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2240 | 430 | 2240 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,55,53,50 | 20 | 58,52,46,38,34,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2250 | 430 | 2250 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,55,53,50 | 20 | 58,52,46,38,34,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2260 | 430 | 2260 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,55,53,50 | 20 | 58,52,46,38,34,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2270 | 430 | 2270 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,55,53,50 | 20 | 58,52,46,38,34,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2280 | 430 | 2280 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,55,53,50 | 21 | 58,52,47,38,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2290 | 430 | 2290 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,55,53,50 | 21 | 58,52,47,38,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2300 | 430 | 2300 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,55,53,50 | 21 | 58,52,47,38,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2310 | 430 | 2310 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,55,53,50 | 21 | 58,52,47,38,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2320 | 430 | 2320 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,55,53,50 | 21 | 58,52,47,39,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2330 | 430 | 2330 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,53,50 | 21 | 58,52,47,39,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2340 | 430 | 2340 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,53,50 | 21 | 58,52,47,39,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2350 | 430 | 2350 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,53,50 | 21 | 58,52,47,39,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2360 | 430 | 2360 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,53,50 | 21 | 59,53,47,39,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2370 | 430 | 2370 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,53,50 | 21 | 59,53,47,39,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2380 | 430 | 2380 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,53,50 | 21 | 59,53,47,39,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2390 | 430 | 2390 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,54,50 | 21 | 59,53,47,39,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2400 | 430 | 2400 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,54,50 | 21 | 59,53,47,39,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2410 | 430 | 2410 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,54,50 | 21 | 59,53,47,39,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2420 | 430 | 2420 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,54,50 | 21 | 59,53,47,39,35,33 | 55 | 75 | 0.5" Fiberglass | 14 | 2420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2430 | 430 | 2430 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,54,50 | 21 | 59,53,47,39,35,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2440 | 430 | 2440 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,54,51 | 21 | 59,53,47,39,35,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2450 | 430 | 2450 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,62,56,54,51 | 21 | 59,53,47,39,35,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2460 | 430 | 2460 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,63,56,54,51 | 21 | 59,53,47,39,35,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2470 | 430 | 2470 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,63,56,54,51 | 21 | 59,53,47,39,35,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2480 | 430 | 2480 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,63,56,54,51 | 22 | 59,53,48,39,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2490 | 430 | 2490 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,63,56,54,51 | 22 | 59,53,48,39,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2500 | 430 | 2500 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,56,54,51 | 22 | 59,53,48,39,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2510 | 430 | 2510 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,56,54,51 | 22 | 59,53,48,39,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2520 | 756 | 2520 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,56,54,51 | 22 | 59,53,48,39,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2530 | 430 | 2530 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,56,54,51 | 22 | 59,53,48,39,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2540 | 430 | 2540 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,56,54,51 | 22 | 59,53,48,39,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2550 | 430 | 2550 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,56,54,51 | 22 | 59,53,48,39,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2560 | 430 | 2560 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,56,54,51 | 22 | 59,53,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2570 | 430 | 2570 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,56,54,51 | 22 | 59,53,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2580 | 430 | 2580 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,56,54,51 | 22 | 59,53,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2590 | 430 | 2590 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,56,54,51 | 22 | 59,53,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2600 | 430 | 2600 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,56,54,51 | 22 | 59,53,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2610 | 430 | 2610 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,57,54,51 | 22 | 59,53,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2620 | 430 | 2620 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,57,54,51 | 22 | 59,53,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2630 | 430 | 2630 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,63,57,54,51 | 22 | 59,53,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2640 | 430 | 2640 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,54,51 | 23 | 60,54,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2650 | 430 | 2650 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,54,51 | 23 | 60,54,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2660 | 430 | 2660 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,54,51 | 23 | 60,54,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2670 | 430 | 2670 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,54,51 | 23 | 60,54,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2680 | 430 | 2680 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,54,51 | 23 | 60,54,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2690 | 430 | 2690 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,54,51 | 23 | 60,54,48,40,36,34 | 55 | 75 | 0.5" Fiberglass | 14 | 2690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2700 | 430 | 2700 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,54,51 | 23 | 60,54,49,40,36,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2710 | 430 | 2710 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,54,51 | 23 | 60,54,49,40,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2720 | 430 | 2720 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,55,51 | 23 | 60,54,49,40,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2730 | 430 | 2730 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,55,51 | 23 | 60,54,49,40,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2740 | 430 | 2740 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,55,51 | 23 | 60,54,49,40,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2750 | 430 | 2750 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,55,51 | 23 | 60,54,49,40,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2800 | 430 | 2800 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,55,51 | 23 | 60,54,49,40,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2770 | 430 | 2770 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,55,51 | 23 | 60,54,49,40,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2780 | 430 | 2780 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,55,51 | 23 | 60,54,49,40,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2790 | 430 | 2790 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,55,51 | 23 | 60,54,49,40,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2800 | 430 | 2800 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,55,51 | 23 | 60,54,49,40,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2810 | 430 | 2810 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,55,51 | 23 | 60,54,49,40,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2820 | 430 | 2820 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,64,57,55,51 | 23 | 60,54,49,41,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2830 | 430 | 2830 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,65,57,55,51 | 23 | 60,54,49,41,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2840 | 430 | 2840 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,62,65,57,55,51 | 23 | 60,54,49,41,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2850 | 430 | 2850 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,62,65,57,55,51 | 23 | 60,54,49,41,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2860 | 430 | 2860 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,62,65,57,55,52 | 23 | 60,54,49,41,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2870 | 430 | 2870 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,62,65,57,55,52 | 23 | 60,54,49,41,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2880 | 430 | 2880 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,62,65,57,55,52 | 23 | 60,54,49,41,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2890 | 430 | 2890 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,65,57,55,52 | 23 | 60,54,49,41,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2900 | 430 | 2900 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,65,57,55,52 | 23 | 60,54,49,41,37,35 | 55 | 75 | 0.5" Fiberglass | 14 | 2900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3000 | 430 | 3000 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,65,58,55,52 | 24 | 61,55,50,41,38,35 | 55 | 75 | 0.5" Fiberglass | 14 | 3000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3010 | 430 | 3010 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,65,58,55,52 | 24 | 61,55,50,41,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3020 | 430 | 3020 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,65,58,55,52 | 24 | 61,55,50,41,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3030 | 430 | 3030 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,55,52 | 24 | 61,55,50,41,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3040 | 430 | 3040 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,55,52 | 24 | 61,55,50,41,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3050 | 430 | 3050 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,55,52 | 24 | 61,55,50,41,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3060 | 430 | 3060 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,55,52 | 24 | 61,55,50,41,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3070 | 430 | 3070 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,55,52 | 24 | 61,55,50,41,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3080 | 430 | 3080 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,55,52 | 24 | 61,55,50,41,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3090 | 430 | 3090 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 24 | 61,55,50,41,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3100 | 430 | 3100 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 24 | 61,55,50,41,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3110 | 430 | 3110 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 24 | 61,55,50,42,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3120 | 430 | 3120 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 24 | 61,55,50,42,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3130 | 430 | 3130 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 24 | 61,55,50,42,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3140 | 430 | 3140 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 24 | 61,55,50,42,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3150 | 430 | 3150 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 24 | 61,55,50,42,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3160 | 430 | 3160 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 24 | 61,55,50,42,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3170 | 430 | 3170 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 24 | 61,55,50,42,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3180 | 430 | 3180 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 24 | 61,55,50,42,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3190 | 430 | 3190 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 24 | 61,55,50,42,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3200 | 430 | 3200 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 25 | 61,55,51,42,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3210 | 430 | 3210 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 25 | 61,55,51,42,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3220 | 430 | 3220 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,66,58,56,52 | 25 | 61,55,51,42,38,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3230 | 430 | 3230 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,66,58,56,52 | 25 | 61,55,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3240 | 430 | 3240 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,66,58,56,52 | 25 | 61,55,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3250 | 430 | 3250 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,67,58,56,52 | 25 | 61,55,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3260 | 430 | 3260 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,67,58,56,52 | 25 | 61,55,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3270 | 430 | 3270 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,67,59,56,52 | 25 | 61,55,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3280 | 430 | 3280 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,67,59,56,52 | 25 | 62,55,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3290 | 430 | 3290 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,67,59,56,52 | 25 | 62,56,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3300 | 430 | 3300 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,67,59,56,52 | 25 | 62,56,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3310 | 430 | 3310 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,67,59,56,52 | 25 | 62,56,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3320 | 430 | 3320 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,67,59,56,52 | 25 | 62,56,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3330 | 430 | 3330 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,67,59,56,52 | 25 | 62,56,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3340 | 430 | 3340 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,67,59,56,52 | 25 | 62,56,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3350 | 430 | 3350 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,67,59,56,53 | 25 | 62,56,51,42,39,36 | 55 | 75 | 0.5" Fiberglass | 14 | 3350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3360 | 430 | 3360 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,67,59,56,53 | 25 | 62,56,51,42,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3370 | 430 | 3370 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,67,59,56,53 | 25 | 62,56,51,42,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3380 | 430 | 3380 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,67,59,56,53 | 25 | 62,56,51,42,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3390 | 430 | 3390 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,67,59,56,53 | 25 | 62,56,51,42,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3400 | 430 | 3400 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,67,59,56,53 | 25 | 62,56,51,42,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3410 | 430 | 3410 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,67,59,56,53 | 25 | 62,56,51,42,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3420 | 430 | 3420 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,67,59,56,53 | 25 | 62,56,51,42,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3430 | 430 | 3430 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,67,59,56,53 | 25 | 62,56,51,43,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3440 | 430 | 3440 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,67,59,56,53 | 25 | 62,56,51,43,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3450 | 430 | 3450 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,67,59,56,53 | 25 | 62,56,51,43,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3460 | 430 | 3460 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,67,59,56,53 | 25 | 62,56,51,43,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3470 | 430 | 3470 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,67,59,56,53 | 25 | 62,56,51,43,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3480 | 430 | 3480 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,56,53 | 26 | 62,56,52,43,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3490 | 430 | 3490 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,56,53 | 26 | 62,56,52,43,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3500 | 430 | 3500 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,56,53 | 26 | 62,56,52,43,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3510 | 430 | 3510 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,56,53 | 26 | 62,56,52,43,39,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3520 | 430 | 3520 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3530 | 430 | 3530 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3540 | 430 | 3540 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3550 | 430 | 3550 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3560 | 430 | 3560 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3570 | 430 | 3570 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3580 | 430 | 3580 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3590 | 430 | 3590 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3600 | 430 | 3600 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3610 | 430 | 3610 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3620 | 430 | 3620 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3630 | 430 | 3630 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3640 | 430 | 3640 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3650 | 430 | 3650 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,59,57,53 | 26 | 62,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3660 | 430 | 3660 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,68,60,57,53 | 26 | 63,56,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3670 | 430 | 3670 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,68,60,57,53 | 26 | 63,57,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3680 | 430 | 3680 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,68,60,57,53 | 26 | 63,57,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3690 | 430 | 3690 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,68,60,57,53 | 26 | 63,57,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3700 | 430 | 3700 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,68,60,57,53 | 26 | 63,57,52,43,40,37 | 55 | 75 | 0.5" Fiberglass | 14 | 3700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1500 | 575 | 1500 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,56,52,52,50,47 | 14 | 50,47,41,34,30,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1505 | 575 | 1505 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,56,53,52,50,47 | 14 | 50,47,41,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1505 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1510 | 575 | 1510 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,56,53,52,50,47 | 14 | 50,47,41,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1515 | 575 | 1515 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,56,53,52,50,47 | 14 | 50,47,41,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1515 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1520 | 575 | 1520 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,56,53,52,50,47 | 14 | 51,47,41,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1525 | 575 | 1525 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,56,53,52,50,47 | 14 | 51,47,41,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1525 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1530 | 575 | 1530 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,56,53,52,50,47 | 14 | 51,47,41,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1535 | 575 | 1535 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 14 | 51,47,41,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1535 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1540 | 575 | 1540 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,41,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1545 | 575 | 1545 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,41,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1545 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1550 | 575 | 1550 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,41,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1555 | 575 | 1555 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1555 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1560 | 575 | 1560 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1565 | 575 | 1565 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1565 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1570 | 575 | 1570 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1575 | 575 | 1575 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1575 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1580 | 575 | 1580 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1585 | 575 | 1585 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1585 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1590 | 575 | 1590 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1595 | 575 | 1595 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1595 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1600 | 575 | 1600 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1605 | 575 | 1605 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,31,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1605 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1610 | 575 | 1610 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,32,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1615 | 575 | 1615 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,32,27 | 55 | 75 | 0.5" Fiberglass | 16 | 1615 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1620 | 575 | 1620 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,50,47 | 15 | 51,48,42,35,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1625 | 575 | 1625 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,51,47 | 15 | 51,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1625 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1630 | 575 | 1630 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,51,47 | 15 | 51,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1635 | 575 | 1635 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,52,51,47 | 15 | 51,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1635 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1640 | 575 | 1640 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,53,51,47 | 15 | 51,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1645 | 575 | 1645 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,53,51,47 | 15 | 51,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1645 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1650 | 575 | 1650 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,53,51,47 | 15 | 51,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1655 | 575 | 1655 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,53,51,47 | 15 | 51,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1655 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1660 | 575 | 1660 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,53,51,47 | 15 | 52,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1665 | 575 | 1665 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,53,51,47 | 15 | 52,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1665 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1670 | 575 | 1670 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,53,51,47 | 15 | 52,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1675 | 575 | 1675 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,53,51,47 | 15 | 52,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1675 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1680 | 575 | 1680 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,53,51,47 | 15 | 52,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1685 | 575 | 1685 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,47 | 15 | 52,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1685 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1690 | 575 | 1690 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,47 | 15 | 52,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1695 | 575 | 1695 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,47 | 15 | 52,48,42,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1695 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1700 | 575 | 1700 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,47 | 16 | 52,48,43,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1705 | 575 | 1705 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,47 | 17 | 52,49,43,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1705 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1710 | 575 | 1710 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1715 | 575 | 1715 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1715 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1720 | 575 | 1720 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,36,32,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1725 | 575 | 1725 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,36,33,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1725 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1730 | 575 | 1730 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,36,33,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1735 | 575 | 1735 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,36,33,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1735 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1740 | 575 | 1740 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,36,33,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1745 | 575 | 1745 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,36,33,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1745 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1750 | 575 | 1750 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,36,33,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1755 | 575 | 1755 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,37,33,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1755 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1760 | 575 | 1760 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,37,33,28 | 55 | 75 | 0.5" Fiberglass | 16 | 1760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1765 | 575 | 1765 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1765 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1770 | 575 | 1770 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1775 | 575 | 1775 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,57,54,53,51,48 | 17 | 52,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1775 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1780 | 575 | 1780 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,53,51,48 | 17 | 52,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1785 | 575 | 1785 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,53,51,48 | 17 | 52,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1785 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1790 | 575 | 1790 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,53,51,48 | 17 | 52,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1795 | 575 | 1795 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,53,51,48 | 17 | 52,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1795 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1800 | 575 | 1800 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,53,51,48 | 17 | 52,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1805 | 575 | 1805 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,53,51,48 | 17 | 52,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1805 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1810 | 575 | 1810 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,51,48 | 17 | 52,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1815 | 575 | 1815 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,51,48 | 17 | 53,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1815 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1820 | 575 | 1820 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,51,48 | 17 | 53,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1825 | 575 | 1825 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,51,48 | 17 | 53,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1825 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1830 | 575 | 1830 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,51,48 | 17 | 53,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1835 | 575 | 1835 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,51,48 | 17 | 53,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1835 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1840 | 575 | 1840 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,51,48 | 17 | 53,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1845 | 575 | 1845 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,51,48 | 17 | 53,49,43,37,33,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1845 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1850 | 575 | 1850 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,51,48 | 17 | 53,49,43,37,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1855 | 575 | 1855 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,51,48 | 17 | 53,49,43,37,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1855 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1860 | 575 | 1860 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,51,48 | 18 | 53,49,44,37,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1865 | 575 | 1865 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,51,48 | 18 | 53,49,44,37,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1865 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1870 | 575 | 1870 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,51,48 | 18 | 53,49,44,37,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1875 | 575 | 1875 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,51,48 | 18 | 53,49,44,37,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1875 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1880 | 575 | 1880 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,51,48 | 18 | 53,49,44,37,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1885 | 575 | 1885 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,51,48 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1885 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1890 | 575 | 1890 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,52,48 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1895 | 575 | 1895 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,52,48 | 18 | 53,50,44,38,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1895 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1900 | 575 | 1900 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,52,48 | 18 | 53,50,44,38,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1905 | 575 | 1905 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,52,48 | 18 | 53,50,44,38,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1905 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1910 | 575 | 1910 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,52,48 | 18 | 53,50,44,38,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1915 | 575 | 1915 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,54,52,48 | 18 | 53,50,44,38,34,29 | 55 | 75 | 0.5" Fiberglass | 16 | 1915 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1920 | 576 | 1920 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 53,50,44,38,34,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1925 | 575 | 1925 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 53,50,44,38,34,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1925 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1930 | 575 | 1930 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 53,50,44,38,34,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1935 | 575 | 1935 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 53,50,44,38,34,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1935 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1940 | 575 | 1940 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 53,50,44,38,34,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1945 | 575 | 1945 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 53,50,44,38,34,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1945 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1950 | 575 | 1950 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 53,50,44,38,34,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1955 | 575 | 1955 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 53,50,44,38,34,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1955 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1960 | 575 | 1960 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 53,50,44,38,34,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1965 | 590 | 1965 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 53,50,44,38,34,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1965 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1970 | 575 | 1970 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 53,50,44,38,34,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1975 | 575 | 1975 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 53,50,44,38,34,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1975 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1980 | 575 | 1980 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,55,54,52,48 | 18 | 54,50,44,38,35,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1990 | 575 | 1990 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,54,52,48 | 18 | 54,50,44,38,35,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1995 | 575 | 1995 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,54,52,48 | 18 | 54,50,44,38,35,30 | 55 | 75 | 0.5" Fiberglass | 16 | 1995 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2000 | 575 | 2000 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,54,52,48 | 18 | 54,50,44,38,35,30 | 55 | 75 | 0.5" Fiberglass | 16 | 2000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2010 | 575 | 2010 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,54,52,49 | 18 | 54,50,44,38,35,30 | 55 | 75 | 0.5" Fiberglass | 16 | 2010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2020 | 575 | 2020 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,54,52,49 | 18 | 54,50,44,38,35,30 | 55 | 75 | 0.5" Fiberglass | 16 | 2020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2030 | 575 | 2030 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,54,52,49 | 18 | 54,50,44,38,35,30 | 55 | 75 | 0.5" Fiberglass | 16 | 2030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2040 | 575 | 2040 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,54,52,49 | 19 | 54,50,45,38,35,30 | 55 | 75 | 0.5" Fiberglass | 16 | 2040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2050 | 575 | 2050 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,58,56,54,52,49 | 19 | 54,50,45,39,35,30 | 55 | 75 | 0.5" Fiberglass | 16 | 2050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2060 | 575 | 2060 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,52,49 | 19 | 54,50,45,39,35,30 | 55 | 75 | 0.5" Fiberglass | 16 | 2060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2070 | 575 | 2070 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,52,49 | 19 | 54,50,45,39,35,30 | 55 | 75 | 0.5" Fiberglass | 16 | 2070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2080 | 575 | 2080 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,52,49 | 19 | 54,50,45,39,35,30 | 55 | 75 | 0.5" Fiberglass | 16 | 2080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2090 | 575 | 2090 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,52,49 | 19 | 54,51,45,39,35,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2100 | 575 | 2100 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,55,52,49 | 19 | 54,51,45,39,35,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2110 | 575 | 2110 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,55,52,49 | 19 | 54,51,45,39,35,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2120 | 575 | 2120 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,55,52,49 | 19 | 54,51,45,39,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2130 | 575 | 2130 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,55,52,49 | 19 | 54,51,45,39,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2140 | 575 | 2140 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,55,52,49 | 19 | 54,51,45,39,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2150 | 575 | 2150 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,55,52,49 | 19 | 54,51,45,39,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2160 | 575 | 2160 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,55,52,49 | 19 | 54,51,45,39,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2170 | 575 | 2170 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,55,52,49 | 19 | 55,51,45,39,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2180 | 575 | 2180 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,55,52,49 | 19 | 55,51,45,39,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2190 | 575 | 2190 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,52,49 | 19 | 55,51,45,39,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2200 | 575 | 2200 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 19 | 55,51,45,39,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2120 | 575 | 2210 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,55,52,49 | 19 | 54,51,45,39,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2220 | 666 | 2220 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 19 | 55,51,45,40,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2230 | 575 | 2230 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 20 | 55,51,46,40,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2240 | 575 | 2240 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 20 | 55,51,46,40,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2250 | 575 | 2250 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 20 | 55,51,46,40,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2260 | 575 | 2260 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 20 | 55,51,46,40,36,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2270 | 575 | 2270 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 20 | 55,51,46,40,37,31 | 55 | 75 | 0.5" Fiberglass | 16 | 2270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2280 | 575 | 2280 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 20 | 55,51,46,40,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2290 | 575 | 2290 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 20 | 55,51,46,40,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2300 | 575 | 2300 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 20 | 55,51,46,40,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2310 | 575 | 2310 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 20 | 55,52,46,40,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2320 | 575 | 2320 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 20 | 55,52,46,40,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2330 | 575 | 2330 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 20 | 55,52,46,40,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2340 | 575 | 2340 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,49 | 20 | 55,52,46,40,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2350 | 575 | 2350 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,50 | 20 | 55,52,46,40,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2360 | 575 | 2360 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,50 | 20 | 55,52,46,40,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2370 | 575 | 2370 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,55,53,50 | 20 | 56,52,46,40,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2380 | 575 | 2380 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,56,53,50 | 20 | 56,52,46,40,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2390 | 575 | 2390 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,56,53,50 | 20 | 56,52,46,41,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2400 | 575 | 2400 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,56,53,50 | 20 | 56,52,46,41,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2410 | 575 | 2410 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,56,53,50 | 20 | 56,52,46,41,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2420 | 575 | 2420 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,56,53,50 | 20 | 56,52,46,41,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2430 | 575 | 2430 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,56,53,50 | 20 | 56,52,46,41,37,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2440 | 575 | 2440 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,56,53,50 | 21 | 56,52,47,41,38,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2450 | 575 | 2450 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,56,53,50 | 21 | 56,52,47,41,38,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2460 | 575 | 2460 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,56,53,50 | 21 | 56,52,47,41,38,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2470 | 575 | 2470 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,56,53,50 | 21 | 56,52,47,41,38,32 | 55 | 75 | 0.5" Fiberglass | 16 | 2470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2480 | 575 | 2480 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,56,53,50 | 21 | 56,52,47,41,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2490 | 575 | 2490 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,56,53,50 | 21 | 56,52,47,41,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2500 | 575 | 2500 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,58,56,53,50 | 21 | 56,52,47,41,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2510 | 575 | 2510 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,58,56,53,50 | 21 | 56,52,47,41,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2520 | 756 | 2520 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,58,56,53,50 | 21 | 56,52,47,41,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2530 | 575 | 2530 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,58,56,53,50 | 21 | 56,52,47,41,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2540 | 575 | 2540 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,58,56,53,50 | 21 | 56,52,47,41,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2550 | 575 | 2550 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,58,56,53,50 | 21 | 56,53,47,41,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2560 | 575 | 2560 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,58,56,54,50 | 21 | 56,53,47,41,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2570 | 575 | 2570 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,58,56,54,50 | 21 | 56,53,47,41,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2580 | 575 | 2580 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,58,56,54,50 | 21 | 56,53,47,42,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2590 | 575 | 2590 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,58,56,54,50 | 21 | 57,53,47,42,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2600 | 575 | 2600 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,58,56,54,50 | 21 | 57,53,47,42,38,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2610 | 575 | 2610 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,58,56,54,50 | 21 | 57,53,47,42,39,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2620 | 575 | 2620 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,56,54,50 | 21 | 57,53,47,42,39,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2630 | 575 | 2630 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,56,54,50 | 21 | 57,53,47,42,39,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2640 | 575 | 2640 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,56,54,50 | 21 | 57,53,47,42,39,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2650 | 575 | 2650 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,56,54,50 | 21 | 57,53,47,42,39,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2660 | 575 | 2660 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,56,54,50 | 21 | 57,53,47,42,39,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2670 | 575 | 2670 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,56,54,50 | 22 | 57,53,48,42,39,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2680 | 575 | 2680 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,56,54,50 | 22 | 57,53,48,42,39,33 | 55 | 75 | 0.5" Fiberglass | 16 | 2680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2690 | 575 | 2690 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,57,54,50 | 22 | 57,53,48,42,39,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2700 | 575 | 2700 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,57,54,50 | 22 | 57,53,48,42,39,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2710 | 575 | 2710 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,57,54,50 | 22 | 57,53,48,42,39,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2720 | 575 | 2720 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,57,54,50 | 22 | 57,53,48,42,39,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2730 | 575 | 2730 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,57,54,50 | 22 | 57,53,48,42,39,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2740 | 575 | 2740 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,57,54,50 | 22 | 57,53,48,42,39,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2750 | 575 | 2750 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,57,54,51 | 22 | 57,53,48,42,39,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2800 | 575 | 2800 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,57,54,51 | 22 | 57,53,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2770 | 575 | 2770 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,57,54,51 | 22 | 57,53,48,42,39,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2780 | 575 | 2780 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,57,54,51 | 22 | 57,53,48,42,39,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2790 | 575 | 2790 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,57,54,51 | 22 | 57,53,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2800 | 575 | 2800 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,57,54,51 | 22 | 57,53,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2810 | 575 | 2810 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,57,54,51 | 22 | 57,53,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2820 | 575 | 2820 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,57,54,51 | 23 | 57,54,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2830 | 575 | 2830 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,57,54,51 | 23 | 58,54,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2840 | 575 | 2840 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,57,54,51 | 23 | 58,54,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2850 | 575 | 2850 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,59,57,54,51 | 23 | 58,54,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2860 | 575 | 2860 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,59,57,54,51 | 23 | 58,54,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2870 | 575 | 2870 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,57,54,51 | 23 | 58,54,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2880 | 575 | 2880 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,57,54,51 | 23 | 58,54,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2890 | 575 | 2890 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,57,54,51 | 23 | 58,54,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2900 | 575 | 2900 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,57,54,51 | 23 | 58,54,48,43,40,34 | 55 | 75 | 0.5" Fiberglass | 16 | 2900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3000 | 575 | 3000 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,57,55,51 | 23 | 58,54,49,43,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3010 | 575 | 3010 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,57,55,51 | 23 | 58,54,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3020 | 575 | 3020 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,57,55,51 | 23 | 58,54,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3030 | 575 | 3030 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,57,55,51 | 23 | 58,54,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3040 | 575 | 3040 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,58,55,51 | 23 | 58,54,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3050 | 575 | 3050 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,58,55,51 | 23 | 58,54,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3060 | 575 | 3060 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,58,55,51 | 23 | 58,54,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3070 | 575 | 3070 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,58,55,51 | 23 | 58,54,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3080 | 575 | 3080 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,58,55,51 | 23 | 58,54,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3090 | 575 | 3090 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,58,55,51 | 23 | 59,54,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3100 | 575 | 3100 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,58,55,51 | 23 | 59,54,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3110 | 575 | 3110 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,58,55,51 | 23 | 59,54,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3120 | 575 | 3120 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,58,55,51 | 24 | 59,55,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3130 | 575 | 3130 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,58,55,51 | 24 | 59,55,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3140 | 575 | 3140 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,58,55,51 | 24 | 59,55,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3150 | 575 | 3150 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,58,55,51 | 24 | 59,55,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3160 | 575 | 3160 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,58,55,51 | 24 | 59,55,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3170 | 575 | 3170 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,58,55,51 | 24 | 59,55,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3180 | 575 | 3180 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,58,55,51 | 24 | 59,55,49,44,41,35 | 55 | 75 | 0.5" Fiberglass | 16 | 3180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3190 | 575 | 3190 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,58,55,51 | 24 | 59,55,50,44,41,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3200 | 575 | 3200 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,58,55,51 | 24 | 59,55,50,44,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3210 | 575 | 3210 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,58,55,51 | 24 | 59,55,50,44,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3220 | 575 | 3220 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,58,55,51 | 24 | 59,55,50,44,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3230 | 575 | 3230 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,58,55,52 | 24 | 59,55,50,44,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3240 | 575 | 3240 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,44,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3250 | 575 | 3250 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3260 | 575 | 3260 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3270 | 575 | 3270 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3280 | 575 | 3280 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3290 | 575 | 3290 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3300 | 575 | 3300 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3310 | 575 | 3310 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3320 | 575 | 3320 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3330 | 575 | 3330 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3340 | 575 | 3340 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3350 | 575 | 3350 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3360 | 575 | 3360 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 59,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3370 | 575 | 3370 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 60,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3380 | 575 | 3380 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 60,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3390 | 575 | 3390 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 60,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3400 | 575 | 3400 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 60,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3410 | 575 | 3410 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 60,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3420 | 575 | 3420 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 60,55,50,45,42,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3430 | 575 | 3430 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,61,58,55,52 | 24 | 60,55,50,45,43,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3440 | 575 | 3440 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,55,52 | 24 | 60,55,50,45,43,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3450 | 575 | 3450 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,55,52 | 25 | 60,56,50,45,43,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3460 | 575 | 3460 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,50,45,43,36 | 55 | 75 | 0.5" Fiberglass | 16 | 3460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3470 | 575 | 3470 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,50,45,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3480 | 575 | 3480 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,50,45,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3490 | 575 | 3490 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,45,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3500 | 575 | 3500 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,45,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3510 | 575 | 3510 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3520 | 575 | 3520 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3530 | 575 | 3530 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3540 | 575 | 3540 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3550 | 575 | 3550 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3560 | 575 | 3560 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3570 | 575 | 3570 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3580 | 575 | 3580 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3590 | 575 | 3590 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3600 | 575 | 3600 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3610 | 575 | 3610 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3620 | 575 | 3620 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3630 | 575 | 3630 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3640 | 575 | 3640 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3650 | 575 | 3650 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3660 | 575 | 3660 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,43,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3670 | 575 | 3670 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,44,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3680 | 575 | 3680 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 60,56,51,46,44,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3690 | 575 | 3690 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,59,56,52 | 25 | 61,56,51,46,44,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3700 | 575 | 3700 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,62,62,59,56,52 | 25 | 61,56,51,46,44,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3710 | 575 | 3710 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,62,62,59,56,52 | 25 | 61,56,51,46,44,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3720 | 575 | 3720 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,62,59,56,52 | 25 | 61,56,51,46,44,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3730 | 575 | 3730 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,62,59,56,52 | 25 | 61,56,51,46,44,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3740 | 575 | 3740 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,62,59,56,52 | 25 | 61,56,51,46,44,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3750 | 575 | 3750 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,62,59,56,52 | 25 | 61,56,51,46,44,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3760 | 575 | 3760 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,62,59,56,52 | 25 | 61,56,51,46,44,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3770 | 575 | 3770 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,52 | 25 | 61,56,51,46,44,37 | 55 | 75 | 0.5" Fiberglass | 16 | 3770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3780 | 575 | 3780 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,53 | 25 | 61,56,51,46,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3790 | 575 | 3790 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,53 | 25 | 61,56,51,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3800 | 575 | 3800 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,53 | 25 | 61,56,51,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3810 | 575 | 3810 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,53 | 25 | 61,56,51,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3820 | 575 | 3820 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,53 | 26 | 61,57,52,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3830 | 575 | 3830 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,53 | 26 | 61,57,52,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3840 | 575 | 3840 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,53 | 26 | 61,57,52,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3850 | 575 | 3850 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,53 | 26 | 61,57,52,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3860 | 575 | 3860 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,53 | 26 | 61,57,52,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3870 | 575 | 3870 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,53 | 26 | 61,57,52,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3880 | 575 | 3880 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,53 | 26 | 61,57,52,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3890 | 575 | 3890 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,59,56,53 | 26 | 61,57,52,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3900 | 575 | 3900 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,56,53 | 26 | 61,57,52,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3910 | 575 | 3910 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,56,53 | 26 | 61,57,52,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3920 | 575 | 3920 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,56,53 | 26 | 61,57,52,47,44,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3930 | 575 | 3930 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,56,53 | 26 | 61,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3940 | 575 | 3940 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,56,53 | 26 | 61,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3950 | 575 | 3950 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,56,53 | 26 | 61,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3960 | 575 | 3960 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,56,53 | 26 | 61,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3970 | 575 | 3970 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,56,53 | 26 | 61,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3980 | 575 | 3980 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,56,53 | 26 | 61,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3990 | 575 | 3990 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,56,53 | 26 | 61,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 3990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4000 | 575 | 4000 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,56,53 | 26 | 61,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 4000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4010 | 575 | 4010 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,56,53 | 26 | 61,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 4010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4020 | 575 | 4020 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,57,53 | 26 | 61,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 4020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4030 | 575 | 4030 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,57,53 | 26 | 62,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 4030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4040 | 575 | 4040 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,57,53 | 26 | 62,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 4040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4050 | 575 | 4050 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,57,53 | 26 | 62,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 4050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4060 | 575 | 4060 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,57,53 | 26 | 62,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 4060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4070 | 575 | 4070 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,57,53 | 26 | 62,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 4070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4080 | 575 | 4080 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,57,53 | 26 | 62,57,52,47,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 4080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4090 | 575 | 4090 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,57,53 | 26 | 62,57,52,48,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 4090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4100 | 575 | 4100 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,57,53 | 26 | 62,57,52,48,45,38 | 55 | 75 | 0.5" Fiberglass | 16 | 4100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4110 | 575 | 4110 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,57,53 | 26 | 62,57,52,48,45,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4120 | 575 | 4120 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,57,53 | 26 | 62,57,52,48,45,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4130 | 575 | 4130 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,60,57,53 | 26 | 62,57,52,48,45,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4140 | 575 | 4140 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,60,57,53 | 26 | 62,57,52,48,45,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4150 | 575 | 4150 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,60,57,53 | 26 | 62,57,52,48,45,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4160 | 575 | 4160 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,60,57,53 | 26 | 62,57,52,48,45,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4170 | 575 | 4170 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,60,57,53 | 27 | 62,57,53,48,45,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4180 | 575 | 4180 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,60,57,53 | 27 | 62,57,53,48,45,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4190 | 575 | 4190 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,60,57,53 | 27 | 62,57,53,48,45,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4200 | 575 | 4200 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,60,57,53 | 27 | 62,57,53,48,45,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4210 | 575 | 4210 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,64,60,57,53 | 27 | 62,57,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4220 | 575 | 4220 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4230 | 575 | 4230 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4240 | 575 | 4240 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4250 | 575 | 4250 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4260 | 575 | 4260 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4270 | 575 | 4270 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4280 | 575 | 4280 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4290 | 575 | 4290 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,63,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4300 | 575 | 4300 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4310 | 575 | 4310 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4320 | 575 | 4320 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4330 | 575 | 4330 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4340 | 575 | 4340 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4350 | 575 | 4350 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4360 | 575 | 4360 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4370 | 575 | 4370 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4380 | 575 | 4380 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4390 | 575 | 4390 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,60,57,53 | 27 | 62,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4400 | 575 | 4400 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,60,57,53 | 27 | 63,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4410 | 575 | 4410 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,61,57,53 | 27 | 63,58,53,48,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4420 | 575 | 4420 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,61,57,53 | 27 | 63,58,53,49,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4430 | 575 | 4430 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,61,57,54 | 27 | 63,58,53,49,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4440 | 575 | 4440 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,61,57,54 | 27 | 63,58,53,49,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4450 | 575 | 4450 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,61,57,54 | 27 | 63,58,53,49,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4460 | 575 | 4460 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,61,57,54 | 27 | 63,58,53,49,46,39 | 55 | 75 | 0.5" Fiberglass | 16 | 4460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4470 | 575 | 4470 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,61,57,54 | 27 | 63,58,53,49,46,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4480 | 575 | 4480 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,61,57,54 | 27 | 63,58,53,49,46,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4490 | 575 | 4490 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,61,57,54 | 27 | 63,58,53,49,46,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4500 | 575 | 4500 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,61,57,54 | 27 | 63,58,53,49,46,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4510 | 575 | 4510 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,61,57,54 | 27 | 63,58,53,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4520 | 575 | 4520 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,64,61,57,54 | 27 | 63,58,53,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4530 | 575 | 4530 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 27 | 63,58,53,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4540 | 575 | 4540 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 27 | 63,58,53,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4550 | 575 | 4550 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 27 | 63,58,53,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4560 | 575 | 4560 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 27 | 63,58,53,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4570 | 575 | 4570 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 28 | 63,58,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4580 | 575 | 4580 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 28 | 63,58,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4590 | 575 | 4590 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 28 | 63,58,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4600 | 575 | 4600 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 28 | 63,58,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4610 | 575 | 4610 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 28 | 63,58,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4620 | 575 | 4620 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 28 | 63,58,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4630 | 575 | 4630 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 28 | 63,58,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4640 | 575 | 4640 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 28 | 63,58,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4650 | 575 | 4650 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 28 | 63,58,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4660 | 575 | 4660 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,57,54 | 28 | 63,58,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4670 | 575 | 4670 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4680 | 575 | 4680 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4690 | 575 | 4690 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4700 | 575 | 4700 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4710 | 575 | 4710 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4720 | 575 | 4720 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4730 | 575 | 4730 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4740 | 575 | 4740 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4750 | 575 | 4750 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4760 | 575 | 4760 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,49,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4770 | 575 | 4770 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,50,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4780 | 575 | 4780 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,50,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4790 | 575 | 4790 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,61,58,54 | 28 | 63,59,54,50,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4800 | 575 | 4800 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 63,59,54,50,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4810 | 575 | 4810 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4820 | 575 | 4820 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,47,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4830 | 575 | 4830 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4840 | 575 | 4840 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4850 | 575 | 4850 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4860 | 575 | 4860 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,40 | 55 | 75 | 0.5" Fiberglass | 16 | 4860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4870 | 575 | 4870 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4880 | 575 | 4880 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4890 | 575 | 4890 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4900 | 575 | 4900 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4910 | 575 | 4910 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4920 | 575 | 4920 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4930 | 575 | 4930 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4940 | 575 | 4940 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4950 | 575 | 4950 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4960 | 575 | 4960 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,65,61,58,54 | 28 | 64,59,54,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4970 | 575 | 4970 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,66,61,58,54 | 28 | 64,59,54,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4980 | 575 | 4980 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,64,66,61,58,54 | 28 | 64,59,54,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4990 | 575 | 4990 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,66,62,58,54 | 30 | 64,59,55,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 4990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 5000 | 575 | 5000 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,66,62,58,54 | 30 | 64,59,55,50,48,41 | 55 | 75 | 0.5" Fiberglass | 16 | 5000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3000 | 1185 | 3000 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,66,64,63,57 | 31 | 67,61,55,47,41,33 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3010 | 1185 | 3010 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,66,64,63,57 | 31 | 67,61,55,47,41,33 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3020 | 1185 | 3020 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,66,64,63,57 | 31 | 67,61,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3030 | 1185 | 3030 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,66,64,63,57 | 31 | 67,61,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3040 | 1185 | 3040 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,66,64,63,57 | 31 | 67,61,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3050 | 1185 | 3050 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,66,64,63,57 | 31 | 67,61,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3060 | 1185 | 3060 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,66,64,63,57 | 31 | 67,61,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3070 | 1185 | 3070 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 31 | 67,61,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3080 | 1185 | 3080 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 31 | 67,61,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3090 | 1185 | 3090 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 31 | 67,61,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3100 | 1185 | 3100 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 31 | 67,61,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3110 | 1185 | 3110 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 31 | 67,61,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3120 | 1185 | 3120 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 32 | 67,62,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3130 | 1185 | 3130 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 32 | 67,62,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3140 | 1185 | 3140 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 32 | 67,62,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3150 | 1185 | 3150 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 32 | 67,62,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3160 | 1185 | 3160 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 32 | 67,62,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3170 | 1185 | 3170 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 32 | 67,62,56,47,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3180 | 1185 | 3180 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 32 | 67,62,56,48,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3190 | 1185 | 3190 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 32 | 67,62,56,48,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3200 | 1185 | 3200 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 32 | 67,62,56,48,42,34 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3210 | 1185 | 3210 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 32 | 67,62,56,48,42,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3220 | 1185 | 3220 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 32 | 67,62,56,48,42,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3230 | 1185 | 3230 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,63,57 | 33 | 68,62,56,48,42,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3240 | 1185 | 3240 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,64,57 | 33 | 68,62,56,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3250 | 1185 | 3250 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,64,57 | 33 | 68,62,56,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3260 | 1185 | 3260 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,64,57 | 33 | 68,62,56,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3270 | 1185 | 3270 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,64,57 | 33 | 68,62,56,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3280 | 1185 | 3280 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,64,58 | 33 | 68,62,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3290 | 1185 | 3290 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,64,64,58 | 33 | 68,62,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3300 | 1185 | 3300 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,65,64,58 | 33 | 68,62,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3310 | 1185 | 3310 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,66,65,64,58 | 33 | 68,62,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3320 | 1185 | 3320 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,66,65,64,58 | 33 | 68,62,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3330 | 1185 | 3330 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,66,65,64,58 | 33 | 68,62,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3340 | 1185 | 3340 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,66,65,64,58 | 33 | 68,62,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3350 | 1185 | 3350 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,66,65,64,58 | 33 | 68,62,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3360 | 1185 | 3360 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,66,65,64,58 | 33 | 68,62,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3370 | 1185 | 3370 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,67,65,64,58 | 33 | 68,62,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3380 | 1185 | 3380 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 33 | 68,63,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3390 | 1185 | 3390 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 33 | 68,63,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3400 | 1185 | 3400 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 33 | 68,63,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3410 | 1185 | 3410 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 33 | 68,63,57,48,43,35 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3420 | 1185 | 3420 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 33 | 68,63,57,48,43,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3430 | 1185 | 3430 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 33 | 68,63,57,48,43,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3440 | 1185 | 3440 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 33 | 68,63,57,48,43,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3450 | 1185 | 3450 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 33 | 68,63,57,49,43,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3460 | 1185 | 3460 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 33 | 68,63,57,49,43,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3470 | 1185 | 3470 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 33 | 68,63,57,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3480 | 1185 | 2600 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 33 | 68,63,57,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3490 | 1185 | 3490 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 34 | 69,63,57,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3500 | 1185 | 3500 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 34 | 69,63,57,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3510 | 1185 | 3510 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 34 | 69,63,57,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3520 | 1185 | 3520 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 34 | 69,63,57,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3530 | 1185 | 3530 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 34 | 69,63,57,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3540 | 1185 | 3540 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 34 | 69,63,57,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3550 | 1185 | 3550 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 34 | 69,63,57,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3560 | 1185 | 3560 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 34 | 69,63,57,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3570 | 1185 | 3570 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 34 | 69,63,58,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3580 | 1185 | 3580 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,67,65,64,58 | 34 | 69,63,58,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3590 | 1185 | 3590 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,67,65,64,58 | 34 | 69,63,58,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3600 | 1185 | 3600 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,67,65,64,58 | 34 | 69,63,58,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3610 | 1185 | 3610 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,67,65,64,58 | 34 | 69,63,58,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3620 | 1185 | 3620 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,67,65,64,58 | 34 | 69,63,58,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3630 | 1185 | 3630 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,67,65,64,58 | 34 | 69,63,58,49,44,36 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3640 | 1185 | 3640 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,67,65,64,58 | 34 | 69,63,58,49,44,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3650 | 1185 | 3650 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,67,65,64,58 | 34 | 69,63,58,49,44,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3660 | 1185 | 3660 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,67,65,64,58 | 34 | 69,63,58,49,44,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3670 | 1185 | 3670 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,67,65,64,58 | 34 | 69,64,58,49,44,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3680 | 1185 | 3680 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,67,65,64,58 | 34 | 69,64,58,49,44,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3690 | 1185 | 3690 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,67,65,64,58 | 34 | 69,64,58,49,44,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3700 | 1185 | 3700 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,67,65,64,58 | 34 | 69,64,58,49,44,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3710 | 1185 | 3710 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,67,65,64,58 | 34 | 69,64,58,49,44,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3720 | 1185 | 3720 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,67,65,64,58 | 34 | 69,64,58,49,44,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3730 | 1185 | 3730 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,67,65,64,58 | 34 | 69,64,58,49,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3740 | 1185 | 3740 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,67,65,64,58 | 34 | 69,64,58,49,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3750 | 1185 | 3750 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,67,65,64,58 | 34 | 69,64,58,50,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3760 | 1185 | 3760 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,67,65,64,58 | 34 | 69,64,58,50,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3770 | 1185 | 3770 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,67,65,64,58 | 35 | 70,64,58,50,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3780 | 1185 | 3780 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,67,65,65,58 | 35 | 70,64,58,50,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3790 | 1185 | 3790 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,67,65,65,58 | 35 | 70,64,58,50,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3800 | 1185 | 3800 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,67,65,65,58 | 35 | 70,64,58,50,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3810 | 1185 | 3810 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,68,65,65,58 | 35 | 70,64,58,50,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3820 | 1185 | 3820 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,68,65,65,58 | 35 | 70,64,58,50,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3830 | 1185 | 3830 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,68,65,65,58 | 35 | 70,64,58,50,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3840 | 1185 | 3840 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,68,65,65,58 | 35 | 70,64,58,50,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3850 | 1185 | 3850 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,68,65,65,58 | 35 | 70,64,58,50,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3860 | 1185 | 3860 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,68,65,65,58 | 35 | 70,64,58,50,45,37 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3870 | 1185 | 3870 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,68,65,65,58 | 35 | 70,64,58,50,45,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3880 | 1185 | 3880 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,68,65,65,59 | 35 | 70,64,59,50,45,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3890 | 1185 | 3890 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,65,65,59 | 35 | 70,64,59,50,45,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3900 | 1185 | 3900 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,65,65,59 | 35 | 70,64,59,50,45,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3910 | 1185 | 3910 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,65,65,59 | 35 | 70,64,59,50,45,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3920 | 1185 | 3920 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,65,65,59 | 35 | 70,64,59,50,45,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3930 | 1185 | 3930 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 35 | 70,64,59,50,45,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3940 | 1185 | 3940 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 35 | 70,64,59,50,45,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3950 | 1185 | 3950 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 35 | 70,64,59,50,45,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3960 | 1185 | 3960 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 35 | 70,64,59,50,45,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3970 | 1185 | 3970 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 35 | 70,64,59,50,45,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3980 | 1185 | 3980 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 36 | 70,65,59,50,45,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3990 | 1185 | 3990 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 36 | 70,65,59,50,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 3990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4000 | 1185 | 4000 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 36 | 70,65,59,50,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4010 | 1185 | 4010 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 36 | 70,65,59,50,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4020 | 1185 | 4020 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 36 | 70,65,59,50,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4030 | 1185 | 4030 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 36 | 70,65,59,50,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4040 | 1185 | 4040 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 36 | 70,65,59,50,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4050 | 1185 | 4050 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 36 | 70,65,59,50,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4060 | 1185 | 4060 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 36 | 70,65,59,50,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4070 | 1185 | 4070 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,68,66,65,59 | 36 | 71,65,59,51,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4080 | 1185 | 4080 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4090 | 1185 | 4090 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4100 | 1185 | 4100 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4110 | 1185 | 4110 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,38 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4120 | 1185 | 4120 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4130 | 1185 | 4130 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4140 | 1185 | 4140 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4150 | 1185 | 4150 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4160 | 1185 | 4160 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4170 | 1185 | 4170 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4180 | 1185 | 4180 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4190 | 1185 | 4190 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4200 | 1185 | 4200 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,68,66,65,59 | 36 | 71,65,59,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4210 | 1185 | 4210 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,68,66,65,59 | 36 | 71,65,59,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4220 | 1185 | 4220 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,68,66,65,59 | 36 | 71,65,59,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4230 | 1185 | 4230 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,68,66,65,59 | 36 | 71,65,60,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4240 | 1185 | 4240 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,68,66,65,59 | 36 | 71,65,60,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4250 | 1185 | 4250 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,68,66,65,59 | 36 | 71,65,60,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4260 | 1185 | 4260 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,68,66,65,59 | 36 | 71,65,60,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4270 | 1185 | 4270 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,68,66,65,59 | 36 | 71,65,60,51,46,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4280 | 1185 | 4280 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,68,66,65,59 | 36 | 71,65,60,51,47,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4290 | 1185 | 4290 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,68,66,65,59 | 36 | 71,65,60,51,47,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4300 | 1185 | 4300 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,65,59 | 36 | 71,65,60,51,47,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4310 | 1185 | 4310 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,65,59 | 37 | 71,66,60,51,47,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4320 | 1185 | 4320 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,65,59 | 37 | 71,66,60,51,47,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4330 | 1185 | 4330 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,65,59 | 37 | 71,66,60,51,47,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4340 | 1185 | 4340 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,65,59 | 37 | 71,66,60,51,47,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4350 | 1185 | 4350 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,65,59 | 37 | 71,66,60,51,47,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4360 | 1185 | 4360 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,65,59 | 37 | 71,66,60,51,47,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4370 | 1185 | 4370 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,65,59 | 37 | 71,66,60,51,47,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4380 | 1185 | 4380 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,65,59 | 37 | 71,66,60,51,47,39 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4390 | 1185 | 4390 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,65,59 | 37 | 71,66,60,51,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4400 | 1185 | 4400 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,65,59 | 38 | 72,66,60,51,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4410 | 1185 | 4410 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,66,59 | 38 | 72,66,60,51,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4420 | 1185 | 4420 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4430 | 1185 | 4430 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4440 | 1185 | 4440 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4450 | 1185 | 4450 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4460 | 1185 | 4460 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4470 | 1185 | 4470 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4480 | 1185 | 4480 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4490 | 1185 | 4490 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4500 | 1185 | 4500 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4510 | 1185 | 4510 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4520 | 1185 | 4520 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4530 | 1185 | 4530 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4540 | 1185 | 4540 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4550 | 1185 | 4550 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4560 | 1185 | 4560 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4570 | 1185 | 4570 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4580 | 1185 | 4580 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,59 | 38 | 72,66,60,52,47,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4590 | 1185 | 4590 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,59 | 38 | 72,66,60,52,48,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4600 | 1185 | 4600 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,60 | 38 | 72,66,61,52,48,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4610 | 1185 | 4610 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,60 | 38 | 72,66,61,52,48,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4620 | 1185 | 4620 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,60 | 38 | 72,66,61,52,48,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4630 | 1185 | 4630 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,60 | 38 | 72,66,61,52,48,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4640 | 1185 | 4640 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,60 | 38 | 72,66,61,52,48,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4650 | 1185 | 4650 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,60 | 38 | 72,66,61,52,48,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4660 | 1185 | 4660 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,60 | 38 | 72,66,61,52,48,40 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4670 | 1185 | 4670 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,66,66,60 | 38 | 72,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4680 | 1185 | 4680 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 38 | 72,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4690 | 1185 | 4690 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 38 | 72,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4700 | 1185 | 4700 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 38 | 72,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4710 | 1185 | 4710 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 38 | 72,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4720 | 1185 | 4720 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 38 | 72,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4730 | 1185 | 4730 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 38 | 72,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4740 | 1185 | 4740 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 38 | 72,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4750 | 1185 | 4750 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 39 | 73,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4760 | 1185 | 4760 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 39 | 73,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4770 | 1185 | 4770 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 39 | 73,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4780 | 1185 | 4780 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 39 | 73,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4790 | 1185 | 4790 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 39 | 73,67,61,52,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4800 | 1185 | 4800 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 39 | 73,67,61,53,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4810 | 1185 | 4810 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 39 | 73,67,61,53,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4820 | 1185 | 4820 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 39 | 73,67,61,53,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4830 | 1185 | 4830 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 39 | 73,67,61,53,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4840 | 1185 | 4840 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 39 | 73,67,61,53,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4850 | 1185 | 4850 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,69,67,66,60 | 39 | 73,67,61,53,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4860 | 1185 | 4860 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,70,67,66,60 | 39 | 73,67,61,53,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4870 | 1185 | 4870 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,70,67,66,60 | 39 | 73,67,61,53,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4880 | 1185 | 4880 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,70,67,66,60 | 39 | 73,67,61,53,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4890 | 1185 | 4890 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,70,67,66,60 | 39 | 73,67,61,53,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4900 | 1185 | 4900 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,70,67,66,60 | 39 | 73,67,61,53,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4910 | 1185 | 4910 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,70,67,66,60 | 39 | 73,67,61,53,48,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4920 | 1185 | 4920 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,70,67,66,60 | 39 | 73,67,61,53,49,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4930 | 1185 | 4930 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,61,53,49,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4940 | 1185 | 4940 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,61,53,49,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4950 | 1185 | 4950 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,61,53,49,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4960 | 1185 | 4960 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,61,53,49,41 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4970 | 1185 | 4970 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,61,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4980 | 1185 | 4980 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,61,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4990 | 1185 | 4990 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,61,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 4990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5000 | 1185 | 5000 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5010 | 1185 | 5010 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5020 | 1185 | 5020 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5030 | 1185 | 5030 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5040 | 1185 | 5040 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5050 | 1185 | 5050 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5060 | 1185 | 5060 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,67,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5070 | 1185 | 5070 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5080 | 1185 | 5080 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5090 | 1185 | 5090 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5100 | 1185 | 5100 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5110 | 1185 | 5110 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5120 | 1185 | 5120 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 39 | 73,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5130 | 1185 | 5130 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,66,60 | 40 | 74,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5140 | 1185 | 5140 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5150 | 1185 | 5150 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5160 | 1185 | 5160 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5170 | 1185 | 5170 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5180 | 1185 | 5180 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5190 | 1185 | 5190 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5200 | 1185 | 5200 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,53,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5210 | 1185 | 5210 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,54,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5220 | 1185 | 5220 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,54,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5230 | 1185 | 5230 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,54,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5240 | 1185 | 5240 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,54,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5250 | 1185 | 5250 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,54,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5260 | 1185 | 5260 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,54,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5270 | 1185 | 5270 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,54,49,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5280 | 1185 | 5280 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,54,50,42 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5290 | 1185 | 5290 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5300 | 1185 | 5300 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5310 | 1185 | 5310 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5320 | 1185 | 5320 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5330 | 1185 | 5330 | 1 | 0.25 | 0.75 | 0.01 | 37 | 82,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5340 | 1185 | 5340 | 1 | 0.25 | 0.75 | 0.01 | 37 | 82,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5350 | 1185 | 5350 | 1 | 0.25 | 0.75 | 0.01 | 37 | 82,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5360 | 1185 | 5360 | 1 | 0.25 | 0.75 | 0.01 | 37 | 82,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5370 | 1185 | 5370 | 1 | 0.25 | 0.75 | 0.01 | 37 | 82,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5380 | 1185 | 5380 | 1 | 0.25 | 0.75 | 0.01 | 37 | 82,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5390 | 1185 | 5390 | 1 | 0.25 | 0.75 | 0.01 | 37 | 82,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5400 | 1185 | 5400 | 1 | 0.25 | 0.75 | 0.01 | 37 | 82,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5410 | 1185 | 5410 | 1 | 0.25 | 0.75 | 0.01 | 37 | 82,77,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5420 | 1185 | 5420 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5430 | 1185 | 5430 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,70,67,67,60 | 40 | 74,68,62,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5440 | 1185 | 5440 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,70,67,67,61 | 40 | 74,68,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5450 | 1185 | 5450 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,70,67,67,61 | 40 | 74,68,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5460 | 1185 | 5460 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,70,67,67,61 | 40 | 74,68,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5470 | 1185 | 5470 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,70,67,67,61 | 40 | 74,68,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5480 | 1185 | 5480 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,70,67,67,61 | 40 | 74,68,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5490 | 1185 | 5490 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,70,67,67,61 | 40 | 74,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5500 | 1185 | 5500 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,67,67,61 | 40 | 74,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5510 | 1185 | 5510 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,67,67,61 | 40 | 74,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5520 | 1185 | 5520 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,67,67,61 | 40 | 74,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5530 | 1185 | 5530 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,67,67,61 | 40 | 74,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5540 | 1185 | 5540 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,67,67,61 | 42 | 75,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5550 | 1185 | 5550 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,67,67,61 | 42 | 75,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5560 | 1185 | 5560 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,67,67,61 | 42 | 75,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5570 | 1185 | 5570 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,67,67,61 | 42 | 75,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5580 | 1185 | 5580 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5590 | 1185 | 5590 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5600 | 1185 | 5600 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5610 | 1185 | 5610 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5620 | 1185 | 5620 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5630 | 1185 | 5630 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,54,50,43 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5640 | 1185 | 5640 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,54,50,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5650 | 1185 | 5650 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,54,50,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5660 | 1185 | 5660 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5670 | 1185 | 5670 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5680 | 1185 | 5680 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5690 | 1185 | 5690 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5700 | 1185 | 5700 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5710 | 1185 | 5710 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5720 | 1185 | 5720 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5730 | 1185 | 5730 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5740 | 1185 | 5740 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5750 | 1185 | 5750 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5760 | 1185 | 5760 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5770 | 1185 | 5770 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5780 | 1185 | 5780 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5790 | 1185 | 5790 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5800 | 1185 | 5800 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5810 | 1185 | 5810 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5820 | 1185 | 5820 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5830 | 1185 | 5830 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5840 | 1185 | 5840 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5850 | 1185 | 5850 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5860 | 1185 | 5860 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5870 | 1185 | 5870 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5880 | 1185 | 5880 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5890 | 1185 | 5890 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5900 | 1185 | 5900 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5910 | 1185 | 5910 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,63,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5920 | 1185 | 5920 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,64,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5930 | 1185 | 5930 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,64,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5940 | 1185 | 5940 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,64,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5950 | 1185 | 5950 | 1 | 0.25 | 0.75 | 0.01 | 38 | 83,78,71,68,67,61 | 42 | 75,69,64,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5960 | 1185 | 5960 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,67,61 | 42 | 75,70,64,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5970 | 1185 | 5970 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,67,61 | 42 | 75,70,64,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5980 | 1185 | 5980 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,67,61 | 43 | 76,70,64,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5990 | 1185 | 5990 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,51,44 | 55 | 75 | 0.5" Fiberglass | 24x16 | 5990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6000 | 1185 | 6000 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,51,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6010 | 1185 | 6010 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,51,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6020 | 1185 | 6020 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,51,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6030 | 1185 | 6030 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,51,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6040 | 1185 | 6040 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,51,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6050 | 1185 | 6050 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,51,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6060 | 1185 | 6060 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,51,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6070 | 1185 | 6070 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6080 | 1185 | 6080 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6090 | 1185 | 6090 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6100 | 1185 | 6100 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6110 | 1185 | 6110 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6120 | 1185 | 6120 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6130 | 1185 | 6130 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6140 | 1185 | 6140 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,55,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6150 | 1185 | 6150 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6160 | 1185 | 6160 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6170 | 1185 | 6170 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6180 | 1185 | 6180 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6190 | 1185 | 6190 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6200 | 1185 | 6200 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6210 | 1185 | 6210 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,71,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6220 | 1185 | 6220 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6230 | 1185 | 6230 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6240 | 1185 | 6240 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6250 | 1185 | 6250 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6260 | 1185 | 6260 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6270 | 1185 | 6270 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6280 | 1185 | 6280 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6290 | 1185 | 6290 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6300 | 1185 | 6300 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6310 | 1185 | 6310 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6320 | 1185 | 6320 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6330 | 1185 | 6330 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6340 | 1185 | 6340 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6350 | 1185 | 6350 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6360 | 1185 | 6360 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6370 | 1185 | 6370 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6380 | 1185 | 6380 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,45 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6390 | 1185 | 6390 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6400 | 1185 | 6400 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6410 | 1185 | 6410 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6420 | 1185 | 6420 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6430 | 1185 | 6430 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,64,56,52,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6440 | 1185 | 6440 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,61 | 43 | 76,70,65,56,52,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6450 | 1185 | 6450 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,62 | 43 | 76,70,65,56,52,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6460 | 1185 | 6460 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,62 | 44 | 77,71,65,56,52,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6470 | 1185 | 6470 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,62 | 44 | 77,71,65,56,52,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6480 | 1185 | 6480 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,62 | 44 | 77,71,65,56,52,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6490 | 1185 | 6490 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,62 | 44 | 77,71,65,56,52,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6500 | 1185 | 6500 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6510 | 1185 | 6510 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6520 | 1185 | 6520 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6530 | 1185 | 6530 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6540 | 1185 | 6540 | 1 | 0.25 | 0.75 | 0.01 | 39 | 84,79,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6550 | 1185 | 6550 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6560 | 1185 | 6560 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6570 | 1185 | 6570 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6580 | 1185 | 6580 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6590 | 1185 | 6590 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6600 | 1185 | 6600 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6610 | 1185 | 6610 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6620 | 1185 | 6620 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6630 | 1185 | 6630 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,68,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6640 | 1185 | 6640 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,69,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6650 | 1185 | 6650 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,69,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6660 | 1185 | 6660 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,69,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6670 | 1185 | 6670 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,69,68,62 | 44 | 77,71,65,56,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6680 | 1185 | 6680 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,69,68,62 | 44 | 77,71,65,57,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6690 | 1185 | 6690 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,69,68,62 | 44 | 77,71,65,57,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6700 | 1185 | 6700 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,69,68,62 | 44 | 77,71,65,57,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6710 | 1185 | 6710 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,69,68,62 | 44 | 77,71,65,57,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6720 | 1185 | 6720 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,69,68,62 | 44 | 77,71,65,57,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6730 | 1185 | 6730 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,69,68,62 | 44 | 77,71,65,57,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6740 | 1185 | 6740 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,69,68,62 | 44 | 77,71,65,57,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6750 | 1185 | 6750 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,72,69,68,62 | 44 | 77,71,65,57,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6760 | 1185 | 6760 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6770 | 1185 | 6770 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6780 | 1185 | 6780 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6790 | 1185 | 6790 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,46 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6800 | 1185 | 6800 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6810 | 1185 | 6810 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6820 | 1185 | 6820 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6830 | 1185 | 6830 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6840 | 1185 | 6840 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6850 | 1185 | 6850 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6860 | 1185 | 6860 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6870 | 1185 | 6870 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6880 | 1185 | 6880 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6890 | 1185 | 6890 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6900 | 1185 | 6900 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6910 | 1185 | 6910 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6920 | 1185 | 6920 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6930 | 1185 | 6930 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6940 | 1185 | 6940 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6950 | 1185 | 6950 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6960 | 1185 | 6960 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,53,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6970 | 1185 | 6970 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,68,62 | 44 | 77,71,65,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6980 | 1185 | 6980 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,69,62 | 45 | 78,71,65,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6990 | 1185 | 6990 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,69,62 | 45 | 78,71,65,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 6990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7000 | 1185 | 7000 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7010 | 1185 | 7010 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7020 | 1185 | 7020 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,72,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7030 | 1185 | 7030 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7040 | 1185 | 7040 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7050 | 1185 | 7050 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7060 | 1185 | 7060 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7070 | 1185 | 7070 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7080 | 1185 | 7080 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7090 | 1185 | 7090 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7100 | 1185 | 7100 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7110 | 1185 | 7110 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7120 | 1185 | 7120 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7130 | 1185 | 7130 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7140 | 1185 | 7140 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7150 | 1185 | 7150 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7160 | 1185 | 7160 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7170 | 1185 | 7170 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7180 | 1185 | 7180 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7190 | 1185 | 7190 | 1 | 0.25 | 0.75 | 0.01 | 40 | 85,80,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7200 | 1185 | 7200 | 1 | 0.25 | 0.75 | 0.01 | 42 | 85,81,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7210 | 1185 | 7210 | 1 | 0.25 | 0.75 | 0.01 | 42 | 85,81,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7220 | 1185 | 7220 | 1 | 0.25 | 0.75 | 0.01 | 42 | 85,81,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7230 | 1185 | 7230 | 1 | 0.25 | 0.75 | 0.01 | 42 | 85,81,73,69,69,62 | 45 | 78,72,66,57,54,47 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7240 | 1185 | 7240 | 1 | 0.25 | 0.75 | 0.01 | 42 | 85,81,73,69,69,62 | 45 | 78,72,66,57,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7250 | 1185 | 7250 | 1 | 0.25 | 0.75 | 0.01 | 42 | 85,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7260 | 1185 | 7260 | 1 | 0.25 | 0.75 | 0.01 | 42 | 85,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7270 | 1185 | 7270 | 1 | 0.25 | 0.75 | 0.01 | 42 | 85,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7280 | 1185 | 7280 | 1 | 0.25 | 0.75 | 0.01 | 42 | 85,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7290 | 1185 | 7290 | 1 | 0.25 | 0.75 | 0.01 | 42 | 85,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7300 | 1185 | 7300 | 1 | 0.25 | 0.75 | 0.01 | 42 | 85,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7310 | 1185 | 7310 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7320 | 1185 | 7320 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7330 | 1185 | 7330 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7340 | 1185 | 7340 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7350 | 1185 | 7350 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7360 | 1185 | 7360 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7370 | 1185 | 7370 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7380 | 1185 | 7380 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7390 | 1185 | 7390 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7400 | 1185 | 7400 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7410 | 1185 | 7410 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7410 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7420 | 1185 | 7420 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7420 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7430 | 1185 | 7430 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7430 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7440 | 1185 | 7440 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7440 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7450 | 1185 | 7450 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7450 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7460 | 1185 | 7460 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,54,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7460 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7470 | 1185 | 7470 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7470 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7480 | 1185 | 7480 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7480 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7490 | 1185 | 7490 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7490 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7500 | 1185 | 7500 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7500 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7510 | 1185 | 7510 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7510 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7520 | 1185 | 7520 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7520 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7530 | 1185 | 7530 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 45 | 78,72,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7530 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7540 | 1185 | 7540 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 47 | 79,72,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7540 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7550 | 1185 | 7550 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 47 | 79,72,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7550 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7560 | 1185 | 7560 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 47 | 79,72,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7560 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7570 | 1185 | 7570 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 47 | 79,72,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7570 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7580 | 1185 | 7580 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 47 | 79,72,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7580 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7590 | 1185 | 7590 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 47 | 79,73,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7590 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7600 | 1185 | 7600 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 47 | 79,73,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7600 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7610 | 1185 | 7610 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 47 | 79,73,66,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7610 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7620 | 1185 | 7620 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,62 | 47 | 79,73,67,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7620 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7630 | 1185 | 7630 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7630 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7640 | 1185 | 7640 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7640 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7650 | 1185 | 7650 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7650 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7660 | 1185 | 7660 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7660 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7670 | 1185 | 7670 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7670 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7680 | 1185 | 7680 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7680 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7690 | 1185 | 7690 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7690 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7700 | 1185 | 7700 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,48 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7700 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7710 | 1185 | 7710 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7710 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7720 | 1185 | 7720 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7720 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7730 | 1185 | 7730 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7730 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7740 | 1185 | 7740 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7740 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7750 | 1185 | 7750 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7750 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7760 | 1185 | 7760 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7760 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7770 | 1185 | 7770 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7770 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7780 | 1185 | 7780 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7780 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7790 | 1185 | 7790 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7790 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7800 | 1185 | 7800 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7800 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7810 | 1185 | 7810 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7810 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7820 | 1185 | 7820 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7820 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7830 | 1185 | 7830 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7830 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7840 | 1185 | 7840 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7840 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7850 | 1185 | 7850 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7850 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7860 | 1185 | 7860 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7860 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7870 | 1185 | 7870 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,58,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7870 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7880 | 1185 | 7880 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7880 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7890 | 1185 | 7890 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7890 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7900 | 1185 | 7900 | 1 | 0.25 | 0.75 | 0.01 | 42 | 86,81,73,69,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7900 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7910 | 1185 | 7910 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,73,70,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7910 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7920 | 1185 | 7920 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,73,70,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7920 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7930 | 1185 | 7930 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,73,70,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7930 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7940 | 1185 | 7940 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,73,70,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7940 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7950 | 1185 | 7950 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7950 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7960 | 1185 | 7960 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7960 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7970 | 1185 | 7970 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7970 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7980 | 1185 | 7980 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7980 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7990 | 1185 | 7990 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 7990 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8000 | 1185 | 8000 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,55,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8000 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8010 | 1185 | 8010 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8010 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8020 | 1185 | 8020 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8020 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8030 | 1185 | 8030 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8030 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8040 | 1185 | 8040 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8040 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8050 | 1185 | 8050 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8050 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8060 | 1185 | 8060 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8060 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8070 | 1185 | 8070 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8070 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8080 | 1185 | 8080 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8080 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8090 | 1185 | 8090 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8090 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8100 | 1185 | 8100 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8100 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8110 | 1185 | 8110 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8110 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8120 | 1185 | 8120 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,69,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8120 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8130 | 1185 | 8130 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 47 | 79,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8130 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8140 | 1185 | 8140 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8140 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8150 | 1185 | 8150 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8150 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8160 | 1185 | 8160 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8160 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8170 | 1185 | 8170 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8170 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8180 | 1185 | 8180 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8180 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8190 | 1185 | 8190 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,73,67,59,56,49 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8190 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8200 | 1185 | 8200 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,73,67,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8200 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8210 | 1185 | 8210 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,73,67,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8210 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8220 | 1185 | 8220 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,73,67,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8220 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8230 | 1185 | 8230 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,67,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8230 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8240 | 1185 | 8240 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,67,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8240 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8250 | 1185 | 8250 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,67,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8250 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8260 | 1185 | 8260 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,67,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8260 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8270 | 1185 | 8270 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,67,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8270 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8280 | 1185 | 8280 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,67,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8280 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8290 | 1185 | 8290 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,68,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8290 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8300 | 1185 | 8300 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,68,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8300 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8310 | 1185 | 8310 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,68,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8310 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8320 | 1185 | 8320 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,68,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8320 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8330 | 1185 | 8330 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,68,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8330 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8340 | 1185 | 8340 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,68,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8340 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8350 | 1185 | 8350 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,68,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8350 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8360 | 1185 | 8360 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,68,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8360 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8370 | 1185 | 8370 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,68,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8370 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8380 | 1185 | 8380 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,68,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8380 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8390 | 1185 | 8390 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,68,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8390 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8400 | 1185 | 8400 | 1 | 0.25 | 0.75 | 0.01 | 43 | 87,82,74,70,70,63 | 48 | 80,74,68,59,56,50 | 55 | 75 | 0.5" Fiberglass | 24x16 | 8400 | 0.5" Fiberglass | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 75 | 45 | 75 | 1 | 0.25 | 0.75 | 0.01 | 15 | 60,55,45,42,37,38 | 6 | 47,39,28,24,20,19 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 75 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 80 | 45 | 80 | 1 | 0.25 | 0.75 | 0.01 | 16 | 61,56,46,43,38,39 | 7 | 48,40,29,25,21,20 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 80 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 85 | 45 | 85 | 1 | 0.25 | 0.75 | 0.01 | 17 | 62,57,47,44,39,39 | 8 | 49,41,30,26,22,20 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 85 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 90 | 45 | 90 | 1 | 0.25 | 0.75 | 0.01 | 19 | 63,58,48,45,40,40 | 10 | 50,41,31,26,22,21 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 90 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 95 | 45 | 95 | 1 | 0.25 | 0.75 | 0.01 | 19 | 63,59,49,46,40,40 | 11 | 51,42,32,27,23,21 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 95 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 100 | 45 | 100 | 1 | 0.25 | 0.75 | 0.01 | 20 | 64,60,49,47,41,41 | 12 | 52,43,33,28,24,22 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 105 | 45 | 105 | 1 | 0.25 | 0.75 | 0.01 | 21 | 65,61,50,48,42,42 | 12 | 52,44,33,28,24,22 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 105 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 110 | 45 | 110 | 1 | 0.25 | 0.75 | 0.01 | 22 | 66,61,51,48,42,42 | 13 | 53,44,34,29,25,23 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 115 | 45 | 115 | 1 | 0.25 | 0.75 | 0.01 | 22 | 66,62,52,49,43,43 | 15 | 54,45,35,30,25,23 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 115 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 120 | 45 | 120 | 1 | 0.25 | 0.75 | 0.01 | 24 | 67,63,52,50,43,43 | 15 | 54,46,35,30,26,24 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 125 | 45 | 125 | 1 | 0.25 | 0.75 | 0.01 | 25 | 68,64,53,50,44,43 | 16 | 55,46,36,31,26,24 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 125 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 130 | 45 | 130 | 1 | 0.25 | 0.75 | 0.01 | 25 | 68,64,53,51,44,44 | 16 | 55,47,36,31,27,24 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 135 | 45 | 135 | 1 | 0.25 | 0.75 | 0.01 | 26 | 69,65,54,51,45,44 | 17 | 56,48,37,32,27,25 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 135 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 140 | 45 | 140 | 1 | 0.25 | 0.75 | 0.01 | 28 | 70,66,54,52,45,45 | 17 | 56,48,37,32,27,25 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 145 | 45 | 145 | 1 | 0.25 | 0.75 | 0.01 | 28 | 70,66,55,52,46,45 | 19 | 57,49,38,33,28,25 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 145 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 150 | 45 | 150 | 1 | 0.25 | 0.75 | 0.01 | 29 | 71,67,55,53,46,45 | 19 | 57,49,38,33,28,26 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 155 | 45 | 155 | 1 | 0.25 | 0.75 | 0.01 | 29 | 71,68,56,53,47,46 | 20 | 58,50,39,34,29,26 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 155 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 160 | 45 | 160 | 1 | 0.25 | 0.75 | 0.01 | 30 | 72,68,56,54,47,46 | 20 | 58,50,39,34,29,26 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 165 | 45 | 165 | 1 | 0.25 | 0.75 | 0.01 | 30 | 72,69,57,54,47,46 | 21 | 59,51,40,35,29,27 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 165 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 170 | 45 | 170 | 1 | 0.25 | 0.75 | 0.01 | 31 | 73,69,57,55,48,47 | 21 | 59,51,40,35,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 175 | 45 | 175 | 1 | 0.25 | 0.75 | 0.01 | 31 | 73,70,58,55,48,47 | 21 | 59,52,41,36,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 175 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 180 | 45 | 180 | 1 | 0.25 | 0.75 | 0.01 | 33 | 74,70,58,56,49,47 | 22 | 60,52,41,36,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 185 | 45 | 185 | 1 | 0.25 | 0.75 | 0.01 | 33 | 74,71,59,56,49,48 | 22 | 60,53,41,36,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 185 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 190 | 45 | 190 | 1 | 0.25 | 0.75 | 0.01 | 34 | 75,71,59,57,49,48 | 24 | 61,53,42,37,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 195 | 45 | 195 | 1 | 0.25 | 0.75 | 0.01 | 34 | 75,72,59,57,50,48 | 24 | 61,53,42,37,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 195 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 200 | 45 | 200 | 1 | 0.25 | 0.75 | 0.01 | 34 | 75,72,60,57,50,48 | 24 | 61,54,43,37,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 205 | 45 | 205 | 1 | 0.25 | 0.75 | 0.01 | 35 | 76,73,60,58,50,49 | 25 | 62,54,43,38,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 205 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 210 | 45 | 210 | 1 | 0.25 | 0.75 | 0.01 | 35 | 76,73,60,58,51,49 | 25 | 62,54,43,38,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 215 | 45 | 215 | 1 | 0.25 | 0.75 | 0.01 | 36 | 77,73,61,58,51,49 | 25 | 62,55,44,38,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 215 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 220 | 45 | 220 | 1 | 0.25 | 0.75 | 0.01 | 36 | 77,74,61,59,51,49 | 26 | 63,55,44,39,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 225 | 45 | 225 | 1 | 0.25 | 0.75 | 0.01 | 36 | 77,74,61,59,51,50 | 26 | 63,56,44,39,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 225 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 230 | 45 | 230 | 1 | 0.25 | 0.75 | 0.01 | 38 | 78,75,62,60,52,50 | 26 | 63,56,45,39,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 235 | 45 | 235 | 1 | 0.25 | 0.75 | 0.01 | 38 | 78,75,62,60,52,50 | 28 | 64,56,45,40,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 235 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 240 | 45 | 240 | 1 | 0.25 | 0.75 | 0.01 | 38 | 78,75,62,60,52,50 | 28 | 64,57,45,40,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 245 | 45 | 245 | 1 | 0.25 | 0.75 | 0.01 | 39 | 79,76,63,60,53,51 | 28 | 64,57,46,40,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 245 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 250 | 45 | 250 | 1 | 0.25 | 0.75 | 0.01 | 39 | 79,76,63,61,53,51 | 29 | 65,57,46,41,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 255 | 45 | 255 | 1 | 0.25 | 0.75 | 0.01 | 39 | 79,76,63,61,53,51 | 29 | 65,57,46,41,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 255 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 260 | 45 | 260 | 1 | 0.25 | 0.75 | 0.01 | 40 | 80,77,64,61,53,51 | 29 | 65,58,46,41,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 265 | 45 | 265 | 1 | 0.25 | 0.75 | 0.01 | 40 | 80,77,64,62,54,51 | 29 | 65,58,47,41,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 265 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 270 | 45 | 270 | 1 | 0.25 | 0.75 | 0.01 | 40 | 80,77,64,62,54,52 | 30 | 66,58,47,42,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 275 | 45 | 275 | 1 | 0.25 | 0.75 | 0.01 | 42 | 81,78,64,62,54,52 | 30 | 66,59,47,42,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 275 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 280 | 45 | 280 | 1 | 0.25 | 0.75 | 0.01 | 42 | 81,78,65,63,54,52 | 30 | 66,59,47,42,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 285 | 45 | 285 | 1 | 0.25 | 0.75 | 0.01 | 42 | 81,78,65,63,55,52 | 30 | 66,59,48,42,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 285 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 290 | 45 | 290 | 1 | 0.25 | 0.75 | 0.01 | 42 | 81,79,65,63,55,52 | 31 | 67,59,48,43,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 295 | 45 | 295 | 1 | 0.25 | 0.75 | 0.01 | 43 | 82,79,65,63,55,53 | 31 | 67,60,48,43,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 295 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 300 | 45 | 300 | 1 | 0.25 | 0.75 | 0.01 | 40 | 82,79,66,64,55,53 | 31 | 67,60,48,43,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 305 | 45 | 305 | 1 | 0.25 | 0.75 | 0.01 | 42 | 82,80,66,64,55,53 | 31 | 67,60,49,43,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 305 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 310 | 45 | 310 | 1 | 0.25 | 0.75 | 0.01 | 42 | 83,80,66,64,56,53 | 33 | 68,61,49,44,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 315 | 45 | 315 | 1 | 0.25 | 0.75 | 0.01 | 42 | 83,80,66,64,56,53 | 33 | 68,61,49,44,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 315 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 320 | 45 | 320 | 1 | 0.25 | 0.75 | 0.01 | 42 | 83,80,67,65,56,53 | 33 | 68,61,49,44,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 325 | 45 | 325 | 1 | 0.25 | 0.75 | 0.01 | 43 | 83,81,67,65,56,54 | 33 | 68,61,50,44,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 325 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 330 | 45 | 330 | 1 | 0.25 | 0.75 | 0.01 | 43 | 84,81,67,65,56,54 | 33 | 68,61,50,44,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 335 | 45 | 335 | 1 | 0.25 | 0.75 | 0.01 | 43 | 84,81,67,65,57,54 | 34 | 69,62,50,45,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 335 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 340 | 45 | 340 | 1 | 0.25 | 0.75 | 0.01 | 44 | 84,82,68,65,57,54 | 34 | 69,62,50,45,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 345 | 45 | 345 | 1 | 0.25 | 0.75 | 0.01 | 44 | 84,82,68,66,57,54 | 34 | 69,62,50,45,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 345 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 350 | 45 | 350 | 1 | 0.25 | 0.75 | 0.01 | 44 | 84,82,68,66,57,54 | 34 | 69,62,51,45,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 355 | 45 | 355 | 1 | 0.25 | 0.75 | 0.01 | 44 | 85,82,68,66,57,55 | 34 | 69,63,51,45,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 355 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 360 | 45 | 360 | 1 | 0.25 | 0.75 | 0.01 | 45 | 85,83,68,66,58,55 | 35 | 70,63,51,46,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 365 | 45 | 365 | 1 | 0.25 | 0.75 | 0.01 | 45 | 85,83,69,67,58,55 | 35 | 70,63,51,46,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 365 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 370 | 45 | 370 | 1 | 0.25 | 0.75 | 0.01 | 45 | 85,83,69,67,58,55 | 35 | 70,63,52,46,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 375 | 45 | 375 | 1 | 0.25 | 0.75 | 0.01 | 45 | 86,83,69,67,58,55 | 35 | 70,63,52,46,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 375 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 380 | 45 | 380 | 1 | 0.25 | 0.75 | 0.01 | 46 | 86,84,69,67,58,55 | 35 | 70,64,52,46,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 385 | 45 | 385 | 1 | 0.25 | 0.75 | 0.01 | 46 | 86,84,69,67,58,55 | 36 | 71,64,52,47,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 385 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 390 | 45 | 390 | 1 | 0.25 | 0.75 | 0.01 | 46 | 86,84,70,68,59,56 | 36 | 71,64,52,47,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 395 | 45 | 395 | 1 | 0.25 | 0.75 | 0.01 | 46 | 86,84,70,68,59,56 | 36 | 71,64,52,47,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 395 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 4 | 400 | 45 | 400 | 1 | 0.25 | 0.75 | 0.01 | 46 | 87,84,70,68,59,56 | 36 | 71,64,53,47,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 4 | 400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 150 | 65 | 150 | 1 | 0.25 | 0.75 | 0.02 | 21 | 65,59,50,46,41,41 | 8 | 49,41,32,27,26,21 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 155 | 65 | 155 | 1 | 0.25 | 0.75 | 0.02 | 21 | 65,59,50,46,41,41 | 8 | 49,41,33,27,26,22 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 155 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 160 | 65 | 160 | 1 | 0.25 | 0.75 | 0.02 | 21 | 65,59,51,47,41,41 | 10 | 50,42,33,28,26,22 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 165 | 65 | 165 | 1 | 0.25 | 0.75 | 0.02 | 22 | 66,60,51,47,42,41 | 10 | 50,42,34,28,26,22 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 165 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 170 | 65 | 170 | 1 | 0.25 | 0.75 | 0.03 | 22 | 66,60,52,48,42,42 | 10 | 50,43,34,28,27,22 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 175 | 65 | 175 | 1 | 0.25 | 0.75 | 0.03 | 22 | 66,60,52,48,42,42 | 11 | 51,43,35,29,27,22 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 175 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 180 | 65 | 180 | 1 | 0.25 | 0.75 | 0.03 | 24 | 67,61,52,48,42,42 | 11 | 51,43,35,29,27,22 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 185 | 65 | 185 | 1 | 0.25 | 0.75 | 0.03 | 24 | 67,61,53,49,43,42 | 11 | 51,44,35,29,27,22 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 185 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 190 | 65 | 190 | 1 | 0.25 | 0.75 | 0.03 | 24 | 67,61,53,49,43,43 | 12 | 52,44,36,30,27,22 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 195 | 65 | 195 | 1 | 0.25 | 0.75 | 0.03 | 24 | 67,62,53,49,43,43 | 12 | 52,44,36,30,28,23 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 195 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 200 | 65 | 200 | 1 | 0.25 | 0.75 | 0.04 | 25 | 68,62,54,50,43,43 | 12 | 52,45,36,30,28,23 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 205 | 65 | 205 | 1 | 0.25 | 0.75 | 0.04 | 25 | 68,62,54,50,44,43 | 12 | 52,45,37,31,28,23 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 205 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 210 | 65 | 210 | 1 | 0.25 | 0.75 | 0.04 | 25 | 68,63,54,50,44,43 | 13 | 53,45,37,31,28,23 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 215 | 65 | 215 | 1 | 0.25 | 0.75 | 0.04 | 25 | 68,63,54,51,44,43 | 13 | 53,46,37,31,28,23 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 215 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 220 | 65 | 220 | 1 | 0.25 | 0.75 | 0.04 | 26 | 69,63,55,51,44,44 | 13 | 53,46,38,31,28,23 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 225 | 65 | 225 | 1 | 0.25 | 0.75 | 0.05 | 26 | 69,63,55,51,44,44 | 13 | 53,46,38,32,29,23 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 225 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 230 | 65 | 230 | 1 | 0.25 | 0.75 | 0.05 | 26 | 69,64,55,51,45,44 | 15 | 54,47,38,32,29,23 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 235 | 65 | 235 | 1 | 0.25 | 0.75 | 0.05 | 26 | 69,64,56,52,45,44 | 15 | 54,47,38,32,29,23 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 235 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 240 | 65 | 240 | 1 | 0.25 | 0.75 | 0.05 | 28 | 70,64,56,52,45,44 | 15 | 54,47,39,32,29,24 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 245 | 65 | 245 | 1 | 0.25 | 0.75 | 0.05 | 28 | 70,64,56,52,45,44 | 15 | 54,47,39,33,29,24 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 245 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 250 | 65 | 250 | 1 | 0.25 | 0.75 | 0.06 | 28 | 70,65,56,52,45,45 | 15 | 54,48,39,33,29,24 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 255 | 65 | 255 | 1 | 0.25 | 0.75 | 0.06 | 28 | 70,65,57,53,46,45 | 16 | 55,48,39,33,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 255 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 260 | 65 | 260 | 1 | 0.25 | 0.75 | 0.06 | 28 | 70,65,57,53,46,45 | 16 | 55,48,40,33,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 265 | 65 | 265 | 1 | 0.25 | 0.75 | 0.06 | 29 | 71,65,57,53,46,45 | 16 | 55,48,40,34,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 265 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 270 | 65 | 270 | 1 | 0.25 | 0.75 | 0.07 | 29 | 71,65,57,53,46,45 | 17 | 55,49,40,34,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 275 | 65 | 275 | 1 | 0.25 | 0.75 | 0.07 | 29 | 71,66,57,54,46,45 | 17 | 56,49,41,34,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 275 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 280 | 65 | 280 | 1 | 0.25 | 0.75 | 0.07 | 29 | 71,66,58,54,46,45 | 17 | 56,49,41,34,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 285 | 65 | 285 | 1 | 0.25 | 0.75 | 0.07 | 29 | 71,66,58,54,47,46 | 17 | 56,49,41,34,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 285 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 290 | 65 | 290 | 1 | 0.25 | 0.75 | 0.08 | 29 | 71,66,58,54,47,46 | 18 | 56,50,41,35,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 295 | 65 | 295 | 1 | 0.25 | 0.75 | 0.08 | 30 | 72,67,58,55,47,46 | 18 | 56,50,41,35,31,24 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 295 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 300 | 65 | 300 | 1 | 0.25 | 0.75 | 0.08 | 26 | 72,67,59,55,47,46 | 18 | 56,50,42,35,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 305 | 65 | 305 | 1 | 0.25 | 0.75 | 0.08 | 26 | 72,67,59,55,47,46 | 19 | 57,50,42,35,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 305 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 310 | 65 | 310 | 1 | 0.25 | 0.75 | 0.09 | 26 | 72,67,59,55,47,46 | 19 | 57,50,42,35,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 315 | 65 | 315 | 1 | 0.25 | 0.75 | 0.09 | 26 | 72,67,59,55,47,46 | 19 | 57,51,42,36,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 315 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 320 | 65 | 320 | 1 | 0.25 | 0.75 | 0.09 | 26 | 72,67,59,56,48,46 | 19 | 57,51,43,36,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 325 | 65 | 325 | 1 | 0.25 | 0.75 | 0.1 | 28 | 73,68,60,56,48,47 | 19 | 57,51,43,36,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 325 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 330 | 65 | 330 | 1 | 0.25 | 0.75 | 0.1 | 28 | 73,68,60,56,48,47 | 19 | 57,51,43,36,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 335 | 65 | 335 | 1 | 0.25 | 0.75 | 0.1 | 28 | 73,68,60,56,48,47 | 20 | 58,51,43,36,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 335 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 340 | 65 | 340 | 1 | 0.25 | 0.75 | 0.1 | 28 | 73,68,60,56,48,47 | 20 | 58,52,43,36,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 345 | 65 | 345 | 1 | 0.25 | 0.75 | 0.11 | 28 | 73,68,60,57,48,47 | 20 | 58,52,44,37,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 345 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 350 | 65 | 350 | 1 | 0.25 | 0.75 | 0.11 | 28 | 73,69,60,57,48,47 | 20 | 58,52,44,37,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 355 | 65 | 355 | 1 | 0.25 | 0.75 | 0.11 | 29 | 74,69,61,57,49,47 | 20 | 58,52,44,37,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 355 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 360 | 65 | 360 | 1 | 0.25 | 0.75 | 0.12 | 29 | 74,69,61,57,49,47 | 20 | 58,52,44,37,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 365 | 65 | 365 | 1 | 0.25 | 0.75 | 0.12 | 29 | 74,69,61,57,49,47 | 21 | 59,52,44,37,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 365 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 370 | 65 | 370 | 1 | 0.25 | 0.75 | 0.12 | 29 | 74,69,61,57,49,48 | 21 | 59,53,44,37,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 375 | 65 | 375 | 1 | 0.25 | 0.75 | 0.13 | 29 | 74,69,61,58,49,48 | 21 | 59,53,45,38,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 375 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 380 | 65 | 380 | 1 | 0.25 | 0.75 | 0.13 | 29 | 74,69,61,58,49,48 | 21 | 59,53,45,38,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 385 | 65 | 385 | 1 | 0.25 | 0.75 | 0.13 | 30 | 74,70,62,58,49,48 | 21 | 59,53,45,38,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 385 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 390 | 65 | 390 | 1 | 0.25 | 0.75 | 0.14 | 30 | 75,70,62,58,49,48 | 21 | 59,53,45,38,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 395 | 65 | 395 | 1 | 0.25 | 0.75 | 0.14 | 30 | 75,70,62,58,50,48 | 23 | 59,54,45,38,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 395 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 400 | 65 | 400 | 1 | 0.25 | 0.75 | 0.14 | 30 | 75,70,62,58,50,48 | 23 | 60,54,45,38,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 405 | 65 | 405 | 1 | 0.25 | 0.75 | 0.15 | 30 | 75,70,62,59,50,48 | 23 | 60,54,46,38,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 405 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 410 | 65 | 410 | 1 | 0.25 | 0.75 | 0.15 | 30 | 75,70,62,59,50,48 | 23 | 60,54,46,39,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 415 | 65 | 415 | 1 | 0.25 | 0.75 | 0.15 | 30 | 75,70,63,59,50,48 | 23 | 60,54,46,39,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 415 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 420 | 65 | 420 | 1 | 0.25 | 0.75 | 0.16 | 31 | 75,71,63,59,50,49 | 23 | 60,54,46,39,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 425 | 65 | 425 | 1 | 0.25 | 0.75 | 0.16 | 31 | 75,71,63,59,50,49 | 23 | 60,54,46,39,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 425 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 430 | 65 | 430 | 1 | 0.25 | 0.75 | 0.17 | 31 | 76,71,63,59,50,49 | 24 | 60,55,46,39,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 435 | 65 | 435 | 1 | 0.25 | 0.75 | 0.17 | 31 | 76,71,63,59,50,49 | 24 | 60,55,47,39,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 435 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 440 | 65 | 440 | 1 | 0.25 | 0.75 | 0.17 | 31 | 76,71,63,60,51,49 | 24 | 61,55,47,39,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 445 | 65 | 445 | 1 | 0.25 | 0.75 | 0.18 | 31 | 76,71,63,60,51,49 | 24 | 61,55,47,40,34,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 445 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 450 | 65 | 450 | 1 | 0.25 | 0.75 | 0.18 | 31 | 76,71,64,60,51,49 | 24 | 61,55,47,40,34,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 455 | 65 | 455 | 1 | 0.25 | 0.75 | 0.19 | 32 | 76,72,64,60,51,49 | 24 | 61,55,47,40,34,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 455 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 460 | 65 | 460 | 1 | 0.25 | 0.75 | 0.19 | 32 | 76,72,64,60,51,49 | 24 | 61,55,47,40,34,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 465 | 65 | 465 | 1 | 0.25 | 0.75 | 0.19 | 32 | 76,72,64,60,51,49 | 25 | 61,56,47,40,34,26 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 465 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 470 | 65 | 470 | 1 | 0.25 | 0.75 | 0.2 | 32 | 76,72,64,60,51,49 | 25 | 61,56,48,40,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 475 | 65 | 475 | 1 | 0.25 | 0.75 | 0.2 | 33 | 77,72,64,61,51,50 | 25 | 61,56,48,40,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 475 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 480 | 65 | 480 | 1 | 0.25 | 0.75 | 0.21 | 33 | 77,72,64,61,51,50 | 25 | 62,56,48,40,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 485 | 65 | 485 | 1 | 0.25 | 0.75 | 0.21 | 33 | 77,72,64,61,51,50 | 25 | 62,56,48,41,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 485 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 490 | 65 | 490 | 1 | 0.25 | 0.75 | 0.22 | 33 | 77,72,65,61,51,50 | 25 | 62,56,48,41,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 495 | 65 | 495 | 1 | 0.25 | 0.75 | 0.22 | 33 | 77,73,65,61,52,50 | 25 | 62,56,48,41,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 495 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 500 | 65 | 500 | 1 | 0.25 | 0.75 | 0.22 | 33 | 77,73,65,61,52,50 | 26 | 62,57,48,41,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 505 | 65 | 505 | 1 | 0.25 | 0.75 | 0.23 | 33 | 77,73,65,61,52,50 | 26 | 62,57,49,41,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 505 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 510 | 65 | 510 | 1 | 0.25 | 0.75 | 0.23 | 33 | 77,73,65,61,52,50 | 26 | 62,57,49,41,35,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 515 | 65 | 515 | 1 | 0.25 | 0.75 | 0.24 | 33 | 77,73,65,62,52,50 | 26 | 62,57,49,41,35,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 515 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 520 | 65 | 520 | 1 | 0.25 | 0.75 | 0.24 | 34 | 78,73,65,62,52,50 | 26 | 62,57,49,41,35,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 525 | 65 | 525 | 1 | 0.25 | 0.75 | 0.25 | 34 | 78,73,65,62,52,50 | 26 | 63,57,49,41,35,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 525 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 530 | 65 | 530 | 1 | 0.25 | 0.75 | 0.25 | 34 | 78,73,66,62,52,50 | 26 | 63,57,49,42,35,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 535 | 65 | 535 | 1 | 0.25 | 0.75 | 0.26 | 34 | 78,73,66,62,52,50 | 26 | 63,57,49,42,35,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 535 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 540 | 65 | 540 | 1 | 0.25 | 0.75 | 0.26 | 34 | 78,74,66,62,52,50 | 27 | 63,58,49,42,35,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 545 | 65 | 545 | 1 | 0.25 | 0.75 | 0.27 | 34 | 78,74,66,62,52,51 | 27 | 63,58,50,42,35,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 545 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 550 | 65 | 550 | 1 | 0.25 | 0.75 | 0.27 | 34 | 78,74,66,62,53,51 | 27 | 63,58,50,42,35,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 6 | 550 | 65 | 550 | 1 | 0.25 | 0.75 | 0.27 | 34 | 78,74,66,62,53,51 | 27 | 63,58,50,42,35,27 | 55 | 75 | 0.5" Fiber Free Foam | 6 | 550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 400 | 125 | 400 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,61,51,48,44,44 | 12 | 52,44,36,31,29,23 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 405 | 125 | 405 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,61,51,48,44,44 | 12 | 52,44,37,31,29,23 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 405 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 410 | 125 | 410 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,61,51,49,44,44 | 12 | 52,44,37,31,29,23 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 415 | 125 | 415 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,61,51,49,44,44 | 12 | 52,44,37,31,29,23 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 415 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 420 | 125 | 420 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,61,51,49,44,44 | 12 | 52,44,37,31,29,23 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 425 | 125 | 425 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,62,51,49,44,44 | 12 | 52,44,37,31,29,23 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 425 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 430 | 125 | 430 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,62,52,49,45,44 | 13 | 53,44,37,32,29,23 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 435 | 125 | 435 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,62,52,49,45,45 | 13 | 53,45,37,32,29,23 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 435 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 440 | 125 | 440 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,62,52,49,45,45 | 13 | 53,45,38,32,29,23 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 445 | 125 | 445 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,62,52,50,45,45 | 13 | 53,45,38,32,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 445 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 450 | 125 | 450 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,62,52,50,45,45 | 13 | 53,45,38,32,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 455 | 125 | 455 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,62,52,50,45,45 | 13 | 53,45,38,32,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 455 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 460 | 125 | 460 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,62,53,50,45,45 | 13 | 53,45,38,32,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 465 | 125 | 465 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,62,53,50,45,45 | 13 | 53,45,38,32,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 465 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 470 | 125 | 470 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,63,53,50,45,45 | 15 | 54,45,38,33,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 475 | 125 | 475 | 1 | 0.25 | 0.75 | 0.01 | 22 | 69,63,53,50,46,45 | 15 | 54,46,39,33,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 475 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 480 | 125 | 480 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,63,53,51,46,45 | 15 | 54,46,39,33,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 485 | 125 | 485 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,63,53,51,46,45 | 15 | 54,46,39,33,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 485 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 490 | 125 | 490 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,63,53,51,46,45 | 15 | 54,46,39,33,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 495 | 125 | 495 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,63,53,51,46,46 | 15 | 54,46,39,33,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 495 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 500 | 125 | 500 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,63,54,51,46,46 | 15 | 54,46,39,33,30,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 505 | 125 | 505 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,63,54,51,46,46 | 16 | 55,46,39,33,31,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 505 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 510 | 125 | 510 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,63,54,51,46,46 | 16 | 55,46,39,33,31,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 515 | 125 | 515 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,63,54,52,46,46 | 16 | 55,46,40,33,31,24 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 515 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 520 | 125 | 520 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,64,54,52,46,46 | 16 | 55,47,40,34,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 525 | 125 | 525 | 1 | 0.25 | 0.75 | 0.01 | 24 | 70,64,54,52,46,46 | 16 | 55,47,40,34,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 525 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 530 | 125 | 530 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,64,54,52,47,46 | 16 | 55,47,40,34,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 535 | 125 | 535 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,64,54,52,47,46 | 16 | 55,47,40,34,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 535 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 540 | 125 | 540 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,64,55,52,47,46 | 16 | 55,47,40,34,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 545 | 125 | 545 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,64,55,52,47,46 | 16 | 55,47,40,34,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 545 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 550 | 125 | 550 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,64,55,52,47,46 | 17 | 56,47,40,34,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 555 | 125 | 555 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,64,55,53,47,46 | 17 | 56,47,41,34,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 555 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 560 | 125 | 560 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,64,55,53,47,47 | 17 | 56,47,41,34,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 565 | 125 | 565 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,64,55,53,47,47 | 17 | 56,47,41,34,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 565 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 570 | 125 | 570 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,64,55,53,47,47 | 17 | 56,48,41,35,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 575 | 125 | 575 | 1 | 0.25 | 0.75 | 0.01 | 25 | 71,64,55,53,47,47 | 17 | 56,48,41,35,31,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 575 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 580 | 125 | 580 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,65,55,53,47,47 | 17 | 56,48,41,35,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 585 | 125 | 585 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,65,56,53,47,47 | 17 | 56,48,41,35,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 585 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 590 | 125 | 590 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,65,56,53,48,47 | 17 | 56,48,41,35,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 595 | 125 | 595 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,65,56,53,48,47 | 19 | 57,48,41,35,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 595 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 600 | 125 | 600 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,65,56,54,48,47 | 19 | 57,48,42,35,32,25 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 605 | 125 | 605 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,65,56,54,48,47 | 19 | 57,48,42,35,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 605 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 610 | 125 | 610 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,65,56,54,48,47 | 19 | 57,48,42,35,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 615 | 125 | 615 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,65,56,54,48,47 | 19 | 57,48,42,35,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 615 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 620 | 125 | 620 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,65,56,54,48,47 | 19 | 57,49,42,35,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 625 | 125 | 625 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,65,56,54,48,47 | 19 | 57,49,42,36,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 625 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 630 | 125 | 630 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,65,57,54,48,48 | 19 | 57,49,42,36,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 635 | 125 | 635 | 1 | 0.25 | 0.75 | 0.01 | 26 | 72,65,57,54,48,48 | 19 | 57,49,42,36,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 635 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 640 | 125 | 640 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,57,54,48,48 | 19 | 57,49,42,36,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 645 | 125 | 645 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,57,54,48,48 | 20 | 58,49,42,36,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 645 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 650 | 125 | 650 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,57,55,48,48 | 20 | 58,49,43,36,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 655 | 125 | 655 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,57,55,49,48 | 20 | 58,49,43,36,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 655 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 660 | 125 | 660 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,57,55,49,48 | 20 | 58,49,43,36,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 665 | 125 | 665 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,57,55,49,48 | 20 | 58,49,43,36,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 665 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 670 | 125 | 670 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,57,55,49,48 | 20 | 58,49,43,36,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 675 | 125 | 675 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,57,55,49,48 | 20 | 58,49,43,36,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 675 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 680 | 125 | 680 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,58,55,49,48 | 20 | 58,50,43,36,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 685 | 125 | 685 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,58,55,49,48 | 20 | 58,50,43,37,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 685 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 690 | 125 | 690 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,58,55,49,48 | 20 | 58,50,43,37,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 695 | 125 | 695 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,58,55,49,48 | 21 | 59,50,43,37,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 695 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 700 | 125 | 700 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,66,58,56,49,48 | 21 | 59,50,43,37,33,26 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 705 | 125 | 705 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,58,56,49,48 | 21 | 59,50,44,37,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 705 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 710 | 125 | 710 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,58,56,49,48 | 21 | 59,50,44,37,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 715 | 125 | 715 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,58,56,49,49 | 21 | 59,50,44,37,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 715 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 720 | 125 | 720 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,58,56,49,49 | 21 | 59,50,44,37,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 725 | 125 | 725 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,58,56,50,49 | 21 | 59,50,44,37,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 725 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 730 | 125 | 730 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,58,56,50,49 | 21 | 59,50,44,37,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 735 | 125 | 735 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,56,50,49 | 21 | 59,50,44,37,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 735 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 740 | 125 | 740 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,56,50,49 | 21 | 59,50,44,37,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 745 | 125 | 745 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,56,50,49 | 21 | 59,51,44,37,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 745 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 750 | 125 | 750 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,56,50,49 | 21 | 59,51,44,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 755 | 125 | 755 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,57,50,49 | 22 | 60,51,44,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 755 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 760 | 125 | 760 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,57,50,49 | 22 | 60,51,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 765 | 125 | 765 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,57,50,49 | 22 | 60,51,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 765 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 770 | 125 | 770 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,57,50,49 | 22 | 60,51,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 775 | 125 | 775 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,59,57,50,49 | 22 | 60,51,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 775 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 780 | 125 | 780 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,59,57,50,49 | 22 | 60,51,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 785 | 125 | 785 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,59,57,50,49 | 22 | 60,51,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 785 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 790 | 125 | 790 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,59,57,50,49 | 22 | 60,51,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 795 | 125 | 795 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,57,50,49 | 22 | 60,51,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 795 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 800 | 125 | 800 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,57,50,49 | 22 | 60,51,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 805 | 125 | 805 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,57,51,49 | 22 | 60,51,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 805 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 810 | 125 | 810 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,57,51,50 | 22 | 60,51,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 815 | 125 | 815 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,58,51,50 | 24 | 61,52,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 815 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 820 | 125 | 820 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,58,51,50 | 24 | 61,52,45,38,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 825 | 125 | 825 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,58,51,50 | 24 | 61,52,46,39,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 825 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 830 | 125 | 830 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,58,51,50 | 24 | 61,52,46,39,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 835 | 125 | 835 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,58,51,50 | 24 | 61,52,46,39,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 835 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 840 | 125 | 840 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,58,51,50 | 24 | 61,52,46,39,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 845 | 125 | 845 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,58,51,50 | 24 | 61,52,46,39,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 845 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 850 | 125 | 850 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,68,60,58,51,50 | 24 | 61,52,46,39,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 855 | 125 | 855 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,60,58,51,50 | 24 | 61,52,46,39,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 855 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 860 | 125 | 860 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,61,58,51,50 | 24 | 61,52,46,39,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 865 | 125 | 865 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,61,58,51,50 | 24 | 61,52,46,39,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 865 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 870 | 125 | 870 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,61,58,51,50 | 24 | 61,52,46,39,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 875 | 125 | 875 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,61,58,51,50 | 24 | 61,52,46,39,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 875 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 880 | 125 | 880 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,61,59,51,50 | 24 | 61,52,46,39,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 885 | 125 | 885 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,61,59,51,50 | 25 | 62,52,46,39,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 885 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 890 | 125 | 890 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,61,59,51,50 | 25 | 62,53,46,39,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 895 | 125 | 895 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,61,59,52,50 | 25 | 62,53,47,39,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 895 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 900 | 125 | 900 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,61,59,52,50 | 25 | 62,53,47,39,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 905 | 125 | 905 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,61,59,52,50 | 25 | 62,53,47,40,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 905 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 910 | 125 | 910 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,61,59,52,50 | 25 | 62,53,47,40,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 915 | 125 | 915 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,61,59,52,51 | 25 | 62,53,47,40,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 915 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 920 | 125 | 920 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,61,59,52,51 | 25 | 62,53,47,40,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 925 | 125 | 925 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,61,59,52,51 | 25 | 62,53,47,40,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 925 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 930 | 125 | 930 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,62,59,52,51 | 25 | 62,53,47,40,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 935 | 125 | 935 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,62,59,52,51 | 25 | 62,53,47,40,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 935 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 940 | 125 | 940 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,69,62,59,52,51 | 25 | 62,53,47,40,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 945 | 125 | 945 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,62,59,52,51 | 25 | 62,53,47,40,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 945 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 950 | 125 | 950 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,62,60,52,51 | 25 | 62,53,47,40,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 955 | 125 | 955 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,62,60,52,51 | 25 | 62,53,47,40,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 955 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 960 | 125 | 960 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,69,62,60,52,51 | 26 | 63,53,47,40,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 965 | 125 | 965 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,62,60,52,51 | 26 | 63,53,48,40,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 965 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 970 | 125 | 970 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,62,60,52,51 | 26 | 63,54,48,40,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 975 | 125 | 975 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,62,60,52,51 | 26 | 63,54,48,40,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 975 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 980 | 125 | 980 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,62,60,52,51 | 26 | 63,54,48,40,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 985 | 125 | 985 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,62,60,52,51 | 26 | 63,54,48,40,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 985 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 990 | 125 | 990 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,62,60,52,51 | 26 | 63,54,48,40,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 995 | 125 | 995 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,62,60,53,51 | 26 | 63,54,48,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 995 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1000 | 125 | 1000 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,62,60,53,51 | 26 | 63,54,48,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1005 | 125 | 1005 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,63,60,53,51 | 26 | 63,54,48,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1005 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1010 | 125 | 1010 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,63,60,53,51 | 26 | 63,54,48,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1015 | 125 | 1015 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,63,60,53,51 | 26 | 63,54,48,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1015 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1020 | 125 | 1020 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,63,60,53,51 | 26 | 63,54,48,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1025 | 125 | 1025 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,63,61,53,51 | 26 | 63,54,48,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1025 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1030 | 125 | 1030 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,63,61,53,51 | 26 | 63,54,48,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1035 | 125 | 1035 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,70,63,61,53,52 | 28 | 64,54,48,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1035 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1040 | 125 | 1040 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,63,61,53,52 | 28 | 64,54,48,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1045 | 125 | 1045 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,63,61,53,52 | 28 | 64,54,49,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1045 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1050 | 125 | 1050 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,63,61,53,52 | 28 | 64,54,49,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1055 | 125 | 1055 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,63,61,53,52 | 28 | 64,54,49,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1055 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1060 | 125 | 1060 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,63,61,53,52 | 28 | 64,55,49,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1065 | 125 | 1065 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,70,63,61,53,52 | 28 | 64,55,49,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1065 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1070 | 125 | 1070 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,63,61,53,52 | 28 | 64,55,49,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1075 | 125 | 1075 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,63,61,53,52 | 28 | 64,55,49,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1075 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1080 | 125 | 1080 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,63,61,53,52 | 28 | 64,55,49,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1085 | 125 | 1085 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,64,61,53,52 | 28 | 64,55,49,41,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1085 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1090 | 125 | 1090 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,64,61,53,52 | 28 | 64,55,49,42,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1095 | 125 | 1095 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,64,61,53,52 | 28 | 64,55,49,42,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1095 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 8 | 1100 | 125 | 1100 | 1 | 0.25 | 0.75 | 0.01 | 31 | 78,71,64,61,53,52 | 28 | 64,55,49,42,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 8 | 1100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 550 | 210 | 550 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,59,50,48,44,44 | 12 | 52,43,38,32,29,26 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 555 | 210 | 555 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,59,50,48,44,44 | 12 | 52,44,38,32,29,26 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 555 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 560 | 210 | 560 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,50,49,44,44 | 12 | 52,44,38,32,29,26 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 565 | 210 | 565 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,50,49,45,44 | 12 | 52,44,38,32,29,26 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 565 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 570 | 210 | 570 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,50,49,45,44 | 12 | 52,44,38,32,29,26 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 575 | 210 | 575 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,51,49,45,45 | 12 | 52,44,38,32,30,26 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 575 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 580 | 210 | 580 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,51,49,45,45 | 12 | 52,44,38,32,30,26 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 585 | 210 | 585 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,51,49,45,45 | 12 | 52,44,38,32,30,26 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 585 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 590 | 210 | 590 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,51,49,45,45 | 12 | 52,44,38,32,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 595 | 210 | 595 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,51,49,45,45 | 12 | 52,44,38,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 595 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 600 | 210 | 600 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,51,49,45,45 | 12 | 52,44,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 605 | 210 | 605 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,59,51,49,45,45 | 12 | 52,44,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 605 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 610 | 210 | 610 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,60,51,50,45,45 | 13 | 53,44,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 615 | 210 | 615 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,60,51,50,45,45 | 13 | 53,44,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 615 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 620 | 210 | 620 | 1 | 0.25 | 0.75 | 0.01 | 19 | 66,60,51,50,45,45 | 13 | 53,45,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 625 | 210 | 625 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,51,50,45,45 | 13 | 53,45,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 625 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 630 | 210 | 630 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,52,50,45,45 | 13 | 53,45,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 635 | 210 | 635 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,52,50,45,45 | 13 | 53,45,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 635 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 640 | 210 | 640 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,52,50,46,45 | 13 | 53,45,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 645 | 210 | 645 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,52,50,46,45 | 13 | 53,45,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 645 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 650 | 210 | 650 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,52,50,46,45 | 13 | 53,45,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 655 | 210 | 655 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,52,50,46,46 | 13 | 53,45,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 655 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 660 | 210 | 660 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,52,50,46,46 | 13 | 53,45,40,34,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 665 | 210 | 665 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,52,51,46,46 | 13 | 53,45,40,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 665 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 670 | 210 | 670 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,52,51,46,46 | 13 | 53,45,40,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 675 | 210 | 675 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,52,51,46,46 | 13 | 53,45,40,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 675 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 680 | 210 | 680 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,52,51,46,46 | 15 | 54,45,40,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 685 | 210 | 685 | 1 | 0.25 | 0.75 | 0.01 | 20 | 67,60,52,51,46,46 | 15 | 54,45,40,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 685 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 690 | 210 | 690 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,61,53,51,46,46 | 15 | 54,45,40,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 695 | 210 | 695 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,61,53,51,46,46 | 15 | 54,46,40,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 695 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 700 | 210 | 700 | 1 | 0.25 | 0.75 | 0.01 | 21 | 68,61,53,51,46,46 | 15 | 54,46,40,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 705 | 210 | 705 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,53,51,46,46 | 15 | 54,46,40,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 705 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 710 | 210 | 710 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,53,51,46,46 | 15 | 54,46,40,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 715 | 210 | 715 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,53,51,46,46 | 15 | 54,46,40,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 715 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 720 | 210 | 720 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,53,51,47,46 | 15 | 54,46,40,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 725 | 210 | 725 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,53,52,47,46 | 15 | 54,46,41,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 725 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 730 | 210 | 730 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,53,52,47,46 | 15 | 54,46,41,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 735 | 210 | 735 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,53,52,47,46 | 15 | 54,46,41,35,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 735 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 740 | 210 | 740 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,53,52,47,47 | 15 | 54,46,41,35,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 745 | 210 | 745 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,53,52,47,47 | 15 | 54,46,41,35,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 745 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 750 | 210 | 750 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,53,52,47,47 | 15 | 54,46,41,35,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 755 | 210 | 755 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,54,52,47,47 | 15 | 54,46,41,35,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 755 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 760 | 210 | 760 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,54,52,47,47 | 16 | 55,46,41,35,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 765 | 210 | 765 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,54,52,47,47 | 16 | 55,46,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 765 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 770 | 210 | 770 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,54,52,47,47 | 16 | 55,46,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 775 | 210 | 775 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,54,52,47,47 | 16 | 55,46,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 775 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 780 | 210 | 780 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,54,52,47,47 | 16 | 55,47,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 785 | 210 | 785 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,54,52,47,47 | 16 | 55,47,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 785 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 790 | 210 | 790 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,54,53,47,47 | 16 | 55,47,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 795 | 210 | 795 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,54,53,47,47 | 16 | 55,47,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 795 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 800 | 210 | 800 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,54,53,47,47 | 16 | 55,47,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 805 | 210 | 805 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,54,53,47,47 | 16 | 55,47,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 805 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 810 | 210 | 810 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,54,53,47,47 | 16 | 55,47,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 815 | 210 | 815 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,54,53,48,47 | 16 | 55,47,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 815 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 820 | 210 | 820 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,54,53,48,47 | 16 | 55,47,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 825 | 210 | 825 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,55,53,48,47 | 16 | 55,47,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 825 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 830 | 210 | 830 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,55,53,48,47 | 16 | 55,47,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 835 | 210 | 835 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,55,53,48,47 | 16 | 55,47,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 835 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 840 | 210 | 840 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,55,53,48,48 | 16 | 55,47,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 845 | 210 | 845 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,55,53,48,48 | 16 | 55,47,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 845 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 850 | 210 | 850 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,55,53,48,48 | 17 | 56,47,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 855 | 210 | 855 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,55,53,48,48 | 17 | 56,47,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 855 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 860 | 210 | 860 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,55,54,48,48 | 17 | 56,47,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 865 | 210 | 865 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,55,54,48,48 | 17 | 56,47,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 865 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 870 | 210 | 870 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,55,54,48,48 | 17 | 56,47,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 875 | 210 | 875 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,55,54,48,48 | 17 | 56,48,43,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 875 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 880 | 210 | 880 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,55,54,48,48 | 17 | 56,48,43,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 885 | 210 | 885 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,55,54,48,48 | 17 | 56,48,43,36,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 885 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 890 | 210 | 890 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,55,54,48,48 | 17 | 56,48,43,36,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 895 | 210 | 895 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,55,54,48,48 | 17 | 56,48,43,36,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 895 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 900 | 210 | 900 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,56,54,48,48 | 17 | 56,48,43,36,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 905 | 210 | 905 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,56,54,48,48 | 17 | 56,48,43,36,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 905 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 910 | 210 | 910 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,56,54,48,48 | 17 | 56,48,43,37,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 915 | 210 | 915 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,56,54,49,48 | 17 | 56,48,43,37,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 915 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 920 | 210 | 920 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,56,54,49,48 | 17 | 56,48,43,37,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 925 | 210 | 925 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,56,54,49,48 | 17 | 56,48,43,37,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 925 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 930 | 210 | 930 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,56,54,49,48 | 17 | 56,48,43,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 935 | 210 | 935 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,56,54,49,48 | 17 | 56,48,43,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 935 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 940 | 210 | 940 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,56,55,49,48 | 17 | 56,48,43,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 945 | 210 | 945 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,56,55,49,48 | 17 | 56,48,43,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 945 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 950 | 210 | 950 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,56,55,49,48 | 17 | 56,48,43,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 955 | 210 | 955 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,56,55,49,49 | 19 | 57,48,43,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 955 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 960 | 210 | 960 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,56,55,49,49 | 19 | 57,48,43,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 965 | 210 | 965 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,56,55,49,49 | 19 | 57,48,44,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 965 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 970 | 210 | 970 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,56,55,49,49 | 19 | 57,48,44,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 975 | 210 | 975 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,56,55,49,49 | 19 | 57,48,44,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 975 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 980 | 210 | 980 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,56,55,49,49 | 19 | 57,49,44,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 985 | 210 | 985 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,57,55,49,49 | 19 | 57,49,44,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 985 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 990 | 210 | 990 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,57,55,49,49 | 19 | 57,49,44,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 995 | 210 | 995 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,57,55,49,49 | 19 | 57,49,44,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 995 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1000 | 210 | 1000 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,57,55,49,49 | 19 | 57,49,44,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1005 | 210 | 1005 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,57,55,49,49 | 19 | 57,49,44,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1005 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1010 | 210 | 1010 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,57,55,49,49 | 19 | 57,49,44,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1015 | 210 | 1015 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,57,55,49,49 | 19 | 57,49,44,38,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1015 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1020 | 210 | 1020 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,57,56,49,49 | 19 | 57,49,44,38,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1025 | 210 | 1025 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,57,56,49,49 | 19 | 57,49,44,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1025 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1030 | 210 | 1030 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,57,56,49,49 | 19 | 57,49,44,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1035 | 210 | 1035 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,57,56,50,49 | 19 | 57,49,44,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1035 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1040 | 210 | 1040 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,57,56,50,49 | 19 | 57,49,44,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1045 | 210 | 1045 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,57,56,50,49 | 19 | 57,49,44,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1045 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1050 | 210 | 1050 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,57,56,50,49 | 19 | 57,49,44,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1055 | 210 | 1055 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,57,56,50,49 | 19 | 57,49,44,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1055 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1060 | 210 | 1060 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,57,56,50,49 | 19 | 57,49,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1065 | 210 | 1065 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,57,56,50,49 | 20 | 58,49,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1065 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1070 | 210 | 1070 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,57,56,50,49 | 20 | 58,49,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1075 | 210 | 1075 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,57,56,50,49 | 20 | 58,49,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1075 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1080 | 210 | 1080 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,58,56,50,49 | 20 | 58,49,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1085 | 210 | 1085 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,58,56,50,50 | 20 | 58,49,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1085 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1090 | 210 | 1090 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,58,56,50,50 | 20 | 58,49,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1095 | 210 | 1095 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,58,56,50,50 | 20 | 58,50,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1095 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1100 | 210 | 1100 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,58,56,50,50 | 20 | 58,50,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1105 | 210 | 1105 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,58,56,50,50 | 20 | 58,50,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1105 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1110 | 210 | 1110 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,58,56,50,50 | 20 | 58,50,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1115 | 210 | 1115 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,58,57,50,50 | 20 | 58,50,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1115 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1120 | 210 | 1120 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,58,57,50,50 | 20 | 58,50,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1125 | 210 | 1125 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,58,57,50,50 | 20 | 58,50,45,38,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1125 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1130 | 210 | 1130 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,58,57,50,50 | 20 | 58,50,45,39,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1135 | 210 | 1135 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,58,57,50,50 | 20 | 58,50,45,39,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1135 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1140 | 210 | 1140 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,58,57,50,50 | 20 | 58,50,45,39,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1145 | 210 | 1145 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,58,57,50,50 | 20 | 58,50,45,39,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1145 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1150 | 210 | 1150 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,58,57,50,50 | 20 | 58,50,45,39,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1155 | 210 | 1155 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,58,57,50,50 | 20 | 58,50,45,39,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1155 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1160 | 210 | 1160 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,58,57,50,50 | 20 | 58,50,45,39,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1165 | 210 | 1165 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,58,57,51,50 | 20 | 58,50,46,39,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1165 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1170 | 210 | 1170 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,58,57,51,50 | 20 | 58,50,46,39,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1175 | 210 | 1175 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,58,57,51,50 | 20 | 58,50,46,39,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1175 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1180 | 210 | 1180 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,57,51,50 | 20 | 58,50,46,39,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1185 | 210 | 1185 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,57,51,50 | 20 | 58,50,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1185 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1190 | 210 | 1190 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,57,51,50 | 21 | 59,50,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1195 | 210 | 1195 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,57,51,50 | 21 | 59,50,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1195 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1200 | 210 | 1200 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,57,51,50 | 21 | 59,50,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1205 | 210 | 1205 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,57,51,50 | 21 | 59,50,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1205 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1210 | 210 | 1210 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,57,51,50 | 21 | 59,50,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1215 | 210 | 1215 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,58,51,50 | 21 | 59,50,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1215 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1220 | 210 | 1220 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,58,51,50 | 21 | 59,50,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1225 | 210 | 1225 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,58,51,50 | 21 | 59,50,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1225 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1230 | 210 | 1230 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,58,51,51 | 21 | 59,51,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1235 | 210 | 1235 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,58,51,51 | 21 | 59,51,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1235 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1240 | 210 | 1240 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,58,51,51 | 21 | 59,51,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1245 | 210 | 1245 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,58,51,51 | 21 | 59,51,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1245 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1250 | 210 | 1250 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,58,51,51 | 21 | 59,51,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1255 | 210 | 1255 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,58,51,51 | 21 | 59,51,46,39,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1255 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1260 | 210 | 1260 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,58,51,51 | 21 | 59,51,46,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1265 | 210 | 1265 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,65,59,58,51,51 | 21 | 59,51,46,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1265 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1270 | 210 | 1270 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,65,59,58,51,51 | 21 | 59,51,46,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1275 | 210 | 1275 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,59,58,51,51 | 21 | 59,51,46,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1275 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1280 | 210 | 1280 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,59,58,51,51 | 21 | 59,51,46,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1285 | 210 | 1285 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,59,58,51,51 | 21 | 59,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1285 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1290 | 210 | 1290 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,58,51,51 | 21 | 59,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1295 | 210 | 1295 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,58,51,51 | 21 | 59,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1295 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1300 | 210 | 1300 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,58,51,51 | 21 | 59,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1305 | 210 | 1305 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,58,51,51 | 21 | 59,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1305 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1310 | 210 | 1310 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,58,51,51 | 21 | 59,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1315 | 210 | 1315 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,58,52,51 | 21 | 59,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1315 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1320 | 210 | 1320 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 21 | 59,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1325 | 210 | 1325 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 21 | 59,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1325 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1330 | 210 | 1330 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 21 | 59,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1335 | 210 | 1335 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 22 | 60,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1335 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1340 | 210 | 1340 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 22 | 60,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1345 | 210 | 1345 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 22 | 60,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1345 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1350 | 210 | 1350 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 22 | 60,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1355 | 210 | 1355 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 22 | 60,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1355 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1360 | 210 | 1360 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 22 | 60,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1365 | 210 | 1365 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 22 | 60,51,47,40,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1365 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1370 | 210 | 1370 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 22 | 60,51,47,40,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1375 | 210 | 1375 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 22 | 60,52,47,40,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1375 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1380 | 210 | 1380 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 22 | 60,52,47,40,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1385 | 210 | 1385 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 22 | 60,52,47,40,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1385 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1390 | 210 | 1390 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,51 | 22 | 60,52,47,40,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1395 | 210 | 1395 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,52 | 22 | 60,52,47,40,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1395 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1400 | 210 | 1400 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,66,60,59,52,52 | 22 | 60,52,47,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1405 | 210 | 1405 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,66,60,59,52,52 | 22 | 60,52,47,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1405 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1410 | 210 | 1410 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,66,61,59,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1415 | 210 | 1415 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,66,61,59,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1415 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1420 | 210 | 1420 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,66,61,59,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1425 | 210 | 1425 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,66,61,59,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1425 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1430 | 210 | 1430 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,66,61,59,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1435 | 210 | 1435 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,66,61,59,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1435 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1440 | 210 | 1440 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1445 | 210 | 1445 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1445 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1450 | 210 | 1450 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1455 | 210 | 1455 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1455 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1460 | 210 | 1460 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1465 | 210 | 1465 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1465 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1470 | 210 | 1470 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,52,52 | 22 | 60,52,48,41,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1475 | 210 | 1475 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,52,52 | 22 | 60,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1475 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1480 | 210 | 1480 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,52,52 | 22 | 60,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1485 | 210 | 1485 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,53,52 | 22 | 60,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1485 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1490 | 210 | 1490 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,53,52 | 24 | 61,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1495 | 210 | 1495 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,53,52 | 24 | 61,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1495 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1500 | 210 | 1500 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,53,52 | 24 | 61,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1505 | 210 | 1505 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,53,52 | 24 | 61,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1505 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1510 | 210 | 1510 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,53,52 | 24 | 61,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1515 | 210 | 1515 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,53,52 | 24 | 61,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1515 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1520 | 210 | 1520 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,53,52 | 24 | 61,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1525 | 210 | 1525 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,53,52 | 24 | 61,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1525 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1530 | 210 | 1530 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,53,52 | 24 | 61,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1535 | 210 | 1535 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,53,52 | 24 | 61,52,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1535 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1540 | 210 | 1540 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,61,60,53,52 | 24 | 61,53,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1545 | 210 | 1545 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,62,60,53,52 | 24 | 61,53,48,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1545 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1550 | 210 | 1550 | 1 | 0.25 | 0.75 | 0.01 | 28 | 75,67,62,60,53,52 | 24 | 61,53,49,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1555 | 210 | 1555 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,60,53,52 | 24 | 61,53,49,41,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1555 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1560 | 210 | 1560 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,60,53,52 | 24 | 61,53,49,42,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1565 | 210 | 1565 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,60,53,52 | 24 | 61,53,49,42,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1565 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1570 | 210 | 1570 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,61,53,52 | 24 | 61,53,49,42,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1575 | 210 | 1575 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,61,53,52 | 24 | 61,53,49,42,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1575 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1580 | 210 | 1580 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,61,53,52 | 24 | 61,53,49,42,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1585 | 210 | 1585 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1585 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1590 | 210 | 1590 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1595 | 210 | 1595 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1595 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1600 | 210 | 1600 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1605 | 210 | 1605 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1605 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1610 | 210 | 1610 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1615 | 210 | 1615 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1615 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1620 | 210 | 1620 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,67,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1625 | 210 | 1625 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1625 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1630 | 210 | 1630 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1635 | 210 | 1635 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1635 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1640 | 210 | 1640 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1645 | 210 | 1645 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1645 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1650 | 210 | 1650 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1655 | 210 | 1655 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1655 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1660 | 210 | 1660 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1665 | 210 | 1665 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,53,53 | 24 | 61,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1665 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1670 | 210 | 1670 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,53,53 | 25 | 62,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1675 | 210 | 1675 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,54,53 | 25 | 62,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1675 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1680 | 210 | 1680 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,54,53 | 25 | 62,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1685 | 210 | 1685 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,62,61,54,53 | 25 | 62,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1685 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1690 | 210 | 1690 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,63,61,54,53 | 25 | 62,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1695 | 210 | 1695 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,63,61,54,53 | 25 | 62,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1695 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1700 | 210 | 1700 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,63,61,54,53 | 25 | 62,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1705 | 210 | 1705 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,63,61,54,53 | 25 | 62,53,49,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1705 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1710 | 210 | 1710 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,63,62,54,53 | 25 | 62,53,50,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1715 | 210 | 1715 | 1 | 0.25 | 0.75 | 0.01 | 29 | 76,68,63,62,54,53 | 25 | 62,53,50,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1715 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1720 | 210 | 1720 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,53,50,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1725 | 210 | 1725 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,53,50,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1725 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1730 | 210 | 1730 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,42,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1735 | 210 | 1735 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1735 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1740 | 210 | 1740 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1745 | 210 | 1745 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1745 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1750 | 210 | 1750 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1755 | 210 | 1755 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1755 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1760 | 210 | 1760 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1765 | 210 | 1765 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1765 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1770 | 210 | 1770 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1775 | 210 | 1775 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1775 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1780 | 210 | 1780 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1785 | 210 | 1785 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1785 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1790 | 210 | 1790 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1795 | 210 | 1795 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,53 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1795 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 10 | 1800 | 210 | 1800 | 1 | 0.25 | 0.75 | 0.01 | 30 | 77,68,63,62,54,54 | 25 | 62,54,50,43,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 10 | 1800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 900 | 300 | 900 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,60,54,52,48,47 | 14 | 52,44,41,34,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 905 | 300 | 905 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,60,54,52,48,47 | 14 | 52,44,41,34,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 905 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 910 | 300 | 910 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,60,54,52,48,47 | 14 | 52,44,41,34,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 915 | 300 | 915 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,60,54,52,48,47 | 14 | 52,44,41,34,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 915 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 920 | 300 | 920 | 1 | 0.25 | 0.75 | 0.01 | 17 | 65,60,54,52,48,48 | 15 | 52,44,42,34,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 925 | 300 | 925 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,54,52,48,48 | 15 | 52,44,42,34,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 925 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 930 | 300 | 930 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,54,52,48,48 | 15 | 52,44,42,34,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 935 | 300 | 935 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,54,52,48,48 | 15 | 52,44,42,34,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 935 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 940 | 300 | 940 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,54,52,49,48 | 15 | 52,44,42,34,32,26 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 945 | 300 | 945 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,54,52,49,48 | 15 | 53,45,42,34,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 945 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 950 | 300 | 950 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,54,52,49,48 | 15 | 53,45,42,34,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 955 | 300 | 955 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,54,52,49,48 | 15 | 53,45,42,34,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 955 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 960 | 300 | 960 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,54,52,49,48 | 15 | 53,45,42,34,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 965 | 300 | 965 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,54,52,49,48 | 15 | 53,45,42,34,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 965 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 970 | 300 | 970 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,54,52,49,48 | 15 | 53,45,42,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 975 | 300 | 975 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,52,49,48 | 15 | 53,45,42,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 975 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 980 | 300 | 980 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,52,49,48 | 15 | 53,45,42,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 985 | 300 | 985 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 15 | 53,45,42,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 985 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 990 | 300 | 990 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 15 | 53,45,42,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 995 | 300 | 995 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 15 | 53,45,42,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 995 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1000 | 300 | 1000 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 15 | 53,45,42,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1005 | 300 | 1005 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 15 | 53,45,42,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1005 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1010 | 300 | 1010 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 16 | 53,45,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1015 | 300 | 1015 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 16 | 53,45,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1015 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1020 | 300 | 1020 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 16 | 53,45,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1025 | 300 | 1025 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 16 | 53,45,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1025 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1030 | 300 | 1030 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 16 | 53,45,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1035 | 300 | 1035 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 16 | 53,45,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1035 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1040 | 300 | 1040 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 16 | 53,45,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1045 | 300 | 1045 | 1 | 0.25 | 0.75 | 0.01 | 18 | 66,61,55,53,49,48 | 16 | 53,45,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1045 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1050 | 300 | 1050 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,55,53,49,48 | 16 | 54,45,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1055 | 300 | 1055 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,55,53,49,48 | 16 | 54,46,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1055 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1060 | 300 | 1060 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,55,53,50,48 | 16 | 54,46,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1065 | 300 | 1065 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,55,53,50,48 | 16 | 54,46,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1065 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1070 | 300 | 1070 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,56,53,50,48 | 16 | 54,46,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1075 | 300 | 1075 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,56,53,50,48 | 16 | 54,46,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1075 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1080 | 300 | 1080 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,56,53,50,49 | 16 | 54,46,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1085 | 300 | 1085 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,56,54,50,49 | 16 | 54,46,43,35,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1085 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1090 | 300 | 1090 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,56,54,50,49 | 16 | 54,46,43,36,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1095 | 300 | 1095 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,56,54,50,49 | 16 | 54,46,43,36,33,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1095 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1100 | 300 | 1100 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,56,54,50,49 | 16 | 54,46,43,36,34,27 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1105 | 300 | 1105 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1105 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1110 | 300 | 1110 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1115 | 300 | 1115 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1115 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1120 | 300 | 1120 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1125 | 300 | 1125 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1125 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1130 | 300 | 1130 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1135 | 300 | 1135 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1135 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1140 | 300 | 1140 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1145 | 300 | 1145 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1145 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1150 | 300 | 1150 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1155 | 300 | 1155 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1155 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1160 | 300 | 1160 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1165 | 300 | 1165 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1165 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1170 | 300 | 1170 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,56,54,50,49 | 18 | 54,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1175 | 300 | 1175 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,57,54,50,49 | 18 | 55,46,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1175 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1180 | 300 | 1180 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,57,54,50,49 | 18 | 55,47,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1185 | 300 | 1185 | 1 | 0.25 | 0.75 | 0.01 | 19 | 67,62,57,54,50,49 | 18 | 55,47,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1185 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1190 | 300 | 1190 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,54,51,49 | 18 | 55,47,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1195 | 300 | 1195 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 18 | 55,47,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1195 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1200 | 300 | 1200 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 18 | 55,47,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1205 | 300 | 1205 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 18 | 55,47,44,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1205 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1210 | 300 | 1210 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 19 | 55,47,45,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1215 | 300 | 1215 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 19 | 55,47,45,36,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1215 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1220 | 300 | 1220 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 19 | 55,47,45,37,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1225 | 300 | 1225 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 19 | 55,47,45,37,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1225 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1230 | 300 | 1230 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 19 | 55,47,45,37,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1235 | 300 | 1235 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 19 | 55,47,45,37,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1235 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1240 | 300 | 1240 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 19 | 55,47,45,37,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1245 | 300 | 1245 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 19 | 55,47,45,37,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1245 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1250 | 300 | 1250 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 19 | 55,47,45,37,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1255 | 300 | 1255 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,49 | 19 | 55,47,45,37,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1255 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1260 | 300 | 1260 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,50 | 19 | 55,47,45,37,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1265 | 300 | 1265 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,50 | 19 | 55,47,45,37,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1265 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1270 | 300 | 1270 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,50 | 19 | 55,47,45,37,34,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1275 | 300 | 1275 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,50 | 19 | 55,47,45,37,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1275 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1280 | 300 | 1280 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,57,55,51,50 | 19 | 55,47,45,37,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1285 | 300 | 1285 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,57,55,51,50 | 19 | 55,47,45,37,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1285 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1290 | 300 | 1290 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,58,55,51,50 | 19 | 55,47,45,37,35,28 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1295 | 300 | 1295 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,58,55,51,50 | 19 | 55,47,45,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1295 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1300 | 300 | 1300 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,58,55,51,50 | 19 | 55,47,45,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1305 | 300 | 1305 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,58,55,51,50 | 19 | 55,47,45,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1305 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1310 | 300 | 1310 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,58,55,51,50 | 19 | 56,47,45,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1315 | 300 | 1315 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,58,55,51,50 | 19 | 56,47,45,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1315 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1320 | 300 | 1320 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,58,56,51,50 | 19 | 56,48,45,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1325 | 300 | 1325 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,58,56,51,50 | 20 | 56,48,46,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1325 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1330 | 300 | 1330 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,58,56,51,50 | 20 | 56,48,46,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1335 | 300 | 1335 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,58,56,51,50 | 20 | 56,48,46,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1335 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1340 | 300 | 1340 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,58,56,52,50 | 20 | 56,48,46,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1345 | 300 | 1345 | 1 | 0.25 | 0.75 | 0.01 | 20 | 68,63,58,56,52,50 | 20 | 56,48,46,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1345 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1350 | 300 | 1350 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1355 | 300 | 1355 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1355 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1360 | 300 | 1360 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,37,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1365 | 300 | 1365 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1365 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1370 | 300 | 1370 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1375 | 300 | 1375 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1375 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1380 | 300 | 1380 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1385 | 300 | 1385 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1385 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1390 | 300 | 1390 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1395 | 300 | 1395 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1395 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1400 | 300 | 1400 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1405 | 300 | 1405 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1405 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1410 | 300 | 1410 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1415 | 300 | 1415 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,58,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1415 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1420 | 300 | 1420 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,59,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1425 | 300 | 1425 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,59,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1425 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1430 | 300 | 1430 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,59,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1435 | 300 | 1435 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,59,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1435 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1440 | 300 | 1440 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,59,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1445 | 300 | 1445 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,59,56,52,50 | 20 | 56,48,46,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1445 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1450 | 300 | 1450 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,59,56,52,50 | 21 | 56,48,47,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1455 | 300 | 1455 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,59,57,52,50 | 21 | 56,48,47,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1455 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1460 | 300 | 1460 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,59,57,52,50 | 21 | 57,48,47,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1465 | 300 | 1465 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,59,57,52,50 | 21 | 57,48,47,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1465 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1470 | 300 | 1470 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,59,57,52,50 | 21 | 57,48,47,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1475 | 300 | 1475 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,59,57,52,51 | 21 | 57,49,47,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1475 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1480 | 300 | 1480 | 1 | 0.25 | 0.75 | 0.01 | 21 | 69,64,59,57,52,51 | 21 | 57,49,47,38,35,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1485 | 300 | 1485 | 1 | 0.25 | 0.75 | 0.01 | 21 | 69,64,59,57,52,51 | 21 | 57,49,47,38,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1485 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1490 | 300 | 1490 | 1 | 0.25 | 0.75 | 0.01 | 21 | 69,64,59,57,52,51 | 21 | 57,49,47,38,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1495 | 300 | 1495 | 1 | 0.25 | 0.75 | 0.01 | 21 | 69,64,59,57,52,51 | 21 | 57,49,47,38,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1495 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1500 | 300 | 1500 | 1 | 0.25 | 0.75 | 0.01 | 21 | 69,64,59,57,52,51 | 21 | 57,49,47,38,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1505 | 300 | 1505 | 1 | 0.25 | 0.75 | 0.01 | 21 | 69,64,59,57,52,51 | 21 | 57,49,47,38,36,29 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1505 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1510 | 300 | 1510 | 1 | 0.25 | 0.75 | 0.01 | 21 | 69,64,59,57,53,51 | 21 | 57,49,47,38,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1515 | 300 | 1515 | 1 | 0.25 | 0.75 | 0.01 | 21 | 69,64,59,57,53,51 | 21 | 57,49,47,38,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1515 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1520 | 300 | 1520 | 1 | 0.25 | 0.75 | 0.01 | 21 | 69,64,59,57,53,51 | 21 | 57,49,47,38,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1525 | 300 | 1525 | 1 | 0.25 | 0.75 | 0.01 | 21 | 69,64,59,57,53,51 | 21 | 57,49,47,38,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1525 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1530 | 300 | 1530 | 1 | 0.25 | 0.75 | 0.01 | 21 | 69,64,59,57,53,51 | 21 | 57,49,47,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1535 | 300 | 1535 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,59,57,53,51 | 21 | 57,49,47,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1535 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1540 | 300 | 1540 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,59,57,53,51 | 21 | 57,49,47,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1545 | 300 | 1545 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,59,57,53,51 | 21 | 57,49,47,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1545 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1550 | 300 | 1550 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,59,57,53,51 | 21 | 57,49,47,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1555 | 300 | 1555 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,59,57,53,51 | 21 | 57,49,47,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1555 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1560 | 300 | 1560 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,57,53,51 | 21 | 57,49,47,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1565 | 300 | 1565 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,57,53,51 | 21 | 57,49,47,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1565 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1570 | 300 | 1570 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,57,53,51 | 21 | 57,49,47,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1575 | 300 | 1575 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,57,53,51 | 21 | 57,49,47,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1575 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1580 | 300 | 1580 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,57,53,51 | 21 | 57,49,47,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1585 | 300 | 1585 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,57,53,51 | 21 | 57,49,47,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1585 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1590 | 300 | 1590 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,57,53,51 | 22 | 57,49,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1595 | 300 | 1595 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,57,53,51 | 22 | 57,49,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1595 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1600 | 300 | 1600 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,57,53,51 | 22 | 57,49,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1605 | 300 | 1605 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,57,53,51 | 22 | 57,49,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1605 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1610 | 300 | 1610 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 57,49,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1615 | 300 | 1615 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 57,49,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1615 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1620 | 300 | 1620 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 57,49,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1625 | 300 | 1625 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 57,49,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1625 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1630 | 300 | 1630 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,49,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1635 | 300 | 1635 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,49,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1635 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1640 | 300 | 1640 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,49,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1645 | 300 | 1645 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,49,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1645 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1650 | 300 | 1650 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1655 | 300 | 1655 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1655 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1660 | 300 | 1660 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1665 | 300 | 1665 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1665 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1670 | 300 | 1670 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1675 | 300 | 1675 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1675 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1680 | 300 | 1680 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1685 | 300 | 1685 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1685 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1690 | 300 | 1690 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1695 | 300 | 1695 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,53,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1695 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1700 | 300 | 1700 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,60,58,54,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1705 | 300 | 1705 | 1 | 0.25 | 0.75 | 0.01 | 23 | 70,65,60,58,54,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1705 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1710 | 300 | 1710 | 1 | 0.25 | 0.75 | 0.01 | 23 | 70,65,61,58,54,51 | 22 | 58,50,48,39,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1715 | 300 | 1715 | 1 | 0.25 | 0.75 | 0.01 | 23 | 70,65,61,58,54,51 | 22 | 58,50,48,40,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1715 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1720 | 300 | 1720 | 1 | 0.25 | 0.75 | 0.01 | 23 | 70,65,61,58,54,51 | 22 | 58,50,48,40,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1725 | 300 | 1725 | 1 | 0.25 | 0.75 | 0.01 | 23 | 70,65,61,58,54,51 | 22 | 58,50,48,40,36,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1725 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1730 | 300 | 1730 | 1 | 0.25 | 0.75 | 0.01 | 23 | 70,65,61,58,54,52 | 22 | 58,50,48,40,37,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1735 | 300 | 1735 | 1 | 0.25 | 0.75 | 0.01 | 23 | 70,65,61,58,54,52 | 22 | 58,50,48,40,37,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1735 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1740 | 300 | 1740 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,58,54,52 | 23 | 58,50,49,40,37,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1745 | 300 | 1745 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,58,54,52 | 23 | 58,50,49,40,37,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1745 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1750 | 300 | 1750 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,58,54,52 | 23 | 58,50,49,40,37,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1755 | 300 | 1755 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,58,54,52 | 23 | 58,50,49,40,37,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1755 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1760 | 300 | 1760 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,58,54,52 | 23 | 58,50,49,40,37,30 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1765 | 300 | 1765 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,58,54,52 | 23 | 58,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1765 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1770 | 300 | 1770 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,58,54,52 | 23 | 58,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1775 | 300 | 1775 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 58,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1775 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1780 | 300 | 1780 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 58,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1785 | 300 | 1785 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 58,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1785 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1790 | 300 | 1790 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 58,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1795 | 300 | 1795 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 58,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1795 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1800 | 300 | 1800 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 58,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1805 | 300 | 1805 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 58,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1805 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1810 | 300 | 1810 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 58,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1815 | 300 | 1815 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1815 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1820 | 300 | 1820 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1825 | 300 | 1825 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1825 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1830 | 300 | 1830 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1835 | 300 | 1835 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1835 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1840 | 300 | 1840 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,50,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1845 | 300 | 1845 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,51,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1845 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1850 | 300 | 1850 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,51,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1855 | 300 | 1855 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,51,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1855 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1860 | 300 | 1860 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,51,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1865 | 300 | 1865 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,51,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1865 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1870 | 300 | 1870 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,51,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1875 | 300 | 1875 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,61,59,54,52 | 23 | 59,51,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1875 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1880 | 300 | 1880 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,54,52 | 23 | 59,51,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1885 | 300 | 1885 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,54,52 | 23 | 59,51,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1885 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1890 | 300 | 1890 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,54,52 | 23 | 59,51,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1895 | 300 | 1895 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,54,52 | 23 | 59,51,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1895 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1900 | 300 | 1900 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,54,52 | 23 | 59,51,49,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1905 | 300 | 1905 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,54,52 | 24 | 59,51,50,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1905 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1910 | 300 | 1910 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,55,52 | 24 | 59,51,50,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1915 | 300 | 1915 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,55,52 | 24 | 59,51,50,40,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1915 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1920 | 576 | 1920 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1925 | 300 | 1925 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1925 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1930 | 300 | 1930 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1935 | 300 | 1935 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1935 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1940 | 300 | 1940 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1945 | 300 | 1945 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1945 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1950 | 300 | 1950 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,59,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1955 | 300 | 1955 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,62,60,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1955 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1960 | 300 | 1960 | 1 | 0.25 | 0.75 | 0.01 | 24 | 71,66,62,60,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1965 | 590 | 1965 | 1 | 0.25 | 0.75 | 0.01 | 24 | 71,66,62,60,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1965 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1970 | 300 | 1970 | 1 | 0.25 | 0.75 | 0.01 | 24 | 71,66,62,60,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1975 | 300 | 1975 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,62,60,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1975 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1980 | 300 | 1980 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,62,60,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1990 | 300 | 1990 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,62,60,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 1995 | 300 | 1995 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,62,60,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 1995 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2000 | 300 | 2000 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,62,60,55,52 | 24 | 59,51,50,41,37,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2010 | 300 | 2010 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,62,60,55,52 | 24 | 59,51,50,41,38,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2020 | 300 | 2020 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,62,60,55,53 | 24 | 59,51,50,41,38,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2030 | 300 | 2030 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,62,60,55,53 | 24 | 60,51,50,41,38,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2040 | 300 | 2040 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,62,60,55,53 | 24 | 60,51,50,41,38,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2050 | 300 | 2050 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,62,60,55,53 | 24 | 60,51,50,41,38,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2060 | 300 | 2060 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,62,60,55,53 | 24 | 60,51,50,41,38,31 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2070 | 300 | 2070 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,60,55,53 | 24 | 60,52,50,41,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2080 | 300 | 2080 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,60,55,53 | 24 | 60,52,50,41,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2090 | 300 | 2090 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,60,55,53 | 25 | 60,52,51,41,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2100 | 300 | 2100 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,60,55,53 | 25 | 60,52,51,41,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2110 | 300 | 2110 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,60,55,53 | 25 | 60,52,51,41,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2120 | 300 | 2120 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,60,55,53 | 25 | 60,52,51,41,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2130 | 300 | 2130 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,60,55,53 | 25 | 60,52,51,41,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2140 | 300 | 2140 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,60,55,53 | 25 | 60,52,51,41,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2150 | 300 | 2150 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,60,56,53 | 25 | 60,52,51,41,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2160 | 300 | 2160 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,61,56,53 | 25 | 60,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2170 | 300 | 2170 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,61,56,53 | 25 | 60,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2180 | 300 | 2180 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,61,56,53 | 25 | 60,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2190 | 300 | 2190 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,61,56,53 | 25 | 60,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2200 | 300 | 2200 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,61,56,53 | 25 | 60,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2210 | 663 | 2210 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,61,56,53 | 25 | 60,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2220 | 666 | 2220 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,61,56,53 | 25 | 60,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2230 | 300 | 2230 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,63,61,56,53 | 25 | 60,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2240 | 300 | 2240 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,63,61,56,53 | 25 | 60,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2250 | 300 | 2250 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,63,61,56,53 | 25 | 60,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2260 | 300 | 2260 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,63,61,56,53 | 25 | 61,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2270 | 300 | 2270 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,61,56,53 | 25 | 61,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2280 | 300 | 2280 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,61,56,53 | 25 | 61,52,51,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2290 | 300 | 2290 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,61,56,53 | 26 | 61,52,52,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2300 | 300 | 2300 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,61,56,53 | 26 | 61,52,52,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2310 | 300 | 2310 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,61,56,53 | 26 | 61,53,52,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2320 | 300 | 2320 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,61,56,53 | 26 | 61,53,52,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2330 | 300 | 2330 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,61,56,53 | 26 | 61,53,52,42,38,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2340 | 300 | 2340 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,61,56,53 | 26 | 61,53,52,42,39,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2350 | 300 | 2350 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,61,56,53 | 26 | 61,53,52,42,39,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2360 | 300 | 2360 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,61,56,53 | 26 | 61,53,52,42,39,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2370 | 300 | 2370 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,61,56,54 | 26 | 61,53,52,42,39,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2380 | 300 | 2380 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,62,56,54 | 26 | 61,53,52,42,39,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2390 | 300 | 2390 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,62,56,54 | 26 | 61,53,52,42,39,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2400 | 300 | 2400 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,62,56,54 | 26 | 61,53,52,42,39,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2410 | 300 | 2410 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,62,56,54 | 26 | 61,53,52,42,39,32 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2420 | 300 | 2420 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,62,57,54 | 26 | 61,53,52,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2430 | 300 | 2430 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,62,57,54 | 26 | 61,53,52,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2440 | 300 | 2440 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,62,57,54 | 26 | 61,53,52,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2450 | 300 | 2450 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,62,57,54 | 26 | 61,53,52,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2460 | 300 | 2460 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,62,57,54 | 26 | 61,53,52,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2470 | 300 | 2470 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,62,57,54 | 26 | 61,53,52,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2480 | 300 | 2480 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,64,62,57,54 | 26 | 61,53,52,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2490 | 300 | 2490 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,65,62,57,54 | 26 | 61,53,52,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2500 | 300 | 2500 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,65,62,57,54 | 27 | 61,53,53,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2510 | 300 | 2510 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,65,62,57,54 | 27 | 61,53,53,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2520 | 756 | 2520 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,65,62,57,54 | 27 | 62,53,53,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2530 | 300 | 2530 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,65,62,57,54 | 27 | 62,53,53,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2540 | 300 | 2540 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,65,62,57,54 | 27 | 62,53,53,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2550 | 300 | 2550 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,65,62,57,54 | 27 | 62,53,53,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2560 | 300 | 2560 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,65,62,57,54 | 27 | 62,53,53,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2570 | 300 | 2570 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,65,62,57,54 | 27 | 62,53,53,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2580 | 300 | 2580 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,65,62,57,54 | 27 | 62,53,53,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2590 | 300 | 2590 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,67,65,62,57,54 | 27 | 62,54,53,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 12 | 2600 | 300 | 2600 | 1 | 0.25 | 0.75 | 0.01 | 26 | 74,68,65,62,57,54 | 27 | 62,54,53,43,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 12 | 2600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1000 | 430 | 1000 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,53,49,48 | 12 | 50,45,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1005 | 430 | 1005 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,53,49,48 | 12 | 50,45,39,33,30,27 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1005 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1010 | 430 | 1010 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,53,49,48 | 12 | 50,45,39,33,30,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1015 | 430 | 1015 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,53,49,48 | 12 | 50,45,39,33,30,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1015 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1020 | 430 | 1020 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,53,49,48 | 12 | 50,45,39,33,30,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1025 | 430 | 1025 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,53,49,48 | 12 | 50,45,39,33,30,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1025 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1030 | 430 | 1030 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,53,49,48 | 12 | 50,45,39,33,30,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1035 | 430 | 1035 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,51,53,49,48 | 12 | 50,45,39,33,30,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1035 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1040 | 430 | 1040 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 12 | 50,45,39,33,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1045 | 430 | 1045 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 12 | 50,45,39,33,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1045 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1050 | 430 | 1050 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 13 | 50,45,40,33,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1055 | 430 | 1055 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 13 | 50,45,40,33,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1055 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1060 | 430 | 1060 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 13 | 50,45,40,33,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1065 | 430 | 1065 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 13 | 50,45,40,33,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1065 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1070 | 430 | 1070 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 13 | 50,45,40,33,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1075 | 430 | 1075 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 13 | 50,45,40,33,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1075 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1080 | 430 | 1080 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 13 | 50,45,40,33,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1085 | 430 | 1085 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 13 | 50,45,40,33,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1085 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1090 | 430 | 1090 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 13 | 50,46,40,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1095 | 430 | 1095 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 13 | 50,46,40,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1095 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1100 | 430 | 1100 | 1 | 0.25 | 0.75 | 0.01 | 12 | 63,56,52,53,49,48 | 13 | 50,46,40,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1105 | 430 | 1105 | 1 | 0.25 | 0.75 | 0.01 | 13 | 63,57,52,54,49,48 | 13 | 50,46,40,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1105 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1110 | 430 | 1110 | 1 | 0.25 | 0.75 | 0.01 | 13 | 63,57,52,54,49,48 | 13 | 51,46,40,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1115 | 430 | 1115 | 1 | 0.25 | 0.75 | 0.01 | 13 | 63,57,52,54,49,48 | 13 | 51,46,40,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1115 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1120 | 430 | 1120 | 1 | 0.25 | 0.75 | 0.01 | 13 | 63,57,52,54,49,48 | 13 | 51,46,40,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1125 | 430 | 1125 | 1 | 0.25 | 0.75 | 0.01 | 13 | 63,57,52,54,50,48 | 13 | 51,46,40,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1125 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1130 | 430 | 1130 | 1 | 0.25 | 0.75 | 0.01 | 13 | 63,57,52,54,50,48 | 13 | 51,46,40,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1135 | 430 | 1135 | 1 | 0.25 | 0.75 | 0.01 | 13 | 63,57,52,54,50,48 | 13 | 51,46,40,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1135 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1140 | 430 | 1140 | 1 | 0.25 | 0.75 | 0.01 | 13 | 63,57,52,54,50,48 | 13 | 51,46,40,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1145 | 430 | 1145 | 1 | 0.25 | 0.75 | 0.01 | 13 | 63,57,53,54,50,48 | 13 | 51,46,40,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1145 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1150 | 430 | 1150 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,48 | 13 | 51,46,40,34,31,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1155 | 430 | 1155 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,48 | 14 | 51,46,41,34,31,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1155 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1160 | 430 | 1160 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,48 | 14 | 51,46,41,34,31,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1165 | 430 | 1165 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,48 | 14 | 51,46,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1165 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1170 | 430 | 1170 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,48 | 14 | 51,46,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1175 | 430 | 1175 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 51,46,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1175 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1180 | 430 | 1180 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 51,46,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1185 | 430 | 1185 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 51,46,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1185 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1190 | 430 | 1190 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 51,46,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1195 | 430 | 1195 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 51,46,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1195 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1200 | 430 | 1200 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 51,46,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1205 | 430 | 1205 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 51,46,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1205 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1210 | 430 | 1210 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 51,46,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1215 | 430 | 1215 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 51,46,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1215 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1220 | 430 | 1220 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 51,47,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1225 | 430 | 1225 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 51,47,41,34,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1225 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1230 | 430 | 1230 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 51,47,41,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1235 | 430 | 1235 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 52,47,41,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1235 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1240 | 430 | 1240 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 52,47,41,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1245 | 430 | 1245 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 52,47,41,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1245 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1250 | 430 | 1250 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,53,54,50,49 | 14 | 52,47,41,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1255 | 430 | 1255 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,55,50,49 | 14 | 52,47,41,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1255 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1260 | 430 | 1260 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,55,50,49 | 14 | 52,47,41,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1265 | 430 | 1265 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,55,50,49 | 14 | 52,47,41,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1265 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1270 | 430 | 1270 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,55,50,49 | 14 | 52,47,41,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1275 | 430 | 1275 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,55,50,49 | 15 | 52,47,42,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1275 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1280 | 430 | 1280 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,55,50,49 | 15 | 52,47,42,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1285 | 430 | 1285 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,55,50,49 | 15 | 52,47,42,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1285 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1290 | 430 | 1290 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,55,50,49 | 15 | 52,47,42,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1295 | 430 | 1295 | 1 | 0.25 | 0.75 | 0.01 | 13 | 64,57,54,55,50,49 | 15 | 52,47,42,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1295 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1300 | 430 | 1300 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,55,51,49 | 15 | 52,47,42,35,32,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1305 | 430 | 1305 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,55,51,49 | 15 | 52,47,42,35,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1305 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1310 | 430 | 1310 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,55,51,49 | 15 | 52,47,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1315 | 430 | 1315 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,55,51,49 | 15 | 52,47,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1315 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1320 | 430 | 1320 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,55,51,49 | 15 | 52,47,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1325 | 430 | 1325 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,55,51,49 | 15 | 52,47,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1325 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1330 | 430 | 1330 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,55,51,49 | 15 | 52,47,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1335 | 430 | 1335 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,55,51,49 | 15 | 52,47,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1335 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1340 | 430 | 1340 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,55,51,49 | 15 | 52,47,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1345 | 430 | 1345 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,55,51,49 | 15 | 52,47,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1345 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1350 | 430 | 1350 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,55,51,49 | 15 | 52,47,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1355 | 430 | 1355 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,55,51,49 | 15 | 52,47,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1355 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1360 | 430 | 1360 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,55,51,49 | 15 | 52,47,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1365 | 430 | 1365 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,55,51,49 | 15 | 52,48,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1365 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1370 | 430 | 1370 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,55,51,49 | 15 | 53,48,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1375 | 430 | 1375 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,54,55,51,49 | 15 | 53,48,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1375 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1380 | 430 | 1380 | 1 | 0.25 | 0.57 | 0.19 | 17 | 65,58,50,51,50,49 | 3 | 45,37,30,22,19,17 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1385 | 430 | 1385 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,55,51,49 | 15 | 53,48,42,35,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1385 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1390 | 430 | 1390 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,55,51,50 | 15 | 53,48,42,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1395 | 430 | 1395 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,55,51,50 | 15 | 53,48,42,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1395 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1400 | 430 | 1400 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,55,51,50 | 15 | 53,48,42,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1405 | 430 | 1405 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,55,51,50 | 16 | 53,48,43,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1405 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1410 | 430 | 1410 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,55,51,50 | 16 | 53,48,43,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1415 | 430 | 1415 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,55,51,50 | 16 | 53,48,43,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1415 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1420 | 430 | 1420 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,55,51,50 | 16 | 53,48,43,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1425 | 430 | 1425 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1425 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1430 | 430 | 1430 | 1 | 0.25 | 0.57 | 0.19 | 17 | 65,58,50,51,50,49 | 3 | 45,37,30,22,19,17 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1435 | 430 | 1435 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1435 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1440 | 430 | 1440 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1445 | 430 | 1445 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1445 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1450 | 430 | 1450 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1455 | 430 | 1455 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1455 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1460 | 430 | 1460 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,33,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1465 | 430 | 1465 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1465 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1470 | 430 | 1470 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1475 | 430 | 1475 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1475 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1480 | 430 | 1480 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1485 | 430 | 1485 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1485 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1490 | 430 | 1490 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1495 | 430 | 1495 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1495 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1500 | 430 | 1500 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,51,50 | 16 | 53,48,43,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1505 | 430 | 1505 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,52,50 | 16 | 53,48,43,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1505 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1510 | 430 | 1510 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,52,50 | 16 | 53,48,43,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1515 | 430 | 1515 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,56,52,50 | 16 | 53,48,43,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1515 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1520 | 430 | 1520 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,56,56,52,50 | 16 | 54,48,43,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1525 | 430 | 1525 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,56,56,52,50 | 16 | 54,48,43,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1525 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1530 | 430 | 1530 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,56,52,50 | 17 | 54,49,43,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1535 | 430 | 1535 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 17 | 54,49,43,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1535 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1540 | 430 | 1540 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 17 | 54,49,43,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1545 | 430 | 1545 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 17 | 54,49,43,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1545 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1550 | 430 | 1550 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1555 | 430 | 1555 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1555 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1560 | 430 | 1560 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1565 | 430 | 1565 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,36,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1565 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1570 | 430 | 1570 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1575 | 430 | 1575 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1575 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1580 | 430 | 1580 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1585 | 430 | 1585 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1585 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1590 | 430 | 1590 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1595 | 430 | 1595 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1595 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1600 | 430 | 1600 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1605 | 430 | 1605 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1605 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1610 | 430 | 1610 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1615 | 430 | 1615 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,56,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1615 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1620 | 430 | 1620 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,57,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1625 | 430 | 1625 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,57,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1625 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1630 | 430 | 1630 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,57,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1635 | 430 | 1635 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,57,52,50 | 18 | 54,49,44,37,34,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1635 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1640 | 430 | 1640 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,57,52,50 | 18 | 54,49,44,37,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1645 | 430 | 1645 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,57,52,51 | 18 | 54,49,44,37,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1645 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1650 | 430 | 1650 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,57,52,51 | 18 | 54,49,44,37,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1655 | 430 | 1655 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,57,52,51 | 18 | 54,49,44,37,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1655 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1660 | 430 | 1660 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,57,52,51 | 18 | 54,49,44,37,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1665 | 430 | 1665 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,57,52,51 | 18 | 54,49,44,37,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1665 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1670 | 430 | 1670 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 18 | 54,49,44,37,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1675 | 430 | 1675 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 18 | 54,49,44,37,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1675 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1680 | 430 | 1680 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 18 | 54,49,44,37,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1685 | 430 | 1685 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 18 | 54,49,44,37,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1685 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1690 | 430 | 1690 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 18 | 55,49,44,37,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1695 | 430 | 1695 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 18 | 55,49,44,37,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1695 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1700 | 430 | 1700 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 18 | 55,49,44,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1705 | 430 | 1705 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 18 | 55,49,44,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1705 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1710 | 430 | 1710 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 19 | 55,49,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1715 | 430 | 1715 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 19 | 55,50,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1715 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1720 | 430 | 1720 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 19 | 55,50,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1725 | 430 | 1725 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 19 | 55,50,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1725 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1730 | 430 | 1730 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 19 | 55,50,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1735 | 430 | 1735 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,52,51 | 19 | 55,50,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1735 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1740 | 430 | 1740 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,53,51 | 19 | 55,50,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1745 | 430 | 1745 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,53,51 | 19 | 55,50,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1745 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1750 | 430 | 1750 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,53,51 | 19 | 55,50,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1755 | 430 | 1755 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,53,51 | 19 | 55,50,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1755 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1760 | 430 | 1760 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,53,51 | 19 | 55,50,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1765 | 430 | 1765 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,57,57,53,51 | 19 | 55,50,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1765 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1770 | 430 | 1770 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,57,53,51 | 19 | 55,50,45,37,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1775 | 430 | 1775 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,57,53,51 | 19 | 55,50,45,38,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1775 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1780 | 430 | 1780 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,57,53,51 | 19 | 55,50,45,38,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1785 | 430 | 1785 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,57,53,51 | 19 | 55,50,45,38,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1785 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1790 | 430 | 1790 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,57,53,51 | 19 | 55,50,45,38,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1795 | 430 | 1795 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,59,57,57,53,51 | 19 | 55,50,45,38,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1795 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1800 | 430 | 1800 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,57,57,53,51 | 19 | 55,50,45,38,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1805 | 430 | 1805 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,57,57,53,51 | 19 | 55,50,45,38,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1805 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1810 | 430 | 1810 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,57,57,53,51 | 19 | 55,50,45,38,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1815 | 430 | 1815 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,57,57,53,51 | 19 | 55,50,45,38,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1815 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1820 | 430 | 1820 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,57,57,53,51 | 19 | 55,50,45,38,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1825 | 430 | 1825 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,57,57,53,51 | 19 | 55,50,45,38,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1825 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1830 | 430 | 1830 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,57,57,53,51 | 19 | 55,50,45,38,35,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1835 | 430 | 1835 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,57,53,51 | 19 | 55,50,45,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1835 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1840 | 430 | 1840 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 19 | 55,50,45,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1845 | 430 | 1845 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 19 | 55,50,45,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1845 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1850 | 430 | 1850 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 19 | 55,50,45,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1855 | 430 | 1855 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 19 | 55,50,45,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1855 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1860 | 430 | 1860 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 19 | 55,50,45,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1865 | 430 | 1865 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 19 | 55,50,45,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1865 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1870 | 430 | 1870 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 19 | 55,50,45,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1875 | 430 | 1875 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 19 | 55,50,45,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1875 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1880 | 430 | 1880 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 19 | 56,50,45,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1885 | 430 | 1885 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 20 | 56,50,46,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1885 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1890 | 430 | 1890 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 20 | 56,50,46,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1895 | 430 | 1895 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 20 | 56,50,46,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1895 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1900 | 430 | 1900 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 20 | 56,50,46,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1905 | 430 | 1905 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 20 | 56,50,46,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1905 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1910 | 430 | 1910 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 20 | 56,50,46,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1915 | 430 | 1915 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 20 | 56,50,46,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1915 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1920 | 576 | 1920 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 20 | 56,51,46,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1925 | 430 | 1925 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 20 | 56,51,46,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1925 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1930 | 430 | 1930 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 20 | 56,51,46,38,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1935 | 430 | 1935 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1935 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1940 | 430 | 1940 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,51 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1945 | 430 | 1945 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,52 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1945 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1950 | 430 | 1950 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,52 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1955 | 430 | 1955 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,52 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1955 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1960 | 430 | 1960 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,52 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1965 | 590 | 1965 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,52 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1965 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1970 | 430 | 1970 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,52 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1975 | 430 | 1975 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,52 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1975 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1980 | 430 | 1980 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,52 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1990 | 430 | 1990 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,52 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 1995 | 430 | 1995 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,52 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 1995 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2000 | 430 | 2000 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,52 | 20 | 56,51,46,38,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2010 | 430 | 2010 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,58,53,52 | 20 | 56,51,46,39,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2020 | 430 | 2020 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,58,54,52 | 20 | 56,51,46,39,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2030 | 430 | 2030 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,58,54,52 | 20 | 56,51,46,39,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2040 | 430 | 2040 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,59,58,54,52 | 20 | 56,51,46,39,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2050 | 430 | 2050 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,58,54,52 | 20 | 56,51,46,39,36,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2060 | 430 | 2060 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,58,54,52 | 20 | 56,51,46,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2070 | 430 | 2070 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,58,54,52 | 20 | 56,51,46,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2080 | 430 | 2080 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,58,54,52 | 21 | 56,51,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2090 | 430 | 2090 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,59,54,52 | 21 | 57,51,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2100 | 430 | 2100 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,59,54,52 | 21 | 57,51,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2110 | 430 | 2110 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,60,59,59,54,52 | 21 | 57,51,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2120 | 430 | 2120 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,59,54,52 | 21 | 57,51,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2130 | 430 | 2130 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,59,54,52 | 21 | 57,51,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2140 | 430 | 2140 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,59,54,52 | 21 | 57,51,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2150 | 430 | 2150 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,59,54,52 | 21 | 57,52,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2160 | 430 | 2160 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,59,54,52 | 21 | 57,52,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2170 | 430 | 2170 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,59,54,52 | 21 | 57,52,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2180 | 430 | 2180 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,59,54,52 | 21 | 57,52,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2190 | 430 | 2190 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,59,54,52 | 21 | 57,52,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2200 | 430 | 2200 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,59,54,52 | 21 | 57,52,47,39,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2210 | 663 | 2210 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,59,54,52 | 21 | 57,52,47,39,37,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2220 | 666 | 2220 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,54,52 | 21 | 57,52,47,39,37,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2230 | 430 | 2230 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,54,52 | 21 | 57,52,47,39,37,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2240 | 430 | 2240 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,54,52 | 21 | 57,52,47,39,37,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2250 | 430 | 2250 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,54,52 | 21 | 57,52,47,39,37,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2260 | 430 | 2260 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,54,52 | 21 | 57,52,47,39,37,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2270 | 430 | 2270 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,54,52 | 21 | 57,52,47,40,37,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2280 | 430 | 2280 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,54,52 | 21 | 57,52,47,40,37,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2290 | 430 | 2290 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,54,52 | 21 | 57,52,47,40,37,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2300 | 430 | 2300 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,54,53 | 22 | 57,52,48,40,37,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2310 | 430 | 2310 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,54,53 | 22 | 57,52,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2320 | 430 | 2320 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,54,53 | 22 | 58,52,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2330 | 430 | 2330 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,55,53 | 22 | 58,52,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2340 | 430 | 2340 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,55,53 | 22 | 58,52,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2350 | 430 | 2350 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,55,53 | 22 | 58,52,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2360 | 430 | 2360 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,60,59,55,53 | 22 | 58,52,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2370 | 430 | 2370 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,59,55,53 | 22 | 58,52,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2380 | 430 | 2380 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,60,55,53 | 22 | 58,52,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2390 | 430 | 2390 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,60,55,53 | 22 | 58,52,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2400 | 430 | 2400 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,60,55,53 | 22 | 58,52,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2410 | 430 | 2410 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,60,55,53 | 22 | 58,53,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2420 | 430 | 2420 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,60,55,53 | 22 | 58,53,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2430 | 430 | 2430 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,60,60,55,53 | 22 | 58,53,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2440 | 430 | 2440 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,60,55,53 | 22 | 58,53,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2450 | 430 | 2450 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,60,55,53 | 22 | 58,53,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2460 | 430 | 2460 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,60,55,53 | 22 | 58,53,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2470 | 430 | 2470 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,60,55,53 | 22 | 58,53,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2480 | 430 | 2480 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,61,61,60,55,53 | 22 | 58,53,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2490 | 430 | 2490 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 22 | 58,53,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2500 | 430 | 2500 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 22 | 58,53,48,40,38,34 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2510 | 430 | 2510 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 22 | 58,53,48,40,38,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2520 | 756 | 2520 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 22 | 58,53,48,40,38,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2530 | 430 | 2530 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 58,53,49,40,38,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2540 | 430 | 2540 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 58,53,49,40,38,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2550 | 430 | 2550 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 58,53,49,40,38,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2560 | 430 | 2560 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 58,53,49,41,38,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2570 | 430 | 2570 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 58,53,49,41,38,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2580 | 430 | 2580 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 59,53,49,41,38,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2590 | 430 | 2590 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 59,53,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2600 | 430 | 2600 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 59,53,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2610 | 430 | 2610 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 59,53,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2620 | 430 | 2620 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 59,53,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2630 | 430 | 2630 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 59,53,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2640 | 430 | 2640 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 59,53,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2650 | 430 | 2650 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 59,53,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2660 | 430 | 2660 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 59,53,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2670 | 430 | 2670 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,61,60,55,53 | 23 | 59,53,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2680 | 430 | 2680 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,62,60,55,53 | 23 | 59,53,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2690 | 430 | 2690 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,62,60,55,53 | 23 | 59,53,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2700 | 430 | 2700 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,62,61,56,53 | 23 | 59,54,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2710 | 430 | 2710 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,62,61,56,53 | 23 | 59,54,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2720 | 430 | 2720 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,62,61,56,54 | 23 | 59,54,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2730 | 430 | 2730 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,62,61,56,54 | 23 | 59,54,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2740 | 430 | 2740 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 23 | 59,54,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2750 | 430 | 2750 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 23 | 59,54,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2800 | 430 | 2800 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 59,54,50,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2770 | 430 | 2770 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 23 | 59,54,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2780 | 430 | 2780 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 23 | 59,54,49,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2790 | 430 | 2790 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 59,54,50,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2800 | 430 | 2800 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 59,54,50,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2810 | 430 | 2810 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 59,54,50,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2820 | 430 | 2820 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 59,54,50,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2830 | 430 | 2830 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 59,54,50,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2840 | 430 | 2840 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 59,54,50,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2850 | 430 | 2850 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 59,54,50,41,39,35 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2860 | 430 | 2860 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 59,54,50,41,39,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2870 | 430 | 2870 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 60,54,50,41,39,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2880 | 430 | 2880 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 60,54,50,41,39,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2890 | 430 | 2890 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 60,54,50,42,39,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 2900 | 430 | 2900 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,62,62,61,56,54 | 24 | 60,54,50,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 2900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3000 | 430 | 3000 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,61,56,54 | 24 | 60,54,50,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3010 | 430 | 3010 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,61,56,54 | 24 | 60,54,50,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3020 | 430 | 3020 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,61,56,54 | 24 | 60,55,50,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3030 | 430 | 3030 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,61,56,54 | 24 | 60,55,50,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3040 | 430 | 3040 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,61,56,54 | 24 | 60,55,50,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3050 | 430 | 3050 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,61,56,54 | 24 | 60,55,50,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3060 | 430 | 3060 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,61,56,54 | 24 | 60,55,50,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3070 | 430 | 3070 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,62,56,54 | 24 | 60,55,50,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3080 | 430 | 3080 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,62,56,54 | 25 | 60,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3090 | 430 | 3090 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,62,56,54 | 25 | 60,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3100 | 430 | 3100 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,62,56,54 | 25 | 60,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3110 | 430 | 3110 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,62,56,54 | 25 | 60,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3120 | 430 | 3120 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,62,56,54 | 25 | 60,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3130 | 430 | 3130 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,62,57,54 | 25 | 60,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3140 | 430 | 3140 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,62,57,54 | 25 | 60,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3150 | 430 | 3150 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,62,57,54 | 25 | 60,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3160 | 430 | 3160 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,63,62,57,54 | 25 | 60,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3170 | 430 | 3170 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,62,57,54 | 25 | 60,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3180 | 430 | 3180 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,62,57,54 | 25 | 61,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3190 | 430 | 3190 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,62,57,54 | 25 | 61,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3200 | 430 | 3200 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,62,57,54 | 25 | 61,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3210 | 430 | 3210 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,62,57,54 | 25 | 61,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3220 | 430 | 3220 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,62,57,55 | 25 | 61,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3230 | 430 | 3230 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,63,62,57,55 | 25 | 61,55,51,42,40,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3240 | 430 | 3240 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,42,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3250 | 430 | 3250 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,42,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3260 | 430 | 3260 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,42,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3270 | 430 | 3270 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3280 | 430 | 3280 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3290 | 430 | 3290 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3300 | 430 | 3300 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3310 | 430 | 3310 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3320 | 430 | 3320 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3330 | 430 | 3330 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3340 | 430 | 3340 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3350 | 430 | 3350 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3360 | 430 | 3360 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3370 | 430 | 3370 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3380 | 430 | 3380 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,55,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3390 | 430 | 3390 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 25 | 61,56,51,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3400 | 430 | 3400 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3410 | 430 | 3410 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3420 | 430 | 3420 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3430 | 430 | 3430 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3440 | 430 | 3440 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,63,64,62,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3450 | 430 | 3450 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,64,62,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3460 | 430 | 3460 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,64,62,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3470 | 430 | 3470 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,64,62,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3480 | 430 | 3480 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,64,62,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3490 | 430 | 3490 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,64,63,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3500 | 430 | 3500 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,64,63,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3510 | 430 | 3510 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,64,63,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3520 | 430 | 3520 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,64,63,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3530 | 430 | 3530 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,64,63,57,55 | 26 | 61,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3540 | 430 | 3540 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,64,63,57,55 | 26 | 62,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3550 | 430 | 3550 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,64,63,57,55 | 26 | 62,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3560 | 430 | 3560 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,65,63,57,55 | 26 | 62,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3570 | 430 | 3570 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,65,63,57,55 | 26 | 62,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3580 | 430 | 3580 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,65,63,57,55 | 26 | 62,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3590 | 430 | 3590 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,65,63,57,55 | 26 | 62,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3600 | 430 | 3600 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,65,63,57,55 | 26 | 62,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3610 | 430 | 3610 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,65,63,57,55 | 26 | 62,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3620 | 430 | 3620 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,65,63,58,55 | 26 | 62,56,52,43,41,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3630 | 430 | 3630 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,65,63,58,55 | 26 | 62,56,52,43,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3640 | 430 | 3640 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,65,63,58,55 | 26 | 62,56,52,43,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3650 | 430 | 3650 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,65,63,58,55 | 26 | 62,56,52,43,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3660 | 430 | 3660 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,63,58,55 | 26 | 62,56,52,43,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3670 | 430 | 3670 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,63,58,55 | 26 | 62,56,52,43,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3680 | 430 | 3680 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,63,58,55 | 26 | 62,56,52,43,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3690 | 430 | 3690 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,63,58,55 | 26 | 62,56,52,44,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 14 | 3700 | 430 | 3700 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,64,65,63,58,55 | 26 | 62,56,52,44,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 14 | 3700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1500 | 575 | 1500 | 1 | 0.25 | 0.75 | 0.01 | 14 | 63,58,54,52,49,49 | 15 | 51,48,41,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1505 | 575 | 1505 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,49,49 | 15 | 51,48,41,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1505 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1510 | 575 | 1510 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,49,49 | 15 | 51,48,41,34,31,27 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1515 | 575 | 1515 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,49,49 | 15 | 51,48,41,34,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1515 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1520 | 575 | 1520 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,49,49 | 15 | 51,48,41,35,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1525 | 575 | 1525 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,49,49 | 15 | 51,48,41,35,31,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1525 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1530 | 575 | 1530 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,49,49 | 15 | 51,48,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1535 | 575 | 1535 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,49,49 | 15 | 51,48,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1535 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1540 | 575 | 1540 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,49,49 | 15 | 51,48,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1545 | 575 | 1545 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,49,49 | 15 | 51,48,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1545 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1550 | 575 | 1550 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,49,49 | 15 | 51,48,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1555 | 575 | 1555 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 51,48,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1555 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1560 | 575 | 1560 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 51,48,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1565 | 575 | 1565 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 51,48,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1565 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1570 | 575 | 1570 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 51,48,41,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1575 | 575 | 1575 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 51,48,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1575 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1580 | 575 | 1580 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 51,48,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1585 | 575 | 1585 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 51,48,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1585 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1590 | 575 | 1590 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 51,48,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1595 | 575 | 1595 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 52,48,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1595 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1600 | 575 | 1600 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 52,48,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1605 | 575 | 1605 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 52,48,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1605 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1610 | 575 | 1610 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 52,48,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1615 | 575 | 1615 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 52,48,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1615 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1620 | 575 | 1620 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 15 | 52,48,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1625 | 575 | 1625 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 17 | 52,49,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1625 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1630 | 575 | 1630 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 17 | 52,49,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1635 | 575 | 1635 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,54,52,50,49 | 17 | 52,49,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1635 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1640 | 575 | 1640 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,55,52,50,49 | 17 | 52,49,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1645 | 575 | 1645 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,55,53,50,49 | 17 | 52,49,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1645 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1650 | 575 | 1650 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,55,53,50,50 | 17 | 52,49,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1655 | 575 | 1655 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,55,53,50,50 | 17 | 52,49,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1655 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1660 | 575 | 1660 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,55,53,50,50 | 17 | 52,49,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1665 | 575 | 1665 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,55,53,50,50 | 17 | 52,49,42,35,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1665 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1670 | 575 | 1670 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,55,53,50,50 | 17 | 52,49,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1675 | 575 | 1675 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,55,53,50,50 | 17 | 52,49,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1675 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1680 | 575 | 1680 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,55,53,50,50 | 17 | 52,49,42,36,32,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1685 | 575 | 1685 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,55,53,50,50 | 17 | 52,49,42,36,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1685 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1690 | 575 | 1690 | 1 | 0.25 | 0.75 | 0.01 | 14 | 64,58,55,53,50,50 | 17 | 52,49,42,36,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1695 | 575 | 1695 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,50,50 | 17 | 52,49,42,36,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1695 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1700 | 575 | 1700 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,50,50 | 17 | 52,49,42,36,33,28 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1705 | 575 | 1705 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,50,50 | 17 | 52,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1705 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1710 | 575 | 1710 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,58,55,53,50,50 | 17 | 52,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1715 | 575 | 1715 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,50,50 | 17 | 52,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1715 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1720 | 575 | 1720 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,50,50 | 17 | 52,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1725 | 575 | 1725 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,50,50 | 17 | 52,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1725 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1730 | 575 | 1730 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,50,50 | 17 | 52,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1735 | 575 | 1735 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,50,50 | 17 | 52,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1735 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1740 | 575 | 1740 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,50,50 | 17 | 52,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1745 | 575 | 1745 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,50,50 | 17 | 52,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1745 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1750 | 575 | 1750 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,50,50 | 17 | 52,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1755 | 575 | 1755 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,50,50 | 17 | 53,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1755 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1760 | 575 | 1760 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,51,50 | 17 | 53,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1765 | 575 | 1765 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,51,50 | 17 | 53,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1765 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1770 | 575 | 1770 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,51,50 | 17 | 53,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1775 | 575 | 1775 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,51,50 | 17 | 53,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1775 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1780 | 575 | 1780 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,51,50 | 17 | 53,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1785 | 575 | 1785 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,51,50 | 17 | 53,49,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1785 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1790 | 575 | 1790 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,51,50 | 18 | 53,50,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1795 | 575 | 1795 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,51,50 | 18 | 53,50,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1795 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1800 | 575 | 1800 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,55,53,51,50 | 18 | 53,50,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1805 | 575 | 1805 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,53,51,50 | 18 | 53,50,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1805 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1810 | 575 | 1810 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,53,51,50 | 18 | 53,50,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1815 | 575 | 1815 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,53,51,50 | 18 | 53,50,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1815 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1820 | 575 | 1820 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,53,51,50 | 18 | 53,50,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1825 | 575 | 1825 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,53,51,50 | 18 | 53,50,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1825 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1830 | 575 | 1830 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,53,51,50 | 18 | 53,50,43,36,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1835 | 575 | 1835 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,53,51,50 | 18 | 53,50,43,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1835 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1840 | 575 | 1840 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,43,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1845 | 575 | 1845 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1845 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1850 | 575 | 1850 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,33,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1855 | 575 | 1855 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1855 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1860 | 575 | 1860 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1865 | 575 | 1865 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1865 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1870 | 575 | 1870 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1875 | 575 | 1875 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1875 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1880 | 575 | 1880 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1885 | 575 | 1885 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1885 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1890 | 575 | 1890 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1895 | 575 | 1895 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1895 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1900 | 575 | 1900 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1905 | 575 | 1905 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,50 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1905 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1910 | 575 | 1910 | 1 | 0.25 | 0.75 | 0.01 | 15 | 65,59,56,54,51,51 | 18 | 53,50,44,37,34,29 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1915 | 575 | 1915 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,51,51 | 18 | 53,50,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1915 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1920 | 576 | 1920 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,51,51 | 18 | 53,50,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1925 | 575 | 1925 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,51,51 | 18 | 53,50,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1925 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1930 | 575 | 1930 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,51,51 | 18 | 54,50,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1935 | 575 | 1935 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,51,51 | 18 | 54,50,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1935 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1940 | 575 | 1940 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,51,51 | 18 | 54,50,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1945 | 575 | 1945 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,51,51 | 18 | 54,50,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1945 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1950 | 575 | 1950 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,51,51 | 18 | 54,50,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1955 | 575 | 1955 | 1 | 0.25 | 0.75 | 0.01 | 16 | 66,59,56,54,51,51 | 18 | 54,50,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1955 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1960 | 575 | 1960 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,56,54,51,51 | 18 | 54,50,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1965 | 590 | 1965 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,56,54,51,51 | 18 | 54,50,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1965 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1970 | 575 | 1970 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,56,54,51,51 | 19 | 54,51,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1975 | 575 | 1975 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,56,54,51,51 | 19 | 54,51,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1975 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1980 | 575 | 1980 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,56,54,51,51 | 19 | 54,51,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1990 | 575 | 1990 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,54,52,51 | 19 | 54,51,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 1995 | 575 | 1995 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,54,52,51 | 19 | 54,51,44,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 1995 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2000 | 575 | 2000 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,54,52,51 | 19 | 54,51,45,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2010 | 575 | 2010 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,54,52,51 | 19 | 54,51,45,37,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2020 | 575 | 2020 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,54,52,51 | 19 | 54,51,45,38,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2030 | 575 | 2030 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,54,52,51 | 19 | 54,51,45,38,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2040 | 575 | 2040 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,54,52,51 | 19 | 54,51,45,38,34,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2050 | 575 | 2050 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,54,52,51 | 19 | 54,51,45,38,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2060 | 575 | 2060 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,55,52,51 | 19 | 54,51,45,38,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2070 | 575 | 2070 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,55,52,51 | 19 | 54,51,45,38,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2080 | 575 | 2080 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,55,52,51 | 19 | 54,51,45,38,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2090 | 575 | 2090 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,55,52,51 | 19 | 54,51,45,38,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2100 | 575 | 2100 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,55,52,51 | 19 | 54,51,45,38,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2110 | 575 | 2110 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,55,52,51 | 19 | 54,51,45,38,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2120 | 575 | 2120 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,55,52,51 | 19 | 54,51,45,38,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2130 | 575 | 2130 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,55,52,51 | 19 | 55,51,45,38,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2140 | 575 | 2140 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,55,52,51 | 19 | 55,51,45,38,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2150 | 575 | 2150 | 1 | 0.25 | 0.75 | 0.01 | 17 | 66,60,57,55,52,51 | 19 | 55,51,45,38,35,30 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2160 | 575 | 2160 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,57,55,52,51 | 20 | 55,51,46,38,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2170 | 575 | 2170 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,57,55,52,51 | 20 | 55,52,46,38,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2180 | 575 | 2180 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,55,52,51 | 20 | 55,52,46,38,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2190 | 575 | 2190 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,55,52,51 | 20 | 55,52,46,38,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2200 | 575 | 2200 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,55,52,51 | 20 | 55,52,46,38,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2210 | 663 | 2210 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,55,52,52 | 20 | 55,52,46,38,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2220 | 666 | 2220 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,55,52,52 | 20 | 55,52,46,39,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2230 | 575 | 2230 | 1 | 0.25 | 0.75 | 0.01 | 17 | 67,60,58,55,52,52 | 20 | 55,52,46,39,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2240 | 575 | 2240 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,55,52,52 | 20 | 55,52,46,39,35,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2250 | 575 | 2250 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,55,53,52 | 20 | 55,52,46,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2260 | 575 | 2260 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,55,53,52 | 20 | 55,52,46,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2270 | 575 | 2270 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,55,53,52 | 20 | 55,52,46,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2280 | 575 | 2280 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,55,53,52 | 20 | 55,52,46,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2290 | 575 | 2290 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,55,53,52 | 20 | 55,52,46,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2300 | 575 | 2300 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,55,53,52 | 20 | 55,52,46,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2310 | 575 | 2310 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,56,53,52 | 20 | 55,52,46,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2320 | 575 | 2320 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,56,53,52 | 20 | 55,52,46,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2330 | 575 | 2330 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,56,53,52 | 20 | 55,52,46,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2340 | 575 | 2340 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,56,53,52 | 21 | 56,52,47,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2350 | 575 | 2350 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,56,53,52 | 21 | 56,52,47,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2360 | 575 | 2360 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,56,53,52 | 21 | 56,52,47,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2370 | 575 | 2370 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,56,53,52 | 21 | 56,52,47,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2380 | 575 | 2380 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,56,53,52 | 21 | 56,52,47,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2390 | 575 | 2390 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,58,56,53,52 | 21 | 56,53,47,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2400 | 575 | 2400 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,59,56,53,52 | 21 | 56,53,47,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2410 | 575 | 2410 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,59,56,53,52 | 21 | 56,53,47,39,36,31 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2420 | 575 | 2420 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,59,56,53,52 | 21 | 56,53,47,39,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2430 | 575 | 2430 | 1 | 0.25 | 0.75 | 0.01 | 18 | 67,61,59,56,53,52 | 21 | 56,53,47,39,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2440 | 575 | 2440 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,56,53,52 | 21 | 56,53,47,39,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2450 | 575 | 2450 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,56,53,52 | 21 | 56,53,47,40,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2460 | 575 | 2460 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,56,53,52 | 21 | 56,53,47,40,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2470 | 575 | 2470 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,56,53,52 | 21 | 56,53,47,40,36,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2480 | 575 | 2480 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,56,53,52 | 21 | 56,53,47,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2490 | 575 | 2490 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,56,53,52 | 21 | 56,53,47,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2500 | 575 | 2500 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,56,53,52 | 21 | 56,53,47,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2510 | 575 | 2510 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,56,53,52 | 21 | 56,53,47,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2520 | 756 | 2520 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,56,53,52 | 21 | 56,53,47,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2530 | 575 | 2530 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,56,53,52 | 22 | 56,53,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2540 | 575 | 2540 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,56,54,52 | 22 | 56,53,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2550 | 575 | 2550 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,61,59,56,54,53 | 22 | 56,53,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2560 | 575 | 2560 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,59,56,54,53 | 22 | 56,53,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2570 | 575 | 2570 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,59,56,54,53 | 22 | 57,53,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2580 | 575 | 2580 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,59,56,54,53 | 22 | 57,53,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2590 | 575 | 2590 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,59,57,54,53 | 22 | 57,53,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2600 | 575 | 2600 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,59,57,54,53 | 22 | 57,53,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2610 | 575 | 2610 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,59,57,54,53 | 22 | 57,53,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2620 | 575 | 2620 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,59,57,54,53 | 22 | 57,53,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2630 | 575 | 2630 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,59,57,54,53 | 22 | 57,53,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2640 | 575 | 2640 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,60,57,54,53 | 23 | 57,54,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2650 | 575 | 2650 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,60,57,54,53 | 23 | 57,54,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2660 | 575 | 2660 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,60,57,54,53 | 23 | 57,54,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2670 | 575 | 2670 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,60,57,54,53 | 23 | 57,54,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2680 | 575 | 2680 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,60,57,54,53 | 23 | 57,54,48,40,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2690 | 575 | 2690 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,60,57,54,53 | 23 | 57,54,48,41,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2700 | 575 | 2700 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,60,57,54,53 | 23 | 57,54,48,41,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2710 | 575 | 2710 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,60,57,54,53 | 23 | 57,54,48,41,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2720 | 575 | 2720 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,60,57,54,53 | 23 | 57,54,48,41,37,32 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2730 | 575 | 2730 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,60,57,54,53 | 23 | 57,54,48,41,37,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2740 | 575 | 2740 | 1 | 0.25 | 0.75 | 0.01 | 19 | 68,62,60,57,54,53 | 23 | 57,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2750 | 575 | 2750 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,54,53 | 23 | 57,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2800 | 575 | 2800 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,54,53 | 23 | 57,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2770 | 575 | 2770 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,54,53 | 23 | 57,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2780 | 575 | 2780 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,54,53 | 23 | 57,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2790 | 575 | 2790 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,54,53 | 23 | 57,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2800 | 575 | 2800 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,54,53 | 23 | 57,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2810 | 575 | 2810 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,54,53 | 23 | 57,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2820 | 575 | 2820 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,54,53 | 23 | 57,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2830 | 575 | 2830 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,54,53 | 23 | 58,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2840 | 575 | 2840 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,54,53 | 23 | 58,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2850 | 575 | 2850 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,54,53 | 23 | 58,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2860 | 575 | 2860 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,54,53 | 23 | 58,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2870 | 575 | 2870 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,55,53 | 23 | 58,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2880 | 575 | 2880 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,55,53 | 23 | 58,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2890 | 575 | 2890 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,57,55,53 | 23 | 58,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 2900 | 575 | 2900 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,62,60,58,55,53 | 23 | 58,54,49,41,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 2900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3000 | 575 | 3000 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,61,58,55,54 | 24 | 58,55,50,42,38,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3010 | 575 | 3010 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,61,58,55,54 | 24 | 58,55,50,42,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3020 | 575 | 3020 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,61,58,55,54 | 24 | 58,55,50,42,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3030 | 575 | 3030 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,61,58,55,54 | 24 | 58,55,50,42,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3040 | 575 | 3040 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,61,58,55,54 | 24 | 58,55,50,42,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3050 | 575 | 3050 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,61,58,55,54 | 24 | 58,55,50,42,39,33 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3060 | 575 | 3060 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,61,58,55,54 | 24 | 58,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3070 | 575 | 3070 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,61,58,55,54 | 24 | 58,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3080 | 575 | 3080 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,61,58,55,54 | 24 | 58,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3090 | 575 | 3090 | 1 | 0.25 | 0.75 | 0.01 | 20 | 69,63,61,58,55,54 | 24 | 58,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3100 | 575 | 3100 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,61,58,55,54 | 24 | 58,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3110 | 575 | 3110 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,61,58,55,54 | 24 | 59,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3120 | 575 | 3120 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,61,58,55,54 | 24 | 59,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3130 | 575 | 3130 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,61,58,55,54 | 24 | 59,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3140 | 575 | 3140 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,61,58,55,54 | 24 | 59,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3150 | 575 | 3150 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,61,58,55,54 | 24 | 59,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3160 | 575 | 3160 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,61,58,55,54 | 24 | 59,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3170 | 575 | 3170 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,61,58,55,54 | 24 | 59,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3180 | 575 | 3180 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,61,58,55,54 | 24 | 59,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3190 | 575 | 3190 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,61,58,55,54 | 24 | 59,55,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3200 | 575 | 3200 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,58,55,54 | 25 | 59,56,50,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3210 | 575 | 3210 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,58,55,54 | 25 | 59,56,51,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3220 | 575 | 3220 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,58,55,54 | 25 | 59,56,51,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3230 | 575 | 3230 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,58,55,54 | 25 | 59,56,51,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3240 | 575 | 3240 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,59,56,54 | 25 | 59,56,51,42,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3250 | 575 | 3250 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,59,56,54 | 25 | 59,56,51,43,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3260 | 575 | 3260 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,59,56,54 | 25 | 59,56,51,43,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3270 | 575 | 3270 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,59,56,54 | 25 | 59,56,51,43,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3280 | 575 | 3280 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,59,56,54 | 25 | 59,56,51,43,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3290 | 575 | 3290 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,59,56,54 | 25 | 59,56,51,43,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3300 | 575 | 3300 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,59,56,54 | 25 | 59,56,51,43,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3310 | 575 | 3310 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,59,56,54 | 25 | 59,56,51,43,39,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3320 | 575 | 3320 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,59,56,54 | 25 | 59,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3330 | 575 | 3330 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,59,56,54 | 25 | 59,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3340 | 575 | 3340 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,63,62,59,56,54 | 25 | 59,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3350 | 575 | 3350 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,54 | 25 | 59,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3360 | 575 | 3360 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,54 | 25 | 59,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3370 | 575 | 3370 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,54 | 25 | 59,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3380 | 575 | 3380 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,54 | 25 | 59,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3390 | 575 | 3390 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,54 | 25 | 59,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3400 | 575 | 3400 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,54 | 25 | 59,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3410 | 575 | 3410 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,55 | 25 | 59,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3420 | 575 | 3420 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,55 | 25 | 60,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3430 | 575 | 3430 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,55 | 25 | 60,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3440 | 575 | 3440 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,55 | 25 | 60,56,51,43,40,34 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3450 | 575 | 3450 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,55 | 25 | 60,56,51,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3460 | 575 | 3460 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,55 | 25 | 60,56,51,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3470 | 575 | 3470 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,55 | 25 | 60,56,51,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3480 | 575 | 3480 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,55 | 26 | 60,56,52,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3490 | 575 | 3490 | 1 | 0.25 | 0.75 | 0.01 | 21 | 70,64,62,59,56,55 | 26 | 60,56,52,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3500 | 575 | 3500 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,62,59,56,55 | 26 | 60,56,52,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3510 | 575 | 3510 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,62,59,56,55 | 26 | 60,56,52,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3520 | 575 | 3520 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,59,56,55 | 26 | 60,56,52,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3530 | 575 | 3530 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,59,56,55 | 26 | 60,57,52,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3540 | 575 | 3540 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,59,56,55 | 26 | 60,57,52,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3550 | 575 | 3550 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,59,56,55 | 26 | 60,57,52,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3560 | 575 | 3560 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,59,56,55 | 26 | 60,57,52,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3570 | 575 | 3570 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,59,56,55 | 26 | 60,57,52,43,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3580 | 575 | 3580 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,59,56,55 | 26 | 60,57,52,44,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3590 | 575 | 3590 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,59,56,55 | 26 | 60,57,52,44,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3600 | 575 | 3600 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,59,56,55 | 26 | 60,57,52,44,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3610 | 575 | 3610 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,59,56,55 | 26 | 60,57,52,44,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3620 | 575 | 3620 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,59,56,55 | 26 | 60,57,52,44,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3630 | 575 | 3630 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,56,55 | 26 | 60,57,52,44,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3640 | 575 | 3640 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,56,55 | 26 | 60,57,52,44,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3650 | 575 | 3650 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,56,55 | 26 | 60,57,52,44,40,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3660 | 575 | 3660 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 26 | 60,57,52,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3670 | 575 | 3670 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 26 | 60,57,52,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3680 | 575 | 3680 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 26 | 60,57,52,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3690 | 575 | 3690 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 26 | 60,57,52,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3700 | 575 | 3700 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 26 | 60,57,52,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3710 | 575 | 3710 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 26 | 60,57,52,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3720 | 575 | 3720 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 26 | 60,57,52,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3730 | 575 | 3730 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 26 | 60,57,52,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3740 | 575 | 3740 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 26 | 60,57,52,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3750 | 575 | 3750 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 26 | 60,57,52,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3760 | 575 | 3760 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 27 | 61,57,53,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3770 | 575 | 3770 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 27 | 61,57,53,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3780 | 575 | 3780 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 27 | 61,57,53,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3790 | 575 | 3790 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 27 | 61,57,53,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3800 | 575 | 3800 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 27 | 61,57,53,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3810 | 575 | 3810 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 27 | 61,57,53,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3820 | 575 | 3820 | 1 | 0.25 | 0.75 | 0.01 | 22 | 71,64,63,60,57,55 | 27 | 61,57,53,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3830 | 575 | 3830 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,63,60,57,55 | 27 | 61,57,53,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3840 | 575 | 3840 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,63,60,57,55 | 27 | 61,57,53,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3850 | 575 | 3850 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,63,60,57,55 | 27 | 61,57,53,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3860 | 575 | 3860 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,63,60,57,55 | 27 | 61,57,53,44,41,35 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3870 | 575 | 3870 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,64,60,57,55 | 27 | 61,57,53,44,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3880 | 575 | 3880 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,64,60,57,55 | 27 | 61,57,53,44,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3890 | 575 | 3890 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,64,60,57,55 | 27 | 61,58,53,44,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3900 | 575 | 3900 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,64,60,57,55 | 27 | 61,58,53,44,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3910 | 575 | 3910 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,64,60,57,55 | 27 | 61,58,53,44,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3920 | 575 | 3920 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,64,60,57,55 | 27 | 61,58,53,44,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3930 | 575 | 3930 | 1 | 0.25 | 0.75 | 0.01 | 23 | 71,65,64,60,57,55 | 27 | 61,58,53,45,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3940 | 575 | 3940 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,60,57,55 | 27 | 61,58,53,45,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3950 | 575 | 3950 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,60,57,56 | 27 | 61,58,53,45,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3960 | 575 | 3960 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,60,57,56 | 27 | 61,58,53,45,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3970 | 575 | 3970 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,60,57,56 | 27 | 61,58,53,45,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3980 | 575 | 3980 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,60,57,56 | 27 | 61,58,53,45,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 3990 | 575 | 3990 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,60,57,56 | 27 | 61,58,53,45,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 3990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4000 | 575 | 4000 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,60,57,56 | 27 | 61,58,53,45,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4010 | 575 | 4010 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,60,57,56 | 27 | 61,58,53,45,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4020 | 575 | 4020 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,60,57,56 | 27 | 61,58,53,45,41,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4030 | 575 | 4030 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,60,57,56 | 27 | 61,58,53,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4040 | 575 | 4040 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,60,57,56 | 27 | 61,58,53,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4050 | 575 | 4050 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,60,57,56 | 27 | 61,58,53,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4060 | 575 | 4060 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,57,56 | 27 | 61,58,53,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4070 | 575 | 4070 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,57,56 | 28 | 61,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4080 | 575 | 4080 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,57,56 | 28 | 61,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4090 | 575 | 4090 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,57,56 | 28 | 61,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4100 | 575 | 4100 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,57,56 | 28 | 61,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4110 | 575 | 4110 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,57,56 | 28 | 61,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4120 | 575 | 4120 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,57,56 | 28 | 61,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4130 | 575 | 4130 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,58,56 | 28 | 61,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4140 | 575 | 4140 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4150 | 575 | 4150 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4160 | 575 | 4160 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4170 | 575 | 4170 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4180 | 575 | 4180 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4190 | 575 | 4190 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4200 | 575 | 4200 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4210 | 575 | 4210 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4220 | 575 | 4220 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4230 | 575 | 4230 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4240 | 575 | 4240 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,64,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4250 | 575 | 4250 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4260 | 575 | 4260 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4270 | 575 | 4270 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,58,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4280 | 575 | 4280 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,59,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4290 | 575 | 4290 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,59,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4300 | 575 | 4300 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,59,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4310 | 575 | 4310 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,59,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4320 | 575 | 4320 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,59,54,45,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4330 | 575 | 4330 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,59,54,46,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4340 | 575 | 4340 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,59,54,46,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4350 | 575 | 4350 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,59,54,46,42,36 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4360 | 575 | 4360 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,59,54,46,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4370 | 575 | 4370 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,65,65,61,58,56 | 28 | 62,59,54,46,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4380 | 575 | 4380 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,65,61,58,56 | 28 | 62,59,54,46,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4390 | 575 | 4390 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,65,61,58,56 | 28 | 62,59,54,46,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4400 | 575 | 4400 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,65,61,58,56 | 28 | 62,59,54,46,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4410 | 575 | 4410 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,65,61,58,56 | 30 | 62,59,55,46,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4420 | 575 | 4420 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,65,61,58,56 | 30 | 62,59,55,46,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4430 | 575 | 4430 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,65,61,58,56 | 30 | 62,59,55,46,42,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4440 | 575 | 4440 | 1 | 0.25 | 0.75 | 0.01 | 24 | 72,66,65,61,58,56 | 30 | 62,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4450 | 575 | 4450 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,61,58,56 | 30 | 62,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4460 | 575 | 4460 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,61,58,56 | 30 | 62,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4470 | 575 | 4470 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,61,58,56 | 30 | 62,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4480 | 575 | 4480 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,61,58,56 | 30 | 62,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4490 | 575 | 4490 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,61,58,56 | 30 | 62,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4500 | 575 | 4500 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,61,58,56 | 30 | 62,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4510 | 575 | 4510 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,61,58,56 | 30 | 62,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4520 | 575 | 4520 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,61,58,56 | 30 | 62,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4530 | 575 | 4530 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,61,58,56 | 30 | 62,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4540 | 575 | 4540 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,61,58,56 | 30 | 62,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4550 | 575 | 4550 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,58,56 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4560 | 575 | 4560 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,58,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4570 | 575 | 4570 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,58,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4580 | 575 | 4580 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,58,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4590 | 575 | 4590 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,58,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4600 | 575 | 4600 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,58,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4610 | 575 | 4610 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,58,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4620 | 575 | 4620 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,58,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4630 | 575 | 4630 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,58,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4640 | 575 | 4640 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,58,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4650 | 575 | 4650 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,58,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4660 | 575 | 4660 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,58,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4670 | 575 | 4670 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,65,62,59,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4680 | 575 | 4680 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4690 | 575 | 4690 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4700 | 575 | 4700 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4710 | 575 | 4710 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 30 | 63,59,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4720 | 575 | 4720 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 30 | 63,60,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4730 | 575 | 4730 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 30 | 63,60,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4740 | 575 | 4740 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 30 | 63,60,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4750 | 575 | 4750 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 30 | 63,60,55,46,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4760 | 575 | 4760 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 30 | 63,60,55,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4770 | 575 | 4770 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4780 | 575 | 4780 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4790 | 575 | 4790 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4800 | 575 | 4800 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4810 | 575 | 4810 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4820 | 575 | 4820 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4830 | 575 | 4830 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4840 | 575 | 4840 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4850 | 575 | 4850 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4860 | 575 | 4860 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4870 | 575 | 4870 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4880 | 575 | 4880 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,43,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4890 | 575 | 4890 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,44,37 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4900 | 575 | 4900 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,44,38 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4910 | 575 | 4910 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,44,38 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4920 | 575 | 4920 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,44,38 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4930 | 575 | 4930 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,44,38 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4940 | 575 | 4940 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,44,38 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4950 | 575 | 4950 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,44,38 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4960 | 575 | 4960 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,44,38 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4970 | 575 | 4970 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,44,38 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4980 | 575 | 4980 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,44,38 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 4990 | 575 | 4990 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,66,66,62,59,57 | 31 | 63,60,56,47,44,38 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 4990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 16 | 5000 | 575 | 5000 | 1 | 0.25 | 0.75 | 0.01 | 25 | 73,67,66,62,59,57 | 31 | 63,60,56,47,44,38 | 55 | 75 | 0.5" Fiber Free Foam | 16 | 5000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3000 | 1185 | 3000 | 1 | 0.25 | 0.75 | 0.01 | 27 | 72,69,67,66,62,59 | 32 | 65,62,55,47,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3010 | 1185 | 3010 | 1 | 0.25 | 0.75 | 0.01 | 27 | 72,69,67,66,62,59 | 32 | 65,62,55,47,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3020 | 1185 | 3020 | 1 | 0.25 | 0.75 | 0.01 | 27 | 72,69,67,66,62,59 | 32 | 65,62,55,47,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3030 | 1185 | 3030 | 1 | 0.25 | 0.75 | 0.01 | 27 | 72,69,67,66,62,59 | 32 | 65,62,55,47,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3040 | 1185 | 3040 | 1 | 0.25 | 0.75 | 0.01 | 27 | 73,69,67,66,62,59 | 32 | 65,62,55,47,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3050 | 1185 | 3050 | 1 | 0.25 | 0.75 | 0.01 | 27 | 73,69,67,66,62,59 | 32 | 65,62,55,48,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3060 | 1185 | 3060 | 1 | 0.25 | 0.75 | 0.01 | 27 | 73,69,67,66,62,59 | 32 | 65,62,55,48,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3070 | 1185 | 3070 | 1 | 0.25 | 0.75 | 0.01 | 27 | 73,69,67,66,62,59 | 32 | 65,62,55,48,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3080 | 1185 | 3080 | 1 | 0.25 | 0.75 | 0.01 | 27 | 73,69,67,66,62,59 | 32 | 65,62,55,48,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3090 | 1185 | 3090 | 1 | 0.25 | 0.75 | 0.01 | 27 | 73,69,67,66,62,59 | 32 | 65,62,55,48,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3100 | 1185 | 3100 | 1 | 0.25 | 0.75 | 0.01 | 27 | 73,69,67,66,62,59 | 32 | 65,62,56,48,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3110 | 1185 | 3110 | 1 | 0.25 | 0.75 | 0.01 | 27 | 73,69,67,66,62,59 | 32 | 65,62,56,48,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3120 | 1185 | 3120 | 1 | 0.25 | 0.75 | 0.01 | 27 | 73,69,68,66,62,59 | 32 | 65,62,56,48,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3130 | 1185 | 3130 | 1 | 0.25 | 0.75 | 0.01 | 27 | 73,69,68,66,62,59 | 32 | 65,62,56,48,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3140 | 1185 | 3140 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,62,59 | 32 | 65,62,56,48,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3150 | 1185 | 3150 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,62,59 | 32 | 65,62,56,48,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3160 | 1185 | 3160 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,62,59 | 32 | 65,62,56,48,45,42 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3170 | 1185 | 3170 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,62,59 | 32 | 65,62,56,48,45,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3180 | 1185 | 3180 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,62,60 | 32 | 65,62,56,48,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3190 | 1185 | 3190 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,62,60 | 32 | 65,62,56,48,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3200 | 1185 | 3200 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,62,60 | 32 | 65,62,56,48,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3210 | 1185 | 3210 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,63,60 | 33 | 66,63,56,48,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3220 | 1185 | 3220 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,63,60 | 33 | 66,63,56,48,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3230 | 1185 | 3230 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,63,60 | 33 | 66,63,56,48,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3240 | 1185 | 3240 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,63,60 | 33 | 66,63,56,48,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3250 | 1185 | 3250 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,63,60 | 33 | 66,63,56,49,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3260 | 1185 | 3260 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,63,60 | 33 | 66,63,56,49,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3270 | 1185 | 3270 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,63,60 | 33 | 66,63,56,49,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3280 | 1185 | 3280 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,63,60 | 33 | 66,63,56,49,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3290 | 1185 | 3290 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,66,63,60 | 33 | 66,63,56,49,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3300 | 1185 | 3300 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,67,63,60 | 33 | 66,63,56,49,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3310 | 1185 | 3310 | 1 | 0.25 | 0.75 | 0.01 | 28 | 73,70,68,67,63,60 | 33 | 66,63,56,49,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3320 | 1185 | 3320 | 1 | 0.25 | 0.75 | 0.01 | 28 | 74,70,68,67,63,60 | 33 | 66,63,56,49,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3330 | 1185 | 3330 | 1 | 0.25 | 0.75 | 0.01 | 28 | 74,70,68,67,63,60 | 33 | 66,63,57,49,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3340 | 1185 | 3340 | 1 | 0.25 | 0.75 | 0.01 | 28 | 74,70,68,67,63,60 | 33 | 66,63,57,49,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3350 | 1185 | 3350 | 1 | 0.25 | 0.75 | 0.01 | 28 | 74,70,68,67,63,60 | 33 | 66,63,57,49,46,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3360 | 1185 | 3360 | 1 | 0.25 | 0.75 | 0.01 | 28 | 74,70,68,67,63,60 | 33 | 66,63,57,49,47,43 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3370 | 1185 | 3370 | 1 | 0.25 | 0.75 | 0.01 | 28 | 74,70,68,67,63,60 | 33 | 66,63,57,49,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3380 | 1185 | 3380 | 1 | 0.25 | 0.75 | 0.01 | 28 | 74,70,68,67,63,60 | 33 | 66,63,57,49,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3390 | 1185 | 3390 | 1 | 0.25 | 0.75 | 0.01 | 28 | 74,70,68,67,63,60 | 33 | 66,63,57,49,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3400 | 1185 | 3400 | 1 | 0.25 | 0.75 | 0.01 | 28 | 74,70,69,67,63,60 | 33 | 66,63,57,49,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3410 | 1185 | 3410 | 1 | 0.25 | 0.75 | 0.01 | 28 | 74,70,69,67,63,60 | 33 | 66,63,57,49,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3420 | 1185 | 3420 | 1 | 0.25 | 0.75 | 0.01 | 28 | 74,70,69,67,63,60 | 33 | 66,63,57,49,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3430 | 1185 | 3430 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,63,60 | 33 | 66,63,57,49,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3440 | 1185 | 3440 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,63,60 | 33 | 67,63,57,49,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3450 | 1185 | 3450 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,63,60 | 33 | 67,63,57,50,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3460 | 1185 | 3460 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,63,60 | 33 | 67,63,57,50,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3470 | 1185 | 3470 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,63,60 | 33 | 67,63,57,50,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3480 | 1185 | 2600 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,63,60 | 34 | 67,64,57,50,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3490 | 1185 | 3490 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,63,60 | 34 | 67,64,57,50,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3500 | 1185 | 3500 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,63,60 | 34 | 67,64,57,50,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3510 | 1185 | 3510 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,64,61 | 34 | 67,64,57,50,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3520 | 1185 | 3520 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,64,61 | 34 | 67,64,57,50,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3530 | 1185 | 3530 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,64,61 | 34 | 67,64,57,50,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3540 | 1185 | 3540 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,64,61 | 34 | 67,64,57,50,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3550 | 1185 | 3550 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,64,61 | 34 | 67,64,57,50,47,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3560 | 1185 | 3560 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,64,61 | 34 | 67,64,57,50,48,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3570 | 1185 | 3570 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,64,61 | 34 | 67,64,57,50,48,44 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3580 | 1185 | 3580 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,64,61 | 34 | 67,64,58,50,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3590 | 1185 | 3590 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,64,61 | 34 | 67,64,58,50,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3600 | 1185 | 3600 | 1 | 0.25 | 0.75 | 0.01 | 30 | 74,71,69,67,64,61 | 34 | 67,64,58,50,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3610 | 1185 | 3610 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,69,67,64,61 | 34 | 67,64,58,50,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3620 | 1185 | 3620 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,69,67,64,61 | 34 | 67,64,58,50,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3630 | 1185 | 3630 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,69,67,64,61 | 34 | 67,64,58,50,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3640 | 1185 | 3640 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,69,68,64,61 | 34 | 67,64,58,50,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3650 | 1185 | 3650 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,69,68,64,61 | 34 | 67,64,58,50,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3660 | 1185 | 3660 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,69,68,64,61 | 34 | 67,64,58,50,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3670 | 1185 | 3670 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,69,68,64,61 | 34 | 67,64,58,51,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3680 | 1185 | 3680 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,69,68,64,61 | 34 | 67,64,58,51,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3690 | 1185 | 3690 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,69,68,64,61 | 34 | 68,64,58,51,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3700 | 1185 | 3700 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,69,68,64,61 | 34 | 68,64,58,51,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3710 | 1185 | 3710 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,70,68,64,61 | 34 | 68,64,58,51,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3720 | 1185 | 3720 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,70,68,64,61 | 34 | 68,64,58,51,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3730 | 1185 | 3730 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,70,68,64,61 | 34 | 68,64,58,51,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3740 | 1185 | 3740 | 1 | 0.25 | 0.75 | 0.01 | 30 | 75,71,70,68,64,61 | 34 | 68,64,58,51,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3750 | 1185 | 3750 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,64,61 | 34 | 68,64,58,51,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3760 | 1185 | 3760 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,64,61 | 34 | 68,64,58,51,48,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3770 | 1185 | 3770 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,64,61 | 34 | 68,64,58,51,49,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3780 | 1185 | 3780 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,64,61 | 36 | 68,65,58,51,49,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3790 | 1185 | 3790 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,64,61 | 36 | 68,65,58,51,49,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3800 | 1185 | 3800 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,64,61 | 36 | 68,65,58,51,49,45 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3810 | 1185 | 3810 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,64,61 | 36 | 68,65,58,51,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3820 | 1185 | 3820 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,64,61 | 36 | 68,65,58,51,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3830 | 1185 | 3830 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,65,61 | 36 | 68,65,58,51,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3840 | 1185 | 3840 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,65,61 | 36 | 68,65,59,51,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3850 | 1185 | 3850 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,65,61 | 36 | 68,65,59,51,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3860 | 1185 | 3860 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,65,62 | 36 | 68,65,59,51,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3870 | 1185 | 3870 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,65,62 | 36 | 68,65,59,51,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3880 | 1185 | 3880 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,65,62 | 36 | 68,65,59,51,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3890 | 1185 | 3890 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,65,62 | 36 | 68,65,59,51,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3900 | 1185 | 3900 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,65,62 | 36 | 68,65,59,51,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3910 | 1185 | 3910 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,65,62 | 36 | 68,65,59,52,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3920 | 1185 | 3920 | 1 | 0.25 | 0.75 | 0.01 | 31 | 75,72,70,68,65,62 | 36 | 68,65,59,52,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3930 | 1185 | 3930 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,70,68,65,62 | 36 | 68,65,59,52,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3940 | 1185 | 3940 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,70,68,65,62 | 36 | 68,65,59,52,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3950 | 1185 | 3950 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,70,68,65,62 | 36 | 68,65,59,52,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3960 | 1185 | 3960 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,70,68,65,62 | 36 | 69,65,59,52,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3970 | 1185 | 3970 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,70,68,65,62 | 36 | 69,65,59,52,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3980 | 1185 | 3980 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,70,68,65,62 | 36 | 69,65,59,52,49,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 3990 | 1185 | 3990 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,70,68,65,62 | 36 | 69,65,59,52,50,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 3990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4000 | 1185 | 4000 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,70,68,65,62 | 36 | 69,65,59,52,50,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4010 | 1185 | 4010 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,70,68,65,62 | 36 | 69,65,59,52,50,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4020 | 1185 | 4020 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,70,69,65,62 | 36 | 69,65,59,52,50,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4030 | 1185 | 4030 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,70,69,65,62 | 36 | 69,65,59,52,50,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4040 | 1185 | 4040 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,70,69,65,62 | 36 | 69,65,59,52,50,46 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4050 | 1185 | 4050 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,71,69,65,62 | 36 | 69,65,59,52,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4060 | 1185 | 4060 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,71,69,65,62 | 36 | 69,65,59,52,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4070 | 1185 | 4070 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,71,69,65,62 | 36 | 69,65,59,52,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4080 | 1185 | 4080 | 1 | 0.25 | 0.75 | 0.01 | 31 | 76,72,71,69,65,62 | 36 | 69,65,59,52,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4090 | 1185 | 4090 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,65,62 | 36 | 69,65,59,52,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4100 | 1185 | 4100 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,65,62 | 37 | 69,66,59,52,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4110 | 1185 | 4110 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,65,62 | 37 | 69,66,59,52,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4120 | 1185 | 4120 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,65,62 | 37 | 69,66,59,52,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4130 | 1185 | 4130 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,65,62 | 37 | 69,66,60,52,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4140 | 1185 | 4140 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,65,62 | 37 | 69,66,60,52,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4150 | 1185 | 4150 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,65,62 | 37 | 69,66,60,52,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4160 | 1185 | 4160 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,65,62 | 37 | 69,66,60,53,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4170 | 1185 | 4170 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,65,62 | 37 | 69,66,60,53,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4180 | 1185 | 4180 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,66,62 | 37 | 69,66,60,53,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4190 | 1185 | 4190 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,66,62 | 37 | 69,66,60,53,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4200 | 1185 | 4200 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,66,62 | 37 | 69,66,60,53,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4210 | 1185 | 4210 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,66,62 | 37 | 69,66,60,53,50,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4220 | 1185 | 4220 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,66,62 | 37 | 69,66,60,53,51,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4230 | 1185 | 4230 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,66,62 | 37 | 69,66,60,53,51,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4240 | 1185 | 4240 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,66,62 | 37 | 69,66,60,53,51,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4250 | 1185 | 4250 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,66,62 | 37 | 70,66,60,53,51,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4260 | 1185 | 4260 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,66,63 | 37 | 70,66,60,53,51,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4270 | 1185 | 4270 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,66,63 | 37 | 70,66,60,53,51,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4280 | 1185 | 4280 | 1 | 0.25 | 0.75 | 0.01 | 32 | 76,73,71,69,66,63 | 37 | 70,66,60,53,51,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4290 | 1185 | 4290 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,71,69,66,63 | 37 | 70,66,60,53,51,47 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4300 | 1185 | 4300 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,71,69,66,63 | 37 | 70,66,60,53,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4310 | 1185 | 4310 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,71,69,66,63 | 37 | 70,66,60,53,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4320 | 1185 | 4320 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,71,69,66,63 | 37 | 70,66,60,53,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4330 | 1185 | 4330 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,71,69,66,63 | 37 | 70,66,60,53,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4340 | 1185 | 4340 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,71,69,66,63 | 37 | 70,66,60,53,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4350 | 1185 | 4350 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,71,69,66,63 | 37 | 70,66,60,53,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4360 | 1185 | 4360 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,71,69,66,63 | 37 | 70,66,60,53,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4370 | 1185 | 4370 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,71,69,66,63 | 37 | 70,66,60,53,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4380 | 1185 | 4380 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,71,69,66,63 | 37 | 70,66,60,53,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4390 | 1185 | 4390 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,71,69,66,63 | 37 | 70,66,60,53,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4400 | 1185 | 4400 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,71,69,66,63 | 37 | 70,66,60,53,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4410 | 1185 | 4410 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,72,69,66,63 | 37 | 70,66,60,53,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4420 | 1185 | 4420 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,72,69,66,63 | 37 | 70,66,60,54,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4430 | 1185 | 4430 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,72,69,66,63 | 37 | 70,66,61,54,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4440 | 1185 | 4440 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,72,70,66,63 | 38 | 70,67,61,54,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4450 | 1185 | 4450 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,72,70,66,63 | 38 | 70,67,61,54,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4460 | 1185 | 4460 | 1 | 0.25 | 0.75 | 0.01 | 32 | 77,73,72,70,66,63 | 38 | 70,67,61,54,51,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4470 | 1185 | 4470 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,66,63 | 38 | 70,67,61,54,52,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4480 | 1185 | 4480 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,66,63 | 38 | 70,67,61,54,52,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4490 | 1185 | 4490 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,66,63 | 38 | 70,67,61,54,52,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4500 | 1185 | 4500 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,66,63 | 38 | 70,67,61,54,52,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4510 | 1185 | 4510 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,66,63 | 38 | 70,67,61,54,52,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4520 | 1185 | 4520 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,66,63 | 38 | 70,67,61,54,52,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4530 | 1185 | 4530 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,66,63 | 38 | 70,67,61,54,52,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4540 | 1185 | 4540 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,66,63 | 38 | 70,67,61,54,52,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4550 | 1185 | 4550 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,66,63 | 38 | 70,67,61,54,52,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4560 | 1185 | 4560 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,66,63 | 38 | 71,67,61,54,52,48 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4570 | 1185 | 4570 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,67,63 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4580 | 1185 | 4580 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,67,63 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4590 | 1185 | 4590 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,67,63 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4600 | 1185 | 4600 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,67,63 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4610 | 1185 | 4610 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,67,63 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4620 | 1185 | 4620 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,67,63 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4630 | 1185 | 4630 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,67,63 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4640 | 1185 | 4640 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,67,63 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4650 | 1185 | 4650 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,67,63 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4660 | 1185 | 4660 | 1 | 0.25 | 0.75 | 0.01 | 33 | 77,74,72,70,67,63 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4670 | 1185 | 4670 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,63 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4680 | 1185 | 4680 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,63 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4690 | 1185 | 4690 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,64 | 38 | 71,67,61,54,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4700 | 1185 | 4700 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,64 | 38 | 71,67,61,55,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4710 | 1185 | 4710 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,64 | 38 | 71,67,61,55,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4720 | 1185 | 4720 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,64 | 38 | 71,67,61,55,52,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4730 | 1185 | 4730 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,64 | 38 | 71,67,61,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4740 | 1185 | 4740 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,64 | 38 | 71,67,61,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4750 | 1185 | 4750 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,64 | 38 | 71,67,61,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4760 | 1185 | 4760 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,64 | 38 | 71,67,62,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4770 | 1185 | 4770 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,64 | 38 | 71,67,62,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4780 | 1185 | 4780 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,64 | 38 | 71,67,62,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4790 | 1185 | 4790 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,64 | 38 | 71,67,62,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4800 | 1185 | 4800 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,72,70,67,64 | 38 | 71,67,62,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4810 | 1185 | 4810 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,73,70,67,64 | 38 | 71,67,62,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4820 | 1185 | 4820 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,73,70,67,64 | 39 | 71,68,62,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4830 | 1185 | 4830 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,73,70,67,64 | 39 | 71,68,62,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4840 | 1185 | 4840 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,73,70,67,64 | 39 | 71,68,62,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4850 | 1185 | 4850 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,73,70,67,64 | 39 | 71,68,62,55,53,49 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4860 | 1185 | 4860 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,73,70,67,64 | 39 | 71,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4870 | 1185 | 4870 | 1 | 0.25 | 0.75 | 0.01 | 33 | 78,74,73,70,67,64 | 39 | 71,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4880 | 1185 | 4880 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,70,67,64 | 39 | 71,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4890 | 1185 | 4890 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,70,67,64 | 39 | 72,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4900 | 1185 | 4900 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,67,64 | 39 | 72,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4910 | 1185 | 4910 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,67,64 | 39 | 72,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4920 | 1185 | 4920 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,67,64 | 39 | 72,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4930 | 1185 | 4930 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,67,64 | 39 | 72,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4940 | 1185 | 4940 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,67,64 | 39 | 72,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4950 | 1185 | 4950 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,67,64 | 39 | 72,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4960 | 1185 | 4960 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,67,64 | 39 | 72,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4970 | 1185 | 4970 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,67,64 | 39 | 72,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4980 | 1185 | 4980 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,67,64 | 39 | 72,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 4990 | 1185 | 4990 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,68,64 | 39 | 72,68,62,55,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 4990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5000 | 1185 | 5000 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,68,64 | 39 | 72,68,62,56,53,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5010 | 1185 | 5010 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,68,64 | 39 | 72,68,62,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5020 | 1185 | 5020 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,68,64 | 39 | 72,68,62,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5030 | 1185 | 5030 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,68,64 | 39 | 72,68,62,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5040 | 1185 | 5040 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,68,64 | 39 | 72,68,62,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5050 | 1185 | 5050 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,68,64 | 39 | 72,68,62,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5060 | 1185 | 5060 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,68,64 | 39 | 72,68,62,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5070 | 1185 | 5070 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,68,64 | 39 | 72,68,62,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5080 | 1185 | 5080 | 1 | 0.25 | 0.75 | 0.01 | 34 | 78,75,73,71,68,64 | 39 | 72,68,62,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5090 | 1185 | 5090 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,64 | 39 | 72,68,62,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5100 | 1185 | 5100 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,64 | 39 | 72,68,62,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5110 | 1185 | 5110 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,64 | 39 | 72,68,62,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5120 | 1185 | 5120 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,64 | 39 | 72,68,63,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5130 | 1185 | 5130 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,64 | 39 | 72,68,63,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5140 | 1185 | 5140 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,64 | 39 | 72,68,63,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5150 | 1185 | 5150 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,64 | 39 | 72,68,63,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5160 | 1185 | 5160 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,64 | 39 | 72,68,63,56,54,50 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5170 | 1185 | 5170 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,65 | 39 | 72,68,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5180 | 1185 | 5180 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,65 | 39 | 72,68,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5190 | 1185 | 5190 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,65 | 39 | 72,68,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5200 | 1185 | 5200 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,65 | 39 | 72,68,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5210 | 1185 | 5210 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,65 | 39 | 72,68,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5220 | 1185 | 5220 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,65 | 40 | 72,69,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5230 | 1185 | 5230 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,65 | 40 | 72,69,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5240 | 1185 | 5240 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,73,71,68,65 | 40 | 72,69,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5250 | 1185 | 5250 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,74,71,68,65 | 40 | 73,69,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5260 | 1185 | 5260 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,74,71,68,65 | 40 | 73,69,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5270 | 1185 | 5270 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,74,71,68,65 | 40 | 73,69,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5280 | 1185 | 5280 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,74,71,68,65 | 40 | 73,69,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5290 | 1185 | 5290 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,74,71,68,65 | 40 | 73,69,63,56,54,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5300 | 1185 | 5300 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,74,71,68,65 | 40 | 73,69,63,56,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5310 | 1185 | 5310 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,74,71,68,65 | 40 | 73,69,63,56,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5320 | 1185 | 5320 | 1 | 0.25 | 0.75 | 0.01 | 34 | 79,75,74,71,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5330 | 1185 | 5330 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,71,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5340 | 1185 | 5340 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,71,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5350 | 1185 | 5350 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,71,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5360 | 1185 | 5360 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,71,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5370 | 1185 | 5370 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,71,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5380 | 1185 | 5380 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,71,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5390 | 1185 | 5390 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,71,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5400 | 1185 | 5400 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5410 | 1185 | 5410 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5420 | 1185 | 5420 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5430 | 1185 | 5430 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5440 | 1185 | 5440 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5450 | 1185 | 5450 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,68,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5460 | 1185 | 5460 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,69,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5470 | 1185 | 5470 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,69,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5480 | 1185 | 5480 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,69,65 | 40 | 73,69,63,57,55,51 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5490 | 1185 | 5490 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,69,65 | 40 | 73,69,63,57,55,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5500 | 1185 | 5500 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,69,65 | 40 | 73,69,64,57,55,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5510 | 1185 | 5510 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,69,65 | 40 | 73,69,64,57,55,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5520 | 1185 | 5520 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,69,65 | 40 | 73,69,64,57,55,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5530 | 1185 | 5530 | 1 | 0.25 | 0.75 | 0.01 | 36 | 79,76,74,72,69,65 | 40 | 73,69,64,57,55,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5540 | 1185 | 5540 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 73,69,64,57,55,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5550 | 1185 | 5550 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 73,69,64,57,55,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5560 | 1185 | 5560 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 73,69,64,57,55,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5570 | 1185 | 5570 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 73,69,64,57,55,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5580 | 1185 | 5580 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 73,69,64,57,55,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5590 | 1185 | 5590 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 73,69,64,57,55,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5600 | 1185 | 5600 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 73,69,64,57,55,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5610 | 1185 | 5610 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 73,69,64,57,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5620 | 1185 | 5620 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 73,69,64,57,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5630 | 1185 | 5630 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 74,69,64,57,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5640 | 1185 | 5640 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 74,69,64,57,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5650 | 1185 | 5650 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 74,69,64,57,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5660 | 1185 | 5660 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 40 | 74,69,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5670 | 1185 | 5670 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5680 | 1185 | 5680 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5690 | 1185 | 5690 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,65 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5700 | 1185 | 5700 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5710 | 1185 | 5710 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5720 | 1185 | 5720 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,74,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5730 | 1185 | 5730 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,75,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5740 | 1185 | 5740 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,75,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5750 | 1185 | 5750 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,75,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5760 | 1185 | 5760 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,75,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5770 | 1185 | 5770 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,75,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5780 | 1185 | 5780 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,75,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5790 | 1185 | 5790 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,75,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5800 | 1185 | 5800 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,75,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5810 | 1185 | 5810 | 1 | 0.25 | 0.75 | 0.01 | 36 | 80,76,75,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5820 | 1185 | 5820 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5830 | 1185 | 5830 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,64,58,56,52 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5840 | 1185 | 5840 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,64,58,56,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5850 | 1185 | 5850 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,64,58,56,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5860 | 1185 | 5860 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,64,58,56,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5870 | 1185 | 5870 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,64,58,56,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5880 | 1185 | 5880 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,64,58,56,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5890 | 1185 | 5890 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,64,58,56,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5900 | 1185 | 5900 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,65,58,56,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5910 | 1185 | 5910 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,65,58,56,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5920 | 1185 | 5920 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,65,58,56,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5930 | 1185 | 5930 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,65,58,56,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5940 | 1185 | 5940 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,65,58,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5950 | 1185 | 5950 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,72,69,66 | 42 | 74,70,65,58,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5960 | 1185 | 5960 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,73,70,66 | 42 | 74,70,65,58,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5970 | 1185 | 5970 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,73,70,66 | 42 | 74,70,65,58,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5980 | 1185 | 5980 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,73,70,66 | 42 | 74,70,65,58,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 5990 | 1185 | 5990 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,73,70,66 | 42 | 74,70,65,58,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 5990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6000 | 1185 | 6000 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,73,70,66 | 42 | 74,70,65,58,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6010 | 1185 | 6010 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,73,70,66 | 42 | 74,70,65,58,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6020 | 1185 | 6020 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,73,70,66 | 42 | 74,70,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6030 | 1185 | 6030 | 1 | 0.25 | 0.75 | 0.01 | 37 | 80,77,75,73,70,66 | 42 | 74,70,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6040 | 1185 | 6040 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 42 | 75,70,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6050 | 1185 | 6050 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 42 | 75,70,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6060 | 1185 | 6060 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 42 | 75,70,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6070 | 1185 | 6070 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 42 | 75,70,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6080 | 1185 | 6080 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 42 | 75,70,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6090 | 1185 | 6090 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 42 | 75,70,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6100 | 1185 | 6100 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 42 | 75,70,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6110 | 1185 | 6110 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 42 | 75,70,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6120 | 1185 | 6120 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 42 | 75,70,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6130 | 1185 | 6130 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 42 | 75,70,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6140 | 1185 | 6140 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 43 | 75,71,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6150 | 1185 | 6150 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 43 | 75,71,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6160 | 1185 | 6160 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 43 | 75,71,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6170 | 1185 | 6170 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 43 | 75,71,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6180 | 1185 | 6180 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 43 | 75,71,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6190 | 1185 | 6190 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 43 | 75,71,65,59,57,53 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6200 | 1185 | 6200 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 43 | 75,71,65,59,57,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6210 | 1185 | 6210 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 43 | 75,71,65,59,57,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6220 | 1185 | 6220 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 43 | 75,71,65,59,57,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6230 | 1185 | 6230 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 43 | 75,71,65,59,57,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6240 | 1185 | 6240 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,75,73,70,66 | 43 | 75,71,65,59,57,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6250 | 1185 | 6250 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,76,73,70,66 | 43 | 75,71,65,59,57,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6260 | 1185 | 6260 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,76,73,70,66 | 43 | 75,71,65,59,57,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6270 | 1185 | 6270 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,76,73,70,66 | 43 | 75,71,65,59,57,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6280 | 1185 | 6280 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,76,73,70,67 | 43 | 75,71,65,59,57,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6290 | 1185 | 6290 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,76,73,70,67 | 43 | 75,71,65,59,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6300 | 1185 | 6300 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,76,73,70,67 | 43 | 75,71,65,59,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6310 | 1185 | 6310 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,76,73,70,67 | 43 | 75,71,65,59,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6320 | 1185 | 6320 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,76,73,70,67 | 43 | 75,71,65,59,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6330 | 1185 | 6330 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,76,73,70,67 | 43 | 75,71,65,59,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6340 | 1185 | 6340 | 1 | 0.25 | 0.75 | 0.01 | 37 | 81,77,76,73,70,67 | 43 | 75,71,66,59,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6350 | 1185 | 6350 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,59,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6360 | 1185 | 6360 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,59,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6370 | 1185 | 6370 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,59,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6380 | 1185 | 6380 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,59,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6390 | 1185 | 6390 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,59,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6400 | 1185 | 6400 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,59,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6410 | 1185 | 6410 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6420 | 1185 | 6420 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6430 | 1185 | 6430 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6440 | 1185 | 6440 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6450 | 1185 | 6450 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6460 | 1185 | 6460 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6470 | 1185 | 6470 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 75,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6480 | 1185 | 6480 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 76,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6490 | 1185 | 6490 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 76,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6500 | 1185 | 6500 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,70,67 | 43 | 76,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6510 | 1185 | 6510 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,71,67 | 43 | 76,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6520 | 1185 | 6520 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,71,67 | 43 | 76,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6530 | 1185 | 6530 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,71,67 | 43 | 76,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6540 | 1185 | 6540 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,71,67 | 43 | 76,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6550 | 1185 | 6550 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,71,67 | 43 | 76,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6560 | 1185 | 6560 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,71,67 | 43 | 76,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6570 | 1185 | 6570 | 1 | 0.25 | 0.75 | 0.01 | 38 | 81,78,76,73,71,67 | 43 | 76,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6580 | 1185 | 6580 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 43 | 76,71,66,60,58,54 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6590 | 1185 | 6590 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 43 | 76,71,66,60,58,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6600 | 1185 | 6600 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 43 | 76,71,66,60,58,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6610 | 1185 | 6610 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 43 | 76,71,66,60,58,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6620 | 1185 | 6620 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 43 | 76,71,66,60,58,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6630 | 1185 | 6630 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 43 | 76,71,66,60,58,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6640 | 1185 | 6640 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 43 | 76,71,66,60,58,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6650 | 1185 | 6650 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 43 | 76,71,66,60,58,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6660 | 1185 | 6660 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6670 | 1185 | 6670 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6680 | 1185 | 6680 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6690 | 1185 | 6690 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6700 | 1185 | 6700 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6710 | 1185 | 6710 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6720 | 1185 | 6720 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6730 | 1185 | 6730 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6740 | 1185 | 6740 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6750 | 1185 | 6750 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6760 | 1185 | 6760 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6770 | 1185 | 6770 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6780 | 1185 | 6780 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6790 | 1185 | 6790 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6800 | 1185 | 6800 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,76,74,71,67 | 44 | 76,72,66,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6810 | 1185 | 6810 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,67 | 44 | 76,72,67,60,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6820 | 1185 | 6820 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,67 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6830 | 1185 | 6830 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,67 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6840 | 1185 | 6840 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,67 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6850 | 1185 | 6850 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,67 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6860 | 1185 | 6860 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,67 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6870 | 1185 | 6870 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,67 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6880 | 1185 | 6880 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,67 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6890 | 1185 | 6890 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,67 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6900 | 1185 | 6900 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,67 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6910 | 1185 | 6910 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,67 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6920 | 1185 | 6920 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,68 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6930 | 1185 | 6930 | 1 | 0.25 | 0.75 | 0.01 | 38 | 82,78,77,74,71,68 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6940 | 1185 | 6940 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 76,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6950 | 1185 | 6950 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6960 | 1185 | 6960 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6970 | 1185 | 6970 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6980 | 1185 | 6980 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 6990 | 1185 | 6990 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 6990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7000 | 1185 | 7000 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,59,55 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7010 | 1185 | 7010 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,59,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7020 | 1185 | 7020 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,59,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7030 | 1185 | 7030 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,59,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7040 | 1185 | 7040 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,59,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7050 | 1185 | 7050 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7060 | 1185 | 7060 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7070 | 1185 | 7070 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7080 | 1185 | 7080 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7090 | 1185 | 7090 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7100 | 1185 | 7100 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,71,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7110 | 1185 | 7110 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,72,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7120 | 1185 | 7120 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,72,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7130 | 1185 | 7130 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,72,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7140 | 1185 | 7140 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,72,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7150 | 1185 | 7150 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,72,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7160 | 1185 | 7160 | 1 | 0.25 | 0.75 | 0.01 | 39 | 82,79,77,74,72,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7170 | 1185 | 7170 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,74,72,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7180 | 1185 | 7180 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,74,72,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7190 | 1185 | 7190 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,74,72,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7200 | 1185 | 7200 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,74,72,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7210 | 1185 | 7210 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,74,72,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7220 | 1185 | 7220 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,74,72,68 | 44 | 77,72,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7230 | 1185 | 7230 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,74,72,68 | 45 | 77,73,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7240 | 1185 | 7240 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,74,72,68 | 45 | 77,73,67,61,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7250 | 1185 | 7250 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,74,72,68 | 45 | 77,73,67,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7260 | 1185 | 7260 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,74,72,68 | 45 | 77,73,67,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7270 | 1185 | 7270 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,67,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7280 | 1185 | 7280 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,67,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7290 | 1185 | 7290 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,67,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7300 | 1185 | 7300 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,67,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7310 | 1185 | 7310 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,67,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7320 | 1185 | 7320 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7330 | 1185 | 7330 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7340 | 1185 | 7340 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7350 | 1185 | 7350 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7360 | 1185 | 7360 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7370 | 1185 | 7370 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7380 | 1185 | 7380 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7390 | 1185 | 7390 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7400 | 1185 | 7400 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7410 | 1185 | 7410 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7410 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7420 | 1185 | 7420 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,77,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7420 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7430 | 1185 | 7430 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7430 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7440 | 1185 | 7440 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 77,73,68,62,60,56 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7440 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7450 | 1185 | 7450 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 78,73,68,62,60,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7450 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7460 | 1185 | 7460 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7460 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7470 | 1185 | 7470 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7470 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7480 | 1185 | 7480 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7480 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7490 | 1185 | 7490 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7490 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7500 | 1185 | 7500 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7500 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7510 | 1185 | 7510 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7510 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7520 | 1185 | 7520 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7520 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7530 | 1185 | 7530 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7530 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7540 | 1185 | 7540 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7540 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7550 | 1185 | 7550 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7550 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7560 | 1185 | 7560 | 1 | 0.25 | 0.75 | 0.01 | 39 | 83,79,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7560 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7570 | 1185 | 7570 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7570 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7580 | 1185 | 7580 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7580 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7590 | 1185 | 7590 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7590 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7600 | 1185 | 7600 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7600 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7610 | 1185 | 7610 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7610 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7620 | 1185 | 7620 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,68 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7620 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7630 | 1185 | 7630 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7630 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7640 | 1185 | 7640 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7640 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7650 | 1185 | 7650 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7650 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7660 | 1185 | 7660 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7660 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7670 | 1185 | 7670 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7670 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7680 | 1185 | 7680 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7680 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7690 | 1185 | 7690 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7690 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7700 | 1185 | 7700 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7700 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7710 | 1185 | 7710 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,62,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7710 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7720 | 1185 | 7720 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7720 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7730 | 1185 | 7730 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7730 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7740 | 1185 | 7740 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7740 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7750 | 1185 | 7750 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7750 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7760 | 1185 | 7760 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,72,69 | 45 | 78,73,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7760 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7770 | 1185 | 7770 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,73,69 | 45 | 78,73,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7770 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7780 | 1185 | 7780 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,73,69 | 45 | 78,73,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7780 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7790 | 1185 | 7790 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,73,69 | 45 | 78,73,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7790 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7800 | 1185 | 7800 | 1 | 0.25 | 0.75 | 0.01 | 40 | 83,80,78,75,73,69 | 45 | 78,73,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7800 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7810 | 1185 | 7810 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 45 | 78,73,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7810 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7820 | 1185 | 7820 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 45 | 78,73,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7820 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7830 | 1185 | 7830 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 45 | 78,73,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7830 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7840 | 1185 | 7840 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7840 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7850 | 1185 | 7850 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,68,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7850 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7860 | 1185 | 7860 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7860 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7870 | 1185 | 7870 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7870 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7880 | 1185 | 7880 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7880 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7890 | 1185 | 7890 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,61,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7890 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7900 | 1185 | 7900 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,62,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7900 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7910 | 1185 | 7910 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,62,57 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7910 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7920 | 1185 | 7920 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7920 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7930 | 1185 | 7930 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7930 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7940 | 1185 | 7940 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7940 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7950 | 1185 | 7950 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7950 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7960 | 1185 | 7960 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7960 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7970 | 1185 | 7970 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7970 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7980 | 1185 | 7980 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7980 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 7990 | 1185 | 7990 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 46 | 78,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 7990 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8000 | 1185 | 8000 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8000 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8010 | 1185 | 8010 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,75,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8010 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8020 | 1185 | 8020 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8020 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8030 | 1185 | 8030 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8030 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8040 | 1185 | 8040 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8040 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8050 | 1185 | 8050 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8050 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8060 | 1185 | 8060 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8060 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8070 | 1185 | 8070 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8070 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8080 | 1185 | 8080 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8080 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8090 | 1185 | 8090 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8090 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8100 | 1185 | 8100 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,78,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8100 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8110 | 1185 | 8110 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8110 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8120 | 1185 | 8120 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8120 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8130 | 1185 | 8130 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8130 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8140 | 1185 | 8140 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8140 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8150 | 1185 | 8150 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8150 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8160 | 1185 | 8160 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8160 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8170 | 1185 | 8170 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8170 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8180 | 1185 | 8180 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8180 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8190 | 1185 | 8190 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8190 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8200 | 1185 | 8200 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,63,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8200 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8210 | 1185 | 8210 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8210 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8220 | 1185 | 8220 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8220 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8230 | 1185 | 8230 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8230 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8240 | 1185 | 8240 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8240 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8250 | 1185 | 8250 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8250 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8260 | 1185 | 8260 | 1 | 0.25 | 0.75 | 0.01 | 40 | 84,80,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8260 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8270 | 1185 | 8270 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8270 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8280 | 1185 | 8280 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8280 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8290 | 1185 | 8290 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8290 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8300 | 1185 | 8300 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8300 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8310 | 1185 | 8310 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8310 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8320 | 1185 | 8320 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8320 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8330 | 1185 | 8330 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8330 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8340 | 1185 | 8340 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8340 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8350 | 1185 | 8350 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,62,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8350 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8360 | 1185 | 8360 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,63,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8360 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8370 | 1185 | 8370 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,63,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8370 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8380 | 1185 | 8380 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,63,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8380 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8390 | 1185 | 8390 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,63,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8390 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV
PRICE | SDV | 24x16 | 8400 | 1185 | 8400 | 1 | 0.25 | 0.75 | 0.01 | 42 | 84,81,79,76,73,69 | 47 | 79,74,69,64,63,58 | 55 | 75 | 0.5" Fiber Free Foam | 24x16 | 8400 | 0.5" Fiber Free Foam | [6 empty] | PERFORMANCE DATA - PRICE SDV |  |  | IM - PRICE SDV