## SCHEDULE
SCHEDULE RANGE | [11 empty] | FILTERS | DOCUMENTATION
AIR IONIZATION DEVICE SCHEDULE - SELF-CLEANING - IN ROOM CEILING MOUNTED FAN | [11 empty] | LOCATION | SUBMITTAL (OUTDOOR UNIT) | SUBMITTAL (INDOOR UNIT) | SUBMITTAL (SYSTEM) | ENGINEERING MANUAL (SYSTEM) | ENGINEERING MANUAL (OUTDOOR UNIT) | ENGINEERING MANUAL (INDOOR UNIT) | CAPACITY TABLE | INSTALLATION MANUAL (OUTDOOR) | INSTALLATION MANUAL (INDOOR) | INSTALLATION MANUAL (SYSTEM) | REVIT (OUTDOOR) | REVIT (INDOOR) | REVIT (SYSTEM) | CAD (OUTDOOR) | CAD (INDOOR) | CAD (SYSTEM) | CONTROLS OPTIONS | OPERATION MANUAL
ZONE TAG | TYPE | GPS MODEL | GPS QUANTITY | COVERAGE | VOLTAGE (AC) | CLEAN/OP WATTS | SOUND LEVEL, MAX (dBA) | NOISE CRITERION LEVEL (NC) | MIN ION DENSITY, DEVICE (IONS/CC) | AVG ION DENSITY, COVERAGE AREA (IONS/CC) | NOTES
| Ceiling Mounted | IDF-2 | 1 | 1,500 SQFT | 120-240 | 15 / 12 | 39 | 34 | 160 Million | 20000 | 1 to 9 | CEILING MOUNTED FAN |  |  | IDF-2 | [6 empty] | IOM - IDF-2
NOTES:
1. Install Ionizations device(s) whereindicated on drawings.
2. Basis of Design: GPS Air. Substitutions must be approved by engineer, any mechanical or electrical modifications are the responsibility of the contractor.
3. Ionizer has a self-cleaning feature to maintain ion output over 10 years, substitute products must document ionization output over time.
4. Electronic air cleaners shall not have service parts, products that require replacement parts like glass tubes, UV lamps, catalysts, etc. are not acceptable.
5. Must be listed to UL-2998 by either UL or ETL. Listing on UL and ETL website must include specific product family.
6. Safety Tested by 3rd party laboratory to UL2998 Zero Ozone (ASHRAE Standard 241 Appendix A).
7. Formaldehyde generation validated by 3rd party to ASTM D8407 emission rate less than 5μg/h (micro grams per hour) (ASHRAE Standard 241 Appendix A).
8. Particle Generation validated by ISO14644 - results shall not exceed one cleanliness class greater than the empty chamber (ASHRAE Standard 241 Appendix A).
9. Ion output is measured in ions per cubic centimeter (ions/cc) are verifiable with field instruments. Devices with ratings of ions/second are not acceptable.
-- optional specifications --
10. Powered by 277V, single phase, 60Hz via remote power supply.
11. Powered by 347V, single phase, 60Hz via remote power supply.
AIR IONIZATION DEVICE SCHEDULE - SELF-CLEANING - DUCT MOUNTED
ZONE TAG | FLOW | MAX FLOW (CFM) | O/A FLOW (CFM) | GPS MODEL | GPS QUANTITY | PRESSURE DROP | VOLTAGE (AC) | CLEAN/OP WATTS | MOUNTING LOCATION | MIN ION DENSITY (IONS/CC) | NOTES
| VAV | 4800 | 150 | GPS-DM48-AC | 1 | 0.05" W.C. | 24-240 | 12 | Duct | 400 Million | 1 to 10, 12 | DUCT MOUNTED |  |  | DM48 | [6 empty] | IOM - DM48
| VAV | 2400 | 150 | DM-2 | 1 | 0.05" W.C. | 24-240 | 14 / 11 | Duct | 200 Million | 1 to 10, 11, 13 | DUCT MOUNTED |  |  | DM-2 | [6 empty] | IOM - DM-2
| CV | 4800 | 150 | GPS-DM48-AC | 1 | 0.05" W.C. | 24-240 | 12 | Duct | 400 Million | 1 to 10, 12 | DUCT MOUNTED |  |  | DM48 | [6 empty] | IOM - DM48
| CV | 2400 | 150 | DM-2 | 1 | 0.05" W.C. | 24-240 | 14 / 11 | Duct | 200 Million | 1 to 10, 11, 13 | DUCT MOUNTED |  |  | DM-2 | [6 empty] | IOM - DM-2
NOTES:
1. Install Ionizations device(s) where indicated on drawings.
2. Basis of Design: GPS Air. Substitutions must be approved by engineer, any mechanical or electrical modifications are the responsibility of the contractor.
3. Ionizer has a self-cleaning feature to maintain ion output over 10 years, substitute products must document ionization output over time.
4. Electronic air cleaners shall not have service parts, products that require replacement parts like glass tubes, UV lamps, catalysts, etc. are not acceptable.
5. Must be listed to UL-2998 by either UL or ETL. Listing on UL and ETL website must include specific product family.
6. Safety Tested by 3rd party laboratory to UL2998 Zero Ozone (ASHRAE Standard 241 Appendix A).
7. Formaldehyde generation validated by 3rd party to ASTM D8407 emission rate less than 5μg/h (micro grams per hour) (ASHRAE Standard 241 Appendix A).
8. Particle Generation validated by ISO14644 - results shall not exceed one cleanliness class greater than the empty chamber (ASHRAE Standard 241 Appendix A).
9. Ion output is measured in ions per cubic centimeter (ions/cc) are verifiable with field instruments. Devices with ratings of ions/second are not acceptable.
10. Provide integral BAS alarm contacts within the air cleaner.
11. Powered by 277V, single phase, 60Hz via remote power supply (DM-2 only.)
12. Must be NEMA-3R rated for outdoor application or provide suitable enclosure (GPS-DM48-AC only)
13. For round duct mounting: use duct mounting saddle accessory without hardware fasteners into ductwork. (DM-2 only.)
AIR IONIZATION DEVICE SCHEDULE - SELF-CLEANING - FAN COIL MOUNTED
ZONE TAG | FLOW | MAX FLOW (CFM) | O/A FLOW (CFM) | GPS MODEL | GPS QUANTITY | PRESSURE DROP | VOLTAGE (AC) | CLEAN/OP WATTS | MOUNTING LOCATION | ION DENSITY (IONS/CC) | NOTES
| VAV | 4800 | 150 | GPS-FC48-AC | 1 | 0.05" W.C. | 24-240 | 10 | AHU, RTU & FCU | 400 Million | 1 to 10 | FAN COIL MOUNTED |  |  | FC48 | [6 empty] | IOM - FC48
| VAV | 2400 | 150 | GPS-FC24-AC | 1 | 0.05" W.C. | 24-240 | 8 | AHU, RTU & FCU | 300 Million | 1 to 10 | FAN COIL MOUNTED |  |  | FC48 | [6 empty] | IOM - FC48
| VAV | 2400 | 150 | CI-2 | 1 | 0.05" W.C. | 24 | 7.0 / 4.0 | AHU, RTU & FCU | 160 Million | 1 to 10, 11 | FAN COIL MOUNTED |  |  | CI-2 | [6 empty] | IOM - CI-2
| CV | 4800 | 150 | GPS-FC48-AC | 1 | 0.05" W.C. | 24-240 | 10 | AHU, RTU & FCU | 400 Million | 1 to 10 | FAN COIL MOUNTED |  |  | FC48 | [6 empty] | IOM - FC48
| CV | 2400 | 150 | GPS-FC24-AC | 1 | 0.05" W.C. | 24-240 | 8 | AHU, RTU & FCU | 300 Million | 1 to 10 | FAN COIL MOUNTED |  |  | FC48 | [6 empty] | IOM - FC48
| CV | 2400 | 150 | CI-2 | 1 | 0.05" W.C. | 24 | 7.0 / 4.0 | AHU, RTU & FCU | 160 Million | 1 to 10, 11 | FAN COIL MOUNTED |  |  | CI-2 | [6 empty] | IOM - CI-2
NOTES:
1. Install Ionizations device(s) where indicated on drawings.
2. Basis of Design: GPS Air. Substitutions must be approved by engineer, any mechanical or electrical modifications are the responsibility of the contractor.
3. Ionizer has a self-cleaning feature to maintain ion output over 10 years, substitute products must document ionization output over time.
4. Electronic air cleaners shall not have service parts, products that require replacement parts like glass tubes, UV lamps, catalysts, etc. are not acceptable.
5. Must be listed to UL-2998 by either UL or ETL. Listing on UL and ETL website must include specific product family.
6. Safety Tested by 3rd party laboratory to UL2998 Zero Ozone (ASHRAE Standard 241 Appendix A).
7. Formaldehyde generation validated by 3rd party to ASTM D8407 emission rate less than 5μg/h (micro grams per hour) (ASHRAE Standard 241 Appendix A).
8. Particle Generation validated by ISO14644 - results shall not exceed one cleanliness class greater than the empty chamber (ASHRAE Standard 241 Appendix A).
9. Ion output is measured in ions per cubic centimeter (ions/cc) are verifiable with field instruments. Devices with ratings of ions/second are not acceptable.
10. Provide integral BAS alarm contacts within the air cleaner.
11. Powered by 110-277V, single phase, 60Hz via remote power supply (CI-2 only.)
AIR IONIZATION DEVICE SCHEDULE - FAN COIL MOUNTED
ZONE TAG | FLOW | MAX FLOW | O/A FLOW | GPS MODEL | GPS QUANTITY | PRESSURE DROP | VOLTAGE (AC) | WATTS | MOUNTING LOCATION | ION DENSITY (IONS/CC) | NOTES
| VAV | 3000 | 150 | GPS-FC-3-BAS | 1 | 0.05" W.C. | 24 | 1.2 | FCU | 350 Million | 1 to 6 | FAN COIL MOUNTED |  |  | FC-3-BAS | [6 empty] | IOM - FC-3-BAS
| VAV | 3000 | 150 | GPS-FC-3T-BAS | 1 | 0.05" W.C. | 110-240 | 1.2 | FCU | 350 Million | 1 to 6, 7 | FAN COIL MOUNTED |  |  | FC-3-BAS | [6 empty] | IOM - FC-3T-BAS
| CV | 3000 | 150 | GPS-FC-3-BAS | 1 | 0.05" W.C. | 24 | 1.2 | FCU | 350 Million | 1 to 6 | FAN COIL MOUNTED |  |  | FC-3-BAS | [6 empty] | IOM - FC-3-BAS
| CV | 3000 | 150 | GPS-FC-3T-BAS | 1 | 0.05" W.C. | 110-240 | 1.2 | FCU | 350 Million | 1 to 6, 7 | FAN COIL MOUNTED |  |  | FC-3-BAS | [6 empty] | IOM - FC-3T-BAS
NOTES:
1. Install Ionizations device(s) where indicated on drawings.
2. Basis of Design: GPS Air. Substitutions must be approved by engineer, any mechanical or electrical modifications are the responsibility of the contractor.
3. Ionizer has a self-cleaning feature to maintain ion output over 10 years, substitute products must document ionization output over time.
4. Electronic air cleaners shall not have service parts, products that require replacement parts like glass tubes, UV lamps, catalysts, etc. are not acceptable.
5. Must be listed to UL-2998 by either UL or ETL. Listing on UL and ETL website must include specific product family.
6. Provide integral BAS alarm contacts within the air cleaner.
7. Powered by 110-230V, single phase, 60Hz via remote power supply
AIR IONIZATION DEVICE SCHEDULE - MODULAR COIL CLEANING
ZONE TAG | FLOW | MAX FLOW | O/A FLOW | GPS MODEL | GPS QUANTITY | ION EMITTERS | VOLTAGE (AC) | WATTS | MOUNTING LOCATION | ION DENSITY (IONS/CC) | NOTES
| VAV | 10000 | 150 | GPS-iMOD | 1 Per Cooling Coil | 1 every 1/2 inch | 24-240 | 15 | AHU | 140 Million per 1.0" | 1 to 14, 15, 16, 17 | COIL MOUNTED |  |  | IMOD | [6 empty] | IOM - IMOD
| CV | 10000 | 150 | GPS-iMOD | 1 Per Cooling Coil | 1 every 1/2 inch | 24-240 | 15 | AHU | 140 Million per 1.0" | 1 to 14, 15, 16, 17 | COIL MOUNTED |  |  | IMOD | [6 empty] | IOM - IMOD
NOTES:
1. Install Ionizations device(s) where indicated on drawings.
2. Basis of Design: GPS Air. Substitutions must be approved by engineer, any mechanical or electrical modifications are the responsibility of the contractor.
3. Ionizer has a self-cleaning feature to maintain ion output over 10 years, substitute products must document ionization output over time.
4. Electronic air cleaners shall not have service parts, products that require replacement parts like glass tubes, UV lamps, catalysts, etc. are not acceptable.
5. Must be listed to UL-2998 by either UL or ETL. Listing on UL and ETL website must include specific product family.
6. Safety Tested by 3rd party laboratory to UL2998 Zero Ozone (ASHRAE Standard 241 Appendix A).
7. Mount GPS-iMOD to air inlet side of cooling coil between 1/8" and 1/2" from grounded coil surface.
8. Provide with integral BAS alarm contacts.
9. Ionization bar to have a minimum of 1 needlepoint every 0.50" of coil width. Systems with needles further apart shall not be acceptable (or shall require additional bars).
10. Ionization systems with multiple ion modules mounted to a bar shall not be an acceptable substitute.
11. Ionization output shall be a minimum of 70 million ions/cc for every 0.50" of coil width.
12. Ionization power supply shall have power on and plasma on indication light.
13. Ionization bars shall be provided with magnets for ease of mounting.
14. Ionization bars shall be modular and designed to cover the entire coil width in 6 inch increments.
15. Provide stand-alone ion field detector to communicate with the BAS. (GPS-iDETECT-P Accessory)
16. Must provide NEMA-4X rated enclosure for outdoor application.
17. HCAI Seismic Compliance: Must be certified to HCAI Seismic Compliance standards.
AIR IONIZATION DEVICE SCHEDULE - SPECIALIZED RIBBON
ZONE TAG | FLOW | MAX FLOW | O/A FLOW (cfm) | GPS MODEL | GPS QUANTITY | ION EMITTERS | VOLTAGE (AC) | WATTS | MOUNTING LOCATION | ION DENSITY (IONS/CC) | NOTES
| VAV | 1600 | 10 | GPS-iRIB-18 | 1 Per Cooling Coil | 1 every 2 inches | 110-240 | 5 | AHU | 52.5 Million | 1 to 12 | COIL MOUNTED (DUCTLESS OR PTAC) |  |  | IRIB-18 | [6 empty] | IOM - IRIB-18
| CV | 1600 | 10 | GPS-iRIB-18 | 1 Per Cooling Coil | 1 every 2 inches | 110-240 | 5 | AHU | 52.5 Million | 1 to 12 | COIL MOUNTED (DUCTLESS OR PTAC) |  |  | IRIB-18 | [6 empty] | IOM - IRIB-18
NOTES:
1. Install Ionizations device(s) where indicated on drawings.
2. Basis of Design: GPS Air. Substitutions must be approved by engineer, any mechanical or electrical modifications are the responsibility of the contractor.
3. Ionizer has a self-cleaning feature to maintain ion output over 10 years, substitute products must document ionization output over time.
4. Electronic air cleaners shall not have service parts, products that require replacement parts like glass tubes, UV lamps, catalysts, etc. are not acceptable.
5. Must be listed to UL-2998 by either UL or ETL. Listing on UL and ETL website must include specific product family.
6. Safety Tested by 3rd party laboratory to UL2998 Zero Ozone (ASHRAE Standard 241 Appendix A).
7. Formaldehyde generation validated by 3rd party to ASTM D8407 emission rate less than 5μg/h (micro grams per hour) (ASHRAE Standard 241 Appendix A).
8. Particle Generation validated by ISO14644 - results shall not exceed one cleanliness class greater than the empty chamber (ASHRAE Standard 241 Appendix A).
9. Ion output is measured in ions per cubic centimeter (ions/cc) are verifiable with field instruments. Devices with ratings of ions/second are not acceptable.
10. Provide integral BAS alarm contacts within the air cleaner.
11. Mount GPS-iRIB to top of cooling coil on air inlet side.
12. Provide flexible ion ribbon with self-sealing adhesive back.
Filter Enhancement System Device Schedule
ZONE TAG | FLOW | MAX FLOW | O/A FLOW | GPS MODEL | GPS QUANTITY | PRESSURE DROP | VOLTAGE (AC) | WATTS | MOUNTING LOCATION | NOTES
| VAV | 3800 | 0-100 | PF-e | 1 | 0.05" W.C. | 24-240 | 11 | pre-filter | 1 to 9 |  | PRE-FILTER |  |  | PF-E | [6 empty] | IOM - PF-E
| VAV | 3800 | 0-100 | PF-i | 1 | 0.05" W.C. | 24-240 | 11 | pre-filter | 1 to 9 |  | PRE-FILTER |  |  | PF-I | [6 empty] | IOM - PF-I
| CV | 3800 | 0-100 | PF-e | 1 | 0.05" W.C. | 24-240 | 11 | pre-filter | 1 to 9 |  | PRE-FILTER |  |  | PF-E | [6 empty] | IOM - PF-E
| CV | 3800 | 0-100 | PF-i | 1 | 0.05" W.C. | 24-240 | 11 | pre-filter | 1 to 9 |  | PRE-FILTER |  |  | PF-I | [6 empty] | IOM - PF-I
NOTES:
1. Install Ionizations device(s) where indicated on drawings.
2. Basis of Design: GPS Air. Substitutions must be approved by engineer, any mechanical or electrical modifications are the responsibility of the contractor.
3. Ionizer has a self-cleaning feature to maintain ion output over 10 years, substitute products must document ionization output over time.
4. Electronic filter enahncement systems shall not have service parts, products that require replacement parts like glass tubes, UV lamps, catalysts, etc. are not acceptable.
5. Must be listed to UL-2998 by either UL or ETL. Listing on UL and ETL website must include specific product family.
6. Provide with integral BAS alarm contacts.
7. Mount GPS-Opti Lok 3 feet before the filter.
8. Ion output is measured in ions per cubic centimeter (ions/cc) are verifiable with field instruments. Devices with ratings of ions/second are not acceptable.
9. Provide integral BAS alarm contacts within the air cleaner.