## Cooling
Model | Tons | CFM | EAT DB (°F) | EAT WB (°F) | OA DB (°F) | MBh | S/T | ∆T (°F)
DSG036*D | 3 | 900 | 70 | 59 | 65 | 35.1 | 0.56 | 19.8
DSG036*D | 3 | 900 | 70 | 63 | 65 | 35.6 | 0.5 | 18.06
DSG036*D | 3 | 900 | 70 | 67 | 65 | 36.7 | 0.4 | 14.82
DSG036*D | 3 | 900 | 70 | 59 | 75 | 34.8 | 0.56 | 19.75
DSG036*D | 3 | 900 | 70 | 63 | 75 | 35.3 | 0.51 | 18.02
DSG036*D | 3 | 900 | 70 | 67 | 75 | 36.4 | 0.4 | 14.77
DSG036*D | 3 | 900 | 70 | 59 | 85 | 33.9 | 0.58 | 20
DSG036*D | 3 | 900 | 70 | 63 | 85 | 34.4 | 0.53 | 18.26
DSG036*D | 3 | 900 | 70 | 67 | 85 | 35.4 | 0.42 | 15.02
DSG036*D | 3 | 900 | 70 | 59 | 95 | 32.3 | 0.61 | 19.73
DSG036*D | 3 | 900 | 70 | 63 | 95 | 32.8 | 0.54 | 18
DSG036*D | 3 | 900 | 70 | 67 | 95 | 33.8 | 0.43 | 14.75
DSG036*D | 3 | 900 | 70 | 59 | 105 | 30.3 | 0.64 | 19.5
DSG036*D | 3 | 900 | 70 | 63 | 105 | 30.8 | 0.57 | 17.77
DSG036*D | 3 | 900 | 70 | 67 | 105 | 31.9 | 0.45 | 14.52
DSG036*D | 3 | 900 | 70 | 59 | 115 | 28.5 | 0.71 | 20.59
DSG036*D | 3 | 900 | 70 | 63 | 115 | 29 | 0.64 | 18.85
DSG036*D | 3 | 900 | 70 | 67 | 115 | 30.1 | 0.51 | 15.61
DSG036*D | 3 | 900 | 75 | 59 | 65 | 35.3 | 0.66 | 23.62
DSG036*D | 3 | 900 | 75 | 63 | 65 | 35.8 | 0.6 | 21.88
DSG036*D | 3 | 900 | 75 | 67 | 65 | 36.9 | 0.5 | 18.64
DSG036*D | 3 | 900 | 75 | 71 | 65 | 38.5 | 0.4 | 15.3
DSG036*D | 3 | 900 | 75 | 59 | 75 | 35 | 0.67 | 23.57
DSG036*D | 3 | 900 | 75 | 63 | 75 | 35.5 | 0.61 | 21.83
DSG036*D | 3 | 900 | 75 | 67 | 75 | 36.6 | 0.5 | 18.59
DSG036*D | 3 | 900 | 75 | 71 | 75 | 38.2 | 0.4 | 15.2
DSG036*D | 3 | 900 | 75 | 59 | 85 | 34.1 | 0.69 | 23.82
DSG036*D | 3 | 900 | 75 | 63 | 85 | 34.6 | 0.63 | 22.08
DSG036*D | 3 | 900 | 75 | 67 | 85 | 35.6 | 0.52 | 18.84
DSG036*D | 3 | 900 | 75 | 71 | 85 | 37.3 | 0.4 | 15.5
DSG036*D | 3 | 900 | 75 | 59 | 95 | 32.5 | 0.72 | 23.55
DSG036*D | 3 | 900 | 75 | 63 | 95 | 33 | 0.66 | 21.82
DSG036*D | 3 | 900 | 75 | 67 | 95 | 34 | 0.54 | 18.57
DSG036*D | 3 | 900 | 75 | 71 | 95 | 35.7 | 0.4 | 15.2
DSG036*D | 3 | 900 | 75 | 59 | 105 | 30.5 | 0.76 | 23.32
DSG036*D | 3 | 900 | 75 | 63 | 105 | 31 | 0.69 | 21.58
DSG036*D | 3 | 900 | 75 | 67 | 105 | 32.1 | 0.57 | 18.34
DSG036*D | 3 | 900 | 75 | 71 | 105 | 33.7 | 0.4 | 15
DSG036*D | 3 | 900 | 75 | 59 | 115 | 28.7 | 0.84 | 24.41
DSG036*D | 3 | 900 | 75 | 63 | 115 | 29.2 | 0.77 | 22.67
DSG036*D | 3 | 900 | 75 | 67 | 115 | 30.3 | 0.64 | 19.43
DSG036*D | 3 | 900 | 75 | 71 | 115 | 31.9 | 0.5 | 16.1
DSG036*D | 3 | 900 | 80 | 59 | 65 | 35.5 | 0.77 | 27.46
DSG036*D | 3 | 900 | 80 | 63 | 65 | 36 | 0.71 | 25.73
DSG036*D | 3 | 900 | 80 | 67 | 65 | 37.1 | 0.6 | 22.48
DSG036*D | 3 | 900 | 80 | 71 | 65 | 38.7 | 0.5 | 19.1
DSG036*D | 3 | 900 | 80 | 59 | 75 | 35.2 | 0.77 | 27.42
DSG036*D | 3 | 900 | 80 | 63 | 75 | 35.7 | 0.71 | 25.68
DSG036*D | 3 | 900 | 80 | 67 | 75 | 36.7 | 0.6 | 22.44
DSG036*D | 3 | 900 | 80 | 71 | 75 | 38.4 | 0.5 | 19.1
DSG036*D | 3 | 900 | 80 | 59 | 85 | 34.2 | 0.8 | 27.66
DSG036*D | 3 | 900 | 80 | 63 | 85 | 34.7 | 0.74 | 25.92
DSG036*D | 3 | 900 | 80 | 67 | 85 | 35.8 | 0.63 | 22.68
DSG036*D | 3 | 900 | 80 | 71 | 85 | 37.4 | 0.5 | 19.3
DSG036*D | 3 | 900 | 80 | 59 | 95 | 32.6 | 0.83 | 27.4
DSG036*D | 3 | 900 | 80 | 63 | 95 | 33.1 | 0.77 | 25.66
DSG036*D | 3 | 900 | 80 | 67 | 95 | 34.2 | 0.65 | 22.42
DSG036*D | 3 | 900 | 80 | 71 | 95 | 35.8 | 0.5 | 19.1
DSG036*D | 3 | 900 | 80 | 59 | 105 | 30.7 | 0.88 | 27.17
DSG036*D | 3 | 900 | 80 | 63 | 105 | 31.2 | 0.81 | 25.43
DSG036*D | 3 | 900 | 80 | 67 | 105 | 32.3 | 0.68 | 22.19
DSG036*D | 3 | 900 | 80 | 71 | 105 | 33.9 | 0.6 | 18.8
DSG036*D | 3 | 900 | 80 | 59 | 115 | 28.9 | 0.97 | 28.25
DSG036*D | 3 | 900 | 80 | 63 | 115 | 29.4 | 0.89 | 26.52
DSG036*D | 3 | 900 | 80 | 67 | 115 | 30.5 | 0.76 | 23.27
DSG036*D | 3 | 900 | 80 | 71 | 115 | 32.1 | 0.6 | 19.9
DSG036*D | 3 | 900 | 85 | 59 | 65 | 36.1 | 0.85 | 30.87
DSG036*D | 3 | 900 | 85 | 63 | 65 | 36.6 | 0.79 | 29.14
DSG036*D | 3 | 900 | 85 | 67 | 65 | 37.7 | 0.68 | 25.89
DSG036*D | 3 | 900 | 85 | 71 | 65 | 39.3 | 0.6 | 22.5
DSG036*D | 3 | 900 | 85 | 59 | 75 | 35.8 | 0.85 | 30.83
DSG036*D | 3 | 900 | 85 | 63 | 75 | 36.3 | 0.79 | 29.09
DSG036*D | 3 | 900 | 85 | 67 | 75 | 37.3 | 0.69 | 25.85
DSG036*D | 3 | 900 | 85 | 71 | 75 | 39 | 0.6 | 22.5
DSG036*D | 3 | 900 | 85 | 59 | 85 | 34.8 | 0.88 | 31.07
DSG036*D | 3 | 900 | 85 | 63 | 85 | 35.3 | 0.82 | 29.33
DSG036*D | 3 | 900 | 85 | 67 | 85 | 36.4 | 0.71 | 26.09
DSG036*D | 3 | 900 | 85 | 71 | 85 | 38 | 0.6 | 22.7
DSG036*D | 3 | 900 | 85 | 59 | 95 | 33.2 | 0.92 | 30.81
DSG036*D | 3 | 900 | 85 | 63 | 95 | 33.7 | 0.85 | 29.07
DSG036*D | 3 | 900 | 85 | 67 | 95 | 34.8 | 0.73 | 25.83
DSG036*D | 3 | 900 | 85 | 71 | 95 | 36.4 | 0.6 | 22.5
DSG036*D | 3 | 900 | 85 | 59 | 105 | 31.3 | 0.97 | 30.58
DSG036*D | 3 | 900 | 85 | 63 | 105 | 31.8 | 0.9 | 28.84
DSG036*D | 3 | 900 | 85 | 67 | 105 | 32.9 | 0.77 | 25.6
DSG036*D | 3 | 900 | 85 | 71 | 105 | 34.5 | 0.6 | 22.2
DSG036*D | 3 | 900 | 85 | 59 | 115 | 29.5 | 1 | 29.8
DSG036*D | 3 | 900 | 85 | 63 | 115 | 30 | 0.99 | 29.93
DSG036*D | 3 | 900 | 85 | 67 | 115 | 31.1 | 0.85 | 26.68
DSG036*D | 3 | 900 | 85 | 71 | 115 | 32.7 | 0.7 | 23.3
DSG036*D | 3 | 1160 | 70 | 59 | 65 | 35.9 | 0.63 | 17.73
DSG036*D | 3 | 1160 | 70 | 63 | 65 | 36.4 | 0.56 | 16
DSG036*D | 3 | 1160 | 70 | 67 | 65 | 37.5 | 0.43 | 12.75
DSG036*D | 3 | 1160 | 70 | 59 | 75 | 35.6 | 0.63 | 17.68
DSG036*D | 3 | 1160 | 70 | 63 | 75 | 36.1 | 0.56 | 15.95
DSG036*D | 3 | 1160 | 70 | 67 | 75 | 37.2 | 0.44 | 12.7
DSG036*D | 3 | 1160 | 70 | 59 | 85 | 34.7 | 0.66 | 17.93
DSG036*D | 3 | 1160 | 70 | 63 | 85 | 35.2 | 0.59 | 16.19
DSG036*D | 3 | 1160 | 70 | 67 | 85 | 36.2 | 0.46 | 12.95
DSG036*D | 3 | 1160 | 70 | 59 | 95 | 33.1 | 0.68 | 17.67
DSG036*D | 3 | 1160 | 70 | 63 | 95 | 33.6 | 0.61 | 15.93
DSG036*D | 3 | 1160 | 70 | 67 | 95 | 34.6 | 0.47 | 12.69
DSG036*D | 3 | 1160 | 70 | 59 | 105 | 31.1 | 0.72 | 17.44
DSG036*D | 3 | 1160 | 70 | 63 | 105 | 31.6 | 0.63 | 15.7
DSG036*D | 3 | 1160 | 70 | 67 | 105 | 32.7 | 0.49 | 12.45
DSG036*D | 3 | 1160 | 70 | 59 | 115 | 29.3 | 0.81 | 18.52
DSG036*D | 3 | 1160 | 70 | 63 | 115 | 29.8 | 0.72 | 16.79
DSG036*D | 3 | 1160 | 70 | 67 | 115 | 30.9 | 0.56 | 13.54
DSG036*D | 3 | 1160 | 75 | 59 | 65 | 36.1 | 0.76 | 21.55
DSG036*D | 3 | 1160 | 75 | 63 | 65 | 36.6 | 0.69 | 19.81
DSG036*D | 3 | 1160 | 75 | 67 | 65 | 37.7 | 0.56 | 16.57
DSG036*D | 3 | 1160 | 75 | 71 | 65 | 39.3 | 0.4 | 13.2
DSG036*D | 3 | 1160 | 75 | 59 | 75 | 35.8 | 0.77 | 21.5
DSG036*D | 3 | 1160 | 75 | 63 | 75 | 36.3 | 0.7 | 19.77
DSG036*D | 3 | 1160 | 75 | 67 | 75 | 37.3 | 0.56 | 16.52
DSG036*D | 3 | 1160 | 75 | 71 | 75 | 39 | 0.4 | 13.2
DSG036*D | 3 | 1160 | 75 | 59 | 85 | 34.8 | 0.8 | 21.75
DSG036*D | 3 | 1160 | 75 | 63 | 85 | 35.4 | 0.72 | 20.01
DSG036*D | 3 | 1160 | 75 | 67 | 85 | 36.4 | 0.59 | 16.77
DSG036*D | 3 | 1160 | 75 | 71 | 85 | 38 | 0.4 | 13.4
DSG036*D | 3 | 1160 | 75 | 59 | 95 | 33.2 | 0.82 | 21.49
DSG036*D | 3 | 1160 | 75 | 63 | 95 | 33.8 | 0.75 | 19.75
DSG036*D | 3 | 1160 | 75 | 67 | 95 | 34.8 | 0.6 | 16.51
DSG036*D | 3 | 1160 | 75 | 71 | 95 | 36.4 | 0.5 | 13.1
DSG036*D | 3 | 1160 | 75 | 59 | 105 | 31.3 | 0.87 | 21.25
DSG036*D | 3 | 1160 | 75 | 63 | 105 | 31.8 | 0.78 | 19.52
DSG036*D | 3 | 1160 | 75 | 67 | 105 | 32.9 | 0.63 | 16.27
DSG036*D | 3 | 1160 | 75 | 71 | 105 | 34.5 | 0.5 | 12.9
DSG036*D | 3 | 1160 | 75 | 59 | 115 | 29.5 | 0.97 | 22.34
DSG036*D | 3 | 1160 | 75 | 63 | 115 | 30 | 0.88 | 20.6
DSG036*D | 3 | 1160 | 75 | 67 | 115 | 31.1 | 0.71 | 17.36
DSG036*D | 3 | 1160 | 75 | 71 | 115 | 32.7 | 0.5 | 14
DSG036*D | 3 | 1160 | 80 | 59 | 65 | 36.3 | 0.89 | 25.4
DSG036*D | 3 | 1160 | 80 | 63 | 65 | 36.8 | 0.82 | 23.66
DSG036*D | 3 | 1160 | 80 | 67 | 65 | 37.8 | 0.69 | 20.42
DSG036*D | 3 | 1160 | 80 | 71 | 65 | 39.5 | 0.6 | 17.1
DSG036*D | 3 | 1160 | 80 | 59 | 75 | 36 | 0.9 | 25.35
DSG036*D | 3 | 1160 | 80 | 63 | 75 | 36.5 | 0.83 | 23.61
DSG036*D | 3 | 1160 | 80 | 67 | 75 | 37.5 | 0.69 | 20.37
DSG036*D | 3 | 1160 | 80 | 71 | 75 | 39.2 | 0.6 | 17
DSG036*D | 3 | 1160 | 80 | 59 | 85 | 35 | 0.93 | 25.59
DSG036*D | 3 | 1160 | 80 | 63 | 85 | 35.5 | 0.86 | 23.86
DSG036*D | 3 | 1160 | 80 | 67 | 85 | 36.6 | 0.72 | 20.61
DSG036*D | 3 | 1160 | 80 | 71 | 85 | 38.2 | 0.6 | 17.3
DSG036*D | 3 | 1160 | 80 | 59 | 95 | 33.4 | 0.97 | 25.33
DSG036*D | 3 | 1160 | 80 | 63 | 95 | 33.9 | 0.89 | 23.59
DSG036*D | 3 | 1160 | 80 | 67 | 95 | 35 | 0.74 | 20.35
DSG036*D | 3 | 1160 | 80 | 71 | 95 | 36.6 | 0.6 | 17
DSG036*D | 3 | 1160 | 80 | 59 | 105 | 31.5 | 1 | 24.67
DSG036*D | 3 | 1160 | 80 | 63 | 105 | 32 | 0.93 | 23.36
DSG036*D | 3 | 1160 | 80 | 67 | 105 | 33 | 0.78 | 20.12
DSG036*D | 3 | 1160 | 80 | 71 | 105 | 34.7 | 0.6 | 16.8
DSG036*D | 3 | 1160 | 80 | 59 | 115 | 29.7 | 1 | 23.27
DSG036*D | 3 | 1160 | 80 | 63 | 115 | 30.2 | 1 | 23.66
DSG036*D | 3 | 1160 | 80 | 67 | 115 | 31.3 | 0.87 | 21.21
DSG036*D | 3 | 1160 | 80 | 71 | 115 | 32.9 | 0.7 | 17.8
DSG036*D | 3 | 1160 | 85 | 59 | 65 | 36.9 | 1 | 28.81
DSG036*D | 3 | 1160 | 85 | 63 | 65 | 37.4 | 0.92 | 27.07
DSG036*D | 3 | 1160 | 85 | 67 | 65 | 38.4 | 0.79 | 23.83
DSG036*D | 3 | 1160 | 85 | 71 | 65 | 40.1 | 0.7 | 20.5
DSG036*D | 3 | 1160 | 85 | 59 | 75 | 36.6 | 1 | 28.65
DSG036*D | 3 | 1160 | 85 | 63 | 75 | 37.1 | 0.93 | 27.02
DSG036*D | 3 | 1160 | 85 | 67 | 75 | 38.1 | 0.8 | 23.78
DSG036*D | 3 | 1160 | 85 | 71 | 75 | 39.8 | 0.7 | 20.4
DSG036*D | 3 | 1160 | 85 | 59 | 85 | 35.6 | 1 | 27.93
DSG036*D | 3 | 1160 | 85 | 63 | 85 | 36.1 | 0.96 | 27.27
DSG036*D | 3 | 1160 | 85 | 67 | 85 | 37.2 | 0.82 | 24.02
DSG036*D | 3 | 1160 | 85 | 71 | 85 | 38.8 | 0.7 | 20.7
DSG036*D | 3 | 1160 | 85 | 59 | 95 | 34 | 1 | 26.67
DSG036*D | 3 | 1160 | 85 | 63 | 95 | 34.5 | 1 | 27
DSG036*D | 3 | 1160 | 85 | 67 | 95 | 35.6 | 0.85 | 23.76
DSG036*D | 3 | 1160 | 85 | 71 | 95 | 37.2 | 0.7 | 20.4
DSG036*D | 3 | 1160 | 85 | 59 | 105 | 32.1 | 1 | 25.14
DSG036*D | 3 | 1160 | 85 | 63 | 105 | 32.6 | 1 | 25.53
DSG036*D | 3 | 1160 | 85 | 67 | 105 | 33.6 | 0.89 | 23.53
DSG036*D | 3 | 1160 | 85 | 71 | 105 | 35.3 | 0.7 | 20.2
DSG036*D | 3 | 1160 | 85 | 59 | 115 | 30.3 | 1 | 23.74
DSG036*D | 3 | 1160 | 85 | 63 | 115 | 30.8 | 1 | 24.13
DSG036*D | 3 | 1160 | 85 | 67 | 115 | 31.9 | 0.99 | 24.62
DSG036*D | 3 | 1160 | 85 | 71 | 115 | 33.5 | 0.8 | 21.3
DSG036*D | 3 | 1350 | 70 | 59 | 65 | 36.7 | 0.67 | 16.6
DSG036*D | 3 | 1350 | 70 | 63 | 65 | 37.2 | 0.59 | 14.86
DSG036*D | 3 | 1350 | 70 | 67 | 65 | 38.2 | 0.45 | 11.62
DSG036*D | 3 | 1350 | 70 | 59 | 75 | 36.4 | 0.68 | 16.55
DSG036*D | 3 | 1350 | 70 | 63 | 75 | 36.9 | 0.6 | 14.81
DSG036*D | 3 | 1350 | 70 | 67 | 75 | 37.9 | 0.45 | 11.57
DSG036*D | 3 | 1350 | 70 | 59 | 85 | 35.4 | 0.7 | 16.79
DSG036*D | 3 | 1350 | 70 | 63 | 85 | 35.9 | 0.62 | 15.06
DSG036*D | 3 | 1350 | 70 | 67 | 85 | 37 | 0.47 | 11.81
DSG036*D | 3 | 1350 | 70 | 59 | 95 | 33.8 | 0.73 | 16.53
DSG036*D | 3 | 1350 | 70 | 63 | 95 | 34.3 | 0.64 | 14.8
DSG036*D | 3 | 1350 | 70 | 67 | 95 | 35.4 | 0.48 | 11.55
DSG036*D | 3 | 1350 | 70 | 59 | 105 | 31.9 | 0.76 | 16.3
DSG036*D | 3 | 1350 | 70 | 63 | 105 | 32.4 | 0.67 | 14.56
DSG036*D | 3 | 1350 | 70 | 67 | 105 | 33.4 | 0.5 | 11.32
DSG036*D | 3 | 1350 | 70 | 59 | 115 | 30.1 | 0.86 | 17.39
DSG036*D | 3 | 1350 | 70 | 63 | 115 | 30.6 | 0.76 | 15.65
DSG036*D | 3 | 1350 | 70 | 67 | 115 | 31.6 | 0.58 | 12.41
DSG036*D | 3 | 1350 | 75 | 59 | 65 | 36.9 | 0.82 | 20.42
DSG036*D | 3 | 1350 | 75 | 63 | 65 | 37.4 | 0.74 | 18.68
DSG036*D | 3 | 1350 | 75 | 67 | 65 | 38.4 | 0.6 | 15.44
DSG036*D | 3 | 1350 | 75 | 71 | 65 | 40 | 0.4 | 12.1
DSG036*D | 3 | 1350 | 75 | 59 | 75 | 36.5 | 0.83 | 20.37
DSG036*D | 3 | 1350 | 75 | 63 | 75 | 37 | 0.75 | 18.63
DSG036*D | 3 | 1350 | 75 | 67 | 75 | 38.1 | 0.6 | 15.39
DSG036*D | 3 | 1350 | 75 | 71 | 75 | 39.7 | 0.4 | 12
DSG036*D | 3 | 1350 | 75 | 59 | 85 | 35.6 | 0.86 | 20.61
DSG036*D | 3 | 1350 | 75 | 63 | 85 | 36.1 | 0.78 | 18.88
DSG036*D | 3 | 1350 | 75 | 67 | 85 | 37.2 | 0.62 | 15.63
DSG036*D | 3 | 1350 | 75 | 71 | 85 | 38.8 | 0.5 | 12.3
DSG036*D | 3 | 1350 | 75 | 59 | 95 | 34 | 0.89 | 20.35
DSG036*D | 3 | 1350 | 75 | 63 | 95 | 34.5 | 0.8 | 18.61
DSG036*D | 3 | 1350 | 75 | 67 | 95 | 35.6 | 0.64 | 15.37
DSG036*D | 3 | 1350 | 75 | 71 | 95 | 37.2 | 0.5 | 12
DSG036*D | 3 | 1350 | 75 | 59 | 105 | 32.1 | 0.93 | 20.12
DSG036*D | 3 | 1350 | 75 | 63 | 105 | 32.6 | 0.84 | 18.38
DSG036*D | 3 | 1350 | 75 | 67 | 105 | 33.6 | 0.67 | 15.14
DSG036*D | 3 | 1350 | 75 | 71 | 105 | 35.2 | 0.5 | 11.8
DSG036*D | 3 | 1350 | 75 | 59 | 115 | 30.3 | 1 | 20.38
DSG036*D | 3 | 1350 | 75 | 63 | 115 | 30.8 | 0.94 | 19.47
DSG036*D | 3 | 1350 | 75 | 67 | 115 | 31.8 | 0.76 | 16.23
DSG036*D | 3 | 1350 | 75 | 71 | 115 | 33.5 | 0.6 | 12.9
DSG036*D | 3 | 1350 | 80 | 59 | 65 | 37 | 0.97 | 24.26
DSG036*D | 3 | 1350 | 80 | 63 | 65 | 37.5 | 0.89 | 22.52
DSG036*D | 3 | 1350 | 80 | 67 | 65 | 38.6 | 0.74 | 19.28
DSG036*D | 3 | 1350 | 80 | 71 | 65 | 40.2 | 0.6 | 15.9
DSG036*D | 3 | 1350 | 80 | 59 | 75 | 36.7 | 0.98 | 24.21
DSG036*D | 3 | 1350 | 80 | 63 | 75 | 37.2 | 0.9 | 22.48
DSG036*D | 3 | 1350 | 80 | 67 | 75 | 38.3 | 0.75 | 19.23
DSG036*D | 3 | 1350 | 80 | 71 | 75 | 39.9 | 0.6 | 15.9
DSG036*D | 3 | 1350 | 80 | 59 | 85 | 35.8 | 1 | 24.1
DSG036*D | 3 | 1350 | 80 | 63 | 85 | 36.3 | 0.93 | 22.72
DSG036*D | 3 | 1350 | 80 | 67 | 85 | 37.4 | 0.77 | 19.48
DSG036*D | 3 | 1350 | 80 | 71 | 85 | 39 | 0.6 | 16.1
DSG036*D | 3 | 1350 | 80 | 59 | 95 | 34.2 | 1 | 23.02
DSG036*D | 3 | 1350 | 80 | 63 | 95 | 34.7 | 0.96 | 22.46
DSG036*D | 3 | 1350 | 80 | 67 | 95 | 35.8 | 0.8 | 19.22
DSG036*D | 3 | 1350 | 80 | 71 | 95 | 37.4 | 0.6 | 15.9
DSG036*D | 3 | 1350 | 80 | 59 | 105 | 32.2 | 1 | 21.71
DSG036*D | 3 | 1350 | 80 | 63 | 105 | 32.7 | 1 | 22.05
DSG036*D | 3 | 1350 | 80 | 67 | 105 | 33.8 | 0.83 | 18.98
DSG036*D | 3 | 1350 | 80 | 71 | 105 | 35.4 | 0.7 | 15.6
DSG036*D | 3 | 1350 | 80 | 59 | 115 | 30.5 | 1 | 20.51
DSG036*D | 3 | 1350 | 80 | 63 | 115 | 31 | 1 | 20.84
DSG036*D | 3 | 1350 | 80 | 67 | 115 | 32 | 0.93 | 20.07
DSG036*D | 3 | 1350 | 80 | 71 | 115 | 33.6 | 0.7 | 16.7
DSG036*D | 3 | 1350 | 85 | 59 | 65 | 37.6 | 1 | 25.35
DSG036*D | 3 | 1350 | 85 | 63 | 65 | 38.1 | 1 | 25.69
DSG036*D | 3 | 1350 | 85 | 67 | 65 | 39.2 | 0.86 | 22.69
DSG036*D | 3 | 1350 | 85 | 71 | 65 | 40.8 | 0.7 | 19.3
DSG036*D | 3 | 1350 | 85 | 59 | 75 | 37.3 | 1 | 25.13
DSG036*D | 3 | 1350 | 85 | 63 | 75 | 37.8 | 1 | 25.47
DSG036*D | 3 | 1350 | 85 | 67 | 75 | 38.9 | 0.86 | 22.64
DSG036*D | 3 | 1350 | 85 | 71 | 75 | 40.5 | 0.7 | 19.3
DSG036*D | 3 | 1350 | 85 | 59 | 85 | 36.4 | 1 | 24.51
DSG036*D | 3 | 1350 | 85 | 63 | 85 | 36.9 | 1 | 24.84
DSG036*D | 3 | 1350 | 85 | 67 | 85 | 38 | 0.9 | 22.89
DSG036*D | 3 | 1350 | 85 | 71 | 85 | 39.6 | 0.7 | 19.5
DSG036*D | 3 | 1350 | 85 | 59 | 95 | 34.8 | 1 | 23.43
DSG036*D | 3 | 1350 | 85 | 63 | 95 | 35.3 | 1 | 23.77
DSG036*D | 3 | 1350 | 85 | 67 | 95 | 36.4 | 0.92 | 22.63
DSG036*D | 3 | 1350 | 85 | 71 | 95 | 38 | 0.8 | 19.3
DSG036*D | 3 | 1350 | 85 | 59 | 105 | 32.8 | 1 | 22.11
DSG036*D | 3 | 1350 | 85 | 63 | 105 | 33.3 | 1 | 22.45
DSG036*D | 3 | 1350 | 85 | 67 | 105 | 34.4 | 0.97 | 22.39
DSG036*D | 3 | 1350 | 85 | 71 | 105 | 36 | 0.8 | 19
DSG036*D | 3 | 1350 | 85 | 59 | 115 | 31.1 | 1 | 20.91
DSG036*D | 3 | 1350 | 85 | 63 | 115 | 31.6 | 1 | 21.25
DSG036*D | 3 | 1350 | 85 | 67 | 115 | 32.6 | 1 | 21.97
DSG036*D | 3 | 1350 | 85 | 71 | 115 | 34.2 | 0.9 | 20.1
DSG048*D | 4 | 1200 | 70 | 59 | 65 | 46.1 | 0.57 | 19.93
DSG048*D | 4 | 1200 | 70 | 63 | 65 | 46.7 | 0.51 | 18.21
DSG048*D | 4 | 1200 | 70 | 67 | 65 | 48.1 | 0.41 | 15
DSG048*D | 4 | 1200 | 70 | 59 | 75 | 45.6 | 0.58 | 19.89
DSG048*D | 4 | 1200 | 70 | 63 | 75 | 46.3 | 0.52 | 18.17
DSG048*D | 4 | 1200 | 70 | 67 | 75 | 47.7 | 0.41 | 14.95
DSG048*D | 4 | 1200 | 70 | 59 | 85 | 44.4 | 0.6 | 20.13
DSG048*D | 4 | 1200 | 70 | 63 | 85 | 45.1 | 0.54 | 18.41
DSG048*D | 4 | 1200 | 70 | 67 | 85 | 46.5 | 0.43 | 15.19
DSG048*D | 4 | 1200 | 70 | 59 | 95 | 42.3 | 0.62 | 19.87
DSG048*D | 4 | 1200 | 70 | 63 | 95 | 43 | 0.56 | 18.15
DSG048*D | 4 | 1200 | 70 | 67 | 95 | 44.4 | 0.44 | 14.93
DSG048*D | 4 | 1200 | 70 | 59 | 105 | 39.8 | 0.65 | 19.64
DSG048*D | 4 | 1200 | 70 | 63 | 105 | 40.4 | 0.59 | 17.92
DSG048*D | 4 | 1200 | 70 | 67 | 105 | 41.8 | 0.46 | 14.7
DSG048*D | 4 | 1200 | 70 | 59 | 115 | 37.4 | 0.73 | 20.72
DSG048*D | 4 | 1200 | 70 | 63 | 115 | 38.1 | 0.66 | 19
DSG048*D | 4 | 1200 | 70 | 67 | 115 | 39.5 | 0.53 | 15.78
DSG048*D | 4 | 1200 | 75 | 59 | 65 | 46.3 | 0.68 | 23.72
DSG048*D | 4 | 1200 | 75 | 63 | 65 | 47 | 0.62 | 22
DSG048*D | 4 | 1200 | 75 | 67 | 65 | 48.4 | 0.51 | 18.78
DSG048*D | 4 | 1200 | 75 | 71 | 65 | 50.5 | 0.4 | 15.5
DSG048*D | 4 | 1200 | 75 | 59 | 75 | 45.9 | 0.68 | 23.67
DSG048*D | 4 | 1200 | 75 | 63 | 75 | 46.5 | 0.62 | 21.95
DSG048*D | 4 | 1200 | 75 | 67 | 75 | 47.9 | 0.52 | 18.74
DSG048*D | 4 | 1200 | 75 | 71 | 75 | 50.1 | 0.4 | 15.4
DSG048*D | 4 | 1200 | 75 | 59 | 85 | 44.7 | 0.71 | 23.92
DSG048*D | 4 | 1200 | 75 | 63 | 85 | 45.3 | 0.65 | 22.19
DSG048*D | 4 | 1200 | 75 | 67 | 85 | 46.7 | 0.54 | 18.98
DSG048*D | 4 | 1200 | 75 | 71 | 85 | 48.9 | 0.4 | 15.6
DSG048*D | 4 | 1200 | 75 | 59 | 95 | 42.6 | 0.73 | 23.66
DSG048*D | 4 | 1200 | 75 | 63 | 95 | 43.2 | 0.67 | 21.93
DSG048*D | 4 | 1200 | 75 | 67 | 95 | 44.6 | 0.55 | 18.72
DSG048*D | 4 | 1200 | 75 | 71 | 95 | 46.8 | 0.4 | 15.4
DSG048*D | 4 | 1200 | 75 | 59 | 105 | 40 | 0.77 | 23.43
DSG048*D | 4 | 1200 | 75 | 63 | 105 | 40.7 | 0.7 | 21.7
DSG048*D | 4 | 1200 | 75 | 67 | 105 | 42.1 | 0.58 | 18.49
DSG048*D | 4 | 1200 | 75 | 71 | 105 | 44.2 | 0.5 | 15.2
DSG048*D | 4 | 1200 | 75 | 59 | 115 | 37.6 | 0.86 | 24.51
DSG048*D | 4 | 1200 | 75 | 63 | 115 | 38.3 | 0.79 | 22.78
DSG048*D | 4 | 1200 | 75 | 67 | 115 | 39.7 | 0.65 | 19.57
DSG048*D | 4 | 1200 | 75 | 71 | 115 | 41.8 | 0.5 | 16.2
DSG048*D | 4 | 1200 | 80 | 59 | 65 | 46.5 | 0.78 | 27.53
DSG048*D | 4 | 1200 | 80 | 63 | 65 | 47.2 | 0.72 | 25.81
DSG048*D | 4 | 1200 | 80 | 67 | 65 | 48.6 | 0.61 | 22.6
DSG048*D | 4 | 1200 | 80 | 71 | 65 | 50.7 | 0.5 | 19.3
DSG048*D | 4 | 1200 | 80 | 59 | 75 | 46.1 | 0.79 | 27.49
DSG048*D | 4 | 1200 | 80 | 63 | 75 | 46.8 | 0.73 | 25.77
DSG048*D | 4 | 1200 | 80 | 67 | 75 | 48.2 | 0.62 | 22.55
DSG048*D | 4 | 1200 | 80 | 71 | 75 | 50.3 | 0.5 | 19.2
DSG048*D | 4 | 1200 | 80 | 59 | 85 | 44.9 | 0.82 | 27.73
DSG048*D | 4 | 1200 | 80 | 63 | 85 | 45.6 | 0.75 | 26.01
DSG048*D | 4 | 1200 | 80 | 67 | 85 | 47 | 0.64 | 22.79
DSG048*D | 4 | 1200 | 80 | 71 | 85 | 49.1 | 0.5 | 19.5
DSG048*D | 4 | 1200 | 80 | 59 | 95 | 42.8 | 0.85 | 27.47
DSG048*D | 4 | 1200 | 80 | 63 | 95 | 43.5 | 0.78 | 25.75
DSG048*D | 4 | 1200 | 80 | 67 | 95 | 44.9 | 0.66 | 22.53
DSG048*D | 4 | 1200 | 80 | 71 | 95 | 47 | 0.5 | 19.2
DSG048*D | 4 | 1200 | 80 | 59 | 105 | 40.2 | 0.89 | 27.24
DSG048*D | 4 | 1200 | 80 | 63 | 105 | 40.9 | 0.82 | 25.52
DSG048*D | 4 | 1200 | 80 | 67 | 105 | 42.3 | 0.7 | 22.3
DSG048*D | 4 | 1200 | 80 | 71 | 105 | 44.4 | 0.6 | 19
DSG048*D | 4 | 1200 | 80 | 59 | 115 | 37.9 | 0.99 | 28.32
DSG048*D | 4 | 1200 | 80 | 63 | 115 | 38.6 | 0.91 | 26.6
DSG048*D | 4 | 1200 | 80 | 67 | 115 | 39.9 | 0.77 | 23.38
DSG048*D | 4 | 1200 | 80 | 71 | 115 | 42.1 | 0.6 | 20
DSG048*D | 4 | 1200 | 85 | 59 | 65 | 47.3 | 0.86 | 30.92
DSG048*D | 4 | 1200 | 85 | 63 | 65 | 48 | 0.8 | 29.19
DSG048*D | 4 | 1200 | 85 | 67 | 65 | 49.4 | 0.69 | 25.98
DSG048*D | 4 | 1200 | 85 | 71 | 65 | 51.5 | 0.6 | 22.6
DSG048*D | 4 | 1200 | 85 | 59 | 75 | 46.9 | 0.87 | 30.87
DSG048*D | 4 | 1200 | 85 | 63 | 75 | 47.6 | 0.81 | 29.15
DSG048*D | 4 | 1200 | 85 | 67 | 75 | 49 | 0.7 | 25.93
DSG048*D | 4 | 1200 | 85 | 71 | 75 | 51.1 | 0.6 | 22.6
DSG048*D | 4 | 1200 | 85 | 59 | 85 | 45.7 | 0.9 | 31.11
DSG048*D | 4 | 1200 | 85 | 63 | 85 | 46.4 | 0.84 | 29.39
DSG048*D | 4 | 1200 | 85 | 67 | 85 | 47.8 | 0.72 | 26.17
DSG048*D | 4 | 1200 | 85 | 71 | 85 | 49.9 | 0.6 | 22.8
DSG048*D | 4 | 1200 | 85 | 59 | 95 | 43.6 | 0.93 | 30.85
DSG048*D | 4 | 1200 | 85 | 63 | 95 | 44.3 | 0.87 | 29.13
DSG048*D | 4 | 1200 | 85 | 67 | 95 | 45.7 | 0.75 | 25.91
DSG048*D | 4 | 1200 | 85 | 71 | 95 | 47.8 | 0.6 | 22.6
DSG048*D | 4 | 1200 | 85 | 59 | 105 | 41 | 0.99 | 30.62
DSG048*D | 4 | 1200 | 85 | 63 | 105 | 41.7 | 0.92 | 28.9
DSG048*D | 4 | 1200 | 85 | 67 | 105 | 43.1 | 0.79 | 25.68
DSG048*D | 4 | 1200 | 85 | 71 | 105 | 45.2 | 0.7 | 22.4
DSG048*D | 4 | 1200 | 85 | 59 | 115 | 38.7 | 1 | 29.3
DSG048*D | 4 | 1200 | 85 | 63 | 115 | 39.3 | 1 | 29.8
DSG048*D | 4 | 1200 | 85 | 67 | 115 | 40.7 | 0.87 | 26.76
DSG048*D | 4 | 1200 | 85 | 71 | 115 | 42.9 | 0.7 | 23.4
DSG048*D | 4 | 1600 | 70 | 59 | 65 | 47.2 | 0.66 | 17.58
DSG048*D | 4 | 1600 | 70 | 63 | 65 | 47.9 | 0.58 | 15.86
DSG048*D | 4 | 1600 | 70 | 67 | 65 | 49.3 | 0.45 | 12.65
DSG048*D | 4 | 1600 | 70 | 59 | 75 | 46.8 | 0.66 | 17.54
DSG048*D | 4 | 1600 | 70 | 63 | 75 | 47.4 | 0.59 | 15.81
DSG048*D | 4 | 1600 | 70 | 67 | 75 | 48.8 | 0.45 | 12.6
DSG048*D | 4 | 1600 | 70 | 59 | 85 | 45.6 | 0.69 | 17.78
DSG048*D | 4 | 1600 | 70 | 63 | 85 | 46.2 | 0.61 | 16.06
DSG048*D | 4 | 1600 | 70 | 67 | 85 | 47.6 | 0.47 | 12.84
DSG048*D | 4 | 1600 | 70 | 59 | 95 | 43.5 | 0.71 | 17.52
DSG048*D | 4 | 1600 | 70 | 63 | 95 | 44.1 | 0.63 | 15.8
DSG048*D | 4 | 1600 | 70 | 67 | 95 | 45.5 | 0.49 | 12.58
DSG048*D | 4 | 1600 | 70 | 59 | 105 | 40.9 | 0.74 | 17.29
DSG048*D | 4 | 1600 | 70 | 63 | 105 | 41.5 | 0.66 | 15.57
DSG048*D | 4 | 1600 | 70 | 67 | 105 | 42.9 | 0.51 | 12.35
DSG048*D | 4 | 1600 | 70 | 59 | 115 | 38.5 | 0.84 | 18.37
DSG048*D | 4 | 1600 | 70 | 63 | 115 | 39.2 | 0.75 | 16.64
DSG048*D | 4 | 1600 | 70 | 67 | 115 | 40.6 | 0.58 | 13.43
DSG048*D | 4 | 1600 | 75 | 59 | 65 | 47.4 | 0.79 | 21.37
DSG048*D | 4 | 1600 | 75 | 63 | 65 | 48.1 | 0.72 | 19.65
DSG048*D | 4 | 1600 | 75 | 67 | 65 | 49.5 | 0.58 | 16.43
DSG048*D | 4 | 1600 | 75 | 71 | 65 | 51.6 | 0.4 | 13.1
DSG048*D | 4 | 1600 | 75 | 59 | 75 | 47 | 0.8 | 21.32
DSG048*D | 4 | 1600 | 75 | 63 | 75 | 47.7 | 0.72 | 19.6
DSG048*D | 4 | 1600 | 75 | 67 | 75 | 49.1 | 0.59 | 16.39
DSG048*D | 4 | 1600 | 75 | 71 | 75 | 51.2 | 0.4 | 13.1
DSG048*D | 4 | 1600 | 75 | 59 | 85 | 45.8 | 0.83 | 21.57
DSG048*D | 4 | 1600 | 75 | 63 | 85 | 46.5 | 0.75 | 19.84
DSG048*D | 4 | 1600 | 75 | 67 | 85 | 47.9 | 0.61 | 16.63
DSG048*D | 4 | 1600 | 75 | 71 | 85 | 50 | 0.5 | 13.3
DSG048*D | 4 | 1600 | 75 | 59 | 95 | 43.7 | 0.86 | 21.31
DSG048*D | 4 | 1600 | 75 | 63 | 95 | 44.4 | 0.78 | 19.58
DSG048*D | 4 | 1600 | 75 | 67 | 95 | 45.8 | 0.63 | 16.37
DSG048*D | 4 | 1600 | 75 | 71 | 95 | 47.9 | 0.5 | 13
DSG048*D | 4 | 1600 | 75 | 59 | 105 | 41.1 | 0.9 | 21.08
DSG048*D | 4 | 1600 | 75 | 63 | 105 | 41.8 | 0.82 | 19.35
DSG048*D | 4 | 1600 | 75 | 67 | 105 | 43.2 | 0.66 | 16.14
DSG048*D | 4 | 1600 | 75 | 71 | 105 | 45.3 | 0.5 | 12.8
DSG048*D | 4 | 1600 | 75 | 59 | 115 | 38.8 | 1 | 22.04
DSG048*D | 4 | 1600 | 75 | 63 | 115 | 39.4 | 0.91 | 20.43
DSG048*D | 4 | 1600 | 75 | 67 | 115 | 40.8 | 0.74 | 17.22
DSG048*D | 4 | 1600 | 75 | 71 | 115 | 43 | 0.6 | 13.9
DSG048*D | 4 | 1600 | 80 | 59 | 65 | 47.7 | 0.93 | 25.18
DSG048*D | 4 | 1600 | 80 | 63 | 65 | 48.3 | 0.85 | 23.46
DSG048*D | 4 | 1600 | 80 | 67 | 65 | 49.7 | 0.72 | 20.24
DSG048*D | 4 | 1600 | 80 | 71 | 65 | 51.9 | 0.6 | 16.9
DSG048*D | 4 | 1600 | 80 | 59 | 75 | 47.3 | 0.94 | 25.14
DSG048*D | 4 | 1600 | 80 | 63 | 75 | 47.9 | 0.86 | 23.41
DSG048*D | 4 | 1600 | 80 | 67 | 75 | 49.3 | 0.72 | 20.2
DSG048*D | 4 | 1600 | 80 | 71 | 75 | 51.5 | 0.6 | 16.9
DSG048*D | 4 | 1600 | 80 | 59 | 85 | 46 | 0.97 | 25.38
DSG048*D | 4 | 1600 | 80 | 63 | 85 | 46.7 | 0.89 | 23.66
DSG048*D | 4 | 1600 | 80 | 67 | 85 | 48.1 | 0.75 | 20.44
DSG048*D | 4 | 1600 | 80 | 71 | 85 | 50.2 | 0.6 | 17.1
DSG048*D | 4 | 1600 | 80 | 59 | 95 | 43.9 | 1 | 24.97
DSG048*D | 4 | 1600 | 80 | 63 | 95 | 44.6 | 0.92 | 23.4
DSG048*D | 4 | 1600 | 80 | 67 | 95 | 46 | 0.77 | 20.18
DSG048*D | 4 | 1600 | 80 | 71 | 95 | 48.1 | 0.6 | 16.8
DSG048*D | 4 | 1600 | 80 | 59 | 105 | 41.4 | 1 | 23.51
DSG048*D | 4 | 1600 | 80 | 63 | 105 | 42 | 0.97 | 23.17
DSG048*D | 4 | 1600 | 80 | 67 | 105 | 43.4 | 0.81 | 19.95
DSG048*D | 4 | 1600 | 80 | 71 | 105 | 45.6 | 0.6 | 16.6
DSG048*D | 4 | 1600 | 80 | 59 | 115 | 39 | 1 | 22.17
DSG048*D | 4 | 1600 | 80 | 63 | 115 | 39.7 | 1 | 22.55
DSG048*D | 4 | 1600 | 80 | 67 | 115 | 41.1 | 0.9 | 21.03
DSG048*D | 4 | 1600 | 80 | 71 | 115 | 43.2 | 0.7 | 17.7
DSG048*D | 4 | 1600 | 85 | 59 | 65 | 48.5 | 1 | 27.54
DSG048*D | 4 | 1600 | 85 | 63 | 65 | 49.1 | 0.96 | 26.84
DSG048*D | 4 | 1600 | 85 | 67 | 65 | 50.5 | 0.82 | 23.63
DSG048*D | 4 | 1600 | 85 | 71 | 65 | 52.7 | 0.7 | 20.3
DSG048*D | 4 | 1600 | 85 | 59 | 75 | 48.1 | 1 | 27.3
DSG048*D | 4 | 1600 | 85 | 63 | 75 | 48.7 | 0.97 | 26.8
DSG048*D | 4 | 1600 | 85 | 67 | 75 | 50.1 | 0.83 | 23.58
DSG048*D | 4 | 1600 | 85 | 71 | 75 | 52.2 | 0.7 | 20.2
DSG048*D | 4 | 1600 | 85 | 59 | 85 | 46.8 | 1 | 26.61
DSG048*D | 4 | 1600 | 85 | 63 | 85 | 47.5 | 1 | 26.98
DSG048*D | 4 | 1600 | 85 | 67 | 85 | 48.9 | 0.86 | 23.82
DSG048*D | 4 | 1600 | 85 | 71 | 85 | 51 | 0.7 | 20.5
DSG048*D | 4 | 1600 | 85 | 59 | 95 | 44.7 | 1 | 25.41
DSG048*D | 4 | 1600 | 85 | 63 | 95 | 45.4 | 1 | 25.79
DSG048*D | 4 | 1600 | 85 | 67 | 95 | 46.8 | 0.89 | 23.56
DSG048*D | 4 | 1600 | 85 | 71 | 95 | 48.9 | 0.7 | 20.2
DSG048*D | 4 | 1600 | 85 | 59 | 105 | 42.2 | 1 | 23.95
DSG048*D | 4 | 1600 | 85 | 63 | 105 | 42.8 | 1 | 24.33
DSG048*D | 4 | 1600 | 85 | 67 | 105 | 44.2 | 0.93 | 23.33
DSG048*D | 4 | 1600 | 85 | 71 | 105 | 46.4 | 0.8 | 20
DSG048*D | 4 | 1600 | 85 | 59 | 115 | 39.8 | 1 | 22.62
DSG048*D | 4 | 1600 | 85 | 63 | 115 | 40.5 | 1 | 23
DSG048*D | 4 | 1600 | 85 | 67 | 115 | 41.9 | 1 | 23.79
DSG048*D | 4 | 1600 | 85 | 71 | 115 | 44 | 0.8 | 21.1
DSG048*D | 4 | 1800 | 70 | 59 | 65 | 47.9 | 0.69 | 16.71
DSG048*D | 4 | 1800 | 70 | 63 | 65 | 48.6 | 0.61 | 14.99
DSG048*D | 4 | 1800 | 70 | 67 | 65 | 50 | 0.47 | 11.77
DSG048*D | 4 | 1800 | 70 | 59 | 75 | 47.5 | 0.69 | 16.66
DSG048*D | 4 | 1800 | 70 | 63 | 75 | 48.2 | 0.61 | 14.94
DSG048*D | 4 | 1800 | 70 | 67 | 75 | 49.6 | 0.47 | 11.72
DSG048*D | 4 | 1800 | 70 | 59 | 85 | 46.3 | 0.72 | 16.9
DSG048*D | 4 | 1800 | 70 | 63 | 85 | 47 | 0.64 | 15.18
DSG048*D | 4 | 1800 | 70 | 67 | 85 | 48.4 | 0.49 | 11.96
DSG048*D | 4 | 1800 | 70 | 59 | 95 | 44.2 | 0.75 | 16.64
DSG048*D | 4 | 1800 | 70 | 63 | 95 | 44.9 | 0.66 | 14.92
DSG048*D | 4 | 1800 | 70 | 67 | 95 | 46.3 | 0.5 | 11.7
DSG048*D | 4 | 1800 | 70 | 59 | 105 | 41.6 | 0.78 | 16.41
DSG048*D | 4 | 1800 | 70 | 63 | 105 | 42.3 | 0.69 | 14.69
DSG048*D | 4 | 1800 | 70 | 67 | 105 | 43.7 | 0.52 | 11.47
DSG048*D | 4 | 1800 | 70 | 59 | 115 | 39.3 | 0.88 | 17.49
DSG048*D | 4 | 1800 | 70 | 63 | 115 | 39.9 | 0.78 | 15.77
DSG048*D | 4 | 1800 | 70 | 67 | 115 | 41.3 | 0.6 | 12.55
DSG048*D | 4 | 1800 | 75 | 59 | 65 | 48.2 | 0.84 | 20.49
DSG048*D | 4 | 1800 | 75 | 63 | 65 | 48.8 | 0.76 | 18.77
DSG048*D | 4 | 1800 | 75 | 67 | 65 | 50.2 | 0.61 | 15.56
DSG048*D | 4 | 1800 | 75 | 71 | 65 | 52.4 | 0.5 | 12.2
DSG048*D | 4 | 1800 | 75 | 59 | 75 | 47.8 | 0.85 | 20.45
DSG048*D | 4 | 1800 | 75 | 63 | 75 | 48.4 | 0.77 | 18.73
DSG048*D | 4 | 1800 | 75 | 67 | 75 | 49.8 | 0.62 | 15.51
DSG048*D | 4 | 1800 | 75 | 71 | 75 | 52 | 0.5 | 12.2
DSG048*D | 4 | 1800 | 75 | 59 | 85 | 46.5 | 0.88 | 20.69
DSG048*D | 4 | 1800 | 75 | 63 | 85 | 47.2 | 0.8 | 18.97
DSG048*D | 4 | 1800 | 75 | 67 | 85 | 48.6 | 0.64 | 15.75
DSG048*D | 4 | 1800 | 75 | 71 | 85 | 50.7 | 0.5 | 12.4
DSG048*D | 4 | 1800 | 75 | 59 | 95 | 44.4 | 0.91 | 20.43
DSG048*D | 4 | 1800 | 75 | 63 | 95 | 45.1 | 0.82 | 18.71
DSG048*D | 4 | 1800 | 75 | 67 | 95 | 46.5 | 0.66 | 15.49
DSG048*D | 4 | 1800 | 75 | 71 | 95 | 48.6 | 0.5 | 12.2
DSG048*D | 4 | 1800 | 75 | 59 | 105 | 41.9 | 0.96 | 20.2
DSG048*D | 4 | 1800 | 75 | 63 | 105 | 42.5 | 0.86 | 18.48
DSG048*D | 4 | 1800 | 75 | 67 | 105 | 43.9 | 0.69 | 15.26
DSG048*D | 4 | 1800 | 75 | 71 | 105 | 46.1 | 0.5 | 11.9
DSG048*D | 4 | 1800 | 75 | 59 | 115 | 39.5 | 1 | 19.96
DSG048*D | 4 | 1800 | 75 | 63 | 115 | 40.2 | 0.96 | 19.56
DSG048*D | 4 | 1800 | 75 | 67 | 115 | 41.6 | 0.78 | 16.34
DSG048*D | 4 | 1800 | 75 | 71 | 115 | 43.7 | 0.6 | 13
DSG048*D | 4 | 1800 | 80 | 59 | 65 | 48.4 | 0.99 | 24.31
DSG048*D | 4 | 1800 | 80 | 63 | 65 | 49.1 | 0.91 | 22.58
DSG048*D | 4 | 1800 | 80 | 67 | 65 | 50.5 | 0.76 | 19.37
DSG048*D | 4 | 1800 | 80 | 71 | 65 | 52.6 | 0.6 | 16
DSG048*D | 4 | 1800 | 80 | 59 | 75 | 48 | 1 | 24.24
DSG048*D | 4 | 1800 | 80 | 63 | 75 | 48.7 | 0.92 | 22.54
DSG048*D | 4 | 1800 | 80 | 67 | 75 | 50.1 | 0.76 | 19.32
DSG048*D | 4 | 1800 | 80 | 71 | 75 | 52.2 | 0.6 | 16
DSG048*D | 4 | 1800 | 80 | 59 | 85 | 46.8 | 1 | 23.63
DSG048*D | 4 | 1800 | 80 | 63 | 85 | 47.4 | 0.95 | 22.78
DSG048*D | 4 | 1800 | 80 | 67 | 85 | 48.8 | 0.79 | 19.56
DSG048*D | 4 | 1800 | 80 | 71 | 85 | 51 | 0.6 | 16.2
DSG048*D | 4 | 1800 | 80 | 59 | 95 | 44.7 | 1 | 22.57
DSG048*D | 4 | 1800 | 80 | 63 | 95 | 45.3 | 0.98 | 22.52
DSG048*D | 4 | 1800 | 80 | 67 | 95 | 46.7 | 0.82 | 19.3
DSG048*D | 4 | 1800 | 80 | 71 | 95 | 48.9 | 0.6 | 16
DSG048*D | 4 | 1800 | 80 | 59 | 105 | 42.1 | 1 | 21.27
DSG048*D | 4 | 1800 | 80 | 63 | 105 | 42.8 | 1 | 21.6
DSG048*D | 4 | 1800 | 80 | 67 | 105 | 44.2 | 0.86 | 19.07
DSG048*D | 4 | 1800 | 80 | 71 | 105 | 46.3 | 0.7 | 15.7
DSG048*D | 4 | 1800 | 80 | 59 | 115 | 39.8 | 1 | 20.08
DSG048*D | 4 | 1800 | 80 | 63 | 115 | 40.4 | 1 | 20.42
DSG048*D | 4 | 1800 | 80 | 67 | 115 | 41.8 | 0.95 | 20.15
DSG048*D | 4 | 1800 | 80 | 71 | 115 | 44 | 0.8 | 16.8
DSG048*D | 4 | 1800 | 85 | 59 | 65 | 49.2 | 1 | 24.85
DSG048*D | 4 | 1800 | 85 | 63 | 65 | 49.9 | 1 | 25.19
DSG048*D | 4 | 1800 | 85 | 67 | 65 | 51.3 | 0.88 | 22.75
DSG048*D | 4 | 1800 | 85 | 71 | 65 | 53.4 | 0.7 | 19.4
DSG048*D | 4 | 1800 | 85 | 59 | 75 | 48.8 | 1 | 24.64
DSG048*D | 4 | 1800 | 85 | 63 | 75 | 49.5 | 1 | 24.98
DSG048*D | 4 | 1800 | 85 | 67 | 75 | 50.9 | 0.88 | 22.7
DSG048*D | 4 | 1800 | 85 | 71 | 75 | 53 | 0.7 | 19.4
DSG048*D | 4 | 1800 | 85 | 59 | 85 | 47.6 | 1 | 24.03
DSG048*D | 4 | 1800 | 85 | 63 | 85 | 48.2 | 1 | 24.36
DSG048*D | 4 | 1800 | 85 | 67 | 85 | 49.6 | 0.92 | 22.95
DSG048*D | 4 | 1800 | 85 | 71 | 85 | 51.8 | 0.8 | 19.6
DSG048*D | 4 | 1800 | 85 | 59 | 95 | 45.5 | 1 | 22.96
DSG048*D | 4 | 1800 | 85 | 63 | 95 | 46.1 | 1 | 23.3
DSG048*D | 4 | 1800 | 85 | 67 | 95 | 47.5 | 0.95 | 22.69
DSG048*D | 4 | 1800 | 85 | 71 | 95 | 49.7 | 0.8 | 19.4
DSG048*D | 4 | 1800 | 85 | 59 | 105 | 42.9 | 1 | 21.67
DSG048*D | 4 | 1800 | 85 | 63 | 105 | 43.6 | 1 | 22
DSG048*D | 4 | 1800 | 85 | 67 | 105 | 45 | 0.99 | 22.46
DSG048*D | 4 | 1800 | 85 | 71 | 105 | 47.1 | 0.8 | 19.1
DSG048*D | 4 | 1800 | 85 | 59 | 115 | 40.6 | 1 | 20.48
DSG048*D | 4 | 1800 | 85 | 63 | 115 | 41.2 | 1 | 20.81
DSG048*D | 4 | 1800 | 85 | 67 | 115 | 42.6 | 1 | 21.52
DSG048*D | 4 | 1800 | 85 | 71 | 115 | 44.7 | 0.9 | 20.2
DSG060*D | 5 | 1500 | 70 | 59 | 65 | 57.9 | 0.56 | 19.75
DSG060*D | 5 | 1500 | 70 | 63 | 65 | 58.7 | 0.51 | 17.99
DSG060*D | 5 | 1500 | 70 | 67 | 65 | 60.4 | 0.4 | 14.7
DSG060*D | 5 | 1500 | 70 | 59 | 75 | 57.3 | 0.57 | 19.7
DSG060*D | 5 | 1500 | 70 | 63 | 75 | 58.2 | 0.51 | 17.94
DSG060*D | 5 | 1500 | 70 | 67 | 75 | 59.9 | 0.4 | 14.65
DSG060*D | 5 | 1500 | 70 | 59 | 85 | 55.8 | 0.59 | 19.95
DSG060*D | 5 | 1500 | 70 | 63 | 85 | 56.6 | 0.53 | 18.19
DSG060*D | 5 | 1500 | 70 | 67 | 85 | 58.4 | 0.42 | 14.9
DSG060*D | 5 | 1500 | 70 | 59 | 95 | 53.2 | 0.61 | 19.69
DSG060*D | 5 | 1500 | 70 | 63 | 95 | 54 | 0.55 | 17.92
DSG060*D | 5 | 1500 | 70 | 67 | 95 | 55.8 | 0.43 | 14.63
DSG060*D | 5 | 1500 | 70 | 59 | 105 | 50 | 0.64 | 19.45
DSG060*D | 5 | 1500 | 70 | 63 | 105 | 50.8 | 0.57 | 17.69
DSG060*D | 5 | 1500 | 70 | 67 | 105 | 52.5 | 0.45 | 14.4
DSG060*D | 5 | 1500 | 70 | 59 | 115 | 47 | 0.72 | 20.55
DSG060*D | 5 | 1500 | 70 | 63 | 115 | 47.9 | 0.65 | 18.79
DSG060*D | 5 | 1500 | 70 | 67 | 115 | 49.6 | 0.52 | 15.5
DSG060*D | 5 | 1500 | 75 | 59 | 65 | 58.2 | 0.67 | 23.63
DSG060*D | 5 | 1500 | 75 | 63 | 65 | 59 | 0.61 | 21.86
DSG060*D | 5 | 1500 | 75 | 67 | 65 | 60.7 | 0.5 | 18.57
DSG060*D | 5 | 1500 | 75 | 71 | 65 | 63.4 | 0.4 | 15.2
DSG060*D | 5 | 1500 | 75 | 59 | 75 | 57.6 | 0.67 | 23.58
DSG060*D | 5 | 1500 | 75 | 63 | 75 | 58.5 | 0.62 | 21.82
DSG060*D | 5 | 1500 | 75 | 67 | 75 | 60.2 | 0.51 | 18.53
DSG060*D | 5 | 1500 | 75 | 71 | 75 | 62.9 | 0.4 | 15.1
DSG060*D | 5 | 1500 | 75 | 59 | 85 | 56.1 | 0.7 | 23.83
DSG060*D | 5 | 1500 | 75 | 63 | 85 | 56.9 | 0.64 | 22.06
DSG060*D | 5 | 1500 | 75 | 67 | 85 | 58.7 | 0.53 | 18.77
DSG060*D | 5 | 1500 | 75 | 71 | 85 | 61.4 | 0.4 | 15.4
DSG060*D | 5 | 1500 | 75 | 59 | 95 | 53.5 | 0.73 | 23.56
DSG060*D | 5 | 1500 | 75 | 63 | 95 | 54.3 | 0.66 | 21.8
DSG060*D | 5 | 1500 | 75 | 67 | 95 | 56.1 | 0.54 | 18.51
DSG060*D | 5 | 1500 | 75 | 71 | 95 | 58.7 | 0.4 | 15.1
DSG060*D | 5 | 1500 | 75 | 59 | 105 | 50.3 | 0.77 | 23.33
DSG060*D | 5 | 1500 | 75 | 63 | 105 | 51.1 | 0.7 | 21.56
DSG060*D | 5 | 1500 | 75 | 67 | 105 | 52.8 | 0.57 | 18.27
DSG060*D | 5 | 1500 | 75 | 71 | 105 | 55.5 | 0.4 | 14.9
DSG060*D | 5 | 1500 | 75 | 59 | 115 | 47.3 | 0.85 | 24.43
DSG060*D | 5 | 1500 | 75 | 63 | 115 | 48.2 | 0.78 | 22.67
DSG060*D | 5 | 1500 | 75 | 67 | 115 | 49.9 | 0.64 | 19.38
DSG060*D | 5 | 1500 | 75 | 71 | 115 | 52.6 | 0.5 | 16
DSG060*D | 5 | 1500 | 80 | 59 | 65 | 58.5 | 0.78 | 27.53
DSG060*D | 5 | 1500 | 80 | 63 | 65 | 59.3 | 0.72 | 25.77
DSG060*D | 5 | 1500 | 80 | 67 | 65 | 61 | 0.61 | 22.48
DSG060*D | 5 | 1500 | 80 | 71 | 65 | 63.7 | 0.5 | 19.1
DSG060*D | 5 | 1500 | 80 | 59 | 75 | 57.9 | 0.78 | 27.48
DSG060*D | 5 | 1500 | 80 | 63 | 75 | 58.8 | 0.72 | 25.72
DSG060*D | 5 | 1500 | 80 | 67 | 75 | 60.5 | 0.61 | 22.43
DSG060*D | 5 | 1500 | 80 | 71 | 75 | 63.2 | 0.5 | 19
DSG060*D | 5 | 1500 | 80 | 59 | 85 | 56.4 | 0.81 | 27.73
DSG060*D | 5 | 1500 | 80 | 63 | 85 | 57.2 | 0.75 | 25.97
DSG060*D | 5 | 1500 | 80 | 67 | 85 | 59 | 0.63 | 22.67
DSG060*D | 5 | 1500 | 80 | 71 | 85 | 61.7 | 0.5 | 19.3
DSG060*D | 5 | 1500 | 80 | 59 | 95 | 53.8 | 0.84 | 27.46
DSG060*D | 5 | 1500 | 80 | 63 | 95 | 54.6 | 0.78 | 25.7
DSG060*D | 5 | 1500 | 80 | 67 | 95 | 56.4 | 0.66 | 22.41
DSG060*D | 5 | 1500 | 80 | 71 | 95 | 59 | 0.5 | 19
DSG060*D | 5 | 1500 | 80 | 59 | 105 | 50.6 | 0.89 | 27.23
DSG060*D | 5 | 1500 | 80 | 63 | 105 | 51.4 | 0.82 | 25.46
DSG060*D | 5 | 1500 | 80 | 67 | 105 | 53.2 | 0.69 | 22.17
DSG060*D | 5 | 1500 | 80 | 71 | 105 | 55.8 | 0.6 | 18.8
DSG060*D | 5 | 1500 | 80 | 59 | 115 | 47.6 | 0.98 | 28.33
DSG060*D | 5 | 1500 | 80 | 63 | 115 | 48.5 | 0.9 | 26.57
DSG060*D | 5 | 1500 | 80 | 67 | 115 | 50.2 | 0.76 | 23.28
DSG060*D | 5 | 1500 | 80 | 71 | 115 | 52.9 | 0.6 | 19.9
DSG060*D | 5 | 1500 | 85 | 59 | 65 | 59.5 | 0.86 | 30.99
DSG060*D | 5 | 1500 | 85 | 63 | 65 | 60.3 | 0.8 | 29.23
DSG060*D | 5 | 1500 | 85 | 67 | 65 | 62 | 0.69 | 25.94
DSG060*D | 5 | 1500 | 85 | 71 | 65 | 64.7 | 0.6 | 22.5
DSG060*D | 5 | 1500 | 85 | 59 | 75 | 58.9 | 0.87 | 30.94
DSG060*D | 5 | 1500 | 85 | 63 | 75 | 59.8 | 0.81 | 29.18
DSG060*D | 5 | 1500 | 85 | 67 | 75 | 61.5 | 0.69 | 25.89
DSG060*D | 5 | 1500 | 85 | 71 | 75 | 64.2 | 0.6 | 22.5
DSG060*D | 5 | 1500 | 85 | 59 | 85 | 57.4 | 0.9 | 31.19
DSG060*D | 5 | 1500 | 85 | 63 | 85 | 58.2 | 0.83 | 29.43
DSG060*D | 5 | 1500 | 85 | 67 | 85 | 60 | 0.72 | 26.14
DSG060*D | 5 | 1500 | 85 | 71 | 85 | 62.6 | 0.6 | 22.7
DSG060*D | 5 | 1500 | 85 | 59 | 95 | 54.8 | 0.93 | 30.92
DSG060*D | 5 | 1500 | 85 | 63 | 95 | 55.6 | 0.87 | 29.16
DSG060*D | 5 | 1500 | 85 | 67 | 95 | 57.3 | 0.74 | 25.87
DSG060*D | 5 | 1500 | 85 | 71 | 95 | 60 | 0.6 | 22.5
DSG060*D | 5 | 1500 | 85 | 59 | 105 | 51.6 | 0.98 | 30.69
DSG060*D | 5 | 1500 | 85 | 63 | 105 | 52.4 | 0.91 | 28.93
DSG060*D | 5 | 1500 | 85 | 67 | 105 | 54.1 | 0.78 | 25.63
DSG060*D | 5 | 1500 | 85 | 71 | 105 | 56.8 | 0.6 | 22.2
DSG060*D | 5 | 1500 | 85 | 59 | 115 | 48.6 | 1 | 29.47
DSG060*D | 5 | 1500 | 85 | 63 | 115 | 49.5 | 1 | 29.97
DSG060*D | 5 | 1500 | 85 | 67 | 115 | 51.2 | 0.86 | 26.74
DSG060*D | 5 | 1500 | 85 | 71 | 115 | 53.9 | 0.7 | 23.3
DSG060*D | 5 | 1860 | 70 | 59 | 65 | 59 | 0.62 | 17.99
DSG060*D | 5 | 1860 | 70 | 63 | 65 | 59.8 | 0.56 | 16.23
DSG060*D | 5 | 1860 | 70 | 67 | 65 | 61.6 | 0.43 | 12.94
DSG060*D | 5 | 1860 | 70 | 59 | 75 | 58.5 | 0.63 | 17.95
DSG060*D | 5 | 1860 | 70 | 63 | 75 | 59.3 | 0.56 | 16.18
DSG060*D | 5 | 1860 | 70 | 67 | 75 | 61 | 0.43 | 12.89
DSG060*D | 5 | 1860 | 70 | 59 | 85 | 56.9 | 0.65 | 18.19
DSG060*D | 5 | 1860 | 70 | 63 | 85 | 57.8 | 0.58 | 16.43
DSG060*D | 5 | 1860 | 70 | 67 | 85 | 59.5 | 0.45 | 13.14
DSG060*D | 5 | 1860 | 70 | 59 | 95 | 54.3 | 0.68 | 17.93
DSG060*D | 5 | 1860 | 70 | 63 | 95 | 55.1 | 0.6 | 16.17
DSG060*D | 5 | 1860 | 70 | 67 | 95 | 56.9 | 0.46 | 12.87
DSG060*D | 5 | 1860 | 70 | 59 | 105 | 51.1 | 0.71 | 17.69
DSG060*D | 5 | 1860 | 70 | 63 | 105 | 51.9 | 0.63 | 15.93
DSG060*D | 5 | 1860 | 70 | 67 | 105 | 53.7 | 0.48 | 12.64
DSG060*D | 5 | 1860 | 70 | 59 | 115 | 48.2 | 0.8 | 18.8
DSG060*D | 5 | 1860 | 70 | 63 | 115 | 49 | 0.71 | 17.03
DSG060*D | 5 | 1860 | 70 | 67 | 115 | 50.7 | 0.55 | 13.74
DSG060*D | 5 | 1860 | 75 | 59 | 65 | 59.3 | 0.75 | 21.87
DSG060*D | 5 | 1860 | 75 | 63 | 65 | 60.1 | 0.68 | 20.11
DSG060*D | 5 | 1860 | 75 | 67 | 65 | 61.9 | 0.56 | 16.82
DSG060*D | 5 | 1860 | 75 | 71 | 65 | 64.5 | 0.4 | 13.4
DSG060*D | 5 | 1860 | 75 | 59 | 75 | 58.8 | 0.76 | 21.82
DSG060*D | 5 | 1860 | 75 | 63 | 75 | 59.6 | 0.69 | 20.06
DSG060*D | 5 | 1860 | 75 | 67 | 75 | 61.4 | 0.56 | 16.77
DSG060*D | 5 | 1860 | 75 | 71 | 75 | 64 | 0.4 | 13.4
DSG060*D | 5 | 1860 | 75 | 59 | 85 | 57.3 | 0.79 | 22.07
DSG060*D | 5 | 1860 | 75 | 63 | 85 | 58.1 | 0.72 | 20.31
DSG060*D | 5 | 1860 | 75 | 67 | 85 | 59.8 | 0.58 | 17.02
DSG060*D | 5 | 1860 | 75 | 71 | 85 | 62.5 | 0.4 | 13.6
DSG060*D | 5 | 1860 | 75 | 59 | 95 | 54.6 | 0.82 | 21.8
DSG060*D | 5 | 1860 | 75 | 63 | 95 | 55.4 | 0.74 | 20.04
DSG060*D | 5 | 1860 | 75 | 67 | 95 | 57.2 | 0.6 | 16.75
DSG060*D | 5 | 1860 | 75 | 71 | 95 | 59.9 | 0.5 | 13.3
DSG060*D | 5 | 1860 | 75 | 59 | 105 | 51.4 | 0.86 | 21.57
DSG060*D | 5 | 1860 | 75 | 63 | 105 | 52.2 | 0.78 | 19.81
DSG060*D | 5 | 1860 | 75 | 67 | 105 | 54 | 0.63 | 16.51
DSG060*D | 5 | 1860 | 75 | 71 | 105 | 56.7 | 0.5 | 13.1
DSG060*D | 5 | 1860 | 75 | 59 | 115 | 48.5 | 0.96 | 22.67
DSG060*D | 5 | 1860 | 75 | 63 | 115 | 49.3 | 0.87 | 20.91
DSG060*D | 5 | 1860 | 75 | 67 | 115 | 51.1 | 0.71 | 17.62
DSG060*D | 5 | 1860 | 75 | 71 | 115 | 53.7 | 0.5 | 14.2
DSG060*D | 5 | 1860 | 80 | 59 | 65 | 59.6 | 0.88 | 25.77
DSG060*D | 5 | 1860 | 80 | 63 | 65 | 60.4 | 0.81 | 24.01
DSG060*D | 5 | 1860 | 80 | 67 | 65 | 62.2 | 0.68 | 20.72
DSG060*D | 5 | 1860 | 80 | 71 | 65 | 64.8 | 0.5 | 17.3
DSG060*D | 5 | 1860 | 80 | 59 | 75 | 59.1 | 0.89 | 25.72
DSG060*D | 5 | 1860 | 80 | 63 | 75 | 59.9 | 0.82 | 23.96
DSG060*D | 5 | 1860 | 80 | 67 | 75 | 61.7 | 0.69 | 20.67
DSG060*D | 5 | 1860 | 80 | 71 | 75 | 64.3 | 0.5 | 17.3
DSG060*D | 5 | 1860 | 80 | 59 | 85 | 57.6 | 0.92 | 25.97
DSG060*D | 5 | 1860 | 80 | 63 | 85 | 58.4 | 0.85 | 24.21
DSG060*D | 5 | 1860 | 80 | 67 | 85 | 60.1 | 0.71 | 20.92
DSG060*D | 5 | 1860 | 80 | 71 | 85 | 62.8 | 0.6 | 17.5
DSG060*D | 5 | 1860 | 80 | 59 | 95 | 54.9 | 0.96 | 25.71
DSG060*D | 5 | 1860 | 80 | 63 | 95 | 55.8 | 0.88 | 23.94
DSG060*D | 5 | 1860 | 80 | 67 | 95 | 57.5 | 0.73 | 20.65
DSG060*D | 5 | 1860 | 80 | 71 | 95 | 60.2 | 0.6 | 17.2
DSG060*D | 5 | 1860 | 80 | 59 | 105 | 51.7 | 1 | 25.28
DSG060*D | 5 | 1860 | 80 | 63 | 105 | 52.5 | 0.92 | 23.71
DSG060*D | 5 | 1860 | 80 | 67 | 105 | 54.3 | 0.77 | 20.42
DSG060*D | 5 | 1860 | 80 | 71 | 105 | 57 | 0.6 | 17
DSG060*D | 5 | 1860 | 80 | 59 | 115 | 48.8 | 1 | 23.84
DSG060*D | 5 | 1860 | 80 | 63 | 115 | 49.6 | 1 | 24.25
DSG060*D | 5 | 1860 | 80 | 67 | 115 | 51.4 | 0.86 | 21.52
DSG060*D | 5 | 1860 | 80 | 71 | 115 | 54 | 0.7 | 18.1
DSG060*D | 5 | 1860 | 85 | 59 | 65 | 60.6 | 0.99 | 29.23
DSG060*D | 5 | 1860 | 85 | 63 | 65 | 61.4 | 0.92 | 27.47
DSG060*D | 5 | 1860 | 85 | 67 | 65 | 63.2 | 0.78 | 24.18
DSG060*D | 5 | 1860 | 85 | 71 | 65 | 65.8 | 0.6 | 20.8
DSG060*D | 5 | 1860 | 85 | 59 | 75 | 60.1 | 0.99 | 29.18
DSG060*D | 5 | 1860 | 85 | 63 | 75 | 60.9 | 0.92 | 27.42
DSG060*D | 5 | 1860 | 85 | 67 | 75 | 62.6 | 0.79 | 24.13
DSG060*D | 5 | 1860 | 85 | 71 | 75 | 65.3 | 0.6 | 20.7
DSG060*D | 5 | 1860 | 85 | 59 | 85 | 58.5 | 1 | 28.61
DSG060*D | 5 | 1860 | 85 | 63 | 85 | 59.4 | 0.95 | 27.67
DSG060*D | 5 | 1860 | 85 | 67 | 85 | 61.1 | 0.82 | 24.38
DSG060*D | 5 | 1860 | 85 | 71 | 85 | 63.8 | 0.7 | 21
DSG060*D | 5 | 1860 | 85 | 59 | 95 | 55.9 | 1 | 27.33
DSG060*D | 5 | 1860 | 85 | 63 | 95 | 56.7 | 0.99 | 27.4
DSG060*D | 5 | 1860 | 85 | 67 | 95 | 58.5 | 0.84 | 24.11
DSG060*D | 5 | 1860 | 85 | 71 | 95 | 61.2 | 0.7 | 20.7
DSG060*D | 5 | 1860 | 85 | 59 | 105 | 52.7 | 1 | 25.76
DSG060*D | 5 | 1860 | 85 | 63 | 105 | 53.5 | 1 | 26.16
DSG060*D | 5 | 1860 | 85 | 67 | 105 | 55.3 | 0.88 | 23.88
DSG060*D | 5 | 1860 | 85 | 71 | 105 | 57.9 | 0.7 | 20.5
DSG060*D | 5 | 1860 | 85 | 59 | 115 | 49.8 | 1 | 24.32
DSG060*D | 5 | 1860 | 85 | 63 | 115 | 50.6 | 1 | 24.73
DSG060*D | 5 | 1860 | 85 | 67 | 115 | 52.3 | 0.98 | 24.98
DSG060*D | 5 | 1860 | 85 | 71 | 115 | 55 | 0.8 | 21.6
DSG060*D | 5 | 2250 | 70 | 59 | 65 | 60.7 | 0.68 | 16.55
DSG060*D | 5 | 2250 | 70 | 63 | 65 | 61.5 | 0.6 | 14.79
DSG060*D | 5 | 2250 | 70 | 67 | 65 | 63.2 | 0.45 | 11.5
DSG060*D | 5 | 2250 | 70 | 59 | 75 | 60.1 | 0.68 | 16.5
DSG060*D | 5 | 2250 | 70 | 63 | 75 | 61 | 0.6 | 14.74
DSG060*D | 5 | 2250 | 70 | 67 | 75 | 62.7 | 0.45 | 11.45
DSG060*D | 5 | 2250 | 70 | 59 | 85 | 58.6 | 0.71 | 16.75
DSG060*D | 5 | 2250 | 70 | 63 | 85 | 59.4 | 0.62 | 14.99
DSG060*D | 5 | 2250 | 70 | 67 | 85 | 61.2 | 0.47 | 11.7
DSG060*D | 5 | 2250 | 70 | 59 | 95 | 56 | 0.73 | 16.49
DSG060*D | 5 | 2250 | 70 | 63 | 95 | 56.8 | 0.64 | 14.72
DSG060*D | 5 | 2250 | 70 | 67 | 95 | 58.5 | 0.48 | 11.43
DSG060*D | 5 | 2250 | 70 | 59 | 105 | 52.8 | 0.76 | 16.25
DSG060*D | 5 | 2250 | 70 | 63 | 105 | 53.6 | 0.67 | 14.49
DSG060*D | 5 | 2250 | 70 | 67 | 105 | 55.3 | 0.5 | 11.2
DSG060*D | 5 | 2250 | 70 | 59 | 115 | 49.8 | 0.86 | 17.35
DSG060*D | 5 | 2250 | 70 | 63 | 115 | 50.7 | 0.76 | 15.59
DSG060*D | 5 | 2250 | 70 | 67 | 115 | 52.4 | 0.58 | 12.3
DSG060*D | 5 | 2250 | 75 | 59 | 65 | 61 | 0.83 | 20.43
DSG060*D | 5 | 2250 | 75 | 63 | 65 | 61.8 | 0.75 | 18.66
DSG060*D | 5 | 2250 | 75 | 67 | 65 | 63.5 | 0.6 | 15.37
DSG060*D | 5 | 2250 | 75 | 71 | 65 | 66.2 | 0.4 | 12
DSG060*D | 5 | 2250 | 75 | 59 | 75 | 60.4 | 0.83 | 20.38
DSG060*D | 5 | 2250 | 75 | 63 | 75 | 61.3 | 0.75 | 18.62
DSG060*D | 5 | 2250 | 75 | 67 | 75 | 63 | 0.6 | 15.33
DSG060*D | 5 | 2250 | 75 | 71 | 75 | 65.7 | 0.4 | 11.9
DSG060*D | 5 | 2250 | 75 | 59 | 85 | 58.9 | 0.87 | 20.63
DSG060*D | 5 | 2250 | 75 | 63 | 85 | 59.7 | 0.78 | 18.86
DSG060*D | 5 | 2250 | 75 | 67 | 85 | 61.5 | 0.63 | 15.57
DSG060*D | 5 | 2250 | 75 | 71 | 85 | 64.1 | 0.5 | 12.2
DSG060*D | 5 | 2250 | 75 | 59 | 95 | 56.3 | 0.9 | 20.36
DSG060*D | 5 | 2250 | 75 | 63 | 95 | 57.1 | 0.81 | 18.6
DSG060*D | 5 | 2250 | 75 | 67 | 95 | 58.8 | 0.64 | 15.31
DSG060*D | 5 | 2250 | 75 | 71 | 95 | 61.5 | 0.5 | 11.9
DSG060*D | 5 | 2250 | 75 | 59 | 105 | 53.1 | 0.94 | 20.13
DSG060*D | 5 | 2250 | 75 | 63 | 105 | 53.9 | 0.84 | 18.36
DSG060*D | 5 | 2250 | 75 | 67 | 105 | 55.6 | 0.67 | 15.07
DSG060*D | 5 | 2250 | 75 | 71 | 105 | 58.3 | 0.5 | 11.7
DSG060*D | 5 | 2250 | 75 | 59 | 115 | 50.1 | 1 | 20.25
DSG060*D | 5 | 2250 | 75 | 63 | 115 | 51 | 0.95 | 19.47
DSG060*D | 5 | 2250 | 75 | 67 | 115 | 52.7 | 0.76 | 16.18
DSG060*D | 5 | 2250 | 75 | 71 | 115 | 55.4 | 0.6 | 12.8
DSG060*D | 5 | 2250 | 80 | 59 | 65 | 61.3 | 0.98 | 24.33
DSG060*D | 5 | 2250 | 80 | 63 | 65 | 62.1 | 0.9 | 22.57
DSG060*D | 5 | 2250 | 80 | 67 | 65 | 63.8 | 0.75 | 19.28
DSG060*D | 5 | 2250 | 80 | 71 | 65 | 66.5 | 0.6 | 15.9
DSG060*D | 5 | 2250 | 80 | 59 | 75 | 60.7 | 0.99 | 24.28
DSG060*D | 5 | 2250 | 80 | 63 | 75 | 61.6 | 0.91 | 22.52
DSG060*D | 5 | 2250 | 80 | 67 | 75 | 63.3 | 0.75 | 19.23
DSG060*D | 5 | 2250 | 80 | 71 | 75 | 66 | 0.6 | 15.8
DSG060*D | 5 | 2250 | 80 | 59 | 85 | 59.2 | 1 | 23.92
DSG060*D | 5 | 2250 | 80 | 63 | 85 | 60 | 0.94 | 22.77
DSG060*D | 5 | 2250 | 80 | 67 | 85 | 61.8 | 0.78 | 19.48
DSG060*D | 5 | 2250 | 80 | 71 | 85 | 64.4 | 0.6 | 16.1
DSG060*D | 5 | 2250 | 80 | 59 | 95 | 56.6 | 1 | 22.86
DSG060*D | 5 | 2250 | 80 | 63 | 95 | 57.4 | 0.97 | 22.5
DSG060*D | 5 | 2250 | 80 | 67 | 95 | 59.2 | 0.8 | 19.21
DSG060*D | 5 | 2250 | 80 | 71 | 95 | 61.8 | 0.6 | 15.8
DSG060*D | 5 | 2250 | 80 | 59 | 105 | 53.4 | 1 | 21.56
DSG060*D | 5 | 2250 | 80 | 63 | 105 | 54.2 | 1 | 21.9
DSG060*D | 5 | 2250 | 80 | 67 | 105 | 55.9 | 0.84 | 18.97
DSG060*D | 5 | 2250 | 80 | 71 | 105 | 58.6 | 0.7 | 15.6
DSG060*D | 5 | 2250 | 80 | 59 | 115 | 50.4 | 1 | 20.38
DSG060*D | 5 | 2250 | 80 | 63 | 115 | 51.3 | 1 | 20.71
DSG060*D | 5 | 2250 | 80 | 67 | 115 | 53 | 0.94 | 20.08
DSG060*D | 5 | 2250 | 80 | 71 | 115 | 55.7 | 0.7 | 16.7
DSG060*D | 5 | 2250 | 85 | 59 | 65 | 62.2 | 1 | 25.15
DSG060*D | 5 | 2250 | 85 | 63 | 65 | 63.1 | 1 | 25.48
DSG060*D | 5 | 2250 | 85 | 67 | 65 | 64.8 | 0.87 | 22.74
DSG060*D | 5 | 2250 | 85 | 71 | 65 | 67.5 | 0.7 | 19.3
DSG060*D | 5 | 2250 | 85 | 59 | 75 | 61.7 | 1 | 24.94
DSG060*D | 5 | 2250 | 85 | 63 | 75 | 62.5 | 1 | 25.27
DSG060*D | 5 | 2250 | 85 | 67 | 75 | 64.3 | 0.87 | 22.69
DSG060*D | 5 | 2250 | 85 | 71 | 75 | 67 | 0.7 | 19.3
DSG060*D | 5 | 2250 | 85 | 59 | 85 | 60.2 | 1 | 24.32
DSG060*D | 5 | 2250 | 85 | 63 | 85 | 61 | 1 | 24.65
DSG060*D | 5 | 2250 | 85 | 67 | 85 | 62.8 | 0.9 | 22.94
DSG060*D | 5 | 2250 | 85 | 71 | 85 | 65.4 | 0.7 | 19.5
DSG060*D | 5 | 2250 | 85 | 59 | 95 | 57.6 | 1 | 23.26
DSG060*D | 5 | 2250 | 85 | 63 | 95 | 58.4 | 1 | 23.59
DSG060*D | 5 | 2250 | 85 | 67 | 95 | 60.1 | 0.93 | 22.67
DSG060*D | 5 | 2250 | 85 | 71 | 95 | 62.8 | 0.8 | 19.3
DSG060*D | 5 | 2250 | 85 | 59 | 105 | 54.4 | 1 | 21.96
DSG060*D | 5 | 2250 | 85 | 63 | 105 | 55.2 | 1 | 22.29
DSG060*D | 5 | 2250 | 85 | 67 | 105 | 56.9 | 0.98 | 22.43
DSG060*D | 5 | 2250 | 85 | 71 | 105 | 59.6 | 0.8 | 19
DSG060*D | 5 | 2250 | 85 | 59 | 115 | 51.4 | 1 | 20.78
DSG060*D | 5 | 2250 | 85 | 63 | 115 | 52.2 | 1 | 21.11
DSG060*D | 5 | 2250 | 85 | 67 | 115 | 54 | 1 | 21.82
DSG060*D | 5 | 2250 | 85 | 71 | 115 | 56.7 | 0.9 | 20.1
DSG072*D | 6 | 1800 | 70 | 59 | 65 | 69.8 | 0.55 | 19.23
DSG072*D | 6 | 1800 | 70 | 63 | 65 | 70.7 | 0.49 | 17.47
DSG072*D | 6 | 1800 | 70 | 67 | 65 | 72.8 | 0.39 | 14.18
DSG072*D | 6 | 1800 | 70 | 59 | 75 | 69.1 | 0.55 | 19.18
DSG072*D | 6 | 1800 | 70 | 63 | 75 | 70.1 | 0.49 | 17.42
DSG072*D | 6 | 1800 | 70 | 67 | 75 | 72.2 | 0.39 | 14.13
DSG072*D | 6 | 1800 | 70 | 59 | 85 | 67.3 | 0.57 | 19.43
DSG072*D | 6 | 1800 | 70 | 63 | 85 | 68.3 | 0.51 | 17.67
DSG072*D | 6 | 1800 | 70 | 67 | 85 | 70.4 | 0.4 | 14.38
DSG072*D | 6 | 1800 | 70 | 59 | 95 | 64.1 | 0.59 | 19.16
DSG072*D | 6 | 1800 | 70 | 63 | 95 | 65.1 | 0.53 | 17.4
DSG072*D | 6 | 1800 | 70 | 67 | 95 | 67.2 | 0.42 | 14.11
DSG072*D | 6 | 1800 | 70 | 59 | 105 | 60.3 | 0.62 | 18.93
DSG072*D | 6 | 1800 | 70 | 63 | 105 | 61.3 | 0.55 | 17.17
DSG072*D | 6 | 1800 | 70 | 67 | 105 | 63.4 | 0.43 | 13.88
DSG072*D | 6 | 1800 | 70 | 59 | 115 | 56.8 | 0.7 | 20.03
DSG072*D | 6 | 1800 | 70 | 63 | 115 | 57.8 | 0.63 | 18.27
DSG072*D | 6 | 1800 | 70 | 67 | 115 | 59.9 | 0.5 | 14.98
DSG072*D | 6 | 1800 | 75 | 59 | 65 | 70.1 | 0.65 | 23.11
DSG072*D | 6 | 1800 | 75 | 63 | 65 | 71.1 | 0.59 | 21.34
DSG072*D | 6 | 1800 | 75 | 67 | 65 | 73.2 | 0.49 | 18.05
DSG072*D | 6 | 1800 | 75 | 71 | 65 | 76.4 | 0.4 | 14.6
DSG072*D | 6 | 1800 | 75 | 59 | 75 | 69.5 | 0.66 | 23.06
DSG072*D | 6 | 1800 | 75 | 63 | 75 | 70.5 | 0.6 | 21.3
DSG072*D | 6 | 1800 | 75 | 67 | 75 | 72.6 | 0.49 | 18
DSG072*D | 6 | 1800 | 75 | 71 | 75 | 75.8 | 0.4 | 14.6
DSG072*D | 6 | 1800 | 75 | 59 | 85 | 67.7 | 0.68 | 23.31
DSG072*D | 6 | 1800 | 75 | 63 | 85 | 68.7 | 0.62 | 21.54
DSG072*D | 6 | 1800 | 75 | 67 | 85 | 70.7 | 0.51 | 18.25
DSG072*D | 6 | 1800 | 75 | 71 | 85 | 74 | 0.4 | 14.8
DSG072*D | 6 | 1800 | 75 | 59 | 95 | 64.5 | 0.71 | 23.04
DSG072*D | 6 | 1800 | 75 | 63 | 95 | 65.5 | 0.64 | 21.28
DSG072*D | 6 | 1800 | 75 | 67 | 95 | 67.6 | 0.53 | 17.99
DSG072*D | 6 | 1800 | 75 | 71 | 95 | 70.8 | 0.4 | 14.6
DSG072*D | 6 | 1800 | 75 | 59 | 105 | 60.7 | 0.74 | 22.81
DSG072*D | 6 | 1800 | 75 | 63 | 105 | 61.6 | 0.68 | 21.04
DSG072*D | 6 | 1800 | 75 | 67 | 105 | 63.7 | 0.55 | 17.75
DSG072*D | 6 | 1800 | 75 | 71 | 105 | 66.9 | 0.4 | 14.3
DSG072*D | 6 | 1800 | 75 | 59 | 115 | 57.1 | 0.83 | 23.91
DSG072*D | 6 | 1800 | 75 | 63 | 115 | 58.1 | 0.75 | 22.15
DSG072*D | 6 | 1800 | 75 | 67 | 115 | 60.2 | 0.62 | 18.85
DSG072*D | 6 | 1800 | 75 | 71 | 115 | 63.4 | 0.5 | 15.4
DSG072*D | 6 | 1800 | 80 | 59 | 65 | 70.5 | 0.76 | 27.01
DSG072*D | 6 | 1800 | 80 | 63 | 65 | 71.5 | 0.7 | 25.25
DSG072*D | 6 | 1800 | 80 | 67 | 65 | 73.6 | 0.59 | 21.95
DSG072*D | 6 | 1800 | 80 | 71 | 65 | 76.8 | 0.5 | 18.5
DSG072*D | 6 | 1800 | 80 | 59 | 75 | 69.9 | 0.76 | 26.96
DSG072*D | 6 | 1800 | 80 | 63 | 75 | 70.8 | 0.7 | 25.2
DSG072*D | 6 | 1800 | 80 | 67 | 75 | 72.9 | 0.59 | 21.91
DSG072*D | 6 | 1800 | 80 | 71 | 75 | 76.1 | 0.5 | 18.5
DSG072*D | 6 | 1800 | 80 | 59 | 85 | 68 | 0.79 | 27.21
DSG072*D | 6 | 1800 | 80 | 63 | 85 | 69 | 0.73 | 25.45
DSG072*D | 6 | 1800 | 80 | 67 | 85 | 71.1 | 0.62 | 22.15
DSG072*D | 6 | 1800 | 80 | 71 | 85 | 74.3 | 0.5 | 18.7
DSG072*D | 6 | 1800 | 80 | 59 | 95 | 64.9 | 0.82 | 26.94
DSG072*D | 6 | 1800 | 80 | 63 | 95 | 65.9 | 0.76 | 25.18
DSG072*D | 6 | 1800 | 80 | 67 | 95 | 68 | 0.64 | 21.89
DSG072*D | 6 | 1800 | 80 | 71 | 95 | 71.2 | 0.5 | 18.5
DSG072*D | 6 | 1800 | 80 | 59 | 105 | 61 | 0.87 | 26.71
DSG072*D | 6 | 1800 | 80 | 63 | 105 | 62 | 0.8 | 24.94
DSG072*D | 6 | 1800 | 80 | 67 | 105 | 64.1 | 0.67 | 21.65
DSG072*D | 6 | 1800 | 80 | 71 | 105 | 67.3 | 0.5 | 18.2
DSG072*D | 6 | 1800 | 80 | 59 | 115 | 57.5 | 0.96 | 27.81
DSG072*D | 6 | 1800 | 80 | 63 | 115 | 58.5 | 0.88 | 26.05
DSG072*D | 6 | 1800 | 80 | 67 | 115 | 60.6 | 0.74 | 22.76
DSG072*D | 6 | 1800 | 80 | 71 | 115 | 63.8 | 0.6 | 19.3
DSG072*D | 6 | 1800 | 85 | 59 | 65 | 71.7 | 0.84 | 30.47
DSG072*D | 6 | 1800 | 85 | 63 | 65 | 72.7 | 0.78 | 28.71
DSG072*D | 6 | 1800 | 85 | 67 | 65 | 74.8 | 0.67 | 25.42
DSG072*D | 6 | 1800 | 85 | 71 | 65 | 78 | 0.6 | 22
DSG072*D | 6 | 1800 | 85 | 59 | 75 | 71 | 0.85 | 30.42
DSG072*D | 6 | 1800 | 85 | 63 | 75 | 72 | 0.79 | 28.66
DSG072*D | 6 | 1800 | 85 | 67 | 75 | 74.1 | 0.68 | 25.37
DSG072*D | 6 | 1800 | 85 | 71 | 75 | 77.3 | 0.6 | 22
DSG072*D | 6 | 1800 | 85 | 59 | 85 | 69.2 | 0.88 | 30.67
DSG072*D | 6 | 1800 | 85 | 63 | 85 | 70.2 | 0.82 | 28.91
DSG072*D | 6 | 1800 | 85 | 67 | 85 | 72.3 | 0.7 | 25.62
DSG072*D | 6 | 1800 | 85 | 71 | 85 | 75.5 | 0.6 | 22.2
DSG072*D | 6 | 1800 | 85 | 59 | 95 | 66.1 | 0.91 | 30.4
DSG072*D | 6 | 1800 | 85 | 63 | 95 | 67 | 0.85 | 28.64
DSG072*D | 6 | 1800 | 85 | 67 | 95 | 69.1 | 0.73 | 25.35
DSG072*D | 6 | 1800 | 85 | 71 | 95 | 72.3 | 0.6 | 21.9
DSG072*D | 6 | 1800 | 85 | 59 | 105 | 62.2 | 0.96 | 30.17
DSG072*D | 6 | 1800 | 85 | 63 | 105 | 63.2 | 0.89 | 28.4
DSG072*D | 6 | 1800 | 85 | 67 | 105 | 65.3 | 0.76 | 25.11
DSG072*D | 6 | 1800 | 85 | 71 | 105 | 68.5 | 0.6 | 21.7
DSG072*D | 6 | 1800 | 85 | 59 | 115 | 58.7 | 1 | 29.64
DSG072*D | 6 | 1800 | 85 | 63 | 115 | 59.7 | 0.98 | 29.51
DSG072*D | 6 | 1800 | 85 | 67 | 115 | 61.8 | 0.84 | 26.22
DSG072*D | 6 | 1800 | 85 | 71 | 115 | 65 | 0.7 | 22.8
DSG072*D | 6 | 2100 | 70 | 59 | 65 | 70.8 | 0.59 | 17.99
DSG072*D | 6 | 2100 | 70 | 63 | 65 | 71.8 | 0.52 | 16.23
DSG072*D | 6 | 2100 | 70 | 67 | 65 | 73.9 | 0.4 | 12.94
DSG072*D | 6 | 2100 | 70 | 59 | 75 | 70.2 | 0.59 | 17.95
DSG072*D | 6 | 2100 | 70 | 63 | 75 | 71.2 | 0.53 | 16.18
DSG072*D | 6 | 2100 | 70 | 67 | 75 | 73.3 | 0.41 | 12.89
DSG072*D | 6 | 2100 | 70 | 59 | 85 | 68.3 | 0.62 | 18.19
DSG072*D | 6 | 2100 | 70 | 63 | 85 | 69.3 | 0.55 | 16.43
DSG072*D | 6 | 2100 | 70 | 67 | 85 | 71.4 | 0.42 | 13.14
DSG072*D | 6 | 2100 | 70 | 59 | 95 | 65.2 | 0.64 | 17.93
DSG072*D | 6 | 2100 | 70 | 63 | 95 | 66.2 | 0.56 | 16.17
DSG072*D | 6 | 2100 | 70 | 67 | 95 | 68.3 | 0.44 | 12.87
DSG072*D | 6 | 2100 | 70 | 59 | 105 | 61.3 | 0.67 | 17.69
DSG072*D | 6 | 2100 | 70 | 63 | 105 | 62.3 | 0.59 | 15.93
DSG072*D | 6 | 2100 | 70 | 67 | 105 | 64.4 | 0.45 | 12.64
DSG072*D | 6 | 2100 | 70 | 59 | 115 | 57.8 | 0.75 | 18.8
DSG072*D | 6 | 2100 | 70 | 63 | 115 | 58.8 | 0.67 | 17.03
DSG072*D | 6 | 2100 | 70 | 67 | 115 | 60.9 | 0.52 | 13.74
DSG072*D | 6 | 2100 | 75 | 59 | 65 | 71.2 | 0.71 | 21.87
DSG072*D | 6 | 2100 | 75 | 63 | 65 | 72.2 | 0.64 | 20.11
DSG072*D | 6 | 2100 | 75 | 67 | 65 | 74.3 | 0.52 | 16.82
DSG072*D | 6 | 2100 | 75 | 71 | 65 | 77.5 | 0.4 | 13.4
DSG072*D | 6 | 2100 | 75 | 59 | 75 | 70.5 | 0.71 | 21.82
DSG072*D | 6 | 2100 | 75 | 63 | 75 | 71.5 | 0.65 | 20.06
DSG072*D | 6 | 2100 | 75 | 67 | 75 | 73.6 | 0.53 | 16.77
DSG072*D | 6 | 2100 | 75 | 71 | 75 | 76.8 | 0.4 | 13.4
DSG072*D | 6 | 2100 | 75 | 59 | 85 | 68.7 | 0.74 | 22.07
DSG072*D | 6 | 2100 | 75 | 63 | 85 | 69.7 | 0.67 | 20.31
DSG072*D | 6 | 2100 | 75 | 67 | 85 | 71.8 | 0.55 | 17.02
DSG072*D | 6 | 2100 | 75 | 71 | 85 | 75 | 0.4 | 13.6
DSG072*D | 6 | 2100 | 75 | 59 | 95 | 65.5 | 0.77 | 21.8
DSG072*D | 6 | 2100 | 75 | 63 | 95 | 66.5 | 0.7 | 20.04
DSG072*D | 6 | 2100 | 75 | 67 | 95 | 68.6 | 0.56 | 16.75
DSG072*D | 6 | 2100 | 75 | 71 | 95 | 71.8 | 0.4 | 13.3
DSG072*D | 6 | 2100 | 75 | 59 | 105 | 61.7 | 0.81 | 21.57
DSG072*D | 6 | 2100 | 75 | 63 | 105 | 62.7 | 0.73 | 19.81
DSG072*D | 6 | 2100 | 75 | 67 | 105 | 64.8 | 0.59 | 16.51
DSG072*D | 6 | 2100 | 75 | 71 | 105 | 68 | 0.4 | 13.1
DSG072*D | 6 | 2100 | 75 | 59 | 115 | 58.2 | 0.9 | 22.67
DSG072*D | 6 | 2100 | 75 | 63 | 115 | 59.2 | 0.82 | 20.91
DSG072*D | 6 | 2100 | 75 | 67 | 115 | 61.3 | 0.66 | 17.62
DSG072*D | 6 | 2100 | 75 | 71 | 115 | 64.5 | 0.5 | 14.2
DSG072*D | 6 | 2100 | 80 | 59 | 65 | 71.5 | 0.83 | 25.77
DSG072*D | 6 | 2100 | 80 | 63 | 65 | 72.5 | 0.76 | 24.01
DSG072*D | 6 | 2100 | 80 | 67 | 65 | 74.6 | 0.64 | 20.72
DSG072*D | 6 | 2100 | 80 | 71 | 65 | 77.8 | 0.5 | 17.3
DSG072*D | 6 | 2100 | 80 | 59 | 75 | 70.9 | 0.84 | 25.72
DSG072*D | 6 | 2100 | 80 | 63 | 75 | 71.9 | 0.77 | 23.96
DSG072*D | 6 | 2100 | 80 | 67 | 75 | 74 | 0.65 | 20.67
DSG072*D | 6 | 2100 | 80 | 71 | 75 | 77.2 | 0.5 | 17.3
DSG072*D | 6 | 2100 | 80 | 59 | 85 | 69.1 | 0.87 | 25.97
DSG072*D | 6 | 2100 | 80 | 63 | 85 | 70.1 | 0.8 | 24.21
DSG072*D | 6 | 2100 | 80 | 67 | 85 | 72.2 | 0.67 | 20.92
DSG072*D | 6 | 2100 | 80 | 71 | 85 | 75.4 | 0.5 | 17.5
DSG072*D | 6 | 2100 | 80 | 59 | 95 | 65.9 | 0.9 | 25.71
DSG072*D | 6 | 2100 | 80 | 63 | 95 | 66.9 | 0.83 | 23.94
DSG072*D | 6 | 2100 | 80 | 67 | 95 | 69 | 0.69 | 20.65
DSG072*D | 6 | 2100 | 80 | 71 | 95 | 72.2 | 0.6 | 17.2
DSG072*D | 6 | 2100 | 80 | 59 | 105 | 62.1 | 0.95 | 25.47
DSG072*D | 6 | 2100 | 80 | 63 | 105 | 63 | 0.87 | 23.71
DSG072*D | 6 | 2100 | 80 | 67 | 105 | 65.1 | 0.72 | 20.42
DSG072*D | 6 | 2100 | 80 | 71 | 105 | 68.3 | 0.6 | 17
DSG072*D | 6 | 2100 | 80 | 59 | 115 | 58.5 | 1 | 25.34
DSG072*D | 6 | 2100 | 80 | 63 | 115 | 59.5 | 0.96 | 24.81
DSG072*D | 6 | 2100 | 80 | 67 | 115 | 61.6 | 0.81 | 21.52
DSG072*D | 6 | 2100 | 80 | 71 | 115 | 64.8 | 0.6 | 18.1
DSG072*D | 6 | 2100 | 85 | 59 | 65 | 72.7 | 0.93 | 29.23
DSG072*D | 6 | 2100 | 85 | 63 | 65 | 73.7 | 0.86 | 27.47
DSG072*D | 6 | 2100 | 85 | 67 | 65 | 75.8 | 0.74 | 24.18
DSG072*D | 6 | 2100 | 85 | 71 | 65 | 79 | 0.6 | 20.8
DSG072*D | 6 | 2100 | 85 | 59 | 75 | 72.1 | 0.94 | 29.18
DSG072*D | 6 | 2100 | 85 | 63 | 75 | 73.1 | 0.87 | 27.42
DSG072*D | 6 | 2100 | 85 | 67 | 75 | 75.2 | 0.74 | 24.13
DSG072*D | 6 | 2100 | 85 | 71 | 75 | 78.4 | 0.6 | 20.7
DSG072*D | 6 | 2100 | 85 | 59 | 85 | 70.2 | 0.97 | 29.43
DSG072*D | 6 | 2100 | 85 | 63 | 85 | 71.2 | 0.9 | 27.67
DSG072*D | 6 | 2100 | 85 | 67 | 85 | 73.3 | 0.77 | 24.38
DSG072*D | 6 | 2100 | 85 | 71 | 85 | 76.5 | 0.6 | 21
DSG072*D | 6 | 2100 | 85 | 59 | 95 | 67.1 | 1 | 29.04
DSG072*D | 6 | 2100 | 85 | 63 | 95 | 68.1 | 0.93 | 27.4
DSG072*D | 6 | 2100 | 85 | 67 | 95 | 70.2 | 0.79 | 24.11
DSG072*D | 6 | 2100 | 85 | 71 | 95 | 73.4 | 0.7 | 20.7
DSG072*D | 6 | 2100 | 85 | 59 | 105 | 63.2 | 1 | 27.38
DSG072*D | 6 | 2100 | 85 | 63 | 105 | 64.2 | 0.98 | 27.17
DSG072*D | 6 | 2100 | 85 | 67 | 105 | 66.3 | 0.83 | 23.88
DSG072*D | 6 | 2100 | 85 | 71 | 105 | 69.5 | 0.7 | 20.5
DSG072*D | 6 | 2100 | 85 | 59 | 115 | 59.7 | 1 | 25.85
DSG072*D | 6 | 2100 | 85 | 63 | 115 | 60.7 | 1 | 26.28
DSG072*D | 6 | 2100 | 85 | 67 | 115 | 62.8 | 0.92 | 24.98
DSG072*D | 6 | 2100 | 85 | 71 | 115 | 66 | 0.8 | 21.6
DSG072*D | 6 | 2700 | 70 | 59 | 65 | 73.7 | 0.65 | 16.09
DSG072*D | 6 | 2700 | 70 | 63 | 65 | 74.7 | 0.57 | 14.33
DSG072*D | 6 | 2700 | 70 | 67 | 65 | 76.8 | 0.43 | 11.03
DSG072*D | 6 | 2700 | 70 | 59 | 75 | 73 | 0.65 | 16.04
DSG072*D | 6 | 2700 | 70 | 63 | 75 | 74 | 0.57 | 14.28
DSG072*D | 6 | 2700 | 70 | 67 | 75 | 76.1 | 0.43 | 10.99
DSG072*D | 6 | 2700 | 70 | 59 | 85 | 71.2 | 0.68 | 16.29
DSG072*D | 6 | 2700 | 70 | 63 | 85 | 72.2 | 0.6 | 14.53
DSG072*D | 6 | 2700 | 70 | 67 | 85 | 74.3 | 0.45 | 11.23
DSG072*D | 6 | 2700 | 70 | 59 | 95 | 68 | 0.7 | 16.02
DSG072*D | 6 | 2700 | 70 | 63 | 95 | 69 | 0.61 | 14.26
DSG072*D | 6 | 2700 | 70 | 67 | 95 | 71.1 | 0.46 | 10.97
DSG072*D | 6 | 2700 | 70 | 59 | 105 | 64.2 | 0.73 | 15.79
DSG072*D | 6 | 2700 | 70 | 63 | 105 | 65.2 | 0.64 | 14.02
DSG072*D | 6 | 2700 | 70 | 67 | 105 | 67.3 | 0.47 | 10.73
DSG072*D | 6 | 2700 | 70 | 59 | 115 | 60.7 | 0.83 | 16.89
DSG072*D | 6 | 2700 | 70 | 63 | 115 | 61.7 | 0.73 | 15.13
DSG072*D | 6 | 2700 | 70 | 67 | 115 | 63.8 | 0.55 | 11.84
DSG072*D | 6 | 2700 | 75 | 59 | 65 | 74 | 0.8 | 19.96
DSG072*D | 6 | 2700 | 75 | 63 | 65 | 75 | 0.72 | 18.2
DSG072*D | 6 | 2700 | 75 | 67 | 65 | 77.1 | 0.57 | 14.91
DSG072*D | 6 | 2700 | 75 | 71 | 65 | 80.3 | 0.4 | 11.5
DSG072*D | 6 | 2700 | 75 | 59 | 75 | 73.4 | 0.81 | 19.92
DSG072*D | 6 | 2700 | 75 | 63 | 75 | 74.4 | 0.72 | 18.15
DSG072*D | 6 | 2700 | 75 | 67 | 75 | 76.5 | 0.58 | 14.86
DSG072*D | 6 | 2700 | 75 | 71 | 75 | 79.7 | 0.4 | 11.5
DSG072*D | 6 | 2700 | 75 | 59 | 85 | 71.6 | 0.84 | 20.16
DSG072*D | 6 | 2700 | 75 | 63 | 85 | 72.6 | 0.75 | 18.4
DSG072*D | 6 | 2700 | 75 | 67 | 85 | 74.7 | 0.6 | 15.11
DSG072*D | 6 | 2700 | 75 | 71 | 85 | 77.9 | 0.4 | 11.7
DSG072*D | 6 | 2700 | 75 | 59 | 95 | 68.4 | 0.86 | 19.9
DSG072*D | 6 | 2700 | 75 | 63 | 95 | 69.4 | 0.78 | 18.14
DSG072*D | 6 | 2700 | 75 | 67 | 95 | 71.5 | 0.62 | 14.84
DSG072*D | 6 | 2700 | 75 | 71 | 95 | 74.7 | 0.5 | 11.4
DSG072*D | 6 | 2700 | 75 | 59 | 105 | 64.6 | 0.9 | 19.66
DSG072*D | 6 | 2700 | 75 | 63 | 105 | 65.5 | 0.81 | 17.9
DSG072*D | 6 | 2700 | 75 | 67 | 105 | 67.6 | 0.64 | 14.61
DSG072*D | 6 | 2700 | 75 | 71 | 105 | 70.8 | 0.5 | 11.2
DSG072*D | 6 | 2700 | 75 | 59 | 115 | 61 | 1 | 20.55
DSG072*D | 6 | 2700 | 75 | 63 | 115 | 62 | 0.91 | 19
DSG072*D | 6 | 2700 | 75 | 67 | 115 | 64.1 | 0.73 | 15.71
DSG072*D | 6 | 2700 | 75 | 71 | 115 | 67.3 | 0.5 | 12.3
DSG072*D | 6 | 2700 | 80 | 59 | 65 | 74.4 | 0.95 | 23.87
DSG072*D | 6 | 2700 | 80 | 63 | 65 | 75.4 | 0.87 | 22.1
DSG072*D | 6 | 2700 | 80 | 67 | 65 | 77.5 | 0.72 | 18.81
DSG072*D | 6 | 2700 | 80 | 71 | 65 | 80.7 | 0.6 | 15.4
DSG072*D | 6 | 2700 | 80 | 59 | 75 | 73.8 | 0.96 | 23.82
DSG072*D | 6 | 2700 | 80 | 63 | 75 | 74.8 | 0.88 | 22.06
DSG072*D | 6 | 2700 | 80 | 67 | 75 | 76.9 | 0.73 | 18.76
DSG072*D | 6 | 2700 | 80 | 71 | 75 | 80.1 | 0.6 | 15.4
DSG072*D | 6 | 2700 | 80 | 59 | 85 | 71.9 | 0.99 | 24.07
DSG072*D | 6 | 2700 | 80 | 63 | 85 | 72.9 | 0.91 | 22.3
DSG072*D | 6 | 2700 | 80 | 67 | 85 | 75 | 0.75 | 19.01
DSG072*D | 6 | 2700 | 80 | 71 | 85 | 78.2 | 0.6 | 15.6
DSG072*D | 6 | 2700 | 80 | 59 | 95 | 68.8 | 1 | 23.16
DSG072*D | 6 | 2700 | 80 | 63 | 95 | 69.8 | 0.94 | 22.04
DSG072*D | 6 | 2700 | 80 | 67 | 95 | 71.9 | 0.77 | 18.75
DSG072*D | 6 | 2700 | 80 | 71 | 95 | 75.1 | 0.6 | 15.3
DSG072*D | 6 | 2700 | 80 | 59 | 105 | 64.9 | 1 | 21.86
DSG072*D | 6 | 2700 | 80 | 63 | 105 | 65.9 | 0.98 | 21.8
DSG072*D | 6 | 2700 | 80 | 67 | 105 | 68 | 0.81 | 18.51
DSG072*D | 6 | 2700 | 80 | 71 | 105 | 71.2 | 0.6 | 15.1
DSG072*D | 6 | 2700 | 80 | 59 | 115 | 61.4 | 1 | 20.67
DSG072*D | 6 | 2700 | 80 | 63 | 115 | 62.4 | 1 | 21.01
DSG072*D | 6 | 2700 | 80 | 67 | 115 | 64.5 | 0.9 | 19.61
DSG072*D | 6 | 2700 | 80 | 71 | 115 | 67.7 | 0.7 | 16.2
DSG072*D | 6 | 2700 | 85 | 59 | 65 | 75.6 | 1 | 25.45
DSG072*D | 6 | 2700 | 85 | 63 | 65 | 76.6 | 0.99 | 25.56
DSG072*D | 6 | 2700 | 85 | 67 | 65 | 78.7 | 0.84 | 22.27
DSG072*D | 6 | 2700 | 85 | 71 | 65 | 81.9 | 0.7 | 18.9
DSG072*D | 6 | 2700 | 85 | 59 | 75 | 74.9 | 1 | 25.23
DSG072*D | 6 | 2700 | 85 | 63 | 75 | 75.9 | 1 | 25.52
DSG072*D | 6 | 2700 | 85 | 67 | 75 | 78 | 0.85 | 22.22
DSG072*D | 6 | 2700 | 85 | 71 | 75 | 81.2 | 0.7 | 18.8
DSG072*D | 6 | 2700 | 85 | 59 | 85 | 73.1 | 1 | 24.62
DSG072*D | 6 | 2700 | 85 | 63 | 85 | 74.1 | 1 | 24.95
DSG072*D | 6 | 2700 | 85 | 67 | 85 | 76.2 | 0.88 | 22.47
DSG072*D | 6 | 2700 | 85 | 71 | 85 | 79.4 | 0.7 | 19.1
DSG072*D | 6 | 2700 | 85 | 59 | 95 | 70 | 1 | 23.55
DSG072*D | 6 | 2700 | 85 | 63 | 95 | 70.9 | 1 | 23.89
DSG072*D | 6 | 2700 | 85 | 67 | 95 | 73 | 0.9 | 22.21
DSG072*D | 6 | 2700 | 85 | 71 | 95 | 76.2 | 0.7 | 18.8
DSG072*D | 6 | 2700 | 85 | 59 | 105 | 66.1 | 1 | 22.26
DSG072*D | 6 | 2700 | 85 | 63 | 105 | 67.1 | 1 | 22.59
DSG072*D | 6 | 2700 | 85 | 67 | 105 | 69.2 | 0.94 | 21.97
DSG072*D | 6 | 2700 | 85 | 71 | 105 | 72.4 | 0.8 | 18.6
DSG072*D | 6 | 2700 | 85 | 59 | 115 | 62.6 | 1 | 21.07
DSG072*D | 6 | 2700 | 85 | 63 | 115 | 63.6 | 1 | 21.41
DSG072*D | 6 | 2700 | 85 | 67 | 115 | 65.7 | 1 | 22.11
DSG072*D | 6 | 2700 | 85 | 71 | 115 | 68.9 | 0.8 | 19.7
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 59 | 65 | 50.4 | 0.51 | 18.56
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 63 | 65 | 51.1 | 0.46 | 16.86
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 67 | 65 | 52.6 | 0.36 | 13.68
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 59 | 75 | 49.9 | 0.51 | 18.51
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 63 | 75 | 50.6 | 0.46 | 16.81
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 67 | 75 | 52.2 | 0.36 | 13.63
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 59 | 85 | 48.6 | 0.53 | 18.75
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 63 | 85 | 49.3 | 0.48 | 17.05
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 67 | 85 | 50.8 | 0.38 | 13.87
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 59 | 95 | 46.4 | 0.55 | 18.49
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 63 | 95 | 47.1 | 0.49 | 16.79
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 67 | 95 | 48.6 | 0.39 | 13.62
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 59 | 105 | 43.6 | 0.58 | 18.27
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 63 | 105 | 44.3 | 0.52 | 16.57
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 67 | 105 | 45.8 | 0.41 | 13.39
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 59 | 115 | 41 | 0.65 | 19.33
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 63 | 115 | 41.8 | 0.59 | 17.63
DSG072*D (70% - Low Stage) | 6 | 1260 | 70 | 67 | 115 | 43.3 | 0.46 | 14.45
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 59 | 65 | 50.4 | 0.61 | 22.3
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 63 | 65 | 51.1 | 0.56 | 20.6
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 67 | 65 | 52.6 | 0.46 | 17.42
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 71 | 65 | 54.9 | 0.4 | 14.1
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 59 | 75 | 50 | 0.62 | 22.25
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 63 | 75 | 50.7 | 0.56 | 20.55
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 67 | 75 | 52.2 | 0.46 | 17.37
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 71 | 75 | 54.5 | 0.4 | 14.1
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 59 | 85 | 48.6 | 0.64 | 22.49
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 63 | 85 | 49.4 | 0.58 | 20.79
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 67 | 85 | 50.9 | 0.48 | 17.61
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 71 | 85 | 53.2 | 0.4 | 14.3
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 59 | 95 | 46.4 | 0.66 | 22.23
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 63 | 95 | 47.1 | 0.6 | 20.53
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 67 | 95 | 48.6 | 0.49 | 17.36
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 71 | 95 | 50.9 | 0.4 | 14.1
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 59 | 105 | 43.6 | 0.7 | 22.01
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 63 | 105 | 44.3 | 0.63 | 20.31
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 67 | 105 | 45.8 | 0.52 | 17.13
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 71 | 105 | 48.1 | 0.4 | 13.8
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 59 | 115 | 41.1 | 0.78 | 23.07
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 63 | 115 | 41.8 | 0.71 | 21.37
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 67 | 115 | 43.3 | 0.58 | 18.19
DSG072*D (70% - Low Stage) | 6 | 1260 | 75 | 71 | 115 | 45.6 | 0.5 | 14.9
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 59 | 65 | 50.7 | 0.71 | 26.06
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 63 | 65 | 51.4 | 0.66 | 24.36
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 67 | 65 | 52.9 | 0.56 | 21.19
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 71 | 65 | 55.2 | 0.4 | 17.9
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 59 | 75 | 50.2 | 0.72 | 26.02
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 63 | 75 | 50.9 | 0.66 | 24.32
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 67 | 75 | 52.4 | 0.56 | 21.14
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 71 | 75 | 54.8 | 0.5 | 17.8
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 59 | 85 | 48.9 | 0.74 | 26.26
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 63 | 85 | 49.6 | 0.69 | 24.56
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 67 | 85 | 51.1 | 0.58 | 21.38
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 71 | 85 | 53.4 | 0.5 | 18.1
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 59 | 95 | 46.6 | 0.77 | 26
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 63 | 95 | 47.4 | 0.71 | 24.3
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 67 | 95 | 48.9 | 0.6 | 21.12
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 71 | 95 | 51.2 | 0.5 | 17.8
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 59 | 105 | 43.9 | 0.81 | 25.77
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 63 | 105 | 44.6 | 0.75 | 24.07
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 67 | 105 | 46.1 | 0.63 | 20.9
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 71 | 105 | 48.4 | 0.5 | 17.6
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 59 | 115 | 41.3 | 0.9 | 26.84
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 63 | 115 | 42.1 | 0.83 | 25.14
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 67 | 115 | 43.6 | 0.7 | 21.96
DSG072*D (70% - Low Stage) | 6 | 1260 | 80 | 71 | 115 | 45.9 | 0.6 | 18.7
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 59 | 65 | 51.5 | 0.79 | 29.4
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 63 | 65 | 52.2 | 0.73 | 27.7
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 67 | 65 | 53.7 | 0.63 | 24.53
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 71 | 65 | 56.1 | 0.5 | 21.2
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 59 | 75 | 51.1 | 0.8 | 29.36
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 63 | 75 | 51.8 | 0.74 | 27.66
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 67 | 75 | 53.3 | 0.64 | 24.48
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 71 | 75 | 55.6 | 0.5 | 21.2
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 59 | 85 | 49.8 | 0.82 | 29.6
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 63 | 85 | 50.5 | 0.77 | 27.89
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 67 | 85 | 52 | 0.66 | 24.72
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 71 | 85 | 54.3 | 0.5 | 21.4
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 59 | 95 | 47.5 | 0.86 | 29.34
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 63 | 95 | 48.2 | 0.79 | 27.64
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 67 | 95 | 49.7 | 0.68 | 24.46
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 71 | 95 | 52 | 0.6 | 21.2
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 59 | 105 | 44.7 | 0.9 | 29.11
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 63 | 105 | 45.4 | 0.84 | 27.41
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 67 | 105 | 46.9 | 0.72 | 24.23
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 71 | 105 | 49.2 | 0.6 | 20.9
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 59 | 115 | 42.2 | 0.99 | 30.18
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 63 | 115 | 42.9 | 0.92 | 28.48
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 67 | 115 | 44.4 | 0.79 | 25.3
DSG072*D (70% - Low Stage) | 6 | 1260 | 85 | 71 | 115 | 46.7 | 0.7 | 22
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 59 | 65 | 51.1 | 0.55 | 17.37
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 63 | 65 | 51.8 | 0.49 | 15.66
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 67 | 65 | 53.4 | 0.38 | 12.49
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 59 | 75 | 50.7 | 0.55 | 17.32
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 63 | 75 | 51.4 | 0.49 | 15.62
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 67 | 75 | 52.9 | 0.38 | 12.44
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 59 | 85 | 49.4 | 0.58 | 17.56
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 63 | 85 | 50.1 | 0.51 | 15.86
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 67 | 85 | 51.6 | 0.4 | 12.68
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 59 | 95 | 47.1 | 0.59 | 17.3
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 63 | 95 | 47.8 | 0.53 | 15.6
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 67 | 95 | 49.3 | 0.41 | 12.42
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 59 | 105 | 44.3 | 0.62 | 17.07
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 63 | 105 | 45 | 0.55 | 15.37
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 67 | 105 | 46.5 | 0.42 | 12.2
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 59 | 115 | 41.8 | 0.7 | 18.14
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 63 | 115 | 42.5 | 0.63 | 16.44
DSG072*D (70% - Low Stage) | 6 | 1470 | 70 | 67 | 115 | 44 | 0.49 | 13.26
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 59 | 65 | 51.2 | 0.67 | 21.11
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 63 | 65 | 51.9 | 0.6 | 19.4
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 67 | 65 | 53.4 | 0.49 | 16.23
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 71 | 65 | 55.7 | 0.4 | 12.9
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 59 | 75 | 50.7 | 0.67 | 21.06
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 63 | 75 | 51.4 | 0.61 | 19.36
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 67 | 75 | 52.9 | 0.49 | 16.18
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 71 | 75 | 55.2 | 0.4 | 12.9
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 59 | 85 | 49.4 | 0.7 | 21.3
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 63 | 85 | 50.1 | 0.63 | 19.6
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 67 | 85 | 51.6 | 0.51 | 16.42
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 71 | 85 | 53.9 | 0.4 | 13.1
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 59 | 95 | 47.1 | 0.72 | 21.04
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 63 | 95 | 47.8 | 0.65 | 19.34
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 67 | 95 | 49.3 | 0.53 | 16.16
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 71 | 95 | 51.7 | 0.4 | 12.9
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 59 | 105 | 44.4 | 0.76 | 20.81
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 63 | 105 | 45.1 | 0.69 | 19.11
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 67 | 105 | 46.6 | 0.55 | 15.94
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 71 | 105 | 48.9 | 0.4 | 12.6
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 59 | 115 | 41.8 | 0.85 | 21.88
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 63 | 115 | 42.5 | 0.77 | 20.18
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 67 | 115 | 44 | 0.62 | 17
DSG072*D (70% - Low Stage) | 6 | 1470 | 75 | 71 | 115 | 46.4 | 0.5 | 13.7
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 59 | 65 | 51.4 | 0.78 | 24.87
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 63 | 65 | 52.1 | 0.72 | 23.17
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 67 | 65 | 53.6 | 0.6 | 19.99
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 71 | 65 | 56 | 0.5 | 16.7
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 59 | 75 | 51 | 0.79 | 24.82
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 63 | 75 | 51.7 | 0.72 | 23.12
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 67 | 75 | 53.2 | 0.61 | 19.95
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 71 | 75 | 55.5 | 0.5 | 16.7
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 59 | 85 | 49.7 | 0.82 | 25.06
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 63 | 85 | 50.4 | 0.75 | 23.36
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 67 | 85 | 51.9 | 0.63 | 20.19
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 71 | 85 | 54.2 | 0.5 | 16.9
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 59 | 95 | 47.4 | 0.85 | 24.81
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 63 | 95 | 48.1 | 0.78 | 23.11
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 67 | 95 | 49.6 | 0.65 | 19.93
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 71 | 95 | 51.9 | 0.5 | 16.6
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 59 | 105 | 44.6 | 0.89 | 24.58
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 63 | 105 | 45.3 | 0.82 | 22.88
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 67 | 105 | 46.8 | 0.68 | 19.7
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 71 | 105 | 49.1 | 0.5 | 16.4
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 59 | 115 | 42.1 | 0.99 | 25.64
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 63 | 115 | 42.8 | 0.9 | 23.94
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 67 | 115 | 44.3 | 0.76 | 20.77
DSG072*D (70% - Low Stage) | 6 | 1470 | 80 | 71 | 115 | 46.6 | 0.6 | 17.5
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 59 | 65 | 52.3 | 0.87 | 28.21
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 63 | 65 | 53 | 0.81 | 26.51
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 67 | 65 | 54.5 | 0.69 | 23.33
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 71 | 65 | 56.8 | 0.6 | 20
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 59 | 75 | 51.8 | 0.88 | 28.16
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 63 | 75 | 52.5 | 0.81 | 26.46
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 67 | 75 | 54 | 0.7 | 23.29
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 71 | 75 | 56.3 | 0.6 | 20
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 59 | 85 | 50.5 | 0.91 | 28.4
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 63 | 85 | 51.2 | 0.84 | 26.7
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 67 | 85 | 52.7 | 0.72 | 23.53
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 71 | 85 | 55 | 0.6 | 20.2
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 59 | 95 | 48.2 | 0.94 | 28.15
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 63 | 95 | 49 | 0.87 | 26.45
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 67 | 95 | 50.5 | 0.75 | 23.27
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 71 | 95 | 52.8 | 0.6 | 20
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 59 | 105 | 45.5 | 0.99 | 27.92
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 63 | 105 | 46.2 | 0.92 | 26.22
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 67 | 105 | 47.7 | 0.78 | 23.04
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 71 | 105 | 50 | 0.6 | 19.8
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 59 | 115 | 42.9 | 1 | 26.55
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 63 | 115 | 43.7 | 1 | 27
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 67 | 115 | 45.2 | 0.86 | 24.11
DSG072*D (70% - Low Stage) | 6 | 1470 | 85 | 71 | 115 | 47.5 | 0.7 | 20.8
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 59 | 65 | 53.2 | 0.61 | 15.53
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 63 | 65 | 53.9 | 0.53 | 13.82
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 67 | 65 | 55.4 | 0.4 | 10.65
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 59 | 75 | 52.7 | 0.61 | 15.48
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 63 | 75 | 53.5 | 0.54 | 13.78
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 67 | 75 | 55 | 0.4 | 10.6
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 59 | 85 | 51.4 | 0.64 | 15.72
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 63 | 85 | 52.1 | 0.56 | 14.02
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 67 | 85 | 53.6 | 0.42 | 10.84
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 59 | 95 | 49.2 | 0.65 | 15.46
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 63 | 95 | 49.9 | 0.57 | 13.76
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 67 | 95 | 51.4 | 0.43 | 10.58
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 59 | 105 | 46.4 | 0.68 | 15.23
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 63 | 105 | 47.1 | 0.6 | 13.53
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 67 | 105 | 48.6 | 0.44 | 10.36
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 59 | 115 | 43.9 | 0.77 | 16.3
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 63 | 115 | 44.6 | 0.68 | 14.6
DSG072*D (70% - Low Stage) | 6 | 1890 | 70 | 67 | 115 | 46.1 | 0.52 | 11.42
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 59 | 65 | 53.2 | 0.75 | 19.27
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 63 | 65 | 53.9 | 0.68 | 17.56
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 67 | 65 | 55.4 | 0.54 | 14.39
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 71 | 65 | 57.7 | 0.4 | 11.1
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 59 | 75 | 52.8 | 0.76 | 19.22
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 63 | 75 | 53.5 | 0.68 | 17.52
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 67 | 75 | 55 | 0.54 | 14.34
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 71 | 75 | 57.3 | 0.4 | 11.1
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 59 | 85 | 51.5 | 0.79 | 19.46
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 63 | 85 | 52.2 | 0.71 | 17.76
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 67 | 85 | 53.7 | 0.56 | 14.58
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 71 | 85 | 56 | 0.4 | 11.3
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 59 | 95 | 49.2 | 0.81 | 19.2
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 63 | 95 | 49.9 | 0.73 | 17.5
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 67 | 95 | 51.4 | 0.58 | 14.32
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 71 | 95 | 53.7 | 0.4 | 11
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 59 | 105 | 46.4 | 0.85 | 18.97
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 63 | 105 | 47.1 | 0.76 | 17.27
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 67 | 105 | 48.6 | 0.6 | 14.1
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 71 | 105 | 50.9 | 0.4 | 10.8
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 59 | 115 | 43.9 | 0.95 | 20.04
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 63 | 115 | 44.6 | 0.85 | 18.34
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 67 | 115 | 46.1 | 0.68 | 15.16
DSG072*D (70% - Low Stage) | 6 | 1890 | 75 | 71 | 115 | 48.4 | 0.5 | 11.9
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 59 | 65 | 53.5 | 0.9 | 23.03
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 63 | 65 | 54.2 | 0.82 | 21.33
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 67 | 65 | 55.7 | 0.68 | 18.15
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 71 | 65 | 58 | 0.5 | 14.9
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 59 | 75 | 53 | 0.9 | 22.98
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 63 | 75 | 53.7 | 0.82 | 21.28
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 67 | 75 | 55.3 | 0.68 | 18.11
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 71 | 75 | 57.6 | 0.5 | 14.8
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 59 | 85 | 51.7 | 0.93 | 23.22
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 63 | 85 | 52.4 | 0.85 | 21.52
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 67 | 85 | 53.9 | 0.71 | 18.35
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 71 | 85 | 56.2 | 0.6 | 15.1
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 59 | 95 | 49.4 | 0.97 | 22.97
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 63 | 95 | 50.2 | 0.88 | 21.27
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 67 | 95 | 51.7 | 0.73 | 18.09
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 71 | 95 | 54 | 0.6 | 14.8
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 59 | 105 | 46.7 | 1 | 22.45
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 63 | 105 | 47.4 | 0.92 | 21.04
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 67 | 105 | 48.9 | 0.76 | 17.86
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 71 | 105 | 51.2 | 0.6 | 14.6
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 59 | 115 | 44.1 | 1 | 21.24
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 63 | 115 | 44.9 | 1 | 21.58
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 67 | 115 | 46.4 | 0.85 | 18.93
DSG072*D (70% - Low Stage) | 6 | 1890 | 80 | 71 | 115 | 48.7 | 0.7 | 15.6
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 59 | 65 | 54.3 | 1 | 26.14
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 63 | 65 | 55 | 0.93 | 24.67
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 67 | 65 | 56.6 | 0.79 | 21.49
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 71 | 65 | 58.9 | 0.6 | 18.2
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 59 | 75 | 53.9 | 1 | 25.92
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 63 | 75 | 54.6 | 0.94 | 24.62
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 67 | 75 | 56.1 | 0.79 | 21.45
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 71 | 75 | 58.4 | 0.6 | 18.2
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 59 | 85 | 52.6 | 1 | 25.28
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 63 | 85 | 53.3 | 0.97 | 24.86
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 67 | 85 | 54.8 | 0.82 | 21.69
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 71 | 85 | 57.1 | 0.7 | 18.4
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 59 | 95 | 50.3 | 1 | 24.19
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 63 | 95 | 51 | 1 | 24.54
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 67 | 95 | 52.5 | 0.85 | 21.43
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 71 | 95 | 54.8 | 0.7 | 18.1
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 59 | 105 | 47.5 | 1 | 22.86
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 63 | 105 | 48.2 | 1 | 23.2
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 67 | 105 | 49.7 | 0.89 | 21.2
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 71 | 105 | 52.1 | 0.7 | 17.9
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 59 | 115 | 45 | 1 | 21.64
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 63 | 115 | 45.7 | 1 | 21.99
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 67 | 115 | 47.2 | 0.98 | 22.27
DSG072*D (70% - Low Stage) | 6 | 1890 | 85 | 71 | 115 | 49.5 | 0.8 | 19
DSG090* | 7.5 | 2625 | 70 | 59 | 65 | 91.1 | 0.6 | 18.78
DSG090* | 7.5 | 2625 | 70 | 63 | 65 | 92.4 | 0.53 | 17.04
DSG090* | 7.5 | 2625 | 70 | 67 | 65 | 95.2 | 0.42 | 13.8
DSG090* | 7.5 | 2625 | 70 | 59 | 75 | 90.3 | 0.6 | 18.73
DSG090* | 7.5 | 2625 | 70 | 63 | 75 | 91.6 | 0.54 | 17
DSG090* | 7.5 | 2625 | 70 | 67 | 75 | 94.4 | 0.42 | 13.75
DSG090* | 7.5 | 2625 | 70 | 59 | 85 | 87.9 | 0.62 | 18.98
DSG090* | 7.5 | 2625 | 70 | 63 | 85 | 89.2 | 0.56 | 17.24
DSG090* | 7.5 | 2625 | 70 | 67 | 85 | 92 | 0.44 | 14
DSG090* | 7.5 | 2625 | 70 | 59 | 95 | 83.8 | 0.64 | 18.72
DSG090* | 7.5 | 2625 | 70 | 63 | 95 | 85.1 | 0.58 | 16.98
DSG090* | 7.5 | 2625 | 70 | 67 | 95 | 87.8 | 0.45 | 13.74
DSG090* | 7.5 | 2625 | 70 | 59 | 105 | 78.8 | 0.68 | 18.48
DSG090* | 7.5 | 2625 | 70 | 63 | 105 | 80.1 | 0.6 | 16.75
DSG090* | 7.5 | 2625 | 70 | 67 | 105 | 82.8 | 0.47 | 13.5
DSG090* | 7.5 | 2625 | 70 | 59 | 115 | 74.2 | 0.76 | 19.57
DSG090* | 7.5 | 2625 | 70 | 63 | 115 | 75.5 | 0.68 | 17.83
DSG090* | 7.5 | 2625 | 70 | 67 | 115 | 78.2 | 0.54 | 14.59
DSG090* | 7.5 | 3000 | 70 | 59 | 65 | 92.8 | 0.63 | 17.73
DSG090* | 7.5 | 3000 | 70 | 63 | 65 | 94.1 | 0.56 | 16
DSG090* | 7.5 | 3000 | 70 | 67 | 65 | 96.8 | 0.43 | 12.75
DSG090* | 7.5 | 3000 | 70 | 59 | 75 | 91.9 | 0.63 | 17.68
DSG090* | 7.5 | 3000 | 70 | 63 | 75 | 93.2 | 0.56 | 15.95
DSG090* | 7.5 | 3000 | 70 | 67 | 75 | 96 | 0.44 | 12.7
DSG090* | 7.5 | 3000 | 70 | 59 | 85 | 89.6 | 0.66 | 17.93
DSG090* | 7.5 | 3000 | 70 | 63 | 85 | 90.9 | 0.59 | 16.19
DSG090* | 7.5 | 3000 | 70 | 67 | 85 | 93.6 | 0.46 | 12.95
DSG090* | 7.5 | 3000 | 70 | 59 | 95 | 85.4 | 0.68 | 17.67
DSG090* | 7.5 | 3000 | 70 | 63 | 95 | 86.7 | 0.61 | 15.93
DSG090* | 7.5 | 3000 | 70 | 67 | 95 | 89.5 | 0.47 | 12.69
DSG090* | 7.5 | 3000 | 70 | 59 | 105 | 80.4 | 0.72 | 17.44
DSG090* | 7.5 | 3000 | 70 | 63 | 105 | 81.7 | 0.63 | 15.7
DSG090* | 7.5 | 3000 | 70 | 67 | 105 | 84.4 | 0.49 | 12.45
DSG090* | 7.5 | 3000 | 70 | 59 | 115 | 75.8 | 0.81 | 18.52
DSG090* | 7.5 | 3000 | 70 | 63 | 115 | 77.1 | 0.72 | 16.79
DSG090* | 7.5 | 3000 | 70 | 67 | 115 | 79.9 | 0.56 | 13.54
DSG090* | 7.5 | 3375 | 70 | 59 | 65 | 94.2 | 0.66 | 16.85
DSG090* | 7.5 | 3375 | 70 | 63 | 65 | 95.5 | 0.59 | 15.11
DSG090* | 7.5 | 3375 | 70 | 67 | 65 | 98.2 | 0.45 | 11.87
DSG090* | 7.5 | 3375 | 70 | 59 | 75 | 93.4 | 0.67 | 16.8
DSG090* | 7.5 | 3375 | 70 | 63 | 75 | 94.7 | 0.59 | 15.06
DSG090* | 7.5 | 3375 | 70 | 67 | 75 | 97.4 | 0.45 | 11.82
DSG090* | 7.5 | 3375 | 70 | 59 | 85 | 91 | 0.7 | 17.05
DSG090* | 7.5 | 3375 | 70 | 63 | 85 | 92.3 | 0.62 | 15.31
DSG090* | 7.5 | 3375 | 70 | 67 | 85 | 95 | 0.47 | 12.07
DSG090* | 7.5 | 3375 | 70 | 59 | 95 | 86.9 | 0.72 | 16.78
DSG090* | 7.5 | 3375 | 70 | 63 | 95 | 88.2 | 0.63 | 15.05
DSG090* | 7.5 | 3375 | 70 | 67 | 95 | 90.9 | 0.48 | 11.8
DSG090* | 7.5 | 3375 | 70 | 59 | 105 | 81.9 | 0.75 | 16.55
DSG090* | 7.5 | 3375 | 70 | 63 | 105 | 83.2 | 0.66 | 14.81
DSG090* | 7.5 | 3375 | 70 | 67 | 105 | 85.9 | 0.5 | 11.57
DSG090* | 7.5 | 3375 | 70 | 59 | 115 | 77.3 | 0.85 | 17.64
DSG090* | 7.5 | 3375 | 70 | 63 | 115 | 78.6 | 0.75 | 15.9
DSG090* | 7.5 | 3375 | 70 | 67 | 115 | 81.3 | 0.58 | 12.66
DSG090* | 7.5 | 2625 | 75 | 59 | 65 | 91.6 | 0.71 | 22.6
DSG090* | 7.5 | 2625 | 75 | 63 | 65 | 92.9 | 0.65 | 20.86
DSG090* | 7.5 | 2625 | 75 | 67 | 65 | 95.6 | 0.53 | 17.62
DSG090* | 7.5 | 2625 | 75 | 71 | 65 | 99.8 | 0.4 | 14.3
DSG090* | 7.5 | 2625 | 75 | 59 | 75 | 90.8 | 0.72 | 22.55
DSG090* | 7.5 | 2625 | 75 | 63 | 75 | 92.1 | 0.65 | 20.82
DSG090* | 7.5 | 2625 | 75 | 67 | 75 | 94.8 | 0.54 | 17.57
DSG090* | 7.5 | 2625 | 75 | 71 | 75 | 99 | 0.4 | 14.2
DSG090* | 7.5 | 2625 | 75 | 59 | 85 | 88.4 | 0.74 | 22.8
DSG090* | 7.5 | 2625 | 75 | 63 | 85 | 89.7 | 0.68 | 21.06
DSG090* | 7.5 | 2625 | 75 | 67 | 85 | 92.4 | 0.56 | 17.82
DSG090* | 7.5 | 2625 | 75 | 71 | 85 | 96.6 | 0.4 | 14.5
DSG090* | 7.5 | 2625 | 75 | 59 | 95 | 84.3 | 0.77 | 22.54
DSG090* | 7.5 | 2625 | 75 | 63 | 95 | 85.6 | 0.7 | 20.8
DSG090* | 7.5 | 2625 | 75 | 67 | 95 | 88.3 | 0.57 | 17.56
DSG090* | 7.5 | 2625 | 75 | 71 | 95 | 92.5 | 0.4 | 14.2
DSG090* | 7.5 | 2625 | 75 | 59 | 105 | 79.3 | 0.81 | 22.3
DSG090* | 7.5 | 2625 | 75 | 63 | 105 | 80.6 | 0.74 | 20.57
DSG090* | 7.5 | 2625 | 75 | 67 | 105 | 83.3 | 0.6 | 17.32
DSG090* | 7.5 | 2625 | 75 | 71 | 105 | 87.5 | 0.5 | 14
DSG090* | 7.5 | 2625 | 75 | 59 | 115 | 74.7 | 0.9 | 23.39
DSG090* | 7.5 | 2625 | 75 | 63 | 115 | 76 | 0.82 | 21.65
DSG090* | 7.5 | 2625 | 75 | 67 | 115 | 78.7 | 0.68 | 18.41
DSG090* | 7.5 | 2625 | 75 | 71 | 115 | 82.9 | 0.5 | 15.1
DSG090* | 7.5 | 3000 | 75 | 59 | 65 | 92.8 | 0.77 | 21.55
DSG090* | 7.5 | 3000 | 75 | 63 | 65 | 94.1 | 0.69 | 19.81
DSG090* | 7.5 | 3000 | 75 | 67 | 65 | 96.8 | 0.56 | 16.57
DSG090* | 7.5 | 3000 | 75 | 71 | 65 | 101 | 0.4 | 13.2
DSG090* | 7.5 | 3000 | 75 | 59 | 75 | 92 | 0.77 | 21.5
DSG090* | 7.5 | 3000 | 75 | 63 | 75 | 93.3 | 0.7 | 19.77
DSG090* | 7.5 | 3000 | 75 | 67 | 75 | 96 | 0.57 | 16.52
DSG090* | 7.5 | 3000 | 75 | 71 | 75 | 100.2 | 0.4 | 13.2
DSG090* | 7.5 | 3000 | 75 | 59 | 85 | 89.6 | 0.8 | 21.75
DSG090* | 7.5 | 3000 | 75 | 63 | 85 | 90.9 | 0.73 | 20.01
DSG090* | 7.5 | 3000 | 75 | 67 | 85 | 93.6 | 0.59 | 16.77
DSG090* | 7.5 | 3000 | 75 | 71 | 85 | 97.8 | 0.5 | 13.4
DSG090* | 7.5 | 3000 | 75 | 59 | 95 | 85.5 | 0.83 | 21.49
DSG090* | 7.5 | 3000 | 75 | 63 | 95 | 86.8 | 0.75 | 19.75
DSG090* | 7.5 | 3000 | 75 | 67 | 95 | 89.5 | 0.61 | 16.51
DSG090* | 7.5 | 3000 | 75 | 71 | 95 | 93.7 | 0.5 | 13.1
DSG090* | 7.5 | 3000 | 75 | 59 | 105 | 80.5 | 0.87 | 21.25
DSG090* | 7.5 | 3000 | 75 | 63 | 105 | 81.8 | 0.79 | 19.52
DSG090* | 7.5 | 3000 | 75 | 67 | 105 | 84.5 | 0.64 | 16.27
DSG090* | 7.5 | 3000 | 75 | 71 | 105 | 88.7 | 0.5 | 12.9
DSG090* | 7.5 | 3000 | 75 | 59 | 115 | 75.9 | 0.97 | 22.34
DSG090* | 7.5 | 3000 | 75 | 63 | 115 | 77.2 | 0.88 | 20.6
DSG090* | 7.5 | 3000 | 75 | 67 | 115 | 79.9 | 0.72 | 17.36
DSG090* | 7.5 | 3000 | 75 | 71 | 115 | 84.1 | 0.5 | 14
DSG090* | 7.5 | 3375 | 75 | 59 | 65 | 94.3 | 0.81 | 20.67
DSG090* | 7.5 | 3375 | 75 | 63 | 65 | 95.6 | 0.74 | 18.93
DSG090* | 7.5 | 3375 | 75 | 67 | 65 | 98.3 | 0.59 | 15.69
DSG090* | 7.5 | 3375 | 75 | 71 | 65 | 102.5 | 0.4 | 12.3
DSG090* | 7.5 | 3375 | 75 | 59 | 75 | 93.4 | 0.82 | 20.62
DSG090* | 7.5 | 3375 | 75 | 63 | 75 | 94.7 | 0.74 | 18.88
DSG090* | 7.5 | 3375 | 75 | 67 | 75 | 97.5 | 0.6 | 15.64
DSG090* | 7.5 | 3375 | 75 | 71 | 75 | 101.7 | 0.4 | 12.3
DSG090* | 7.5 | 3375 | 75 | 59 | 85 | 91.1 | 0.85 | 20.86
DSG090* | 7.5 | 3375 | 75 | 63 | 85 | 92.3 | 0.77 | 19.13
DSG090* | 7.5 | 3375 | 75 | 67 | 85 | 95.1 | 0.62 | 15.88
DSG090* | 7.5 | 3375 | 75 | 71 | 85 | 99.3 | 0.5 | 12.5
DSG090* | 7.5 | 3375 | 75 | 59 | 95 | 86.9 | 0.88 | 20.6
DSG090* | 7.5 | 3375 | 75 | 63 | 95 | 88.2 | 0.79 | 18.87
DSG090* | 7.5 | 3375 | 75 | 67 | 95 | 91 | 0.64 | 15.62
DSG090* | 7.5 | 3375 | 75 | 71 | 95 | 95.1 | 0.5 | 12.3
DSG090* | 7.5 | 3375 | 75 | 59 | 105 | 81.9 | 0.92 | 20.37
DSG090* | 7.5 | 3375 | 75 | 63 | 105 | 83.2 | 0.83 | 18.63
DSG090* | 7.5 | 3375 | 75 | 67 | 105 | 85.9 | 0.66 | 15.39
DSG090* | 7.5 | 3375 | 75 | 71 | 105 | 90.1 | 0.5 | 12
DSG090* | 7.5 | 3375 | 75 | 59 | 115 | 77.3 | 1 | 20.83
DSG090* | 7.5 | 3375 | 75 | 63 | 115 | 78.6 | 0.93 | 19.72
DSG090* | 7.5 | 3375 | 75 | 67 | 115 | 81.4 | 0.75 | 16.48
DSG090* | 7.5 | 3375 | 75 | 71 | 115 | 85.5 | 0.6 | 13.1
DSG090* | 7.5 | 2625 | 80 | 59 | 65 | 92.1 | 0.83 | 26.45
DSG090* | 7.5 | 2625 | 80 | 63 | 65 | 93.4 | 0.76 | 24.71
DSG090* | 7.5 | 2625 | 80 | 67 | 65 | 96.1 | 0.64 | 21.47
DSG090* | 7.5 | 2625 | 80 | 71 | 65 | 100.3 | 0.5 | 18.1
DSG090* | 7.5 | 2625 | 80 | 59 | 75 | 91.3 | 0.84 | 26.4
DSG090* | 7.5 | 2625 | 80 | 63 | 75 | 92.6 | 0.77 | 24.66
DSG090* | 7.5 | 2625 | 80 | 67 | 75 | 95.3 | 0.65 | 21.42
DSG090* | 7.5 | 2625 | 80 | 71 | 75 | 99.5 | 0.5 | 18.1
DSG090* | 7.5 | 2625 | 80 | 59 | 85 | 88.9 | 0.87 | 26.64
DSG090* | 7.5 | 2625 | 80 | 63 | 85 | 90.2 | 0.8 | 24.91
DSG090* | 7.5 | 2625 | 80 | 67 | 85 | 92.9 | 0.67 | 21.66
DSG090* | 7.5 | 2625 | 80 | 71 | 85 | 97.1 | 0.5 | 18.3
DSG090* | 7.5 | 2625 | 80 | 59 | 95 | 84.8 | 0.9 | 26.38
DSG090* | 7.5 | 2625 | 80 | 63 | 95 | 86.1 | 0.83 | 24.64
DSG090* | 7.5 | 2625 | 80 | 67 | 95 |  |  | 21.4
DSG090* | 7.5 | 2625 | 80 | 71 | 95 | 93 | 0.6 | 18
DSG090* | 7.5 | 2625 | 80 | 59 | 105 | 79.7 | 0.95 | 26.15
DSG090* | 7.5 | 2625 | 80 | 63 | 105 | 81 | 0.87 | 24.41
DSG090* | 7.5 | 2625 | 80 | 67 | 105 | 83.8 | 0.73 | 21.17
DSG090* | 7.5 | 2625 | 80 | 71 | 105 | 87.9 | 0.6 | 17.8
DSG090* | 7.5 | 2625 | 80 | 59 | 115 | 75.2 | 1 | 26.03
DSG090* | 7.5 | 2625 | 80 | 63 | 115 | 76.4 | 0.96 | 25.5
DSG090* | 7.5 | 2625 | 80 | 67 | 115 | 79.2 | 0.81 | 22.26
DSG090* | 7.5 | 2625 | 80 | 71 | 115 | 83.4 | 0.7 | 18.9
DSG090* | 7.5 | 3000 | 80 | 59 | 65 | 93.3 | 0.9 | 25.4
DSG090* | 7.5 | 3000 | 80 | 63 | 65 | 94.6 | 0.83 | 23.66
DSG090* | 7.5 | 3000 | 80 | 67 | 65 | 97.3 | 0.69 | 20.42
DSG090* | 7.5 | 3000 | 80 | 71 | 65 | 101.5 | 0.6 | 17.1
DSG090* | 7.5 | 3000 | 80 | 59 | 75 | 92.5 | 0.9 | 25.35
DSG090* | 7.5 | 3000 | 80 | 63 | 75 | 93.8 | 0.83 | 23.61
DSG090* | 7.5 | 3000 | 80 | 67 | 75 | 96.5 | 0.7 | 20.37
DSG090* | 7.5 | 3000 | 80 | 71 | 75 | 100.7 | 0.6 | 17
DSG090* | 7.5 | 3000 | 80 | 59 | 85 | 90.1 | 0.94 | 25.59
DSG090* | 7.5 | 3000 | 80 | 63 | 85 | 91.4 | 0.86 | 23.86
DSG090* | 7.5 | 3000 | 80 | 67 | 85 | 94.1 | 0.72 | 20.61
DSG090* | 7.5 | 3000 | 80 | 71 | 85 | 98.3 | 0.6 | 17.3
DSG090* | 7.5 | 3000 | 80 | 59 | 95 | 86 | 0.97 | 25.33
DSG090* | 7.5 | 3000 | 80 | 63 | 95 | 87.3 | 0.89 | 23.59
DSG090* | 7.5 | 3000 | 80 | 67 | 95 | 90 | 0.75 | 20.35
DSG090* | 7.5 | 3000 | 80 | 71 | 95 | 94.2 | 0.6 | 17
DSG090* | 7.5 | 3000 | 80 | 59 | 105 | 80.9 | 1 | 24.53
DSG090* | 7.5 | 3000 | 80 | 63 | 105 | 82.2 | 0.94 | 23.36
DSG090* | 7.5 | 3000 | 80 | 67 | 105 | 85 | 0.78 | 20.12
DSG090* | 7.5 | 3000 | 80 | 71 | 105 | 89.2 | 0.6 | 16.8
DSG090* | 7.5 | 3000 | 80 | 59 | 115 | 76.4 | 1 | 23.14
DSG090* | 7.5 | 3000 | 80 | 63 | 115 | 77.6 | 1 | 23.53
DSG090* | 7.5 | 3000 | 80 | 67 | 115 | 80.4 | 0.87 | 21.21
DSG090* | 7.5 | 3000 | 80 | 71 | 115 | 84.6 | 0.7 | 17.8
DSG090* | 7.5 | 3375 | 80 | 59 | 65 | 94.7 | 0.96 | 24.51
DSG090* | 7.5 | 3375 | 80 | 63 | 65 | 96 | 0.88 | 22.78
DSG090* | 7.5 | 3375 | 80 | 67 | 65 | 98.8 | 0.73 | 19.53
DSG090* | 7.5 | 3375 | 80 | 71 | 65 | 102.9 | 0.6 | 16.2
DSG090* | 7.5 | 3375 | 80 | 59 | 75 | 93.9 | 0.97 | 24.47
DSG090* | 7.5 | 3375 | 80 | 63 | 75 | 95.2 | 0.89 | 22.73
DSG090* | 7.5 | 3375 | 80 | 67 | 75 | 97.9 | 0.74 | 19.49
DSG090* | 7.5 | 3375 | 80 | 71 | 75 | 102.1 | 0.6 | 16.1
DSG090* | 7.5 | 3375 | 80 | 59 | 85 | 91.5 | 1 | 24.65
DSG090* | 7.5 | 3375 | 80 | 63 | 85 | 92.8 | 0.92 | 22.97
DSG090* | 7.5 | 3375 | 80 | 67 | 85 | 95.6 | 0.77 | 19.73
DSG090* | 7.5 | 3375 | 80 | 71 | 85 | 99.7 | 0.6 | 16.4
DSG090* | 7.5 | 3375 | 80 | 59 | 95 | 87.4 | 1 | 23.55
DSG090* | 7.5 | 3375 | 80 | 63 | 95 | 88.7 | 0.95 | 22.71
DSG090* | 7.5 | 3375 | 80 | 67 | 95 | 91.4 | 0.79 | 19.47
DSG090* | 7.5 | 3375 | 80 | 71 | 95 | 95.6 | 0.6 | 16.1
DSG090* | 7.5 | 3375 | 80 | 59 | 105 | 82.4 | 1 | 22.19
DSG090* | 7.5 | 3375 | 80 | 63 | 105 | 83.7 | 1 | 22.48
DSG090* | 7.5 | 3375 | 80 | 67 | 105 | 86.4 | 0.83 | 19.24
DSG090* | 7.5 | 3375 | 80 | 71 | 105 | 90.6 | 0.7 | 15.9
DSG090* | 7.5 | 3375 | 80 | 59 | 115 | 77.8 | 1 | 20.96
DSG090* | 7.5 | 3375 | 80 | 63 | 115 | 79.1 | 1 | 21.3
DSG090* | 7.5 | 3375 | 80 | 67 | 115 | 81.8 | 0.92 | 20.32
DSG090* | 7.5 | 3375 | 80 | 71 | 115 | 86 | 0.7 | 17
DSG090* | 7.5 | 2625 | 85 | 59 | 65 | 93.6 | 0.92 | 29.86
DSG090* | 7.5 | 2625 | 85 | 63 | 65 | 94.9 | 0.86 | 28.12
DSG090* | 7.5 | 2625 | 85 | 67 | 65 | 97.7 | 0.74 | 24.88
DSG090* | 7.5 | 2625 | 85 | 71 | 65 | 101.8 | 0.6 | 21.5
DSG090* | 7.5 | 2625 | 85 | 59 | 75 | 92.8 | 0.93 | 29.81
DSG090* | 7.5 | 2625 | 85 | 63 | 75 | 94.1 | 0.86 | 28.07
DSG090* | 7.5 | 2625 | 85 | 67 | 75 | 96.8 | 0.74 | 24.83
DSG090* | 7.5 | 2625 | 85 | 71 | 75 | 101 | 0.6 | 21.5
DSG090* | 7.5 | 2625 | 85 | 59 | 85 | 90.4 | 0.96 | 30.05
DSG090* | 7.5 | 2625 | 85 | 63 | 85 | 91.7 | 0.89 | 28.32
DSG090* | 7.5 | 2625 | 85 | 67 | 85 | 94.5 | 0.77 | 25.07
DSG090* | 7.5 | 2625 | 85 | 71 | 85 | 98.6 | 0.6 | 21.7
DSG090* | 7.5 | 2625 | 85 | 59 | 95 | 86.3 | 1 | 29.79
DSG090* | 7.5 | 2625 | 85 | 63 | 95 | 87.6 | 0.92 | 28.05
DSG090* | 7.5 | 2625 | 85 | 67 | 95 | 90.3 | 0.79 | 24.81
DSG090* | 7.5 | 2625 | 85 | 71 | 95 | 94.5 | 0.7 | 21.5
DSG090* | 7.5 | 2625 | 85 | 59 | 105 | 81.3 | 1 | 28.15
DSG090* | 7.5 | 2625 | 85 | 63 | 105 | 82.6 | 0.97 | 27.82
DSG090* | 7.5 | 2625 | 85 | 67 | 105 | 85.3 | 0.83 | 24.58
DSG090* | 7.5 | 2625 | 85 | 71 | 105 | 89.5 | 0.7 | 21.2
DSG090* | 7.5 | 2625 | 85 | 59 | 115 | 76.7 | 1 | 26.56
DSG090* | 7.5 | 2625 | 85 | 63 | 115 | 78 | 1 | 27.01
DSG090* | 7.5 | 2625 | 85 | 67 | 115 | 80.7 | 0.92 | 25.67
DSG090* | 7.5 | 2625 | 85 | 71 | 115 | 84.9 | 0.8 | 22.3
DSG090* | 7.5 | 3000 | 85 | 59 | 65 | 94.8 | 1 | 28.74
DSG090* | 7.5 | 3000 | 85 | 63 | 65 | 96.1 | 0.93 | 27.07
DSG090* | 7.5 | 3000 | 85 | 67 | 65 | 98.9 | 0.8 | 23.83
DSG090* | 7.5 | 3000 | 85 | 71 | 65 | 103 | 0.7 | 20.5
DSG090* | 7.5 | 3000 | 85 | 59 | 75 | 94 | 1 | 28.49
DSG090* | 7.5 | 3000 | 85 | 63 | 75 | 95.3 | 0.94 | 27.02
DSG090* | 7.5 | 3000 | 85 | 67 | 75 | 98 | 0.8 | 23.78
DSG090* | 7.5 | 3000 | 85 | 71 | 75 | 102.2 | 0.7 | 20.4
DSG090* | 7.5 | 3000 | 85 | 59 | 85 | 91.6 | 1 | 27.77
DSG090* | 7.5 | 3000 | 85 | 63 | 85 | 92.9 | 0.97 | 27.27
DSG090* | 7.5 | 3000 | 85 | 67 | 85 | 95.7 | 0.83 | 24.02
DSG090* | 7.5 | 3000 | 85 | 71 | 85 | 99.8 | 0.7 | 20.7
DSG090* | 7.5 | 3000 | 85 | 59 | 95 | 87.5 | 1 | 26.52
DSG090* | 7.5 | 3000 | 85 | 63 | 95 | 88.8 | 1 | 26.91
DSG090* | 7.5 | 3000 | 85 | 67 | 95 | 91.5 | 0.86 | 23.76
DSG090* | 7.5 | 3000 | 85 | 71 | 95 | 95.7 | 0.7 | 20.4
DSG090* | 7.5 | 3000 | 85 | 59 | 105 | 82.5 | 1 | 25
DSG090* | 7.5 | 3000 | 85 | 63 | 105 | 83.8 | 1 | 25.39
DSG090* | 7.5 | 3000 | 85 | 67 | 105 | 86.5 | 0.9 | 23.53
DSG090* | 7.5 | 3000 | 85 | 71 | 105 | 90.7 | 0.7 | 20.2
DSG090* | 7.5 | 3000 | 85 | 59 | 115 | 77.9 | 1 | 23.61
DSG090* | 7.5 | 3000 | 85 | 63 | 115 | 79.2 | 1 | 24
DSG090* | 7.5 | 3000 | 85 | 67 | 115 | 81.9 | 0.99 | 24.62
DSG090* | 7.5 | 3000 | 85 | 71 | 115 | 86.1 | 0.8 | 21.3
DSG090* | 7.5 | 3375 | 85 | 59 | 65 | 96.3 | 1 | 25.93
DSG090* | 7.5 | 3375 | 85 | 63 | 65 | 97.6 | 1 | 26.19
DSG090* | 7.5 | 3375 | 85 | 67 | 65 | 100.3 | 0.85 | 22.94
DSG090* | 7.5 | 3375 | 85 | 71 | 65 | 104.5 | 0.7 | 19.6
DSG090* | 7.5 | 3375 | 85 | 59 | 75 | 95.5 | 1 | 25.71
DSG090* | 7.5 | 3375 | 85 | 63 | 75 | 96.8 | 1 | 26.06
DSG090* | 7.5 | 3375 | 85 | 67 | 75 | 99.5 | 0.85 | 22.9
DSG090* | 7.5 | 3375 | 85 | 71 | 75 | 103.7 | 0.7 | 19.5
DSG090* | 7.5 | 3375 | 85 | 59 | 85 | 93.1 | 1 | 25.07
DSG090* | 7.5 | 3375 | 85 | 63 | 85 | 94.4 | 1 | 25.42
DSG090* | 7.5 | 3375 | 85 | 67 | 85 | 97.1 | 0.88 | 23.14
DSG090* | 7.5 | 3375 | 85 | 71 | 85 | 101.3 | 0.7 | 19.8
DSG090* | 7.5 | 3375 | 85 | 59 | 95 | 89 | 1 | 23.96
DSG090* | 7.5 | 3375 | 85 | 63 | 95 | 90.3 | 1 | 24.31
DSG090* | 7.5 | 3375 | 85 | 67 | 95 | 93 | 0.91 | 22.88
DSG090* | 7.5 | 3375 | 85 | 71 | 95 | 97.2 | 0.7 | 19.5
DSG090* | 7.5 | 3375 | 85 | 59 | 105 | 83.9 | 1 | 22.61
DSG090* | 7.5 | 3375 | 85 | 63 | 105 | 85.2 | 1 | 22.96
DSG090* | 7.5 | 3375 | 85 | 67 | 105 | 88 | 0.96 | 22.65
DSG090* | 7.5 | 3375 | 85 | 71 | 105 | 92.1 | 0.8 | 19.3
DSG090* | 7.5 | 3375 | 85 | 59 | 115 | 79.3 | 1 | 21.37
DSG090* | 7.5 | 3375 | 85 | 63 | 115 | 80.6 | 1 | 21.72
DSG090* | 7.5 | 3375 | 85 | 67 | 115 | 83.4 | 1 | 22.46
DSG090* | 7.5 | 3375 | 85 | 71 | 115 | 87.5 | 0.9 | 20.4
DSG102* | 8.5 | 2975 | 70 | 59 | 65 | 98.8 | 0.61 | 18.3
DSG102* | 8.5 | 2975 | 70 | 63 | 65 | 100.2 | 0.54 | 16.56
DSG102* | 8.5 | 2975 | 70 | 67 | 65 | 103.1 | 0.42 | 13.32
DSG102* | 8.5 | 2975 | 70 | 59 | 75 | 97.9 | 0.61 | 18.25
DSG102* | 8.5 | 2975 | 70 | 63 | 75 | 99.3 | 0.54 | 16.51
DSG102* | 8.5 | 2975 | 70 | 67 | 75 | 102.2 | 0.42 | 13.27
DSG102* | 8.5 | 2975 | 70 | 59 | 85 | 95.3 | 0.63 | 18.49
DSG102* | 8.5 | 2975 | 70 | 63 | 85 | 96.7 | 0.57 | 16.76
DSG102* | 8.5 | 2975 | 70 | 67 | 85 | 99.7 | 0.44 | 13.51
DSG102* | 8.5 | 2975 | 70 | 59 | 95 | 90.9 | 0.66 | 18.23
DSG102* | 8.5 | 2975 | 70 | 63 | 95 | 92.3 | 0.58 | 16.49
DSG102* | 8.5 | 2975 | 70 | 67 | 95 | 95.2 | 0.46 | 13.25
DSG102* | 8.5 | 2975 | 70 | 59 | 105 | 85.5 | 0.69 | 18
DSG102* | 8.5 | 2975 | 70 | 63 | 105 | 86.9 | 0.61 | 16.26
DSG102* | 8.5 | 2975 | 70 | 67 | 105 | 89.8 | 0.47 | 13.02
DSG102* | 8.5 | 2975 | 70 | 59 | 115 | 80.5 | 0.78 | 19.09
DSG102* | 8.5 | 2975 | 70 | 63 | 115 | 81.9 | 0.69 | 17.35
DSG102* | 8.5 | 2975 | 70 | 67 | 115 | 84.9 | 0.54 | 14.11
DSG102* | 8.5 | 3200 | 70 | 59 | 65 | 100 | 0.62 | 17.73
DSG102* | 8.5 | 3200 | 70 | 63 | 65 | 101.4 | 0.56 | 16
DSG102* | 8.5 | 3200 | 70 | 67 | 65 | 104.3 | 0.43 | 12.75
DSG102* | 8.5 | 3200 | 70 | 59 | 75 | 99.1 | 0.63 | 17.68
DSG102* | 8.5 | 3200 | 70 | 63 | 75 | 100.5 | 0.56 | 15.95
DSG102* | 8.5 | 3200 | 70 | 67 | 75 | 103.4 | 0.43 | 12.7
DSG102* | 8.5 | 3200 | 70 | 59 | 85 | 96.5 | 0.65 | 17.93
DSG102* | 8.5 | 3200 | 70 | 63 | 85 | 97.9 | 0.58 | 16.19
DSG102* | 8.5 | 3200 | 70 | 67 | 85 | 100.9 | 0.45 | 12.95
DSG102* | 8.5 | 3200 | 70 | 59 | 95 | 92.1 | 0.68 | 17.67
DSG102* | 8.5 | 3200 | 70 | 63 | 95 | 93.5 | 0.6 | 15.93
DSG102* | 8.5 | 3200 | 70 | 67 | 95 | 96.4 | 0.46 | 12.69
DSG102* | 8.5 | 3200 | 70 | 59 | 105 | 86.7 | 0.71 | 17.44
DSG102* | 8.5 | 3200 | 70 | 63 | 105 | 88.1 | 0.63 | 15.7
DSG102* | 8.5 | 3200 | 70 | 67 | 105 | 91 | 0.48 | 12.45
DSG102* | 8.5 | 3200 | 70 | 59 | 115 | 81.7 | 0.8 | 18.52
DSG102* | 8.5 | 3200 | 70 | 63 | 115 | 83.1 | 0.71 | 16.79
DSG102* | 8.5 | 3200 | 70 | 67 | 115 | 86.1 | 0.55 | 13.54
DSG102* | 8.5 | 3825 | 70 | 59 | 65 | 102.6 | 0.67 | 16.4
DSG102* | 8.5 | 3825 | 70 | 63 | 65 | 103.9 | 0.59 | 14.66
DSG102* | 8.5 | 3825 | 70 | 67 | 65 | 106.9 | 0.45 | 11.42
DSG102* | 8.5 | 3825 | 70 | 59 | 75 | 101.7 | 0.68 | 16.35
DSG102* | 8.5 | 3825 | 70 | 63 | 75 | 103.1 | 0.6 | 14.61
DSG102* | 8.5 | 3825 | 70 | 67 | 75 | 106 | 0.45 | 11.37
DSG102* | 8.5 | 3825 | 70 | 59 | 85 | 99.1 | 0.7 | 16.6
DSG102* | 8.5 | 3825 | 70 | 63 | 85 | 100.5 | 0.62 | 14.86
DSG102* | 8.5 | 3825 | 70 | 67 | 85 | 103.4 | 0.47 | 11.62
DSG102* | 8.5 | 3825 | 70 | 59 | 95 | 94.7 | 0.73 | 16.33
DSG102* | 8.5 | 3825 | 70 | 63 | 95 | 96 | 0.64 | 14.6
DSG102* | 8.5 | 3825 | 70 | 67 | 95 | 99 | 0.48 | 11.35
DSG102* | 8.5 | 3825 | 70 | 59 | 105 | 89.2 | 0.76 | 16.1
DSG102* | 8.5 | 3825 | 70 | 63 | 105 | 90.6 | 0.67 | 14.36
DSG102* | 8.5 | 3825 | 70 | 67 | 105 | 93.6 | 0.5 | 11.12
DSG102* | 8.5 | 3825 | 70 | 59 | 115 | 84.3 | 0.86 | 17.19
DSG102* | 8.5 | 3825 | 70 | 63 | 115 | 85.7 | 0.76 | 15.45
DSG102* | 8.5 | 3825 | 70 | 67 | 115 | 88.6 | 0.58 | 12.21
DSG102* | 8.5 | 2975 | 75 | 59 | 65 | 99.3 | 0.73 | 22.12
DSG102* | 8.5 | 2975 | 75 | 63 | 65 | 100.7 | 0.66 | 20.38
DSG102* | 8.5 | 2975 | 75 | 67 | 65 | 103.6 | 0.54 | 17.14
DSG102* | 8.5 | 2975 | 75 | 71 | 65 | 108.1 | 0.4 | 13.8
DSG102* | 8.5 | 2975 | 75 | 59 | 75 | 98.4 | 0.73 | 22.07
DSG102* | 8.5 | 2975 | 75 | 63 | 75 | 99.8 | 0.67 | 20.33
DSG102* | 8.5 | 2975 | 75 | 67 | 75 | 102.7 | 0.54 | 17.09
DSG102* | 8.5 | 2975 | 75 | 71 | 75 | 107.2 | 0.4 | 13.7
DSG102* | 8.5 | 2975 | 75 | 59 | 85 | 95.8 | 0.76 | 22.31
DSG102* | 8.5 | 2975 | 75 | 63 | 85 | 97.2 | 0.69 | 20.58
DSG102* | 8.5 | 2975 | 75 | 67 | 85 | 100.2 | 0.57 | 17.33
DSG102* | 8.5 | 2975 | 75 | 71 | 85 | 104.7 | 0.4 | 14
DSG102* | 8.5 | 2975 | 75 | 59 | 95 | 91.4 | 0.79 | 22.05
DSG102* | 8.5 | 2975 | 75 | 63 | 95 | 92.8 | 0.72 | 20.31
DSG102* | 8.5 | 2975 | 75 | 67 | 95 | 95.7 | 0.58 | 17.07
DSG102* | 8.5 | 2975 | 75 | 71 | 95 | 100.2 | 0.4 | 13.7
DSG102* | 8.5 | 2975 | 75 | 59 | 105 | 86 | 0.83 | 21.82
DSG102* | 8.5 | 2975 | 75 | 63 | 105 | 87.4 | 0.75 | 20.08
DSG102* | 8.5 | 2975 | 75 | 67 | 105 | 90.3 | 0.61 | 16.84
DSG102* | 8.5 | 2975 | 75 | 71 | 105 | 94.8 | 0.5 | 13.5
DSG102* | 8.5 | 2975 | 75 | 59 | 115 | 81 | 0.93 | 22.91
DSG102* | 8.5 | 2975 | 75 | 63 | 115 | 82.4 | 0.84 | 21.17
DSG102* | 8.5 | 2975 | 75 | 67 | 115 | 85.4 | 0.69 | 17.93
DSG102* | 8.5 | 2975 | 75 | 71 | 115 | 89.9 | 0.5 | 14.6
DSG102* | 8.5 | 3200 | 75 | 59 | 65 | 100 | 0.76 | 21.55
DSG102* | 8.5 | 3200 | 75 | 63 | 65 | 101.4 | 0.69 | 19.81
DSG102* | 8.5 | 3200 | 75 | 67 | 65 | 104.4 | 0.56 | 16.57
DSG102* | 8.5 | 3200 | 75 | 71 | 65 | 108.9 | 0.4 | 13.2
DSG102* | 8.5 | 3200 | 75 | 59 | 75 | 99.2 | 0.76 | 21.5
DSG102* | 8.5 | 3200 | 75 | 63 | 75 | 100.6 | 0.69 | 19.77
DSG102* | 8.5 | 3200 | 75 | 67 | 75 | 103.5 | 0.56 | 16.52
DSG102* | 8.5 | 3200 | 75 | 71 | 75 | 108 | 0.4 | 13.2
DSG102* | 8.5 | 3200 | 75 | 59 | 85 | 96.6 | 0.79 | 21.75
DSG102* | 8.5 | 3200 | 75 | 63 | 85 | 98 | 0.72 | 20.01
DSG102* | 8.5 | 3200 | 75 | 67 | 85 | 100.9 | 0.58 | 16.77
DSG102* | 8.5 | 3200 | 75 | 71 | 85 | 105.4 | 0.4 | 13.4
DSG102* | 8.5 | 3200 | 75 | 59 | 95 | 92.1 | 0.82 | 21.49
DSG102* | 8.5 | 3200 | 75 | 63 | 95 | 93.5 | 0.74 | 19.75
DSG102* | 8.5 | 3200 | 75 | 67 | 95 | 96.5 | 0.6 | 16.51
DSG102* | 8.5 | 3200 | 75 | 71 | 95 | 101 | 0.5 | 13.1
DSG102* | 8.5 | 3200 | 75 | 59 | 105 | 86.7 | 0.86 | 21.25
DSG102* | 8.5 | 3200 | 75 | 63 | 105 | 88.1 | 0.78 | 19.52
DSG102* | 8.5 | 3200 | 75 | 67 | 105 | 91.1 | 0.63 | 16.27
DSG102* | 8.5 | 3200 | 75 | 71 | 105 | 95.6 | 0.5 | 12.9
DSG102* | 8.5 | 3200 | 75 | 59 | 115 | 81.8 | 0.96 | 22.34
DSG102* | 8.5 | 3200 | 75 | 63 | 115 | 83.2 | 0.87 | 20.6
DSG102* | 8.5 | 3200 | 75 | 67 | 115 | 86.1 | 0.71 | 17.36
DSG102* | 8.5 | 3200 | 75 | 71 | 115 | 90.6 | 0.5 | 14
DSG102* | 8.5 | 3825 | 75 | 59 | 65 | 102.6 | 0.83 | 20.22
DSG102* | 8.5 | 3825 | 75 | 63 | 65 | 104 | 0.75 | 18.48
DSG102* | 8.5 | 3825 | 75 | 67 | 65 | 106.9 | 0.6 | 15.24
DSG102* | 8.5 | 3825 | 75 | 71 | 65 | 111.5 | 0.4 | 11.9
DSG102* | 8.5 | 3825 | 75 | 59 | 75 | 101.7 | 0.83 | 20.17
DSG102* | 8.5 | 3825 | 75 | 63 | 75 | 103.1 | 0.75 | 18.43
DSG102* | 8.5 | 3825 | 75 | 67 | 75 | 106.1 | 0.6 | 15.19
DSG102* | 8.5 | 3825 | 75 | 71 | 75 | 110.6 | 0.5 | 11.8
DSG102* | 8.5 | 3825 | 75 | 59 | 85 | 99.1 | 0.87 | 20.41
DSG102* | 8.5 | 3825 | 75 | 63 | 85 | 100.5 | 0.78 | 18.68
DSG102* | 8.5 | 3825 | 75 | 67 | 85 | 103.5 | 0.63 | 15.43
DSG102* | 8.5 | 3825 | 75 | 71 | 85 | 108 | 0.5 | 12.1
DSG102* | 8.5 | 3825 | 75 | 59 | 95 | 94.7 | 0.9 | 20.15
DSG102* | 8.5 | 3825 | 75 | 63 | 95 | 96.1 | 0.81 | 18.42
DSG102* | 8.5 | 3825 | 75 | 67 | 95 | 99.1 | 0.64 | 15.17
DSG102* | 8.5 | 3825 | 75 | 71 | 95 | 103.6 | 0.5 | 11.8
DSG102* | 8.5 | 3825 | 75 | 59 | 105 | 89.3 | 0.94 | 19.92
DSG102* | 8.5 | 3825 | 75 | 63 | 105 | 90.7 | 0.84 | 18.18
DSG102* | 8.5 | 3825 | 75 | 67 | 105 | 93.6 | 0.67 | 14.94
DSG102* | 8.5 | 3825 | 75 | 71 | 105 | 98.1 | 0.5 | 11.6
DSG102* | 8.5 | 3825 | 75 | 59 | 115 | 84.3 | 1 | 20.05
DSG102* | 8.5 | 3825 | 75 | 63 | 115 | 85.7 | 0.95 | 19.27
DSG102* | 8.5 | 3825 | 75 | 67 | 115 | 88.7 | 0.76 | 16.03
DSG102* | 8.5 | 3825 | 75 | 71 | 115 | 93.2 | 0.6 | 12.7
DSG102* | 8.5 | 2975 | 80 | 59 | 65 | 99.8 | 0.85 | 25.96
DSG102* | 8.5 | 2975 | 80 | 63 | 65 | 101.2 | 0.78 | 24.22
DSG102* | 8.5 | 2975 | 80 | 67 | 65 | 104.1 | 0.66 | 20.98
DSG102* | 8.5 | 2975 | 80 | 71 | 65 | 108.6 | 0.5 | 17.6
DSG102* | 8.5 | 2975 | 80 | 59 | 75 | 98.9 | 0.86 | 25.91
DSG102* | 8.5 | 2975 | 80 | 63 | 75 | 100.3 | 0.79 | 24.18
DSG102* | 8.5 | 2975 | 80 | 67 | 75 | 103.3 | 0.66 | 20.93
DSG102* | 8.5 | 2975 | 80 | 71 | 75 | 107.8 | 0.5 | 17.6
DSG102* | 8.5 | 2975 | 80 | 59 | 85 | 96.3 | 0.89 | 26.16
DSG102* | 8.5 | 2975 | 80 | 63 | 85 | 97.7 | 0.82 | 24.42
DSG102* | 8.5 | 2975 | 80 | 67 | 85 | 100.7 | 0.69 | 21.18
DSG102* | 8.5 | 2975 | 80 | 71 | 85 | 105.2 | 0.6 | 17.8
DSG102* | 8.5 | 2975 | 80 | 59 | 95 | 91.9 | 0.92 | 25.9
DSG102* | 8.5 | 2975 | 80 | 63 | 95 | 93.3 | 0.85 | 24.16
DSG102* | 8.5 | 2975 | 80 | 67 | 95 |  |  | 20.92
DSG102* | 8.5 | 2975 | 80 | 71 | 95 | 100.7 | 0.6 | 17.6
DSG102* | 8.5 | 2975 | 80 | 59 | 105 | 86.5 | 0.97 | 25.66
DSG102* | 8.5 | 2975 | 80 | 63 | 105 | 87.9 | 0.89 | 23.93
DSG102* | 8.5 | 2975 | 80 | 67 | 105 | 90.8 | 0.75 | 20.68
DSG102* | 8.5 | 2975 | 80 | 71 | 105 | 95.3 | 0.6 | 17.3
DSG102* | 8.5 | 2975 | 80 | 59 | 115 | 81.5 | 1 | 24.92
DSG102* | 8.5 | 2975 | 80 | 63 | 115 | 82.9 | 0.99 | 25.01
DSG102* | 8.5 | 2975 | 80 | 67 | 115 | 85.9 | 0.83 | 21.77
DSG102* | 8.5 | 2975 | 80 | 71 | 115 | 90.4 | 0.7 | 18.4
DSG102* | 8.5 | 3200 | 80 | 59 | 65 | 100.6 | 0.89 | 25.4
DSG102* | 8.5 | 3200 | 80 | 63 | 65 | 101.9 | 0.82 | 23.66
DSG102* | 8.5 | 3200 | 80 | 67 | 65 | 104.9 | 0.69 | 20.42
DSG102* | 8.5 | 3200 | 80 | 71 | 65 | 109.4 | 0.5 | 17.1
DSG102* | 8.5 | 3200 | 80 | 59 | 75 | 99.7 | 0.9 | 25.35
DSG102* | 8.5 | 3200 | 80 | 63 | 75 | 101.1 | 0.82 | 23.61
DSG102* | 8.5 | 3200 | 80 | 67 | 75 | 104 | 0.69 | 20.37
DSG102* | 8.5 | 3200 | 80 | 71 | 75 | 108.5 | 0.6 | 17
DSG102* | 8.5 | 3200 | 80 | 59 | 85 | 97.1 | 0.93 | 25.59
DSG102* | 8.5 | 3200 | 80 | 63 | 85 | 98.5 | 0.85 | 23.86
DSG102* | 8.5 | 3200 | 80 | 67 | 85 | 101.4 | 0.72 | 20.61
DSG102* | 8.5 | 3200 | 80 | 71 | 85 | 105.9 | 0.6 | 17.3
DSG102* | 8.5 | 3200 | 80 | 59 | 95 | 92.7 | 0.96 | 25.33
DSG102* | 8.5 | 3200 | 80 | 63 | 95 | 94.1 | 0.88 | 23.59
DSG102* | 8.5 | 3200 | 80 | 67 | 95 | 97 | 0.74 | 20.35
DSG102* | 8.5 | 3200 | 80 | 71 | 95 | 101.5 | 0.6 | 17
DSG102* | 8.5 | 3200 | 80 | 59 | 105 | 87.2 | 1 | 24.78
DSG102* | 8.5 | 3200 | 80 | 63 | 105 | 88.6 | 0.93 | 23.36
DSG102* | 8.5 | 3200 | 80 | 67 | 105 | 91.6 | 0.77 | 20.12
DSG102* | 8.5 | 3200 | 80 | 71 | 105 | 96.1 | 0.6 | 16.8
DSG102* | 8.5 | 3200 | 80 | 59 | 115 | 82.3 | 1 | 23.38
DSG102* | 8.5 | 3200 | 80 | 63 | 115 | 83.7 | 1 | 23.77
DSG102* | 8.5 | 3200 | 80 | 67 | 115 | 86.6 | 0.86 | 21.21
DSG102* | 8.5 | 3200 | 80 | 71 | 115 | 91.1 | 0.7 | 17.8
DSG102* | 8.5 | 3825 | 80 | 59 | 65 | 103.1 | 0.98 | 24.06
DSG102* | 8.5 | 3825 | 80 | 63 | 65 | 104.5 | 0.9 | 22.33
DSG102* | 8.5 | 3825 | 80 | 67 | 65 | 107.5 | 0.75 | 19.08
DSG102* | 8.5 | 3825 | 80 | 71 | 65 | 112 | 0.6 | 15.7
DSG102* | 8.5 | 3825 | 80 | 59 | 75 | 102.2 | 0.99 | 24.02
DSG102* | 8.5 | 3825 | 80 | 63 | 75 | 103.6 | 0.9 | 22.28
DSG102* | 8.5 | 3825 | 80 | 67 | 75 | 106.6 | 0.75 | 19.04
DSG102* | 8.5 | 3825 | 80 | 71 | 75 | 111.1 | 0.6 | 15.7
DSG102* | 8.5 | 3825 | 80 | 59 | 85 | 99.7 | 1 | 23.69
DSG102* | 8.5 | 3825 | 80 | 63 | 85 | 101.1 | 0.94 | 22.52
DSG102* | 8.5 | 3825 | 80 | 67 | 85 | 104 | 0.78 | 19.28
DSG102* | 8.5 | 3825 | 80 | 71 | 85 | 108.5 | 0.6 | 15.9
DSG102* | 8.5 | 3825 | 80 | 59 | 95 | 95.2 | 1 | 22.63
DSG102* | 8.5 | 3825 | 80 | 63 | 95 | 96.6 | 0.97 | 22.26
DSG102* | 8.5 | 3825 | 80 | 67 | 95 | 99.6 | 0.8 | 19.02
DSG102* | 8.5 | 3825 | 80 | 71 | 95 | 104.1 | 0.6 | 15.7
DSG102* | 8.5 | 3825 | 80 | 59 | 105 | 89.8 | 1 | 21.34
DSG102* | 8.5 | 3825 | 80 | 63 | 105 | 91.2 | 1 | 21.68
DSG102* | 8.5 | 3825 | 80 | 67 | 105 | 94.1 | 0.84 | 18.79
DSG102* | 8.5 | 3825 | 80 | 71 | 105 | 98.7 | 0.7 | 15.4
DSG102* | 8.5 | 3825 | 80 | 59 | 115 | 84.9 | 1 | 20.17
DSG102* | 8.5 | 3825 | 80 | 63 | 115 | 86.3 | 1 | 20.5
DSG102* | 8.5 | 3825 | 80 | 67 | 115 | 89.2 | 0.94 | 19.87
DSG102* | 8.5 | 3825 | 80 | 71 | 115 | 93.7 | 0.7 | 16.5
DSG102* | 8.5 | 2975 | 85 | 59 | 65 | 101.5 | 0.95 | 29.37
DSG102* | 8.5 | 2975 | 85 | 63 | 65 | 102.9 | 0.88 | 27.63
DSG102* | 8.5 | 2975 | 85 | 67 | 65 | 105.8 | 0.75 | 24.39
DSG102* | 8.5 | 2975 | 85 | 71 | 65 | 110.3 | 0.6 | 21
DSG102* | 8.5 | 2975 | 85 | 59 | 75 | 100.6 | 0.95 | 29.32
DSG102* | 8.5 | 2975 | 85 | 63 | 75 | 102 | 0.89 | 27.59
DSG102* | 8.5 | 2975 | 85 | 67 | 75 | 104.9 | 0.76 | 24.34
DSG102* | 8.5 | 2975 | 85 | 71 | 75 | 109.4 | 0.6 | 21
DSG102* | 8.5 | 2975 | 85 | 59 | 85 | 98 | 0.99 | 29.57
DSG102* | 8.5 | 2975 | 85 | 63 | 85 | 99.4 | 0.92 | 27.83
DSG102* | 8.5 | 2975 | 85 | 67 | 85 | 102.3 | 0.79 | 24.59
DSG102* | 8.5 | 2975 | 85 | 71 | 85 | 106.8 | 0.7 | 21.2
DSG102* | 8.5 | 2975 | 85 | 59 | 95 | 93.6 | 1 | 28.59
DSG102* | 8.5 | 2975 | 85 | 63 | 95 | 95 | 0.95 | 27.57
DSG102* | 8.5 | 2975 | 85 | 67 | 95 | 97.9 | 0.81 | 24.33
DSG102* | 8.5 | 2975 | 85 | 71 | 95 | 102.4 | 0.7 | 21
DSG102* | 8.5 | 2975 | 85 | 59 | 105 | 88.1 | 1 | 26.93
DSG102* | 8.5 | 2975 | 85 | 63 | 105 | 89.5 | 1 | 27.34
DSG102* | 8.5 | 2975 | 85 | 67 | 105 | 92.5 | 0.85 | 24.09
DSG102* | 8.5 | 2975 | 85 | 71 | 105 | 97 | 0.7 | 20.7
DSG102* | 8.5 | 2975 | 85 | 59 | 115 | 83.2 | 1 | 25.42
DSG102* | 8.5 | 2975 | 85 | 63 | 115 | 84.6 | 1 | 25.85
DSG102* | 8.5 | 2975 | 85 | 67 | 115 | 87.5 | 0.94 | 25.18
DSG102* | 8.5 | 2975 | 85 | 71 | 115 | 92 | 0.8 | 21.8
DSG102* | 8.5 | 3200 | 85 | 59 | 65 | 102.2 | 0.99 | 28.81
DSG102* | 8.5 | 3200 | 85 | 63 | 65 | 103.6 | 0.92 | 27.07
DSG102* | 8.5 | 3200 | 85 | 67 | 65 | 106.6 | 0.79 | 23.83
DSG102* | 8.5 | 3200 | 85 | 71 | 65 | 111.1 | 0.6 | 20.5
DSG102* | 8.5 | 3200 | 85 | 59 | 75 | 101.3 | 1 | 28.76
DSG102* | 8.5 | 3200 | 85 | 63 | 75 | 102.7 | 0.93 | 27.02
DSG102* | 8.5 | 3200 | 85 | 67 | 75 | 105.7 | 0.79 | 23.78
DSG102* | 8.5 | 3200 | 85 | 71 | 75 | 110.2 | 0.7 | 20.4
DSG102* | 8.5 | 3200 | 85 | 59 | 85 | 98.8 | 1 | 28.06
DSG102* | 8.5 | 3200 | 85 | 63 | 85 | 100.1 | 0.96 | 27.27
DSG102* | 8.5 | 3200 | 85 | 67 | 85 | 103.1 | 0.82 | 24.02
DSG102* | 8.5 | 3200 | 85 | 71 | 85 | 107.6 | 0.7 | 20.7
DSG102* | 8.5 | 3200 | 85 | 59 | 95 | 94.3 | 1 | 26.8
DSG102* | 8.5 | 3200 | 85 | 63 | 95 | 95.7 | 0.99 | 27
DSG102* | 8.5 | 3200 | 85 | 67 | 95 | 98.7 | 0.85 | 23.76
DSG102* | 8.5 | 3200 | 85 | 71 | 95 | 103.2 | 0.7 | 20.4
DSG102* | 8.5 | 3200 | 85 | 59 | 105 | 88.9 | 1 | 25.26
DSG102* | 8.5 | 3200 | 85 | 63 | 105 | 90.3 | 1 | 25.65
DSG102* | 8.5 | 3200 | 85 | 67 | 105 | 93.2 | 0.89 | 23.53
DSG102* | 8.5 | 3200 | 85 | 71 | 105 | 97.7 | 0.7 | 20.2
DSG102* | 8.5 | 3200 | 85 | 59 | 115 | 84 | 1 | 23.85
DSG102* | 8.5 | 3200 | 85 | 63 | 115 | 85.3 | 1 | 24.25
DSG102* | 8.5 | 3200 | 85 | 67 | 115 | 88.3 | 0.98 | 24.62
DSG102* | 8.5 | 3200 | 85 | 71 | 115 | 92.8 | 0.8 | 21.3
DSG102* | 8.5 | 3825 | 85 | 59 | 65 | 104.8 | 1 | 24.9
DSG102* | 8.5 | 3825 | 85 | 63 | 65 | 106.2 | 1 | 25.23
DSG102* | 8.5 | 3825 | 85 | 67 | 65 | 109.1 | 0.87 | 22.49
DSG102* | 8.5 | 3825 | 85 | 71 | 65 | 113.6 | 0.7 | 19.1
DSG102* | 8.5 | 3825 | 85 | 59 | 75 | 103.9 | 1 | 24.69
DSG102* | 8.5 | 3825 | 85 | 63 | 75 | 105.3 | 1 | 25.02
DSG102* | 8.5 | 3825 | 85 | 67 | 75 | 108.2 | 0.87 | 22.45
DSG102* | 8.5 | 3825 | 85 | 71 | 75 | 112.7 | 0.7 | 19.1
DSG102* | 8.5 | 3825 | 85 | 59 | 85 | 101.3 | 1 | 24.08
DSG102* | 8.5 | 3825 | 85 | 63 | 85 | 102.7 | 1 | 24.41
DSG102* | 8.5 | 3825 | 85 | 67 | 85 | 105.7 | 0.9 | 22.69
DSG102* | 8.5 | 3825 | 85 | 71 | 85 | 110.2 | 0.7 | 19.3
DSG102* | 8.5 | 3825 | 85 | 59 | 95 | 96.9 | 1 | 23.03
DSG102* | 8.5 | 3825 | 85 | 63 | 95 | 98.3 | 1 | 23.36
DSG102* | 8.5 | 3825 | 85 | 67 | 95 | 101.2 | 0.93 | 22.43
DSG102* | 8.5 | 3825 | 85 | 71 | 95 | 105.7 | 0.8 | 19.1
DSG102* | 8.5 | 3825 | 85 | 59 | 105 | 91.5 | 1 | 21.74
DSG102* | 8.5 | 3825 | 85 | 63 | 105 | 92.9 | 1 | 22.07
DSG102* | 8.5 | 3825 | 85 | 67 | 105 | 95.8 | 0.97 | 22.2
DSG102* | 8.5 | 3825 | 85 | 71 | 105 | 100.3 | 0.8 | 18.8
DSG102* | 8.5 | 3825 | 85 | 59 | 115 | 86.5 | 1 | 20.56
DSG102* | 8.5 | 3825 | 85 | 63 | 115 | 87.9 | 1 | 20.9
DSG102* | 8.5 | 3825 | 85 | 67 | 115 | 90.9 | 1 | 21.6
DSG102* | 8.5 | 3825 | 85 | 71 | 115 | 95.4 | 0.9 | 19.9
DSG120* | 10 | 3150 | 70 | 59 | 65 | 118.1 | 0.59 | 20.1
DSG120* | 10 | 3150 | 70 | 63 | 65 | 119.8 | 0.53 | 18.19
DSG120* | 10 | 3150 | 70 | 67 | 65 | 123.3 | 0.41 | 14.62
DSG120* | 10 | 3150 | 70 | 59 | 75 | 117.1 | 0.59 | 20.05
DSG120* | 10 | 3150 | 70 | 63 | 75 | 118.8 | 0.53 | 18.14
DSG120* | 10 | 3150 | 70 | 67 | 75 | 122.3 | 0.41 | 14.57
DSG120* | 10 | 3150 | 70 | 59 | 85 | 114 | 0.62 | 20.32
DSG120* | 10 | 3150 | 70 | 63 | 85 | 115.7 | 0.55 | 18.41
DSG120* | 10 | 3150 | 70 | 67 | 85 | 119.2 | 0.43 | 14.84
DSG120* | 10 | 3150 | 70 | 59 | 95 | 108.7 | 0.64 | 20.03
DSG120* | 10 | 3150 | 70 | 63 | 95 | 110.4 | 0.57 | 18.12
DSG120* | 10 | 3150 | 70 | 67 | 95 | 113.9 | 0.44 | 14.55
DSG120* | 10 | 3150 | 70 | 59 | 105 | 102.2 | 0.67 | 19.77
DSG120* | 10 | 3150 | 70 | 63 | 105 | 103.9 | 0.6 | 17.86
DSG120* | 10 | 3150 | 70 | 67 | 105 | 107.4 | 0.46 | 14.3
DSG120* | 10 | 3150 | 70 | 59 | 115 | 96.3 | 0.75 | 20.97
DSG120* | 10 | 3150 | 70 | 63 | 115 | 98 | 0.67 | 19.06
DSG120* | 10 | 3150 | 70 | 67 | 115 | 101.5 | 0.53 | 15.49
DSG120* | 10 | 3400 | 70 | 59 | 65 | 119.1 | 0.61 | 19.45
DSG120* | 10 | 3400 | 70 | 63 | 65 | 120.8 | 0.54 | 17.54
DSG120* | 10 | 3400 | 70 | 67 | 65 | 124.3 | 0.42 | 13.97
DSG120* | 10 | 3400 | 70 | 59 | 75 | 118 | 0.61 | 19.4
DSG120* | 10 | 3400 | 70 | 63 | 75 | 119.7 | 0.55 | 17.49
DSG120* | 10 | 3400 | 70 | 67 | 75 | 123.2 | 0.42 | 13.92
DSG120* | 10 | 3400 | 70 | 59 | 85 | 115 | 0.64 | 19.67
DSG120* | 10 | 3400 | 70 | 63 | 85 | 116.6 | 0.57 | 17.76
DSG120* | 10 | 3400 | 70 | 67 | 85 | 120.2 | 0.44 | 14.19
DSG120* | 10 | 3400 | 70 | 59 | 95 | 109.7 | 0.66 | 19.38
DSG120* | 10 | 3400 | 70 | 63 | 95 | 111.3 | 0.59 | 17.47
DSG120* | 10 | 3400 | 70 | 67 | 95 | 114.9 | 0.45 | 13.9
DSG120* | 10 | 3400 | 70 | 59 | 105 | 103.2 | 0.69 | 19.12
DSG120* | 10 | 3400 | 70 | 63 | 105 | 104.9 | 0.61 | 17.21
DSG120* | 10 | 3400 | 70 | 67 | 105 | 108.4 | 0.47 | 13.65
DSG120* | 10 | 3400 | 70 | 59 | 115 | 97.3 | 0.78 | 20.32
DSG120* | 10 | 3400 | 70 | 63 | 115 | 98.9 | 0.7 | 18.41
DSG120* | 10 | 3400 | 70 | 67 | 115 | 102.5 | 0.54 | 14.84
DSG120* | 10 | 4050 | 70 | 59 | 65 | 122.1 | 0.66 | 18.01
DSG120* | 10 | 4050 | 70 | 63 | 65 | 123.8 | 0.58 | 16.1
DSG120* | 10 | 4050 | 70 | 67 | 65 | 127.3 | 0.44 | 12.54
DSG120* | 10 | 4050 | 70 | 59 | 75 | 121.1 | 0.66 | 17.96
DSG120* | 10 | 4050 | 70 | 63 | 75 | 122.8 | 0.58 | 16.05
DSG120* | 10 | 4050 | 70 | 67 | 75 | 126.3 | 0.44 | 12.49
DSG120* | 10 | 4050 | 70 | 59 | 85 | 118 | 0.69 | 18.23
DSG120* | 10 | 4050 | 70 | 63 | 85 | 119.7 | 0.61 | 16.32
DSG120* | 10 | 4050 | 70 | 67 | 85 | 123.2 | 0.46 | 12.75
DSG120* | 10 | 4050 | 70 | 59 | 95 | 112.7 | 0.71 | 17.94
DSG120* | 10 | 4050 | 70 | 63 | 95 | 114.4 | 0.62 | 16.03
DSG120* | 10 | 4050 | 70 | 67 | 95 | 117.9 | 0.47 | 12.47
DSG120* | 10 | 4050 | 70 | 59 | 105 | 106.2 | 0.74 | 17.69
DSG120* | 10 | 4050 | 70 | 63 | 105 | 107.9 | 0.65 | 15.78
DSG120* | 10 | 4050 | 70 | 67 | 105 | 111.4 | 0.49 | 12.21
DSG120* | 10 | 4050 | 70 | 59 | 115 | 100.3 | 0.84 | 18.88
DSG120* | 10 | 4050 | 70 | 63 | 115 | 102 | 0.74 | 16.97
DSG120* | 10 | 4050 | 70 | 67 | 115 | 105.5 | 0.57 | 13.41
DSG120* | 10 | 3150 | 75 | 59 | 65 | 118.8 | 0.71 | 24.3
DSG120* | 10 | 3150 | 75 | 63 | 65 | 120.4 | 0.64 | 22.39
DSG120* | 10 | 3150 | 75 | 67 | 65 | 123.9 | 0.53 | 18.82
DSG120* | 10 | 3150 | 75 | 71 | 65 | 129.3 | 0.4 | 15.1
DSG120* | 10 | 3150 | 75 | 59 | 75 | 117.7 | 0.71 | 24.25
DSG120* | 10 | 3150 | 75 | 63 | 75 | 119.4 | 0.65 | 22.34
DSG120* | 10 | 3150 | 75 | 67 | 75 | 122.9 | 0.53 | 18.77
DSG120* | 10 | 3150 | 75 | 71 | 75 | 128.3 | 0.4 | 15.1
DSG120* | 10 | 3150 | 75 | 59 | 85 | 114.6 | 0.74 | 24.52
DSG120* | 10 | 3150 | 75 | 63 | 85 | 116.3 | 0.67 | 22.61
DSG120* | 10 | 3150 | 75 | 67 | 85 | 119.8 | 0.55 | 19.04
DSG120* | 10 | 3150 | 75 | 71 | 85 | 125.2 | 0.4 | 15.3
DSG120* | 10 | 3150 | 75 | 59 | 95 | 109.3 | 0.77 | 24.23
DSG120* | 10 | 3150 | 75 | 63 | 95 | 111 | 0.7 | 22.32
DSG120* | 10 | 3150 | 75 | 67 | 95 | 114.5 | 0.57 | 18.75
DSG120* | 10 | 3150 | 75 | 71 | 95 | 119.9 | 0.4 | 15.1
DSG120* | 10 | 3150 | 75 | 59 | 105 | 102.8 | 0.81 | 23.97
DSG120* | 10 | 3150 | 75 | 63 | 105 | 104.5 | 0.73 | 22.06
DSG120* | 10 | 3150 | 75 | 67 | 105 | 108 | 0.59 | 18.5
DSG120* | 10 | 3150 | 75 | 71 | 105 | 113.4 | 0.5 | 14.8
DSG120* | 10 | 3150 | 75 | 59 | 115 | 96.9 | 0.9 | 25.17
DSG120* | 10 | 3150 | 75 | 63 | 115 | 98.6 | 0.82 | 23.26
DSG120* | 10 | 3150 | 75 | 67 | 115 | 102.1 | 0.67 | 19.69
DSG120* | 10 | 3150 | 75 | 71 | 115 | 107.5 | 0.5 | 16
DSG120* | 10 | 3400 | 75 | 59 | 65 | 119.7 | 0.74 | 23.65
DSG120* | 10 | 3400 | 75 | 63 | 65 | 121.4 | 0.67 | 21.74
DSG120* | 10 | 3400 | 75 | 67 | 65 | 124.9 | 0.54 | 18.17
DSG120* | 10 | 3400 | 75 | 71 | 65 | 130.3 | 0.4 | 14.5
DSG120* | 10 | 3400 | 75 | 59 | 75 | 118.7 | 0.74 | 23.6
DSG120* | 10 | 3400 | 75 | 63 | 75 | 120.3 | 0.67 | 21.69
DSG120* | 10 | 3400 | 75 | 67 | 75 | 123.9 | 0.55 | 18.12
DSG120* | 10 | 3400 | 75 | 71 | 75 | 129.2 | 0.4 | 14.4
DSG120* | 10 | 3400 | 75 | 59 | 85 | 115.6 | 0.77 | 23.87
DSG120* | 10 | 3400 | 75 | 63 | 85 | 117.2 | 0.7 | 21.96
DSG120* | 10 | 3400 | 75 | 67 | 85 | 120.8 | 0.57 | 18.39
DSG120* | 10 | 3400 | 75 | 71 | 85 | 126.2 | 0.4 | 14.7
DSG120* | 10 | 3400 | 75 | 59 | 95 | 110.3 | 0.8 | 23.58
DSG120* | 10 | 3400 | 75 | 63 | 95 | 111.9 | 0.72 | 21.67
DSG120* | 10 | 3400 | 75 | 67 | 95 | 115.5 | 0.59 | 18.1
DSG120* | 10 | 3400 | 75 | 71 | 95 | 120.9 | 0.4 | 14.4
DSG120* | 10 | 3400 | 75 | 59 | 105 | 103.8 | 0.84 | 23.32
DSG120* | 10 | 3400 | 75 | 63 | 105 | 105.5 | 0.76 | 21.41
DSG120* | 10 | 3400 | 75 | 67 | 105 | 109 | 0.61 | 17.85
DSG120* | 10 | 3400 | 75 | 71 | 105 | 114.4 | 0.5 | 14.2
DSG120* | 10 | 3400 | 75 | 59 | 115 | 97.9 | 0.94 | 24.52
DSG120* | 10 | 3400 | 75 | 63 | 115 | 99.5 | 0.85 | 22.61
DSG120* | 10 | 3400 | 75 | 67 | 115 | 103.1 | 0.69 | 19.04
DSG120* | 10 | 3400 | 75 | 71 | 115 | 108.5 | 0.5 | 15.3
DSG120* | 10 | 4050 | 75 | 59 | 65 | 122.8 | 0.81 | 22.21
DSG120* | 10 | 4050 | 75 | 63 | 65 | 124.4 | 0.73 | 20.3
DSG120* | 10 | 4050 | 75 | 67 | 65 | 128 | 0.58 | 16.74
DSG120* | 10 | 4050 | 75 | 71 | 65 | 133.3 | 0.4 | 13
DSG120* | 10 | 4050 | 75 | 59 | 75 | 121.7 | 0.81 | 22.16
DSG120* | 10 | 4050 | 75 | 63 | 75 | 123.4 | 0.73 | 20.25
DSG120* | 10 | 4050 | 75 | 67 | 75 | 126.9 | 0.59 | 16.69
DSG120* | 10 | 4050 | 75 | 71 | 75 | 132.3 | 0.4 | 13
DSG120* | 10 | 4050 | 75 | 59 | 85 | 118.6 | 0.84 | 22.43
DSG120* | 10 | 4050 | 75 | 63 | 85 | 120.3 | 0.76 | 20.52
DSG120* | 10 | 4050 | 75 | 67 | 85 | 123.8 | 0.61 | 16.95
DSG120* | 10 | 4050 | 75 | 71 | 85 | 129.2 | 0.5 | 13.3
DSG120* | 10 | 4050 | 75 | 59 | 95 | 113.3 | 0.87 | 22.14
DSG120* | 10 | 4050 | 75 | 63 | 95 | 115 | 0.78 | 20.23
DSG120* | 10 | 4050 | 75 | 67 | 95 | 118.5 | 0.63 | 16.67
DSG120* | 10 | 4050 | 75 | 71 | 95 | 123.9 | 0.5 | 13
DSG120* | 10 | 4050 | 75 | 59 | 105 | 106.8 | 0.91 | 21.89
DSG120* | 10 | 4050 | 75 | 63 | 105 | 108.5 | 0.82 | 19.98
DSG120* | 10 | 4050 | 75 | 67 | 105 | 112 | 0.65 | 16.41
DSG120* | 10 | 4050 | 75 | 71 | 105 | 117.4 | 0.5 | 12.7
DSG120* | 10 | 4050 | 75 | 59 | 115 | 100.9 | 1 | 22.65
DSG120* | 10 | 4050 | 75 | 63 | 115 | 102.6 | 0.92 | 21.17
DSG120* | 10 | 4050 | 75 | 67 | 115 | 106.1 | 0.74 | 17.61
DSG120* | 10 | 4050 | 75 | 71 | 115 | 111.5 | 0.6 | 13.9
DSG120* | 10 | 3150 | 80 | 59 | 65 | 119.4 | 0.83 | 28.53
DSG120* | 10 | 3150 | 80 | 63 | 65 | 121 | 0.76 | 26.62
DSG120* | 10 | 3150 | 80 | 67 | 65 | 124.6 | 0.64 | 23.05
DSG120* | 10 | 3150 | 80 | 71 | 65 | 129.9 | 0.5 | 19.4
DSG120* | 10 | 3150 | 80 | 59 | 75 | 118.3 | 0.83 | 28.48
DSG120* | 10 | 3150 | 80 | 63 | 75 | 120 | 0.77 | 26.57
DSG120* | 10 | 3150 | 80 | 67 | 75 | 123.5 | 0.65 | 23
DSG120* | 10 | 3150 | 80 | 71 | 75 | 128.9 | 0.5 | 19.3
DSG120* | 10 | 3150 | 80 | 59 | 85 | 115.2 | 0.86 | 28.74
DSG120* | 10 | 3150 | 80 | 63 | 85 | 116.9 | 0.8 | 26.83
DSG120* | 10 | 3150 | 80 | 67 | 85 | 120.4 | 0.67 | 23.27
DSG120* | 10 | 3150 | 80 | 71 | 85 | 125.8 | 0.5 | 19.6
DSG120* | 10 | 3150 | 80 | 59 | 95 | 109.9 | 0.9 | 28.46
DSG120* | 10 | 3150 | 80 | 63 | 95 | 111.6 | 0.82 | 26.55
DSG120* | 10 | 3150 | 80 | 67 | 95 |  |  | 22.98
DSG120* | 10 | 3150 | 80 | 71 | 95 | 120.5 | 0.6 | 19.3
DSG120* | 10 | 3150 | 80 | 59 | 105 | 103.4 | 0.94 | 28.2
DSG120* | 10 | 3150 | 80 | 63 | 105 | 105.1 | 0.87 | 26.29
DSG120* | 10 | 3150 | 80 | 67 | 105 | 108.6 | 0.72 | 22.72
DSG120* | 10 | 3150 | 80 | 71 | 105 | 114 | 0.6 | 19
DSG120* | 10 | 3150 | 80 | 59 | 115 | 97.5 | 1 | 28.15
DSG120* | 10 | 3150 | 80 | 63 | 115 | 99.2 | 0.96 | 27.49
DSG120* | 10 | 3150 | 80 | 67 | 115 | 102.7 | 0.81 | 23.92
DSG120* | 10 | 3150 | 80 | 71 | 115 | 108.1 | 0.6 | 20.2
DSG120* | 10 | 3400 | 80 | 59 | 65 | 120.3 | 0.87 | 27.88
DSG120* | 10 | 3400 | 80 | 63 | 65 | 122 | 0.8 | 25.97
DSG120* | 10 | 3400 | 80 | 67 | 65 | 125.5 | 0.67 | 22.4
DSG120* | 10 | 3400 | 80 | 71 | 65 | 130.9 | 0.5 | 18.7
DSG120* | 10 | 3400 | 80 | 59 | 75 | 119.3 | 0.87 | 27.83
DSG120* | 10 | 3400 | 80 | 63 | 75 | 120.9 | 0.8 | 25.92
DSG120* | 10 | 3400 | 80 | 67 | 75 | 124.5 | 0.67 | 22.35
DSG120* | 10 | 3400 | 80 | 71 | 75 | 129.8 | 0.5 | 18.7
DSG120* | 10 | 3400 | 80 | 59 | 85 | 116.2 | 0.9 | 28.1
DSG120* | 10 | 3400 | 80 | 63 | 85 | 117.9 | 0.83 | 26.19
DSG120* | 10 | 3400 | 80 | 67 | 85 | 121.4 | 0.7 | 22.62
DSG120* | 10 | 3400 | 80 | 71 | 85 | 126.8 | 0.6 | 18.9
DSG120* | 10 | 3400 | 80 | 59 | 95 | 110.9 | 0.94 | 27.81
DSG120* | 10 | 3400 | 80 | 63 | 95 | 112.6 | 0.86 | 25.9
DSG120* | 10 | 3400 | 80 | 67 | 95 | 116.1 | 0.72 | 22.33
DSG120* | 10 | 3400 | 80 | 71 | 95 | 121.5 | 0.6 | 18.6
DSG120* | 10 | 3400 | 80 | 59 | 105 | 104.4 | 0.99 | 27.55
DSG120* | 10 | 3400 | 80 | 63 | 105 | 106.1 | 0.9 | 25.64
DSG120* | 10 | 3400 | 80 | 67 | 105 | 109.6 | 0.75 | 22.08
DSG120* | 10 | 3400 | 80 | 71 | 105 | 115 | 0.6 | 18.4
DSG120* | 10 | 3400 | 80 | 59 | 115 | 98.5 | 1 | 26.33
DSG120* | 10 | 3400 | 80 | 63 | 115 | 100.2 | 1 | 26.78
DSG120* | 10 | 3400 | 80 | 67 | 115 | 103.7 | 0.84 | 23.27
DSG120* | 10 | 3400 | 80 | 71 | 115 | 109.1 | 0.7 | 19.6
DSG120* | 10 | 4050 | 80 | 59 | 65 | 123.4 | 0.95 | 26.44
DSG120* | 10 | 4050 | 80 | 63 | 65 | 125 | 0.87 | 24.53
DSG120* | 10 | 4050 | 80 | 67 | 65 | 128.6 | 0.73 | 20.97
DSG120* | 10 | 4050 | 80 | 71 | 65 | 133.9 | 0.6 | 17.3
DSG120* | 10 | 4050 | 80 | 59 | 75 | 122.3 | 0.96 | 26.39
DSG120* | 10 | 4050 | 80 | 63 | 75 | 124 | 0.88 | 24.48
DSG120* | 10 | 4050 | 80 | 67 | 75 | 127.5 | 0.73 | 20.91
DSG120* | 10 | 4050 | 80 | 71 | 75 | 132.9 | 0.6 | 17.2
DSG120* | 10 | 4050 | 80 | 59 | 85 | 119.2 | 1 | 26.66
DSG120* | 10 | 4050 | 80 | 63 | 85 | 120.9 | 0.91 | 24.75
DSG120* | 10 | 4050 | 80 | 67 | 85 | 124.4 | 0.76 | 21.18
DSG120* | 10 | 4050 | 80 | 71 | 85 | 129.8 | 0.6 | 17.5
DSG120* | 10 | 4050 | 80 | 59 | 95 | 113.9 | 1 | 25.57
DSG120* | 10 | 4050 | 80 | 63 | 95 | 115.6 | 0.94 | 24.46
DSG120* | 10 | 4050 | 80 | 67 | 95 | 119.1 | 0.78 | 20.89
DSG120* | 10 | 4050 | 80 | 71 | 95 | 124.5 | 0.6 | 17.2
DSG120* | 10 | 4050 | 80 | 59 | 105 | 107.5 | 1 | 24.12
DSG120* | 10 | 4050 | 80 | 63 | 105 | 109.1 | 0.99 | 24.21
DSG120* | 10 | 4050 | 80 | 67 | 105 | 112.6 | 0.82 | 20.64
DSG120* | 10 | 4050 | 80 | 71 | 105 | 118 | 0.6 | 16.9
DSG120* | 10 | 4050 | 80 | 59 | 115 | 101.5 | 1 | 22.79
DSG120* | 10 | 4050 | 80 | 63 | 115 | 103.2 | 1 | 23.17
DSG120* | 10 | 4050 | 80 | 67 | 115 | 106.7 | 0.91 | 21.83
DSG120* | 10 | 4050 | 80 | 71 | 115 | 112.1 | 0.7 | 18.1
DSG120* | 10 | 3150 | 85 | 59 | 65 | 121.4 | 0.92 | 32.28
DSG120* | 10 | 3150 | 85 | 63 | 65 | 123 | 0.86 | 30.37
DSG120* | 10 | 3150 | 85 | 67 | 65 | 126.5 | 0.73 | 26.8
DSG120* | 10 | 3150 | 85 | 71 | 65 | 131.9 | 0.6 | 23.1
DSG120* | 10 | 3150 | 85 | 59 | 75 | 120.3 | 0.93 | 32.23
DSG120* | 10 | 3150 | 85 | 63 | 75 | 122 | 0.86 | 30.32
DSG120* | 10 | 3150 | 85 | 67 | 75 | 125.5 | 0.74 | 26.75
DSG120* | 10 | 3150 | 85 | 71 | 75 | 130.9 | 0.6 | 23.1
DSG120* | 10 | 3150 | 85 | 59 | 85 | 117.2 | 0.96 | 32.49
DSG120* | 10 | 3150 | 85 | 63 | 85 | 118.9 | 0.89 | 30.58
DSG120* | 10 | 3150 | 85 | 67 | 85 | 122.4 | 0.76 | 27.02
DSG120* | 10 | 3150 | 85 | 71 | 85 | 127.8 | 0.6 | 23.3
DSG120* | 10 | 3150 | 85 | 59 | 95 | 111.9 | 1 | 32.21
DSG120* | 10 | 3150 | 85 | 63 | 95 | 113.6 | 0.92 | 30.3
DSG120* | 10 | 3150 | 85 | 67 | 95 | 117.1 | 0.79 | 26.73
DSG120* | 10 | 3150 | 85 | 71 | 95 | 122.5 | 0.7 | 23
DSG120* | 10 | 3150 | 85 | 59 | 105 | 105.4 | 1 | 30.43
DSG120* | 10 | 3150 | 85 | 63 | 105 | 107.1 | 0.97 | 30.04
DSG120* | 10 | 3150 | 85 | 67 | 105 | 110.6 | 0.83 | 26.47
DSG120* | 10 | 3150 | 85 | 71 | 105 | 116 | 0.7 | 22.8
DSG120* | 10 | 3150 | 85 | 59 | 115 | 99.5 | 1 | 28.72
DSG120* | 10 | 3150 | 85 | 63 | 115 | 101.2 | 1 | 29.2
DSG120* | 10 | 3150 | 85 | 67 | 115 | 104.7 | 0.92 | 27.67
DSG120* | 10 | 3150 | 85 | 71 | 115 | 110.1 | 0.8 | 24
DSG120* | 10 | 3400 | 85 | 59 | 65 | 122.3 | 0.97 | 31.63
DSG120* | 10 | 3400 | 85 | 63 | 65 | 124 | 0.9 | 29.72
DSG120* | 10 | 3400 | 85 | 67 | 65 | 127.5 | 0.77 | 26.15
DSG120* | 10 | 3400 | 85 | 71 | 65 | 132.9 | 0.6 | 22.5
DSG120* | 10 | 3400 | 85 | 59 | 75 | 121.3 | 0.97 | 31.58
DSG120* | 10 | 3400 | 85 | 63 | 75 | 122.9 | 0.9 | 29.67
DSG120* | 10 | 3400 | 85 | 67 | 75 | 126.5 | 0.77 | 26.1
DSG120* | 10 | 3400 | 85 | 71 | 75 | 131.8 | 0.6 | 22.4
DSG120* | 10 | 3400 | 85 | 59 | 85 | 118.2 | 1 | 31.6
DSG120* | 10 | 3400 | 85 | 63 | 85 | 119.8 | 0.93 | 29.94
DSG120* | 10 | 3400 | 85 | 67 | 85 | 123.4 | 0.8 | 26.37
DSG120* | 10 | 3400 | 85 | 71 | 85 | 128.8 | 0.7 | 22.7
DSG120* | 10 | 3400 | 85 | 59 | 95 | 112.9 | 1 | 30.18
DSG120* | 10 | 3400 | 85 | 63 | 95 | 114.5 | 0.97 | 29.65
DSG120* | 10 | 3400 | 85 | 67 | 95 | 118.1 | 0.83 | 26.08
DSG120* | 10 | 3400 | 85 | 71 | 95 | 123.5 | 0.7 | 22.4
DSG120* | 10 | 3400 | 85 | 59 | 105 | 106.4 | 1 | 28.45
DSG120* | 10 | 3400 | 85 | 63 | 105 | 108.1 | 1 | 28.89
DSG120* | 10 | 3400 | 85 | 67 | 105 | 111.6 | 0.87 | 25.83
DSG120* | 10 | 3400 | 85 | 71 | 105 | 117 | 0.7 | 22.1
DSG120* | 10 | 3400 | 85 | 59 | 115 | 100.5 | 1 | 26.87
DSG120* | 10 | 3400 | 85 | 63 | 115 | 102.1 | 1 | 27.31
DSG120* | 10 | 3400 | 85 | 67 | 115 | 105.7 | 0.96 | 27.02
DSG120* | 10 | 3400 | 85 | 71 | 115 | 111.1 | 0.8 | 23.3
DSG120* | 10 | 4050 | 85 | 59 | 65 | 125.4 | 1 | 28.14
DSG120* | 10 | 4050 | 85 | 63 | 65 | 127 | 0.99 | 28.28
DSG120* | 10 | 4050 | 85 | 67 | 65 | 130.6 | 0.84 | 24.72
DSG120* | 10 | 4050 | 85 | 71 | 65 | 135.9 | 0.7 | 21
DSG120* | 10 | 4050 | 85 | 59 | 75 | 124.3 | 1 | 27.9
DSG120* | 10 | 4050 | 85 | 63 | 75 | 126 | 1 | 28.23
DSG120* | 10 | 4050 | 85 | 67 | 75 | 129.5 | 0.85 | 24.66
DSG120* | 10 | 4050 | 85 | 71 | 75 | 134.9 | 0.7 | 21
DSG120* | 10 | 4050 | 85 | 59 | 85 | 121.2 | 1 | 27.21
DSG120* | 10 | 4050 | 85 | 63 | 85 | 122.9 | 1 | 27.58
DSG120* | 10 | 4050 | 85 | 67 | 85 | 126.4 | 0.88 | 24.93
DSG120* | 10 | 4050 | 85 | 71 | 85 | 131.8 | 0.7 | 21.2
DSG120* | 10 | 4050 | 85 | 59 | 95 | 115.9 | 1 | 26.02
DSG120* | 10 | 4050 | 85 | 63 | 95 | 117.6 | 1 | 26.39
DSG120* | 10 | 4050 | 85 | 67 | 95 | 121.1 | 0.91 | 24.64
DSG120* | 10 | 4050 | 85 | 71 | 95 | 126.5 | 0.7 | 20.9
DSG120* | 10 | 4050 | 85 | 59 | 105 | 109.4 | 1 | 24.57
DSG120* | 10 | 4050 | 85 | 63 | 105 | 111.1 | 1 | 24.94
DSG120* | 10 | 4050 | 85 | 67 | 105 | 114.6 | 0.95 | 24.39
DSG120* | 10 | 4050 | 85 | 71 | 105 | 120 | 0.8 | 20.7
DSG120* | 10 | 4050 | 85 | 59 | 115 | 103.5 | 1 | 23.24
DSG120* | 10 | 4050 | 85 | 63 | 115 | 105.2 | 1 | 23.61
DSG120* | 10 | 4050 | 85 | 67 | 115 | 108.7 | 1 | 24.4
DSG120* | 10 | 4050 | 85 | 71 | 115 | 114.1 | 0.9 | 21.9
DSG180*D | 15 | 4500 | 70 | 59 | 65 | 174.6 | 0.6 | 21.09
DSG180*D | 15 | 4500 | 70 | 63 | 65 | 177 | 0.53 | 19.11
DSG180*D | 15 | 4500 | 70 | 67 | 65 | 182.3 | 0.42 | 15.43
DSG180*D | 15 | 4500 | 70 | 59 | 75 | 173 | 0.6 | 21.03
DSG180*D | 15 | 4500 | 70 | 63 | 75 | 175.5 | 0.54 | 19.06
DSG180*D | 15 | 4500 | 70 | 67 | 75 | 180.7 | 0.42 | 15.38
DSG180*D | 15 | 4500 | 70 | 59 | 85 | 168.4 | 0.63 | 21.31
DSG180*D | 15 | 4500 | 70 | 63 | 85 | 170.9 | 0.56 | 19.34
DSG180*D | 15 | 4500 | 70 | 67 | 85 | 176.1 | 0.44 | 15.66
DSG180*D | 15 | 4500 | 70 | 59 | 95 | 160.6 | 0.65 | 21.01
DSG180*D | 15 | 4500 | 70 | 63 | 95 | 163.1 | 0.58 | 19.04
DSG180*D | 15 | 4500 | 70 | 67 | 95 | 168.3 | 0.45 | 15.36
DSG180*D | 15 | 4500 | 70 | 59 | 105 | 151 | 0.68 | 20.75
DSG180*D | 15 | 4500 | 70 | 63 | 105 | 153.4 | 0.61 | 18.78
DSG180*D | 15 | 4500 | 70 | 67 | 105 | 158.7 | 0.47 | 15.09
DSG180*D | 15 | 4500 | 70 | 59 | 115 | 142.2 | 0.77 | 21.98
DSG180*D | 15 | 4500 | 70 | 63 | 115 | 144.7 | 0.68 | 20.01
DSG180*D | 15 | 4500 | 70 | 67 | 115 | 149.9 | 0.54 | 16.33
DSG180*D | 15 | 5012 | 70 | 59 | 65 | 176.5 | 0.63 | 20.13
DSG180*D | 15 | 5012 | 70 | 63 | 65 | 179 | 0.56 | 18.16
DSG180*D | 15 | 5012 | 70 | 67 | 65 | 184.2 | 0.43 | 14.48
DSG180*D | 15 | 5012 | 70 | 59 | 75 | 174.9 | 0.63 | 20.08
DSG180*D | 15 | 5012 | 70 | 63 | 75 | 177.4 | 0.56 | 18.1
DSG180*D | 15 | 5012 | 70 | 67 | 75 | 182.6 | 0.44 | 14.42
DSG180*D | 15 | 5012 | 70 | 59 | 85 | 170.3 | 0.66 | 20.35
DSG180*D | 15 | 5012 | 70 | 63 | 85 | 172.8 | 0.59 | 18.38
DSG180*D | 15 | 5012 | 70 | 67 | 85 | 178 | 0.46 | 14.7
DSG180*D | 15 | 5012 | 70 | 59 | 95 | 162.5 | 0.68 | 20.06
DSG180*D | 15 | 5012 | 70 | 63 | 95 | 165 | 0.6 | 18.08
DSG180*D | 15 | 5012 | 70 | 67 | 95 | 170.2 | 0.47 | 14.4
DSG180*D | 15 | 5012 | 70 | 59 | 105 | 152.9 | 0.71 | 19.79
DSG180*D | 15 | 5012 | 70 | 63 | 105 | 155.4 | 0.63 | 17.82
DSG180*D | 15 | 5012 | 70 | 67 | 105 | 160.6 | 0.49 | 14.14
DSG180*D | 15 | 5012 | 70 | 59 | 115 | 144.1 | 0.8 | 21.03
DSG180*D | 15 | 5012 | 70 | 63 | 115 | 146.6 | 0.72 | 19.06
DSG180*D | 15 | 5012 | 70 | 67 | 115 | 151.8 | 0.56 | 15.37
DSG180*D | 15 | 6000 | 70 | 59 | 65 | 181.1 | 0.68 | 18.6
DSG180*D | 15 | 6000 | 70 | 63 | 65 | 183.6 | 0.6 | 16.63
DSG180*D | 15 | 6000 | 70 | 67 | 65 | 188.8 | 0.45 | 12.95
DSG180*D | 15 | 6000 | 70 | 59 | 75 | 179.5 | 0.68 | 18.55
DSG180*D | 15 | 6000 | 70 | 63 | 75 | 182 | 0.6 | 16.58
DSG180*D | 15 | 6000 | 70 | 67 | 75 | 187.2 | 0.45 | 12.9
DSG180*D | 15 | 6000 | 70 | 59 | 85 | 174.9 | 0.71 | 18.83
DSG180*D | 15 | 6000 | 70 | 63 | 85 | 177.4 | 0.63 | 16.86
DSG180*D | 15 | 6000 | 70 | 67 | 85 | 182.6 | 0.48 | 13.17
DSG180*D | 15 | 6000 | 70 | 59 | 95 | 167.1 | 0.73 | 18.53
DSG180*D | 15 | 6000 | 70 | 63 | 95 | 169.6 | 0.64 | 16.56
DSG180*D | 15 | 6000 | 70 | 67 | 95 | 174.8 | 0.49 | 12.88
DSG180*D | 15 | 6000 | 70 | 59 | 105 | 157.5 | 0.77 | 18.27
DSG180*D | 15 | 6000 | 70 | 63 | 105 | 160 | 0.67 | 16.29
DSG180*D | 15 | 6000 | 70 | 67 | 105 | 165.2 | 0.5 | 12.61
DSG180*D | 15 | 6000 | 70 | 59 | 115 | 148.7 | 0.87 | 19.5
DSG180*D | 15 | 6000 | 70 | 63 | 115 | 151.2 | 0.77 | 17.53
DSG180*D | 15 | 6000 | 70 | 67 | 115 | 156.4 | 0.58 | 13.85
DSG180*D | 15 | 4500 | 75 | 59 | 65 | 175.5 | 0.72 | 25.42
DSG180*D | 15 | 4500 | 75 | 63 | 65 | 178 | 0.65 | 23.45
DSG180*D | 15 | 4500 | 75 | 67 | 65 | 183.2 | 0.53 | 19.77
DSG180*D | 15 | 4500 | 75 | 71 | 65 | 191.2 | 0.41 | 16
DSG180*D | 15 | 4500 | 75 | 59 | 75 | 173.9 | 0.72 | 25.37
DSG180*D | 15 | 4500 | 75 | 63 | 75 | 176.4 | 0.66 | 23.4
DSG180*D | 15 | 4500 | 75 | 67 | 75 | 181.6 | 0.54 | 19.71
DSG180*D | 15 | 4500 | 75 | 71 | 75 | 189.6 | 0.42 | 15.9
DSG180*D | 15 | 4500 | 75 | 59 | 85 | 169.3 | 0.75 | 25.64
DSG180*D | 15 | 4500 | 75 | 63 | 85 | 171.8 | 0.68 | 23.67
DSG180*D | 15 | 4500 | 75 | 67 | 85 | 177 | 0.56 | 19.99
DSG180*D | 15 | 4500 | 75 | 71 | 85 | 185 | 0.43 | 16.2
DSG180*D | 15 | 4500 | 75 | 59 | 95 | 161.5 | 0.78 | 25.35
DSG180*D | 15 | 4500 | 75 | 63 | 95 | 164 | 0.71 | 23.37
DSG180*D | 15 | 4500 | 75 | 67 | 95 | 169.2 | 0.58 | 19.69
DSG180*D | 15 | 4500 | 75 | 71 | 95 | 177.2 | 0.44 | 15.9
DSG180*D | 15 | 4500 | 75 | 59 | 105 | 151.9 | 0.82 | 25.08
DSG180*D | 15 | 4500 | 75 | 63 | 105 | 154.3 | 0.74 | 23.11
DSG180*D | 15 | 4500 | 75 | 67 | 105 | 159.6 | 0.6 | 19.43
DSG180*D | 15 | 4500 | 75 | 71 | 105 | 167.6 | 0.46 | 15.6
DSG180*D | 15 | 4500 | 75 | 59 | 115 | 143.1 | 0.91 | 26.32
DSG180*D | 15 | 4500 | 75 | 63 | 115 | 145.6 | 0.83 | 24.35
DSG180*D | 15 | 4500 | 75 | 67 | 115 | 150.8 | 0.68 | 20.66
DSG180*D | 15 | 4500 | 75 | 71 | 115 | 158.8 | 0.53 | 16.8
DSG180*D | 15 | 5012 | 75 | 59 | 65 | 177.4 | 0.76 | 24.47
DSG180*D | 15 | 5012 | 75 | 63 | 65 | 179.9 | 0.69 | 22.49
DSG180*D | 15 | 5012 | 75 | 67 | 65 | 185.1 | 0.56 | 18.81
DSG180*D | 15 | 5012 | 75 | 71 | 65 | 193.1 | 0.43 | 15
DSG180*D | 15 | 5012 | 75 | 59 | 75 | 175.8 | 0.77 | 24.41
DSG180*D | 15 | 5012 | 75 | 63 | 75 | 178.3 | 0.69 | 22.44
DSG180*D | 15 | 5012 | 75 | 67 | 75 | 183.5 | 0.56 | 18.76
DSG180*D | 15 | 5012 | 75 | 71 | 75 | 191.5 | 0.43 | 14.9
DSG180*D | 15 | 5012 | 75 | 59 | 85 | 171.3 | 0.79 | 24.69
DSG180*D | 15 | 5012 | 75 | 63 | 85 | 173.7 | 0.72 | 22.72
DSG180*D | 15 | 5012 | 75 | 67 | 85 | 179 | 0.59 | 19.04
DSG180*D | 15 | 5012 | 75 | 71 | 85 | 186.9 | 0.45 | 15.2
DSG180*D | 15 | 5012 | 75 | 59 | 95 | 163.4 | 0.82 | 24.39
DSG180*D | 15 | 5012 | 75 | 63 | 95 | 165.9 | 0.75 | 22.42
DSG180*D | 15 | 5012 | 75 | 67 | 95 | 171.1 | 0.6 | 18.74
DSG180*D | 15 | 5012 | 75 | 71 | 95 | 179.1 | 0.46 | 14.9
DSG180*D | 15 | 5012 | 75 | 59 | 105 | 153.8 | 0.87 | 24.13
DSG180*D | 15 | 5012 | 75 | 63 | 105 | 156.3 | 0.78 | 22.16
DSG180*D | 15 | 5012 | 75 | 67 | 105 | 161.5 | 0.63 | 18.47
DSG180*D | 15 | 5012 | 75 | 71 | 105 | 169.5 | 0.48 | 14.7
DSG180*D | 15 | 5012 | 75 | 59 | 115 | 145 | 0.96 | 25.36
DSG180*D | 15 | 5012 | 75 | 63 | 115 | 147.5 | 0.87 | 23.39
DSG180*D | 15 | 5012 | 75 | 67 | 115 | 152.7 | 0.71 | 19.71
DSG180*D | 15 | 5012 | 75 | 71 | 115 | 160.7 | 0.55 | 15.9
DSG180*D | 15 | 6000 | 75 | 59 | 65 | 182 | 0.83 | 22.94
DSG180*D | 15 | 6000 | 75 | 63 | 65 | 184.5 | 0.75 | 20.97
DSG180*D | 15 | 6000 | 75 | 67 | 65 | 189.7 | 0.6 | 17.29
DSG180*D | 15 | 6000 | 75 | 71 | 65 | 197.7 | 0.45 | 13.5
DSG180*D | 15 | 6000 | 75 | 59 | 75 | 180.4 | 0.84 | 22.89
DSG180*D | 15 | 6000 | 75 | 63 | 75 | 182.9 | 0.75 | 20.91
DSG180*D | 15 | 6000 | 75 | 67 | 75 | 188.1 | 0.6 | 17.23
DSG180*D | 15 | 6000 | 75 | 71 | 75 | 196.1 | 0.45 | 13.4
DSG180*D | 15 | 6000 | 75 | 59 | 85 | 175.9 | 0.87 | 23.16
DSG180*D | 15 | 6000 | 75 | 63 | 85 | 178.3 | 0.78 | 21.19
DSG180*D | 15 | 6000 | 75 | 67 | 85 | 183.6 | 0.63 | 17.51
DSG180*D | 15 | 6000 | 75 | 71 | 85 | 191.5 | 0.47 | 13.7
DSG180*D | 15 | 6000 | 75 | 59 | 95 | 168 | 0.9 | 22.87
DSG180*D | 15 | 6000 | 75 | 63 | 95 | 170.5 | 0.81 | 20.89
DSG180*D | 15 | 6000 | 75 | 67 | 95 | 175.7 | 0.65 | 17.21
DSG180*D | 15 | 6000 | 75 | 71 | 95 | 183.7 | 0.48 | 13.4
DSG180*D | 15 | 6000 | 75 | 59 | 105 | 158.4 | 0.94 | 22.6
DSG180*D | 15 | 6000 | 75 | 63 | 105 | 160.9 | 0.85 | 20.63
DSG180*D | 15 | 6000 | 75 | 67 | 105 | 166.1 | 0.67 | 16.95
DSG180*D | 15 | 6000 | 75 | 71 | 105 | 174.1 | 0.5 | 13.1
DSG180*D | 15 | 6000 | 75 | 59 | 115 | 149.6 | 1 | 22.67
DSG180*D | 15 | 6000 | 75 | 63 | 115 | 152.1 | 0.95 | 21.86
DSG180*D | 15 | 6000 | 75 | 67 | 115 | 157.3 | 0.76 | 18.18
DSG180*D | 15 | 6000 | 75 | 71 | 115 | 165.3 | 0.57 | 14.4
DSG180*D | 15 | 4500 | 80 | 59 | 65 | 176.4 | 0.84 | 29.79
DSG180*D | 15 | 4500 | 80 | 63 | 65 | 178.9 | 0.77 | 27.81
DSG180*D | 15 | 4500 | 80 | 67 | 65 | 184.1 | 0.65 | 24.13
DSG180*D | 15 | 4500 | 80 | 71 | 65 | 192.1 | 0.52 | 20.3
DSG180*D | 15 | 4500 | 80 | 59 | 75 | 174.8 | 0.84 | 29.73
DSG180*D | 15 | 4500 | 80 | 63 | 75 | 177.3 | 0.78 | 27.76
DSG180*D | 15 | 4500 | 80 | 67 | 75 | 182.5 | 0.65 | 24.08
DSG180*D | 15 | 4500 | 80 | 71 | 75 | 190.5 | 0.53 | 20.3
DSG180*D | 15 | 4500 | 80 | 59 | 85 | 170.3 | 0.87 | 30.01
DSG180*D | 15 | 4500 | 80 | 63 | 85 | 172.7 | 0.8 | 28.04
DSG180*D | 15 | 4500 | 80 | 67 | 85 | 178 | 0.68 | 24.36
DSG180*D | 15 | 4500 | 80 | 71 | 85 | 185.9 | 0.55 | 20.5
DSG180*D | 15 | 4500 | 80 | 59 | 95 | 162.4 | 0.91 | 29.71
DSG180*D | 15 | 4500 | 80 | 63 | 95 | 164.9 | 0.83 | 27.74
DSG180*D | 15 | 4500 | 80 | 67 | 95 | 170.1 | 0.7 | 24.06
DSG180*D | 15 | 4500 | 80 | 71 | 95 | 178.1 | 0.56 | 20.2
DSG180*D | 15 | 4500 | 80 | 59 | 105 | 152.8 | 0.95 | 29.45
DSG180*D | 15 | 4500 | 80 | 63 | 105 | 155.3 | 0.88 | 27.48
DSG180*D | 15 | 4500 | 80 | 67 | 105 | 160.5 | 0.73 | 23.79
DSG180*D | 15 | 4500 | 80 | 71 | 105 | 168.5 | 0.59 | 20
DSG180*D | 15 | 4500 | 80 | 59 | 115 | 144 | 1 | 29.09
DSG180*D | 15 | 4500 | 80 | 63 | 115 | 146.5 | 0.97 | 28.71
DSG180*D | 15 | 4500 | 80 | 67 | 115 | 151.7 | 0.82 | 25.03
DSG180*D | 15 | 4500 | 80 | 71 | 115 | 159.7 | 0.66 | 21.2
DSG180*D | 15 | 5012 | 80 | 59 | 65 | 178.3 | 0.89 | 28.83
DSG180*D | 15 | 5012 | 80 | 63 | 65 | 180.8 | 0.82 | 26.86
DSG180*D | 15 | 5012 | 80 | 67 | 65 | 186 | 0.69 | 23.18
DSG180*D | 15 | 5012 | 80 | 71 | 65 | 194 | 0.55 | 19.4
DSG180*D | 15 | 5012 | 80 | 59 | 75 | 176.7 | 0.9 | 28.78
DSG180*D | 15 | 5012 | 80 | 63 | 75 | 179.2 | 0.82 | 26.81
DSG180*D | 15 | 5012 | 80 | 67 | 75 | 184.4 | 0.69 | 23.12
DSG180*D | 15 | 5012 | 80 | 71 | 75 | 192.4 | 0.55 | 19.3
DSG180*D | 15 | 5012 | 80 | 59 | 85 | 172.2 | 0.93 | 29.05
DSG180*D | 15 | 5012 | 80 | 63 | 85 | 174.6 | 0.85 | 27.08
DSG180*D | 15 | 5012 | 80 | 67 | 85 | 179.9 | 0.72 | 23.4
DSG180*D | 15 | 5012 | 80 | 71 | 85 | 187.8 | 0.57 | 19.6
DSG180*D | 15 | 5012 | 80 | 59 | 95 | 164.3 | 0.96 | 28.76
DSG180*D | 15 | 5012 | 80 | 63 | 95 | 166.8 | 0.89 | 26.79
DSG180*D | 15 | 5012 | 80 | 67 | 95 | 172 | 0.74 | 23.1
DSG180*D | 15 | 5012 | 80 | 71 | 95 | 180 | 0.59 | 19.3
DSG180*D | 15 | 5012 | 80 | 59 | 105 | 154.7 | 1 | 28.06
DSG180*D | 15 | 5012 | 80 | 63 | 105 | 157.2 | 0.93 | 26.52
DSG180*D | 15 | 5012 | 80 | 67 | 105 | 162.4 | 0.78 | 22.84
DSG180*D | 15 | 5012 | 80 | 71 | 105 | 170.4 | 0.62 | 19
DSG180*D | 15 | 5012 | 80 | 59 | 115 | 145.9 | 1 | 26.47
DSG180*D | 15 | 5012 | 80 | 63 | 115 | 148.4 | 1 | 26.92
DSG180*D | 15 | 5012 | 80 | 67 | 115 | 153.6 | 0.86 | 24.07
DSG180*D | 15 | 5012 | 80 | 71 | 115 | 161.6 | 0.69 | 20.3
DSG180*D | 15 | 6000 | 80 | 59 | 65 | 182.9 | 0.99 | 27.3
DSG180*D | 15 | 6000 | 80 | 63 | 65 | 185.4 | 0.9 | 25.33
DSG180*D | 15 | 6000 | 80 | 67 | 65 | 190.6 | 0.75 | 21.65
DSG180*D | 15 | 6000 | 80 | 71 | 65 | 198.6 | 0.59 | 17.8
DSG180*D | 15 | 6000 | 80 | 59 | 75 | 181.3 | 0.99 | 27.25
DSG180*D | 15 | 6000 | 80 | 63 | 75 | 183.8 | 0.91 | 25.28
DSG180*D | 15 | 6000 | 80 | 67 | 75 | 189 | 0.75 | 21.6
DSG180*D | 15 | 6000 | 80 | 71 | 75 | 197 | 0.6 | 17.8
DSG180*D | 15 | 6000 | 80 | 59 | 85 | 176.8 | 1 | 26.78
DSG180*D | 15 | 6000 | 80 | 63 | 85 | 179.2 | 0.94 | 25.56
DSG180*D | 15 | 6000 | 80 | 67 | 85 | 184.5 | 0.78 | 21.87
DSG180*D | 15 | 6000 | 80 | 71 | 85 | 192.4 | 0.62 | 18.1
DSG180*D | 15 | 6000 | 80 | 59 | 95 | 168.9 | 1 | 25.59
DSG180*D | 15 | 6000 | 80 | 63 | 95 | 171.4 | 0.97 | 25.26
DSG180*D | 15 | 6000 | 80 | 67 | 95 | 176.6 | 0.81 | 21.58
DSG180*D | 15 | 6000 | 80 | 71 | 95 | 184.6 | 0.64 | 17.8
DSG180*D | 15 | 6000 | 80 | 59 | 105 | 159.3 | 1 | 24.14
DSG180*D | 15 | 6000 | 80 | 63 | 105 | 161.8 | 1 | 24.51
DSG180*D | 15 | 6000 | 80 | 67 | 105 | 167 | 0.84 | 21.31
DSG180*D | 15 | 6000 | 80 | 71 | 105 | 175 | 0.66 | 17.5
DSG180*D | 15 | 6000 | 80 | 59 | 115 | 150.5 | 1 | 22.81
DSG180*D | 15 | 6000 | 80 | 63 | 115 | 153 | 1 | 23.18
DSG180*D | 15 | 6000 | 80 | 67 | 115 | 158.2 | 0.94 | 22.55
DSG180*D | 15 | 6000 | 80 | 71 | 115 | 166.2 | 0.74 | 18.7
DSG180*D | 15 | 4500 | 85 | 59 | 65 | 179.3 | 0.93 | 33.66
DSG180*D | 15 | 4500 | 85 | 63 | 65 | 181.8 | 0.86 | 31.69
DSG180*D | 15 | 4500 | 85 | 67 | 65 | 187 | 0.74 | 28
DSG180*D | 15 | 4500 | 85 | 71 | 65 | 195 | 0.61 | 24.2
DSG180*D | 15 | 4500 | 85 | 59 | 75 | 177.8 | 0.94 | 33.6
DSG180*D | 15 | 4500 | 85 | 63 | 75 | 180.2 | 0.87 | 31.63
DSG180*D | 15 | 4500 | 85 | 67 | 75 | 185.5 | 0.75 | 27.95
DSG180*D | 15 | 4500 | 85 | 71 | 75 | 193.5 | 0.62 | 24.1
DSG180*D | 15 | 4500 | 85 | 59 | 85 | 173.2 | 0.97 | 33.88
DSG180*D | 15 | 4500 | 85 | 63 | 85 | 175.7 | 0.9 | 31.91
DSG180*D | 15 | 4500 | 85 | 67 | 85 | 180.9 | 0.77 | 28.23
DSG180*D | 15 | 4500 | 85 | 71 | 85 | 188.9 | 0.64 | 24.4
DSG180*D | 15 | 4500 | 85 | 59 | 95 | 165.3 | 1 | 33.4
DSG180*D | 15 | 4500 | 85 | 63 | 95 | 167.8 | 0.93 | 31.61
DSG180*D | 15 | 4500 | 85 | 67 | 95 | 173 | 0.8 | 27.93
DSG180*D | 15 | 4500 | 85 | 71 | 95 | 181 | 0.66 | 24.1
DSG180*D | 15 | 4500 | 85 | 59 | 105 | 155.7 | 1 | 31.46
DSG180*D | 15 | 4500 | 85 | 63 | 105 | 158.2 | 0.98 | 31.35
DSG180*D | 15 | 4500 | 85 | 67 | 105 | 163.4 | 0.84 | 27.67
DSG180*D | 15 | 4500 | 85 | 71 | 105 | 171.4 | 0.69 | 23.9
DSG180*D | 15 | 4500 | 85 | 59 | 115 | 147 | 1 | 29.69
DSG180*D | 15 | 4500 | 85 | 63 | 115 | 149.4 | 1 | 30.19
DSG180*D | 15 | 4500 | 85 | 67 | 115 | 154.7 | 0.92 | 28.9
DSG180*D | 15 | 4500 | 85 | 71 | 115 | 162.6 | 0.76 | 25.1
DSG180*D | 15 | 5012 | 85 | 59 | 65 | 181.2 | 0.99 | 32.7
DSG180*D | 15 | 5012 | 85 | 63 | 65 | 183.7 | 0.92 | 30.73
DSG180*D | 15 | 5012 | 85 | 67 | 65 | 188.9 | 0.79 | 27.05
DSG180*D | 15 | 5012 | 85 | 71 | 65 | 196.9 | 0.65 | 23.2
DSG180*D | 15 | 5012 | 85 | 59 | 75 | 179.7 | 1 | 32.59
DSG180*D | 15 | 5012 | 85 | 63 | 75 | 182.2 | 0.93 | 30.68
DSG180*D | 15 | 5012 | 85 | 67 | 75 | 187.4 | 0.79 | 26.99
DSG180*D | 15 | 5012 | 85 | 71 | 75 | 195.4 | 0.65 | 23.2
DSG180*D | 15 | 5012 | 85 | 59 | 85 | 175.1 | 1 | 31.76
DSG180*D | 15 | 5012 | 85 | 63 | 85 | 177.6 | 0.96 | 30.95
DSG180*D | 15 | 5012 | 85 | 67 | 85 | 182.8 | 0.82 | 27.27
DSG180*D | 15 | 5012 | 85 | 71 | 85 | 190.8 | 0.68 | 23.5
DSG180*D | 15 | 5012 | 85 | 59 | 95 | 167.2 | 1 | 30.34
DSG180*D | 15 | 5012 | 85 | 63 | 95 | 169.7 | 1 | 30.66
DSG180*D | 15 | 5012 | 85 | 67 | 95 | 174.9 | 0.85 | 26.97
DSG180*D | 15 | 5012 | 85 | 71 | 95 | 182.9 | 0.7 | 23.2
DSG180*D | 15 | 5012 | 85 | 59 | 105 | 157.6 | 1 | 28.59
DSG180*D | 15 | 5012 | 85 | 63 | 105 | 160.1 | 1 | 29.04
DSG180*D | 15 | 5012 | 85 | 67 | 105 | 165.3 | 0.89 | 26.71
DSG180*D | 15 | 5012 | 85 | 71 | 105 | 173.3 | 0.73 | 22.9
DSG180*D | 15 | 5012 | 85 | 59 | 115 | 148.9 | 1 | 27
DSG180*D | 15 | 5012 | 85 | 63 | 115 | 151.3 | 1 | 27.45
DSG180*D | 15 | 5012 | 85 | 67 | 115 | 156.6 | 0.98 | 27.95
DSG180*D | 15 | 5012 | 85 | 71 | 115 | 164.6 | 0.81 | 24.1
DSG180*D | 15 | 6000 | 85 | 59 | 65 | 185.8 | 1 | 28.16
DSG180*D | 15 | 6000 | 85 | 63 | 65 | 188.3 | 1 | 28.53
DSG180*D | 15 | 6000 | 85 | 67 | 65 | 193.5 | 0.87 | 25.52
DSG180*D | 15 | 6000 | 85 | 71 | 65 | 201.5 | 0.71 | 21.7
DSG180*D | 15 | 6000 | 85 | 59 | 75 | 184.3 | 1 | 27.92
DSG180*D | 15 | 6000 | 85 | 63 | 75 | 186.8 | 1 | 28.3
DSG180*D | 15 | 6000 | 85 | 67 | 75 | 192 | 0.88 | 25.47
DSG180*D | 15 | 6000 | 85 | 71 | 75 | 200 | 0.71 | 21.7
DSG180*D | 15 | 6000 | 85 | 59 | 85 | 179.7 | 1 | 27.23
DSG180*D | 15 | 6000 | 85 | 63 | 85 | 182.2 | 1 | 27.6
DSG180*D | 15 | 6000 | 85 | 67 | 85 | 187.4 | 0.91 | 25.75
DSG180*D | 15 | 6000 | 85 | 71 | 85 | 195.4 | 0.74 | 21.9
DSG180*D | 15 | 6000 | 85 | 59 | 95 | 171.8 | 1 | 26.04
DSG180*D | 15 | 6000 | 85 | 63 | 95 | 174.3 | 1 | 26.41
DSG180*D | 15 | 6000 | 85 | 67 | 95 | 179.5 | 0.94 | 25.45
DSG180*D | 15 | 6000 | 85 | 71 | 95 | 187.5 | 0.76 | 21.6
DSG180*D | 15 | 6000 | 85 | 59 | 105 | 162.2 | 1 | 24.58
DSG180*D | 15 | 6000 | 85 | 63 | 105 | 164.7 | 1 | 24.96
DSG180*D | 15 | 6000 | 85 | 67 | 105 | 169.9 | 0.98 | 25.18
DSG180*D | 15 | 6000 | 85 | 71 | 105 | 177.9 | 0.79 | 21.4
DSG180*D | 15 | 6000 | 85 | 59 | 115 | 153.5 | 1 | 23.25
DSG180*D | 15 | 6000 | 85 | 63 | 115 | 155.9 | 1 | 23.63
DSG180*D | 15 | 6000 | 85 | 67 | 115 | 161.2 | 1 | 24.42
DSG180*D | 15 | 6000 | 85 | 71 | 115 | 169.2 | 0.88 | 22.6
DSG240*D | 20 | 6000 | 70 | 59 | 65 | 234.4 | 0.58 | 20.7
DSG240*D | 20 | 6000 | 70 | 63 | 65 | 237.7 | 0.52 | 18.72
DSG240*D | 20 | 6000 | 70 | 67 | 65 | 244.7 | 0.41 | 15.04
DSG240*D | 20 | 6000 | 70 | 59 | 75 | 232.3 | 0.59 | 20.64
DSG240*D | 20 | 6000 | 70 | 63 | 75 | 235.6 | 0.52 | 18.67
DSG240*D | 20 | 6000 | 70 | 67 | 75 | 242.6 | 0.41 | 14.99
DSG240*D | 20 | 6000 | 70 | 59 | 85 | 226.2 | 0.61 | 20.92
DSG240*D | 20 | 6000 | 70 | 63 | 85 | 229.5 | 0.54 | 18.95
DSG240*D | 20 | 6000 | 70 | 67 | 85 | 236.5 | 0.43 | 15.27
DSG240*D | 20 | 6000 | 70 | 59 | 95 | 215.7 | 0.63 | 20.62
DSG240*D | 20 | 6000 | 70 | 63 | 95 | 219 | 0.56 | 18.65
DSG240*D | 20 | 6000 | 70 | 67 | 95 | 226 | 0.44 | 14.97
DSG240*D | 20 | 6000 | 70 | 59 | 105 | 202.8 | 0.66 | 20.36
DSG240*D | 20 | 6000 | 70 | 63 | 105 | 206.1 | 0.59 | 18.39
DSG240*D | 20 | 6000 | 70 | 67 | 105 | 213.1 | 0.46 | 14.71
DSG240*D | 20 | 6000 | 70 | 59 | 115 | 191.1 | 0.75 | 21.59
DSG240*D | 20 | 6000 | 70 | 63 | 115 | 194.4 | 0.67 | 19.62
DSG240*D | 20 | 6000 | 70 | 67 | 115 | 201.4 | 0.52 | 15.94
DSG240*D | 20 | 6400 | 70 | 59 | 65 | 236 | 0.6 | 20.13
DSG240*D | 20 | 6400 | 70 | 63 | 65 | 239.3 | 0.53 | 18.16
DSG240*D | 20 | 6400 | 70 | 67 | 65 | 246.3 | 0.41 | 14.48
DSG240*D | 20 | 6400 | 70 | 59 | 75 | 233.9 | 0.6 | 20.08
DSG240*D | 20 | 6400 | 70 | 63 | 75 | 237.2 | 0.54 | 18.1
DSG240*D | 20 | 6400 | 70 | 67 | 75 | 244.2 | 0.42 | 14.42
DSG240*D | 20 | 6400 | 70 | 59 | 85 | 227.8 | 0.63 | 20.35
DSG240*D | 20 | 6400 | 70 | 63 | 85 | 231.1 | 0.56 | 18.38
DSG240*D | 20 | 6400 | 70 | 67 | 85 | 238.1 | 0.43 | 14.7
DSG240*D | 20 | 6400 | 70 | 59 | 95 | 217.3 | 0.65 | 20.06
DSG240*D | 20 | 6400 | 70 | 63 | 95 | 220.6 | 0.58 | 18.08
DSG240*D | 20 | 6400 | 70 | 67 | 95 | 227.6 | 0.45 | 14.4
DSG240*D | 20 | 6400 | 70 | 59 | 105 | 204.4 | 0.68 | 19.79
DSG240*D | 20 | 6400 | 70 | 63 | 105 | 207.7 | 0.6 | 17.82
DSG240*D | 20 | 6400 | 70 | 67 | 105 | 214.7 | 0.46 | 14.14
DSG240*D | 20 | 6400 | 70 | 59 | 115 | 192.7 | 0.77 | 21.03
DSG240*D | 20 | 6400 | 70 | 63 | 115 | 196 | 0.68 | 19.06
DSG240*D | 20 | 6400 | 70 | 67 | 115 | 203 | 0.53 | 15.37
DSG240*D | 20 | 8000 | 70 | 59 | 65 | 244.1 | 0.66 | 18.24
DSG240*D | 20 | 8000 | 70 | 63 | 65 | 247.4 | 0.58 | 16.27
DSG240*D | 20 | 8000 | 70 | 67 | 65 | 254.4 | 0.44 | 12.58
DSG240*D | 20 | 8000 | 70 | 59 | 75 | 242 | 0.66 | 18.18
DSG240*D | 20 | 8000 | 70 | 63 | 75 | 245.3 | 0.58 | 16.21
DSG240*D | 20 | 8000 | 70 | 67 | 75 | 252.3 | 0.44 | 12.53
DSG240*D | 20 | 8000 | 70 | 59 | 85 | 235.9 | 0.69 | 18.46
DSG240*D | 20 | 8000 | 70 | 63 | 85 | 239.2 | 0.61 | 16.49
DSG240*D | 20 | 8000 | 70 | 67 | 85 | 246.2 | 0.46 | 12.81
DSG240*D | 20 | 8000 | 70 | 59 | 95 | 225.4 | 0.71 | 18.16
DSG240*D | 20 | 8000 | 70 | 63 | 95 | 228.7 | 0.62 | 16.19
DSG240*D | 20 | 8000 | 70 | 67 | 95 | 235.7 | 0.47 | 12.51
DSG240*D | 20 | 8000 | 70 | 59 | 105 | 212.6 | 0.74 | 17.9
DSG240*D | 20 | 8000 | 70 | 63 | 105 | 215.9 | 0.65 | 15.93
DSG240*D | 20 | 8000 | 70 | 67 | 105 | 222.9 | 0.48 | 12.25
DSG240*D | 20 | 8000 | 70 | 59 | 115 | 200.8 | 0.84 | 19.14
DSG240*D | 20 | 8000 | 70 | 63 | 115 | 204.1 | 0.74 | 17.16
DSG240*D | 20 | 8000 | 70 | 67 | 115 | 211.1 | 0.56 | 13.48
DSG240*D | 20 | 6000 | 75 | 59 | 65 | 235.6 | 0.7 | 25.03
DSG240*D | 20 | 6000 | 75 | 63 | 65 | 238.9 | 0.64 | 23.06
DSG240*D | 20 | 6000 | 75 | 67 | 65 | 245.9 | 0.52 | 19.38
DSG240*D | 20 | 6000 | 75 | 71 | 65 | 256.6 | 0.4 | 15.6
DSG240*D | 20 | 6000 | 75 | 59 | 75 | 233.5 | 0.71 | 24.98
DSG240*D | 20 | 6000 | 75 | 63 | 75 | 236.8 | 0.64 | 23.01
DSG240*D | 20 | 6000 | 75 | 67 | 75 | 243.8 | 0.52 | 19.32
DSG240*D | 20 | 6000 | 75 | 71 | 75 | 254.5 | 0.4 | 15.5
DSG240*D | 20 | 6000 | 75 | 59 | 85 | 227.4 | 0.73 | 25.26
DSG240*D | 20 | 6000 | 75 | 63 | 85 | 230.7 | 0.67 | 23.28
DSG240*D | 20 | 6000 | 75 | 67 | 85 | 237.7 | 0.54 | 19.6
DSG240*D | 20 | 6000 | 75 | 71 | 85 | 248.4 | 0.42 | 15.8
DSG240*D | 20 | 6000 | 75 | 59 | 95 | 216.9 | 0.76 | 24.96
DSG240*D | 20 | 6000 | 75 | 63 | 95 | 220.2 | 0.69 | 22.99
DSG240*D | 20 | 6000 | 75 | 67 | 95 | 227.2 | 0.56 | 19.3
DSG240*D | 20 | 6000 | 75 | 71 | 95 | 237.9 | 0.43 | 15.5
DSG240*D | 20 | 6000 | 75 | 59 | 105 | 204 | 0.8 | 24.69
DSG240*D | 20 | 6000 | 75 | 63 | 105 | 207.3 | 0.72 | 22.72
DSG240*D | 20 | 6000 | 75 | 67 | 105 | 214.3 | 0.59 | 19.04
DSG240*D | 20 | 6000 | 75 | 71 | 105 | 225 | 0.45 | 15.2
DSG240*D | 20 | 6000 | 75 | 59 | 115 | 192.3 | 0.89 | 25.93
DSG240*D | 20 | 6000 | 75 | 63 | 115 | 195.6 | 0.81 | 23.96
DSG240*D | 20 | 6000 | 75 | 67 | 115 | 202.6 | 0.66 | 20.28
DSG240*D | 20 | 6000 | 75 | 71 | 115 | 213.3 | 0.51 | 16.5
DSG240*D | 20 | 6400 | 75 | 59 | 65 | 237.2 | 0.73 | 24.47
DSG240*D | 20 | 6400 | 75 | 63 | 65 | 240.5 | 0.66 | 22.49
DSG240*D | 20 | 6400 | 75 | 67 | 65 | 247.5 | 0.54 | 18.81
DSG240*D | 20 | 6400 | 75 | 71 | 65 | 258.2 | 0.41 | 15
DSG240*D | 20 | 6400 | 75 | 59 | 75 | 235.1 | 0.73 | 24.41
DSG240*D | 20 | 6400 | 75 | 63 | 75 | 238.4 | 0.66 | 22.44
DSG240*D | 20 | 6400 | 75 | 67 | 75 | 245.4 | 0.54 | 18.76
DSG240*D | 20 | 6400 | 75 | 71 | 75 | 256.1 | 0.41 | 14.9
DSG240*D | 20 | 6400 | 75 | 59 | 85 | 229 | 0.76 | 24.69
DSG240*D | 20 | 6400 | 75 | 63 | 85 | 232.3 | 0.69 | 22.72
DSG240*D | 20 | 6400 | 75 | 67 | 85 | 239.3 | 0.56 | 19.04
DSG240*D | 20 | 6400 | 75 | 71 | 85 | 250 | 0.43 | 15.2
DSG240*D | 20 | 6400 | 75 | 59 | 95 | 218.5 | 0.79 | 24.39
DSG240*D | 20 | 6400 | 75 | 63 | 95 | 221.8 | 0.71 | 22.42
DSG240*D | 20 | 6400 | 75 | 67 | 95 | 228.8 | 0.58 | 18.74
DSG240*D | 20 | 6400 | 75 | 71 | 95 | 239.5 | 0.44 | 14.9
DSG240*D | 20 | 6400 | 75 | 59 | 105 | 205.6 | 0.83 | 24.13
DSG240*D | 20 | 6400 | 75 | 63 | 105 | 208.9 | 0.75 | 22.16
DSG240*D | 20 | 6400 | 75 | 67 | 105 | 215.9 | 0.6 | 18.47
DSG240*D | 20 | 6400 | 75 | 71 | 105 | 226.6 | 0.46 | 14.7
DSG240*D | 20 | 6400 | 75 | 59 | 115 | 193.9 | 0.92 | 25.36
DSG240*D | 20 | 6400 | 75 | 63 | 115 | 197.2 | 0.83 | 23.39
DSG240*D | 20 | 6400 | 75 | 67 | 115 | 204.2 | 0.68 | 19.71
DSG240*D | 20 | 6400 | 75 | 71 | 115 | 214.9 | 0.52 | 15.9
DSG240*D | 20 | 8000 | 75 | 59 | 65 | 245.3 | 0.81 | 22.57
DSG240*D | 20 | 8000 | 75 | 63 | 65 | 248.6 | 0.73 | 20.6
DSG240*D | 20 | 8000 | 75 | 67 | 65 | 255.6 | 0.58 | 16.92
DSG240*D | 20 | 8000 | 75 | 71 | 65 | 266.3 | 0.43 | 13.1
DSG240*D | 20 | 8000 | 75 | 59 | 75 | 243.2 | 0.81 | 22.52
DSG240*D | 20 | 8000 | 75 | 63 | 75 | 246.5 | 0.73 | 20.55
DSG240*D | 20 | 8000 | 75 | 67 | 75 | 253.5 | 0.59 | 16.87
DSG240*D | 20 | 8000 | 75 | 71 | 75 | 264.2 | 0.43 | 13.1
DSG240*D | 20 | 8000 | 75 | 59 | 85 | 237.1 | 0.85 | 22.8
DSG240*D | 20 | 8000 | 75 | 63 | 85 | 240.4 | 0.76 | 20.83
DSG240*D | 20 | 8000 | 75 | 67 | 85 | 247.4 | 0.61 | 17.14
DSG240*D | 20 | 8000 | 75 | 71 | 85 | 258.1 | 0.45 | 13.3
DSG240*D | 20 | 8000 | 75 | 59 | 95 | 226.6 | 0.87 | 22.5
DSG240*D | 20 | 8000 | 75 | 63 | 95 | 229.9 | 0.79 | 20.53
DSG240*D | 20 | 8000 | 75 | 67 | 95 | 236.9 | 0.63 | 16.85
DSG240*D | 20 | 8000 | 75 | 71 | 95 | 247.6 | 0.46 | 13
DSG240*D | 20 | 8000 | 75 | 59 | 105 | 213.8 | 0.92 | 22.24
DSG240*D | 20 | 8000 | 75 | 63 | 105 | 217.1 | 0.82 | 20.26
DSG240*D | 20 | 8000 | 75 | 67 | 105 | 224.1 | 0.65 | 16.58
DSG240*D | 20 | 8000 | 75 | 71 | 105 | 234.7 | 0.48 | 12.8
DSG240*D | 20 | 8000 | 75 | 59 | 115 | 202 | 1 | 22.96
DSG240*D | 20 | 8000 | 75 | 63 | 115 | 205.3 | 0.92 | 21.5
DSG240*D | 20 | 8000 | 75 | 67 | 115 | 212.3 | 0.74 | 17.82
DSG240*D | 20 | 8000 | 75 | 71 | 115 | 223 | 0.55 | 14
DSG240*D | 20 | 6000 | 80 | 59 | 65 | 236.8 | 0.82 | 29.4
DSG240*D | 20 | 6000 | 80 | 63 | 65 | 240.1 | 0.75 | 27.43
DSG240*D | 20 | 6000 | 80 | 67 | 65 | 247.1 | 0.63 | 23.74
DSG240*D | 20 | 6000 | 80 | 71 | 65 | 257.8 | 0.51 | 19.9
DSG240*D | 20 | 6000 | 80 | 59 | 75 | 234.7 | 0.83 | 29.34
DSG240*D | 20 | 6000 | 80 | 63 | 75 | 238 | 0.76 | 27.37
DSG240*D | 20 | 6000 | 80 | 67 | 75 | 245 | 0.64 | 23.69
DSG240*D | 20 | 6000 | 80 | 71 | 75 | 255.7 | 0.51 | 19.9
DSG240*D | 20 | 6000 | 80 | 59 | 85 | 228.6 | 0.86 | 29.62
DSG240*D | 20 | 6000 | 80 | 63 | 85 | 231.9 | 0.79 | 27.65
DSG240*D | 20 | 6000 | 80 | 67 | 85 | 238.9 | 0.66 | 23.97
DSG240*D | 20 | 6000 | 80 | 71 | 85 | 249.6 | 0.53 | 20.2
DSG240*D | 20 | 6000 | 80 | 59 | 95 | 218.1 | 0.89 | 29.32
DSG240*D | 20 | 6000 | 80 | 63 | 95 | 221.4 | 0.82 | 27.35
DSG240*D | 20 | 6000 | 80 | 67 | 95 | 228.4 | 0.68 | 23.67
DSG240*D | 20 | 6000 | 80 | 71 | 95 | 239.1 | 0.55 | 19.9
DSG240*D | 20 | 6000 | 80 | 59 | 105 | 205.2 | 0.93 | 29.06
DSG240*D | 20 | 6000 | 80 | 63 | 105 | 208.6 | 0.86 | 27.09
DSG240*D | 20 | 6000 | 80 | 67 | 105 | 215.5 | 0.72 | 23.41
DSG240*D | 20 | 6000 | 80 | 71 | 105 | 226.2 | 0.57 | 19.6
DSG240*D | 20 | 6000 | 80 | 59 | 115 | 193.5 | 1 | 29.32
DSG240*D | 20 | 6000 | 80 | 63 | 115 | 196.8 | 0.95 | 28.32
DSG240*D | 20 | 6000 | 80 | 67 | 115 | 203.8 | 0.8 | 24.64
DSG240*D | 20 | 6000 | 80 | 71 | 115 | 214.5 | 0.64 | 20.8
DSG240*D | 20 | 6400 | 80 | 59 | 65 | 238.4 | 0.85 | 28.83
DSG240*D | 20 | 6400 | 80 | 63 | 65 | 241.7 | 0.78 | 26.86
DSG240*D | 20 | 6400 | 80 | 67 | 65 | 248.7 | 0.66 | 23.18
DSG240*D | 20 | 6400 | 80 | 71 | 65 | 259.4 | 0.53 | 19.4
DSG240*D | 20 | 6400 | 80 | 59 | 75 | 236.3 | 0.86 | 28.78
DSG240*D | 20 | 6400 | 80 | 63 | 75 | 239.6 | 0.79 | 26.81
DSG240*D | 20 | 6400 | 80 | 67 | 75 | 246.6 | 0.66 | 23.12
DSG240*D | 20 | 6400 | 80 | 71 | 75 | 257.3 | 0.53 | 19.3
DSG240*D | 20 | 6400 | 80 | 59 | 85 | 230.2 | 0.89 | 29.05
DSG240*D | 20 | 6400 | 80 | 63 | 85 | 233.5 | 0.82 | 27.08
DSG240*D | 20 | 6400 | 80 | 67 | 85 | 240.5 | 0.68 | 23.4
DSG240*D | 20 | 6400 | 80 | 71 | 85 | 251.2 | 0.55 | 19.6
DSG240*D | 20 | 6400 | 80 | 59 | 95 | 219.7 | 0.92 | 28.76
DSG240*D | 20 | 6400 | 80 | 63 | 95 | 223 | 0.85 | 26.79
DSG240*D | 20 | 6400 | 80 | 67 | 95 | 230 | 0.71 | 23.1
DSG240*D | 20 | 6400 | 80 | 71 | 95 | 240.7 | 0.56 | 19.3
DSG240*D | 20 | 6400 | 80 | 59 | 105 | 206.9 | 0.97 | 28.49
DSG240*D | 20 | 6400 | 80 | 63 | 105 | 210.2 | 0.89 | 26.52
DSG240*D | 20 | 6400 | 80 | 67 | 105 | 217.2 | 0.74 | 22.84
DSG240*D | 20 | 6400 | 80 | 71 | 105 | 227.8 | 0.59 | 19
DSG240*D | 20 | 6400 | 80 | 59 | 115 | 195.1 | 1 | 27.72
DSG240*D | 20 | 6400 | 80 | 63 | 115 | 198.4 | 0.98 | 27.76
DSG240*D | 20 | 6400 | 80 | 67 | 115 | 205.4 | 0.83 | 24.07
DSG240*D | 20 | 6400 | 80 | 71 | 115 | 216.1 | 0.66 | 20.3
DSG240*D | 20 | 8000 | 80 | 59 | 65 | 246.5 | 0.96 | 26.94
DSG240*D | 20 | 8000 | 80 | 63 | 65 | 249.9 | 0.88 | 24.97
DSG240*D | 20 | 8000 | 80 | 67 | 65 | 256.8 | 0.73 | 21.29
DSG240*D | 20 | 8000 | 80 | 71 | 65 | 267.5 | 0.57 | 17.5
DSG240*D | 20 | 8000 | 80 | 59 | 75 | 244.5 | 0.97 | 26.89
DSG240*D | 20 | 8000 | 80 | 63 | 75 | 247.8 | 0.88 | 24.91
DSG240*D | 20 | 8000 | 80 | 67 | 75 | 254.7 | 0.73 | 21.23
DSG240*D | 20 | 8000 | 80 | 71 | 75 | 265.4 | 0.58 | 17.4
DSG240*D | 20 | 8000 | 80 | 59 | 85 | 238.3 | 1 | 27.08
DSG240*D | 20 | 8000 | 80 | 63 | 85 | 241.6 | 0.92 | 25.19
DSG240*D | 20 | 8000 | 80 | 67 | 85 | 248.6 | 0.76 | 21.51
DSG240*D | 20 | 8000 | 80 | 71 | 85 | 259.3 | 0.6 | 17.7
DSG240*D | 20 | 8000 | 80 | 59 | 95 | 227.8 | 1 | 25.89
DSG240*D | 20 | 8000 | 80 | 63 | 95 | 231.1 | 0.95 | 24.89
DSG240*D | 20 | 8000 | 80 | 67 | 95 | 238.1 | 0.78 | 21.21
DSG240*D | 20 | 8000 | 80 | 71 | 95 | 248.8 | 0.62 | 17.4
DSG240*D | 20 | 8000 | 80 | 59 | 105 | 215 | 1 | 24.43
DSG240*D | 20 | 8000 | 80 | 63 | 105 | 218.3 | 0.99 | 24.63
DSG240*D | 20 | 8000 | 80 | 67 | 105 | 225.3 | 0.82 | 20.95
DSG240*D | 20 | 8000 | 80 | 71 | 105 | 236 | 0.64 | 17.1
DSG240*D | 20 | 8000 | 80 | 59 | 115 | 203.3 | 1 | 23.1
DSG240*D | 20 | 8000 | 80 | 63 | 115 | 206.6 | 1 | 23.47
DSG240*D | 20 | 8000 | 80 | 67 | 115 | 213.5 | 0.91 | 22.18
DSG240*D | 20 | 8000 | 80 | 71 | 115 | 224.2 | 0.72 | 18.4
DSG240*D | 20 | 6000 | 85 | 59 | 65 | 240.8 | 0.91 | 33.27
DSG240*D | 20 | 6000 | 85 | 63 | 65 | 244.1 | 0.85 | 31.3
DSG240*D | 20 | 6000 | 85 | 67 | 65 | 251.1 | 0.73 | 27.61
DSG240*D | 20 | 6000 | 85 | 71 | 65 | 261.7 | 0.6 | 23.8
DSG240*D | 20 | 6000 | 85 | 59 | 75 | 238.7 | 0.92 | 33.21
DSG240*D | 20 | 6000 | 85 | 63 | 75 | 242 | 0.85 | 31.24
DSG240*D | 20 | 6000 | 85 | 67 | 75 | 249 | 0.73 | 27.56
DSG240*D | 20 | 6000 | 85 | 71 | 75 | 259.6 | 0.6 | 23.7
DSG240*D | 20 | 6000 | 85 | 59 | 85 | 232.6 | 0.95 | 33.49
DSG240*D | 20 | 6000 | 85 | 63 | 85 | 235.9 | 0.88 | 31.52
DSG240*D | 20 | 6000 | 85 | 67 | 85 | 242.8 | 0.76 | 27.84
DSG240*D | 20 | 6000 | 85 | 71 | 85 | 253.5 | 0.63 | 24
DSG240*D | 20 | 6000 | 85 | 59 | 95 | 222 | 0.99 | 33.19
DSG240*D | 20 | 6000 | 85 | 63 | 95 | 225.3 | 0.91 | 31.22
DSG240*D | 20 | 6000 | 85 | 67 | 95 | 232.3 | 0.78 | 27.54
DSG240*D | 20 | 6000 | 85 | 71 | 95 | 243 | 0.64 | 23.7
DSG240*D | 20 | 6000 | 85 | 59 | 105 | 209.2 | 1 | 31.7
DSG240*D | 20 | 6000 | 85 | 63 | 105 | 212.5 | 0.96 | 30.96
DSG240*D | 20 | 6000 | 85 | 67 | 105 | 219.5 | 0.82 | 27.28
DSG240*D | 20 | 6000 | 85 | 71 | 105 | 230.2 | 0.67 | 23.5
DSG240*D | 20 | 6000 | 85 | 59 | 115 | 197.5 | 1 | 29.92
DSG240*D | 20 | 6000 | 85 | 63 | 115 | 200.8 | 1 | 30.42
DSG240*D | 20 | 6000 | 85 | 67 | 115 | 207.8 | 0.91 | 28.51
DSG240*D | 20 | 6000 | 85 | 71 | 115 | 218.4 | 0.75 | 24.7
DSG240*D | 20 | 6400 | 85 | 59 | 65 | 242.4 | 0.95 | 32.7
DSG240*D | 20 | 6400 | 85 | 63 | 65 | 245.7 | 0.88 | 30.73
DSG240*D | 20 | 6400 | 85 | 67 | 65 | 252.7 | 0.75 | 27.05
DSG240*D | 20 | 6400 | 85 | 71 | 65 | 263.3 | 0.62 | 23.2
DSG240*D | 20 | 6400 | 85 | 59 | 75 | 240.3 | 0.96 | 32.65
DSG240*D | 20 | 6400 | 85 | 63 | 75 | 243.6 | 0.89 | 30.68
DSG240*D | 20 | 6400 | 85 | 67 | 75 | 250.6 | 0.76 | 26.99
DSG240*D | 20 | 6400 | 85 | 71 | 75 | 261.2 | 0.62 | 23.2
DSG240*D | 20 | 6400 | 85 | 59 | 85 | 234.2 | 0.99 | 32.93
DSG240*D | 20 | 6400 | 85 | 63 | 85 | 237.5 | 0.92 | 30.95
DSG240*D | 20 | 6400 | 85 | 67 | 85 | 244.5 | 0.79 | 27.27
DSG240*D | 20 | 6400 | 85 | 71 | 85 | 255.1 | 0.65 | 23.5
DSG240*D | 20 | 6400 | 85 | 59 | 95 | 223.6 | 1 | 31.77
DSG240*D | 20 | 6400 | 85 | 63 | 95 | 227 | 0.95 | 30.66
DSG240*D | 20 | 6400 | 85 | 67 | 95 | 233.9 | 0.81 | 26.97
DSG240*D | 20 | 6400 | 85 | 71 | 95 | 244.6 | 0.67 | 23.2
DSG240*D | 20 | 6400 | 85 | 59 | 105 | 210.8 | 1 | 29.94
DSG240*D | 20 | 6400 | 85 | 63 | 105 | 214.1 | 1 | 30.39
DSG240*D | 20 | 6400 | 85 | 67 | 105 | 221.1 | 0.85 | 26.71
DSG240*D | 20 | 6400 | 85 | 71 | 105 | 231.8 | 0.7 | 22.9
DSG240*D | 20 | 6400 | 85 | 59 | 115 | 199.1 | 1 | 28.28
DSG240*D | 20 | 6400 | 85 | 63 | 115 | 202.4 | 1 | 28.75
DSG240*D | 20 | 6400 | 85 | 67 | 115 | 209.4 | 0.94 | 27.95
DSG240*D | 20 | 6400 | 85 | 71 | 115 | 220 | 0.77 | 24.1
DSG240*D | 20 | 8000 | 85 | 59 | 65 | 250.5 | 1 | 28.46
DSG240*D | 20 | 8000 | 85 | 63 | 65 | 253.8 | 1 | 28.84
DSG240*D | 20 | 8000 | 85 | 67 | 65 | 260.8 | 0.85 | 25.16
DSG240*D | 20 | 8000 | 85 | 71 | 65 | 271.5 | 0.69 | 21.3
DSG240*D | 20 | 8000 | 85 | 59 | 75 | 248.4 | 1 | 28.23
DSG240*D | 20 | 8000 | 85 | 63 | 75 | 251.7 | 1 | 28.6
DSG240*D | 20 | 8000 | 85 | 67 | 75 | 258.7 | 0.85 | 25.1
DSG240*D | 20 | 8000 | 85 | 71 | 75 | 269.4 | 0.7 | 21.3
DSG240*D | 20 | 8000 | 85 | 59 | 85 | 242.3 | 1 | 27.53
DSG240*D | 20 | 8000 | 85 | 63 | 85 | 245.6 | 1 | 27.91
DSG240*D | 20 | 8000 | 85 | 67 | 85 | 252.6 | 0.88 | 25.38
DSG240*D | 20 | 8000 | 85 | 71 | 85 | 263.3 | 0.72 | 21.6
DSG240*D | 20 | 8000 | 85 | 59 | 95 | 231.8 | 1 | 26.34
DSG240*D | 20 | 8000 | 85 | 63 | 95 | 235.1 | 1 | 26.71
DSG240*D | 20 | 8000 | 85 | 67 | 95 | 242.1 | 0.91 | 25.08
DSG240*D | 20 | 8000 | 85 | 71 | 95 | 252.7 | 0.74 | 21.3
DSG240*D | 20 | 8000 | 85 | 59 | 105 | 218.9 | 1 | 24.88
DSG240*D | 20 | 8000 | 85 | 63 | 105 | 222.2 | 1 | 25.25
DSG240*D | 20 | 8000 | 85 | 67 | 105 | 229.2 | 0.95 | 24.82
DSG240*D | 20 | 8000 | 85 | 71 | 105 | 239.9 | 0.77 | 21
DSG240*D | 20 | 8000 | 85 | 59 | 115 | 207.2 | 1 | 23.54
DSG240*D | 20 | 8000 | 85 | 63 | 115 | 210.5 | 1 | 23.92
DSG240*D | 20 | 8000 | 85 | 67 | 115 | 217.5 | 1 | 24.71
DSG240*D | 20 | 8000 | 85 | 71 | 115 | 228.2 | 0.86 | 22.2
DSG300*D | 25 | 7500 | 70 | 59 | 65 | 296.9 | 0.56 | 20.17
DSG300*D | 25 | 7500 | 70 | 63 | 65 | 301.1 | 0.5 | 18.21
DSG300*D | 25 | 7500 | 70 | 67 | 65 | 309.9 | 0.39 | 14.55
DSG300*D | 25 | 7500 | 70 | 59 | 75 | 294.3 | 0.56 | 20.12
DSG300*D | 25 | 7500 | 70 | 63 | 75 | 298.4 | 0.5 | 18.16
DSG300*D | 25 | 7500 | 70 | 67 | 75 | 307.2 | 0.39 | 14.5
DSG300*D | 25 | 7500 | 70 | 59 | 85 | 286.6 | 0.59 | 20.39
DSG300*D | 25 | 7500 | 70 | 63 | 85 | 290.7 | 0.52 | 18.43
DSG300*D | 25 | 7500 | 70 | 67 | 85 | 299.5 | 0.41 | 14.78
DSG300*D | 25 | 7500 | 70 | 59 | 95 | 273.3 | 0.61 | 20.1
DSG300*D | 25 | 7500 | 70 | 63 | 95 | 277.5 | 0.54 | 18.14
DSG300*D | 25 | 7500 | 70 | 67 | 95 | 286.3 | 0.42 | 14.48
DSG300*D | 25 | 7500 | 70 | 59 | 105 | 257.1 | 0.64 | 19.83
DSG300*D | 25 | 7500 | 70 | 63 | 105 | 261.3 | 0.56 | 17.88
DSG300*D | 25 | 7500 | 70 | 67 | 105 | 270.1 | 0.43 | 14.22
DSG300*D | 25 | 7500 | 70 | 59 | 115 | 242.3 | 0.72 | 21.06
DSG300*D | 25 | 7500 | 70 | 63 | 115 | 246.5 | 0.64 | 19.1
DSG300*D | 25 | 7500 | 70 | 67 | 115 | 255.3 | 0.5 | 15.44
DSG300*D | 25 | 7650 | 70 | 59 | 65 | 297.6 | 0.57 | 20
DSG300*D | 25 | 7650 | 70 | 63 | 65 | 301.7 | 0.5 | 18.04
DSG300*D | 25 | 7650 | 70 | 67 | 65 | 310.5 | 0.39 | 14.38
DSG300*D | 25 | 7650 | 70 | 59 | 75 | 294.9 | 0.57 | 19.95
DSG300*D | 25 | 7650 | 70 | 63 | 75 | 299.1 | 0.51 | 17.99
DSG300*D | 25 | 7650 | 70 | 67 | 75 | 307.9 | 0.39 | 14.33
DSG300*D | 25 | 7650 | 70 | 59 | 85 | 287.2 | 0.59 | 20.22
DSG300*D | 25 | 7650 | 70 | 63 | 85 | 291.4 | 0.53 | 18.26
DSG300*D | 25 | 7650 | 70 | 67 | 85 | 300.2 | 0.41 | 14.6
DSG300*D | 25 | 7650 | 70 | 59 | 95 | 274 | 0.61 | 19.93
DSG300*D | 25 | 7650 | 70 | 63 | 95 | 278.1 | 0.54 | 17.97
DSG300*D | 25 | 7650 | 70 | 67 | 95 | 286.9 | 0.42 | 14.31
DSG300*D | 25 | 7650 | 70 | 59 | 105 | 257.8 | 0.64 | 19.66
DSG300*D | 25 | 7650 | 70 | 63 | 105 | 261.9 | 0.57 | 17.7
DSG300*D | 25 | 7650 | 70 | 67 | 105 | 270.7 | 0.44 | 14.05
DSG300*D | 25 | 7650 | 70 | 59 | 115 | 243 | 0.72 | 20.89
DSG300*D | 25 | 7650 | 70 | 63 | 115 | 247.1 | 0.64 | 18.93
DSG300*D | 25 | 7650 | 70 | 67 | 115 | 256 | 0.5 | 15.27
DSG300*D | 25 | 10000 | 70 | 59 | 65 | 310.7 | 0.63 | 17.74
DSG300*D | 25 | 10000 | 70 | 63 | 65 | 314.9 | 0.55 | 15.78
DSG300*D | 25 | 10000 | 70 | 67 | 65 | 323.7 | 0.41 | 12.12
DSG300*D | 25 | 10000 | 70 | 59 | 75 | 308.1 | 0.63 | 17.69
DSG300*D | 25 | 10000 | 70 | 63 | 75 | 312.2 | 0.55 | 15.73
DSG300*D | 25 | 10000 | 70 | 67 | 75 | 321.1 | 0.41 | 12.07
DSG300*D | 25 | 10000 | 70 | 59 | 85 | 300.4 | 0.66 | 17.96
DSG300*D | 25 | 10000 | 70 | 63 | 85 | 304.5 | 0.58 | 16
DSG300*D | 25 | 10000 | 70 | 67 | 85 | 313.4 | 0.43 | 12.34
DSG300*D | 25 | 10000 | 70 | 59 | 95 | 287.1 | 0.68 | 17.67
DSG300*D | 25 | 10000 | 70 | 63 | 95 | 291.3 | 0.59 | 15.71
DSG300*D | 25 | 10000 | 70 | 67 | 95 | 300.1 | 0.44 | 12.05
DSG300*D | 25 | 10000 | 70 | 59 | 105 | 270.9 | 0.71 | 17.4
DSG300*D | 25 | 10000 | 70 | 63 | 105 | 275.1 | 0.62 | 15.44
DSG300*D | 25 | 10000 | 70 | 67 | 105 | 283.9 | 0.46 | 11.79
DSG300*D | 25 | 10000 | 70 | 59 | 115 | 256.1 | 0.8 | 18.63
DSG300*D | 25 | 10000 | 70 | 63 | 115 | 260.3 | 0.7 | 16.67
DSG300*D | 25 | 10000 | 70 | 67 | 115 | 269.1 | 0.53 | 13.01
DSG300*D | 25 | 7500 | 75 | 59 | 65 | 298.4 | 0.68 | 24.48
DSG300*D | 25 | 7500 | 75 | 63 | 65 | 302.6 | 0.61 | 22.52
DSG300*D | 25 | 7500 | 75 | 67 | 65 | 311.4 | 0.5 | 18.86
DSG300*D | 25 | 7500 | 75 | 71 | 65 | 324.9 | 0.38 | 15.1
DSG300*D | 25 | 7500 | 75 | 59 | 75 | 295.8 | 0.68 | 24.42
DSG300*D | 25 | 7500 | 75 | 63 | 75 | 300 | 0.62 | 22.46
DSG300*D | 25 | 7500 | 75 | 67 | 75 | 308.8 | 0.5 | 18.81
DSG300*D | 25 | 7500 | 75 | 71 | 75 | 322.2 | 0.38 | 15
DSG300*D | 25 | 7500 | 75 | 59 | 85 | 288.1 | 0.71 | 24.7
DSG300*D | 25 | 7500 | 75 | 63 | 85 | 292.3 | 0.64 | 22.74
DSG300*D | 25 | 7500 | 75 | 67 | 85 | 301.1 | 0.52 | 19.08
DSG300*D | 25 | 7500 | 75 | 71 | 85 | 314.5 | 0.4 | 15.3
DSG300*D | 25 | 7500 | 75 | 59 | 95 | 274.8 | 0.73 | 24.4
DSG300*D | 25 | 7500 | 75 | 63 | 95 | 279 | 0.66 | 22.44
DSG300*D | 25 | 7500 | 75 | 67 | 95 | 287.8 | 0.54 | 18.79
DSG300*D | 25 | 7500 | 75 | 71 | 95 | 301.3 | 0.41 | 15
DSG300*D | 25 | 7500 | 75 | 59 | 105 | 258.6 | 0.77 | 24.14
DSG300*D | 25 | 7500 | 75 | 63 | 105 | 262.8 | 0.7 | 22.18
DSG300*D | 25 | 7500 | 75 | 67 | 105 | 271.6 | 0.56 | 18.53
DSG300*D | 25 | 7500 | 75 | 71 | 105 | 285.1 | 0.43 | 14.7
DSG300*D | 25 | 7500 | 75 | 59 | 115 | 243.8 | 0.86 | 25.37
DSG300*D | 25 | 7500 | 75 | 63 | 115 | 248 | 0.78 | 23.41
DSG300*D | 25 | 7500 | 75 | 67 | 115 | 256.8 | 0.63 | 19.75
DSG300*D | 25 | 7500 | 75 | 71 | 115 | 270.3 | 0.49 | 16
DSG300*D | 25 | 7650 | 75 | 59 | 65 | 299.1 | 0.68 | 24.31
DSG300*D | 25 | 7650 | 75 | 63 | 65 | 303.3 | 0.62 | 22.35
DSG300*D | 25 | 7650 | 75 | 67 | 65 | 312.1 | 0.5 | 18.69
DSG300*D | 25 | 7650 | 75 | 71 | 65 | 325.5 | 0.39 | 14.9
DSG300*D | 25 | 7650 | 75 | 59 | 75 | 296.4 | 0.69 | 24.25
DSG300*D | 25 | 7650 | 75 | 63 | 75 | 300.6 | 0.62 | 22.29
DSG300*D | 25 | 7650 | 75 | 67 | 75 | 309.4 | 0.51 | 18.64
DSG300*D | 25 | 7650 | 75 | 71 | 75 | 322.9 | 0.39 | 14.8
DSG300*D | 25 | 7650 | 75 | 59 | 85 | 288.7 | 0.71 | 24.53
DSG300*D | 25 | 7650 | 75 | 63 | 85 | 292.9 | 0.65 | 22.57
DSG300*D | 25 | 7650 | 75 | 67 | 85 | 301.7 | 0.53 | 18.91
DSG300*D | 25 | 7650 | 75 | 71 | 85 | 315.2 | 0.4 | 15.1
DSG300*D | 25 | 7650 | 75 | 59 | 95 | 275.5 | 0.74 | 24.23
DSG300*D | 25 | 7650 | 75 | 63 | 95 | 279.7 | 0.67 | 22.27
DSG300*D | 25 | 7650 | 75 | 67 | 95 | 288.5 | 0.54 | 18.62
DSG300*D | 25 | 7650 | 75 | 71 | 95 | 301.9 | 0.41 | 14.8
DSG300*D | 25 | 7650 | 75 | 59 | 105 | 259.3 | 0.78 | 23.97
DSG300*D | 25 | 7650 | 75 | 63 | 105 | 263.5 | 0.7 | 22.01
DSG300*D | 25 | 7650 | 75 | 67 | 105 | 272.3 | 0.57 | 18.35
DSG300*D | 25 | 7650 | 75 | 71 | 105 | 285.7 | 0.43 | 14.6
DSG300*D | 25 | 7650 | 75 | 59 | 115 | 244.5 | 0.87 | 25.2
DSG300*D | 25 | 7650 | 75 | 63 | 115 | 248.7 | 0.79 | 23.24
DSG300*D | 25 | 7650 | 75 | 67 | 115 | 257.5 | 0.64 | 19.58
DSG300*D | 25 | 7650 | 75 | 71 | 115 | 270.9 | 0.49 | 15.8
DSG300*D | 25 | 10000 | 75 | 59 | 65 | 312.2 | 0.78 | 22.05
DSG300*D | 25 | 10000 | 75 | 63 | 65 | 316.4 | 0.7 | 20.09
DSG300*D | 25 | 10000 | 75 | 67 | 65 | 325.2 | 0.56 | 16.43
DSG300*D | 25 | 10000 | 75 | 71 | 65 | 338.7 | 0.41 | 12.6
DSG300*D | 25 | 10000 | 75 | 59 | 75 | 309.6 | 0.78 | 21.99
DSG300*D | 25 | 10000 | 75 | 63 | 75 | 313.8 | 0.7 | 20.03
DSG300*D | 25 | 10000 | 75 | 67 | 75 | 322.6 | 0.56 | 16.38
DSG300*D | 25 | 10000 | 75 | 71 | 75 | 336 | 0.41 | 12.6
DSG300*D | 25 | 10000 | 75 | 59 | 85 | 301.9 | 0.81 | 22.27
DSG300*D | 25 | 10000 | 75 | 63 | 85 | 306.1 | 0.73 | 20.31
DSG300*D | 25 | 10000 | 75 | 67 | 85 | 314.9 | 0.58 | 16.65
DSG300*D | 25 | 10000 | 75 | 71 | 85 | 328.3 | 0.43 | 12.9
DSG300*D | 25 | 10000 | 75 | 59 | 95 | 288.6 | 0.84 | 21.97
DSG300*D | 25 | 10000 | 75 | 63 | 95 | 292.8 | 0.75 | 20.01
DSG300*D | 25 | 10000 | 75 | 67 | 95 | 301.6 | 0.6 | 16.36
DSG300*D | 25 | 10000 | 75 | 71 | 95 | 315.1 | 0.44 | 12.6
DSG300*D | 25 | 10000 | 75 | 59 | 105 | 272.4 | 0.88 | 21.71
DSG300*D | 25 | 10000 | 75 | 63 | 105 | 276.6 | 0.79 | 19.75
DSG300*D | 25 | 10000 | 75 | 67 | 105 | 285.4 | 0.62 | 16.09
DSG300*D | 25 | 10000 | 75 | 71 | 105 | 298.9 | 0.45 | 12.3
DSG300*D | 25 | 10000 | 75 | 59 | 115 | 257.7 | 0.98 | 22.94
DSG300*D | 25 | 10000 | 75 | 63 | 115 | 261.8 | 0.88 | 20.98
DSG300*D | 25 | 10000 | 75 | 67 | 115 | 270.6 | 0.7 | 17.32
DSG300*D | 25 | 10000 | 75 | 71 | 115 | 284.1 | 0.52 | 13.5
DSG300*D | 25 | 7500 | 80 | 59 | 65 | 300 | 0.79 | 28.81
DSG300*D | 25 | 7500 | 80 | 63 | 65 | 304.1 | 0.73 | 26.85
DSG300*D | 25 | 7500 | 80 | 67 | 65 | 312.9 | 0.61 | 23.2
DSG300*D | 25 | 7500 | 80 | 71 | 65 | 326.4 | 0.49 | 19.4
DSG300*D | 25 | 7500 | 80 | 59 | 75 | 297.3 | 0.8 | 28.76
DSG300*D | 25 | 7500 | 80 | 63 | 75 | 301.5 | 0.73 | 26.8
DSG300*D | 25 | 7500 | 80 | 67 | 75 | 310.3 | 0.62 | 23.14
DSG300*D | 25 | 7500 | 80 | 71 | 75 | 323.8 | 0.49 | 19.4
DSG300*D | 25 | 7500 | 80 | 59 | 85 | 289.6 | 0.83 | 29.04
DSG300*D | 25 | 7500 | 80 | 63 | 85 | 293.8 | 0.76 | 27.08
DSG300*D | 25 | 7500 | 80 | 67 | 85 | 302.6 | 0.64 | 23.42
DSG300*D | 25 | 7500 | 80 | 71 | 85 | 316.1 | 0.51 | 19.6
DSG300*D | 25 | 7500 | 80 | 59 | 95 | 276.4 | 0.86 | 28.74
DSG300*D | 25 | 7500 | 80 | 63 | 95 | 280.5 | 0.79 | 26.78
DSG300*D | 25 | 7500 | 80 | 67 | 95 | 289.3 | 0.66 | 23.12
DSG300*D | 25 | 7500 | 80 | 71 | 95 | 302.8 | 0.53 | 19.3
DSG300*D | 25 | 7500 | 80 | 59 | 105 | 260.2 | 0.9 | 28.48
DSG300*D | 25 | 7500 | 80 | 63 | 105 | 264.3 | 0.83 | 26.52
DSG300*D | 25 | 7500 | 80 | 67 | 105 | 273.1 | 0.69 | 22.86
DSG300*D | 25 | 7500 | 80 | 71 | 105 | 286.6 | 0.55 | 19.1
DSG300*D | 25 | 7500 | 80 | 59 | 115 | 245.4 | 1 | 29.71
DSG300*D | 25 | 7500 | 80 | 63 | 115 | 249.5 | 0.92 | 27.75
DSG300*D | 25 | 7500 | 80 | 67 | 115 | 258.4 | 0.77 | 24.09
DSG300*D | 25 | 7500 | 80 | 71 | 115 | 271.8 | 0.62 | 20.3
DSG300*D | 25 | 7650 | 80 | 59 | 65 | 300.6 | 0.8 | 28.64
DSG300*D | 25 | 7650 | 80 | 63 | 65 | 304.8 | 0.74 | 26.68
DSG300*D | 25 | 7650 | 80 | 67 | 65 | 313.6 | 0.62 | 23.03
DSG300*D | 25 | 7650 | 80 | 71 | 65 | 327.1 | 0.49 | 19.2
DSG300*D | 25 | 7650 | 80 | 59 | 75 | 298 | 0.81 | 28.59
DSG300*D | 25 | 7650 | 80 | 63 | 75 | 302.1 | 0.74 | 26.63
DSG300*D | 25 | 7650 | 80 | 67 | 75 | 311 | 0.62 | 22.97
DSG300*D | 25 | 7650 | 80 | 71 | 75 | 324.4 | 0.5 | 19.2
DSG300*D | 25 | 7650 | 80 | 59 | 85 | 290.3 | 0.84 | 28.86
DSG300*D | 25 | 7650 | 80 | 63 | 85 | 294.4 | 0.77 | 26.91
DSG300*D | 25 | 7650 | 80 | 67 | 85 | 303.3 | 0.65 | 23.25
DSG300*D | 25 | 7650 | 80 | 71 | 85 | 316.7 | 0.52 | 19.5
DSG300*D | 25 | 7650 | 80 | 59 | 95 | 277 | 0.87 | 28.57
DSG300*D | 25 | 7650 | 80 | 63 | 95 | 281.2 | 0.8 | 26.61
DSG300*D | 25 | 7650 | 80 | 67 | 95 | 290 | 0.67 | 22.95
DSG300*D | 25 | 7650 | 80 | 71 | 95 | 303.5 | 0.53 | 19.2
DSG300*D | 25 | 7650 | 80 | 59 | 105 | 260.8 | 0.91 | 28.31
DSG300*D | 25 | 7650 | 80 | 63 | 105 | 265 | 0.84 | 26.35
DSG300*D | 25 | 7650 | 80 | 67 | 105 | 273.8 | 0.7 | 22.69
DSG300*D | 25 | 7650 | 80 | 71 | 105 | 287.3 | 0.55 | 18.9
DSG300*D | 25 | 7650 | 80 | 59 | 115 | 246 | 1 | 29.24
DSG300*D | 25 | 7650 | 80 | 63 | 115 | 250.2 | 0.93 | 27.58
DSG300*D | 25 | 7650 | 80 | 67 | 115 | 259 | 0.78 | 23.92
DSG300*D | 25 | 7650 | 80 | 71 | 115 | 272.5 | 0.62 | 20.1
DSG300*D | 25 | 10000 | 80 | 59 | 65 | 313.8 | 0.92 | 26.38
DSG300*D | 25 | 10000 | 80 | 63 | 65 | 317.9 | 0.84 | 24.42
DSG300*D | 25 | 10000 | 80 | 67 | 65 | 326.8 | 0.7 | 20.77
DSG300*D | 25 | 10000 | 80 | 71 | 65 | 340.2 | 0.55 | 17
DSG300*D | 25 | 10000 | 80 | 59 | 75 | 311.1 | 0.93 | 26.33
DSG300*D | 25 | 10000 | 80 | 63 | 75 | 315.3 | 0.85 | 24.37
DSG300*D | 25 | 10000 | 80 | 67 | 75 | 324.1 | 0.7 | 20.71
DSG300*D | 25 | 10000 | 80 | 71 | 75 | 337.6 | 0.55 | 16.9
DSG300*D | 25 | 10000 | 80 | 59 | 85 | 303.4 | 0.96 | 26.6
DSG300*D | 25 | 10000 | 80 | 63 | 85 | 307.6 | 0.88 | 24.65
DSG300*D | 25 | 10000 | 80 | 67 | 85 | 316.4 | 0.73 | 20.99
DSG300*D | 25 | 10000 | 80 | 71 | 85 | 329.9 | 0.57 | 17.2
DSG300*D | 25 | 10000 | 80 | 59 | 95 | 290.2 | 1 | 26.31
DSG300*D | 25 | 10000 | 80 | 63 | 95 | 294.3 | 0.91 | 24.35
DSG300*D | 25 | 10000 | 80 | 67 | 95 | 303.2 | 0.75 | 20.69
DSG300*D | 25 | 10000 | 80 | 71 | 95 | 316.6 | 0.59 | 16.9
DSG300*D | 25 | 10000 | 80 | 59 | 105 | 274 | 1 | 24.91
DSG300*D | 25 | 10000 | 80 | 63 | 105 | 278.1 | 0.95 | 24.09
DSG300*D | 25 | 10000 | 80 | 67 | 105 | 287 | 0.78 | 20.43
DSG300*D | 25 | 10000 | 80 | 71 | 105 | 300.4 | 0.61 | 16.6
DSG300*D | 25 | 10000 | 80 | 59 | 115 | 259.2 | 1 | 23.56
DSG300*D | 25 | 10000 | 80 | 63 | 115 | 263.4 | 1 | 23.94
DSG300*D | 25 | 10000 | 80 | 67 | 115 | 272.2 | 0.88 | 21.66
DSG300*D | 25 | 10000 | 80 | 71 | 115 | 285.6 | 0.69 | 17.9
DSG300*D | 25 | 7500 | 85 | 59 | 65 | 304.9 | 0.88 | 32.66
DSG300*D | 25 | 7500 | 85 | 63 | 65 | 309.1 | 0.82 | 30.7
DSG300*D | 25 | 7500 | 85 | 67 | 65 | 317.9 | 0.7 | 27.04
DSG300*D | 25 | 7500 | 85 | 71 | 65 | 331.4 | 0.58 | 23.3
DSG300*D | 25 | 7500 | 85 | 59 | 75 | 302.3 | 0.89 | 32.61
DSG300*D | 25 | 7500 | 85 | 63 | 75 | 306.5 | 0.83 | 30.65
DSG300*D | 25 | 7500 | 85 | 67 | 75 | 315.3 | 0.71 | 26.99
DSG300*D | 25 | 7500 | 85 | 71 | 75 | 328.7 | 0.58 | 23.2
DSG300*D | 25 | 7500 | 85 | 59 | 85 | 294.6 | 0.92 | 32.88
DSG300*D | 25 | 7500 | 85 | 63 | 85 | 298.8 | 0.85 | 30.92
DSG300*D | 25 | 7500 | 85 | 67 | 85 | 307.6 | 0.73 | 27.27
DSG300*D | 25 | 7500 | 85 | 71 | 85 | 321 | 0.6 | 23.5
DSG300*D | 25 | 7500 | 85 | 59 | 95 | 281.3 | 0.96 | 32.59
DSG300*D | 25 | 7500 | 85 | 63 | 95 | 285.5 | 0.89 | 30.63
DSG300*D | 25 | 7500 | 85 | 67 | 95 | 294.3 | 0.76 | 26.97
DSG300*D | 25 | 7500 | 85 | 71 | 95 | 307.8 | 0.62 | 23.2
DSG300*D | 25 | 7500 | 85 | 59 | 105 | 265.1 | 1 | 32.14
DSG300*D | 25 | 7500 | 85 | 63 | 105 | 269.3 | 0.93 | 30.37
DSG300*D | 25 | 7500 | 85 | 67 | 105 | 278.1 | 0.79 | 26.71
DSG300*D | 25 | 7500 | 85 | 71 | 105 | 291.6 | 0.65 | 22.9
DSG300*D | 25 | 7500 | 85 | 59 | 115 | 250.3 | 1 | 30.34
DSG300*D | 25 | 7500 | 85 | 63 | 115 | 254.5 | 1 | 30.85
DSG300*D | 25 | 7500 | 85 | 67 | 115 | 263.3 | 0.88 | 27.93
DSG300*D | 25 | 7500 | 85 | 71 | 115 | 276.8 | 0.72 | 24.1
DSG300*D | 25 | 7650 | 85 | 59 | 65 | 305.6 | 0.89 | 32.49
DSG300*D | 25 | 7650 | 85 | 63 | 65 | 309.8 | 0.83 | 30.53
DSG300*D | 25 | 7650 | 85 | 67 | 65 | 318.6 | 0.71 | 26.87
DSG300*D | 25 | 7650 | 85 | 71 | 65 | 332 | 0.59 | 23.1
DSG300*D | 25 | 7650 | 85 | 59 | 75 | 302.9 | 0.9 | 32.44
DSG300*D | 25 | 7650 | 85 | 63 | 75 | 307.1 | 0.84 | 30.48
DSG300*D | 25 | 7650 | 85 | 67 | 75 | 315.9 | 0.71 | 26.82
DSG300*D | 25 | 7650 | 85 | 71 | 75 | 329.4 | 0.59 | 23
DSG300*D | 25 | 7650 | 85 | 59 | 85 | 295.2 | 0.93 | 32.71
DSG300*D | 25 | 7650 | 85 | 63 | 85 | 299.4 | 0.86 | 30.75
DSG300*D | 25 | 7650 | 85 | 67 | 85 | 308.2 | 0.74 | 27.09
DSG300*D | 25 | 7650 | 85 | 71 | 85 | 321.7 | 0.61 | 23.3
DSG300*D | 25 | 7650 | 85 | 59 | 95 | 282 | 0.97 | 32.42
DSG300*D | 25 | 7650 | 85 | 63 | 95 | 286.2 | 0.9 | 30.46
DSG300*D | 25 | 7650 | 85 | 67 | 95 | 295 | 0.76 | 26.8
DSG300*D | 25 | 7650 | 85 | 71 | 95 | 308.4 | 0.63 | 23
DSG300*D | 25 | 7650 | 85 | 59 | 105 | 265.8 | 1 | 31.59
DSG300*D | 25 | 7650 | 85 | 63 | 105 | 270 | 0.94 | 30.19
DSG300*D | 25 | 7650 | 85 | 67 | 105 | 278.8 | 0.8 | 26.54
DSG300*D | 25 | 7650 | 85 | 71 | 105 | 292.2 | 0.66 | 22.7
DSG300*D | 25 | 7650 | 85 | 59 | 115 | 251 | 1 | 29.83
DSG300*D | 25 | 7650 | 85 | 63 | 115 | 255.2 | 1 | 30.32
DSG300*D | 25 | 7650 | 85 | 67 | 115 | 264 | 0.89 | 27.76
DSG300*D | 25 | 7650 | 85 | 71 | 115 | 277.4 | 0.73 | 24
DSG300*D | 25 | 10000 | 85 | 59 | 65 | 318.7 | 1 | 28.98
DSG300*D | 25 | 10000 | 85 | 63 | 65 | 322.9 | 0.96 | 28.27
DSG300*D | 25 | 10000 | 85 | 67 | 65 | 331.7 | 0.82 | 24.61
DSG300*D | 25 | 10000 | 85 | 71 | 65 | 345.2 | 0.66 | 20.8
DSG300*D | 25 | 10000 | 85 | 59 | 75 | 316.1 | 1 | 28.74
DSG300*D | 25 | 10000 | 85 | 63 | 75 | 320.3 | 0.97 | 28.22
DSG300*D | 25 | 10000 | 85 | 67 | 75 | 329.1 | 0.82 | 24.56
DSG300*D | 25 | 10000 | 85 | 71 | 75 | 342.5 | 0.67 | 20.8
DSG300*D | 25 | 10000 | 85 | 59 | 85 | 308.4 | 1 | 28.04
DSG300*D | 25 | 10000 | 85 | 63 | 85 | 312.6 | 1 | 28.42
DSG300*D | 25 | 10000 | 85 | 67 | 85 | 321.4 | 0.85 | 24.83
DSG300*D | 25 | 10000 | 85 | 71 | 85 | 334.8 | 0.69 | 21
DSG300*D | 25 | 10000 | 85 | 59 | 95 | 295.1 | 1 | 26.83
DSG300*D | 25 | 10000 | 85 | 63 | 95 | 299.3 | 1 | 27.21
DSG300*D | 25 | 10000 | 85 | 67 | 95 | 308.1 | 0.88 | 24.54
DSG300*D | 25 | 10000 | 85 | 71 | 95 | 321.6 | 0.71 | 20.7
DSG300*D | 25 | 10000 | 85 | 59 | 105 | 278.9 | 1 | 25.36
DSG300*D | 25 | 10000 | 85 | 63 | 105 | 283.1 | 1 | 25.74
DSG300*D | 25 | 10000 | 85 | 67 | 105 | 291.9 | 0.91 | 24.28
DSG300*D | 25 | 10000 | 85 | 71 | 105 | 305.4 | 0.74 | 20.5
DSG300*D | 25 | 10000 | 85 | 59 | 115 | 264.2 | 1 | 24.01
DSG300*D | 25 | 10000 | 85 | 63 | 115 | 268.3 | 1 | 24.39
DSG300*D | 25 | 10000 | 85 | 67 | 115 | 277.1 | 1 | 25.19
DSG300*D | 25 | 10000 | 85 | 71 | 115 | 290.6 | 0.82 | 21.7
DHG036* | 3 | 900 | 70 | 59 | 65 | 35.1 | 0.59 | 20.87
DHG036* | 3 | 900 | 70 | 63 | 65 | 35.6 | 0.53 | 19.04
DHG036* | 3 | 900 | 70 | 67 | 65 | 36.7 | 0.42 | 15.62
DHG036* | 3 | 900 | 70 | 59 | 75 | 34.8 | 0.59 | 20.82
DHG036* | 3 | 900 | 70 | 63 | 75 | 35.3 | 0.53 | 18.99
DHG036* | 3 | 900 | 70 | 67 | 75 | 36.4 | 0.42 | 15.57
DHG036* | 3 | 900 | 70 | 59 | 85 | 33.9 | 0.62 | 21.07
DHG036* | 3 | 900 | 70 | 63 | 85 | 34.4 | 0.55 | 19.24
DHG036* | 3 | 900 | 70 | 67 | 85 | 35.4 | 0.44 | 15.82
DHG036* | 3 | 900 | 70 | 59 | 95 | 32.3 | 0.64 | 20.8
DHG036* | 3 | 900 | 70 | 63 | 95 | 32.8 | 0.57 | 18.97
DHG036* | 3 | 900 | 70 | 67 | 95 | 33.8 | 0.45 | 15.55
DHG036* | 3 | 900 | 70 | 59 | 105 | 30.3 | 0.67 | 20.55
DHG036* | 3 | 900 | 70 | 63 | 105 | 30.8 | 0.6 | 18.72
DHG036* | 3 | 900 | 70 | 67 | 105 | 31.9 | 0.48 | 15.3
DHG036* | 3 | 900 | 70 | 59 | 115 | 28.5 | 0.75 | 21.7
DHG036* | 3 | 900 | 70 | 63 | 115 | 29 | 0.68 | 19.87
DHG036* | 3 | 900 | 70 | 67 | 115 | 30.1 | 0.54 | 16.45
DHG036* | 3 | 1160 | 70 | 59 | 65 | 35.9 | 0.66 | 18.69
DHG036* | 3 | 1160 | 70 | 63 | 65 | 36.4 | 0.59 | 16.86
DHG036* | 3 | 1160 | 70 | 67 | 65 | 37.5 | 0.46 | 13.44
DHG036* | 3 | 1160 | 70 | 59 | 75 | 35.6 | 0.67 | 18.64
DHG036* | 3 | 1160 | 70 | 63 | 75 | 36.1 | 0.59 | 16.81
DHG036* | 3 | 1160 | 70 | 67 | 75 | 37.2 | 0.46 | 13.39
DHG036* | 3 | 1160 | 70 | 59 | 85 | 34.7 | 0.7 | 18.89
DHG036* | 3 | 1160 | 70 | 63 | 85 | 35.2 | 0.62 | 17.06
DHG036* | 3 | 1160 | 70 | 67 | 85 | 36.2 | 0.48 | 13.65
DHG036* | 3 | 1160 | 70 | 59 | 95 | 33.1 | 0.72 | 18.62
DHG036* | 3 | 1160 | 70 | 63 | 95 | 33.6 | 0.64 | 16.79
DHG036* | 3 | 1160 | 70 | 67 | 95 | 34.6 | 0.49 | 13.37
DHG036* | 3 | 1160 | 70 | 59 | 105 | 31.1 | 0.75 | 18.37
DHG036* | 3 | 1160 | 70 | 63 | 105 | 31.6 | 0.67 | 16.54
DHG036* | 3 | 1160 | 70 | 67 | 105 | 32.7 | 0.51 | 13.13
DHG036* | 3 | 1160 | 70 | 59 | 115 | 29.3 | 0.85 | 19.52
DHG036* | 3 | 1160 | 70 | 63 | 115 | 29.8 | 0.76 | 17.69
DHG036* | 3 | 1160 | 70 | 67 | 115 | 30.9 | 0.59 | 14.27
DHG036* | 3 | 1500 | 70 | 59 | 65 | 37.4 | 0.73 | 16.66
DHG036* | 3 | 1500 | 70 | 63 | 65 | 37.9 | 0.65 | 14.83
DHG036* | 3 | 1500 | 70 | 67 | 65 | 39 | 0.48 | 11.41
DHG036* | 3 | 1500 | 70 | 59 | 75 | 37.1 | 0.74 | 16.61
DHG036* | 3 | 1500 | 70 | 63 | 75 | 37.6 | 0.65 | 14.78
DHG036* | 3 | 1500 | 70 | 67 | 75 | 38.7 | 0.48 | 11.36
DHG036* | 3 | 1500 | 70 | 59 | 85 | 36.2 | 0.77 | 16.87
DHG036* | 3 | 1500 | 70 | 63 | 85 | 36.7 | 0.68 | 15.04
DHG036* | 3 | 1500 | 70 | 67 | 85 | 37.7 | 0.51 | 11.62
DHG036* | 3 | 1500 | 70 | 59 | 95 | 34.6 | 0.79 | 16.59
DHG036* | 3 | 1500 | 70 | 63 | 95 | 35.1 | 0.69 | 14.76
DHG036* | 3 | 1500 | 70 | 67 | 95 | 36.1 | 0.52 | 11.34
DHG036* | 3 | 1500 | 70 | 59 | 105 | 32.6 | 0.83 | 16.35
DHG036* | 3 | 1500 | 70 | 63 | 105 | 33.1 | 0.72 | 14.52
DHG036* | 3 | 1500 | 70 | 67 | 105 | 34.2 | 0.54 | 11.1
DHG036* | 3 | 1500 | 70 | 59 | 115 | 30.8 | 0.94 | 17.49
DHG036* | 3 | 1500 | 70 | 63 | 115 | 31.3 | 0.83 | 15.66
DHG036* | 3 | 1500 | 70 | 67 | 115 | 32.4 | 0.62 | 12.25
DHG036* | 3 | 900 | 75 | 59 | 65 | 35.3 | 0.7 | 24.89
DHG036* | 3 | 900 | 75 | 63 | 65 | 35.8 | 0.64 | 23.06
DHG036* | 3 | 900 | 75 | 67 | 65 | 36.9 | 0.53 | 19.64
DHG036* | 3 | 900 | 75 | 71 | 65 | 38.5 | 0.4 | 16.1
DHG036* | 3 | 900 | 75 | 59 | 75 | 35 | 0.7 | 24.84
DHG036* | 3 | 900 | 75 | 63 | 75 | 35.5 | 0.64 | 23.01
DHG036* | 3 | 900 | 75 | 67 | 75 | 36.6 | 0.53 | 19.59
DHG036* | 3 | 900 | 75 | 71 | 75 | 38.2 | 0.4 | 16.1
DHG036* | 3 | 900 | 75 | 59 | 85 | 34.1 | 0.73 | 25.1
DHG036* | 3 | 900 | 75 | 63 | 85 | 34.6 | 0.67 | 23.27
DHG036* | 3 | 900 | 75 | 67 | 85 | 35.6 | 0.55 | 19.85
DHG036* | 3 | 900 | 75 | 71 | 85 | 37.3 | 0.4 | 16.3
DHG036* | 3 | 900 | 75 | 59 | 95 | 32.5 | 0.76 | 24.82
DHG036* | 3 | 900 | 75 | 63 | 95 | 33 | 0.69 | 22.99
DHG036* | 3 | 900 | 75 | 67 | 95 | 34 | 0.57 | 19.57
DHG036* | 3 | 900 | 75 | 71 | 95 | 35.7 | 0.4 | 16
DHG036* | 3 | 900 | 75 | 59 | 105 | 30.5 | 0.8 | 24.58
DHG036* | 3 | 900 | 75 | 63 | 105 | 31 | 0.73 | 22.75
DHG036* | 3 | 900 | 75 | 67 | 105 | 32.1 | 0.6 | 19.33
DHG036* | 3 | 900 | 75 | 71 | 105 | 33.7 | 0.5 | 15.8
DHG036* | 3 | 900 | 75 | 59 | 115 | 28.7 | 0.89 | 25.72
DHG036* | 3 | 900 | 75 | 63 | 115 | 29.2 | 0.81 | 23.89
DHG036* | 3 | 900 | 75 | 67 | 115 | 30.3 | 0.67 | 20.47
DHG036* | 3 | 900 | 75 | 71 | 115 | 31.9 | 0.5 | 16.9
DHG036* | 3 | 1160 | 75 | 59 | 65 | 36.1 | 0.8 | 22.71
DHG036* | 3 | 1160 | 75 | 63 | 65 | 36.6 | 0.73 | 20.88
DHG036* | 3 | 1160 | 75 | 67 | 65 | 37.7 | 0.59 | 17.46
DHG036* | 3 | 1160 | 75 | 71 | 65 | 39.3 | 0.5 | 13.9
DHG036* | 3 | 1160 | 75 | 59 | 75 | 35.8 | 0.81 | 22.66
DHG036* | 3 | 1160 | 75 | 63 | 75 | 36.3 | 0.73 | 20.83
DHG036* | 3 | 1160 | 75 | 67 | 75 | 37.3 | 0.59 | 17.41
DHG036* | 3 | 1160 | 75 | 71 | 75 | 39 | 0.5 | 13.9
DHG036* | 3 | 1160 | 75 | 59 | 85 | 34.8 | 0.84 | 22.92
DHG036* | 3 | 1160 | 75 | 63 | 85 | 35.4 | 0.76 | 21.09
DHG036* | 3 | 1160 | 75 | 67 | 85 | 36.4 | 0.62 | 17.67
DHG036* | 3 | 1160 | 75 | 71 | 85 | 38 | 0.5 | 14.1
DHG036* | 3 | 1160 | 75 | 59 | 95 | 33.2 | 0.87 | 22.64
DHG036* | 3 | 1160 | 75 | 63 | 95 | 33.8 | 0.79 | 20.81
DHG036* | 3 | 1160 | 75 | 67 | 95 | 34.8 | 0.64 | 17.39
DHG036* | 3 | 1160 | 75 | 71 | 95 | 36.4 | 0.5 | 13.9
DHG036* | 3 | 1160 | 75 | 59 | 105 | 31.3 | 0.91 | 22.4
DHG036* | 3 | 1160 | 75 | 63 | 105 | 31.8 | 0.83 | 20.57
DHG036* | 3 | 1160 | 75 | 67 | 105 | 32.9 | 0.67 | 17.15
DHG036* | 3 | 1160 | 75 | 71 | 105 | 34.5 | 0.5 | 13.6
DHG036* | 3 | 1160 | 75 | 59 | 115 | 29.5 | 1 | 23.13
DHG036* | 3 | 1160 | 75 | 63 | 115 | 30 | 0.92 | 21.71
DHG036* | 3 | 1160 | 75 | 67 | 115 | 31.1 | 0.75 | 18.3
DHG036* | 3 | 1160 | 75 | 71 | 115 | 32.7 | 0.6 | 14.8
DHG036* | 3 | 1500 | 75 | 59 | 65 | 37.6 | 0.91 | 20.69
DHG036* | 3 | 1500 | 75 | 63 | 65 | 38.1 | 0.82 | 18.85
DHG036* | 3 | 1500 | 75 | 67 | 65 | 39.2 | 0.65 | 15.44
DHG036* | 3 | 1500 | 75 | 71 | 65 | 40.8 | 0.5 | 11.9
DHG036* | 3 | 1500 | 75 | 59 | 75 | 37.3 | 0.91 | 20.64
DHG036* | 3 | 1500 | 75 | 63 | 75 | 37.8 | 0.82 | 18.8
DHG036* | 3 | 1500 | 75 | 67 | 75 | 38.8 | 0.65 | 15.39
DHG036* | 3 | 1500 | 75 | 71 | 75 | 40.5 | 0.5 | 11.8
DHG036* | 3 | 1500 | 75 | 59 | 85 | 36.3 | 0.95 | 20.89
DHG036* | 3 | 1500 | 75 | 63 | 85 | 36.9 | 0.85 | 19.06
DHG036* | 3 | 1500 | 75 | 67 | 85 | 37.9 | 0.68 | 15.64
DHG036* | 3 | 1500 | 75 | 71 | 85 | 39.5 | 0.5 | 12.1
DHG036* | 3 | 1500 | 75 | 59 | 95 | 34.7 | 0.98 | 20.62
DHG036* | 3 | 1500 | 75 | 63 | 95 | 35.3 | 0.88 | 18.79
DHG036* | 3 | 1500 | 75 | 67 | 95 | 36.3 | 0.7 | 15.37
DHG036* | 3 | 1500 | 75 | 71 | 95 | 37.9 | 0.5 | 11.8
DHG036* | 3 | 1500 | 75 | 59 | 105 | 32.8 | 1 | 19.87
DHG036* | 3 | 1500 | 75 | 63 | 105 | 33.3 | 0.92 | 18.54
DHG036* | 3 | 1500 | 75 | 67 | 105 | 34.4 | 0.73 | 15.12
DHG036* | 3 | 1500 | 75 | 71 | 105 | 36 | 0.5 | 11.6
DHG036* | 3 | 1500 | 75 | 59 | 115 | 31 | 1 | 18.79
DHG036* | 3 | 1500 | 75 | 63 | 115 | 31.5 | 1 | 19.1
DHG036* | 3 | 1500 | 75 | 67 | 115 | 32.6 | 0.82 | 16.27
DHG036* | 3 | 1500 | 75 | 71 | 115 | 34.2 | 0.6 | 12.7
DHG036* | 3 | 900 | 80 | 59 | 65 | 35.5 | 0.81 | 28.94
DHG036* | 3 | 900 | 80 | 63 | 65 | 36 | 0.75 | 27.11
DHG036* | 3 | 900 | 80 | 67 | 65 | 37.1 | 0.63 | 23.69
DHG036* | 3 | 900 | 80 | 71 | 65 | 38.7 | 0.5 | 20.2
DHG036* | 3 | 900 | 80 | 59 | 75 | 35.2 | 0.81 | 28.89
DHG036* | 3 | 900 | 80 | 63 | 75 | 35.7 | 0.75 | 27.06
DHG036* | 3 | 900 | 80 | 67 | 75 | 36.7 | 0.64 | 23.64
DHG036* | 3 | 900 | 80 | 71 | 75 | 38.4 | 0.5 | 20.1
DHG036* | 3 | 900 | 80 | 59 | 85 | 34.2 | 0.84 | 29.15
DHG036* | 3 | 900 | 80 | 63 | 85 | 34.7 | 0.78 | 27.32
DHG036* | 3 | 900 | 80 | 67 | 85 | 35.8 | 0.66 | 23.9
DHG036* | 3 | 900 | 80 | 71 | 85 | 37.4 | 0.5 | 20.4
DHG036* | 3 | 900 | 80 | 59 | 95 | 32.6 | 0.88 | 28.87
DHG036* | 3 | 900 | 80 | 63 | 95 | 33.1 | 0.81 | 27.04
DHG036* | 3 | 900 | 80 | 67 | 95 | 34.2 | 0.68 | 23.63
DHG036* | 3 | 900 | 80 | 71 | 95 | 35.8 | 0.6 | 20.1
DHG036* | 3 | 900 | 80 | 59 | 105 | 30.7 | 0.92 | 28.63
DHG036* | 3 | 900 | 80 | 63 | 105 | 31.2 | 0.85 | 26.8
DHG036* | 3 | 900 | 80 | 67 | 105 | 32.3 | 0.72 | 23.38
DHG036* | 3 | 900 | 80 | 71 | 105 | 33.9 | 0.6 | 19.8
DHG036* | 3 | 900 | 80 | 59 | 115 | 28.9 | 1 | 29.2
DHG036* | 3 | 900 | 80 | 63 | 115 | 29.4 | 0.94 | 27.94
DHG036* | 3 | 900 | 80 | 67 | 115 | 30.5 | 0.8 | 24.53
DHG036* | 3 | 900 | 80 | 71 | 115 | 32.1 | 0.6 | 21
DHG036* | 3 | 1160 | 80 | 59 | 65 | 36.3 | 0.94 | 26.76
DHG036* | 3 | 1160 | 80 | 63 | 65 | 36.8 | 0.86 | 24.93
DHG036* | 3 | 1160 | 80 | 67 | 65 | 37.8 | 0.73 | 21.51
DHG036* | 3 | 1160 | 80 | 71 | 65 | 39.5 | 0.6 | 18
DHG036* | 3 | 1160 | 80 | 59 | 75 | 36 | 0.95 | 26.71
DHG036* | 3 | 1160 | 80 | 63 | 75 | 36.5 | 0.87 | 24.88
DHG036* | 3 | 1160 | 80 | 67 | 75 | 37.5 | 0.73 | 21.46
DHG036* | 3 | 1160 | 80 | 71 | 75 | 39.2 | 0.6 | 17.9
DHG036* | 3 | 1160 | 80 | 59 | 85 | 35 | 0.98 | 26.97
DHG036* | 3 | 1160 | 80 | 63 | 85 | 35.5 | 0.9 | 25.14
DHG036* | 3 | 1160 | 80 | 67 | 85 | 36.6 | 0.76 | 21.72
DHG036* | 3 | 1160 | 80 | 71 | 85 | 38.2 | 0.6 | 18.2
DHG036* | 3 | 1160 | 80 | 59 | 95 | 33.4 | 1 | 26.2
DHG036* | 3 | 1160 | 80 | 63 | 95 | 33.9 | 0.93 | 24.86
DHG036* | 3 | 1160 | 80 | 67 | 95 | 35 | 0.78 | 21.45
DHG036* | 3 | 1160 | 80 | 71 | 95 | 36.6 | 0.6 | 17.9
DHG036* | 3 | 1160 | 80 | 59 | 105 | 31.5 | 1 | 24.67
DHG036* | 3 | 1160 | 80 | 63 | 105 | 32 | 0.98 | 24.62
DHG036* | 3 | 1160 | 80 | 67 | 105 | 33 | 0.82 | 21.2
DHG036* | 3 | 1160 | 80 | 71 | 105 | 34.7 | 0.6 | 17.7
DHG036* | 3 | 1160 | 80 | 59 | 115 | 29.7 | 1 | 23.27
DHG036* | 3 | 1160 | 80 | 63 | 115 | 30.2 | 1 | 23.66
DHG036* | 3 | 1160 | 80 | 67 | 115 | 31.3 | 0.91 | 22.35
DHG036* | 3 | 1160 | 80 | 71 | 115 | 32.9 | 0.7 | 18.8
DHG036* | 3 | 1500 | 80 | 59 | 65 | 37.8 | 1 | 22.9
DHG036* | 3 | 1500 | 80 | 63 | 65 | 38.3 | 0.99 | 22.91
DHG036* | 3 | 1500 | 80 | 67 | 65 | 39.3 | 0.82 | 19.49
DHG036* | 3 | 1500 | 80 | 71 | 65 | 41 | 0.6 | 15.9
DHG036* | 3 | 1500 | 80 | 59 | 75 | 37.5 | 1 | 22.7
DHG036* | 3 | 1500 | 80 | 63 | 75 | 38 | 0.99 | 22.86
DHG036* | 3 | 1500 | 80 | 67 | 75 | 39 | 0.82 | 19.44
DHG036* | 3 | 1500 | 80 | 71 | 75 | 40.7 | 0.6 | 15.9
DHG036* | 3 | 1500 | 80 | 59 | 85 | 36.5 | 1 | 22.14
DHG036* | 3 | 1500 | 80 | 63 | 85 | 37 | 1 | 22.45
DHG036* | 3 | 1500 | 80 | 67 | 85 | 38.1 | 0.85 | 19.7
DHG036* | 3 | 1500 | 80 | 71 | 85 | 39.7 | 0.7 | 16.2
DHG036* | 3 | 1500 | 80 | 59 | 95 | 34.9 | 1 | 21.17
DHG036* | 3 | 1500 | 80 | 63 | 95 | 35.4 | 1 | 21.48
DHG036* | 3 | 1500 | 80 | 67 | 95 | 36.5 | 0.88 | 19.42
DHG036* | 3 | 1500 | 80 | 71 | 95 | 38.1 | 0.7 | 15.9
DHG036* | 3 | 1500 | 80 | 59 | 105 | 33 | 1 | 19.99
DHG036* | 3 | 1500 | 80 | 63 | 105 | 33.5 | 1 | 20.29
DHG036* | 3 | 1500 | 80 | 67 | 105 | 34.5 | 0.92 | 19.18
DHG036* | 3 | 1500 | 80 | 71 | 105 | 36.2 | 0.7 | 15.6
DHG036* | 3 | 1500 | 80 | 59 | 115 | 31.2 | 1 | 18.9
DHG036* | 3 | 1500 | 80 | 63 | 115 | 31.7 | 1 | 19.21
DHG036* | 3 | 1500 | 80 | 67 | 115 | 32.8 | 1 | 19.85
DHG036* | 3 | 1500 | 80 | 71 | 115 | 34.4 | 0.8 | 16.8
DHG036* | 3 | 900 | 85 | 59 | 65 | 36.1 | 0.89 | 32.54
DHG036* | 3 | 900 | 85 | 63 | 65 | 36.6 | 0.83 | 30.71
DHG036* | 3 | 900 | 85 | 67 | 65 | 37.7 | 0.72 | 27.29
DHG036* | 3 | 900 | 85 | 71 | 65 | 39.3 | 0.6 | 23.7
DHG036* | 3 | 900 | 85 | 59 | 75 | 35.8 | 0.9 | 32.49
DHG036* | 3 | 900 | 85 | 63 | 75 | 36.3 | 0.84 | 30.66
DHG036* | 3 | 900 | 85 | 67 | 75 | 37.3 | 0.72 | 27.24
DHG036* | 3 | 900 | 85 | 71 | 75 | 39 | 0.6 | 23.7
DHG036* | 3 | 900 | 85 | 59 | 85 | 34.8 | 0.93 | 32.74
DHG036* | 3 | 900 | 85 | 63 | 85 | 35.3 | 0.87 | 30.91
DHG036* | 3 | 900 | 85 | 67 | 85 | 36.4 | 0.75 | 27.49
DHG036* | 3 | 900 | 85 | 71 | 85 | 38 | 0.6 | 24
DHG036* | 3 | 900 | 85 | 59 | 95 | 33.2 | 0.97 | 32.47
DHG036* | 3 | 900 | 85 | 63 | 95 | 33.7 | 0.9 | 30.64
DHG036* | 3 | 900 | 85 | 67 | 95 | 34.8 | 0.77 | 27.22
DHG036* | 3 | 900 | 85 | 71 | 95 | 36.4 | 0.6 | 23.7
DHG036* | 3 | 900 | 85 | 59 | 105 | 31.3 | 1 | 31.61
DHG036* | 3 | 900 | 85 | 63 | 105 | 31.8 | 0.95 | 30.39
DHG036* | 3 | 900 | 85 | 67 | 105 | 32.9 | 0.81 | 26.97
DHG036* | 3 | 900 | 85 | 71 | 105 | 34.5 | 0.7 | 23.4
DHG036* | 3 | 900 | 85 | 59 | 115 | 29.5 | 1 | 29.8
DHG036* | 3 | 900 | 85 | 63 | 115 | 30 | 1 | 30.31
DHG036* | 3 | 900 | 85 | 67 | 115 | 31.1 | 0.9 | 28.12
DHG036* | 3 | 900 | 85 | 71 | 115 | 32.7 | 0.7 | 24.6
DHG036* | 3 | 1160 | 85 | 59 | 65 | 36.9 | 1 | 28.9
DHG036* | 3 | 1160 | 85 | 63 | 65 | 37.4 | 0.97 | 28.53
DHG036* | 3 | 1160 | 85 | 67 | 65 | 38.4 | 0.83 | 25.11
DHG036* | 3 | 1160 | 85 | 71 | 65 | 40.1 | 0.7 | 21.6
DHG036* | 3 | 1160 | 85 | 59 | 75 | 36.6 | 1 | 28.65
DHG036* | 3 | 1160 | 85 | 63 | 75 | 37.1 | 0.98 | 28.48
DHG036* | 3 | 1160 | 85 | 67 | 75 | 38.1 | 0.84 | 25.06
DHG036* | 3 | 1160 | 85 | 71 | 75 | 39.8 | 0.7 | 21.5
DHG036* | 3 | 1160 | 85 | 59 | 85 | 35.6 | 1 | 27.93
DHG036* | 3 | 1160 | 85 | 63 | 85 | 36.1 | 1 | 28.32
DHG036* | 3 | 1160 | 85 | 67 | 85 | 37.2 | 0.87 | 25.32
DHG036* | 3 | 1160 | 85 | 71 | 85 | 38.8 | 0.7 | 21.8
DHG036* | 3 | 1160 | 85 | 59 | 95 | 34 | 1 | 26.67
DHG036* | 3 | 1160 | 85 | 63 | 95 | 34.5 | 1 | 27.07
DHG036* | 3 | 1160 | 85 | 67 | 95 | 35.6 | 0.9 | 25.04
DHG036* | 3 | 1160 | 85 | 71 | 95 | 37.2 | 0.7 | 21.5
DHG036* | 3 | 1160 | 85 | 59 | 105 | 32.1 | 1 | 25.14
DHG036* | 3 | 1160 | 85 | 63 | 105 | 32.6 | 1 | 25.53
DHG036* | 3 | 1160 | 85 | 67 | 105 | 33.6 | 0.94 | 24.8
DHG036* | 3 | 1160 | 85 | 71 | 105 | 35.3 | 0.8 | 21.3
DHG036* | 3 | 1160 | 85 | 59 | 115 | 30.3 | 1 | 23.74
DHG036* | 3 | 1160 | 85 | 63 | 115 | 30.8 | 1 | 24.13
DHG036* | 3 | 1160 | 85 | 67 | 115 | 31.9 | 1 | 24.97
DHG036* | 3 | 1160 | 85 | 71 | 115 | 33.5 | 0.9 | 22.4
DHG036* | 3 | 1500 | 85 | 59 | 65 | 38.4 | 1 | 23.26
DHG036* | 3 | 1500 | 85 | 63 | 65 | 38.9 | 1 | 23.57
DHG036* | 3 | 1500 | 85 | 67 | 65 | 39.9 | 0.95 | 23.08
DHG036* | 3 | 1500 | 85 | 71 | 65 | 41.6 | 0.8 | 19.5
DHG036* | 3 | 1500 | 85 | 59 | 75 | 38.1 | 1 | 23.07
DHG036* | 3 | 1500 | 85 | 63 | 75 | 38.6 | 1 | 23.37
DHG036* | 3 | 1500 | 85 | 67 | 75 | 39.6 | 0.96 | 23.03
DHG036* | 3 | 1500 | 85 | 71 | 75 | 41.3 | 0.8 | 19.5
DHG036* | 3 | 1500 | 85 | 59 | 85 | 37.1 | 1 | 22.5
DHG036* | 3 | 1500 | 85 | 63 | 85 | 37.6 | 1 | 22.81
DHG036* | 3 | 1500 | 85 | 67 | 85 | 38.7 | 0.99 | 23.29
DHG036* | 3 | 1500 | 85 | 71 | 85 | 40.3 | 0.8 | 19.7
DHG036* | 3 | 1500 | 85 | 59 | 95 | 35.5 | 1 | 21.53
DHG036* | 3 | 1500 | 85 | 63 | 95 | 36 | 1 | 21.84
DHG036* | 3 | 1500 | 85 | 67 | 95 | 37.1 | 1 | 22.48
DHG036* | 3 | 1500 | 85 | 71 | 95 | 38.7 | 0.8 | 19.5
DHG036* | 3 | 1500 | 85 | 59 | 105 | 33.6 | 1 | 20.35
DHG036* | 3 | 1500 | 85 | 63 | 105 | 34.1 | 1 | 20.65
DHG036* | 3 | 1500 | 85 | 67 | 105 | 35.1 | 1 | 21.3
DHG036* | 3 | 1500 | 85 | 71 | 105 | 36.8 | 0.9 | 19.2
DHG036* | 3 | 1500 | 85 | 59 | 115 | 31.8 | 1 | 19.27
DHG036* | 3 | 1500 | 85 | 63 | 115 | 32.3 | 1 | 19.57
DHG036* | 3 | 1500 | 85 | 67 | 115 | 33.4 | 1 | 20.22
DHG036* | 3 | 1500 | 85 | 71 | 115 | 35 | 1 | 20.4
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 59 | 65 | 25 | 0.61 | 21.85
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 63 | 65 | 25.4 | 0.55 | 20.08
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 67 | 65 | 26.1 | 0.45 | 16.79
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 59 | 75 | 24.8 | 0.61 | 21.8
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 63 | 75 | 25.1 | 0.55 | 20.04
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 67 | 75 | 25.9 | 0.45 | 16.74
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 59 | 85 | 24.1 | 0.63 | 22.05
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 63 | 85 | 24.5 | 0.57 | 20.28
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 67 | 85 | 25.2 | 0.47 | 16.99
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 59 | 95 | 22.9 | 0.66 | 21.78
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 63 | 95 | 23.3 | 0.6 | 20.02
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 67 | 95 | 24.1 | 0.48 | 16.72
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 59 | 105 | 21.5 | 0.69 | 21.55
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 63 | 105 | 21.9 | 0.63 | 19.78
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 67 | 105 | 22.7 | 0.5 | 16.48
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 59 | 115 | 20.3 | 0.77 | 22.65
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 63 | 115 | 20.6 | 0.7 | 20.89
DHG036* (70% - Low Stage) | 3 | 630 | 70 | 67 | 115 | 21.4 | 0.57 | 17.59
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 59 | 65 | 25.8 | 0.75 | 18.03
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 63 | 65 | 26.2 | 0.66 | 16.27
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 67 | 65 | 26.9 | 0.51 | 12.97
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 59 | 75 | 25.6 | 0.75 | 17.98
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 63 | 75 | 26 | 0.67 | 16.22
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 67 | 75 | 26.7 | 0.52 | 12.92
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 59 | 85 | 24.9 | 0.78 | 18.23
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 63 | 85 | 25.3 | 0.69 | 16.47
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 67 | 85 | 26 | 0.54 | 13.17
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 59 | 95 | 23.8 | 0.81 | 17.97
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 63 | 95 | 24.1 | 0.72 | 16.2
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 67 | 95 | 24.9 | 0.55 | 12.9
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 59 | 105 | 22.4 | 0.85 | 17.73
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 63 | 105 | 22.7 | 0.75 | 15.96
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 67 | 105 | 23.5 | 0.58 | 12.67
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 59 | 115 | 21.1 | 0.95 | 18.84
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 63 | 115 | 21.4 | 0.85 | 17.07
DHG036* (70% - Low Stage) | 3 | 970 | 70 | 67 | 115 | 22.2 | 0.66 | 13.77
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 59 | 65 | 26.1 | 0.77 | 17.43
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 63 | 65 | 26.4 | 0.68 | 15.66
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 67 | 65 | 27.2 | 0.52 | 12.36
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 59 | 75 | 25.8 | 0.78 | 17.38
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 63 | 75 | 26.2 | 0.69 | 15.61
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 67 | 75 | 27 | 0.53 | 12.31
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 59 | 85 | 25.2 | 0.81 | 17.63
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 63 | 85 | 25.5 | 0.72 | 15.86
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 67 | 85 | 26.3 | 0.55 | 12.56
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 59 | 95 | 24 | 0.83 | 17.36
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 63 | 95 | 24.4 | 0.74 | 15.59
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 67 | 95 | 25.2 | 0.56 | 12.29
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 59 | 105 | 22.6 | 0.87 | 17.12
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 63 | 105 | 23 | 0.77 | 15.36
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 67 | 105 | 23.8 | 0.59 | 12.06
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 59 | 115 | 21.3 | 0.99 | 18.23
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 63 | 115 | 21.7 | 0.88 | 16.46
DHG036* (70% - Low Stage) | 3 | 1050 | 70 | 67 | 115 | 22.5 | 0.68 | 13.16
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 59 | 65 | 25.1 | 0.71 | 25.73
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 63 | 65 | 25.5 | 0.65 | 23.97
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 67 | 65 | 26.3 | 0.55 | 20.67
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 71 | 65 | 27.4 | 0.4 | 17.3
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 59 | 75 | 24.9 | 0.71 | 25.69
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 63 | 75 | 25.3 | 0.66 | 23.92
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 67 | 75 | 26 | 0.55 | 20.62
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 71 | 75 | 27.2 | 0.4 | 17.2
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 59 | 85 | 24.2 | 0.74 | 25.93
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 63 | 85 | 24.6 | 0.68 | 24.17
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 67 | 85 | 25.4 | 0.57 | 20.87
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 71 | 85 | 26.5 | 0.5 | 17.5
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 59 | 95 | 23.1 | 0.77 | 25.67
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 63 | 95 | 23.4 | 0.71 | 23.9
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 67 | 95 | 24.2 | 0.59 | 20.6
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 71 | 95 | 25.4 | 0.5 | 17.2
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 59 | 105 | 21.7 | 0.81 | 25.43
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 63 | 105 | 22 | 0.74 | 23.67
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 67 | 105 | 22.8 | 0.62 | 20.37
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 71 | 105 | 24 | 0.5 | 17
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 59 | 115 | 20.4 | 0.9 | 26.54
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 63 | 115 | 20.8 | 0.83 | 24.77
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 67 | 115 | 21.5 | 0.69 | 21.47
DHG036* (70% - Low Stage) | 3 | 630 | 75 | 71 | 115 | 22.7 | 0.6 | 18.1
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 59 | 65 | 26 | 0.9 | 21.92
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 63 | 65 | 26.3 | 0.82 | 20.15
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 67 | 65 | 27.1 | 0.66 | 16.85
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 71 | 65 | 28.2 | 0.5 | 13.4
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 59 | 75 | 25.7 | 0.91 | 21.87
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 63 | 75 | 26.1 | 0.82 | 20.1
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 67 | 75 | 26.9 | 0.67 | 16.8
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 71 | 75 | 28 | 0.5 | 13.4
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 59 | 85 | 25.1 | 0.94 | 22.12
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 63 | 85 | 25.4 | 0.85 | 20.35
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 67 | 85 | 26.2 | 0.69 | 17.05
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 71 | 85 | 27.4 | 0.5 | 13.6
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 59 | 95 | 23.9 | 0.98 | 21.85
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 63 | 95 | 24.3 | 0.88 | 20.08
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 67 | 95 | 25 | 0.72 | 16.79
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 71 | 95 | 26.2 | 0.5 | 13.4
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 59 | 105 | 22.5 | 1 | 21.09
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 63 | 105 | 22.9 | 0.93 | 19.85
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 67 | 105 | 23.6 | 0.75 | 16.55
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 71 | 105 | 24.8 | 0.6 | 13.1
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 59 | 115 | 21.2 | 1 | 19.88
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 63 | 115 | 21.6 | 1 | 20.22
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 67 | 115 | 22.3 | 0.84 | 17.66
DHG036* (70% - Low Stage) | 3 | 970 | 75 | 71 | 115 | 23.5 | 0.6 | 14.2
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 59 | 65 | 26.2 | 0.94 | 21.31
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 63 | 65 | 26.6 | 0.85 | 19.54
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 67 | 65 | 27.3 | 0.69 | 16.24
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 71 | 65 | 28.5 | 0.5 | 12.8
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 59 | 75 | 26 | 0.95 | 21.26
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 63 | 75 | 26.3 | 0.85 | 19.49
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 67 | 75 | 27.1 | 0.69 | 16.2
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 71 | 75 | 28.3 | 0.5 | 12.8
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 59 | 85 | 25.3 | 0.98 | 21.51
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 63 | 85 | 25.7 | 0.89 | 19.74
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 67 | 85 | 26.4 | 0.72 | 16.44
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 71 | 85 | 27.6 | 0.5 | 13
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 59 | 95 | 24.2 | 1 | 20.92
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 63 | 95 | 24.5 | 0.92 | 19.48
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 67 | 95 | 25.3 | 0.74 | 16.18
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 71 | 95 | 26.5 | 0.6 | 12.8
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 59 | 105 | 22.8 | 1 | 19.7
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 63 | 105 | 23.1 | 0.96 | 19.24
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 67 | 105 | 23.9 | 0.77 | 15.94
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 71 | 105 | 25.1 | 0.6 | 12.5
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 59 | 115 | 21.5 | 1 | 18.59
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 63 | 115 | 21.8 | 1 | 18.91
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 67 | 115 | 22.6 | 0.87 | 17.05
DHG036* (70% - Low Stage) | 3 | 1050 | 75 | 71 | 115 | 23.8 | 0.7 | 13.6
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 59 | 65 | 25.3 | 0.81 | 29.64
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 63 | 65 | 25.6 | 0.75 | 27.88
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 67 | 65 | 26.4 | 0.65 | 24.58
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 71 | 65 | 27.6 | 0.5 | 21.2
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 59 | 75 | 25 | 0.82 | 29.6
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 63 | 75 | 25.4 | 0.76 | 27.83
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 67 | 75 | 26.2 | 0.65 | 24.53
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 71 | 75 | 27.3 | 0.5 | 21.1
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 59 | 85 | 24.4 | 0.85 | 29.84
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 63 | 85 | 24.7 | 0.79 | 28.08
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 67 | 85 | 25.5 | 0.67 | 24.78
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 71 | 85 | 26.7 | 0.6 | 21.4
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 59 | 95 | 23.2 | 0.88 | 29.58
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 63 | 95 | 23.6 | 0.82 | 27.81
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 67 | 95 | 24.3 | 0.7 | 24.51
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 71 | 95 | 25.5 | 0.6 | 21.1
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 59 | 105 | 21.8 | 0.93 | 29.34
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 63 | 105 | 22.2 | 0.86 | 27.58
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 67 | 105 | 22.9 | 0.73 | 24.28
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 71 | 105 | 24.1 | 0.6 | 20.9
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 59 | 115 | 20.5 | 1 | 29.61
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 63 | 115 | 20.9 | 0.95 | 28.68
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 67 | 115 | 21.6 | 0.81 | 25.38
DHG036* (70% - Low Stage) | 3 | 630 | 80 | 71 | 115 | 22.8 | 0.7 | 22
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 59 | 65 | 26.1 | 1 | 24.45
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 63 | 65 | 26.4 | 0.97 | 24.06
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 67 | 65 | 27.2 | 0.81 | 20.76
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 71 | 65 | 28.4 | 0.7 | 17.3
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 59 | 75 | 25.9 | 1 | 24.23
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 63 | 75 | 26.2 | 0.98 | 24.01
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 67 | 75 | 27 | 0.82 | 20.71
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 71 | 75 | 28.2 | 0.7 | 17.3
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 59 | 85 | 25.2 | 1 | 23.61
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 63 | 85 | 25.6 | 1 | 23.95
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 67 | 85 | 26.3 | 0.85 | 20.96
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 71 | 85 | 27.5 | 0.7 | 17.5
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 59 | 95 | 24 | 1 | 22.53
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 63 | 95 | 24.4 | 1 | 22.87
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 67 | 95 | 25.2 | 0.88 | 20.7
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 71 | 95 | 26.3 | 0.7 | 17.3
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 59 | 105 | 22.6 | 1 | 21.21
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 63 | 105 | 23 | 1 | 21.55
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 67 | 105 | 23.8 | 0.92 | 20.46
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 71 | 105 | 24.9 | 0.7 | 17
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 59 | 115 | 21.3 | 1 | 20.01
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 63 | 115 | 21.7 | 1 | 20.35
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 67 | 115 | 22.5 | 1 | 21.06
DHG036* (70% - Low Stage) | 3 | 970 | 80 | 71 | 115 | 23.6 | 0.8 | 18.1
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 59 | 65 | 26.3 | 1 | 22.81
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 63 | 65 | 26.7 | 1 | 23.12
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 67 | 65 | 27.5 | 0.85 | 20.15
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 71 | 65 | 28.6 | 0.7 | 16.7
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 59 | 75 | 26.1 | 1 | 22.61
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 63 | 75 | 26.5 | 1 | 22.92
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 67 | 75 | 27.2 | 0.85 | 20.11
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 71 | 75 | 28.4 | 0.7 | 16.7
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 59 | 85 | 25.4 | 1 | 22.03
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 63 | 85 | 25.8 | 1 | 22.34
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 67 | 85 | 26.6 | 0.88 | 20.35
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 71 | 85 | 27.7 | 0.7 | 16.9
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 59 | 95 | 24.3 | 1 | 21.04
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 63 | 95 | 24.7 | 1 | 21.35
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 67 | 95 | 25.4 | 0.91 | 20.09
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 71 | 95 | 26.6 | 0.7 | 16.7
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 59 | 105 | 22.9 | 1 | 19.82
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 63 | 105 | 23.3 | 1 | 20.13
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 67 | 105 | 24 | 0.95 | 19.85
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 71 | 105 | 25.2 | 0.8 | 16.4
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 59 | 115 | 21.6 | 1 | 18.71
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 63 | 115 | 22 | 1 | 19.02
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 67 | 115 | 22.7 | 1 | 19.68
DHG036* (70% - Low Stage) | 3 | 1050 | 80 | 71 | 115 | 23.9 | 0.8 | 17.5
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 59 | 65 | 25.7 | 0.89 | 33.11
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 63 | 65 | 26.1 | 0.83 | 31.35
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 67 | 65 | 26.8 | 0.72 | 28.05
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 71 | 65 | 28 | 0.6 | 24.6
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 59 | 75 | 25.5 | 0.9 | 33.06
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 63 | 75 | 25.8 | 0.84 | 31.3
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 67 | 75 | 26.6 | 0.73 | 28
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 71 | 75 | 27.8 | 0.6 | 24.6
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 59 | 85 | 24.8 | 0.93 | 33.31
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 63 | 85 | 25.2 | 0.87 | 31.55
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 67 | 85 | 25.9 | 0.76 | 28.25
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 71 | 85 | 27.1 | 0.6 | 24.8
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 59 | 95 | 23.6 | 0.97 | 33.05
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 63 | 95 | 24 | 0.9 | 31.28
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 67 | 95 | 24.8 | 0.78 | 27.98
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 71 | 95 | 25.9 | 0.7 | 24.6
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 59 | 105 | 22.2 | 1 | 32.09
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 63 | 105 | 22.6 | 0.95 | 31.04
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 67 | 105 | 23.4 | 0.82 | 27.75
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 71 | 105 | 24.5 | 0.7 | 24.3
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 59 | 115 | 21 | 1 | 30.24
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 63 | 115 | 21.3 | 1 | 30.76
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 67 | 115 | 22.1 | 0.91 | 28.85
DHG036* (70% - Low Stage) | 3 | 630 | 85 | 71 | 115 | 23.2 | 0.8 | 25.4
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 59 | 65 | 26.5 | 1 | 24.85
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 63 | 65 | 26.9 | 1 | 25.19
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 67 | 65 | 27.6 | 0.94 | 24.23
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 71 | 65 | 28.8 | 0.8 | 20.8
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 59 | 75 | 26.3 | 1 | 24.64
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 63 | 75 | 26.7 | 1 | 24.98
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 67 | 75 | 27.4 | 0.94 | 24.18
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 71 | 75 | 28.6 | 0.8 | 20.8
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 59 | 85 | 25.6 | 1 | 24.01
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 63 | 85 | 26 | 1 | 24.35
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 67 | 85 | 26.7 | 0.97 | 24.43
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 71 | 85 | 27.9 | 0.8 | 21
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 59 | 95 | 24.5 | 1 | 22.93
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 63 | 95 | 24.8 | 1 | 23.27
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 67 | 95 | 25.6 | 1 | 23.99
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 71 | 95 | 26.8 | 0.8 | 20.7
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 59 | 105 | 23.1 | 1 | 21.62
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 63 | 105 | 23.4 | 1 | 21.95
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 67 | 105 | 24.2 | 1 | 22.67
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 71 | 105 | 25.4 | 0.9 | 20.5
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 59 | 115 | 21.8 | 1 | 20.41
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 63 | 115 | 22.1 | 1 | 20.75
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 67 | 115 | 22.9 | 1 | 21.47
DHG036* (70% - Low Stage) | 3 | 970 | 85 | 71 | 115 | 24.1 | 1 | 21.6
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 59 | 65 | 26.8 | 1 | 23.18
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 63 | 65 | 27.1 | 1 | 23.5
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 67 | 65 | 27.9 | 0.98 | 23.62
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 71 | 65 | 29.1 | 0.8 | 20.2
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 59 | 75 | 26.5 | 1 | 22.98
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 63 | 75 | 26.9 | 1 | 23.3
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 67 | 75 | 27.7 | 0.98 | 23.57
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 71 | 75 | 28.8 | 0.8 | 20.2
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 59 | 85 | 25.9 | 1 | 22.41
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 63 | 85 | 26.2 | 1 | 22.72
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 67 | 85 | 27 | 1 | 23.38
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 71 | 85 | 28.2 | 0.8 | 20.4
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 59 | 95 | 24.7 | 1 | 21.41
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 63 | 95 | 25.1 | 1 | 21.72
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 67 | 95 | 25.9 | 1 | 22.38
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 71 | 95 | 27 | 0.9 | 20.1
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 59 | 105 | 23.3 | 1 | 20.19
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 63 | 105 | 23.7 | 1 | 20.51
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 67 | 105 | 24.4 | 1 | 21.17
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 71 | 105 | 25.6 | 0.9 | 19.9
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 59 | 115 | 22 | 1 | 19.08
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 63 | 115 | 22.4 | 1 | 19.39
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 67 | 115 | 23.2 | 1 | 20.06
DHG036* (70% - Low Stage) | 3 | 1050 | 85 | 71 | 115 | 24.3 | 1 | 21
DHG048* | 4 | 1200 | 70 | 59 | 65 | 46.4 | 0.59 | 20.58
DHG048* | 4 | 1200 | 70 | 63 | 65 | 47 | 0.53 | 18.73
DHG048* | 4 | 1200 | 70 | 67 | 65 | 48.4 | 0.42 | 15.27
DHG048* | 4 | 1200 | 70 | 59 | 75 | 45.9 | 0.59 | 20.53
DHG048* | 4 | 1200 | 70 | 63 | 75 | 46.6 | 0.53 | 18.68
DHG048* | 4 | 1200 | 70 | 67 | 75 | 48 | 0.42 | 15.22
DHG048* | 4 | 1200 | 70 | 59 | 85 | 44.7 | 0.61 | 20.79
DHG048* | 4 | 1200 | 70 | 63 | 85 | 45.4 | 0.55 | 18.94
DHG048* | 4 | 1200 | 70 | 67 | 85 | 46.8 | 0.44 | 15.48
DHG048* | 4 | 1200 | 70 | 59 | 95 | 42.6 | 0.64 | 20.51
DHG048* | 4 | 1200 | 70 | 63 | 95 | 43.3 | 0.57 | 18.66
DHG048* | 4 | 1200 | 70 | 67 | 95 | 44.7 | 0.45 | 15.2
DHG048* | 4 | 1200 | 70 | 59 | 105 | 40 | 0.67 | 20.26
DHG048* | 4 | 1200 | 70 | 63 | 105 | 40.7 | 0.6 | 18.41
DHG048* | 4 | 1200 | 70 | 67 | 105 | 42.1 | 0.47 | 14.95
DHG048* | 4 | 1200 | 70 | 59 | 115 | 37.7 | 0.75 | 21.42
DHG048* | 4 | 1200 | 70 | 63 | 115 | 38.4 | 0.67 | 19.57
DHG048* | 4 | 1200 | 70 | 67 | 115 | 39.8 | 0.53 | 16.11
DHG048* | 4 | 1460 | 70 | 59 | 65 | 47.2 | 0.64 | 18.91
DHG048* | 4 | 1460 | 70 | 63 | 65 | 47.9 | 0.57 | 17.05
DHG048* | 4 | 1460 | 70 | 67 | 65 | 49.3 | 0.44 | 13.6
DHG048* | 4 | 1460 | 70 | 59 | 75 | 46.8 | 0.65 | 18.85
DHG048* | 4 | 1460 | 70 | 63 | 75 | 47.4 | 0.58 | 17
DHG048* | 4 | 1460 | 70 | 67 | 75 | 48.8 | 0.45 | 13.55
DHG048* | 4 | 1460 | 70 | 59 | 85 | 45.6 | 0.67 | 19.11
DHG048* | 4 | 1460 | 70 | 63 | 85 | 46.2 | 0.6 | 17.26
DHG048* | 4 | 1460 | 70 | 67 | 85 | 47.6 | 0.47 | 13.81
DHG048* | 4 | 1460 | 70 | 59 | 95 | 43.5 | 0.7 | 18.84
DHG048* | 4 | 1460 | 70 | 63 | 95 | 44.1 | 0.62 | 16.98
DHG048* | 4 | 1460 | 70 | 67 | 95 | 45.5 | 0.48 | 13.53
DHG048* | 4 | 1460 | 70 | 59 | 105 | 40.9 | 0.73 | 18.59
DHG048* | 4 | 1460 | 70 | 63 | 105 | 41.5 | 0.65 | 16.74
DHG048* | 4 | 1460 | 70 | 67 | 105 | 42.9 | 0.5 | 13.28
DHG048* | 4 | 1460 | 70 | 59 | 115 | 38.5 | 0.82 | 19.75
DHG048* | 4 | 1460 | 70 | 63 | 115 | 39.2 | 0.73 | 17.9
DHG048* | 4 | 1460 | 70 | 67 | 115 | 40.6 | 0.57 | 14.44
DHG048* | 4 | 2000 | 70 | 59 | 65 | 49.8 | 0.72 | 16.38
DHG048* | 4 | 2000 | 70 | 63 | 65 | 50.5 | 0.63 | 14.53
DHG048* | 4 | 2000 | 70 | 67 | 65 | 51.9 | 0.47 | 11.07
DHG048* | 4 | 2000 | 70 | 59 | 75 | 49.4 | 0.73 | 16.33
DHG048* | 4 | 2000 | 70 | 63 | 75 | 50.1 | 0.64 | 14.48
DHG048* | 4 | 2000 | 70 | 67 | 75 | 51.5 | 0.47 | 11.02
DHG048* | 4 | 2000 | 70 | 59 | 85 | 48.2 | 0.76 | 16.59
DHG048* | 4 | 2000 | 70 | 63 | 85 | 48.9 | 0.66 | 14.74
DHG048* | 4 | 2000 | 70 | 67 | 85 | 50.3 | 0.49 | 11.28
DHG048* | 4 | 2000 | 70 | 59 | 95 | 46.1 | 0.78 | 16.31
DHG048* | 4 | 2000 | 70 | 63 | 95 | 46.8 | 0.68 | 14.46
DHG048* | 4 | 2000 | 70 | 67 | 95 | 48.2 | 0.5 | 11.01
DHG048* | 4 | 2000 | 70 | 59 | 105 | 43.5 | 0.81 | 16.07
DHG048* | 4 | 2000 | 70 | 63 | 105 | 44.2 | 0.71 | 14.22
DHG048* | 4 | 2000 | 70 | 67 | 105 | 45.6 | 0.52 | 10.76
DHG048* | 4 | 2000 | 70 | 59 | 115 | 41.2 | 0.92 | 17.23
DHG048* | 4 | 2000 | 70 | 63 | 115 | 41.8 | 0.81 | 15.37
DHG048* | 4 | 2000 | 70 | 67 | 115 | 43.2 | 0.61 | 11.92
DHG048* | 4 | 1200 | 75 | 59 | 65 | 46.6 | 0.7 | 24.65
DHG048* | 4 | 1200 | 75 | 63 | 65 | 47.3 | 0.64 | 22.8
DHG048* | 4 | 1200 | 75 | 67 | 65 | 48.7 | 0.52 | 19.34
DHG048* | 4 | 1200 | 75 | 71 | 65 | 50.8 | 0.4 | 15.8
DHG048* | 4 | 1200 | 75 | 59 | 75 | 46.2 | 0.7 | 24.6
DHG048* | 4 | 1200 | 75 | 63 | 75 | 46.8 | 0.64 | 22.75
DHG048* | 4 | 1200 | 75 | 67 | 75 | 48.2 | 0.53 | 19.29
DHG048* | 4 | 1200 | 75 | 71 | 75 | 50.4 | 0.4 | 15.7
DHG048* | 4 | 1200 | 75 | 59 | 85 | 45 | 0.73 | 24.86
DHG048* | 4 | 1200 | 75 | 63 | 85 | 45.6 | 0.67 | 23.01
DHG048* | 4 | 1200 | 75 | 67 | 85 | 47 | 0.55 | 19.55
DHG048* | 4 | 1200 | 75 | 71 | 85 | 49.1 | 0.4 | 16
DHG048* | 4 | 1200 | 75 | 59 | 95 | 42.9 | 0.76 | 24.58
DHG048* | 4 | 1200 | 75 | 63 | 95 | 43.5 | 0.69 | 22.73
DHG048* | 4 | 1200 | 75 | 67 | 95 | 44.9 | 0.57 | 19.27
DHG048* | 4 | 1200 | 75 | 71 | 95 | 47 | 0.4 | 15.7
DHG048* | 4 | 1200 | 75 | 59 | 105 | 40.3 | 0.8 | 24.33
DHG048* | 4 | 1200 | 75 | 63 | 105 | 40.9 | 0.72 | 22.48
DHG048* | 4 | 1200 | 75 | 67 | 105 | 42.3 | 0.59 | 19.02
DHG048* | 4 | 1200 | 75 | 71 | 105 | 44.5 | 0.5 | 15.4
DHG048* | 4 | 1200 | 75 | 59 | 115 | 37.9 | 0.89 | 25.49
DHG048* | 4 | 1200 | 75 | 63 | 115 | 38.6 | 0.81 | 23.64
DHG048* | 4 | 1200 | 75 | 67 | 115 | 40 | 0.67 | 20.18
DHG048* | 4 | 1200 | 75 | 71 | 115 | 42.1 | 0.5 | 16.6
DHG048* | 4 | 1460 | 75 | 59 | 65 | 47.4 | 0.78 | 22.98
DHG048* | 4 | 1460 | 75 | 63 | 65 | 48.1 | 0.71 | 21.12
DHG048* | 4 | 1460 | 75 | 67 | 65 | 49.5 | 0.57 | 17.67
DHG048* | 4 | 1460 | 75 | 71 | 65 | 51.6 | 0.4 | 14.1
DHG048* | 4 | 1460 | 75 | 59 | 75 | 47 | 0.78 | 22.93
DHG048* | 4 | 1460 | 75 | 63 | 75 | 47.7 | 0.71 | 21.07
DHG048* | 4 | 1460 | 75 | 67 | 75 | 49.1 | 0.58 | 17.62
DHG048* | 4 | 1460 | 75 | 71 | 75 | 51.2 | 0.4 | 14
DHG048* | 4 | 1460 | 75 | 59 | 85 | 45.8 | 0.81 | 23.19
DHG048* | 4 | 1460 | 75 | 63 | 85 | 46.5 | 0.74 | 21.33
DHG048* | 4 | 1460 | 75 | 67 | 85 | 47.9 | 0.6 | 17.88
DHG048* | 4 | 1460 | 75 | 71 | 85 | 50 | 0.5 | 14.3
DHG048* | 4 | 1460 | 75 | 59 | 95 | 43.7 | 0.84 | 22.91
DHG048* | 4 | 1460 | 75 | 63 | 95 | 44.4 | 0.76 | 21.06
DHG048* | 4 | 1460 | 75 | 67 | 95 | 45.8 | 0.62 | 17.6
DHG048* | 4 | 1460 | 75 | 71 | 95 | 47.9 | 0.5 | 14
DHG048* | 4 | 1460 | 75 | 59 | 105 | 41.1 | 0.88 | 22.66
DHG048* | 4 | 1460 | 75 | 63 | 105 | 41.8 | 0.8 | 20.81
DHG048* | 4 | 1460 | 75 | 67 | 105 | 43.2 | 0.65 | 17.35
DHG048* | 4 | 1460 | 75 | 71 | 105 | 45.3 | 0.5 | 13.8
DHG048* | 4 | 1460 | 75 | 59 | 115 | 38.8 | 0.99 | 23.82
DHG048* | 4 | 1460 | 75 | 63 | 115 | 39.4 | 0.89 | 21.97
DHG048* | 4 | 1460 | 75 | 67 | 115 | 40.8 | 0.73 | 18.51
DHG048* | 4 | 1460 | 75 | 71 | 115 | 43 | 0.6 | 14.9
DHG048* | 4 | 2000 | 75 | 59 | 65 | 50.1 | 0.9 | 20.46
DHG048* | 4 | 2000 | 75 | 63 | 65 | 50.7 | 0.81 | 18.6
DHG048* | 4 | 2000 | 75 | 67 | 65 | 52.1 | 0.64 | 15.15
DHG048* | 4 | 2000 | 75 | 71 | 65 | 54.3 | 0.5 | 11.6
DHG048* | 4 | 2000 | 75 | 59 | 75 | 49.7 | 0.9 | 20.41
DHG048* | 4 | 2000 | 75 | 63 | 75 | 50.3 | 0.81 | 18.55
DHG048* | 4 | 2000 | 75 | 67 | 75 | 51.7 | 0.64 | 15.1
DHG048* | 4 | 2000 | 75 | 71 | 75 | 53.9 | 0.5 | 11.5
DHG048* | 4 | 2000 | 75 | 59 | 85 | 48.4 | 0.94 | 20.67
DHG048* | 4 | 2000 | 75 | 63 | 85 | 49.1 | 0.84 | 18.81
DHG048* | 4 | 2000 | 75 | 67 | 85 | 50.5 | 0.67 | 15.36
DHG048* | 4 | 2000 | 75 | 71 | 85 | 52.6 | 0.5 | 11.8
DHG048* | 4 | 2000 | 75 | 59 | 95 | 46.3 | 0.97 | 20.39
DHG048* | 4 | 2000 | 75 | 63 | 95 | 47 | 0.87 | 18.53
DHG048* | 4 | 2000 | 75 | 67 | 95 | 48.4 | 0.69 | 15.08
DHG048* | 4 | 2000 | 75 | 71 | 95 | 50.5 | 0.5 | 11.5
DHG048* | 4 | 2000 | 75 | 59 | 105 | 43.8 | 1 | 19.89
DHG048* | 4 | 2000 | 75 | 63 | 105 | 44.4 | 0.91 | 18.29
DHG048* | 4 | 2000 | 75 | 67 | 105 | 45.8 | 0.71 | 14.83
DHG048* | 4 | 2000 | 75 | 71 | 105 | 48 | 0.5 | 11.2
DHG048* | 4 | 2000 | 75 | 59 | 115 | 41.4 | 1 | 18.83
DHG048* | 4 | 2000 | 75 | 63 | 115 | 42.1 | 1 | 19.13
DHG048* | 4 | 2000 | 75 | 67 | 115 | 43.5 | 0.81 | 15.99
DHG048* | 4 | 2000 | 75 | 71 | 115 | 45.6 | 0.6 | 12.4
DHG048* | 4 | 1200 | 80 | 59 | 65 | 46.8 | 0.81 | 28.75
DHG048* | 4 | 1200 | 80 | 63 | 65 | 47.5 | 0.75 | 26.9
DHG048* | 4 | 1200 | 80 | 67 | 65 | 48.9 | 0.63 | 23.44
DHG048* | 4 | 1200 | 80 | 71 | 65 | 51 | 0.5 | 19.9
DHG048* | 4 | 1200 | 80 | 59 | 75 | 46.4 | 0.82 | 28.7
DHG048* | 4 | 1200 | 80 | 63 | 75 | 47.1 | 0.75 | 26.85
DHG048* | 4 | 1200 | 80 | 67 | 75 | 48.5 | 0.64 | 23.39
DHG048* | 4 | 1200 | 80 | 71 | 75 | 50.6 | 0.5 | 19.8
DHG048* | 4 | 1200 | 80 | 59 | 85 | 45.2 | 0.85 | 28.96
DHG048* | 4 | 1200 | 80 | 63 | 85 | 45.9 | 0.78 | 27.11
DHG048* | 4 | 1200 | 80 | 67 | 85 | 47.3 | 0.66 | 23.65
DHG048* | 4 | 1200 | 80 | 71 | 85 | 49.4 | 0.5 | 20.1
DHG048* | 4 | 1200 | 80 | 59 | 95 | 43.1 | 0.88 | 28.68
DHG048* | 4 | 1200 | 80 | 63 | 95 | 43.8 | 0.81 | 26.83
DHG048* | 4 | 1200 | 80 | 67 | 95 | 45.2 | 0.68 | 23.37
DHG048* | 4 | 1200 | 80 | 71 | 95 | 47.3 | 0.6 | 19.8
DHG048* | 4 | 1200 | 80 | 59 | 105 | 40.5 | 0.93 | 28.43
DHG048* | 4 | 1200 | 80 | 63 | 105 | 41.2 | 0.85 | 26.58
DHG048* | 4 | 1200 | 80 | 67 | 105 | 42.6 | 0.72 | 23.12
DHG048* | 4 | 1200 | 80 | 71 | 105 | 44.7 | 0.6 | 19.5
DHG048* | 4 | 1200 | 80 | 59 | 115 | 38.2 | 1 | 28.92
DHG048* | 4 | 1200 | 80 | 63 | 115 | 38.8 | 0.94 | 27.74
DHG048* | 4 | 1200 | 80 | 67 | 115 | 40.2 | 0.8 | 24.28
DHG048* | 4 | 1200 | 80 | 71 | 115 | 42.4 | 0.6 | 20.7
DHG048* | 4 | 1460 | 80 | 59 | 65 | 47.7 | 0.91 | 27.08
DHG048* | 4 | 1460 | 80 | 63 | 65 | 48.3 | 0.84 | 25.22
DHG048* | 4 | 1460 | 80 | 67 | 65 | 49.7 | 0.7 | 21.77
DHG048* | 4 | 1460 | 80 | 71 | 65 | 51.9 | 0.6 | 18.2
DHG048* | 4 | 1460 | 80 | 59 | 75 | 47.3 | 0.92 | 27.03
DHG048* | 4 | 1460 | 80 | 63 | 75 | 47.9 | 0.84 | 25.17
DHG048* | 4 | 1460 | 80 | 67 | 75 | 49.3 | 0.71 | 21.72
DHG048* | 4 | 1460 | 80 | 71 | 75 | 51.5 | 0.6 | 18.1
DHG048* | 4 | 1460 | 80 | 59 | 85 | 46 | 0.95 | 27.29
DHG048* | 4 | 1460 | 80 | 63 | 85 | 46.7 | 0.87 | 25.43
DHG048* | 4 | 1460 | 80 | 67 | 85 | 48.1 | 0.73 | 21.98
DHG048* | 4 | 1460 | 80 | 71 | 85 | 50.2 | 0.6 | 18.4
DHG048* | 4 | 1460 | 80 | 59 | 95 | 43.9 | 0.99 | 27.01
DHG048* | 4 | 1460 | 80 | 63 | 95 | 44.6 | 0.91 | 25.15
DHG048* | 4 | 1460 | 80 | 67 | 95 | 46 | 0.76 | 21.7
DHG048* | 4 | 1460 | 80 | 71 | 95 | 48.1 | 0.6 | 18.1
DHG048* | 4 | 1460 | 80 | 59 | 105 | 41.4 | 1 | 25.76
DHG048* | 4 | 1460 | 80 | 63 | 105 | 42 | 0.95 | 24.91
DHG048* | 4 | 1460 | 80 | 67 | 105 | 43.4 | 0.79 | 21.45
DHG048* | 4 | 1460 | 80 | 71 | 105 | 45.6 | 0.6 | 17.9
DHG048* | 4 | 1460 | 80 | 59 | 115 | 39 | 1 | 24.3
DHG048* | 4 | 1460 | 80 | 63 | 115 | 39.7 | 1 | 24.71
DHG048* | 4 | 1460 | 80 | 67 | 115 | 41.1 | 0.88 | 22.61
DHG048* | 4 | 1460 | 80 | 71 | 115 | 43.2 | 0.7 | 19
DHG048* | 4 | 2000 | 80 | 59 | 65 | 50.3 | 1 | 22.87
DHG048* | 4 | 2000 | 80 | 63 | 65 | 51 | 0.98 | 22.7
DHG048* | 4 | 2000 | 80 | 67 | 65 | 52.4 | 0.81 | 19.25
DHG048* | 4 | 2000 | 80 | 71 | 65 | 54.5 | 0.6 | 15.7
DHG048* | 4 | 2000 | 80 | 59 | 75 | 49.9 | 1 | 22.68
DHG048* | 4 | 2000 | 80 | 63 | 75 | 50.6 | 0.99 | 22.65
DHG048* | 4 | 2000 | 80 | 67 | 75 | 52 | 0.81 | 19.2
DHG048* | 4 | 2000 | 80 | 71 | 75 | 54.1 | 0.6 | 15.6
DHG048* | 4 | 2000 | 80 | 59 | 85 | 48.7 | 1 | 22.13
DHG048* | 4 | 2000 | 80 | 63 | 85 | 49.3 | 1 | 22.43
DHG048* | 4 | 2000 | 80 | 67 | 85 | 50.7 | 0.84 | 19.46
DHG048* | 4 | 2000 | 80 | 71 | 85 | 52.9 | 0.7 | 15.9
DHG048* | 4 | 2000 | 80 | 59 | 95 | 46.6 | 1 | 21.17
DHG048* | 4 | 2000 | 80 | 63 | 95 | 47.2 | 1 | 21.47
DHG048* | 4 | 2000 | 80 | 67 | 95 | 48.6 | 0.87 | 19.18
DHG048* | 4 | 2000 | 80 | 71 | 95 | 50.8 | 0.7 | 15.6
DHG048* | 4 | 2000 | 80 | 59 | 105 | 44 | 1 | 20
DHG048* | 4 | 2000 | 80 | 63 | 105 | 44.7 | 1 | 20.3
DHG048* | 4 | 2000 | 80 | 67 | 105 | 46.1 | 0.9 | 18.93
DHG048* | 4 | 2000 | 80 | 71 | 105 | 48.2 | 0.7 | 15.3
DHG048* | 4 | 2000 | 80 | 59 | 115 | 41.7 | 1 | 18.94
DHG048* | 4 | 2000 | 80 | 63 | 115 | 42.3 | 1 | 19.24
DHG048* | 4 | 2000 | 80 | 67 | 115 | 43.7 | 1 | 19.87
DHG048* | 4 | 2000 | 80 | 71 | 115 | 45.9 | 0.8 | 16.5
DHG048* | 4 | 1200 | 85 | 59 | 65 | 47.6 | 0.9 | 32.38
DHG048* | 4 | 1200 | 85 | 63 | 65 | 48.3 | 0.83 | 30.53
DHG048* | 4 | 1200 | 85 | 67 | 65 | 49.7 | 0.72 | 27.08
DHG048* | 4 | 1200 | 85 | 71 | 65 | 51.8 | 0.6 | 23.5
DHG048* | 4 | 1200 | 85 | 59 | 75 | 47.2 | 0.9 | 32.33
DHG048* | 4 | 1200 | 85 | 63 | 75 | 47.9 | 0.84 | 30.48
DHG048* | 4 | 1200 | 85 | 67 | 75 | 49.3 | 0.72 | 27.02
DHG048* | 4 | 1200 | 85 | 71 | 75 | 51.4 | 0.6 | 23.4
DHG048* | 4 | 1200 | 85 | 59 | 85 | 46 | 0.94 | 32.59
DHG048* | 4 | 1200 | 85 | 63 | 85 | 46.6 | 0.87 | 30.74
DHG048* | 4 | 1200 | 85 | 67 | 85 | 48 | 0.75 | 27.28
DHG048* | 4 | 1200 | 85 | 71 | 85 | 50.2 | 0.6 | 23.7
DHG048* | 4 | 1200 | 85 | 59 | 95 | 43.9 | 0.97 | 32.32
DHG048* | 4 | 1200 | 85 | 63 | 95 | 44.5 | 0.9 | 30.46
DHG048* | 4 | 1200 | 85 | 67 | 95 | 45.9 | 0.78 | 27.01
DHG048* | 4 | 1200 | 85 | 71 | 95 | 48.1 | 0.6 | 23.4
DHG048* | 4 | 1200 | 85 | 59 | 105 | 41.3 | 1 | 31.3
DHG048* | 4 | 1200 | 85 | 63 | 105 | 42 | 0.95 | 30.22
DHG048* | 4 | 1200 | 85 | 67 | 105 | 43.4 | 0.81 | 26.76
DHG048* | 4 | 1200 | 85 | 71 | 105 | 45.5 | 0.7 | 23.2
DHG048* | 4 | 1200 | 85 | 59 | 115 | 39 | 1 | 29.52
DHG048* | 4 | 1200 | 85 | 63 | 115 | 39.6 | 1 | 30.02
DHG048* | 4 | 1200 | 85 | 67 | 115 | 41 | 0.9 | 27.92
DHG048* | 4 | 1200 | 85 | 71 | 115 | 43.2 | 0.7 | 24.3
DHG048* | 4 | 1460 | 85 | 59 | 65 | 48.5 | 1 | 30.18
DHG048* | 4 | 1460 | 85 | 63 | 65 | 49.1 | 0.94 | 28.86
DHG048* | 4 | 1460 | 85 | 67 | 65 | 50.5 | 0.81 | 25.4
DHG048* | 4 | 1460 | 85 | 71 | 65 | 52.7 | 0.7 | 21.8
DHG048* | 4 | 1460 | 85 | 59 | 75 | 48.1 | 1 | 29.92
DHG048* | 4 | 1460 | 85 | 63 | 75 | 48.7 | 0.95 | 28.81
DHG048* | 4 | 1460 | 85 | 67 | 75 | 50.1 | 0.81 | 25.35
DHG048* | 4 | 1460 | 85 | 71 | 75 | 52.2 | 0.7 | 21.8
DHG048* | 4 | 1460 | 85 | 59 | 85 | 46.8 | 1 | 29.16
DHG048* | 4 | 1460 | 85 | 63 | 85 | 47.5 | 0.98 | 29.07
DHG048* | 4 | 1460 | 85 | 67 | 85 | 48.9 | 0.84 | 25.61
DHG048* | 4 | 1460 | 85 | 71 | 85 | 51 | 0.7 | 22
DHG048* | 4 | 1460 | 85 | 59 | 95 | 44.7 | 1 | 27.85
DHG048* | 4 | 1460 | 85 | 63 | 95 | 45.4 | 1 | 28.26
DHG048* | 4 | 1460 | 85 | 67 | 95 | 46.8 | 0.87 | 25.33
DHG048* | 4 | 1460 | 85 | 71 | 95 | 48.9 | 0.7 | 21.8
DHG048* | 4 | 1460 | 85 | 59 | 105 | 42.2 | 1 | 26.25
DHG048* | 4 | 1460 | 85 | 63 | 105 | 42.8 | 1 | 26.66
DHG048* | 4 | 1460 | 85 | 67 | 105 | 44.2 | 0.91 | 25.09
DHG048* | 4 | 1460 | 85 | 71 | 105 | 46.4 | 0.7 | 21.5
DHG048* | 4 | 1460 | 85 | 59 | 115 | 39.8 | 1 | 24.79
DHG048* | 4 | 1460 | 85 | 63 | 115 | 40.5 | 1 | 25.2
DHG048* | 4 | 1460 | 85 | 67 | 115 | 41.9 | 1 | 26.07
DHG048* | 4 | 1460 | 85 | 71 | 115 | 44 | 0.8 | 22.7
DHG048* | 4 | 2000 | 85 | 59 | 65 | 51.1 | 1 | 23.23
DHG048* | 4 | 2000 | 85 | 63 | 65 | 51.8 | 1 | 23.53
DHG048* | 4 | 2000 | 85 | 67 | 65 | 53.2 | 0.95 | 22.88
DHG048* | 4 | 2000 | 85 | 71 | 65 | 55.3 | 0.8 | 19.3
DHG048* | 4 | 2000 | 85 | 59 | 75 | 50.7 | 1 | 23.04
DHG048* | 4 | 2000 | 85 | 63 | 75 | 51.4 | 1 | 23.34
DHG048* | 4 | 2000 | 85 | 67 | 75 | 52.7 | 0.95 | 22.83
DHG048* | 4 | 2000 | 85 | 71 | 75 | 54.9 | 0.8 | 19.2
DHG048* | 4 | 2000 | 85 | 59 | 85 | 49.5 | 1 | 22.49
DHG048* | 4 | 2000 | 85 | 63 | 85 | 50.1 | 1 | 22.79
DHG048* | 4 | 2000 | 85 | 67 | 85 | 51.5 | 0.99 | 23.09
DHG048* | 4 | 2000 | 85 | 71 | 85 | 53.7 | 0.8 | 19.5
DHG048* | 4 | 2000 | 85 | 59 | 95 | 47.4 | 1 | 21.53
DHG048* | 4 | 2000 | 85 | 63 | 95 | 48 | 1 | 21.83
DHG048* | 4 | 2000 | 85 | 67 | 95 | 49.4 | 1 | 22.47
DHG048* | 4 | 2000 | 85 | 71 | 95 | 51.6 | 0.8 | 19.2
DHG048* | 4 | 2000 | 85 | 59 | 105 | 44.8 | 1 | 20.36
DHG048* | 4 | 2000 | 85 | 63 | 105 | 45.5 | 1 | 20.66
DHG048* | 4 | 2000 | 85 | 67 | 105 | 46.9 | 1 | 21.3
DHG048* | 4 | 2000 | 85 | 71 | 105 | 49 | 0.9 | 19
DHG048* | 4 | 2000 | 85 | 59 | 115 | 42.5 | 1 | 19.3
DHG048* | 4 | 2000 | 85 | 63 | 115 | 43.1 | 1 | 19.6
DHG048* | 4 | 2000 | 85 | 67 | 115 | 44.5 | 1 | 20.23
DHG048* | 4 | 2000 | 85 | 71 | 115 | 46.6 | 0.9 | 20.1
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 59 | 65 | 33.2 | 0.56 | 20.18
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 63 | 65 | 33.7 | 0.5 | 18.39
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 67 | 65 | 34.7 | 0.4 | 15.06
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 59 | 75 | 32.9 | 0.56 | 20.13
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 63 | 75 | 33.4 | 0.51 | 18.34
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 67 | 75 | 34.4 | 0.4 | 15.01
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 59 | 85 | 32.1 | 0.59 | 20.38
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 63 | 85 | 32.5 | 0.53 | 18.6
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 67 | 85 | 33.5 | 0.42 | 15.26
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 59 | 95 | 30.5 | 0.61 | 20.11
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 63 | 95 | 31 | 0.55 | 18.33
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 67 | 95 | 32 | 0.43 | 14.99
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 59 | 105 | 28.7 | 0.64 | 19.87
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 63 | 105 | 29.2 | 0.57 | 18.09
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 67 | 105 | 30.2 | 0.45 | 14.75
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 59 | 115 | 27 | 0.72 | 20.99
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 63 | 115 | 27.5 | 0.65 | 19.21
DHG048* (70% - Low Stage) | 4 | 840 | 70 | 67 | 115 | 28.5 | 0.51 | 15.87
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 59 | 65 | 33.9 | 0.63 | 18.24
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 63 | 65 | 34.4 | 0.56 | 16.46
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 67 | 65 | 35.4 | 0.43 | 13.12
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 59 | 75 | 33.6 | 0.63 | 18.19
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 63 | 75 | 34.1 | 0.56 | 16.41
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 67 | 75 | 35.1 | 0.43 | 13.07
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 59 | 85 | 32.8 | 0.66 | 18.45
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 63 | 85 | 33.2 | 0.58 | 16.66
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 67 | 85 | 34.2 | 0.45 | 13.32
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 59 | 95 | 31.2 | 0.68 | 18.18
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 63 | 95 | 31.7 | 0.6 | 16.39
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 67 | 95 | 32.7 | 0.47 | 13.05
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 59 | 105 | 29.4 | 0.71 | 17.94
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 63 | 105 | 29.9 | 0.63 | 16.15
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 67 | 105 | 30.9 | 0.48 | 12.81
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 59 | 115 | 27.7 | 0.8 | 19.06
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 63 | 115 | 28.2 | 0.71 | 17.27
DHG048* (70% - Low Stage) | 4 | 1060 | 70 | 67 | 115 | 29.2 | 0.56 | 13.93
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 59 | 65 | 35.5 | 0.7 | 16.1
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 63 | 65 | 36 | 0.61 | 14.31
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 67 | 65 | 37 | 0.46 | 10.98
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 59 | 75 | 35.2 | 0.7 | 16.05
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 63 | 75 | 35.7 | 0.62 | 14.26
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 67 | 75 | 36.7 | 0.46 | 10.93
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 59 | 85 | 34.3 | 0.73 | 16.3
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 63 | 85 | 34.8 | 0.64 | 14.52
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 67 | 85 | 35.8 | 0.48 | 11.18
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 59 | 95 | 32.8 | 0.75 | 16.03
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 63 | 95 | 33.3 | 0.66 | 14.25
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 67 | 95 | 34.3 | 0.49 | 10.91
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 59 | 105 | 31 | 0.79 | 15.79
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 63 | 105 | 31.5 | 0.69 | 14.01
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 67 | 105 | 32.5 | 0.51 | 10.67
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 59 | 115 | 29.3 | 0.89 | 16.91
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 63 | 115 | 29.8 | 0.78 | 15.13
DHG048* (70% - Low Stage) | 4 | 1400 | 70 | 67 | 115 | 30.8 | 0.59 | 11.79
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 59 | 65 | 33.4 | 0.67 | 24.11
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 63 | 65 | 33.9 | 0.61 | 22.32
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 67 | 65 | 34.9 | 0.5 | 18.99
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 71 | 65 | 36.4 | 0.4 | 15.5
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 59 | 75 | 33.1 | 0.67 | 24.06
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 63 | 75 | 33.6 | 0.61 | 22.27
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 67 | 75 | 34.6 | 0.51 | 18.94
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 71 | 75 | 36.1 | 0.4 | 15.5
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 59 | 85 | 32.2 | 0.7 | 24.31
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 63 | 85 | 32.7 | 0.64 | 22.52
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 67 | 85 | 33.7 | 0.53 | 19.19
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 71 | 85 | 35.3 | 0.4 | 15.7
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 59 | 95 | 30.7 | 0.72 | 24.04
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 63 | 95 | 31.2 | 0.66 | 22.26
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 67 | 95 | 32.2 | 0.54 | 18.92
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 71 | 95 | 33.7 | 0.4 | 15.5
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 59 | 105 | 28.9 | 0.76 | 23.8
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 63 | 105 | 29.4 | 0.69 | 22.02
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 67 | 105 | 30.4 | 0.57 | 18.68
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 71 | 105 | 31.9 | 0.4 | 15.2
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 59 | 115 | 27.2 | 0.85 | 24.92
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 63 | 115 | 27.7 | 0.77 | 23.14
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 67 | 115 | 28.7 | 0.64 | 19.8
DHG048* (70% - Low Stage) | 4 | 840 | 75 | 71 | 115 | 30.2 | 0.5 | 16.3
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 59 | 65 | 34.1 | 0.76 | 22.17
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 63 | 65 | 34.6 | 0.69 | 20.39
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 67 | 65 | 35.6 | 0.56 | 17.05
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 71 | 65 | 37.1 | 0.4 | 13.6
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 59 | 75 | 33.8 | 0.76 | 22.12
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 63 | 75 | 34.3 | 0.69 | 20.34
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 67 | 75 | 35.3 | 0.56 | 17
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 71 | 75 | 36.8 | 0.4 | 13.5
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 59 | 85 | 32.9 | 0.79 | 22.37
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 63 | 85 | 33.4 | 0.72 | 20.59
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 67 | 85 | 34.4 | 0.58 | 17.25
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 71 | 85 | 35.9 | 0.4 | 13.8
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 59 | 95 | 31.4 | 0.82 | 22.11
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 63 | 95 | 31.9 | 0.74 | 20.32
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 67 | 95 | 32.9 | 0.6 | 16.98
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 71 | 95 | 34.4 | 0.5 | 13.5
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 59 | 105 | 29.6 | 0.86 | 21.87
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 63 | 105 | 30 | 0.78 | 20.08
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 67 | 105 | 31.1 | 0.63 | 16.74
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 71 | 105 | 32.6 | 0.5 | 13.3
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 59 | 115 | 27.9 | 0.96 | 22.99
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 63 | 115 | 28.4 | 0.87 | 21.2
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 67 | 115 | 29.4 | 0.71 | 17.86
DHG048* (70% - Low Stage) | 4 | 1060 | 75 | 71 | 115 | 30.9 | 0.5 | 14.4
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 59 | 65 | 35.7 | 0.86 | 20.03
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 63 | 65 | 36.2 | 0.78 | 18.24
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 67 | 65 | 37.2 | 0.62 | 14.91
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 71 | 65 | 38.7 | 0.5 | 11.4
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 59 | 75 | 35.4 | 0.87 | 19.98
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 63 | 75 | 35.9 | 0.78 | 18.19
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 67 | 75 | 36.9 | 0.62 | 14.86
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 71 | 75 | 38.4 | 0.5 | 11.4
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 59 | 85 | 34.5 | 0.9 | 20.23
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 63 | 85 | 35 | 0.81 | 18.44
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 67 | 85 | 36 | 0.65 | 15.11
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 71 | 85 | 37.5 | 0.5 | 11.7
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 59 | 95 | 33 | 0.93 | 19.96
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 63 | 95 | 33.5 | 0.84 | 18.18
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 67 | 95 | 34.5 | 0.66 | 14.84
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 71 | 95 | 36 | 0.5 | 11.4
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 59 | 105 | 31.2 | 0.97 | 19.72
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 63 | 105 | 31.6 | 0.87 | 17.94
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 67 | 105 | 32.6 | 0.69 | 14.6
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 71 | 105 | 34.2 | 0.5 | 11.1
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 59 | 115 | 29.5 | 1 | 19.14
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 63 | 115 | 29.9 | 0.98 | 19.06
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 67 | 115 | 30.9 | 0.78 | 15.72
DHG048* (70% - Low Stage) | 4 | 1400 | 75 | 71 | 115 | 32.5 | 0.6 | 12.3
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 59 | 65 | 33.6 | 0.77 | 28.07
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 63 | 65 | 34.1 | 0.71 | 26.28
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 67 | 65 | 35.1 | 0.6 | 22.94
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 71 | 65 | 36.6 | 0.5 | 19.5
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 59 | 75 | 33.3 | 0.78 | 28.02
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 63 | 75 | 33.8 | 0.72 | 26.23
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 67 | 75 | 34.8 | 0.61 | 22.89
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 71 | 75 | 36.3 | 0.5 | 19.4
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 59 | 85 | 32.4 | 0.81 | 28.27
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 63 | 85 | 32.9 | 0.74 | 26.48
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 67 | 85 | 33.9 | 0.63 | 23.14
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 71 | 85 | 35.4 | 0.5 | 19.7
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 59 | 95 | 30.9 | 0.84 | 28
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 63 | 95 | 31.4 | 0.77 | 26.21
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 67 | 95 | 32.4 | 0.65 | 22.87
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 71 | 95 | 33.9 | 0.5 | 19.4
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 59 | 105 | 29.1 | 0.88 | 27.76
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 63 | 105 | 29.5 | 0.81 | 25.97
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 67 | 105 | 30.5 | 0.69 | 22.64
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 71 | 105 | 32.1 | 0.6 | 19.2
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 59 | 115 | 27.4 | 0.98 | 28.88
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 63 | 115 | 27.8 | 0.9 | 27.09
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 67 | 115 | 28.8 | 0.76 | 23.75
DHG048* (70% - Low Stage) | 4 | 840 | 80 | 71 | 115 | 30.4 | 0.6 | 20.3
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 59 | 65 | 34.3 | 0.89 | 26.13
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 63 | 65 | 34.8 | 0.82 | 24.34
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 67 | 65 | 35.8 | 0.68 | 21
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 71 | 65 | 37.3 | 0.5 | 17.5
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 59 | 75 | 34 | 0.89 | 26.08
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 63 | 75 | 34.5 | 0.82 | 24.29
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 67 | 75 | 35.5 | 0.69 | 20.96
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 71 | 75 | 37 | 0.6 | 17.5
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 59 | 85 | 33.1 | 0.93 | 26.33
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 63 | 85 | 33.6 | 0.85 | 24.54
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 67 | 85 | 34.6 | 0.71 | 21.21
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 71 | 85 | 36.1 | 0.6 | 17.8
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 59 | 95 | 31.6 | 0.96 | 26.06
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 63 | 95 | 32.1 | 0.88 | 24.27
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 67 | 95 | 33.1 | 0.74 | 20.94
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 71 | 95 | 34.6 | 0.6 | 17.5
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 59 | 105 | 29.7 | 1 | 25.51
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 63 | 105 | 30.2 | 0.93 | 24.04
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 67 | 105 | 31.2 | 0.77 | 20.7
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 71 | 105 | 32.8 | 0.6 | 17.2
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 59 | 115 | 28.1 | 1 | 24.06
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 63 | 115 | 28.5 | 1 | 24.47
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 67 | 115 | 29.5 | 0.86 | 21.82
DHG048* (70% - Low Stage) | 4 | 1060 | 80 | 71 | 115 | 31.1 | 0.7 | 18.4
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 59 | 65 | 35.9 | 1 | 23.29
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 63 | 65 | 36.3 | 0.94 | 22.2
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 67 | 65 | 37.3 | 0.78 | 18.86
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 71 | 65 | 38.9 | 0.6 | 15.4
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 59 | 75 | 35.6 | 1 | 23.1
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 63 | 75 | 36 | 0.95 | 22.15
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 67 | 75 | 37 | 0.78 | 18.81
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 71 | 75 | 38.6 | 0.6 | 15.4
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 59 | 85 | 34.7 | 1 | 22.52
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 63 | 85 | 35.2 | 0.98 | 22.4
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 67 | 85 | 36.2 | 0.81 | 19.06
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 71 | 85 | 37.7 | 0.6 | 15.6
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 59 | 95 | 33.2 | 1 | 21.54
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 63 | 95 | 33.7 | 1 | 21.85
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 67 | 95 | 34.7 | 0.84 | 18.79
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 71 | 95 | 36.2 | 0.7 | 15.3
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 59 | 105 | 31.3 | 1 | 20.34
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 63 | 105 | 31.8 | 1 | 20.65
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 67 | 105 | 32.8 | 0.87 | 18.56
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 71 | 105 | 34.3 | 0.7 | 15.1
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 59 | 115 | 29.6 | 1 | 19.25
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 63 | 115 | 30.1 | 1 | 19.56
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 67 | 115 | 31.1 | 0.97 | 19.67
DHG048* (70% - Low Stage) | 4 | 1400 | 80 | 71 | 115 | 32.7 | 0.8 | 16.2
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 59 | 65 | 34.2 | 0.85 | 31.57
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 63 | 65 | 34.6 | 0.79 | 29.79
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 67 | 65 | 35.6 | 0.69 | 26.45
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 71 | 65 | 37.2 | 0.6 | 23
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 59 | 75 | 33.9 | 0.86 | 31.52
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 63 | 75 | 34.3 | 0.8 | 29.74
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 67 | 75 | 35.3 | 0.69 | 26.4
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 71 | 75 | 36.9 | 0.6 | 22.9
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 59 | 85 | 33 | 0.89 | 31.78
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 63 | 85 | 33.5 | 0.83 | 29.99
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 67 | 85 | 34.5 | 0.71 | 26.65
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 71 | 85 | 36 | 0.6 | 23.2
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 59 | 95 | 31.5 | 0.93 | 31.51
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 63 | 95 | 31.9 | 0.86 | 29.72
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 67 | 95 | 32.9 | 0.74 | 26.38
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 71 | 95 | 34.5 | 0.6 | 22.9
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 59 | 105 | 29.6 | 0.98 | 31.27
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 63 | 105 | 30.1 | 0.91 | 29.48
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 67 | 105 | 31.1 | 0.78 | 26.14
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 71 | 105 | 32.6 | 0.6 | 22.7
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 59 | 115 | 27.9 | 1 | 30.23
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 63 | 115 | 28.4 | 1 | 30.6
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 67 | 115 | 29.4 | 0.86 | 27.26
DHG048* (70% - Low Stage) | 4 | 840 | 85 | 71 | 115 | 30.9 | 0.7 | 23.8
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 59 | 65 | 34.9 | 0.99 | 29.64
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 63 | 65 | 35.3 | 0.92 | 27.85
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 67 | 65 | 36.3 | 0.79 | 24.51
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 71 | 65 | 37.9 | 0.6 | 21.1
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 59 | 75 | 34.6 | 1 | 29.59
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 63 | 75 | 35 | 0.93 | 27.8
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 67 | 75 | 36 | 0.79 | 24.46
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 71 | 75 | 37.6 | 0.7 | 21
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 59 | 85 | 33.7 | 1 | 28.88
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 63 | 85 | 34.1 | 0.96 | 28.05
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 67 | 85 | 35.2 | 0.82 | 24.72
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 71 | 85 | 36.7 | 0.7 | 21.3
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 59 | 95 | 32.2 | 1 | 27.58
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 63 | 95 | 32.6 | 0.99 | 27.78
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 67 | 95 | 33.6 | 0.85 | 24.45
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 71 | 95 | 35.2 | 0.7 | 21
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 59 | 105 | 30.3 | 1 | 26
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 63 | 105 | 30.8 | 1 | 26.4
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 67 | 105 | 31.8 | 0.89 | 24.21
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 71 | 105 | 33.3 | 0.7 | 20.8
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 59 | 115 | 28.6 | 1 | 24.55
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 63 | 115 | 29.1 | 1 | 24.96
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 67 | 115 | 30.1 | 0.98 | 25.33
DHG048* (70% - Low Stage) | 4 | 1060 | 85 | 71 | 115 | 31.6 | 0.8 | 21.9
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 59 | 65 | 36.4 | 1 | 23.66
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 63 | 65 | 36.9 | 1 | 23.97
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 67 | 65 | 37.9 | 0.91 | 22.37
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 71 | 65 | 39.5 | 0.7 | 18.9
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 59 | 75 | 36.1 | 1 | 23.46
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 63 | 75 | 36.6 | 1 | 23.77
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 67 | 75 | 37.6 | 0.91 | 22.32
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 71 | 75 | 39.1 | 0.7 | 18.9
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 59 | 85 | 35.3 | 1 | 22.89
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 63 | 85 | 35.7 | 1 | 23.2
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 67 | 85 | 36.7 | 0.95 | 22.57
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 71 | 85 | 38.3 | 0.8 | 19.1
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 59 | 95 | 33.7 | 1 | 21.91
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 63 | 95 | 34.2 | 1 | 22.22
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 67 | 95 | 35.2 | 0.98 | 22.3
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 71 | 95 | 36.8 | 0.8 | 18.8
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 59 | 105 | 31.9 | 1 | 20.71
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 63 | 105 | 32.4 | 1 | 21.02
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 67 | 105 | 33.4 | 1 | 21.67
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 71 | 105 | 34.9 | 0.8 | 18.6
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 59 | 115 | 30.2 | 1 | 19.62
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 63 | 115 | 30.7 | 1 | 19.93
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 67 | 115 | 31.7 | 1 | 20.58
DHG048* (70% - Low Stage) | 4 | 1400 | 85 | 71 | 115 | 33.2 | 0.9 | 19.7
DHG060* | 5 | 1500 | 70 | 59 | 65 | 59.3 | 0.56 | 20.1
DHG060* | 5 | 1500 | 70 | 63 | 65 | 60.2 | 0.5 | 18.31
DHG060* | 5 | 1500 | 70 | 67 | 65 | 62 | 0.4 | 14.98
DHG060* | 5 | 1500 | 70 | 59 | 75 | 58.8 | 0.56 | 20.05
DHG060* | 5 | 1500 | 70 | 63 | 75 | 59.6 | 0.51 | 18.26
DHG060* | 5 | 1500 | 70 | 67 | 75 | 61.4 | 0.4 | 14.93
DHG060* | 5 | 1500 | 70 | 59 | 85 | 57.2 | 0.59 | 20.3
DHG060* | 5 | 1500 | 70 | 63 | 85 | 58.1 | 0.53 | 18.51
DHG060* | 5 | 1500 | 70 | 67 | 85 | 59.9 | 0.42 | 15.18
DHG060* | 5 | 1500 | 70 | 59 | 95 | 54.5 | 0.61 | 20.03
DHG060* | 5 | 1500 | 70 | 63 | 95 | 55.4 | 0.54 | 18.24
DHG060* | 5 | 1500 | 70 | 67 | 95 | 57.2 | 0.43 | 14.91
DHG060* | 5 | 1500 | 70 | 59 | 105 | 51.2 | 0.64 | 19.79
DHG060* | 5 | 1500 | 70 | 63 | 105 | 52.1 | 0.57 | 18.01
DHG060* | 5 | 1500 | 70 | 67 | 105 | 53.9 | 0.45 | 14.67
DHG060* | 5 | 1500 | 70 | 59 | 115 | 48.2 | 0.72 | 20.91
DHG060* | 5 | 1500 | 70 | 63 | 115 | 49.1 | 0.64 | 19.12
DHG060* | 5 | 1500 | 70 | 67 | 115 | 50.9 | 0.51 | 15.79
DHG060* | 5 | 1880 | 70 | 59 | 65 | 60.5 | 0.62 | 18.22
DHG060* | 5 | 1880 | 70 | 63 | 65 | 61.4 | 0.55 | 16.44
DHG060* | 5 | 1880 | 70 | 67 | 65 | 63.2 | 0.43 | 13.1
DHG060* | 5 | 1880 | 70 | 59 | 75 | 60 | 0.63 | 18.17
DHG060* | 5 | 1880 | 70 | 63 | 75 | 60.8 | 0.56 | 16.39
DHG060* | 5 | 1880 | 70 | 67 | 75 | 62.6 | 0.43 | 13.06
DHG060* | 5 | 1880 | 70 | 59 | 85 | 58.4 | 0.65 | 18.42
DHG060* | 5 | 1880 | 70 | 63 | 85 | 59.3 | 0.58 | 16.64
DHG060* | 5 | 1880 | 70 | 67 | 85 | 61.1 | 0.45 | 13.31
DHG060* | 5 | 1880 | 70 | 59 | 95 | 55.7 | 0.67 | 18.16
DHG060* | 5 | 1880 | 70 | 63 | 95 | 56.6 | 0.6 | 16.37
DHG060* | 5 | 1880 | 70 | 67 | 95 | 58.4 | 0.46 | 13.04
DHG060* | 5 | 1880 | 70 | 59 | 105 | 52.4 | 0.71 | 17.92
DHG060* | 5 | 1880 | 70 | 63 | 105 | 53.3 | 0.63 | 16.13
DHG060* | 5 | 1880 | 70 | 67 | 105 | 55.1 | 0.48 | 12.8
DHG060* | 5 | 1880 | 70 | 59 | 115 | 49.4 | 0.8 | 19.03
DHG060* | 5 | 1880 | 70 | 63 | 115 | 50.3 | 0.71 | 17.25
DHG060* | 5 | 1880 | 70 | 67 | 115 | 52.1 | 0.55 | 13.92
DHG060* | 5 | 2500 | 70 | 59 | 65 | 63.5 | 0.69 | 16.03
DHG060* | 5 | 2500 | 70 | 63 | 65 | 64.3 | 0.61 | 14.24
DHG060* | 5 | 2500 | 70 | 67 | 65 | 66.1 | 0.45 | 10.91
DHG060* | 5 | 2500 | 70 | 59 | 75 | 62.9 | 0.7 | 15.98
DHG060* | 5 | 2500 | 70 | 63 | 75 | 63.8 | 0.61 | 14.19
DHG060* | 5 | 2500 | 70 | 67 | 75 | 65.6 | 0.46 | 10.86
DHG060* | 5 | 2500 | 70 | 59 | 85 | 61.4 | 0.73 | 16.23
DHG060* | 5 | 2500 | 70 | 63 | 85 | 62.2 | 0.64 | 14.45
DHG060* | 5 | 2500 | 70 | 67 | 85 | 64 | 0.48 | 11.11
DHG060* | 5 | 2500 | 70 | 59 | 95 | 58.7 | 0.75 | 15.96
DHG060* | 5 | 2500 | 70 | 63 | 95 | 59.5 | 0.66 | 14.18
DHG060* | 5 | 2500 | 70 | 67 | 95 | 61.3 | 0.49 | 10.84
DHG060* | 5 | 2500 | 70 | 59 | 105 | 55.4 | 0.78 | 15.72
DHG060* | 5 | 2500 | 70 | 63 | 105 | 56.2 | 0.68 | 13.94
DHG060* | 5 | 2500 | 70 | 67 | 105 | 58 | 0.5 | 10.61
DHG060* | 5 | 2500 | 70 | 59 | 115 | 52.4 | 0.88 | 16.84
DHG060* | 5 | 2500 | 70 | 63 | 115 | 53.2 | 0.78 | 15.06
DHG060* | 5 | 2500 | 70 | 67 | 115 | 55 | 0.59 | 11.72
DHG060* | 5 | 1500 | 75 | 59 | 65 | 59.6 | 0.66 | 24.02
DHG060* | 5 | 1500 | 75 | 63 | 65 | 60.5 | 0.61 | 22.24
DHG060* | 5 | 1500 | 75 | 67 | 65 | 62.3 | 0.5 | 18.9
DHG060* | 5 | 1500 | 75 | 71 | 65 | 65 | 0.4 | 15.5
DHG060* | 5 | 1500 | 75 | 59 | 75 | 59.1 | 0.67 | 23.97
DHG060* | 5 | 1500 | 75 | 63 | 75 | 59.9 | 0.61 | 22.19
DHG060* | 5 | 1500 | 75 | 67 | 75 | 61.7 | 0.5 | 18.85
DHG060* | 5 | 1500 | 75 | 71 | 75 | 64.5 | 0.4 | 15.4
DHG060* | 5 | 1500 | 75 | 59 | 85 | 57.5 | 0.69 | 24.22
DHG060* | 5 | 1500 | 75 | 63 | 85 | 58.4 | 0.63 | 22.44
DHG060* | 5 | 1500 | 75 | 67 | 85 | 60.2 | 0.52 | 19.11
DHG060* | 5 | 1500 | 75 | 71 | 85 | 62.9 | 0.4 | 15.7
DHG060* | 5 | 1500 | 75 | 59 | 95 | 54.8 | 0.72 | 23.95
DHG060* | 5 | 1500 | 75 | 63 | 95 | 55.7 | 0.66 | 22.17
DHG060* | 5 | 1500 | 75 | 67 | 95 | 57.5 | 0.54 | 18.84
DHG060* | 5 | 1500 | 75 | 71 | 95 | 60.2 | 0.4 | 15.4
DHG060* | 5 | 1500 | 75 | 59 | 105 | 51.5 | 0.76 | 23.72
DHG060* | 5 | 1500 | 75 | 63 | 105 | 52.4 | 0.69 | 21.93
DHG060* | 5 | 1500 | 75 | 67 | 105 | 54.2 | 0.57 | 18.6
DHG060* | 5 | 1500 | 75 | 71 | 105 | 56.9 | 0.4 | 15.1
DHG060* | 5 | 1500 | 75 | 59 | 115 | 48.5 | 0.84 | 24.83
DHG060* | 5 | 1500 | 75 | 63 | 115 | 49.4 | 0.77 | 23.05
DHG060* | 5 | 1500 | 75 | 67 | 115 | 51.2 | 0.64 | 19.71
DHG060* | 5 | 1500 | 75 | 71 | 115 | 53.9 | 0.5 | 16.3
DHG060* | 5 | 1880 | 75 | 59 | 65 | 60.8 | 0.75 | 22.15
DHG060* | 5 | 1880 | 75 | 63 | 65 | 61.7 | 0.68 | 20.36
DHG060* | 5 | 1880 | 75 | 67 | 65 | 63.5 | 0.55 | 17.03
DHG060* | 5 | 1880 | 75 | 71 | 65 | 66.2 | 0.4 | 13.6
DHG060* | 5 | 1880 | 75 | 59 | 75 | 60.3 | 0.76 | 22.1
DHG060* | 5 | 1880 | 75 | 63 | 75 | 61.2 | 0.69 | 20.31
DHG060* | 5 | 1880 | 75 | 67 | 75 | 63 | 0.56 | 16.98
DHG060* | 5 | 1880 | 75 | 71 | 75 | 65.7 | 0.4 | 13.5
DHG060* | 5 | 1880 | 75 | 59 | 85 | 58.7 | 0.79 | 22.35
DHG060* | 5 | 1880 | 75 | 63 | 85 | 59.6 | 0.71 | 20.56
DHG060* | 5 | 1880 | 75 | 67 | 85 | 61.4 | 0.58 | 17.23
DHG060* | 5 | 1880 | 75 | 71 | 85 | 64.1 | 0.4 | 13.8
DHG060* | 5 | 1880 | 75 | 59 | 95 | 56 | 0.81 | 22.08
DHG060* | 5 | 1880 | 75 | 63 | 95 | 56.9 | 0.74 | 20.29
DHG060* | 5 | 1880 | 75 | 67 | 95 | 58.7 | 0.6 | 16.96
DHG060* | 5 | 1880 | 75 | 71 | 95 | 61.4 | 0.5 | 13.5
DHG060* | 5 | 1880 | 75 | 59 | 105 | 52.8 | 0.86 | 21.84
DHG060* | 5 | 1880 | 75 | 63 | 105 | 53.6 | 0.77 | 20.06
DHG060* | 5 | 1880 | 75 | 67 | 105 | 55.4 | 0.62 | 16.72
DHG060* | 5 | 1880 | 75 | 71 | 105 | 58.1 | 0.5 | 13.3
DHG060* | 5 | 1880 | 75 | 59 | 115 | 49.7 | 0.95 | 22.96
DHG060* | 5 | 1880 | 75 | 63 | 115 | 50.6 | 0.87 | 21.17
DHG060* | 5 | 1880 | 75 | 67 | 115 | 52.4 | 0.7 | 17.84
DHG060* | 5 | 1880 | 75 | 71 | 115 | 55.1 | 0.5 | 14.4
DHG060* | 5 | 2500 | 75 | 59 | 65 | 63.8 | 0.86 | 19.95
DHG060* | 5 | 2500 | 75 | 63 | 65 | 64.6 | 0.77 | 18.17
DHG060* | 5 | 2500 | 75 | 67 | 65 | 66.4 | 0.61 | 14.84
DHG060* | 5 | 2500 | 75 | 71 | 65 | 69.2 | 0.5 | 11.4
DHG060* | 5 | 2500 | 75 | 59 | 75 | 63.2 | 0.87 | 19.9
DHG060* | 5 | 2500 | 75 | 63 | 75 | 64.1 | 0.78 | 18.12
DHG060* | 5 | 2500 | 75 | 67 | 75 | 65.9 | 0.62 | 14.79
DHG060* | 5 | 2500 | 75 | 71 | 75 | 68.6 | 0.5 | 11.3
DHG060* | 5 | 2500 | 75 | 59 | 85 | 61.7 | 0.9 | 20.16
DHG060* | 5 | 2500 | 75 | 63 | 85 | 62.5 | 0.81 | 18.37
DHG060* | 5 | 2500 | 75 | 67 | 85 | 64.3 | 0.64 | 15.04
DHG060* | 5 | 2500 | 75 | 71 | 85 | 67 | 0.5 | 11.6
DHG060* | 5 | 2500 | 75 | 59 | 95 | 59 | 0.93 | 19.89
DHG060* | 5 | 2500 | 75 | 63 | 95 | 59.8 | 0.83 | 18.1
DHG060* | 5 | 2500 | 75 | 67 | 95 | 61.6 | 0.66 | 14.77
DHG060* | 5 | 2500 | 75 | 71 | 95 | 64.4 | 0.5 | 11.3
DHG060* | 5 | 2500 | 75 | 59 | 105 | 55.7 | 0.97 | 19.65
DHG060* | 5 | 2500 | 75 | 63 | 105 | 56.5 | 0.87 | 17.86
DHG060* | 5 | 2500 | 75 | 67 | 105 | 58.3 | 0.69 | 14.53
DHG060* | 5 | 2500 | 75 | 71 | 105 | 61.1 | 0.5 | 11.1
DHG060* | 5 | 2500 | 75 | 59 | 115 | 52.7 | 1 | 19.15
DHG060* | 5 | 2500 | 75 | 63 | 115 | 53.5 | 0.98 | 18.98
DHG060* | 5 | 2500 | 75 | 67 | 115 | 55.3 | 0.78 | 15.65
DHG060* | 5 | 2500 | 75 | 71 | 115 | 58 | 0.6 | 12.2
DHG060* | 5 | 1500 | 80 | 59 | 65 | 59.9 | 0.77 | 27.97
DHG060* | 5 | 1500 | 80 | 63 | 65 | 60.8 | 0.71 | 26.19
DHG060* | 5 | 1500 | 80 | 67 | 65 | 62.6 | 0.6 | 22.85
DHG060* | 5 | 1500 | 80 | 71 | 65 | 65.3 | 0.5 | 19.4
DHG060* | 5 | 1500 | 80 | 59 | 75 | 59.4 | 0.78 | 27.92
DHG060* | 5 | 1500 | 80 | 63 | 75 | 60.3 | 0.72 | 26.14
DHG060* | 5 | 1500 | 80 | 67 | 75 | 62.1 | 0.61 | 22.81
DHG060* | 5 | 1500 | 80 | 71 | 75 | 64.8 | 0.5 | 19.4
DHG060* | 5 | 1500 | 80 | 59 | 85 | 57.8 | 0.8 | 28.17
DHG060* | 5 | 1500 | 80 | 63 | 85 | 58.7 | 0.74 | 26.39
DHG060* | 5 | 1500 | 80 | 67 | 85 | 60.5 | 0.63 | 23.06
DHG060* | 5 | 1500 | 80 | 71 | 85 | 63.2 | 0.5 | 19.6
DHG060* | 5 | 1500 | 80 | 59 | 95 | 55.1 | 0.83 | 27.9
DHG060* | 5 | 1500 | 80 | 63 | 95 | 56 | 0.77 | 26.12
DHG060* | 5 | 1500 | 80 | 67 | 95 | 57.8 | 0.65 | 22.79
DHG060* | 5 | 1500 | 80 | 71 | 95 | 60.5 | 0.5 | 19.3
DHG060* | 5 | 1500 | 80 | 59 | 105 | 51.9 | 0.88 | 27.67
DHG060* | 5 | 1500 | 80 | 63 | 105 | 52.7 | 0.81 | 25.88
DHG060* | 5 | 1500 | 80 | 67 | 105 | 54.5 | 0.68 | 22.55
DHG060* | 5 | 1500 | 80 | 71 | 105 | 57.2 | 0.6 | 19.1
DHG060* | 5 | 1500 | 80 | 59 | 115 | 48.8 | 0.97 | 28.78
DHG060* | 5 | 1500 | 80 | 63 | 115 | 49.7 | 0.9 | 27
DHG060* | 5 | 1500 | 80 | 67 | 115 | 51.5 | 0.76 | 23.67
DHG060* | 5 | 1500 | 80 | 71 | 115 | 54.2 | 0.6 | 20.2
DHG060* | 5 | 1880 | 80 | 59 | 65 | 61.2 | 0.88 | 26.1
DHG060* | 5 | 1880 | 80 | 63 | 65 | 62 | 0.81 | 24.31
DHG060* | 5 | 1880 | 80 | 67 | 65 | 63.8 | 0.68 | 20.98
DHG060* | 5 | 1880 | 80 | 71 | 65 | 66.5 | 0.5 | 17.5
DHG060* | 5 | 1880 | 80 | 59 | 75 | 60.6 | 0.89 | 26.05
DHG060* | 5 | 1880 | 80 | 63 | 75 | 61.5 | 0.82 | 24.26
DHG060* | 5 | 1880 | 80 | 67 | 75 | 63.3 | 0.68 | 20.93
DHG060* | 5 | 1880 | 80 | 71 | 75 | 66 | 0.5 | 17.5
DHG060* | 5 | 1880 | 80 | 59 | 85 | 59.1 | 0.92 | 26.3
DHG060* | 5 | 1880 | 80 | 63 | 85 | 59.9 | 0.85 | 24.52
DHG060* | 5 | 1880 | 80 | 67 | 85 | 61.7 | 0.71 | 21.18
DHG060* | 5 | 1880 | 80 | 71 | 85 | 64.4 | 0.6 | 17.7
DHG060* | 5 | 1880 | 80 | 59 | 95 | 56.4 | 0.96 | 26.03
DHG060* | 5 | 1880 | 80 | 63 | 95 | 57.2 | 0.88 | 24.25
DHG060* | 5 | 1880 | 80 | 67 | 95 | 59 | 0.73 | 20.91
DHG060* | 5 | 1880 | 80 | 71 | 95 | 61.7 | 0.6 | 17.5
DHG060* | 5 | 1880 | 80 | 59 | 105 | 53.1 | 1 | 25.66
DHG060* | 5 | 1880 | 80 | 63 | 105 | 53.9 | 0.92 | 24.01
DHG060* | 5 | 1880 | 80 | 67 | 105 | 55.7 | 0.77 | 20.68
DHG060* | 5 | 1880 | 80 | 71 | 105 | 58.4 | 0.6 | 17.2
DHG060* | 5 | 1880 | 80 | 59 | 115 | 50.1 | 1 | 24.2
DHG060* | 5 | 1880 | 80 | 63 | 115 | 50.9 | 1 | 24.61
DHG060* | 5 | 1880 | 80 | 67 | 115 | 52.7 | 0.86 | 21.79
DHG060* | 5 | 1880 | 80 | 71 | 115 | 55.4 | 0.7 | 18.3
DHG060* | 5 | 2500 | 80 | 59 | 65 | 64.1 | 1 | 23.3
DHG060* | 5 | 2500 | 80 | 63 | 65 | 64.9 | 0.94 | 22.12
DHG060* | 5 | 2500 | 80 | 67 | 65 | 66.7 | 0.77 | 18.79
DHG060* | 5 | 2500 | 80 | 71 | 65 | 69.5 | 0.6 | 15.3
DHG060* | 5 | 2500 | 80 | 59 | 75 | 63.5 | 1 | 23.11
DHG060* | 5 | 2500 | 80 | 63 | 75 | 64.4 | 0.94 | 22.07
DHG060* | 5 | 2500 | 80 | 67 | 75 | 66.2 | 0.78 | 18.74
DHG060* | 5 | 2500 | 80 | 71 | 75 | 68.9 | 0.6 | 15.3
DHG060* | 5 | 2500 | 80 | 59 | 85 | 62 | 1 | 22.54
DHG060* | 5 | 2500 | 80 | 63 | 85 | 62.8 | 0.98 | 22.32
DHG060* | 5 | 2500 | 80 | 67 | 85 | 64.6 | 0.81 | 18.99
DHG060* | 5 | 2500 | 80 | 71 | 85 | 67.4 | 0.6 | 15.5
DHG060* | 5 | 2500 | 80 | 59 | 95 | 59.3 | 1 | 21.56
DHG060* | 5 | 2500 | 80 | 63 | 95 | 60.1 | 1 | 21.87
DHG060* | 5 | 2500 | 80 | 67 | 95 | 61.9 | 0.83 | 18.72
DHG060* | 5 | 2500 | 80 | 71 | 95 | 64.7 | 0.6 | 15.3
DHG060* | 5 | 2500 | 80 | 59 | 105 | 56 | 1 | 20.36
DHG060* | 5 | 2500 | 80 | 63 | 105 | 56.8 | 1 | 20.67
DHG060* | 5 | 2500 | 80 | 67 | 105 | 58.6 | 0.87 | 18.48
DHG060* | 5 | 2500 | 80 | 71 | 105 | 61.4 | 0.7 | 15
DHG060* | 5 | 2500 | 80 | 59 | 115 | 53 | 1 | 19.26
DHG060* | 5 | 2500 | 80 | 63 | 115 | 53.8 | 1 | 19.57
DHG060* | 5 | 2500 | 80 | 67 | 115 | 55.6 | 0.97 | 19.6
DHG060* | 5 | 2500 | 80 | 71 | 115 | 58.4 | 0.8 | 16.1
DHG060* | 5 | 1500 | 85 | 59 | 65 | 61 | 0.85 | 31.48
DHG060* | 5 | 1500 | 85 | 63 | 65 | 61.8 | 0.79 | 29.69
DHG060* | 5 | 1500 | 85 | 67 | 65 | 63.6 | 0.68 | 26.36
DHG060* | 5 | 1500 | 85 | 71 | 65 | 66.3 | 0.6 | 22.9
DHG060* | 5 | 1500 | 85 | 59 | 75 | 60.4 | 0.86 | 31.43
DHG060* | 5 | 1500 | 85 | 63 | 75 | 61.3 | 0.8 | 29.64
DHG060* | 5 | 1500 | 85 | 67 | 75 | 63.1 | 0.69 | 26.31
DHG060* | 5 | 1500 | 85 | 71 | 75 | 65.8 | 0.6 | 22.9
DHG060* | 5 | 1500 | 85 | 59 | 85 | 58.9 | 0.89 | 31.68
DHG060* | 5 | 1500 | 85 | 63 | 85 | 59.7 | 0.83 | 29.89
DHG060* | 5 | 1500 | 85 | 67 | 85 | 61.5 | 0.71 | 26.56
DHG060* | 5 | 1500 | 85 | 71 | 85 | 64.2 | 0.6 | 23.1
DHG060* | 5 | 1500 | 85 | 59 | 95 | 56.2 | 0.92 | 31.41
DHG060* | 5 | 1500 | 85 | 63 | 95 | 57 | 0.86 | 29.62
DHG060* | 5 | 1500 | 85 | 67 | 95 | 58.8 | 0.74 | 26.29
DHG060* | 5 | 1500 | 85 | 71 | 95 | 61.5 | 0.6 | 22.8
DHG060* | 5 | 1500 | 85 | 59 | 105 | 52.9 | 0.97 | 31.17
DHG060* | 5 | 1500 | 85 | 63 | 105 | 53.7 | 0.9 | 29.39
DHG060* | 5 | 1500 | 85 | 67 | 105 | 55.5 | 0.77 | 26.05
DHG060* | 5 | 1500 | 85 | 71 | 105 | 58.2 | 0.6 | 22.6
DHG060* | 5 | 1500 | 85 | 59 | 115 | 49.9 | 1 | 30.21
DHG060* | 5 | 1500 | 85 | 63 | 115 | 50.7 | 0.99 | 30.5
DHG060* | 5 | 1500 | 85 | 67 | 115 | 52.5 | 0.85 | 27.17
DHG060* | 5 | 1500 | 85 | 71 | 115 | 55.2 | 0.7 | 23.7
DHG060* | 5 | 1880 | 85 | 59 | 65 | 62.2 | 0.98 | 29.6
DHG060* | 5 | 1880 | 85 | 63 | 65 | 63 | 0.91 | 27.82
DHG060* | 5 | 1880 | 85 | 67 | 65 | 64.8 | 0.78 | 24.49
DHG060* | 5 | 1880 | 85 | 71 | 65 | 67.6 | 0.6 | 21
DHG060* | 5 | 1880 | 85 | 59 | 75 | 61.6 | 0.99 | 29.55
DHG060* | 5 | 1880 | 85 | 63 | 75 | 62.5 | 0.92 | 27.77
DHG060* | 5 | 1880 | 85 | 67 | 75 | 64.3 | 0.79 | 24.44
DHG060* | 5 | 1880 | 85 | 71 | 75 | 67 | 0.6 | 21
DHG060* | 5 | 1880 | 85 | 59 | 85 | 60.1 | 1 | 29.05
DHG060* | 5 | 1880 | 85 | 63 | 85 | 60.9 | 0.95 | 28.02
DHG060* | 5 | 1880 | 85 | 67 | 85 | 62.7 | 0.81 | 24.69
DHG060* | 5 | 1880 | 85 | 71 | 85 | 65.4 | 0.7 | 21.2
DHG060* | 5 | 1880 | 85 | 59 | 95 | 57.4 | 1 | 27.74
DHG060* | 5 | 1880 | 85 | 63 | 95 | 58.2 | 0.99 | 27.75
DHG060* | 5 | 1880 | 85 | 67 | 95 | 60 | 0.84 | 24.42
DHG060* | 5 | 1880 | 85 | 71 | 95 | 62.8 | 0.7 | 21
DHG060* | 5 | 1880 | 85 | 59 | 105 | 54.1 | 1 | 26.15
DHG060* | 5 | 1880 | 85 | 63 | 105 | 54.9 | 1 | 26.56
DHG060* | 5 | 1880 | 85 | 67 | 105 | 56.7 | 0.88 | 24.18
DHG060* | 5 | 1880 | 85 | 71 | 105 | 59.5 | 0.7 | 20.7
DHG060* | 5 | 1880 | 85 | 59 | 115 | 51.1 | 1 | 24.69
DHG060* | 5 | 1880 | 85 | 63 | 115 | 51.9 | 1 | 25.1
DHG060* | 5 | 1880 | 85 | 67 | 115 | 53.7 | 0.97 | 25.3
DHG060* | 5 | 1880 | 85 | 71 | 115 | 56.4 | 0.8 | 21.8
DHG060* | 5 | 2500 | 85 | 59 | 65 | 65.1 | 1 | 23.67
DHG060* | 5 | 2500 | 85 | 63 | 65 | 65.9 | 1 | 23.98
DHG060* | 5 | 2500 | 85 | 67 | 65 | 67.7 | 0.9 | 22.29
DHG060* | 5 | 2500 | 85 | 71 | 65 | 70.5 | 0.7 | 18.8
DHG060* | 5 | 2500 | 85 | 59 | 75 | 64.6 | 1 | 23.48
DHG060* | 5 | 2500 | 85 | 63 | 75 | 65.4 | 1 | 23.78
DHG060* | 5 | 2500 | 85 | 67 | 75 | 67.2 | 0.91 | 22.24
DHG060* | 5 | 2500 | 85 | 71 | 75 | 69.9 | 0.7 | 18.8
DHG060* | 5 | 2500 | 85 | 59 | 85 | 63 | 1 | 22.91
DHG060* | 5 | 2500 | 85 | 63 | 85 | 63.8 | 1 | 23.21
DHG060* | 5 | 2500 | 85 | 67 | 85 | 65.6 | 0.94 | 22.49
DHG060* | 5 | 2500 | 85 | 71 | 85 | 68.4 | 0.8 | 19
DHG060* | 5 | 2500 | 85 | 59 | 95 | 60.3 | 1 | 21.93
DHG060* | 5 | 2500 | 85 | 63 | 95 | 61.1 | 1 | 22.23
DHG060* | 5 | 2500 | 85 | 67 | 95 | 62.9 | 0.97 | 22.22
DHG060* | 5 | 2500 | 85 | 71 | 95 | 65.7 | 0.8 | 18.8
DHG060* | 5 | 2500 | 85 | 59 | 105 | 57 | 1 | 20.73
DHG060* | 5 | 2500 | 85 | 63 | 105 | 57.8 | 1 | 21.03
DHG060* | 5 | 2500 | 85 | 67 | 105 | 59.6 | 1 | 21.69
DHG060* | 5 | 2500 | 85 | 71 | 105 | 62.4 | 0.8 | 18.5
DHG060* | 5 | 2500 | 85 | 59 | 115 | 54 | 1 | 19.63
DHG060* | 5 | 2500 | 85 | 63 | 115 | 54.8 | 1 | 19.94
DHG060* | 5 | 2500 | 85 | 67 | 115 | 56.6 | 1 | 20.59
DHG060* | 5 | 2500 | 85 | 71 | 115 | 59.4 | 0.9 | 19.7
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 59 | 65 | 42.8 | 0.51 | 18.89
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 63 | 65 | 43.5 | 0.46 | 17.17
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 67 | 65 | 44.7 | 0.36 | 13.95
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 59 | 75 | 42.5 | 0.51 | 18.85
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 63 | 75 | 43.1 | 0.46 | 17.12
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 67 | 75 | 44.4 | 0.36 | 13.91
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 59 | 85 | 41.3 | 0.53 | 19.09
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 63 | 85 | 41.9 | 0.48 | 17.37
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 67 | 85 | 43.2 | 0.38 | 14.15
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 59 | 95 | 39.4 | 0.55 | 18.83
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 63 | 95 | 40 | 0.49 | 17.11
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 67 | 95 | 41.3 | 0.39 | 13.89
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 59 | 105 | 37 | 0.58 | 18.6
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 63 | 105 | 37.6 | 0.52 | 16.88
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 67 | 105 | 38.9 | 0.41 | 13.66
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 59 | 115 | 34.9 | 0.65 | 19.68
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 63 | 115 | 35.5 | 0.58 | 17.95
DHG060* (70% - Low Stage) | 5 | 1050 | 70 | 67 | 115 | 36.8 | 0.46 | 14.74
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 59 | 65 | 43.5 | 0.55 | 17.58
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 63 | 65 | 44.1 | 0.49 | 15.86
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 67 | 65 | 45.4 | 0.38 | 12.65
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 59 | 75 | 43.1 | 0.55 | 17.54
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 63 | 75 | 43.8 | 0.49 | 15.82
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 67 | 75 | 45 | 0.38 | 12.6
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 59 | 85 | 42 | 0.58 | 17.78
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 63 | 85 | 42.6 | 0.51 | 16.06
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 67 | 85 | 43.9 | 0.4 | 12.84
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 59 | 95 | 40.1 | 0.6 | 17.52
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 63 | 95 | 40.7 | 0.53 | 15.8
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 67 | 95 | 42 | 0.41 | 12.58
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 59 | 105 | 37.7 | 0.63 | 17.29
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 63 | 105 | 38.3 | 0.55 | 15.57
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 67 | 105 | 39.6 | 0.43 | 12.35
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 59 | 115 | 35.5 | 0.7 | 18.37
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 63 | 115 | 36.2 | 0.63 | 16.65
DHG060* (70% - Low Stage) | 5 | 1240 | 70 | 67 | 115 | 37.4 | 0.49 | 13.43
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 59 | 65 | 46.3 | 0.62 | 15.01
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 63 | 65 | 46.9 | 0.54 | 13.29
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 67 | 65 | 48.2 | 0.4 | 10.07
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 59 | 75 | 45.9 | 0.63 | 14.96
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 63 | 75 | 46.5 | 0.55 | 13.24
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 67 | 75 | 47.8 | 0.4 | 10.02
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 59 | 85 | 44.8 | 0.65 | 15.2
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 63 | 85 | 45.4 | 0.57 | 13.48
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 67 | 85 | 46.7 | 0.42 | 10.26
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 59 | 95 | 42.9 | 0.67 | 14.94
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 63 | 95 | 43.5 | 0.59 | 13.22
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 67 | 95 | 44.8 | 0.43 | 10
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 59 | 105 | 40.5 | 0.7 | 14.71
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 63 | 105 | 41.1 | 0.61 | 12.99
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 67 | 105 | 42.4 | 0.44 | 9.77
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 59 | 115 | 38.3 | 0.79 | 15.79
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 63 | 115 | 38.9 | 0.7 | 14.07
DHG060* (70% - Low Stage) | 5 | 1750 | 70 | 67 | 115 | 40.2 | 0.52 | 10.85
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 59 | 65 | 43.1 | 0.61 | 22.68
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 63 | 65 | 43.7 | 0.55 | 20.96
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 67 | 65 | 45 | 0.46 | 17.74
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 71 | 65 | 46.9 | 0.4 | 14.4
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 59 | 75 | 42.7 | 0.61 | 22.63
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 63 | 75 | 43.3 | 0.56 | 20.91
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 67 | 75 | 44.6 | 0.46 | 17.69
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 71 | 75 | 46.6 | 0.4 | 14.4
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 59 | 85 | 41.6 | 0.64 | 22.87
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 63 | 85 | 42.2 | 0.58 | 21.15
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 67 | 85 | 43.5 | 0.48 | 17.94
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 71 | 85 | 45.4 | 0.4 | 14.6
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 59 | 95 | 39.6 | 0.66 | 22.62
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 63 | 95 | 40.2 | 0.6 | 20.89
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 67 | 95 | 41.5 | 0.49 | 17.68
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 71 | 95 | 43.5 | 0.4 | 14.3
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 59 | 105 | 37.2 | 0.69 | 22.39
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 63 | 105 | 37.9 | 0.63 | 20.66
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 67 | 105 | 39.1 | 0.51 | 17.45
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 71 | 105 | 41.1 | 0.4 | 14.1
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 59 | 115 | 35.1 | 0.77 | 23.46
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 63 | 115 | 35.7 | 0.7 | 21.74
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 67 | 115 | 37 | 0.58 | 18.52
DHG060* (70% - Low Stage) | 5 | 1050 | 75 | 71 | 115 | 39 | 0.5 | 15.2
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 59 | 65 | 43.8 | 0.67 | 21.37
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 63 | 65 | 44.4 | 0.6 | 19.65
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 67 | 65 | 45.6 | 0.49 | 16.43
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 71 | 65 | 47.6 | 0.4 | 13.1
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 59 | 75 | 43.4 | 0.67 | 21.32
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 63 | 75 | 44 | 0.61 | 19.6
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 67 | 75 | 45.3 | 0.49 | 16.39
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 71 | 75 | 47.2 | 0.4 | 13.1
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 59 | 85 | 42.2 | 0.7 | 21.57
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 63 | 85 | 42.8 | 0.63 | 19.84
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 67 | 85 | 44.1 | 0.51 | 16.63
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 71 | 85 | 46.1 | 0.4 | 13.3
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 59 | 95 | 40.3 | 0.72 | 21.31
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 63 | 95 | 40.9 | 0.65 | 19.58
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 67 | 95 | 42.2 | 0.53 | 16.37
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 71 | 95 | 44.2 | 0.4 | 13
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 59 | 105 | 37.9 | 0.76 | 21.08
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 63 | 105 | 38.5 | 0.69 | 19.35
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 67 | 105 | 39.8 | 0.55 | 16.14
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 71 | 105 | 41.8 | 0.4 | 12.8
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 59 | 115 | 35.8 | 0.84 | 22.16
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 63 | 115 | 36.4 | 0.77 | 20.43
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 67 | 115 | 37.7 | 0.62 | 17.22
DHG060* (70% - Low Stage) | 5 | 1240 | 75 | 71 | 115 | 39.6 | 0.5 | 13.9
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 59 | 65 | 46.5 | 0.78 | 18.79
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 63 | 65 | 47.2 | 0.7 | 17.07
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 67 | 65 | 48.4 | 0.55 | 13.86
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 71 | 65 | 50.4 | 0.4 | 10.5
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 59 | 75 | 46.2 | 0.78 | 18.75
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 63 | 75 | 46.8 | 0.7 | 17.03
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 67 | 75 | 48.1 | 0.55 | 13.81
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 71 | 75 | 50 | 0.4 | 10.5
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 59 | 85 | 45 | 0.81 | 18.99
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 63 | 85 | 45.6 | 0.73 | 17.27
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 67 | 85 | 46.9 | 0.58 | 14.05
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 71 | 85 | 48.9 | 0.4 | 10.7
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 59 | 95 | 43.1 | 0.84 | 18.73
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 63 | 95 | 43.7 | 0.75 | 17.01
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 67 | 95 | 45 | 0.59 | 13.79
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 71 | 95 | 47 | 0.4 | 10.5
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 59 | 105 | 40.7 | 0.87 | 18.5
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 63 | 105 | 41.3 | 0.78 | 16.78
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 67 | 105 | 42.6 | 0.61 | 13.56
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 71 | 105 | 44.6 | 0.4 | 10.2
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 59 | 115 | 38.6 | 0.98 | 19.58
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 63 | 115 | 39.2 | 0.88 | 17.86
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 67 | 115 | 40.5 | 0.7 | 14.64
DHG060* (70% - Low Stage) | 5 | 1750 | 75 | 71 | 115 | 42.4 | 0.5 | 11.3
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 59 | 65 | 43.3 | 0.71 | 26.49
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 63 | 65 | 43.9 | 0.65 | 24.77
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 67 | 65 | 45.2 | 0.55 | 21.55
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 71 | 65 | 47.2 | 0.4 | 18.2
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 59 | 75 | 42.9 | 0.71 | 26.45
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 63 | 75 | 43.5 | 0.66 | 24.72
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 67 | 75 | 44.8 | 0.55 | 21.51
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 71 | 75 | 46.8 | 0.4 | 18.2
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 59 | 85 | 41.8 | 0.74 | 26.69
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 63 | 85 | 42.4 | 0.68 | 24.97
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 67 | 85 | 43.7 | 0.58 | 21.75
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 71 | 85 | 45.6 | 0.5 | 18.4
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 59 | 95 | 39.8 | 0.77 | 26.43
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 63 | 95 | 40.4 | 0.71 | 24.71
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 67 | 95 | 41.7 | 0.59 | 21.49
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 71 | 95 | 43.7 | 0.5 | 18.2
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 59 | 105 | 37.5 | 0.81 | 26.2
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 63 | 105 | 38.1 | 0.74 | 24.48
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 67 | 105 | 39.4 | 0.62 | 21.26
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 71 | 105 | 41.3 | 0.5 | 17.9
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 59 | 115 | 35.3 | 0.89 | 27.28
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 63 | 115 | 35.9 | 0.82 | 25.55
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 67 | 115 | 37.2 | 0.69 | 22.34
DHG060* (70% - Low Stage) | 5 | 1050 | 80 | 71 | 115 | 39.2 | 0.6 | 19
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 59 | 65 | 44 | 0.78 | 25.18
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 63 | 65 | 44.6 | 0.72 | 23.46
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 67 | 65 | 45.9 | 0.6 | 20.25
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 71 | 65 | 47.8 | 0.5 | 16.9
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 59 | 75 | 43.6 | 0.79 | 25.14
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 63 | 75 | 44.2 | 0.72 | 23.42
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 67 | 75 | 45.5 | 0.61 | 20.2
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 71 | 75 | 47.5 | 0.5 | 16.9
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 59 | 85 | 42.5 | 0.82 | 25.38
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 63 | 85 | 43.1 | 0.75 | 23.66
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 67 | 85 | 44.4 | 0.63 | 20.44
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 71 | 85 | 46.3 | 0.5 | 17.1
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 59 | 95 | 40.5 | 0.85 | 25.12
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 63 | 95 | 41.1 | 0.78 | 23.4
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 67 | 95 | 42.4 | 0.65 | 20.18
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 71 | 95 | 44.4 | 0.5 | 16.8
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 59 | 105 | 38.2 | 0.89 | 24.89
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 63 | 105 | 38.8 | 0.82 | 23.17
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 67 | 105 | 40.1 | 0.68 | 19.95
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 71 | 105 | 42 | 0.5 | 16.6
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 59 | 115 | 36 | 0.98 | 25.97
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 63 | 115 | 36.6 | 0.9 | 24.25
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 67 | 115 | 37.9 | 0.76 | 21.03
DHG060* (70% - Low Stage) | 5 | 1240 | 80 | 71 | 115 | 39.9 | 0.6 | 17.7
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 59 | 65 | 46.8 | 0.93 | 22.61
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 63 | 65 | 47.4 | 0.85 | 20.89
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 67 | 65 | 48.7 | 0.7 | 17.67
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 71 | 65 | 50.6 | 0.5 | 14.3
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 59 | 75 | 46.4 | 0.94 | 22.56
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 63 | 75 | 47 | 0.85 | 20.84
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 67 | 75 | 48.3 | 0.7 | 17.62
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 71 | 75 | 50.2 | 0.5 | 14.3
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 59 | 85 | 45.3 | 0.97 | 22.8
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 63 | 85 | 45.9 | 0.88 | 21.08
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 67 | 85 | 47.1 | 0.73 | 17.86
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 71 | 85 | 49.1 | 0.6 | 14.5
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 59 | 95 | 43.3 | 1 | 22.5
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 63 | 95 | 43.9 | 0.91 | 20.82
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 67 | 95 | 45.2 | 0.75 | 17.6
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 71 | 95 | 47.2 | 0.6 | 14.3
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 59 | 105 | 40.9 | 1 | 21.27
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 63 | 105 | 41.6 | 0.95 | 20.59
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 67 | 105 | 42.8 | 0.78 | 17.37
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 71 | 105 | 44.8 | 0.6 | 14
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 59 | 115 | 38.8 | 1 | 20.15
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 63 | 115 | 39.4 | 1 | 20.46
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 67 | 115 | 40.7 | 0.87 | 18.45
DHG060* (70% - Low Stage) | 5 | 1750 | 80 | 71 | 115 | 42.6 | 0.7 | 15.1
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 59 | 65 | 44 | 0.78 | 29.87
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 63 | 65 | 44.6 | 0.73 | 28.15
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 67 | 65 | 45.9 | 0.63 | 24.94
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 71 | 65 | 47.9 | 0.5 | 21.6
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 59 | 75 | 43.6 | 0.79 | 29.83
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 63 | 75 | 44.2 | 0.73 | 28.11
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 67 | 75 | 45.5 | 0.63 | 24.89
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 71 | 75 | 47.5 | 0.5 | 21.6
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 59 | 85 | 42.5 | 0.82 | 30.07
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 63 | 85 | 43.1 | 0.76 | 28.35
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 67 | 85 | 44.4 | 0.65 | 25.13
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 71 | 85 | 46.4 | 0.5 | 21.8
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 59 | 95 | 40.6 | 0.85 | 29.81
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 63 | 95 | 41.2 | 0.79 | 28.09
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 67 | 95 | 42.5 | 0.68 | 24.87
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 71 | 95 | 44.4 | 0.6 | 21.5
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 59 | 105 | 38.2 | 0.89 | 29.58
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 63 | 105 | 38.8 | 0.83 | 27.86
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 67 | 105 | 40.1 | 0.71 | 24.64
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 71 | 105 | 42.1 | 0.6 | 21.3
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 59 | 115 | 36 | 0.98 | 30.66
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 63 | 115 | 36.6 | 0.91 | 28.94
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 67 | 115 | 37.9 | 0.78 | 25.72
DHG060* (70% - Low Stage) | 5 | 1050 | 85 | 71 | 115 | 39.9 | 0.6 | 22.4
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 59 | 65 | 44.7 | 0.87 | 28.57
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 63 | 65 | 45.3 | 0.81 | 26.84
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 67 | 65 | 46.6 | 0.69 | 23.63
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 71 | 65 | 48.6 | 0.6 | 20.3
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 59 | 75 | 44.3 | 0.88 | 28.52
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 63 | 75 | 44.9 | 0.81 | 26.8
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 67 | 75 | 46.2 | 0.7 | 23.58
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 71 | 75 | 48.2 | 0.6 | 20.2
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 59 | 85 | 43.2 | 0.91 | 28.76
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 63 | 85 | 43.8 | 0.84 | 27.04
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 67 | 85 | 45.1 | 0.72 | 23.82
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 71 | 85 | 47.1 | 0.6 | 20.5
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 59 | 95 | 41.2 | 0.94 | 28.5
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 63 | 95 | 41.9 | 0.87 | 26.78
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 67 | 95 | 43.1 | 0.74 | 23.56
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 71 | 95 | 45.1 | 0.6 | 20.2
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 59 | 105 | 38.9 | 0.99 | 28.27
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 63 | 105 | 39.5 | 0.92 | 26.55
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 67 | 105 | 40.8 | 0.78 | 23.33
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 71 | 105 | 42.7 | 0.6 | 20
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 59 | 115 | 36.7 | 1 | 26.92
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 63 | 115 | 37.3 | 1 | 27.36
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 67 | 115 | 38.6 | 0.86 | 24.41
DHG060* (70% - Low Stage) | 5 | 1240 | 85 | 71 | 115 | 40.6 | 0.7 | 21.1
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 59 | 65 | 47.5 | 1 | 24.67
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 63 | 65 | 48.1 | 0.97 | 24.27
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 67 | 65 | 49.4 | 0.82 | 21.05
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 71 | 65 | 51.4 | 0.7 | 17.7
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 59 | 75 | 47.1 | 1 | 24.47
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 63 | 75 | 47.7 | 0.98 | 24.22
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 67 | 75 | 49 | 0.83 | 21
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 71 | 75 | 51 | 0.7 | 17.7
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 59 | 85 | 46 | 1 | 23.88
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 63 | 85 | 46.6 | 1 | 24.2
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 67 | 85 | 47.9 | 0.85 | 21.25
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 71 | 85 | 49.8 | 0.7 | 17.9
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 59 | 95 | 44 | 1 | 22.88
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 63 | 95 | 44.6 | 1 | 23.19
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 67 | 95 | 45.9 | 0.88 | 20.99
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 71 | 95 | 47.9 | 0.7 | 17.7
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 59 | 105 | 41.7 | 1 | 21.65
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 63 | 105 | 42.3 | 1 | 21.96
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 67 | 105 | 43.6 | 0.92 | 20.76
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 71 | 105 | 45.5 | 0.7 | 17.4
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 59 | 115 | 39.5 | 1 | 20.52
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 63 | 115 | 40.1 | 1 | 20.84
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 67 | 115 | 41.4 | 1 | 21.51
DHG060* (70% - Low Stage) | 5 | 1750 | 85 | 71 | 115 | 43.4 | 0.8 | 18.5
DHG072* | 6 | 1800 | 70 | 59 | 65 | 69.6 | 0.58 | 20.47
DHG072* | 6 | 1800 | 70 | 63 | 65 | 70.6 | 0.52 | 18.61
DHG072* | 6 | 1800 | 70 | 67 | 65 | 72.7 | 0.41 | 15.14
DHG072* | 6 | 1800 | 70 | 59 | 75 | 69 | 0.59 | 20.42
DHG072* | 6 | 1800 | 70 | 63 | 75 | 70 | 0.53 | 18.56
DHG072* | 6 | 1800 | 70 | 67 | 75 | 72.1 | 0.41 | 15.09
DHG072* | 6 | 1800 | 70 | 59 | 85 | 67.2 | 0.61 | 20.68
DHG072* | 6 | 1800 | 70 | 63 | 85 | 68.2 | 0.55 | 18.82
DHG072* | 6 | 1800 | 70 | 67 | 85 | 70.3 | 0.43 | 15.36
DHG072* | 6 | 1800 | 70 | 59 | 95 | 64 | 0.63 | 20.4
DHG072* | 6 | 1800 | 70 | 63 | 95 | 65 | 0.56 | 18.54
DHG072* | 6 | 1800 | 70 | 67 | 95 | 67.1 | 0.44 | 15.08
DHG072* | 6 | 1800 | 70 | 59 | 105 | 60.2 | 0.66 | 20.15
DHG072* | 6 | 1800 | 70 | 63 | 105 | 61.2 | 0.59 | 18.29
DHG072* | 6 | 1800 | 70 | 67 | 105 | 63.2 | 0.46 | 14.83
DHG072* | 6 | 1800 | 70 | 59 | 115 | 56.6 | 0.75 | 21.31
DHG072* | 6 | 1800 | 70 | 63 | 115 | 57.6 | 0.67 | 19.46
DHG072* | 6 | 1800 | 70 | 67 | 115 | 59.7 | 0.53 | 15.99
DHG072* | 6 | 2150 | 70 | 59 | 65 | 70.8 | 0.63 | 18.96
DHG072* | 6 | 2150 | 70 | 63 | 65 | 71.8 | 0.56 | 17.1
DHG072* | 6 | 2150 | 70 | 67 | 65 | 73.9 | 0.44 | 13.63
DHG072* | 6 | 2150 | 70 | 59 | 75 | 70.2 | 0.64 | 18.91
DHG072* | 6 | 2150 | 70 | 63 | 75 | 71.2 | 0.57 | 17.05
DHG072* | 6 | 2150 | 70 | 67 | 75 | 73.3 | 0.44 | 13.58
DHG072* | 6 | 2150 | 70 | 59 | 85 | 68.3 | 0.66 | 19.17
DHG072* | 6 | 2150 | 70 | 63 | 85 | 69.3 | 0.59 | 17.31
DHG072* | 6 | 2150 | 70 | 67 | 85 | 71.4 | 0.46 | 13.84
DHG072* | 6 | 2150 | 70 | 59 | 95 | 65.2 | 0.69 | 18.89
DHG072* | 6 | 2150 | 70 | 63 | 95 | 66.2 | 0.61 | 17.03
DHG072* | 6 | 2150 | 70 | 67 | 95 | 68.3 | 0.47 | 13.56
DHG072* | 6 | 2150 | 70 | 59 | 105 | 61.3 | 0.72 | 18.64
DHG072* | 6 | 2150 | 70 | 63 | 105 | 62.3 | 0.64 | 16.78
DHG072* | 6 | 2150 | 70 | 67 | 105 | 64.4 | 0.49 | 13.32
DHG072* | 6 | 2150 | 70 | 59 | 115 | 57.8 | 0.81 | 19.8
DHG072* | 6 | 2150 | 70 | 63 | 115 | 58.8 | 0.72 | 17.95
DHG072* | 6 | 2150 | 70 | 67 | 115 | 60.9 | 0.56 | 14.48
DHG072* | 6 | 3000 | 70 | 59 | 65 | 75.1 | 0.72 | 16.28
DHG072* | 6 | 3000 | 70 | 63 | 65 | 76.1 | 0.63 | 14.42
DHG072* | 6 | 3000 | 70 | 67 | 65 | 78.2 | 0.46 | 10.95
DHG072* | 6 | 3000 | 70 | 59 | 75 | 74.5 | 0.72 | 16.22
DHG072* | 6 | 3000 | 70 | 63 | 75 | 75.5 | 0.63 | 14.37
DHG072* | 6 | 3000 | 70 | 67 | 75 | 77.6 | 0.46 | 10.9
DHG072* | 6 | 3000 | 70 | 59 | 85 | 72.6 | 0.75 | 16.49
DHG072* | 6 | 3000 | 70 | 63 | 85 | 73.6 | 0.66 | 14.63
DHG072* | 6 | 3000 | 70 | 67 | 85 | 75.7 | 0.49 | 11.16
DHG072* | 6 | 3000 | 70 | 59 | 95 | 69.5 | 0.77 | 16.21
DHG072* | 6 | 3000 | 70 | 63 | 95 | 70.5 | 0.67 | 14.35
DHG072* | 6 | 3000 | 70 | 67 | 95 | 72.6 | 0.49 | 10.88
DHG072* | 6 | 3000 | 70 | 59 | 105 | 65.6 | 0.8 | 15.96
DHG072* | 6 | 3000 | 70 | 63 | 105 | 66.6 | 0.7 | 14.1
DHG072* | 6 | 3000 | 70 | 67 | 105 | 68.7 | 0.51 | 10.63
DHG072* | 6 | 3000 | 70 | 59 | 115 | 62.1 | 0.91 | 17.12
DHG072* | 6 | 3000 | 70 | 63 | 115 | 63.1 | 0.8 | 15.26
DHG072* | 6 | 3000 | 70 | 67 | 115 | 65.2 | 0.6 | 11.8
DHG072* | 6 | 1800 | 75 | 59 | 65 | 70 | 0.69 | 24.55
DHG072* | 6 | 1800 | 75 | 63 | 65 | 71 | 0.63 | 22.69
DHG072* | 6 | 1800 | 75 | 67 | 65 | 73.1 | 0.52 | 19.23
DHG072* | 6 | 1800 | 75 | 71 | 65 | 76.3 | 0.4 | 15.6
DHG072* | 6 | 1800 | 75 | 59 | 75 | 69.4 | 0.7 | 24.5
DHG072* | 6 | 1800 | 75 | 63 | 75 | 70.4 | 0.64 | 22.64
DHG072* | 6 | 1800 | 75 | 67 | 75 | 72.5 | 0.52 | 19.18
DHG072* | 6 | 1800 | 75 | 71 | 75 | 75.7 | 0.4 | 15.6
DHG072* | 6 | 1800 | 75 | 59 | 85 | 67.5 | 0.73 | 24.76
DHG072* | 6 | 1800 | 75 | 63 | 85 | 68.5 | 0.66 | 22.91
DHG072* | 6 | 1800 | 75 | 67 | 85 | 70.6 | 0.54 | 19.44
DHG072* | 6 | 1800 | 75 | 71 | 85 | 73.8 | 0.4 | 15.8
DHG072* | 6 | 1800 | 75 | 59 | 95 | 64.4 | 0.75 | 24.48
DHG072* | 6 | 1800 | 75 | 63 | 95 | 65.4 | 0.69 | 22.63
DHG072* | 6 | 1800 | 75 | 67 | 95 | 67.5 | 0.56 | 19.16
DHG072* | 6 | 1800 | 75 | 71 | 95 | 70.7 | 0.4 | 15.6
DHG072* | 6 | 1800 | 75 | 59 | 105 | 60.5 | 0.79 | 24.23
DHG072* | 6 | 1800 | 75 | 63 | 105 | 61.5 | 0.72 | 22.38
DHG072* | 6 | 1800 | 75 | 67 | 105 | 63.6 | 0.59 | 18.91
DHG072* | 6 | 1800 | 75 | 71 | 105 | 66.8 | 0.5 | 15.3
DHG072* | 6 | 1800 | 75 | 59 | 115 | 57 | 0.88 | 25.4
DHG072* | 6 | 1800 | 75 | 63 | 115 | 58 | 0.8 | 23.54
DHG072* | 6 | 1800 | 75 | 67 | 115 | 60.1 | 0.66 | 20.07
DHG072* | 6 | 1800 | 75 | 71 | 115 | 63.3 | 0.5 | 16.5
DHG072* | 6 | 2150 | 75 | 59 | 65 | 71.2 | 0.77 | 23.04
DHG072* | 6 | 2150 | 75 | 63 | 65 | 72.2 | 0.69 | 21.18
DHG072* | 6 | 2150 | 75 | 67 | 65 | 74.3 | 0.56 | 17.72
DHG072* | 6 | 2150 | 75 | 71 | 65 | 77.5 | 0.4 | 14.1
DHG072* | 6 | 2150 | 75 | 59 | 75 | 70.5 | 0.77 | 22.99
DHG072* | 6 | 2150 | 75 | 63 | 75 | 71.5 | 0.7 | 21.13
DHG072* | 6 | 2150 | 75 | 67 | 75 | 73.6 | 0.57 | 17.67
DHG072* | 6 | 2150 | 75 | 71 | 75 | 76.8 | 0.4 | 14.1
DHG072* | 6 | 2150 | 75 | 59 | 85 | 68.7 | 0.8 | 23.25
DHG072* | 6 | 2150 | 75 | 63 | 85 | 69.7 | 0.73 | 21.39
DHG072* | 6 | 2150 | 75 | 67 | 85 | 71.8 | 0.59 | 17.93
DHG072* | 6 | 2150 | 75 | 71 | 85 | 75 | 0.5 | 14.3
DHG072* | 6 | 2150 | 75 | 59 | 95 | 65.5 | 0.83 | 22.97
DHG072* | 6 | 2150 | 75 | 63 | 95 | 66.5 | 0.75 | 21.11
DHG072* | 6 | 2150 | 75 | 67 | 95 | 68.6 | 0.61 | 17.65
DHG072* | 6 | 2150 | 75 | 71 | 95 | 71.8 | 0.5 | 14.1
DHG072* | 6 | 2150 | 75 | 59 | 105 | 61.7 | 0.87 | 22.72
DHG072* | 6 | 2150 | 75 | 63 | 105 | 62.7 | 0.79 | 20.87
DHG072* | 6 | 2150 | 75 | 67 | 105 | 64.8 | 0.64 | 17.4
DHG072* | 6 | 2150 | 75 | 71 | 105 | 68 | 0.5 | 13.8
DHG072* | 6 | 2150 | 75 | 59 | 115 | 58.2 | 0.97 | 23.89
DHG072* | 6 | 2150 | 75 | 63 | 115 | 59.2 | 0.88 | 22.03
DHG072* | 6 | 2150 | 75 | 67 | 115 | 61.3 | 0.72 | 18.56
DHG072* | 6 | 2150 | 75 | 71 | 115 | 64.5 | 0.5 | 15
DHG072* | 6 | 3000 | 75 | 59 | 65 | 75.5 | 0.89 | 20.36
DHG072* | 6 | 3000 | 75 | 63 | 65 | 76.5 | 0.8 | 18.5
DHG072* | 6 | 3000 | 75 | 67 | 65 | 78.6 | 0.63 | 15.03
DHG072* | 6 | 3000 | 75 | 71 | 65 | 81.8 | 0.5 | 11.4
DHG072* | 6 | 3000 | 75 | 59 | 75 | 74.8 | 0.9 | 20.31
DHG072* | 6 | 3000 | 75 | 63 | 75 | 75.8 | 0.8 | 18.45
DHG072* | 6 | 3000 | 75 | 67 | 75 | 77.9 | 0.63 | 14.98
DHG072* | 6 | 3000 | 75 | 71 | 75 | 81.1 | 0.5 | 11.4
DHG072* | 6 | 3000 | 75 | 59 | 85 | 73 | 0.93 | 20.57
DHG072* | 6 | 3000 | 75 | 63 | 85 | 74 | 0.83 | 18.71
DHG072* | 6 | 3000 | 75 | 67 | 85 | 76.1 | 0.66 | 15.24
DHG072* | 6 | 3000 | 75 | 71 | 85 | 79.3 | 0.5 | 11.7
DHG072* | 6 | 3000 | 75 | 59 | 95 | 69.9 | 0.96 | 20.29
DHG072* | 6 | 3000 | 75 | 63 | 95 | 70.8 | 0.86 | 18.43
DHG072* | 6 | 3000 | 75 | 67 | 95 | 72.9 | 0.68 | 14.96
DHG072* | 6 | 3000 | 75 | 71 | 95 | 76.1 | 0.5 | 11.4
DHG072* | 6 | 3000 | 75 | 59 | 105 | 66 | 1 | 20
DHG072* | 6 | 3000 | 75 | 63 | 105 | 67 | 0.9 | 18.18
DHG072* | 6 | 3000 | 75 | 67 | 105 | 69.1 | 0.7 | 14.72
DHG072* | 6 | 3000 | 75 | 71 | 105 | 72.3 | 0.5 | 11.1
DHG072* | 6 | 3000 | 75 | 59 | 115 | 62.5 | 1 | 18.93
DHG072* | 6 | 3000 | 75 | 63 | 115 | 63.5 | 1 | 19.24
DHG072* | 6 | 3000 | 75 | 67 | 115 | 65.6 | 0.8 | 15.88
DHG072* | 6 | 3000 | 75 | 71 | 115 | 68.8 | 0.6 | 12.3
DHG072* | 6 | 1800 | 80 | 59 | 65 | 70.4 | 0.81 | 28.66
DHG072* | 6 | 1800 | 80 | 63 | 65 | 71.3 | 0.74 | 26.81
DHG072* | 6 | 1800 | 80 | 67 | 65 | 73.4 | 0.63 | 23.34
DHG072* | 6 | 1800 | 80 | 71 | 65 | 76.6 | 0.5 | 19.7
DHG072* | 6 | 1800 | 80 | 59 | 75 | 69.7 | 0.81 | 28.61
DHG072* | 6 | 1800 | 80 | 63 | 75 | 70.7 | 0.75 | 26.76
DHG072* | 6 | 1800 | 80 | 67 | 75 | 72.8 | 0.63 | 23.29
DHG072* | 6 | 1800 | 80 | 71 | 75 | 76 | 0.5 | 19.7
DHG072* | 6 | 1800 | 80 | 59 | 85 | 67.9 | 0.84 | 28.87
DHG072* | 6 | 1800 | 80 | 63 | 85 | 68.9 | 0.78 | 27.02
DHG072* | 6 | 1800 | 80 | 67 | 85 | 71 | 0.66 | 23.55
DHG072* | 6 | 1800 | 80 | 71 | 85 | 74.2 | 0.5 | 20
DHG072* | 6 | 1800 | 80 | 59 | 95 | 64.7 | 0.87 | 28.59
DHG072* | 6 | 1800 | 80 | 63 | 95 | 65.7 | 0.81 | 26.74
DHG072* | 6 | 1800 | 80 | 67 | 95 | 67.8 | 0.68 | 23.27
DHG072* | 6 | 1800 | 80 | 71 | 95 | 71 | 0.5 | 19.7
DHG072* | 6 | 1800 | 80 | 59 | 105 | 60.9 | 0.92 | 28.34
DHG072* | 6 | 1800 | 80 | 63 | 105 | 61.9 | 0.85 | 26.49
DHG072* | 6 | 1800 | 80 | 67 | 105 | 64 | 0.71 | 23.02
DHG072* | 6 | 1800 | 80 | 71 | 105 | 67.2 | 0.6 | 19.4
DHG072* | 6 | 1800 | 80 | 59 | 115 | 57.4 | 1 | 28.97
DHG072* | 6 | 1800 | 80 | 63 | 115 | 58.4 | 0.94 | 27.65
DHG072* | 6 | 1800 | 80 | 67 | 115 | 60.5 | 0.79 | 24.18
DHG072* | 6 | 1800 | 80 | 71 | 115 | 63.7 | 0.6 | 20.6
DHG072* | 6 | 2150 | 80 | 59 | 65 | 71.5 | 0.9 | 27.15
DHG072* | 6 | 2150 | 80 | 63 | 65 | 72.5 | 0.82 | 25.29
DHG072* | 6 | 2150 | 80 | 67 | 65 | 74.6 | 0.69 | 21.83
DHG072* | 6 | 2150 | 80 | 71 | 65 | 77.8 | 0.6 | 18.2
DHG072* | 6 | 2150 | 80 | 59 | 75 | 70.9 | 0.9 | 27.1
DHG072* | 6 | 2150 | 80 | 63 | 75 | 71.9 | 0.83 | 25.24
DHG072* | 6 | 2150 | 80 | 67 | 75 | 74 | 0.7 | 21.78
DHG072* | 6 | 2150 | 80 | 71 | 75 | 77.2 | 0.6 | 18.2
DHG072* | 6 | 2150 | 80 | 59 | 85 | 69.1 | 0.94 | 27.36
DHG072* | 6 | 2150 | 80 | 63 | 85 | 70.1 | 0.86 | 25.5
DHG072* | 6 | 2150 | 80 | 67 | 85 | 72.2 | 0.72 | 22.04
DHG072* | 6 | 2150 | 80 | 71 | 85 | 75.4 | 0.6 | 18.4
DHG072* | 6 | 2150 | 80 | 59 | 95 | 65.9 | 0.97 | 27.08
DHG072* | 6 | 2150 | 80 | 63 | 95 | 66.9 | 0.89 | 25.22
DHG072* | 6 | 2150 | 80 | 67 | 95 | 69 | 0.75 | 21.76
DHG072* | 6 | 2150 | 80 | 71 | 95 | 72.2 | 0.6 | 18.2
DHG072* | 6 | 2150 | 80 | 59 | 105 | 62.1 | 1 | 26.24
DHG072* | 6 | 2150 | 80 | 63 | 105 | 63 | 0.94 | 24.98
DHG072* | 6 | 2150 | 80 | 67 | 105 | 65.1 | 0.78 | 21.51
DHG072* | 6 | 2150 | 80 | 71 | 105 | 68.3 | 0.6 | 17.9
DHG072* | 6 | 2150 | 80 | 59 | 115 | 58.5 | 1 | 24.75
DHG072* | 6 | 2150 | 80 | 63 | 115 | 59.5 | 1 | 25.17
DHG072* | 6 | 2150 | 80 | 67 | 115 | 61.6 | 0.87 | 22.67
DHG072* | 6 | 2150 | 80 | 71 | 115 | 64.8 | 0.7 | 19.1
DHG072* | 6 | 3000 | 80 | 59 | 65 | 75.8 | 1 | 22.98
DHG072* | 6 | 3000 | 80 | 63 | 65 | 76.8 | 0.97 | 22.61
DHG072* | 6 | 3000 | 80 | 67 | 65 | 78.9 | 0.8 | 19.14
DHG072* | 6 | 3000 | 80 | 71 | 65 | 82.1 | 0.6 | 15.6
DHG072* | 6 | 3000 | 80 | 59 | 75 | 75.2 | 1 | 22.79
DHG072* | 6 | 3000 | 80 | 63 | 75 | 76.2 | 0.98 | 22.56
DHG072* | 6 | 3000 | 80 | 67 | 75 | 78.3 | 0.8 | 19.09
DHG072* | 6 | 3000 | 80 | 71 | 75 | 81.5 | 0.6 | 15.5
DHG072* | 6 | 3000 | 80 | 59 | 85 | 73.4 | 1 | 22.23
DHG072* | 6 | 3000 | 80 | 63 | 85 | 74.4 | 1 | 22.54
DHG072* | 6 | 3000 | 80 | 67 | 85 | 76.5 | 0.84 | 19.36
DHG072* | 6 | 3000 | 80 | 71 | 85 | 79.7 | 0.7 | 15.8
DHG072* | 6 | 3000 | 80 | 59 | 95 | 70.2 | 1 | 21.28
DHG072* | 6 | 3000 | 80 | 63 | 95 | 71.2 | 1 | 21.58
DHG072* | 6 | 3000 | 80 | 67 | 95 | 73.3 | 0.86 | 19.08
DHG072* | 6 | 3000 | 80 | 71 | 95 | 76.5 | 0.7 | 15.5
DHG072* | 6 | 3000 | 80 | 59 | 105 | 66.4 | 1 | 20.11
DHG072* | 6 | 3000 | 80 | 63 | 105 | 67.4 | 1 | 20.41
DHG072* | 6 | 3000 | 80 | 67 | 105 | 69.5 | 0.89 | 18.83
DHG072* | 6 | 3000 | 80 | 71 | 105 | 72.7 | 0.7 | 15.2
DHG072* | 6 | 3000 | 80 | 59 | 115 | 62.8 | 1 | 19.04
DHG072* | 6 | 3000 | 80 | 63 | 115 | 63.8 | 1 | 19.35
DHG072* | 6 | 3000 | 80 | 67 | 115 | 65.9 | 1 | 19.98
DHG072* | 6 | 3000 | 80 | 71 | 115 | 69.1 | 0.8 | 16.4
DHG072* | 6 | 1800 | 85 | 59 | 65 | 71.5 | 0.89 | 32.31
DHG072* | 6 | 1800 | 85 | 63 | 65 | 72.5 | 0.83 | 30.45
DHG072* | 6 | 1800 | 85 | 67 | 65 | 74.6 | 0.72 | 26.98
DHG072* | 6 | 1800 | 85 | 71 | 65 | 77.8 | 0.6 | 23.4
DHG072* | 6 | 1800 | 85 | 59 | 75 | 70.9 | 0.9 | 32.26
DHG072* | 6 | 1800 | 85 | 63 | 75 | 71.9 | 0.84 | 30.4
DHG072* | 6 | 1800 | 85 | 67 | 75 | 74 | 0.72 | 26.93
DHG072* | 6 | 1800 | 85 | 71 | 75 | 77.2 | 0.6 | 23.3
DHG072* | 6 | 1800 | 85 | 59 | 85 | 69.1 | 0.93 | 32.52
DHG072* | 6 | 1800 | 85 | 63 | 85 | 70.1 | 0.87 | 30.66
DHG072* | 6 | 1800 | 85 | 67 | 85 | 72.2 | 0.75 | 27.19
DHG072* | 6 | 1800 | 85 | 71 | 85 | 75.4 | 0.6 | 23.6
DHG072* | 6 | 1800 | 85 | 59 | 95 | 65.9 | 0.97 | 32.24
DHG072* | 6 | 1800 | 85 | 63 | 95 | 66.9 | 0.9 | 30.38
DHG072* | 6 | 1800 | 85 | 67 | 95 | 69 | 0.77 | 26.91
DHG072* | 6 | 1800 | 85 | 71 | 95 | 72.2 | 0.6 | 23.3
DHG072* | 6 | 1800 | 85 | 59 | 105 | 62.1 | 1 | 31.35
DHG072* | 6 | 1800 | 85 | 63 | 105 | 63.1 | 0.95 | 30.13
DHG072* | 6 | 1800 | 85 | 67 | 105 | 65.2 | 0.81 | 26.67
DHG072* | 6 | 1800 | 85 | 71 | 105 | 68.4 | 0.7 | 23.1
DHG072* | 6 | 1800 | 85 | 59 | 115 | 58.5 | 1 | 29.57
DHG072* | 6 | 1800 | 85 | 63 | 115 | 59.5 | 1 | 30.07
DHG072* | 6 | 1800 | 85 | 67 | 115 | 61.6 | 0.89 | 27.83
DHG072* | 6 | 1800 | 85 | 71 | 115 | 64.8 | 0.7 | 24.2
DHG072* | 6 | 2150 | 85 | 59 | 65 | 72.7 | 1 | 30.74
DHG072* | 6 | 2150 | 85 | 63 | 65 | 73.7 | 0.93 | 28.94
DHG072* | 6 | 2150 | 85 | 67 | 65 | 75.8 | 0.79 | 25.47
DHG072* | 6 | 2150 | 85 | 71 | 65 | 79 | 0.7 | 21.9
DHG072* | 6 | 2150 | 85 | 59 | 75 | 72.1 | 1 | 30.48
DHG072* | 6 | 2150 | 85 | 63 | 75 | 73.1 | 0.94 | 28.89
DHG072* | 6 | 2150 | 85 | 67 | 75 | 75.2 | 0.8 | 25.42
DHG072* | 6 | 2150 | 85 | 71 | 75 | 78.4 | 0.7 | 21.8
DHG072* | 6 | 2150 | 85 | 59 | 85 | 70.2 | 1 | 29.7
DHG072* | 6 | 2150 | 85 | 63 | 85 | 71.2 | 0.97 | 29.15
DHG072* | 6 | 2150 | 85 | 67 | 85 | 73.3 | 0.83 | 25.68
DHG072* | 6 | 2150 | 85 | 71 | 85 | 76.5 | 0.7 | 22.1
DHG072* | 6 | 2150 | 85 | 59 | 95 | 67.1 | 1 | 28.37
DHG072* | 6 | 2150 | 85 | 63 | 95 | 68.1 | 1 | 28.79
DHG072* | 6 | 2150 | 85 | 67 | 95 | 70.2 | 0.86 | 25.4
DHG072* | 6 | 2150 | 85 | 71 | 95 | 73.4 | 0.7 | 21.8
DHG072* | 6 | 2150 | 85 | 59 | 105 | 63.2 | 1 | 26.74
DHG072* | 6 | 2150 | 85 | 63 | 105 | 64.2 | 1 | 27.16
DHG072* | 6 | 2150 | 85 | 67 | 105 | 66.3 | 0.9 | 25.16
DHG072* | 6 | 2150 | 85 | 71 | 105 | 69.5 | 0.7 | 21.6
DHG072* | 6 | 2150 | 85 | 59 | 115 | 59.7 | 1 | 25.25
DHG072* | 6 | 2150 | 85 | 63 | 115 | 60.7 | 1 | 25.67
DHG072* | 6 | 2150 | 85 | 67 | 115 | 62.8 | 0.99 | 26.32
DHG072* | 6 | 2150 | 85 | 71 | 115 | 66 | 0.8 | 22.7
DHG072* | 6 | 3000 | 85 | 59 | 65 | 77 | 1 | 23.34
DHG072* | 6 | 3000 | 85 | 63 | 65 | 78 | 1 | 23.64
DHG072* | 6 | 3000 | 85 | 67 | 65 | 80.1 | 0.94 | 22.79
DHG072* | 6 | 3000 | 85 | 71 | 65 | 83.3 | 0.8 | 19.2
DHG072* | 6 | 3000 | 85 | 59 | 75 | 76.4 | 1 | 23.15
DHG072* | 6 | 3000 | 85 | 63 | 75 | 77.4 | 1 | 23.45
DHG072* | 6 | 3000 | 85 | 67 | 75 | 79.5 | 0.94 | 22.74
DHG072* | 6 | 3000 | 85 | 71 | 75 | 82.7 | 0.8 | 19.1
DHG072* | 6 | 3000 | 85 | 59 | 85 | 74.6 | 1 | 22.59
DHG072* | 6 | 3000 | 85 | 63 | 85 | 75.5 | 1 | 22.89
DHG072* | 6 | 3000 | 85 | 67 | 85 | 77.6 | 0.98 | 23
DHG072* | 6 | 3000 | 85 | 71 | 85 | 80.8 | 0.8 | 19.4
DHG072* | 6 | 3000 | 85 | 59 | 95 | 71.4 | 1 | 21.64
DHG072* | 6 | 3000 | 85 | 63 | 95 | 72.4 | 1 | 21.94
DHG072* | 6 | 3000 | 85 | 67 | 95 | 74.5 | 1 | 22.57
DHG072* | 6 | 3000 | 85 | 71 | 95 | 77.7 | 0.8 | 19.1
DHG072* | 6 | 3000 | 85 | 59 | 105 | 67.5 | 1 | 20.47
DHG072* | 6 | 3000 | 85 | 63 | 105 | 68.5 | 1 | 20.77
DHG072* | 6 | 3000 | 85 | 67 | 105 | 70.6 | 1 | 21.41
DHG072* | 6 | 3000 | 85 | 71 | 105 | 73.8 | 0.8 | 18.9
DHG072* | 6 | 3000 | 85 | 59 | 115 | 64 | 1 | 19.4
DHG072* | 6 | 3000 | 85 | 63 | 115 | 65 | 1 | 19.7
DHG072* | 6 | 3000 | 85 | 67 | 115 | 67.1 | 1 | 20.34
DHG072* | 6 | 3000 | 85 | 71 | 115 | 70.3 | 0.9 | 20
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 59 | 65 | 50 | 0.55 | 19.84
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 63 | 65 | 50.7 | 0.49 | 18.05
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 67 | 65 | 52.2 | 0.39 | 14.7
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 59 | 75 | 49.6 | 0.55 | 19.79
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 63 | 75 | 50.3 | 0.5 | 18
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 67 | 75 | 51.8 | 0.39 | 14.65
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 59 | 85 | 48.3 | 0.58 | 20.04
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 63 | 85 | 49 | 0.52 | 18.25
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 67 | 85 | 50.5 | 0.41 | 14.9
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 59 | 95 | 46 | 0.6 | 19.77
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 63 | 95 | 46.7 | 0.53 | 17.98
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 67 | 95 | 48.2 | 0.42 | 14.63
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 59 | 105 | 43.2 | 0.63 | 19.53
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 63 | 105 | 43.9 | 0.56 | 17.74
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 67 | 105 | 45.4 | 0.44 | 14.39
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 59 | 115 | 40.7 | 0.7 | 20.65
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 63 | 115 | 41.4 | 0.63 | 18.86
DHG072* (70% - Low Stage) | 6 | 1260 | 70 | 67 | 115 | 42.9 | 0.5 | 15.52
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 59 | 65 | 50.9 | 0.6 | 18.29
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 63 | 65 | 51.6 | 0.53 | 16.5
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 67 | 65 | 53.1 | 0.41 | 13.16
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 59 | 75 | 50.5 | 0.6 | 18.25
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 63 | 75 | 51.2 | 0.54 | 16.45
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 67 | 75 | 52.7 | 0.42 | 13.11
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 59 | 85 | 49.1 | 0.63 | 18.5
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 63 | 85 | 49.8 | 0.56 | 16.71
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 67 | 85 | 51.4 | 0.43 | 13.36
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 59 | 95 | 46.9 | 0.65 | 18.23
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 63 | 95 | 47.6 | 0.58 | 16.43
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 67 | 95 | 49.1 | 0.45 | 13.09
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 59 | 105 | 44.1 | 0.68 | 17.99
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 63 | 105 | 44.8 | 0.6 | 16.2
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 67 | 105 | 46.3 | 0.46 | 12.85
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 59 | 115 | 41.6 | 0.77 | 19.11
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 63 | 115 | 42.3 | 0.68 | 17.32
DHG072* (70% - Low Stage) | 6 | 1520 | 70 | 67 | 115 | 43.8 | 0.53 | 13.97
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 59 | 65 | 53.9 | 0.68 | 15.79
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 63 | 65 | 54.6 | 0.59 | 13.99
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 67 | 65 | 56.1 | 0.44 | 10.65
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 59 | 75 | 53.4 | 0.68 | 15.74
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 63 | 75 | 54.1 | 0.6 | 13.95
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 67 | 75 | 55.6 | 0.44 | 10.6
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 59 | 85 | 52.1 | 0.71 | 15.99
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 63 | 85 | 52.8 | 0.62 | 14.2
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 67 | 85 | 54.3 | 0.46 | 10.85
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 59 | 95 | 49.8 | 0.73 | 15.72
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 63 | 95 | 50.5 | 0.64 | 13.93
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 67 | 95 | 52 | 0.47 | 10.58
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 59 | 105 | 47.1 | 0.76 | 15.48
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 63 | 105 | 47.8 | 0.66 | 13.69
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 67 | 105 | 49.3 | 0.48 | 10.34
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 59 | 115 | 44.5 | 0.86 | 16.6
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 63 | 115 | 45.2 | 0.76 | 14.81
DHG072* (70% - Low Stage) | 6 | 2100 | 70 | 67 | 115 | 46.7 | 0.57 | 11.46
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 59 | 65 | 50.3 | 0.66 | 23.78
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 63 | 65 | 51 | 0.6 | 21.99
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 67 | 65 | 52.5 | 0.49 | 18.64
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 71 | 65 | 54.8 | 0.4 | 15.2
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 59 | 75 | 49.8 | 0.66 | 23.73
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 63 | 75 | 50.5 | 0.6 | 21.94
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 67 | 75 | 52.1 | 0.5 | 18.59
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 71 | 75 | 54.4 | 0.4 | 15.1
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 59 | 85 | 48.5 | 0.69 | 23.98
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 63 | 85 | 49.2 | 0.62 | 22.19
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 67 | 85 | 50.7 | 0.51 | 18.84
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 71 | 85 | 53 | 0.4 | 15.4
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 59 | 95 | 46.2 | 0.71 | 23.71
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 63 | 95 | 47 | 0.65 | 21.92
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 67 | 95 | 48.5 | 0.53 | 18.57
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 71 | 95 | 50.8 | 0.4 | 15.1
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 59 | 105 | 43.5 | 0.75 | 23.47
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 63 | 105 | 44.2 | 0.68 | 21.68
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 67 | 105 | 45.7 | 0.56 | 18.33
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 71 | 105 | 48 | 0.4 | 14.9
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 59 | 115 | 40.9 | 0.83 | 24.59
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 63 | 115 | 41.7 | 0.76 | 22.8
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 67 | 115 | 43.2 | 0.62 | 19.46
DHG072* (70% - Low Stage) | 6 | 1260 | 75 | 71 | 115 | 45.5 | 0.5 | 16
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 59 | 65 | 51.2 | 0.73 | 22.23
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 63 | 65 | 51.9 | 0.66 | 20.44
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 67 | 65 | 53.4 | 0.54 | 17.1
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 71 | 65 | 55.7 | 0.4 | 13.6
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 59 | 75 | 50.7 | 0.73 | 22.19
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 63 | 75 | 51.4 | 0.66 | 20.39
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 67 | 75 | 52.9 | 0.54 | 17.05
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 71 | 75 | 55.2 | 0.4 | 13.6
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 59 | 85 | 49.4 | 0.76 | 22.44
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 63 | 85 | 50.1 | 0.69 | 20.65
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 67 | 85 | 51.6 | 0.56 | 17.3
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 71 | 85 | 53.9 | 0.4 | 13.8
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 59 | 95 | 47.1 | 0.79 | 22.17
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 63 | 95 | 47.8 | 0.71 | 20.37
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 67 | 95 | 49.3 | 0.58 | 17.03
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 71 | 95 | 51.7 | 0.4 | 13.6
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 59 | 105 | 44.4 | 0.83 | 21.93
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 63 | 105 | 45.1 | 0.75 | 20.14
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 67 | 105 | 46.6 | 0.6 | 16.79
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 71 | 105 | 48.9 | 0.5 | 13.3
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 59 | 115 | 41.8 | 0.92 | 23.05
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 63 | 115 | 42.5 | 0.84 | 21.26
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 67 | 115 | 44 | 0.68 | 17.91
DHG072* (70% - Low Stage) | 6 | 1520 | 75 | 71 | 115 | 46.4 | 0.5 | 14.4
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 59 | 65 | 54.1 | 0.84 | 19.73
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 63 | 65 | 54.8 | 0.76 | 17.93
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 67 | 65 | 56.3 | 0.6 | 14.59
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 71 | 65 | 58.6 | 0.4 | 11.1
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 59 | 75 | 53.7 | 0.85 | 19.68
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 63 | 75 | 54.4 | 0.76 | 17.89
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 67 | 75 | 55.9 | 0.6 | 14.54
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 71 | 75 | 58.2 | 0.4 | 11.1
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 59 | 85 | 52.4 | 0.88 | 19.93
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 63 | 85 | 53.1 | 0.79 | 18.14
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 67 | 85 | 54.6 | 0.63 | 14.79
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 71 | 85 | 56.9 | 0.5 | 11.3
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 59 | 95 | 50.1 | 0.91 | 19.66
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 63 | 95 | 50.8 | 0.81 | 17.87
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 67 | 95 | 52.3 | 0.64 | 14.52
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 71 | 95 | 54.6 | 0.5 | 11.1
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 59 | 105 | 47.3 | 0.95 | 19.42
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 63 | 105 | 48 | 0.85 | 17.63
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 67 | 105 | 49.5 | 0.67 | 14.28
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 71 | 105 | 51.8 | 0.5 | 10.8
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 59 | 115 | 44.8 | 1 | 19.39
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 63 | 115 | 45.5 | 0.95 | 18.75
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 67 | 115 | 47 | 0.76 | 15.4
DHG072* (70% - Low Stage) | 6 | 2100 | 75 | 71 | 115 | 49.3 | 0.6 | 11.9
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 59 | 65 | 50.5 | 0.76 | 27.75
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 63 | 65 | 51.3 | 0.7 | 25.95
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 67 | 65 | 52.8 | 0.59 | 22.61
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 71 | 65 | 55.1 | 0.5 | 19.1
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 59 | 75 | 50.1 | 0.77 | 27.7
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 63 | 75 | 50.8 | 0.71 | 25.9
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 67 | 75 | 52.3 | 0.6 | 22.56
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 71 | 75 | 54.6 | 0.5 | 19.1
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 59 | 85 | 48.8 | 0.79 | 27.95
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 63 | 85 | 49.5 | 0.73 | 26.16
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 67 | 85 | 51 | 0.62 | 22.81
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 71 | 85 | 53.3 | 0.5 | 19.3
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 59 | 95 | 46.5 | 0.82 | 27.68
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 63 | 95 | 47.2 | 0.76 | 25.89
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 67 | 95 | 48.7 | 0.64 | 22.54
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 71 | 95 | 51 | 0.5 | 19.1
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 59 | 105 | 43.7 | 0.87 | 27.44
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 63 | 105 | 44.5 | 0.8 | 25.65
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 67 | 105 | 46 | 0.67 | 22.3
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 71 | 105 | 48.3 | 0.5 | 18.8
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 59 | 115 | 41.2 | 0.96 | 28.56
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 63 | 115 | 41.9 | 0.89 | 26.77
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 67 | 115 | 43.4 | 0.75 | 23.42
DHG072* (70% - Low Stage) | 6 | 1260 | 80 | 71 | 115 | 45.7 | 0.6 | 20
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 59 | 65 | 51.4 | 0.85 | 26.2
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 63 | 65 | 52.1 | 0.78 | 24.41
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 67 | 65 | 53.6 | 0.66 | 21.06
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 71 | 65 | 56 | 0.5 | 17.6
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 59 | 75 | 51 | 0.86 | 26.15
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 63 | 75 | 51.7 | 0.79 | 24.36
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 67 | 75 | 53.2 | 0.66 | 21.01
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 71 | 75 | 55.5 | 0.5 | 17.5
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 59 | 85 | 49.7 | 0.89 | 26.4
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 63 | 85 | 50.4 | 0.82 | 24.61
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 67 | 85 | 51.9 | 0.69 | 21.27
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 71 | 85 | 54.2 | 0.5 | 17.8
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 59 | 95 | 47.4 | 0.92 | 26.13
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 63 | 95 | 48.1 | 0.85 | 24.34
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 67 | 95 | 49.6 | 0.71 | 21
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 71 | 95 | 51.9 | 0.6 | 17.5
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 59 | 105 | 44.6 | 0.97 | 25.89
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 63 | 105 | 45.3 | 0.89 | 24.1
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 67 | 105 | 46.8 | 0.74 | 20.76
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 71 | 105 | 49.1 | 0.6 | 17.3
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 59 | 115 | 42.1 | 1 | 25.17
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 63 | 115 | 42.8 | 0.99 | 25.22
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 67 | 115 | 44.3 | 0.83 | 21.88
DHG072* (70% - Low Stage) | 6 | 1520 | 80 | 71 | 115 | 46.6 | 0.7 | 18.4
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 59 | 65 | 54.4 | 1 | 23.54
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 63 | 65 | 55.1 | 0.92 | 21.9
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 67 | 65 | 56.6 | 0.76 | 18.56
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 71 | 65 | 58.9 | 0.6 | 15.1
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 59 | 75 | 53.9 | 1 | 23.35
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 63 | 75 | 54.6 | 0.92 | 21.85
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 67 | 75 | 56.2 | 0.76 | 18.51
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 71 | 75 | 58.5 | 0.6 | 15
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 59 | 85 | 52.6 | 1 | 22.78
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 63 | 85 | 53.3 | 0.96 | 22.1
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 67 | 85 | 54.8 | 0.79 | 18.76
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 71 | 85 | 57.1 | 0.6 | 15.3
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 59 | 95 | 50.3 | 1 | 21.8
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 63 | 95 | 51.1 | 0.99 | 21.83
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 67 | 95 | 52.6 | 0.81 | 18.49
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 71 | 95 | 54.9 | 0.6 | 15
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 59 | 105 | 47.6 | 1 | 20.6
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 63 | 105 | 48.3 | 1 | 20.91
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 67 | 105 | 49.8 | 0.85 | 18.25
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 71 | 105 | 52.1 | 0.7 | 14.8
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 59 | 115 | 45 | 1 | 19.5
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 63 | 115 | 45.8 | 1 | 19.81
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 67 | 115 | 47.3 | 0.95 | 19.37
DHG072* (70% - Low Stage) | 6 | 2100 | 80 | 71 | 115 | 49.6 | 0.7 | 15.9
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 59 | 65 | 51.4 | 0.84 | 31.26
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 63 | 65 | 52.1 | 0.78 | 29.47
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 67 | 65 | 53.6 | 0.68 | 26.13
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 71 | 65 | 55.9 | 0.6 | 22.7
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 59 | 75 | 50.9 | 0.85 | 31.21
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 63 | 75 | 51.7 | 0.79 | 29.42
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 67 | 75 | 53.2 | 0.68 | 26.08
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 71 | 75 | 55.5 | 0.6 | 22.6
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 59 | 85 | 49.6 | 0.88 | 31.47
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 63 | 85 | 50.3 | 0.82 | 29.67
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 67 | 85 | 51.8 | 0.7 | 26.33
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 71 | 85 | 54.2 | 0.6 | 22.9
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 59 | 95 | 47.4 | 0.91 | 31.2
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 63 | 95 | 48.1 | 0.85 | 29.4
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 67 | 95 | 49.6 | 0.73 | 26.06
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 71 | 95 | 51.9 | 0.6 | 22.6
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 59 | 105 | 44.6 | 0.96 | 30.96
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 63 | 105 | 45.3 | 0.89 | 29.16
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 67 | 105 | 46.8 | 0.76 | 25.82
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 71 | 105 | 49.1 | 0.6 | 22.4
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 59 | 115 | 42.1 | 1 | 30.35
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 63 | 115 | 42.8 | 0.98 | 30.29
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 67 | 115 | 44.3 | 0.84 | 26.94
DHG072* (70% - Low Stage) | 6 | 1260 | 85 | 71 | 115 | 46.6 | 0.7 | 23.5
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 59 | 65 | 52.3 | 0.95 | 29.72
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 63 | 65 | 53 | 0.88 | 27.93
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 67 | 65 | 54.5 | 0.75 | 24.58
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 71 | 65 | 56.8 | 0.6 | 21.1
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 59 | 75 | 51.8 | 0.96 | 29.67
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 63 | 75 | 52.5 | 0.89 | 27.88
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 67 | 75 | 54 | 0.76 | 24.53
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 71 | 75 | 56.3 | 0.6 | 21.1
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 59 | 85 | 50.5 | 0.99 | 29.92
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 63 | 85 | 51.2 | 0.92 | 28.13
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 67 | 85 | 52.7 | 0.79 | 24.78
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 71 | 85 | 55 | 0.6 | 21.3
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 59 | 95 | 48.2 | 1 | 28.85
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 63 | 95 | 49 | 0.95 | 27.86
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 67 | 95 | 50.5 | 0.81 | 24.51
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 71 | 95 | 52.8 | 0.7 | 21
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 59 | 105 | 45.5 | 1 | 27.19
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 63 | 105 | 46.2 | 1 | 27.62
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 67 | 105 | 47.7 | 0.85 | 24.27
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 71 | 105 | 50 | 0.7 | 20.8
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 59 | 115 | 42.9 | 1 | 25.68
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 63 | 115 | 43.7 | 1 | 26.11
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 67 | 115 | 45.2 | 0.94 | 25.4
DHG072* (70% - Low Stage) | 6 | 1520 | 85 | 71 | 115 | 47.5 | 0.8 | 21.9
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 59 | 65 | 55.2 | 1 | 23.91
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 63 | 65 | 56 | 1 | 24.22
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 67 | 65 | 57.5 | 0.89 | 22.07
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 71 | 65 | 59.8 | 0.7 | 18.6
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 59 | 75 | 54.8 | 1 | 23.72
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 63 | 75 | 55.5 | 1 | 24.03
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 67 | 75 | 57 | 0.89 | 22.02
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 71 | 75 | 59.3 | 0.7 | 18.6
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 59 | 85 | 53.5 | 1 | 23.15
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 63 | 85 | 54.2 | 1 | 23.45
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 67 | 85 | 55.7 | 0.92 | 22.28
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 71 | 85 | 58 | 0.7 | 18.8
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 59 | 95 | 51.2 | 1 | 22.16
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 63 | 95 | 51.9 | 1 | 22.47
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 67 | 95 | 53.4 | 0.95 | 22.01
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 71 | 95 | 55.7 | 0.8 | 18.5
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 59 | 105 | 48.4 | 1 | 20.96
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 63 | 105 | 49.1 | 1 | 21.27
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 67 | 105 | 50.6 | 0.99 | 21.77
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 71 | 105 | 53 | 0.8 | 18.3
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 59 | 115 | 45.9 | 1 | 19.87
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 63 | 115 | 46.6 | 1 | 20.18
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 67 | 115 | 48.1 | 1 | 20.83
DHG072* (70% - Low Stage) | 6 | 2100 | 85 | 71 | 115 | 50.4 | 0.9 | 19.4
DHG090* | 7.5 | 2625 | 70 | 59 | 65 | 91.1 | 0.63 | 19.75
DHG090* | 7.5 | 2625 | 70 | 63 | 65 | 92.4 | 0.56 | 17.92
DHG090* | 7.5 | 2625 | 70 | 67 | 65 | 95.1 | 0.44 | 14.51
DHG090* | 7.5 | 2625 | 70 | 59 | 75 | 90.3 | 0.63 | 19.7
DHG090* | 7.5 | 2625 | 70 | 63 | 75 | 91.6 | 0.56 | 17.87
DHG090* | 7.5 | 2625 | 70 | 67 | 75 | 94.3 | 0.44 | 14.46
DHG090* | 7.5 | 2625 | 70 | 59 | 85 | 87.9 | 0.66 | 19.95
DHG090* | 7.5 | 2625 | 70 | 63 | 85 | 89.2 | 0.59 | 18.13
DHG090* | 7.5 | 2625 | 70 | 67 | 85 | 91.9 | 0.46 | 14.72
DHG090* | 7.5 | 2625 | 70 | 59 | 95 | 83.8 | 0.68 | 19.68
DHG090* | 7.5 | 2625 | 70 | 63 | 95 | 85.1 | 0.61 | 17.85
DHG090* | 7.5 | 2625 | 70 | 67 | 95 | 87.8 | 0.47 | 14.44
DHG090* | 7.5 | 2625 | 70 | 59 | 105 | 78.7 | 0.71 | 19.43
DHG090* | 7.5 | 2625 | 70 | 63 | 105 | 80 | 0.64 | 17.61
DHG090* | 7.5 | 2625 | 70 | 67 | 105 | 82.8 | 0.5 | 14.2
DHG090* | 7.5 | 2625 | 70 | 59 | 115 | 74.1 | 0.8 | 20.58
DHG090* | 7.5 | 2625 | 70 | 63 | 115 | 75.4 | 0.72 | 18.75
DHG090* | 7.5 | 2625 | 70 | 67 | 115 | 78.2 | 0.57 | 15.34
DHG090* | 7.5 | 3000 | 70 | 59 | 65 | 92.3 | 0.67 | 18.64
DHG090* | 7.5 | 3000 | 70 | 63 | 65 | 93.6 | 0.59 | 16.82
DHG090* | 7.5 | 3000 | 70 | 67 | 65 | 96.3 | 0.46 | 13.41
DHG090* | 7.5 | 3000 | 70 | 59 | 75 | 91.5 | 0.67 | 18.59
DHG090* | 7.5 | 3000 | 70 | 63 | 75 | 92.8 | 0.6 | 16.77
DHG090* | 7.5 | 3000 | 70 | 67 | 75 | 95.5 | 0.46 | 13.36
DHG090* | 7.5 | 3000 | 70 | 59 | 85 | 89.1 | 0.7 | 18.85
DHG090* | 7.5 | 3000 | 70 | 63 | 85 | 90.4 | 0.62 | 17.02
DHG090* | 7.5 | 3000 | 70 | 67 | 85 | 93.1 | 0.48 | 13.61
DHG090* | 7.5 | 3000 | 70 | 59 | 95 | 85 | 0.72 | 18.57
DHG090* | 7.5 | 3000 | 70 | 63 | 95 | 86.3 | 0.64 | 16.75
DHG090* | 7.5 | 3000 | 70 | 67 | 95 | 89 | 0.49 | 13.34
DHG090* | 7.5 | 3000 | 70 | 59 | 105 | 79.9 | 0.76 | 18.33
DHG090* | 7.5 | 3000 | 70 | 63 | 105 | 81.2 | 0.67 | 16.5
DHG090* | 7.5 | 3000 | 70 | 67 | 105 | 84 | 0.51 | 13.09
DHG090* | 7.5 | 3000 | 70 | 59 | 115 | 75.4 | 0.85 | 19.47
DHG090* | 7.5 | 3000 | 70 | 63 | 115 | 76.6 | 0.76 | 17.65
DHG090* | 7.5 | 3000 | 70 | 67 | 115 | 79.4 | 0.59 | 14.24
DHG090* | 7.5 | 3375 | 70 | 59 | 65 | 93.7 | 0.7 | 17.71
DHG090* | 7.5 | 3375 | 70 | 63 | 65 | 95 | 0.62 | 15.89
DHG090* | 7.5 | 3375 | 70 | 67 | 65 | 97.8 | 0.47 | 12.48
DHG090* | 7.5 | 3375 | 70 | 59 | 75 | 92.9 | 0.71 | 17.66
DHG090* | 7.5 | 3375 | 70 | 63 | 75 | 94.2 | 0.62 | 15.84
DHG090* | 7.5 | 3375 | 70 | 67 | 75 | 96.9 | 0.48 | 12.43
DHG090* | 7.5 | 3375 | 70 | 59 | 85 | 90.5 | 0.73 | 17.92
DHG090* | 7.5 | 3375 | 70 | 63 | 85 | 91.8 | 0.65 | 16.09
DHG090* | 7.5 | 3375 | 70 | 67 | 85 | 94.6 | 0.5 | 12.68
DHG090* | 7.5 | 3375 | 70 | 59 | 95 | 86.4 | 0.76 | 17.65
DHG090* | 7.5 | 3375 | 70 | 63 | 95 | 87.7 | 0.67 | 15.82
DHG090* | 7.5 | 3375 | 70 | 67 | 95 | 90.4 | 0.51 | 12.41
DHG090* | 7.5 | 3375 | 70 | 59 | 105 | 81.4 | 0.79 | 17.4
DHG090* | 7.5 | 3375 | 70 | 63 | 105 | 82.7 | 0.7 | 15.58
DHG090* | 7.5 | 3375 | 70 | 67 | 105 | 85.4 | 0.53 | 12.17
DHG090* | 7.5 | 3375 | 70 | 59 | 115 | 76.8 | 0.9 | 18.54
DHG090* | 7.5 | 3375 | 70 | 63 | 115 | 78.1 | 0.79 | 16.72
DHG090* | 7.5 | 3375 | 70 | 67 | 115 | 80.8 | 0.61 | 13.31
DHG090* | 7.5 | 2625 | 75 | 59 | 65 | 91.6 | 0.75 | 23.76
DHG090* | 7.5 | 2625 | 75 | 63 | 65 | 92.9 | 0.68 | 21.93
DHG090* | 7.5 | 2625 | 75 | 67 | 65 | 95.6 | 0.56 | 18.53
DHG090* | 7.5 | 2625 | 75 | 71 | 65 | 99.8 | 0.4 | 15
DHG090* | 7.5 | 2625 | 75 | 59 | 75 | 90.8 | 0.75 | 23.71
DHG090* | 7.5 | 2625 | 75 | 63 | 75 | 92.1 | 0.69 | 21.88
DHG090* | 7.5 | 2625 | 75 | 67 | 75 | 94.8 | 0.56 | 18.48
DHG090* | 7.5 | 2625 | 75 | 71 | 75 | 99 | 0.4 | 14.9
DHG090* | 7.5 | 2625 | 75 | 59 | 85 | 88.4 | 0.78 | 23.97
DHG090* | 7.5 | 2625 | 75 | 63 | 85 | 89.7 | 0.71 | 22.14
DHG090* | 7.5 | 2625 | 75 | 67 | 85 | 92.4 | 0.59 | 18.73
DHG090* | 7.5 | 2625 | 75 | 71 | 85 | 96.6 | 0.5 | 15.2
DHG090* | 7.5 | 2625 | 75 | 59 | 95 | 84.3 | 0.81 | 23.69
DHG090* | 7.5 | 2625 | 75 | 63 | 95 | 85.6 | 0.74 | 21.87
DHG090* | 7.5 | 2625 | 75 | 67 | 95 | 88.3 | 0.6 | 18.46
DHG090* | 7.5 | 2625 | 75 | 71 | 95 | 92.5 | 0.5 | 14.9
DHG090* | 7.5 | 2625 | 75 | 59 | 105 | 79.3 | 0.85 | 23.45
DHG090* | 7.5 | 2625 | 75 | 63 | 105 | 80.6 | 0.78 | 21.62
DHG090* | 7.5 | 2625 | 75 | 67 | 105 | 83.3 | 0.63 | 18.21
DHG090* | 7.5 | 2625 | 75 | 71 | 105 | 87.5 | 0.5 | 14.7
DHG090* | 7.5 | 2625 | 75 | 59 | 115 | 74.7 | 0.95 | 24.59
DHG090* | 7.5 | 2625 | 75 | 63 | 115 | 76 | 0.87 | 22.77
DHG090* | 7.5 | 2625 | 75 | 67 | 115 | 78.7 | 0.71 | 19.36
DHG090* | 7.5 | 2625 | 75 | 71 | 115 | 82.9 | 0.6 | 15.8
DHG090* | 7.5 | 3000 | 75 | 59 | 65 | 92.8 | 0.81 | 22.66
DHG090* | 7.5 | 3000 | 75 | 63 | 65 | 94.1 | 0.73 | 20.83
DHG090* | 7.5 | 3000 | 75 | 67 | 65 | 96.8 | 0.59 | 17.42
DHG090* | 7.5 | 3000 | 75 | 71 | 65 | 101 | 0.5 | 13.9
DHG090* | 7.5 | 3000 | 75 | 59 | 75 | 92 | 0.81 | 22.61
DHG090* | 7.5 | 3000 | 75 | 63 | 75 | 93.3 | 0.74 | 20.78
DHG090* | 7.5 | 3000 | 75 | 67 | 75 | 96 | 0.6 | 17.37
DHG090* | 7.5 | 3000 | 75 | 71 | 75 | 100.2 | 0.5 | 13.8
DHG090* | 7.5 | 3000 | 75 | 59 | 85 | 89.6 | 0.84 | 22.86
DHG090* | 7.5 | 3000 | 75 | 63 | 85 | 90.9 | 0.76 | 21.04
DHG090* | 7.5 | 3000 | 75 | 67 | 85 | 93.6 | 0.62 | 17.63
DHG090* | 7.5 | 3000 | 75 | 71 | 85 | 97.8 | 0.5 | 14.1
DHG090* | 7.5 | 3000 | 75 | 59 | 95 | 85.5 | 0.87 | 22.59
DHG090* | 7.5 | 3000 | 75 | 63 | 95 | 86.8 | 0.79 | 20.76
DHG090* | 7.5 | 3000 | 75 | 67 | 95 | 89.5 | 0.64 | 17.35
DHG090* | 7.5 | 3000 | 75 | 71 | 95 | 93.7 | 0.5 | 13.8
DHG090* | 7.5 | 3000 | 75 | 59 | 105 | 80.5 | 0.92 | 22.35
DHG090* | 7.5 | 3000 | 75 | 63 | 105 | 81.8 | 0.83 | 20.52
DHG090* | 7.5 | 3000 | 75 | 67 | 105 | 84.5 | 0.67 | 17.11
DHG090* | 7.5 | 3000 | 75 | 71 | 105 | 88.7 | 0.5 | 13.6
DHG090* | 7.5 | 3000 | 75 | 59 | 115 | 75.9 | 1 | 22.99
DHG090* | 7.5 | 3000 | 75 | 63 | 115 | 77.2 | 0.93 | 21.66
DHG090* | 7.5 | 3000 | 75 | 67 | 115 | 79.9 | 0.75 | 18.25
DHG090* | 7.5 | 3000 | 75 | 71 | 115 | 84.1 | 0.6 | 14.7
DHG090* | 7.5 | 3375 | 75 | 59 | 65 | 94.3 | 0.86 | 21.73
DHG090* | 7.5 | 3375 | 75 | 63 | 65 | 95.6 | 0.77 | 19.9
DHG090* | 7.5 | 3375 | 75 | 67 | 65 | 98.3 | 0.62 | 16.49
DHG090* | 7.5 | 3375 | 75 | 71 | 65 | 102.5 | 0.5 | 13
DHG090* | 7.5 | 3375 | 75 | 59 | 75 | 93.4 | 0.86 | 21.68
DHG090* | 7.5 | 3375 | 75 | 63 | 75 | 94.7 | 0.78 | 19.85
DHG090* | 7.5 | 3375 | 75 | 67 | 75 | 97.5 | 0.63 | 16.44
DHG090* | 7.5 | 3375 | 75 | 71 | 75 | 101.7 | 0.5 | 12.9
DHG090* | 7.5 | 3375 | 75 | 59 | 85 | 91.1 | 0.89 | 21.94
DHG090* | 7.5 | 3375 | 75 | 63 | 85 | 92.3 | 0.81 | 20.11
DHG090* | 7.5 | 3375 | 75 | 67 | 85 | 95.1 | 0.65 | 16.7
DHG090* | 7.5 | 3375 | 75 | 71 | 85 | 99.3 | 0.5 | 13.2
DHG090* | 7.5 | 3375 | 75 | 59 | 95 | 86.9 | 0.92 | 21.66
DHG090* | 7.5 | 3375 | 75 | 63 | 95 | 88.2 | 0.83 | 19.83
DHG090* | 7.5 | 3375 | 75 | 67 | 95 | 91 | 0.67 | 16.42
DHG090* | 7.5 | 3375 | 75 | 71 | 95 | 95.1 | 0.5 | 12.9
DHG090* | 7.5 | 3375 | 75 | 59 | 105 | 81.9 | 0.97 | 21.42
DHG090* | 7.5 | 3375 | 75 | 63 | 105 | 83.2 | 0.87 | 19.59
DHG090* | 7.5 | 3375 | 75 | 67 | 105 | 85.9 | 0.7 | 16.18
DHG090* | 7.5 | 3375 | 75 | 71 | 105 | 90.1 | 0.5 | 12.6
DHG090* | 7.5 | 3375 | 75 | 59 | 115 | 77.3 | 1 | 20.83
DHG090* | 7.5 | 3375 | 75 | 63 | 115 | 78.6 | 0.98 | 20.73
DHG090* | 7.5 | 3375 | 75 | 67 | 115 | 81.4 | 0.79 | 17.32
DHG090* | 7.5 | 3375 | 75 | 71 | 115 | 85.5 | 0.6 | 13.8
DHG090* | 7.5 | 2625 | 80 | 59 | 65 | 92.1 | 0.87 | 27.8
DHG090* | 7.5 | 2625 | 80 | 63 | 65 | 93.4 | 0.8 | 25.98
DHG090* | 7.5 | 2625 | 80 | 67 | 65 | 96.1 | 0.68 | 22.57
DHG090* | 7.5 | 2625 | 80 | 71 | 65 | 100.3 | 0.5 | 19
DHG090* | 7.5 | 2625 | 80 | 59 | 75 | 91.3 | 0.88 | 27.75
DHG090* | 7.5 | 2625 | 80 | 63 | 75 | 92.6 | 0.81 | 25.93
DHG090* | 7.5 | 2625 | 80 | 67 | 75 | 95.3 | 0.68 | 22.52
DHG090* | 7.5 | 2625 | 80 | 71 | 75 | 99.5 | 0.6 | 19
DHG090* | 7.5 | 2625 | 80 | 59 | 85 | 88.9 | 0.91 | 28.01
DHG090* | 7.5 | 2625 | 80 | 63 | 85 | 90.2 | 0.84 | 26.18
DHG090* | 7.5 | 2625 | 80 | 67 | 85 | 92.9 | 0.71 | 22.77
DHG090* | 7.5 | 2625 | 80 | 71 | 85 | 97.1 | 0.6 | 19.2
DHG090* | 7.5 | 2625 | 80 | 59 | 95 | 84.8 | 0.94 | 27.73
DHG090* | 7.5 | 2625 | 80 | 63 | 95 | 86.1 | 0.87 | 25.91
DHG090* | 7.5 | 2625 | 80 | 67 | 95 | 88.8 | 0.73 | 22.5
DHG090* | 7.5 | 2625 | 80 | 71 | 95 | 93 | 0.6 | 19
DHG090* | 7.5 | 2625 | 80 | 59 | 105 | 79.7 | 1 | 27.49
DHG090* | 7.5 | 2625 | 80 | 63 | 105 | 81 | 0.91 | 25.66
DHG090* | 7.5 | 2625 | 80 | 67 | 105 | 83.8 | 0.77 | 22.25
DHG090* | 7.5 | 2625 | 80 | 71 | 105 | 87.9 | 0.6 | 18.7
DHG090* | 7.5 | 2625 | 80 | 59 | 115 | 75.2 | 1 | 26.03
DHG090* | 7.5 | 2625 | 80 | 63 | 115 | 76.4 | 1 | 26.47
DHG090* | 7.5 | 2625 | 80 | 67 | 115 | 79.2 | 0.85 | 23.4
DHG090* | 7.5 | 2625 | 80 | 71 | 115 | 83.4 | 0.7 | 19.9
DHG090* | 7.5 | 3000 | 80 | 59 | 65 | 93.3 | 0.94 | 26.7
DHG090* | 7.5 | 3000 | 80 | 63 | 65 | 94.6 | 0.87 | 24.87
DHG090* | 7.5 | 3000 | 80 | 67 | 65 | 97.3 | 0.73 | 21.46
DHG090* | 7.5 | 3000 | 80 | 71 | 65 | 101.5 | 0.6 | 17.9
DHG090* | 7.5 | 3000 | 80 | 59 | 75 | 92.5 | 0.95 | 26.65
DHG090* | 7.5 | 3000 | 80 | 63 | 75 | 93.8 | 0.87 | 24.82
DHG090* | 7.5 | 3000 | 80 | 67 | 75 | 96.5 | 0.73 | 21.41
DHG090* | 7.5 | 3000 | 80 | 71 | 75 | 100.7 | 0.6 | 17.9
DHG090* | 7.5 | 3000 | 80 | 59 | 85 | 90.1 | 0.99 | 26.91
DHG090* | 7.5 | 3000 | 80 | 63 | 85 | 91.4 | 0.91 | 25.08
DHG090* | 7.5 | 3000 | 80 | 67 | 85 | 94.1 | 0.76 | 21.67
DHG090* | 7.5 | 3000 | 80 | 71 | 85 | 98.3 | 0.6 | 18.1
DHG090* | 7.5 | 3000 | 80 | 59 | 95 | 86 | 1 | 26.05
DHG090* | 7.5 | 3000 | 80 | 63 | 95 | 87.3 | 0.94 | 24.81
DHG090* | 7.5 | 3000 | 80 | 67 | 95 | 90 | 0.78 | 21.4
DHG090* | 7.5 | 3000 | 80 | 71 | 95 | 94.2 | 0.6 | 17.9
DHG090* | 7.5 | 3000 | 80 | 59 | 105 | 80.9 | 1 | 24.53
DHG090* | 7.5 | 3000 | 80 | 63 | 105 | 82.2 | 0.99 | 24.56
DHG090* | 7.5 | 3000 | 80 | 67 | 105 | 85 | 0.82 | 21.15
DHG090* | 7.5 | 3000 | 80 | 71 | 105 | 89.2 | 0.7 | 17.6
DHG090* | 7.5 | 3000 | 80 | 59 | 115 | 76.4 | 1 | 23.14
DHG090* | 7.5 | 3000 | 80 | 63 | 115 | 77.6 | 1 | 23.53
DHG090* | 7.5 | 3000 | 80 | 67 | 115 | 80.4 | 0.92 | 22.3
DHG090* | 7.5 | 3000 | 80 | 71 | 115 | 84.6 | 0.7 | 18.8
DHG090* | 7.5 | 3375 | 80 | 59 | 65 | 94.7 | 1 | 25.52
DHG090* | 7.5 | 3375 | 80 | 63 | 65 | 96 | 0.93 | 23.95
DHG090* | 7.5 | 3375 | 80 | 67 | 65 | 98.8 | 0.77 | 20.54
DHG090* | 7.5 | 3375 | 80 | 71 | 65 | 102.9 | 0.6 | 17
DHG090* | 7.5 | 3375 | 80 | 59 | 75 | 93.9 | 1 | 25.3
DHG090* | 7.5 | 3375 | 80 | 63 | 75 | 95.2 | 0.93 | 23.9
DHG090* | 7.5 | 3375 | 80 | 67 | 75 | 97.9 | 0.78 | 20.49
DHG090* | 7.5 | 3375 | 80 | 71 | 75 | 102.1 | 0.6 | 17
DHG090* | 7.5 | 3375 | 80 | 59 | 85 | 91.5 | 1 | 24.65
DHG090* | 7.5 | 3375 | 80 | 63 | 85 | 92.8 | 0.97 | 24.15
DHG090* | 7.5 | 3375 | 80 | 67 | 85 | 95.6 | 0.81 | 20.74
DHG090* | 7.5 | 3375 | 80 | 71 | 85 | 99.7 | 0.6 | 17.2
DHG090* | 7.5 | 3375 | 80 | 59 | 95 | 87.4 | 1 | 23.55
DHG090* | 7.5 | 3375 | 80 | 63 | 95 | 88.7 | 1 | 23.88
DHG090* | 7.5 | 3375 | 80 | 67 | 95 | 91.4 | 0.83 | 20.47
DHG090* | 7.5 | 3375 | 80 | 71 | 95 | 95.6 | 0.7 | 16.9
DHG090* | 7.5 | 3375 | 80 | 59 | 105 | 82.4 | 1 | 22.19
DHG090* | 7.5 | 3375 | 80 | 63 | 105 | 83.7 | 1 | 22.54
DHG090* | 7.5 | 3375 | 80 | 67 | 105 | 86.4 | 0.87 | 20.22
DHG090* | 7.5 | 3375 | 80 | 71 | 105 | 90.6 | 0.7 | 16.7
DHG090* | 7.5 | 3375 | 80 | 59 | 115 | 77.8 | 1 | 20.96
DHG090* | 7.5 | 3375 | 80 | 63 | 115 | 79.1 | 1 | 21.3
DHG090* | 7.5 | 3375 | 80 | 67 | 115 | 81.8 | 0.97 | 21.37
DHG090* | 7.5 | 3375 | 80 | 71 | 115 | 86 | 0.8 | 17.8
DHG090* | 7.5 | 2625 | 85 | 59 | 65 | 93.6 | 0.97 | 31.39
DHG090* | 7.5 | 2625 | 85 | 63 | 65 | 94.9 | 0.9 | 29.56
DHG090* | 7.5 | 2625 | 85 | 67 | 65 | 97.7 | 0.77 | 26.15
DHG090* | 7.5 | 2625 | 85 | 71 | 65 | 101.8 | 0.6 | 22.6
DHG090* | 7.5 | 2625 | 85 | 59 | 75 | 92.8 | 0.97 | 31.34
DHG090* | 7.5 | 2625 | 85 | 63 | 75 | 94.1 | 0.91 | 29.51
DHG090* | 7.5 | 2625 | 85 | 67 | 75 | 96.8 | 0.78 | 26.1
DHG090* | 7.5 | 2625 | 85 | 71 | 75 | 101 | 0.6 | 22.6
DHG090* | 7.5 | 2625 | 85 | 59 | 85 | 90.4 | 1 | 31.32
DHG090* | 7.5 | 2625 | 85 | 63 | 85 | 91.7 | 0.94 | 29.77
DHG090* | 7.5 | 2625 | 85 | 67 | 85 | 94.5 | 0.81 | 26.36
DHG090* | 7.5 | 2625 | 85 | 71 | 85 | 98.6 | 0.7 | 22.8
DHG090* | 7.5 | 2625 | 85 | 59 | 95 | 86.3 | 1 | 29.89
DHG090* | 7.5 | 2625 | 85 | 63 | 95 | 87.6 | 0.97 | 29.49
DHG090* | 7.5 | 2625 | 85 | 67 | 95 | 90.3 | 0.83 | 26.08
DHG090* | 7.5 | 2625 | 85 | 71 | 95 | 94.5 | 0.7 | 22.6
DHG090* | 7.5 | 2625 | 85 | 59 | 105 | 81.3 | 1 | 28.15
DHG090* | 7.5 | 2625 | 85 | 63 | 105 | 82.6 | 1 | 28.6
DHG090* | 7.5 | 2625 | 85 | 67 | 105 | 85.3 | 0.87 | 25.84
DHG090* | 7.5 | 2625 | 85 | 71 | 105 | 89.5 | 0.7 | 22.3
DHG090* | 7.5 | 2625 | 85 | 59 | 115 | 76.7 | 1 | 26.56
DHG090* | 7.5 | 2625 | 85 | 63 | 115 | 78 | 1 | 27.01
DHG090* | 7.5 | 2625 | 85 | 67 | 115 | 80.7 | 0.97 | 26.98
DHG090* | 7.5 | 2625 | 85 | 71 | 115 | 84.9 | 0.8 | 23.5
DHG090* | 7.5 | 3000 | 85 | 59 | 65 | 94.8 | 1 | 28.74
DHG090* | 7.5 | 3000 | 85 | 63 | 65 | 96.1 | 0.98 | 28.46
DHG090* | 7.5 | 3000 | 85 | 67 | 65 | 98.9 | 0.84 | 25.05
DHG090* | 7.5 | 3000 | 85 | 71 | 65 | 103 | 0.7 | 21.5
DHG090* | 7.5 | 3000 | 85 | 59 | 75 | 94 | 1 | 28.49
DHG090* | 7.5 | 3000 | 85 | 63 | 75 | 95.3 | 0.98 | 28.41
DHG090* | 7.5 | 3000 | 85 | 67 | 75 | 98 | 0.84 | 25
DHG090* | 7.5 | 3000 | 85 | 71 | 75 | 102.2 | 0.7 | 21.5
DHG090* | 7.5 | 3000 | 85 | 59 | 85 | 91.6 | 1 | 27.77
DHG090* | 7.5 | 3000 | 85 | 63 | 85 | 92.9 | 1 | 28.16
DHG090* | 7.5 | 3000 | 85 | 67 | 85 | 95.7 | 0.87 | 25.26
DHG090* | 7.5 | 3000 | 85 | 71 | 85 | 99.8 | 0.7 | 21.7
DHG090* | 7.5 | 3000 | 85 | 59 | 95 | 87.5 | 1 | 26.52
DHG090* | 7.5 | 3000 | 85 | 63 | 95 | 88.8 | 1 | 26.91
DHG090* | 7.5 | 3000 | 85 | 67 | 95 | 91.5 | 0.9 | 24.98
DHG090* | 7.5 | 3000 | 85 | 71 | 95 | 95.7 | 0.7 | 21.4
DHG090* | 7.5 | 3000 | 85 | 59 | 105 | 82.5 | 1 | 25
DHG090* | 7.5 | 3000 | 85 | 63 | 105 | 83.8 | 1 | 25.39
DHG090* | 7.5 | 3000 | 85 | 67 | 105 | 86.5 | 0.94 | 24.74
DHG090* | 7.5 | 3000 | 85 | 71 | 105 | 90.7 | 0.8 | 21.2
DHG090* | 7.5 | 3000 | 85 | 59 | 115 | 77.9 | 1 | 23.61
DHG090* | 7.5 | 3000 | 85 | 63 | 115 | 79.2 | 1 | 24
DHG090* | 7.5 | 3000 | 85 | 67 | 115 | 81.9 | 1 | 24.83
DHG090* | 7.5 | 3000 | 85 | 71 | 115 | 86.1 | 0.9 | 22.3
DHG090* | 7.5 | 3375 | 85 | 59 | 65 | 96.3 | 1 | 25.93
DHG090* | 7.5 | 3375 | 85 | 63 | 65 | 97.6 | 1 | 26.28
DHG090* | 7.5 | 3375 | 85 | 67 | 65 | 100.3 | 0.89 | 24.12
DHG090* | 7.5 | 3375 | 85 | 71 | 65 | 104.5 | 0.7 | 20.6
DHG090* | 7.5 | 3375 | 85 | 59 | 75 | 95.5 | 1 | 25.71
DHG090* | 7.5 | 3375 | 85 | 63 | 75 | 96.8 | 1 | 26.06
DHG090* | 7.5 | 3375 | 85 | 67 | 75 | 99.5 | 0.9 | 24.07
DHG090* | 7.5 | 3375 | 85 | 71 | 75 | 103.7 | 0.7 | 20.5
DHG090* | 7.5 | 3375 | 85 | 59 | 85 | 93.1 | 1 | 25.07
DHG090* | 7.5 | 3375 | 85 | 63 | 85 | 94.4 | 1 | 25.42
DHG090* | 7.5 | 3375 | 85 | 67 | 85 | 97.1 | 0.93 | 24.33
DHG090* | 7.5 | 3375 | 85 | 71 | 85 | 101.3 | 0.8 | 20.8
DHG090* | 7.5 | 3375 | 85 | 59 | 95 | 89 | 1 | 23.96
DHG090* | 7.5 | 3375 | 85 | 63 | 95 | 90.3 | 1 | 24.31
DHG090* | 7.5 | 3375 | 85 | 67 | 95 | 93 | 0.96 | 24.05
DHG090* | 7.5 | 3375 | 85 | 71 | 95 | 97.2 | 0.8 | 20.5
DHG090* | 7.5 | 3375 | 85 | 59 | 105 | 83.9 | 1 | 22.61
DHG090* | 7.5 | 3375 | 85 | 63 | 105 | 85.2 | 1 | 22.96
DHG090* | 7.5 | 3375 | 85 | 67 | 105 | 88 | 1 | 23.69
DHG090* | 7.5 | 3375 | 85 | 71 | 105 | 92.1 | 0.8 | 20.3
DHG090* | 7.5 | 3375 | 85 | 59 | 115 | 79.3 | 1 | 21.37
DHG090* | 7.5 | 3375 | 85 | 63 | 115 | 80.6 | 1 | 21.72
DHG090* | 7.5 | 3375 | 85 | 67 | 115 | 83.4 | 1 | 22.46
DHG090* | 7.5 | 3375 | 85 | 71 | 115 | 87.5 | 0.9 | 21.4
DHG102* | 8.5 | 2800 | 70 | 59 | 65 | 103.9 | 0.58 | 19.55
DHG102* | 8.5 | 2800 | 70 | 63 | 65 | 105.3 | 0.52 | 17.7
DHG102* | 8.5 | 2800 | 70 | 67 | 65 | 108.4 | 0.4 | 14.24
DHG102* | 8.5 | 2800 | 70 | 59 | 75 | 102.9 | 0.58 | 19.5
DHG102* | 8.5 | 2800 | 70 | 63 | 75 | 104.4 | 0.52 | 17.65
DHG102* | 8.5 | 2800 | 70 | 67 | 75 | 107.5 | 0.41 | 14.19
DHG102* | 8.5 | 2800 | 70 | 59 | 85 | 100.2 | 0.61 | 19.76
DHG102* | 8.5 | 2800 | 70 | 63 | 85 | 101.7 | 0.54 | 17.91
DHG102* | 8.5 | 2800 | 70 | 67 | 85 | 104.8 | 0.42 | 14.45
DHG102* | 8.5 | 2800 | 70 | 59 | 95 | 95.6 | 0.63 | 19.48
DHG102* | 8.5 | 2800 | 70 | 63 | 95 | 97 | 0.56 | 17.63
DHG102* | 8.5 | 2800 | 70 | 67 | 95 | 100.1 | 0.44 | 14.17
DHG102* | 8.5 | 2800 | 70 | 59 | 105 | 89.9 | 0.66 | 19.23
DHG102* | 8.5 | 2800 | 70 | 63 | 105 | 91.3 | 0.59 | 17.38
DHG102* | 8.5 | 2800 | 70 | 67 | 105 | 94.4 | 0.45 | 13.92
DHG102* | 8.5 | 2800 | 70 | 59 | 115 | 84.7 | 0.74 | 20.39
DHG102* | 8.5 | 2800 | 70 | 63 | 115 | 86.1 | 0.66 | 18.54
DHG102* | 8.5 | 2800 | 70 | 67 | 115 | 89.2 | 0.52 | 15.08
DHG102* | 8.5 | 3025 | 70 | 59 | 65 | 104.7 | 0.6 | 18.91
DHG102* | 8.5 | 3025 | 70 | 63 | 65 | 106.1 | 0.53 | 17.06
DHG102* | 8.5 | 3025 | 70 | 67 | 65 | 109.2 | 0.41 | 13.6
DHG102* | 8.5 | 3025 | 70 | 59 | 75 | 103.7 | 0.6 | 18.86
DHG102* | 8.5 | 3025 | 70 | 63 | 75 | 105.2 | 0.54 | 17.01
DHG102* | 8.5 | 3025 | 70 | 67 | 75 | 108.3 | 0.42 | 13.55
DHG102* | 8.5 | 3025 | 70 | 59 | 85 | 101 | 0.63 | 19.12
DHG102* | 8.5 | 3025 | 70 | 63 | 85 | 102.5 | 0.56 | 17.27
DHG102* | 8.5 | 3025 | 70 | 67 | 85 | 105.6 | 0.44 | 13.81
DHG102* | 8.5 | 3025 | 70 | 59 | 95 | 96.4 | 0.65 | 18.84
DHG102* | 8.5 | 3025 | 70 | 63 | 95 | 97.8 | 0.58 | 16.99
DHG102* | 8.5 | 3025 | 70 | 67 | 95 | 100.9 | 0.45 | 13.53
DHG102* | 8.5 | 3025 | 70 | 59 | 105 | 90.7 | 0.68 | 18.59
DHG102* | 8.5 | 3025 | 70 | 63 | 105 | 92.1 | 0.6 | 16.74
DHG102* | 8.5 | 3025 | 70 | 67 | 105 | 95.2 | 0.46 | 13.28
DHG102* | 8.5 | 3025 | 70 | 59 | 115 | 85.5 | 0.77 | 19.75
DHG102* | 8.5 | 3025 | 70 | 63 | 115 | 86.9 | 0.69 | 17.9
DHG102* | 8.5 | 3025 | 70 | 67 | 115 | 90 | 0.53 | 14.44
DHG102* | 8.5 | 3600 | 70 | 59 | 65 | 107.3 | 0.65 | 17.52
DHG102* | 8.5 | 3600 | 70 | 63 | 65 | 108.7 | 0.57 | 15.67
DHG102* | 8.5 | 3600 | 70 | 67 | 65 | 111.8 | 0.43 | 12.21
DHG102* | 8.5 | 3600 | 70 | 59 | 75 | 106.3 | 0.65 | 17.47
DHG102* | 8.5 | 3600 | 70 | 63 | 75 | 107.8 | 0.57 | 15.62
DHG102* | 8.5 | 3600 | 70 | 67 | 75 | 110.9 | 0.43 | 12.16
DHG102* | 8.5 | 3600 | 70 | 59 | 85 | 103.6 | 0.68 | 17.73
DHG102* | 8.5 | 3600 | 70 | 63 | 85 | 105.1 | 0.6 | 15.88
DHG102* | 8.5 | 3600 | 70 | 67 | 85 | 108.2 | 0.45 | 12.42
DHG102* | 8.5 | 3600 | 70 | 59 | 95 | 99 | 0.7 | 17.45
DHG102* | 8.5 | 3600 | 70 | 63 | 95 | 100.4 | 0.62 | 15.6
DHG102* | 8.5 | 3600 | 70 | 67 | 95 | 103.5 | 0.46 | 12.14
DHG102* | 8.5 | 3600 | 70 | 59 | 105 | 93.3 | 0.73 | 17.21
DHG102* | 8.5 | 3600 | 70 | 63 | 105 | 94.7 | 0.64 | 15.35
DHG102* | 8.5 | 3600 | 70 | 67 | 105 | 97.8 | 0.48 | 11.9
DHG102* | 8.5 | 3600 | 70 | 59 | 115 | 88.1 | 0.83 | 18.37
DHG102* | 8.5 | 3600 | 70 | 63 | 115 | 89.5 | 0.73 | 16.51
DHG102* | 8.5 | 3600 | 70 | 67 | 115 | 92.6 | 0.56 | 13.06
DHG102* | 8.5 | 2800 | 75 | 59 | 65 | 104.4 | 0.7 | 23.62
DHG102* | 8.5 | 2800 | 75 | 63 | 65 | 105.8 | 0.63 | 21.77
DHG102* | 8.5 | 2800 | 75 | 67 | 65 | 108.9 | 0.52 | 18.31
DHG102* | 8.5 | 2800 | 75 | 71 | 65 | 113.7 | 0.4 | 14.7
DHG102* | 8.5 | 2800 | 75 | 59 | 75 | 103.4 | 0.7 | 23.57
DHG102* | 8.5 | 2800 | 75 | 63 | 75 | 104.9 | 0.64 | 21.72
DHG102* | 8.5 | 2800 | 75 | 67 | 75 | 108 | 0.52 | 18.26
DHG102* | 8.5 | 2800 | 75 | 71 | 75 | 112.7 | 0.4 | 14.7
DHG102* | 8.5 | 2800 | 75 | 59 | 85 | 100.7 | 0.73 | 23.83
DHG102* | 8.5 | 2800 | 75 | 63 | 85 | 102.2 | 0.66 | 21.98
DHG102* | 8.5 | 2800 | 75 | 67 | 85 | 105.3 | 0.54 | 18.52
DHG102* | 8.5 | 2800 | 75 | 71 | 85 | 110 | 0.4 | 14.9
DHG102* | 8.5 | 2800 | 75 | 59 | 95 | 96.1 | 0.76 | 23.55
DHG102* | 8.5 | 2800 | 75 | 63 | 95 | 97.5 | 0.69 | 21.7
DHG102* | 8.5 | 2800 | 75 | 67 | 95 | 100.6 | 0.56 | 18.24
DHG102* | 8.5 | 2800 | 75 | 71 | 95 | 105.4 | 0.4 | 14.7
DHG102* | 8.5 | 2800 | 75 | 59 | 105 | 90.4 | 0.79 | 23.3
DHG102* | 8.5 | 2800 | 75 | 63 | 105 | 91.8 | 0.72 | 21.45
DHG102* | 8.5 | 2800 | 75 | 67 | 105 | 94.9 | 0.58 | 17.99
DHG102* | 8.5 | 2800 | 75 | 71 | 105 | 99.7 | 0.4 | 14.4
DHG102* | 8.5 | 2800 | 75 | 59 | 115 | 85.2 | 0.88 | 24.46
DHG102* | 8.5 | 2800 | 75 | 63 | 115 | 86.6 | 0.8 | 22.61
DHG102* | 8.5 | 2800 | 75 | 67 | 115 | 89.7 | 0.66 | 19.15
DHG102* | 8.5 | 2800 | 75 | 71 | 115 | 94.5 | 0.5 | 15.6
DHG102* | 8.5 | 3025 | 75 | 59 | 65 | 105.2 | 0.73 | 22.98
DHG102* | 8.5 | 3025 | 75 | 63 | 65 | 106.7 | 0.66 | 21.13
DHG102* | 8.5 | 3025 | 75 | 67 | 65 | 109.8 | 0.54 | 17.67
DHG102* | 8.5 | 3025 | 75 | 71 | 65 | 114.5 | 0.4 | 14.1
DHG102* | 8.5 | 3025 | 75 | 59 | 75 | 104.3 | 0.73 | 22.93
DHG102* | 8.5 | 3025 | 75 | 63 | 75 | 105.7 | 0.66 | 21.08
DHG102* | 8.5 | 3025 | 75 | 67 | 75 | 108.8 | 0.54 | 17.62
DHG102* | 8.5 | 3025 | 75 | 71 | 75 | 113.6 | 0.4 | 14
DHG102* | 8.5 | 3025 | 75 | 59 | 85 | 101.6 | 0.76 | 23.19
DHG102* | 8.5 | 3025 | 75 | 63 | 85 | 103 | 0.69 | 21.34
DHG102* | 8.5 | 3025 | 75 | 67 | 85 | 106.1 | 0.56 | 17.88
DHG102* | 8.5 | 3025 | 75 | 71 | 85 | 110.9 | 0.4 | 14.3
DHG102* | 8.5 | 3025 | 75 | 59 | 95 | 96.9 | 0.79 | 22.91
DHG102* | 8.5 | 3025 | 75 | 63 | 95 | 98.4 | 0.71 | 21.06
DHG102* | 8.5 | 3025 | 75 | 67 | 95 | 101.5 | 0.58 | 17.6
DHG102* | 8.5 | 3025 | 75 | 71 | 95 | 106.2 | 0.4 | 14
DHG102* | 8.5 | 3025 | 75 | 59 | 105 | 91.2 | 0.83 | 22.67
DHG102* | 8.5 | 3025 | 75 | 63 | 105 | 92.7 | 0.75 | 20.81
DHG102* | 8.5 | 3025 | 75 | 67 | 105 | 95.8 | 0.6 | 17.36
DHG102* | 8.5 | 3025 | 75 | 71 | 105 | 100.5 | 0.5 | 13.8
DHG102* | 8.5 | 3025 | 75 | 59 | 115 | 86 | 0.92 | 23.83
DHG102* | 8.5 | 3025 | 75 | 63 | 115 | 87.5 | 0.84 | 21.97
DHG102* | 8.5 | 3025 | 75 | 67 | 115 | 90.6 | 0.68 | 18.51
DHG102* | 8.5 | 3025 | 75 | 71 | 115 | 95.3 | 0.5 | 14.9
DHG102* | 8.5 | 3600 | 75 | 59 | 65 | 107.8 | 0.79 | 21.6
DHG102* | 8.5 | 3600 | 75 | 63 | 65 | 109.3 | 0.72 | 19.74
DHG102* | 8.5 | 3600 | 75 | 67 | 65 | 112.4 | 0.57 | 16.29
DHG102* | 8.5 | 3600 | 75 | 71 | 65 | 117.1 | 0.4 | 12.7
DHG102* | 8.5 | 3600 | 75 | 59 | 75 | 106.9 | 0.8 | 21.55
DHG102* | 8.5 | 3600 | 75 | 63 | 75 | 108.4 | 0.72 | 19.69
DHG102* | 8.5 | 3600 | 75 | 67 | 75 | 111.5 | 0.58 | 16.23
DHG102* | 8.5 | 3600 | 75 | 71 | 75 | 116.2 | 0.4 | 12.7
DHG102* | 8.5 | 3600 | 75 | 59 | 85 | 104.2 | 0.83 | 21.81
DHG102* | 8.5 | 3600 | 75 | 63 | 85 | 105.6 | 0.75 | 19.95
DHG102* | 8.5 | 3600 | 75 | 67 | 85 | 108.7 | 0.6 | 16.49
DHG102* | 8.5 | 3600 | 75 | 71 | 85 | 113.5 | 0.5 | 12.9
DHG102* | 8.5 | 3600 | 75 | 59 | 95 | 99.5 | 0.86 | 21.53
DHG102* | 8.5 | 3600 | 75 | 63 | 95 | 101 | 0.77 | 19.67
DHG102* | 8.5 | 3600 | 75 | 67 | 95 | 104.1 | 0.62 | 16.22
DHG102* | 8.5 | 3600 | 75 | 71 | 95 | 108.8 | 0.5 | 12.6
DHG102* | 8.5 | 3600 | 75 | 59 | 105 | 93.8 | 0.9 | 21.28
DHG102* | 8.5 | 3600 | 75 | 63 | 105 | 95.3 | 0.81 | 19.43
DHG102* | 8.5 | 3600 | 75 | 67 | 105 | 98.4 | 0.64 | 15.97
DHG102* | 8.5 | 3600 | 75 | 71 | 105 | 103.1 | 0.5 | 12.4
DHG102* | 8.5 | 3600 | 75 | 59 | 115 | 88.6 | 1 | 22.38
DHG102* | 8.5 | 3600 | 75 | 63 | 115 | 90.1 | 0.91 | 20.59
DHG102* | 8.5 | 3600 | 75 | 67 | 115 | 93.2 | 0.73 | 17.13
DHG102* | 8.5 | 3600 | 75 | 71 | 115 | 97.9 | 0.5 | 13.5
DHG102* | 8.5 | 2800 | 80 | 59 | 65 | 104.9 | 0.81 | 27.72
DHG102* | 8.5 | 2800 | 80 | 63 | 65 | 106.4 | 0.75 | 25.87
DHG102* | 8.5 | 2800 | 80 | 67 | 65 | 109.5 | 0.63 | 22.41
DHG102* | 8.5 | 2800 | 80 | 71 | 65 | 114.2 | 0.5 | 18.8
DHG102* | 8.5 | 2800 | 80 | 59 | 75 | 104 | 0.82 | 27.67
DHG102* | 8.5 | 2800 | 80 | 63 | 75 | 105.4 | 0.75 | 25.82
DHG102* | 8.5 | 2800 | 80 | 67 | 75 | 108.5 | 0.63 | 22.36
DHG102* | 8.5 | 2800 | 80 | 71 | 75 | 113.3 | 0.5 | 18.8
DHG102* | 8.5 | 2800 | 80 | 59 | 85 | 101.3 | 0.85 | 27.93
DHG102* | 8.5 | 2800 | 80 | 63 | 85 | 102.7 | 0.78 | 26.08
DHG102* | 8.5 | 2800 | 80 | 67 | 85 | 105.8 | 0.66 | 22.62
DHG102* | 8.5 | 2800 | 80 | 71 | 85 | 110.6 | 0.5 | 19
DHG102* | 8.5 | 2800 | 80 | 59 | 95 | 96.6 | 0.88 | 27.65
DHG102* | 8.5 | 2800 | 80 | 63 | 95 | 98.1 | 0.81 | 25.8
DHG102* | 8.5 | 2800 | 80 | 67 | 95 | 101.2 | 0.68 | 22.34
DHG102* | 8.5 | 2800 | 80 | 71 | 95 | 105.9 | 0.5 | 18.8
DHG102* | 8.5 | 2800 | 80 | 59 | 105 | 90.9 | 0.93 | 27.41
DHG102* | 8.5 | 2800 | 80 | 63 | 105 | 92.4 | 0.85 | 25.55
DHG102* | 8.5 | 2800 | 80 | 67 | 105 | 95.5 | 0.71 | 22.09
DHG102* | 8.5 | 2800 | 80 | 71 | 105 | 100.2 | 0.6 | 18.5
DHG102* | 8.5 | 2800 | 80 | 59 | 115 | 85.7 | 1 | 27.82
DHG102* | 8.5 | 2800 | 80 | 63 | 115 | 87.2 | 0.94 | 26.71
DHG102* | 8.5 | 2800 | 80 | 67 | 115 | 90.3 | 0.79 | 23.25
DHG102* | 8.5 | 2800 | 80 | 71 | 115 | 95 | 0.6 | 19.7
DHG102* | 8.5 | 3025 | 80 | 59 | 65 | 105.7 | 0.85 | 27.08
DHG102* | 8.5 | 3025 | 80 | 63 | 65 | 107.2 | 0.78 | 25.23
DHG102* | 8.5 | 3025 | 80 | 67 | 65 | 110.3 | 0.66 | 21.77
DHG102* | 8.5 | 3025 | 80 | 71 | 65 | 115 | 0.5 | 18.2
DHG102* | 8.5 | 3025 | 80 | 59 | 75 | 104.8 | 0.86 | 27.03
DHG102* | 8.5 | 3025 | 80 | 63 | 75 | 106.3 | 0.79 | 25.18
DHG102* | 8.5 | 3025 | 80 | 67 | 75 | 109.4 | 0.66 | 21.72
DHG102* | 8.5 | 3025 | 80 | 71 | 75 | 114.1 | 0.5 | 18.1
DHG102* | 8.5 | 3025 | 80 | 59 | 85 | 102.1 | 0.89 | 27.29
DHG102* | 8.5 | 3025 | 80 | 63 | 85 | 103.6 | 0.82 | 25.44
DHG102* | 8.5 | 3025 | 80 | 67 | 85 | 106.7 | 0.69 | 21.98
DHG102* | 8.5 | 3025 | 80 | 71 | 85 | 111.4 | 0.5 | 18.4
DHG102* | 8.5 | 3025 | 80 | 59 | 95 | 97.4 | 0.92 | 27.01
DHG102* | 8.5 | 3025 | 80 | 63 | 95 | 98.9 | 0.85 | 25.16
DHG102* | 8.5 | 3025 | 80 | 67 | 95 | 102 | 0.71 | 21.7
DHG102* | 8.5 | 3025 | 80 | 71 | 95 | 106.7 | 0.6 | 18.1
DHG102* | 8.5 | 3025 | 80 | 59 | 105 | 91.7 | 0.97 | 26.77
DHG102* | 8.5 | 3025 | 80 | 63 | 105 | 93.2 | 0.89 | 24.91
DHG102* | 8.5 | 3025 | 80 | 67 | 105 | 96.3 | 0.74 | 21.46
DHG102* | 8.5 | 3025 | 80 | 71 | 105 | 101 | 0.6 | 17.9
DHG102* | 8.5 | 3025 | 80 | 59 | 115 | 86.5 | 1 | 26.01
DHG102* | 8.5 | 3025 | 80 | 63 | 115 | 88 | 0.99 | 26.07
DHG102* | 8.5 | 3025 | 80 | 67 | 115 | 91.1 | 0.83 | 22.62
DHG102* | 8.5 | 3025 | 80 | 71 | 115 | 95.8 | 0.7 | 19
DHG102* | 8.5 | 3600 | 80 | 59 | 65 | 108.4 | 0.94 | 25.7
DHG102* | 8.5 | 3600 | 80 | 63 | 65 | 109.8 | 0.86 | 23.84
DHG102* | 8.5 | 3600 | 80 | 67 | 65 | 112.9 | 0.71 | 20.39
DHG102* | 8.5 | 3600 | 80 | 71 | 65 | 117.7 | 0.6 | 16.8
DHG102* | 8.5 | 3600 | 80 | 59 | 75 | 107.4 | 0.95 | 25.65
DHG102* | 8.5 | 3600 | 80 | 63 | 75 | 108.9 | 0.87 | 23.79
DHG102* | 8.5 | 3600 | 80 | 67 | 75 | 112 | 0.72 | 20.34
DHG102* | 8.5 | 3600 | 80 | 71 | 75 | 116.7 | 0.6 | 16.8
DHG102* | 8.5 | 3600 | 80 | 59 | 85 | 104.7 | 0.98 | 25.91
DHG102* | 8.5 | 3600 | 80 | 63 | 85 | 106.2 | 0.9 | 24.05
DHG102* | 8.5 | 3600 | 80 | 67 | 85 | 109.3 | 0.75 | 20.6
DHG102* | 8.5 | 3600 | 80 | 71 | 85 | 114 | 0.6 | 17
DHG102* | 8.5 | 3600 | 80 | 59 | 95 | 100.1 | 1 | 25.27
DHG102* | 8.5 | 3600 | 80 | 63 | 95 | 101.5 | 0.93 | 23.77
DHG102* | 8.5 | 3600 | 80 | 67 | 95 | 104.6 | 0.77 | 20.32
DHG102* | 8.5 | 3600 | 80 | 71 | 95 | 109.4 | 0.6 | 16.7
DHG102* | 8.5 | 3600 | 80 | 59 | 105 | 94.4 | 1 | 23.83
DHG102* | 8.5 | 3600 | 80 | 63 | 105 | 95.8 | 0.97 | 23.53
DHG102* | 8.5 | 3600 | 80 | 67 | 105 | 98.9 | 0.8 | 20.07
DHG102* | 8.5 | 3600 | 80 | 71 | 105 | 103.7 | 0.6 | 16.5
DHG102* | 8.5 | 3600 | 80 | 59 | 115 | 89.2 | 1 | 22.51
DHG102* | 8.5 | 3600 | 80 | 63 | 115 | 90.6 | 1 | 22.88
DHG102* | 8.5 | 3600 | 80 | 67 | 115 | 93.7 | 0.9 | 21.23
DHG102* | 8.5 | 3600 | 80 | 71 | 115 | 98.5 | 0.7 | 17.6
DHG102* | 8.5 | 2800 | 85 | 59 | 65 | 106.6 | 0.91 | 31.36
DHG102* | 8.5 | 2800 | 85 | 63 | 65 | 108.1 | 0.84 | 29.51
DHG102* | 8.5 | 2800 | 85 | 67 | 65 | 111.2 | 0.72 | 26.05
DHG102* | 8.5 | 2800 | 85 | 71 | 65 | 115.9 | 0.6 | 22.5
DHG102* | 8.5 | 2800 | 85 | 59 | 75 | 105.7 | 0.91 | 31.31
DHG102* | 8.5 | 2800 | 85 | 63 | 75 | 107.2 | 0.85 | 29.46
DHG102* | 8.5 | 2800 | 85 | 67 | 75 | 110.3 | 0.73 | 26
DHG102* | 8.5 | 2800 | 85 | 71 | 75 | 115 | 0.6 | 22.4
DHG102* | 8.5 | 2800 | 85 | 59 | 85 | 103 | 0.94 | 31.57
DHG102* | 8.5 | 2800 | 85 | 63 | 85 | 104.5 | 0.88 | 29.72
DHG102* | 8.5 | 2800 | 85 | 67 | 85 | 107.6 | 0.75 | 26.26
DHG102* | 8.5 | 2800 | 85 | 71 | 85 | 112.3 | 0.6 | 22.7
DHG102* | 8.5 | 2800 | 85 | 59 | 95 | 98.3 | 0.98 | 31.29
DHG102* | 8.5 | 2800 | 85 | 63 | 95 | 99.8 | 0.91 | 29.44
DHG102* | 8.5 | 2800 | 85 | 67 | 95 | 102.9 | 0.78 | 25.98
DHG102* | 8.5 | 2800 | 85 | 71 | 95 | 107.6 | 0.6 | 22.4
DHG102* | 8.5 | 2800 | 85 | 59 | 105 | 92.6 | 1 | 30.08
DHG102* | 8.5 | 2800 | 85 | 63 | 105 | 94.1 | 0.96 | 29.19
DHG102* | 8.5 | 2800 | 85 | 67 | 105 | 97.2 | 0.82 | 25.73
DHG102* | 8.5 | 2800 | 85 | 71 | 105 | 101.9 | 0.7 | 22.1
DHG102* | 8.5 | 2800 | 85 | 59 | 115 | 87.4 | 1 | 28.39
DHG102* | 8.5 | 2800 | 85 | 63 | 115 | 88.9 | 1 | 28.87
DHG102* | 8.5 | 2800 | 85 | 67 | 115 | 92 | 0.9 | 26.89
DHG102* | 8.5 | 2800 | 85 | 71 | 115 | 96.7 | 0.7 | 23.3
DHG102* | 8.5 | 3025 | 85 | 59 | 65 | 107.5 | 0.95 | 30.72
DHG102* | 8.5 | 3025 | 85 | 63 | 65 | 108.9 | 0.88 | 28.87
DHG102* | 8.5 | 3025 | 85 | 67 | 65 | 112 | 0.75 | 25.41
DHG102* | 8.5 | 3025 | 85 | 71 | 65 | 116.8 | 0.6 | 21.8
DHG102* | 8.5 | 3025 | 85 | 59 | 75 | 106.6 | 0.96 | 30.67
DHG102* | 8.5 | 3025 | 85 | 63 | 75 | 108 | 0.89 | 28.82
DHG102* | 8.5 | 3025 | 85 | 67 | 75 | 111.1 | 0.76 | 25.36
DHG102* | 8.5 | 3025 | 85 | 71 | 75 | 115.9 | 0.6 | 21.8
DHG102* | 8.5 | 3025 | 85 | 59 | 85 | 103.8 | 0.99 | 30.93
DHG102* | 8.5 | 3025 | 85 | 63 | 85 | 105.3 | 0.92 | 29.08
DHG102* | 8.5 | 3025 | 85 | 67 | 85 | 108.4 | 0.79 | 25.62
DHG102* | 8.5 | 3025 | 85 | 71 | 85 | 113.1 | 0.6 | 22
DHG102* | 8.5 | 3025 | 85 | 59 | 95 | 99.2 | 1 | 29.81
DHG102* | 8.5 | 3025 | 85 | 63 | 95 | 100.6 | 0.95 | 28.8
DHG102* | 8.5 | 3025 | 85 | 67 | 95 | 103.7 | 0.81 | 25.34
DHG102* | 8.5 | 3025 | 85 | 71 | 95 | 108.5 | 0.7 | 21.8
DHG102* | 8.5 | 3025 | 85 | 59 | 105 | 93.5 | 1 | 28.09
DHG102* | 8.5 | 3025 | 85 | 63 | 105 | 95 | 1 | 28.53
DHG102* | 8.5 | 3025 | 85 | 67 | 105 | 98.1 | 0.85 | 25.09
DHG102* | 8.5 | 3025 | 85 | 71 | 105 | 102.8 | 0.7 | 21.5
DHG102* | 8.5 | 3025 | 85 | 59 | 115 | 88.3 | 1 | 26.53
DHG102* | 8.5 | 3025 | 85 | 63 | 115 | 89.7 | 1 | 26.97
DHG102* | 8.5 | 3025 | 85 | 67 | 115 | 92.8 | 0.94 | 26.25
DHG102* | 8.5 | 3025 | 85 | 71 | 115 | 97.6 | 0.8 | 22.7
DHG102* | 8.5 | 3600 | 85 | 59 | 65 | 110.1 | 1 | 27.8
DHG102* | 8.5 | 3600 | 85 | 63 | 65 | 111.6 | 0.98 | 27.48
DHG102* | 8.5 | 3600 | 85 | 67 | 65 | 114.7 | 0.83 | 24.02
DHG102* | 8.5 | 3600 | 85 | 71 | 65 | 119.4 | 0.7 | 20.4
DHG102* | 8.5 | 3600 | 85 | 59 | 75 | 109.2 | 1 | 27.57
DHG102* | 8.5 | 3600 | 85 | 63 | 75 | 110.6 | 0.98 | 27.43
DHG102* | 8.5 | 3600 | 85 | 67 | 75 | 113.7 | 0.83 | 23.97
DHG102* | 8.5 | 3600 | 85 | 71 | 75 | 118.5 | 0.7 | 20.4
DHG102* | 8.5 | 3600 | 85 | 59 | 85 | 106.5 | 1 | 26.88
DHG102* | 8.5 | 3600 | 85 | 63 | 85 | 107.9 | 1 | 27.25
DHG102* | 8.5 | 3600 | 85 | 67 | 85 | 111 | 0.86 | 24.23
DHG102* | 8.5 | 3600 | 85 | 71 | 85 | 115.8 | 0.7 | 20.6
DHG102* | 8.5 | 3600 | 85 | 59 | 95 | 101.8 | 1 | 25.71
DHG102* | 8.5 | 3600 | 85 | 63 | 95 | 103.3 | 1 | 26.08
DHG102* | 8.5 | 3600 | 85 | 67 | 95 | 106.4 | 0.89 | 23.95
DHG102* | 8.5 | 3600 | 85 | 71 | 95 | 111.1 | 0.7 | 20.4
DHG102* | 8.5 | 3600 | 85 | 59 | 105 | 96.1 | 1 | 24.27
DHG102* | 8.5 | 3600 | 85 | 63 | 105 | 97.6 | 1 | 24.64
DHG102* | 8.5 | 3600 | 85 | 67 | 105 | 100.7 | 0.93 | 23.71
DHG102* | 8.5 | 3600 | 85 | 71 | 105 | 105.4 | 0.8 | 20.1
DHG102* | 8.5 | 3600 | 85 | 59 | 115 | 90.9 | 1 | 22.95
DHG102* | 8.5 | 3600 | 85 | 63 | 115 | 92.4 | 1 | 23.32
DHG102* | 8.5 | 3600 | 85 | 67 | 115 | 95.5 | 1 | 24.11
DHG102* | 8.5 | 3600 | 85 | 71 | 115 | 100.2 | 0.8 | 21.3
DHG120* | 10 | 3250 | 70 | 59 | 65 | 118.6 | 0.54 | 17.91
DHG120* | 10 | 3250 | 70 | 63 | 65 | 120.3 | 0.48 | 16.21
DHG120* | 10 | 3250 | 70 | 67 | 65 | 123.8 | 0.38 | 13.04
DHG120* | 10 | 3250 | 70 | 59 | 75 | 117.6 | 0.54 | 17.87
DHG120* | 10 | 3250 | 70 | 63 | 75 | 119.3 | 0.48 | 16.17
DHG120* | 10 | 3250 | 70 | 67 | 75 | 122.8 | 0.38 | 12.99
DHG120* | 10 | 3250 | 70 | 59 | 85 | 114.5 | 0.57 | 18.11
DHG120* | 10 | 3250 | 70 | 63 | 85 | 116.2 | 0.5 | 16.41
DHG120* | 10 | 3250 | 70 | 67 | 85 | 119.7 | 0.4 | 13.23
DHG120* | 10 | 3250 | 70 | 59 | 95 | 109.2 | 0.58 | 17.85
DHG120* | 10 | 3250 | 70 | 63 | 95 | 110.9 | 0.52 | 16.15
DHG120* | 10 | 3250 | 70 | 67 | 95 | 114.4 | 0.41 | 12.98
DHG120* | 10 | 3250 | 70 | 59 | 105 | 102.7 | 0.61 | 17.62
DHG120* | 10 | 3250 | 70 | 63 | 105 | 104.4 | 0.55 | 15.92
DHG120* | 10 | 3250 | 70 | 67 | 105 | 107.9 | 0.42 | 12.75
DHG120* | 10 | 3250 | 70 | 59 | 115 | 96.8 | 0.69 | 18.69
DHG120* | 10 | 3250 | 70 | 63 | 115 | 98.5 | 0.62 | 16.99
DHG120* | 10 | 3250 | 70 | 67 | 115 | 102 | 0.48 | 13.81
DHG120* | 10 | 3500 | 70 | 59 | 65 | 119.6 | 0.56 | 17.35
DHG120* | 10 | 3500 | 70 | 63 | 65 | 121.2 | 0.5 | 15.65
DHG120* | 10 | 3500 | 70 | 67 | 65 | 124.8 | 0.39 | 12.48
DHG120* | 10 | 3500 | 70 | 59 | 75 | 118.5 | 0.56 | 17.31
DHG120* | 10 | 3500 | 70 | 63 | 75 | 120.2 | 0.5 | 15.61
DHG120* | 10 | 3500 | 70 | 67 | 75 | 123.7 | 0.39 | 12.43
DHG120* | 10 | 3500 | 70 | 59 | 85 | 115.4 | 0.59 | 17.54
DHG120* | 10 | 3500 | 70 | 63 | 85 | 117.1 | 0.52 | 15.85
DHG120* | 10 | 3500 | 70 | 67 | 85 | 120.6 | 0.4 | 12.67
DHG120* | 10 | 3500 | 70 | 59 | 95 | 110.1 | 0.6 | 17.29
DHG120* | 10 | 3500 | 70 | 63 | 95 | 111.8 | 0.54 | 15.59
DHG120* | 10 | 3500 | 70 | 67 | 95 | 115.3 | 0.41 | 12.42
DHG120* | 10 | 3500 | 70 | 59 | 105 | 103.6 | 0.63 | 17.06
DHG120* | 10 | 3500 | 70 | 63 | 105 | 105.3 | 0.56 | 15.36
DHG120* | 10 | 3500 | 70 | 67 | 105 | 108.8 | 0.43 | 12.19
DHG120* | 10 | 3500 | 70 | 59 | 115 | 97.7 | 0.71 | 18.13
DHG120* | 10 | 3500 | 70 | 63 | 115 | 99.4 | 0.64 | 16.43
DHG120* | 10 | 3500 | 70 | 67 | 115 | 102.9 | 0.5 | 13.25
DHG120* | 10 | 4150 | 70 | 59 | 65 | 122.5 | 0.6 | 16.11
DHG120* | 10 | 4150 | 70 | 63 | 65 | 124.1 | 0.53 | 14.41
DHG120* | 10 | 4150 | 70 | 67 | 65 | 127.7 | 0.4 | 11.23
DHG120* | 10 | 4150 | 70 | 59 | 75 | 121.4 | 0.6 | 16.06
DHG120* | 10 | 4150 | 70 | 63 | 75 | 123.1 | 0.53 | 14.36
DHG120* | 10 | 4150 | 70 | 67 | 75 | 126.6 | 0.4 | 11.19
DHG120* | 10 | 4150 | 70 | 59 | 85 | 118.3 | 0.63 | 16.3
DHG120* | 10 | 4150 | 70 | 63 | 85 | 120 | 0.56 | 14.6
DHG120* | 10 | 4150 | 70 | 67 | 85 | 123.5 | 0.42 | 11.43
DHG120* | 10 | 4150 | 70 | 59 | 95 | 113 | 0.65 | 16.04
DHG120* | 10 | 4150 | 70 | 63 | 95 | 114.7 | 0.57 | 14.34
DHG120* | 10 | 4150 | 70 | 67 | 95 | 118.2 | 0.43 | 11.17
DHG120* | 10 | 4150 | 70 | 59 | 105 | 106.5 | 0.68 | 15.82
DHG120* | 10 | 4150 | 70 | 63 | 105 | 108.2 | 0.6 | 14.12
DHG120* | 10 | 4150 | 70 | 67 | 105 | 111.7 | 0.45 | 10.94
DHG120* | 10 | 4150 | 70 | 59 | 115 | 100.6 | 0.77 | 16.88
DHG120* | 10 | 4150 | 70 | 63 | 115 | 102.3 | 0.68 | 15.18
DHG120* | 10 | 4150 | 70 | 67 | 115 | 105.8 | 0.52 | 12.01
DHG120* | 10 | 3250 | 75 | 59 | 65 | 118.7 | 0.65 | 21.65
DHG120* | 10 | 3250 | 75 | 63 | 65 | 120.4 | 0.59 | 19.95
DHG120* | 10 | 3250 | 75 | 67 | 65 | 123.9 | 0.48 | 16.78
DHG120* | 10 | 3250 | 75 | 71 | 65 | 129.3 | 0.4 | 13.5
DHG120* | 10 | 3250 | 75 | 59 | 75 | 117.7 | 0.66 | 21.6
DHG120* | 10 | 3250 | 75 | 63 | 75 | 119.3 | 0.6 | 19.9
DHG120* | 10 | 3250 | 75 | 67 | 75 | 122.9 | 0.49 | 16.73
DHG120* | 10 | 3250 | 75 | 71 | 75 | 128.2 | 0.4 | 13.4
DHG120* | 10 | 3250 | 75 | 59 | 85 | 114.6 | 0.68 | 21.84
DHG120* | 10 | 3250 | 75 | 63 | 85 | 116.2 | 0.62 | 20.14
DHG120* | 10 | 3250 | 75 | 67 | 85 | 119.8 | 0.51 | 16.97
DHG120* | 10 | 3250 | 75 | 71 | 85 | 125.2 | 0.4 | 13.7
DHG120* | 10 | 3250 | 75 | 59 | 95 | 109.3 | 0.71 | 21.59
DHG120* | 10 | 3250 | 75 | 63 | 95 | 110.9 | 0.64 | 19.89
DHG120* | 10 | 3250 | 75 | 67 | 95 | 114.5 | 0.52 | 16.71
DHG120* | 10 | 3250 | 75 | 71 | 95 | 119.9 | 0.4 | 13.4
DHG120* | 10 | 3250 | 75 | 59 | 105 | 102.8 | 0.74 | 21.36
DHG120* | 10 | 3250 | 75 | 63 | 105 | 104.5 | 0.67 | 19.66
DHG120* | 10 | 3250 | 75 | 67 | 105 | 108 | 0.55 | 16.49
DHG120* | 10 | 3250 | 75 | 71 | 105 | 113.4 | 0.4 | 13.2
DHG120* | 10 | 3250 | 75 | 59 | 115 | 96.9 | 0.83 | 22.42
DHG120* | 10 | 3250 | 75 | 63 | 115 | 98.5 | 0.75 | 20.72
DHG120* | 10 | 3250 | 75 | 67 | 115 | 102.1 | 0.61 | 17.55
DHG120* | 10 | 3250 | 75 | 71 | 115 | 107.5 | 0.5 | 14.3
DHG120* | 10 | 3500 | 75 | 59 | 65 | 119.6 | 0.68 | 21.09
DHG120* | 10 | 3500 | 75 | 63 | 65 | 121.3 | 0.62 | 19.39
DHG120* | 10 | 3500 | 75 | 67 | 65 | 124.8 | 0.5 | 16.22
DHG120* | 10 | 3500 | 75 | 71 | 65 | 130.2 | 0.4 | 12.9
DHG120* | 10 | 3500 | 75 | 59 | 75 | 118.6 | 0.68 | 21.04
DHG120* | 10 | 3500 | 75 | 63 | 75 | 120.2 | 0.62 | 19.34
DHG120* | 10 | 3500 | 75 | 67 | 75 | 123.8 | 0.5 | 16.17
DHG120* | 10 | 3500 | 75 | 71 | 75 | 129.2 | 0.4 | 12.9
DHG120* | 10 | 3500 | 75 | 59 | 85 | 115.5 | 0.71 | 21.28
DHG120* | 10 | 3500 | 75 | 63 | 85 | 117.2 | 0.64 | 19.58
DHG120* | 10 | 3500 | 75 | 67 | 85 | 120.7 | 0.52 | 16.41
DHG120* | 10 | 3500 | 75 | 71 | 85 | 126.1 | 0.4 | 13.1
DHG120* | 10 | 3500 | 75 | 59 | 95 | 110.2 | 0.73 | 21.03
DHG120* | 10 | 3500 | 75 | 63 | 95 | 111.9 | 0.67 | 19.33
DHG120* | 10 | 3500 | 75 | 67 | 95 | 115.4 | 0.54 | 16.15
DHG120* | 10 | 3500 | 75 | 71 | 95 | 120.8 | 0.4 | 12.9
DHG120* | 10 | 3500 | 75 | 59 | 105 | 103.7 | 0.77 | 20.8
DHG120* | 10 | 3500 | 75 | 63 | 105 | 105.4 | 0.7 | 19.1
DHG120* | 10 | 3500 | 75 | 67 | 105 | 108.9 | 0.56 | 15.93
DHG120* | 10 | 3500 | 75 | 71 | 105 | 114.3 | 0.4 | 12.6
DHG120* | 10 | 3500 | 75 | 59 | 115 | 97.8 | 0.86 | 21.86
DHG120* | 10 | 3500 | 75 | 63 | 115 | 99.5 | 0.78 | 20.16
DHG120* | 10 | 3500 | 75 | 67 | 115 | 103 | 0.64 | 16.99
DHG120* | 10 | 3500 | 75 | 71 | 115 | 108.4 | 0.5 | 13.7
DHG120* | 10 | 4150 | 75 | 59 | 65 | 122.5 | 0.74 | 19.84
DHG120* | 10 | 4150 | 75 | 63 | 65 | 124.2 | 0.67 | 18.14
DHG120* | 10 | 4150 | 75 | 67 | 65 | 127.7 | 0.54 | 14.97
DHG120* | 10 | 4150 | 75 | 71 | 65 | 133.1 | 0.4 | 11.7
DHG120* | 10 | 4150 | 75 | 59 | 75 | 121.5 | 0.74 | 19.8
DHG120* | 10 | 4150 | 75 | 63 | 75 | 123.1 | 0.67 | 18.1
DHG120* | 10 | 4150 | 75 | 67 | 75 | 126.7 | 0.54 | 14.92
DHG120* | 10 | 4150 | 75 | 71 | 75 | 132.1 | 0.4 | 11.6
DHG120* | 10 | 4150 | 75 | 59 | 85 | 118.4 | 0.77 | 20.04
DHG120* | 10 | 4150 | 75 | 63 | 85 | 120.1 | 0.7 | 18.34
DHG120* | 10 | 4150 | 75 | 67 | 85 | 123.6 | 0.56 | 15.16
DHG120* | 10 | 4150 | 75 | 71 | 85 | 129 | 0.4 | 11.9
DHG120* | 10 | 4150 | 75 | 59 | 95 | 113.1 | 0.8 | 19.78
DHG120* | 10 | 4150 | 75 | 63 | 95 | 114.8 | 0.72 | 18.08
DHG120* | 10 | 4150 | 75 | 67 | 95 | 118.3 | 0.58 | 14.91
DHG120* | 10 | 4150 | 75 | 71 | 95 | 123.7 | 0.4 | 11.6
DHG120* | 10 | 4150 | 75 | 59 | 105 | 106.6 | 0.84 | 19.55
DHG120* | 10 | 4150 | 75 | 63 | 105 | 108.3 | 0.75 | 17.85
DHG120* | 10 | 4150 | 75 | 67 | 105 | 111.8 | 0.6 | 14.68
DHG120* | 10 | 4150 | 75 | 71 | 105 | 117.2 | 0.4 | 11.4
DHG120* | 10 | 4150 | 75 | 59 | 115 | 100.7 | 0.93 | 20.62
DHG120* | 10 | 4150 | 75 | 63 | 115 | 102.4 | 0.84 | 18.92
DHG120* | 10 | 4150 | 75 | 67 | 115 | 105.9 | 0.68 | 15.74
DHG120* | 10 | 4150 | 75 | 71 | 115 | 111.3 | 0.5 | 12.5
DHG120* | 10 | 3250 | 80 | 59 | 65 | 119.3 | 0.76 | 25.41
DHG120* | 10 | 3250 | 80 | 63 | 65 | 121 | 0.7 | 23.71
DHG120* | 10 | 3250 | 80 | 67 | 65 | 124.5 | 0.59 | 20.54
DHG120* | 10 | 3250 | 80 | 71 | 65 | 129.9 | 0.5 | 17.3
DHG120* | 10 | 3250 | 80 | 59 | 75 | 118.3 | 0.77 | 25.37
DHG120* | 10 | 3250 | 80 | 63 | 75 | 119.9 | 0.71 | 23.67
DHG120* | 10 | 3250 | 80 | 67 | 75 | 123.5 | 0.59 | 20.49
DHG120* | 10 | 3250 | 80 | 71 | 75 | 128.8 | 0.5 | 17.2
DHG120* | 10 | 3250 | 80 | 59 | 85 | 115.2 | 0.79 | 25.61
DHG120* | 10 | 3250 | 80 | 63 | 85 | 116.9 | 0.73 | 23.91
DHG120* | 10 | 3250 | 80 | 67 | 85 | 120.4 | 0.62 | 20.73
DHG120* | 10 | 3250 | 80 | 71 | 85 | 125.8 | 0.5 | 17.4
DHG120* | 10 | 3250 | 80 | 59 | 95 | 109.9 | 0.82 | 25.35
DHG120* | 10 | 3250 | 80 | 63 | 95 | 111.6 | 0.76 | 23.65
DHG120* | 10 | 3250 | 80 | 67 | 95 | 115.1 | 0.64 | 20.48
DHG120* | 10 | 3250 | 80 | 71 | 95 | 120.5 | 0.5 | 17.2
DHG120* | 10 | 3250 | 80 | 59 | 105 | 103.4 | 0.87 | 25.12
DHG120* | 10 | 3250 | 80 | 63 | 105 | 105.1 | 0.8 | 23.42
DHG120* | 10 | 3250 | 80 | 67 | 105 | 108.6 | 0.67 | 20.25
DHG120* | 10 | 3250 | 80 | 71 | 105 | 114 | 0.5 | 17
DHG120* | 10 | 3250 | 80 | 59 | 115 | 97.5 | 0.96 | 26.19
DHG120* | 10 | 3250 | 80 | 63 | 115 | 99.2 | 0.88 | 24.49
DHG120* | 10 | 3250 | 80 | 67 | 115 | 102.7 | 0.74 | 21.31
DHG120* | 10 | 3250 | 80 | 71 | 115 | 108.1 | 0.6 | 18
DHG120* | 10 | 3500 | 80 | 59 | 65 | 120.2 | 0.8 | 24.85
DHG120* | 10 | 3500 | 80 | 63 | 65 | 121.9 | 0.73 | 23.15
DHG120* | 10 | 3500 | 80 | 67 | 65 | 125.4 | 0.61 | 19.98
DHG120* | 10 | 3500 | 80 | 71 | 65 | 130.8 | 0.5 | 16.7
DHG120* | 10 | 3500 | 80 | 59 | 75 | 119.2 | 0.8 | 24.81
DHG120* | 10 | 3500 | 80 | 63 | 75 | 120.9 | 0.74 | 23.11
DHG120* | 10 | 3500 | 80 | 67 | 75 | 124.4 | 0.62 | 19.93
DHG120* | 10 | 3500 | 80 | 71 | 75 | 129.8 | 0.5 | 16.6
DHG120* | 10 | 3500 | 80 | 59 | 85 | 116.1 | 0.83 | 25.04
DHG120* | 10 | 3500 | 80 | 63 | 85 | 117.8 | 0.76 | 23.35
DHG120* | 10 | 3500 | 80 | 67 | 85 | 121.3 | 0.64 | 20.17
DHG120* | 10 | 3500 | 80 | 71 | 85 | 126.7 | 0.5 | 16.9
DHG120* | 10 | 3500 | 80 | 59 | 95 | 110.8 | 0.86 | 24.79
DHG120* | 10 | 3500 | 80 | 63 | 95 | 112.5 | 0.79 | 23.09
DHG120* | 10 | 3500 | 80 | 67 | 95 | 116 | 0.66 | 19.92
DHG120* | 10 | 3500 | 80 | 71 | 95 | 121.4 | 0.5 | 16.6
DHG120* | 10 | 3500 | 80 | 59 | 105 | 104.3 | 0.91 | 24.56
DHG120* | 10 | 3500 | 80 | 63 | 105 | 106 | 0.83 | 22.86
DHG120* | 10 | 3500 | 80 | 67 | 105 | 109.5 | 0.69 | 19.69
DHG120* | 10 | 3500 | 80 | 71 | 105 | 114.9 | 0.5 | 16.4
DHG120* | 10 | 3500 | 80 | 59 | 115 | 98.4 | 1 | 25.56
DHG120* | 10 | 3500 | 80 | 63 | 115 | 100.1 | 0.92 | 23.93
DHG120* | 10 | 3500 | 80 | 67 | 115 | 103.6 | 0.77 | 20.75
DHG120* | 10 | 3500 | 80 | 71 | 115 | 109 | 0.6 | 17.5
DHG120* | 10 | 4150 | 80 | 59 | 65 | 123.1 | 0.88 | 23.61
DHG120* | 10 | 4150 | 80 | 63 | 65 | 124.8 | 0.8 | 21.91
DHG120* | 10 | 4150 | 80 | 67 | 65 | 128.3 | 0.67 | 18.73
DHG120* | 10 | 4150 | 80 | 71 | 65 | 133.7 | 0.5 | 15.4
DHG120* | 10 | 4150 | 80 | 59 | 75 | 122.1 | 0.88 | 23.56
DHG120* | 10 | 4150 | 80 | 63 | 75 | 123.8 | 0.81 | 21.86
DHG120* | 10 | 4150 | 80 | 67 | 75 | 127.3 | 0.67 | 18.69
DHG120* | 10 | 4150 | 80 | 71 | 75 | 132.7 | 0.5 | 15.4
DHG120* | 10 | 4150 | 80 | 59 | 85 | 119 | 0.91 | 23.8
DHG120* | 10 | 4150 | 80 | 63 | 85 | 120.7 | 0.84 | 22.1
DHG120* | 10 | 4150 | 80 | 67 | 85 | 124.2 | 0.7 | 18.93
DHG120* | 10 | 4150 | 80 | 71 | 85 | 129.6 | 0.6 | 15.6
DHG120* | 10 | 4150 | 80 | 59 | 95 | 113.7 | 0.95 | 23.54
DHG120* | 10 | 4150 | 80 | 63 | 95 | 115.4 | 0.86 | 21.84
DHG120* | 10 | 4150 | 80 | 67 | 95 | 118.9 | 0.72 | 18.67
DHG120* | 10 | 4150 | 80 | 71 | 95 | 124.3 | 0.6 | 15.4
DHG120* | 10 | 4150 | 80 | 59 | 105 | 107.2 | 0.99 | 23.32
DHG120* | 10 | 4150 | 80 | 63 | 105 | 108.9 | 0.91 | 21.62
DHG120* | 10 | 4150 | 80 | 67 | 105 | 112.4 | 0.75 | 18.44
DHG120* | 10 | 4150 | 80 | 71 | 105 | 117.8 | 0.6 | 15.2
DHG120* | 10 | 4150 | 80 | 59 | 115 | 101.3 | 1 | 22.19
DHG120* | 10 | 4150 | 80 | 63 | 115 | 103 | 1 | 22.56
DHG120* | 10 | 4150 | 80 | 67 | 115 | 106.5 | 0.84 | 19.51
DHG120* | 10 | 4150 | 80 | 71 | 115 | 111.9 | 0.7 | 16.2
DHG120* | 10 | 3250 | 85 | 59 | 65 | 121.3 | 0.85 | 28.75
DHG120* | 10 | 3250 | 85 | 63 | 65 | 123 | 0.79 | 27.05
DHG120* | 10 | 3250 | 85 | 67 | 65 | 126.5 | 0.67 | 23.88
DHG120* | 10 | 3250 | 85 | 71 | 65 | 131.9 | 0.6 | 20.6
DHG120* | 10 | 3250 | 85 | 59 | 75 | 120.3 | 0.85 | 28.7
DHG120* | 10 | 3250 | 85 | 63 | 75 | 121.9 | 0.79 | 27
DHG120* | 10 | 3250 | 85 | 67 | 75 | 125.5 | 0.68 | 23.83
DHG120* | 10 | 3250 | 85 | 71 | 75 | 130.8 | 0.6 | 20.5
DHG120* | 10 | 3250 | 85 | 59 | 85 | 117.2 | 0.88 | 28.94
DHG120* | 10 | 3250 | 85 | 63 | 85 | 118.8 | 0.82 | 27.24
DHG120* | 10 | 3250 | 85 | 67 | 85 | 122.4 | 0.7 | 24.07
DHG120* | 10 | 3250 | 85 | 71 | 85 | 127.8 | 0.6 | 20.8
DHG120* | 10 | 3250 | 85 | 59 | 95 | 111.9 | 0.92 | 28.69
DHG120* | 10 | 3250 | 85 | 63 | 95 | 113.5 | 0.85 | 26.99
DHG120* | 10 | 3250 | 85 | 67 | 95 | 117.1 | 0.73 | 23.81
DHG120* | 10 | 3250 | 85 | 71 | 95 | 122.5 | 0.6 | 20.5
DHG120* | 10 | 3250 | 85 | 59 | 105 | 105.4 | 0.97 | 28.46
DHG120* | 10 | 3250 | 85 | 63 | 105 | 107.1 | 0.89 | 26.76
DHG120* | 10 | 3250 | 85 | 67 | 105 | 110.6 | 0.76 | 23.59
DHG120* | 10 | 3250 | 85 | 71 | 105 | 116 | 0.6 | 20.3
DHG120* | 10 | 3250 | 85 | 59 | 115 | 99.5 | 1 | 27.83
DHG120* | 10 | 3250 | 85 | 63 | 115 | 101.1 | 0.98 | 27.82
DHG120* | 10 | 3250 | 85 | 67 | 115 | 104.7 | 0.84 | 24.65
DHG120* | 10 | 3250 | 85 | 71 | 115 | 110.1 | 0.7 | 21.4
DHG120* | 10 | 3500 | 85 | 59 | 65 | 122.2 | 0.89 | 28.19
DHG120* | 10 | 3500 | 85 | 63 | 65 | 123.9 | 0.82 | 26.49
DHG120* | 10 | 3500 | 85 | 67 | 65 | 127.4 | 0.7 | 23.32
DHG120* | 10 | 3500 | 85 | 71 | 65 | 132.8 | 0.6 | 20
DHG120* | 10 | 3500 | 85 | 59 | 75 | 121.2 | 0.89 | 28.14
DHG120* | 10 | 3500 | 85 | 63 | 75 | 122.8 | 0.83 | 26.44
DHG120* | 10 | 3500 | 85 | 67 | 75 | 126.4 | 0.71 | 23.27
DHG120* | 10 | 3500 | 85 | 71 | 75 | 131.8 | 0.6 | 20
DHG120* | 10 | 3500 | 85 | 59 | 85 | 118.1 | 0.93 | 28.38
DHG120* | 10 | 3500 | 85 | 63 | 85 | 119.8 | 0.86 | 26.68
DHG120* | 10 | 3500 | 85 | 67 | 85 | 123.3 | 0.73 | 23.51
DHG120* | 10 | 3500 | 85 | 71 | 85 | 128.7 | 0.6 | 20.2
DHG120* | 10 | 3500 | 85 | 59 | 95 | 112.8 | 0.96 | 28.13
DHG120* | 10 | 3500 | 85 | 63 | 95 | 114.5 | 0.89 | 26.43
DHG120* | 10 | 3500 | 85 | 67 | 95 | 118 | 0.76 | 23.25
DHG120* | 10 | 3500 | 85 | 71 | 95 | 123.4 | 0.6 | 20
DHG120* | 10 | 3500 | 85 | 59 | 105 | 106.3 | 1 | 27.61
DHG120* | 10 | 3500 | 85 | 63 | 105 | 108 | 0.93 | 26.2
DHG120* | 10 | 3500 | 85 | 67 | 105 | 111.5 | 0.79 | 23.03
DHG120* | 10 | 3500 | 85 | 71 | 105 | 116.9 | 0.7 | 19.7
DHG120* | 10 | 3500 | 85 | 59 | 115 | 100.4 | 1 | 26.08
DHG120* | 10 | 3500 | 85 | 63 | 115 | 102.1 | 1 | 26.51
DHG120* | 10 | 3500 | 85 | 67 | 115 | 105.6 | 0.88 | 24.09
DHG120* | 10 | 3500 | 85 | 71 | 115 | 111 | 0.7 | 20.8
DHG120* | 10 | 4150 | 85 | 59 | 65 | 125.1 | 0.98 | 26.94
DHG120* | 10 | 4150 | 85 | 63 | 65 | 126.8 | 0.91 | 25.24
DHG120* | 10 | 4150 | 85 | 67 | 65 | 130.3 | 0.77 | 22.07
DHG120* | 10 | 4150 | 85 | 71 | 65 | 135.7 | 0.6 | 18.8
DHG120* | 10 | 4150 | 85 | 59 | 75 | 124.1 | 0.99 | 26.9
DHG120* | 10 | 4150 | 85 | 63 | 75 | 125.7 | 0.91 | 25.2
DHG120* | 10 | 4150 | 85 | 67 | 75 | 129.3 | 0.78 | 22.02
DHG120* | 10 | 4150 | 85 | 71 | 75 | 134.7 | 0.6 | 18.7
DHG120* | 10 | 4150 | 85 | 59 | 85 | 121 | 1 | 26.51
DHG120* | 10 | 4150 | 85 | 63 | 85 | 122.7 | 0.95 | 25.44
DHG120* | 10 | 4150 | 85 | 67 | 85 | 126.2 | 0.81 | 22.26
DHG120* | 10 | 4150 | 85 | 71 | 85 | 131.6 | 0.7 | 19
DHG120* | 10 | 4150 | 85 | 59 | 95 | 115.7 | 1 | 25.34
DHG120* | 10 | 4150 | 85 | 63 | 95 | 117.4 | 0.98 | 25.18
DHG120* | 10 | 4150 | 85 | 67 | 95 | 120.9 | 0.83 | 22.01
DHG120* | 10 | 4150 | 85 | 71 | 95 | 126.3 | 0.7 | 18.7
DHG120* | 10 | 4150 | 85 | 59 | 105 | 109.2 | 1 | 23.92
DHG120* | 10 | 4150 | 85 | 63 | 105 | 110.9 | 1 | 24.29
DHG120* | 10 | 4150 | 85 | 67 | 105 | 114.4 | 0.87 | 21.78
DHG120* | 10 | 4150 | 85 | 71 | 105 | 119.8 | 0.7 | 18.5
DHG120* | 10 | 4150 | 85 | 59 | 115 | 103.3 | 1 | 22.63
DHG120* | 10 | 4150 | 85 | 63 | 115 | 105 | 1 | 22.99
DHG120* | 10 | 4150 | 85 | 67 | 115 | 108.5 | 0.96 | 22.84
DHG120* | 10 | 4150 | 85 | 71 | 115 | 113.9 | 0.8 | 19.6
DHG150* | 12.5 | 3500 | 70 | 59 | 65 | 140.4 | 0.58 | 21.08
DHG150* | 12.5 | 3500 | 70 | 63 | 65 | 142.4 | 0.52 | 19.09
DHG150* | 12.5 | 3500 | 70 | 67 | 65 | 146.6 | 0.4 | 15.37
DHG150* | 12.5 | 3500 | 70 | 59 | 75 | 139.2 | 0.58 | 21.03
DHG150* | 12.5 | 3500 | 70 | 63 | 75 | 141.1 | 0.52 | 19.04
DHG150* | 12.5 | 3500 | 70 | 67 | 75 | 145.3 | 0.41 | 15.31
DHG150* | 12.5 | 3500 | 70 | 59 | 85 | 135.5 | 0.61 | 21.31
DHG150* | 12.5 | 3500 | 70 | 63 | 85 | 137.5 | 0.54 | 19.32
DHG150* | 12.5 | 3500 | 70 | 67 | 85 | 141.7 | 0.42 | 15.59
DHG150* | 12.5 | 3500 | 70 | 59 | 95 | 129.2 | 0.63 | 21.01
DHG150* | 12.5 | 3500 | 70 | 63 | 95 | 131.2 | 0.56 | 19.02
DHG150* | 12.5 | 3500 | 70 | 67 | 95 | 135.4 | 0.43 | 15.29
DHG150* | 12.5 | 3500 | 70 | 59 | 105 | 121.5 | 0.66 | 20.74
DHG150* | 12.5 | 3500 | 70 | 63 | 105 | 123.5 | 0.58 | 18.75
DHG150* | 12.5 | 3500 | 70 | 67 | 105 | 127.7 | 0.45 | 15.03
DHG150* | 12.5 | 3500 | 70 | 59 | 115 | 114.4 | 0.74 | 21.99
DHG150* | 12.5 | 3500 | 70 | 63 | 115 | 116.4 | 0.66 | 20
DHG150* | 12.5 | 3500 | 70 | 67 | 115 | 120.6 | 0.52 | 16.28
DHG150* | 12.5 | 3800 | 70 | 59 | 65 | 141.5 | 0.6 | 20.35
DHG150* | 12.5 | 3800 | 70 | 63 | 65 | 143.5 | 0.53 | 18.36
DHG150* | 12.5 | 3800 | 70 | 67 | 65 | 147.7 | 0.41 | 14.64
DHG150* | 12.5 | 3800 | 70 | 59 | 75 | 140.3 | 0.6 | 20.3
DHG150* | 12.5 | 3800 | 70 | 63 | 75 | 142.3 | 0.54 | 18.3
DHG150* | 12.5 | 3800 | 70 | 67 | 75 | 146.4 | 0.42 | 14.58
DHG150* | 12.5 | 3800 | 70 | 59 | 85 | 136.6 | 0.63 | 20.58
DHG150* | 12.5 | 3800 | 70 | 63 | 85 | 138.6 | 0.56 | 18.58
DHG150* | 12.5 | 3800 | 70 | 67 | 85 | 142.8 | 0.44 | 14.86
DHG150* | 12.5 | 3800 | 70 | 59 | 95 | 130.3 | 0.65 | 20.28
DHG150* | 12.5 | 3800 | 70 | 63 | 95 | 132.3 | 0.58 | 18.28
DHG150* | 12.5 | 3800 | 70 | 67 | 95 | 136.5 | 0.45 | 14.56
DHG150* | 12.5 | 3800 | 70 | 59 | 105 | 122.6 | 0.68 | 20.01
DHG150* | 12.5 | 3800 | 70 | 63 | 105 | 124.6 | 0.6 | 18.02
DHG150* | 12.5 | 3800 | 70 | 67 | 105 | 128.8 | 0.46 | 14.29
DHG150* | 12.5 | 3800 | 70 | 59 | 115 | 115.5 | 0.77 | 21.26
DHG150* | 12.5 | 3800 | 70 | 63 | 115 | 117.5 | 0.69 | 19.27
DHG150* | 12.5 | 3800 | 70 | 67 | 115 | 121.7 | 0.53 | 15.54
DHG150* | 12.5 | 4500 | 70 | 59 | 65 | 144.9 | 0.65 | 18.9
DHG150* | 12.5 | 4500 | 70 | 63 | 65 | 146.9 | 0.57 | 16.91
DHG150* | 12.5 | 4500 | 70 | 67 | 65 | 151.1 | 0.43 | 13.19
DHG150* | 12.5 | 4500 | 70 | 59 | 75 | 143.7 | 0.65 | 18.85
DHG150* | 12.5 | 4500 | 70 | 63 | 75 | 145.7 | 0.57 | 16.85
DHG150* | 12.5 | 4500 | 70 | 67 | 75 | 149.9 | 0.43 | 13.13
DHG150* | 12.5 | 4500 | 70 | 59 | 85 | 140 | 0.68 | 19.13
DHG150* | 12.5 | 4500 | 70 | 63 | 85 | 142 | 0.6 | 17.13
DHG150* | 12.5 | 4500 | 70 | 67 | 85 | 146.2 | 0.45 | 13.41
DHG150* | 12.5 | 4500 | 70 | 59 | 95 | 133.7 | 0.7 | 18.83
DHG150* | 12.5 | 4500 | 70 | 63 | 95 | 135.7 | 0.61 | 16.83
DHG150* | 12.5 | 4500 | 70 | 67 | 95 | 139.9 | 0.46 | 13.11
DHG150* | 12.5 | 4500 | 70 | 59 | 105 | 126 | 0.73 | 18.56
DHG150* | 12.5 | 4500 | 70 | 63 | 105 | 128 | 0.64 | 16.57
DHG150* | 12.5 | 4500 | 70 | 67 | 105 | 132.2 | 0.48 | 12.84
DHG150* | 12.5 | 4500 | 70 | 59 | 115 | 119 | 0.82 | 19.81
DHG150* | 12.5 | 4500 | 70 | 63 | 115 | 120.9 | 0.73 | 17.81
DHG150* | 12.5 | 4500 | 70 | 67 | 115 | 125.1 | 0.56 | 14.09
DHG150* | 12.5 | 3500 | 75 | 59 | 65 | 141.1 | 0.69 | 25.47
DHG150* | 12.5 | 3500 | 75 | 63 | 65 | 143.1 | 0.63 | 23.47
DHG150* | 12.5 | 3500 | 75 | 67 | 65 | 147.3 | 0.52 | 19.75
DHG150* | 12.5 | 3500 | 75 | 71 | 65 | 153.7 | 0.4 | 15.9
DHG150* | 12.5 | 3500 | 75 | 59 | 75 | 139.9 | 0.7 | 25.41
DHG150* | 12.5 | 3500 | 75 | 63 | 75 | 141.8 | 0.64 | 23.42
DHG150* | 12.5 | 3500 | 75 | 67 | 75 | 146 | 0.52 | 19.7
DHG150* | 12.5 | 3500 | 75 | 71 | 75 | 152.4 | 0.4 | 15.8
DHG150* | 12.5 | 3500 | 75 | 59 | 85 | 136.2 | 0.73 | 25.69
DHG150* | 12.5 | 3500 | 75 | 63 | 85 | 138.2 | 0.66 | 23.7
DHG150* | 12.5 | 3500 | 75 | 67 | 85 | 142.4 | 0.54 | 19.98
DHG150* | 12.5 | 3500 | 75 | 71 | 85 | 148.8 | 0.42 | 16.1
DHG150* | 12.5 | 3500 | 75 | 59 | 95 | 129.9 | 0.75 | 25.39
DHG150* | 12.5 | 3500 | 75 | 63 | 95 | 131.9 | 0.68 | 23.4
DHG150* | 12.5 | 3500 | 75 | 67 | 95 | 136.1 | 0.56 | 19.68
DHG150* | 12.5 | 3500 | 75 | 71 | 95 | 142.5 | 0.43 | 15.8
DHG150* | 12.5 | 3500 | 75 | 59 | 105 | 122.2 | 0.79 | 25.13
DHG150* | 12.5 | 3500 | 75 | 63 | 105 | 124.2 | 0.72 | 23.13
DHG150* | 12.5 | 3500 | 75 | 67 | 105 | 128.4 | 0.58 | 19.41
DHG150* | 12.5 | 3500 | 75 | 71 | 105 | 134.8 | 0.44 | 15.6
DHG150* | 12.5 | 3500 | 75 | 59 | 115 | 115.1 | 0.88 | 26.37
DHG150* | 12.5 | 3500 | 75 | 63 | 115 | 117.1 | 0.8 | 24.38
DHG150* | 12.5 | 3500 | 75 | 67 | 115 | 121.3 | 0.66 | 20.66
DHG150* | 12.5 | 3500 | 75 | 71 | 115 | 127.7 | 0.51 | 16.8
DHG150* | 12.5 | 3800 | 75 | 59 | 65 | 142.3 | 0.73 | 24.74
DHG150* | 12.5 | 3800 | 75 | 63 | 65 | 144.3 | 0.66 | 22.74
DHG150* | 12.5 | 3800 | 75 | 67 | 65 | 148.5 | 0.54 | 19.02
DHG150* | 12.5 | 3800 | 75 | 71 | 65 | 154.9 | 0.41 | 15.2
DHG150* | 12.5 | 3800 | 75 | 59 | 75 | 141.1 | 0.73 | 24.68
DHG150* | 12.5 | 3800 | 75 | 63 | 75 | 143.1 | 0.66 | 22.69
DHG150* | 12.5 | 3800 | 75 | 67 | 75 | 147.2 | 0.54 | 18.96
DHG150* | 12.5 | 3800 | 75 | 71 | 75 | 153.7 | 0.41 | 15.1
DHG150* | 12.5 | 3800 | 75 | 59 | 85 | 137.4 | 0.76 | 24.96
DHG150* | 12.5 | 3800 | 75 | 63 | 85 | 139.4 | 0.69 | 22.97
DHG150* | 12.5 | 3800 | 75 | 67 | 85 | 143.6 | 0.56 | 19.24
DHG150* | 12.5 | 3800 | 75 | 71 | 85 | 150 | 0.43 | 15.4
DHG150* | 12.5 | 3800 | 75 | 59 | 95 | 131.1 | 0.79 | 24.66
DHG150* | 12.5 | 3800 | 75 | 63 | 95 | 133.1 | 0.71 | 22.67
DHG150* | 12.5 | 3800 | 75 | 67 | 95 | 137.3 | 0.58 | 18.94
DHG150* | 12.5 | 3800 | 75 | 71 | 95 | 143.7 | 0.44 | 15.1
DHG150* | 12.5 | 3800 | 75 | 59 | 105 | 123.4 | 0.83 | 24.39
DHG150* | 12.5 | 3800 | 75 | 63 | 105 | 125.4 | 0.75 | 22.4
DHG150* | 12.5 | 3800 | 75 | 67 | 105 | 129.6 | 0.6 | 18.68
DHG150* | 12.5 | 3800 | 75 | 71 | 105 | 136 | 0.46 | 14.8
DHG150* | 12.5 | 3800 | 75 | 59 | 115 | 116.3 | 0.92 | 25.64
DHG150* | 12.5 | 3800 | 75 | 63 | 115 | 118.3 | 0.84 | 23.65
DHG150* | 12.5 | 3800 | 75 | 67 | 115 | 122.5 | 0.68 | 19.93
DHG150* | 12.5 | 3800 | 75 | 71 | 115 | 128.9 | 0.52 | 16.1
DHG150* | 12.5 | 4500 | 75 | 59 | 65 | 145.7 | 0.79 | 23.28
DHG150* | 12.5 | 4500 | 75 | 63 | 65 | 147.7 | 0.71 | 21.29
DHG150* | 12.5 | 4500 | 75 | 67 | 65 | 151.9 | 0.57 | 17.57
DHG150* | 12.5 | 4500 | 75 | 71 | 65 | 158.3 | 0.43 | 13.7
DHG150* | 12.5 | 4500 | 75 | 59 | 75 | 144.5 | 0.8 | 23.23
DHG150* | 12.5 | 4500 | 75 | 63 | 75 | 146.5 | 0.72 | 21.24
DHG150* | 12.5 | 4500 | 75 | 67 | 75 | 150.7 | 0.58 | 17.51
DHG150* | 12.5 | 4500 | 75 | 71 | 75 | 157.1 | 0.43 | 13.7
DHG150* | 12.5 | 4500 | 75 | 59 | 85 | 140.8 | 0.83 | 23.51
DHG150* | 12.5 | 4500 | 75 | 63 | 85 | 142.8 | 0.75 | 21.52
DHG150* | 12.5 | 4500 | 75 | 67 | 85 | 147 | 0.6 | 17.79
DHG150* | 12.5 | 4500 | 75 | 71 | 85 | 153.4 | 0.45 | 13.9
DHG150* | 12.5 | 4500 | 75 | 59 | 95 | 134.5 | 0.85 | 23.21
DHG150* | 12.5 | 4500 | 75 | 63 | 95 | 136.5 | 0.77 | 21.22
DHG150* | 12.5 | 4500 | 75 | 67 | 95 | 140.7 | 0.62 | 17.49
DHG150* | 12.5 | 4500 | 75 | 71 | 95 | 147.1 | 0.46 | 13.6
DHG150* | 12.5 | 4500 | 75 | 59 | 105 | 126.8 | 0.9 | 22.94
DHG150* | 12.5 | 4500 | 75 | 63 | 105 | 128.8 | 0.81 | 20.95
DHG150* | 12.5 | 4500 | 75 | 67 | 105 | 133 | 0.64 | 17.23
DHG150* | 12.5 | 4500 | 75 | 71 | 105 | 139.4 | 0.47 | 13.4
DHG150* | 12.5 | 4500 | 75 | 59 | 115 | 119.8 | 1 | 24.19
DHG150* | 12.5 | 4500 | 75 | 63 | 115 | 121.7 | 0.9 | 22.2
DHG150* | 12.5 | 4500 | 75 | 67 | 115 | 125.9 | 0.73 | 18.48
DHG150* | 12.5 | 4500 | 75 | 71 | 115 | 132.3 | 0.55 | 14.6
DHG150* | 12.5 | 3500 | 80 | 59 | 65 | 141.8 | 0.81 | 29.88
DHG150* | 12.5 | 3500 | 80 | 63 | 65 | 143.8 | 0.75 | 27.89
DHG150* | 12.5 | 3500 | 80 | 67 | 65 | 148 | 0.63 | 24.16
DHG150* | 12.5 | 3500 | 80 | 71 | 65 | 154.4 | 0.51 | 20.3
DHG150* | 12.5 | 3500 | 80 | 59 | 75 | 140.6 | 0.82 | 29.83
DHG150* | 12.5 | 3500 | 80 | 63 | 75 | 142.6 | 0.75 | 27.83
DHG150* | 12.5 | 3500 | 80 | 67 | 75 | 146.8 | 0.63 | 24.11
DHG150* | 12.5 | 3500 | 80 | 71 | 75 | 153.2 | 0.51 | 20.3
DHG150* | 12.5 | 3500 | 80 | 59 | 85 | 136.9 | 0.85 | 30.11
DHG150* | 12.5 | 3500 | 80 | 63 | 85 | 138.9 | 0.78 | 28.11
DHG150* | 12.5 | 3500 | 80 | 67 | 85 | 143.1 | 0.66 | 24.39
DHG150* | 12.5 | 3500 | 80 | 71 | 85 | 149.5 | 0.53 | 20.5
DHG150* | 12.5 | 3500 | 80 | 59 | 95 | 130.6 | 0.88 | 29.81
DHG150* | 12.5 | 3500 | 80 | 63 | 95 | 132.6 | 0.81 | 27.81
DHG150* | 12.5 | 3500 | 80 | 67 | 95 | 136.8 | 0.68 | 24.09
DHG150* | 12.5 | 3500 | 80 | 71 | 95 | 143.2 | 0.54 | 20.2
DHG150* | 12.5 | 3500 | 80 | 59 | 105 | 122.9 | 0.93 | 29.54
DHG150* | 12.5 | 3500 | 80 | 63 | 105 | 124.9 | 0.85 | 27.55
DHG150* | 12.5 | 3500 | 80 | 67 | 105 | 129.1 | 0.71 | 23.82
DHG150* | 12.5 | 3500 | 80 | 71 | 105 | 135.5 | 0.57 | 20
DHG150* | 12.5 | 3500 | 80 | 59 | 115 | 115.9 | 1 | 30.1
DHG150* | 12.5 | 3500 | 80 | 63 | 115 | 117.9 | 0.94 | 28.79
DHG150* | 12.5 | 3500 | 80 | 67 | 115 | 122.1 | 0.79 | 25.07
DHG150* | 12.5 | 3500 | 80 | 71 | 115 | 128.5 | 0.64 | 21.2
DHG150* | 12.5 | 3800 | 80 | 59 | 65 | 143.1 | 0.85 | 29.15
DHG150* | 12.5 | 3800 | 80 | 63 | 65 | 145 | 0.78 | 27.15
DHG150* | 12.5 | 3800 | 80 | 67 | 65 | 149.2 | 0.66 | 23.43
DHG150* | 12.5 | 3800 | 80 | 71 | 65 | 155.6 | 0.53 | 19.6
DHG150* | 12.5 | 3800 | 80 | 59 | 75 | 141.8 | 0.86 | 29.09
DHG150* | 12.5 | 3800 | 80 | 63 | 75 | 143.8 | 0.79 | 27.1
DHG150* | 12.5 | 3800 | 80 | 67 | 75 | 148 | 0.66 | 23.38
DHG150* | 12.5 | 3800 | 80 | 71 | 75 | 154.4 | 0.53 | 19.5
DHG150* | 12.5 | 3800 | 80 | 59 | 85 | 138.1 | 0.89 | 29.37
DHG150* | 12.5 | 3800 | 80 | 63 | 85 | 140.1 | 0.82 | 27.38
DHG150* | 12.5 | 3800 | 80 | 67 | 85 | 144.3 | 0.69 | 23.66
DHG150* | 12.5 | 3800 | 80 | 71 | 85 | 150.7 | 0.55 | 19.8
DHG150* | 12.5 | 3800 | 80 | 59 | 95 | 131.8 | 0.92 | 29.07
DHG150* | 12.5 | 3800 | 80 | 63 | 95 | 133.8 | 0.85 | 27.08
DHG150* | 12.5 | 3800 | 80 | 67 | 95 | 138 | 0.71 | 23.36
DHG150* | 12.5 | 3800 | 80 | 71 | 95 | 144.4 | 0.56 | 19.5
DHG150* | 12.5 | 3800 | 80 | 59 | 105 | 124.1 | 0.97 | 28.81
DHG150* | 12.5 | 3800 | 80 | 63 | 105 | 126.1 | 0.89 | 26.81
DHG150* | 12.5 | 3800 | 80 | 67 | 105 | 130.3 | 0.74 | 23.09
DHG150* | 12.5 | 3800 | 80 | 71 | 105 | 136.7 | 0.59 | 19.2
DHG150* | 12.5 | 3800 | 80 | 59 | 115 | 117.1 | 1 | 28.01
DHG150* | 12.5 | 3800 | 80 | 63 | 115 | 119.1 | 0.99 | 28.06
DHG150* | 12.5 | 3800 | 80 | 67 | 115 | 123.3 | 0.83 | 24.34
DHG150* | 12.5 | 3800 | 80 | 71 | 115 | 129.7 | 0.66 | 20.5
DHG150* | 12.5 | 4500 | 80 | 59 | 65 | 146.5 | 0.94 | 27.7
DHG150* | 12.5 | 4500 | 80 | 63 | 65 | 148.5 | 0.86 | 25.7
DHG150* | 12.5 | 4500 | 80 | 67 | 65 | 152.6 | 0.71 | 21.98
DHG150* | 12.5 | 4500 | 80 | 71 | 65 | 159.1 | 0.56 | 18.1
DHG150* | 12.5 | 4500 | 80 | 59 | 75 | 145.2 | 0.94 | 27.64
DHG150* | 12.5 | 4500 | 80 | 63 | 75 | 147.2 | 0.86 | 25.65
DHG150* | 12.5 | 4500 | 80 | 67 | 75 | 151.4 | 0.72 | 21.93
DHG150* | 12.5 | 4500 | 80 | 71 | 75 | 157.8 | 0.57 | 18.1
DHG150* | 12.5 | 4500 | 80 | 59 | 85 | 141.5 | 0.98 | 27.92
DHG150* | 12.5 | 4500 | 80 | 63 | 85 | 143.5 | 0.89 | 25.93
DHG150* | 12.5 | 4500 | 80 | 67 | 85 | 147.7 | 0.74 | 22.21
DHG150* | 12.5 | 4500 | 80 | 71 | 85 | 154.1 | 0.59 | 18.4
DHG150* | 12.5 | 4500 | 80 | 59 | 95 | 135.2 | 1 | 27.32
DHG150* | 12.5 | 4500 | 80 | 63 | 95 | 137.2 | 0.92 | 25.63
DHG150* | 12.5 | 4500 | 80 | 67 | 95 | 141.4 | 0.77 | 21.91
DHG150* | 12.5 | 4500 | 80 | 71 | 95 | 147.8 | 0.6 | 18.1
DHG150* | 12.5 | 4500 | 80 | 59 | 105 | 127.5 | 1 | 25.76
DHG150* | 12.5 | 4500 | 80 | 63 | 105 | 129.5 | 0.97 | 25.36
DHG150* | 12.5 | 4500 | 80 | 67 | 105 | 133.7 | 0.8 | 21.64
DHG150* | 12.5 | 4500 | 80 | 71 | 105 | 140.1 | 0.63 | 17.8
DHG150* | 12.5 | 4500 | 80 | 59 | 115 | 120.5 | 1 | 24.34
DHG150* | 12.5 | 4500 | 80 | 63 | 115 | 122.5 | 1 | 24.74
DHG150* | 12.5 | 4500 | 80 | 67 | 115 | 126.7 | 0.89 | 22.89
DHG150* | 12.5 | 4500 | 80 | 71 | 115 | 133.1 | 0.71 | 19
DHG150* | 12.5 | 3500 | 85 | 59 | 65 | 144.2 | 0.9 | 33.79
DHG150* | 12.5 | 3500 | 85 | 63 | 65 | 146.2 | 0.84 | 31.8
DHG150* | 12.5 | 3500 | 85 | 67 | 65 | 150.4 | 0.72 | 28.08
DHG150* | 12.5 | 3500 | 85 | 71 | 65 | 156.8 | 0.59 | 24.2
DHG150* | 12.5 | 3500 | 85 | 59 | 75 | 143 | 0.91 | 33.74
DHG150* | 12.5 | 3500 | 85 | 63 | 75 | 144.9 | 0.84 | 31.75
DHG150* | 12.5 | 3500 | 85 | 67 | 75 | 149.1 | 0.72 | 28.02
DHG150* | 12.5 | 3500 | 85 | 71 | 75 | 155.5 | 0.6 | 24.2
DHG150* | 12.5 | 3500 | 85 | 59 | 85 | 139.3 | 0.94 | 34.02
DHG150* | 12.5 | 3500 | 85 | 63 | 85 | 141.3 | 0.87 | 32.03
DHG150* | 12.5 | 3500 | 85 | 67 | 85 | 145.5 | 0.75 | 28.3
DHG150* | 12.5 | 3500 | 85 | 71 | 85 | 151.9 | 0.62 | 24.4
DHG150* | 12.5 | 3500 | 85 | 59 | 95 | 133 | 0.98 | 33.72
DHG150* | 12.5 | 3500 | 85 | 63 | 95 | 135 | 0.9 | 31.73
DHG150* | 12.5 | 3500 | 85 | 67 | 95 | 139.2 | 0.77 | 28
DHG150* | 12.5 | 3500 | 85 | 71 | 95 | 145.6 | 0.64 | 24.1
DHG150* | 12.5 | 3500 | 85 | 59 | 105 | 125.3 | 1 | 32.54
DHG150* | 12.5 | 3500 | 85 | 63 | 105 | 127.3 | 0.95 | 31.46
DHG150* | 12.5 | 3500 | 85 | 67 | 105 | 131.5 | 0.81 | 27.74
DHG150* | 12.5 | 3500 | 85 | 71 | 105 | 137.9 | 0.67 | 23.9
DHG150* | 12.5 | 3500 | 85 | 59 | 115 | 118.2 | 1 | 30.71
DHG150* | 12.5 | 3500 | 85 | 63 | 115 | 120.2 | 1 | 31.23
DHG150* | 12.5 | 3500 | 85 | 67 | 115 | 124.4 | 0.9 | 28.99
DHG150* | 12.5 | 3500 | 85 | 71 | 115 | 130.8 | 0.74 | 25.1
DHG150* | 12.5 | 3800 | 85 | 59 | 65 | 145.4 | 0.95 | 33.06
DHG150* | 12.5 | 3800 | 85 | 63 | 65 | 147.4 | 0.88 | 31.07
DHG150* | 12.5 | 3800 | 85 | 67 | 65 | 151.6 | 0.75 | 27.35
DHG150* | 12.5 | 3800 | 85 | 71 | 65 | 158 | 0.62 | 23.5
DHG150* | 12.5 | 3800 | 85 | 59 | 75 | 144.2 | 0.96 | 33.01
DHG150* | 12.5 | 3800 | 85 | 63 | 75 | 146.1 | 0.89 | 31.01
DHG150* | 12.5 | 3800 | 85 | 67 | 75 | 150.3 | 0.76 | 27.29
DHG150* | 12.5 | 3800 | 85 | 71 | 75 | 156.7 | 0.62 | 23.4
DHG150* | 12.5 | 3800 | 85 | 59 | 85 | 140.5 | 0.99 | 33.29
DHG150* | 12.5 | 3800 | 85 | 63 | 85 | 142.5 | 0.92 | 31.29
DHG150* | 12.5 | 3800 | 85 | 67 | 85 | 146.7 | 0.79 | 27.57
DHG150* | 12.5 | 3800 | 85 | 71 | 85 | 153.1 | 0.65 | 23.7
DHG150* | 12.5 | 3800 | 85 | 59 | 95 | 134.2 | 1 | 32.1
DHG150* | 12.5 | 3800 | 85 | 63 | 95 | 136.2 | 0.95 | 30.99
DHG150* | 12.5 | 3800 | 85 | 67 | 95 | 140.4 | 0.81 | 27.27
DHG150* | 12.5 | 3800 | 85 | 71 | 95 | 146.8 | 0.67 | 23.4
DHG150* | 12.5 | 3800 | 85 | 59 | 105 | 126.5 | 1 | 30.26
DHG150* | 12.5 | 3800 | 85 | 63 | 105 | 128.5 | 1 | 30.73
DHG150* | 12.5 | 3800 | 85 | 67 | 105 | 132.7 | 0.85 | 27
DHG150* | 12.5 | 3800 | 85 | 71 | 105 | 139.1 | 0.7 | 23.1
DHG150* | 12.5 | 3800 | 85 | 59 | 115 | 119.4 | 1 | 28.57
DHG150* | 12.5 | 3800 | 85 | 63 | 115 | 121.4 | 1 | 29.05
DHG150* | 12.5 | 3800 | 85 | 67 | 115 | 125.6 | 0.94 | 28.25
DHG150* | 12.5 | 3800 | 85 | 71 | 115 | 132 | 0.77 | 24.4
DHG150* | 12.5 | 4500 | 85 | 59 | 65 | 148.8 | 1 | 30.07
DHG150* | 12.5 | 4500 | 85 | 63 | 65 | 150.8 | 0.97 | 29.62
DHG150* | 12.5 | 4500 | 85 | 67 | 65 | 155 | 0.83 | 25.9
DHG150* | 12.5 | 4500 | 85 | 71 | 65 | 161.4 | 0.68 | 22
DHG150* | 12.5 | 4500 | 85 | 59 | 75 | 147.6 | 1 | 29.81
DHG150* | 12.5 | 4500 | 85 | 63 | 75 | 149.6 | 0.98 | 29.56
DHG150* | 12.5 | 4500 | 85 | 67 | 75 | 153.8 | 0.83 | 25.84
DHG150* | 12.5 | 4500 | 85 | 71 | 75 | 160.2 | 0.68 | 22
DHG150* | 12.5 | 4500 | 85 | 59 | 85 | 143.9 | 1 | 29.07
DHG150* | 12.5 | 4500 | 85 | 63 | 85 | 145.9 | 1 | 29.47
DHG150* | 12.5 | 4500 | 85 | 67 | 85 | 150.1 | 0.86 | 26.12
DHG150* | 12.5 | 4500 | 85 | 71 | 85 | 156.5 | 0.7 | 22.3
DHG150* | 12.5 | 4500 | 85 | 59 | 95 | 137.6 | 1 | 27.8
DHG150* | 12.5 | 4500 | 85 | 63 | 95 | 139.6 | 1 | 28.2
DHG150* | 12.5 | 4500 | 85 | 67 | 95 | 143.8 | 0.89 | 25.82
DHG150* | 12.5 | 4500 | 85 | 71 | 95 | 150.2 | 0.72 | 22
DHG150* | 12.5 | 4500 | 85 | 59 | 105 | 129.9 | 1 | 26.24
DHG150* | 12.5 | 4500 | 85 | 63 | 105 | 131.9 | 1 | 26.64
DHG150* | 12.5 | 4500 | 85 | 67 | 105 | 136.1 | 0.93 | 25.55
DHG150* | 12.5 | 4500 | 85 | 71 | 105 | 142.5 | 0.75 | 21.7
DHG150* | 12.5 | 4500 | 85 | 59 | 115 | 122.9 | 1 | 24.82
DHG150* | 12.5 | 4500 | 85 | 63 | 115 | 124.8 | 1 | 25.22
DHG150* | 12.5 | 4500 | 85 | 67 | 115 | 129 | 1 | 26.07
DHG150* | 12.5 | 4500 | 85 | 71 | 115 | 135.4 | 0.84 | 22.9
DSH036*D | 3 | 900 | 70 | 59 | 65 | 35 | 0.57 | 20.08
DSH036*D | 3 | 900 | 70 | 63 | 65 | 35.5 | 0.51 | 18.36
DSH036*D | 3 | 900 | 70 | 67 | 65 | 36.6 | 0.41 | 15.15
DSH036*D | 3 | 900 | 70 | 59 | 75 | 34.7 | 0.57 | 20.04
DSH036*D | 3 | 900 | 70 | 63 | 75 | 35.2 | 0.52 | 18.31
DSH036*D | 3 | 900 | 70 | 67 | 75 | 36.3 | 0.41 | 15.1
DSH036*D | 3 | 900 | 70 | 59 | 85 | 33.8 | 0.59 | 20.28
DSH036*D | 3 | 900 | 70 | 63 | 85 | 34.3 | 0.54 | 18.56
DSH036*D | 3 | 900 | 70 | 67 | 85 | 35.3 | 0.43 | 15.34
DSH036*D | 3 | 900 | 70 | 59 | 95 | 32.2 | 0.62 | 20.02
DSH036*D | 3 | 900 | 70 | 63 | 95 | 32.7 | 0.55 | 18.3
DSH036*D | 3 | 900 | 70 | 67 | 95 | 33.7 | 0.44 | 15.08
DSH036*D | 3 | 900 | 70 | 59 | 105 | 30.2 | 0.65 | 19.79
DSH036*D | 3 | 900 | 70 | 63 | 105 | 30.7 | 0.58 | 18.07
DSH036*D | 3 | 900 | 70 | 67 | 105 | 31.8 | 0.46 | 14.85
DSH036*D | 3 | 900 | 70 | 59 | 115 | 28.4 | 0.73 | 20.87
DSH036*D | 3 | 900 | 70 | 63 | 115 | 28.9 | 0.66 | 19.15
DSH036*D | 3 | 900 | 70 | 67 | 115 | 30 | 0.53 | 15.93
DSH036*D | 3 | 900 | 75 | 59 | 65 | 35.2 | 0.67 | 23.87
DSH036*D | 3 | 900 | 75 | 63 | 65 | 35.7 | 0.61 | 22.15
DSH036*D | 3 | 900 | 75 | 67 | 65 | 36.8 | 0.51 | 18.93
DSH036*D | 3 | 900 | 75 | 71 | 65 | 38.4 | 0.4 | 15.6
DSH036*D | 3 | 900 | 75 | 59 | 75 | 34.9 | 0.68 | 23.83
DSH036*D | 3 | 900 | 75 | 63 | 75 | 35.4 | 0.62 | 22.1
DSH036*D | 3 | 900 | 75 | 67 | 75 | 36.4 | 0.51 | 18.89
DSH036*D | 3 | 900 | 75 | 71 | 75 | 38.1 | 0.4 | 15.6
DSH036*D | 3 | 900 | 75 | 59 | 85 | 33.9 | 0.7 | 24.07
DSH036*D | 3 | 900 | 75 | 63 | 85 | 34.5 | 0.64 | 22.35
DSH036*D | 3 | 900 | 75 | 67 | 85 | 35.5 | 0.53 | 19.13
DSH036*D | 3 | 900 | 75 | 71 | 85 | 37.1 | 0.4 | 15.8
DSH036*D | 3 | 900 | 75 | 59 | 95 | 32.3 | 0.73 | 23.81
DSH036*D | 3 | 900 | 75 | 63 | 95 | 32.9 | 0.67 | 22.09
DSH036*D | 3 | 900 | 75 | 67 | 95 | 33.9 | 0.55 | 18.87
DSH036*D | 3 | 900 | 75 | 71 | 95 | 35.5 | 0.4 | 15.5
DSH036*D | 3 | 900 | 75 | 59 | 105 | 30.4 | 0.77 | 23.58
DSH036*D | 3 | 900 | 75 | 63 | 105 | 30.9 | 0.7 | 21.86
DSH036*D | 3 | 900 | 75 | 67 | 105 | 32 | 0.58 | 18.64
DSH036*D | 3 | 900 | 75 | 71 | 105 | 33.6 | 0.5 | 15.3
DSH036*D | 3 | 900 | 75 | 59 | 115 | 28.6 | 0.85 | 24.66
DSH036*D | 3 | 900 | 75 | 63 | 115 | 29.1 | 0.78 | 22.93
DSH036*D | 3 | 900 | 75 | 67 | 115 | 30.2 | 0.65 | 19.72
DSH036*D | 3 | 900 | 75 | 71 | 115 | 31.8 | 0.5 | 16.4
DSH036*D | 3 | 900 | 80 | 59 | 65 | 35.4 | 0.77 | 27.69
DSH036*D | 3 | 900 | 80 | 63 | 65 | 35.9 | 0.72 | 25.96
DSH036*D | 3 | 900 | 80 | 67 | 65 | 36.9 | 0.61 | 22.75
DSH036*D | 3 | 900 | 80 | 71 | 65 | 38.6 | 0.5 | 19.4
DSH036*D | 3 | 900 | 80 | 59 | 75 | 35.1 | 0.78 | 27.64
DSH036*D | 3 | 900 | 80 | 63 | 75 | 35.6 | 0.72 | 25.92
DSH036*D | 3 | 900 | 80 | 67 | 75 | 36.6 | 0.61 | 22.7
DSH036*D | 3 | 900 | 80 | 71 | 75 | 38.3 | 0.5 | 19.4
DSH036*D | 3 | 900 | 80 | 59 | 85 | 34.1 | 0.81 | 27.88
DSH036*D | 3 | 900 | 80 | 63 | 85 | 34.6 | 0.75 | 26.16
DSH036*D | 3 | 900 | 80 | 67 | 85 | 35.7 | 0.64 | 22.94
DSH036*D | 3 | 900 | 80 | 71 | 85 | 37.3 | 0.5 | 19.6
DSH036*D | 3 | 900 | 80 | 59 | 95 | 32.5 | 0.84 | 27.62
DSH036*D | 3 | 900 | 80 | 63 | 95 | 33 | 0.78 | 25.9
DSH036*D | 3 | 900 | 80 | 67 | 95 | 34.1 | 0.66 | 22.68
DSH036*D | 3 | 900 | 80 | 71 | 95 | 35.7 | 0.5 | 19.4
DSH036*D | 3 | 900 | 80 | 59 | 105 | 30.6 | 0.89 | 27.39
DSH036*D | 3 | 900 | 80 | 63 | 105 | 31.1 | 0.82 | 25.67
DSH036*D | 3 | 900 | 80 | 67 | 105 | 32.1 | 0.69 | 22.45
DSH036*D | 3 | 900 | 80 | 71 | 105 | 33.8 | 0.6 | 19.1
DSH036*D | 3 | 900 | 80 | 59 | 115 | 28.8 | 0.98 | 28.47
DSH036*D | 3 | 900 | 80 | 63 | 115 | 29.3 | 0.9 | 26.75
DSH036*D | 3 | 900 | 80 | 67 | 115 | 30.4 | 0.77 | 23.53
DSH036*D | 3 | 900 | 80 | 71 | 115 | 32 | 0.6 | 20.2
DSH036*D | 3 | 900 | 85 | 59 | 65 | 36 | 0.85 | 31.07
DSH036*D | 3 | 900 | 85 | 63 | 65 | 36.5 | 0.8 | 29.35
DSH036*D | 3 | 900 | 85 | 67 | 65 | 37.5 | 0.69 | 26.13
DSH036*D | 3 | 900 | 85 | 71 | 65 | 39.2 | 0.6 | 22.8
DSH036*D | 3 | 900 | 85 | 59 | 75 | 35.7 | 0.86 | 31.02
DSH036*D | 3 | 900 | 85 | 63 | 75 | 36.2 | 0.8 | 29.3
DSH036*D | 3 | 900 | 85 | 67 | 75 | 37.2 | 0.69 | 26.08
DSH036*D | 3 | 900 | 85 | 71 | 75 | 38.9 | 0.6 | 22.8
DSH036*D | 3 | 900 | 85 | 59 | 85 | 34.7 | 0.89 | 31.26
DSH036*D | 3 | 900 | 85 | 63 | 85 | 35.2 | 0.83 | 29.54
DSH036*D | 3 | 900 | 85 | 67 | 85 | 36.3 | 0.72 | 26.32
DSH036*D | 3 | 900 | 85 | 71 | 85 | 37.9 | 0.6 | 23
DSH036*D | 3 | 900 | 85 | 59 | 95 | 33.1 | 0.93 | 31
DSH036*D | 3 | 900 | 85 | 63 | 95 | 33.6 | 0.86 | 29.28
DSH036*D | 3 | 900 | 85 | 67 | 95 | 34.7 | 0.74 | 26.06
DSH036*D | 3 | 900 | 85 | 71 | 95 | 36.3 | 0.6 | 22.7
DSH036*D | 3 | 900 | 85 | 59 | 105 | 31.2 | 0.98 | 30.77
DSH036*D | 3 | 900 | 85 | 63 | 105 | 31.7 | 0.91 | 29.05
DSH036*D | 3 | 900 | 85 | 67 | 105 | 32.7 | 0.78 | 25.83
DSH036*D | 3 | 900 | 85 | 71 | 105 | 34.4 | 0.6 | 22.5
DSH036*D | 3 | 900 | 85 | 59 | 115 | 29.4 | 1 | 29.69
DSH036*D | 3 | 900 | 85 | 63 | 115 | 29.9 | 1 | 30.13
DSH036*D | 3 | 900 | 85 | 67 | 115 | 31 | 0.86 | 26.91
DSH036*D | 3 | 900 | 85 | 71 | 115 | 32.6 | 0.7 | 23.6
DSH036*D | 3 | 1220 | 70 | 59 | 65 | 35.9 | 0.66 | 17.58
DSH036*D | 3 | 1220 | 70 | 63 | 65 | 36.4 | 0.58 | 15.86
DSH036*D | 3 | 1220 | 70 | 67 | 65 | 37.5 | 0.45 | 12.65
DSH036*D | 3 | 1220 | 70 | 59 | 75 | 35.6 | 0.66 | 17.54
DSH036*D | 3 | 1220 | 70 | 63 | 75 | 36.1 | 0.59 | 15.81
DSH036*D | 3 | 1220 | 70 | 67 | 75 | 37.2 | 0.45 | 12.6
DSH036*D | 3 | 1220 | 70 | 59 | 85 | 34.7 | 0.69 | 17.78
DSH036*D | 3 | 1220 | 70 | 63 | 85 | 35.2 | 0.61 | 16.06
DSH036*D | 3 | 1220 | 70 | 67 | 85 | 36.2 | 0.48 | 12.84
DSH036*D | 3 | 1220 | 70 | 59 | 95 | 33.1 | 0.71 | 17.52
DSH036*D | 3 | 1220 | 70 | 63 | 95 | 33.6 | 0.63 | 15.8
DSH036*D | 3 | 1220 | 70 | 67 | 95 | 34.6 | 0.49 | 12.58
DSH036*D | 3 | 1220 | 70 | 59 | 105 | 31.1 | 0.75 | 17.29
DSH036*D | 3 | 1220 | 70 | 63 | 105 | 31.6 | 0.66 | 15.57
DSH036*D | 3 | 1220 | 70 | 67 | 105 | 32.7 | 0.51 | 12.35
DSH036*D | 3 | 1220 | 70 | 59 | 115 | 29.3 | 0.84 | 18.37
DSH036*D | 3 | 1220 | 70 | 63 | 115 | 29.8 | 0.75 | 16.64
DSH036*D | 3 | 1220 | 70 | 67 | 115 | 30.9 | 0.58 | 13.43
DSH036*D | 3 | 1220 | 75 | 59 | 65 | 36.1 | 0.79 | 21.37
DSH036*D | 3 | 1220 | 75 | 63 | 65 | 36.6 | 0.72 | 19.65
DSH036*D | 3 | 1220 | 75 | 67 | 65 | 37.7 | 0.59 | 16.43
DSH036*D | 3 | 1220 | 75 | 71 | 65 | 39.3 | 0.4 | 13.1
DSH036*D | 3 | 1220 | 75 | 59 | 75 | 35.8 | 0.8 | 21.33
DSH036*D | 3 | 1220 | 75 | 63 | 75 | 36.3 | 0.73 | 19.6
DSH036*D | 3 | 1220 | 75 | 67 | 75 | 37.3 | 0.59 | 16.39
DSH036*D | 3 | 1220 | 75 | 71 | 75 | 39 | 0.4 | 13.1
DSH036*D | 3 | 1220 | 75 | 59 | 85 | 34.8 | 0.83 | 21.57
DSH036*D | 3 | 1220 | 75 | 63 | 85 | 35.4 | 0.75 | 19.84
DSH036*D | 3 | 1220 | 75 | 67 | 85 | 36.4 | 0.61 | 16.63
DSH036*D | 3 | 1220 | 75 | 71 | 85 | 38 | 0.5 | 13.3
DSH036*D | 3 | 1220 | 75 | 59 | 95 | 33.2 | 0.86 | 21.31
DSH036*D | 3 | 1220 | 75 | 63 | 95 | 33.8 | 0.78 | 19.58
DSH036*D | 3 | 1220 | 75 | 67 | 95 | 34.8 | 0.63 | 16.37
DSH036*D | 3 | 1220 | 75 | 71 | 95 | 36.4 | 0.5 | 13
DSH036*D | 3 | 1220 | 75 | 59 | 105 | 31.3 | 0.9 | 21.08
DSH036*D | 3 | 1220 | 75 | 63 | 105 | 31.8 | 0.82 | 19.35
DSH036*D | 3 | 1220 | 75 | 67 | 105 | 32.9 | 0.66 | 16.14
DSH036*D | 3 | 1220 | 75 | 71 | 105 | 34.5 | 0.5 | 12.8
DSH036*D | 3 | 1220 | 75 | 59 | 115 | 29.5 | 1 | 21.99
DSH036*D | 3 | 1220 | 75 | 63 | 115 | 30 | 0.91 | 20.43
DSH036*D | 3 | 1220 | 75 | 67 | 115 | 31.1 | 0.74 | 17.22
DSH036*D | 3 | 1220 | 75 | 71 | 115 | 32.7 | 0.6 | 13.9
DSH036*D | 3 | 1220 | 80 | 59 | 65 | 36.3 | 0.93 | 25.19
DSH036*D | 3 | 1220 | 80 | 63 | 65 | 36.8 | 0.86 | 23.46
DSH036*D | 3 | 1220 | 80 | 67 | 65 | 37.8 | 0.72 | 20.25
DSH036*D | 3 | 1220 | 80 | 71 | 65 | 39.5 | 0.6 | 16.9
DSH036*D | 3 | 1220 | 80 | 59 | 75 | 36 | 0.94 | 25.14
DSH036*D | 3 | 1220 | 80 | 63 | 75 | 36.5 | 0.86 | 23.42
DSH036*D | 3 | 1220 | 80 | 67 | 75 | 37.5 | 0.72 | 20.2
DSH036*D | 3 | 1220 | 80 | 71 | 75 | 39.2 | 0.6 | 16.9
DSH036*D | 3 | 1220 | 80 | 59 | 85 | 35 | 0.97 | 25.38
DSH036*D | 3 | 1220 | 80 | 63 | 85 | 35.5 | 0.89 | 23.66
DSH036*D | 3 | 1220 | 80 | 67 | 85 | 36.6 | 0.75 | 20.44
DSH036*D | 3 | 1220 | 80 | 71 | 85 | 38.2 | 0.6 | 17.1
DSH036*D | 3 | 1220 | 80 | 59 | 95 | 33.4 | 1 | 24.91
DSH036*D | 3 | 1220 | 80 | 63 | 95 | 33.9 | 0.93 | 23.4
DSH036*D | 3 | 1220 | 80 | 67 | 95 | 35 | 0.77 | 20.18
DSH036*D | 3 | 1220 | 80 | 71 | 95 | 36.6 | 0.6 | 16.8
DSH036*D | 3 | 1220 | 80 | 59 | 105 | 31.5 | 1 | 23.46
DSH036*D | 3 | 1220 | 80 | 63 | 105 | 32 | 0.97 | 23.17
DSH036*D | 3 | 1220 | 80 | 67 | 105 | 33 | 0.81 | 19.95
DSH036*D | 3 | 1220 | 80 | 71 | 105 | 34.7 | 0.6 | 16.6
DSH036*D | 3 | 1220 | 80 | 59 | 115 | 29.7 | 1 | 22.13
DSH036*D | 3 | 1220 | 80 | 63 | 115 | 30.2 | 1 | 22.5
DSH036*D | 3 | 1220 | 80 | 67 | 115 | 31.3 | 0.9 | 21.03
DSH036*D | 3 | 1220 | 80 | 71 | 115 | 32.9 | 0.7 | 17.7
DSH036*D | 3 | 1220 | 85 | 59 | 65 | 36.9 | 1 | 27.48
DSH036*D | 3 | 1220 | 85 | 63 | 65 | 37.4 | 0.96 | 26.84
DSH036*D | 3 | 1220 | 85 | 67 | 65 | 38.4 | 0.82 | 23.63
DSH036*D | 3 | 1220 | 85 | 71 | 65 | 40.1 | 0.7 | 20.3
DSH036*D | 3 | 1220 | 85 | 59 | 75 | 36.6 | 1 | 27.24
DSH036*D | 3 | 1220 | 85 | 63 | 75 | 37.1 | 0.97 | 26.8
DSH036*D | 3 | 1220 | 85 | 67 | 75 | 38.1 | 0.83 | 23.58
DSH036*D | 3 | 1220 | 85 | 71 | 75 | 39.8 | 0.7 | 20.2
DSH036*D | 3 | 1220 | 85 | 59 | 85 | 35.6 | 1 | 26.55
DSH036*D | 3 | 1220 | 85 | 63 | 85 | 36.1 | 1 | 26.93
DSH036*D | 3 | 1220 | 85 | 67 | 85 | 37.2 | 0.86 | 23.82
DSH036*D | 3 | 1220 | 85 | 71 | 85 | 38.8 | 0.7 | 20.5
DSH036*D | 3 | 1220 | 85 | 59 | 95 | 34 | 1 | 25.36
DSH036*D | 3 | 1220 | 85 | 63 | 95 | 34.5 | 1 | 25.73
DSH036*D | 3 | 1220 | 85 | 67 | 95 | 35.6 | 0.89 | 23.56
DSH036*D | 3 | 1220 | 85 | 71 | 95 | 37.2 | 0.7 | 20.2
DSH036*D | 3 | 1220 | 85 | 59 | 105 | 32.1 | 1 | 23.9
DSH036*D | 3 | 1220 | 85 | 63 | 105 | 32.6 | 1 | 24.28
DSH036*D | 3 | 1220 | 85 | 67 | 105 | 33.6 | 0.93 | 23.33
DSH036*D | 3 | 1220 | 85 | 71 | 105 | 35.3 | 0.8 | 20
DSH036*D | 3 | 1220 | 85 | 59 | 115 | 30.3 | 1 | 22.57
DSH036*D | 3 | 1220 | 85 | 63 | 115 | 30.8 | 1 | 22.95
DSH036*D | 3 | 1220 | 85 | 67 | 115 | 31.9 | 1 | 23.74
DSH036*D | 3 | 1220 | 85 | 71 | 115 | 33.5 | 0.8 | 21.1
DSH036*D | 3 | 1350 | 70 | 59 | 65 | 36.4 | 0.69 | 16.83
DSH036*D | 3 | 1350 | 70 | 63 | 65 | 36.9 | 0.61 | 15.11
DSH036*D | 3 | 1350 | 70 | 67 | 65 | 38 | 0.47 | 11.89
DSH036*D | 3 | 1350 | 70 | 59 | 75 | 36.1 | 0.69 | 16.78
DSH036*D | 3 | 1350 | 70 | 63 | 75 | 36.6 | 0.61 | 15.06
DSH036*D | 3 | 1350 | 70 | 67 | 75 | 37.6 | 0.47 | 11.84
DSH036*D | 3 | 1350 | 70 | 59 | 85 | 35.1 | 0.72 | 17.02
DSH036*D | 3 | 1350 | 70 | 63 | 85 | 35.6 | 0.64 | 15.3
DSH036*D | 3 | 1350 | 70 | 67 | 85 | 36.7 | 0.49 | 12.09
DSH036*D | 3 | 1350 | 70 | 59 | 95 | 33.5 | 0.74 | 16.76
DSH036*D | 3 | 1350 | 70 | 63 | 95 | 34 | 0.66 | 15.04
DSH036*D | 3 | 1350 | 70 | 67 | 95 | 35.1 | 0.5 | 11.83
DSH036*D | 3 | 1350 | 70 | 59 | 105 | 31.6 | 0.78 | 16.53
DSH036*D | 3 | 1350 | 70 | 63 | 105 | 32.1 | 0.69 | 14.81
DSH036*D | 3 | 1350 | 70 | 67 | 105 | 33.1 | 0.52 | 11.6
DSH036*D | 3 | 1350 | 70 | 59 | 115 | 29.8 | 0.88 | 17.61
DSH036*D | 3 | 1350 | 70 | 63 | 115 | 30.3 | 0.78 | 15.89
DSH036*D | 3 | 1350 | 70 | 67 | 115 | 31.4 | 0.6 | 12.67
DSH036*D | 3 | 1350 | 75 | 59 | 65 | 36.6 | 0.84 | 20.62
DSH036*D | 3 | 1350 | 75 | 63 | 65 | 37.1 | 0.76 | 18.9
DSH036*D | 3 | 1350 | 75 | 67 | 65 | 38.1 | 0.61 | 15.68
DSH036*D | 3 | 1350 | 75 | 71 | 65 | 39.8 | 0.5 | 12.3
DSH036*D | 3 | 1350 | 75 | 59 | 75 | 36.3 | 0.84 | 20.57
DSH036*D | 3 | 1350 | 75 | 63 | 75 | 36.8 | 0.76 | 18.85
DSH036*D | 3 | 1350 | 75 | 67 | 75 | 37.8 | 0.61 | 15.63
DSH036*D | 3 | 1350 | 75 | 71 | 75 | 39.4 | 0.5 | 12.3
DSH036*D | 3 | 1350 | 75 | 59 | 85 | 35.3 | 0.88 | 20.81
DSH036*D | 3 | 1350 | 75 | 63 | 85 | 35.8 | 0.79 | 19.09
DSH036*D | 3 | 1350 | 75 | 67 | 85 | 36.9 | 0.64 | 15.87
DSH036*D | 3 | 1350 | 75 | 71 | 85 | 38.5 | 0.5 | 12.5
DSH036*D | 3 | 1350 | 75 | 59 | 95 | 33.7 | 0.91 | 20.55
DSH036*D | 3 | 1350 | 75 | 63 | 95 | 34.2 | 0.82 | 18.83
DSH036*D | 3 | 1350 | 75 | 67 | 95 | 35.3 | 0.66 | 15.61
DSH036*D | 3 | 1350 | 75 | 71 | 95 | 36.9 | 0.5 | 12.3
DSH036*D | 3 | 1350 | 75 | 59 | 105 | 31.8 | 0.95 | 20.32
DSH036*D | 3 | 1350 | 75 | 63 | 105 | 32.3 | 0.86 | 18.6
DSH036*D | 3 | 1350 | 75 | 67 | 105 | 33.3 | 0.69 | 15.38
DSH036*D | 3 | 1350 | 75 | 71 | 105 | 35 | 0.5 | 12.1
DSH036*D | 3 | 1350 | 75 | 59 | 115 | 30 | 1 | 20.19
DSH036*D | 3 | 1350 | 75 | 63 | 115 | 30.5 | 0.96 | 19.68
DSH036*D | 3 | 1350 | 75 | 67 | 115 | 31.5 | 0.77 | 16.46
DSH036*D | 3 | 1350 | 75 | 71 | 115 | 33.2 | 0.6 | 13.1
DSH036*D | 3 | 1350 | 80 | 59 | 65 | 36.8 | 0.99 | 24.43
DSH036*D | 3 | 1350 | 80 | 63 | 65 | 37.3 | 0.91 | 22.71
DSH036*D | 3 | 1350 | 80 | 67 | 65 | 38.3 | 0.76 | 19.49
DSH036*D | 3 | 1350 | 80 | 71 | 65 | 39.9 | 0.6 | 16.2
DSH036*D | 3 | 1350 | 80 | 59 | 75 | 36.4 | 0.99 | 24.38
DSH036*D | 3 | 1350 | 80 | 63 | 75 | 36.9 | 0.91 | 22.66
DSH036*D | 3 | 1350 | 80 | 67 | 75 | 38 | 0.76 | 19.45
DSH036*D | 3 | 1350 | 80 | 71 | 75 | 39.6 | 0.6 | 16.1
DSH036*D | 3 | 1350 | 80 | 59 | 85 | 35.5 | 1 | 23.91
DSH036*D | 3 | 1350 | 80 | 63 | 85 | 36 | 0.94 | 22.9
DSH036*D | 3 | 1350 | 80 | 67 | 85 | 37.1 | 0.79 | 19.69
DSH036*D | 3 | 1350 | 80 | 71 | 85 | 38.7 | 0.6 | 16.4
DSH036*D | 3 | 1350 | 80 | 59 | 95 | 33.9 | 1 | 22.83
DSH036*D | 3 | 1350 | 80 | 63 | 95 | 34.4 | 0.98 | 22.64
DSH036*D | 3 | 1350 | 80 | 67 | 95 | 35.5 | 0.81 | 19.43
DSH036*D | 3 | 1350 | 80 | 71 | 95 | 37.1 | 0.6 | 16.1
DSH036*D | 3 | 1350 | 80 | 59 | 105 | 32 | 1 | 21.52
DSH036*D | 3 | 1350 | 80 | 63 | 105 | 32.5 | 1 | 21.85
DSH036*D | 3 | 1350 | 80 | 67 | 105 | 33.5 | 0.85 | 19.2
DSH036*D | 3 | 1350 | 80 | 71 | 105 | 35.1 | 0.7 | 15.9
DSH036*D | 3 | 1350 | 80 | 59 | 115 | 30.2 | 1 | 20.31
DSH036*D | 3 | 1350 | 80 | 63 | 115 | 30.7 | 1 | 20.65
DSH036*D | 3 | 1350 | 80 | 67 | 115 | 31.7 | 0.95 | 20.28
DSH036*D | 3 | 1350 | 80 | 71 | 115 | 33.4 | 0.8 | 16.9
DSH036*D | 3 | 1350 | 85 | 59 | 65 | 37.4 | 1 | 25.15
DSH036*D | 3 | 1350 | 85 | 63 | 65 | 37.9 | 1 | 25.49
DSH036*D | 3 | 1350 | 85 | 67 | 65 | 38.9 | 0.87 | 22.87
DSH036*D | 3 | 1350 | 85 | 71 | 65 | 40.5 | 0.7 | 19.5
DSH036*D | 3 | 1350 | 85 | 59 | 75 | 37 | 1 | 24.94
DSH036*D | 3 | 1350 | 85 | 63 | 75 | 37.5 | 1 | 25.28
DSH036*D | 3 | 1350 | 85 | 67 | 75 | 38.6 | 0.88 | 22.83
DSH036*D | 3 | 1350 | 85 | 71 | 75 | 40.2 | 0.7 | 19.5
DSH036*D | 3 | 1350 | 85 | 59 | 85 | 36.1 | 1 | 24.31
DSH036*D | 3 | 1350 | 85 | 63 | 85 | 36.6 | 1 | 24.65
DSH036*D | 3 | 1350 | 85 | 67 | 85 | 37.7 | 0.91 | 23.07
DSH036*D | 3 | 1350 | 85 | 71 | 85 | 39.3 | 0.7 | 19.7
DSH036*D | 3 | 1350 | 85 | 59 | 95 | 34.5 | 1 | 23.24
DSH036*D | 3 | 1350 | 85 | 63 | 95 | 35 | 1 | 23.57
DSH036*D | 3 | 1350 | 85 | 67 | 95 | 36.1 | 0.94 | 22.81
DSH036*D | 3 | 1350 | 85 | 71 | 95 | 37.7 | 0.8 | 19.5
DSH036*D | 3 | 1350 | 85 | 59 | 105 | 32.6 | 1 | 21.92
DSH036*D | 3 | 1350 | 85 | 63 | 105 | 33.1 | 1 | 22.26
DSH036*D | 3 | 1350 | 85 | 67 | 105 | 34.1 | 0.98 | 22.58
DSH036*D | 3 | 1350 | 85 | 71 | 105 | 35.7 | 0.8 | 19.2
DSH036*D | 3 | 1350 | 85 | 59 | 115 | 30.8 | 1 | 20.72
DSH036*D | 3 | 1350 | 85 | 63 | 115 | 31.3 | 1 | 21.06
DSH036*D | 3 | 1350 | 85 | 67 | 115 | 32.3 | 1 | 21.77
DSH036*D | 3 | 1350 | 85 | 71 | 115 | 34 | 0.9 | 20.3
DSH048*D | 4 | 1200 | 70 | 59 | 65 | 46.1 | 0.58 | 20.41
DSH048*D | 4 | 1200 | 70 | 63 | 65 | 46.8 | 0.53 | 18.64
DSH048*D | 4 | 1200 | 70 | 67 | 65 | 48.2 | 0.42 | 15.33
DSH048*D | 4 | 1200 | 70 | 59 | 75 | 45.7 | 0.59 | 20.37
DSH048*D | 4 | 1200 | 70 | 63 | 75 | 46.3 | 0.53 | 18.59
DSH048*D | 4 | 1200 | 70 | 67 | 75 | 47.7 | 0.42 | 15.28
DSH048*D | 4 | 1200 | 70 | 59 | 85 | 44.5 | 0.61 | 20.62
DSH048*D | 4 | 1200 | 70 | 63 | 85 | 45.1 | 0.55 | 18.84
DSH048*D | 4 | 1200 | 70 | 67 | 85 | 46.5 | 0.44 | 15.53
DSH048*D | 4 | 1200 | 70 | 59 | 95 | 42.4 | 0.63 | 20.35
DSH048*D | 4 | 1200 | 70 | 63 | 95 | 43 | 0.57 | 18.57
DSH048*D | 4 | 1200 | 70 | 67 | 95 | 44.4 | 0.45 | 15.26
DSH048*D | 4 | 1200 | 70 | 59 | 105 | 39.8 | 0.67 | 20.11
DSH048*D | 4 | 1200 | 70 | 63 | 105 | 40.4 | 0.6 | 18.34
DSH048*D | 4 | 1200 | 70 | 67 | 105 | 41.8 | 0.47 | 15.02
DSH048*D | 4 | 1200 | 70 | 59 | 115 | 37.4 | 0.75 | 21.22
DSH048*D | 4 | 1200 | 70 | 63 | 115 | 38.1 | 0.67 | 19.45
DSH048*D | 4 | 1200 | 70 | 67 | 115 | 39.5 | 0.54 | 16.14
DSH048*D | 4 | 1200 | 75 | 59 | 65 | 46.3 | 0.69 | 24.31
DSH048*D | 4 | 1200 | 75 | 63 | 65 | 47 | 0.63 | 22.54
DSH048*D | 4 | 1200 | 75 | 67 | 65 | 48.4 | 0.52 | 19.23
DSH048*D | 4 | 1200 | 75 | 71 | 65 | 50.5 | 0.4 | 15.8
DSH048*D | 4 | 1200 | 75 | 59 | 75 | 45.9 | 0.7 | 24.27
DSH048*D | 4 | 1200 | 75 | 63 | 75 | 46.6 | 0.64 | 22.49
DSH048*D | 4 | 1200 | 75 | 67 | 75 | 48 | 0.53 | 19.18
DSH048*D | 4 | 1200 | 75 | 71 | 75 | 50.1 | 0.4 | 15.7
DSH048*D | 4 | 1200 | 75 | 59 | 85 | 44.7 | 0.72 | 24.52
DSH048*D | 4 | 1200 | 75 | 63 | 85 | 45.4 | 0.66 | 22.74
DSH048*D | 4 | 1200 | 75 | 67 | 85 | 46.8 | 0.55 | 19.43
DSH048*D | 4 | 1200 | 75 | 71 | 85 | 48.9 | 0.4 | 16
DSH048*D | 4 | 1200 | 75 | 59 | 95 | 42.6 | 0.75 | 24.25
DSH048*D | 4 | 1200 | 75 | 63 | 95 | 43.3 | 0.69 | 22.47
DSH048*D | 4 | 1200 | 75 | 67 | 95 | 44.7 | 0.57 | 19.16
DSH048*D | 4 | 1200 | 75 | 71 | 95 | 46.8 | 0.4 | 15.7
DSH048*D | 4 | 1200 | 75 | 59 | 105 | 40 | 0.79 | 24.01
DSH048*D | 4 | 1200 | 75 | 63 | 105 | 40.7 | 0.72 | 22.24
DSH048*D | 4 | 1200 | 75 | 67 | 105 | 42.1 | 0.59 | 18.92
DSH048*D | 4 | 1200 | 75 | 71 | 105 | 44.2 | 0.5 | 15.5
DSH048*D | 4 | 1200 | 75 | 59 | 115 | 37.7 | 0.88 | 25.12
DSH048*D | 4 | 1200 | 75 | 63 | 115 | 38.3 | 0.8 | 23.35
DSH048*D | 4 | 1200 | 75 | 67 | 115 | 39.7 | 0.67 | 20.04
DSH048*D | 4 | 1200 | 75 | 71 | 115 | 41.9 | 0.5 | 16.6
DSH048*D | 4 | 1200 | 80 | 59 | 65 | 46.6 | 0.8 | 28.24
DSH048*D | 4 | 1200 | 80 | 63 | 65 | 47.2 | 0.74 | 26.47
DSH048*D | 4 | 1200 | 80 | 67 | 65 | 48.6 | 0.63 | 23.16
DSH048*D | 4 | 1200 | 80 | 71 | 65 | 50.8 | 0.5 | 19.7
DSH048*D | 4 | 1200 | 80 | 59 | 75 | 46.2 | 0.81 | 28.19
DSH048*D | 4 | 1200 | 80 | 63 | 75 | 46.8 | 0.74 | 26.42
DSH048*D | 4 | 1200 | 80 | 67 | 75 | 48.2 | 0.63 | 23.11
DSH048*D | 4 | 1200 | 80 | 71 | 75 | 50.4 | 0.5 | 19.7
DSH048*D | 4 | 1200 | 80 | 59 | 85 | 44.9 | 0.84 | 28.44
DSH048*D | 4 | 1200 | 80 | 63 | 85 | 45.6 | 0.77 | 26.67
DSH048*D | 4 | 1200 | 80 | 67 | 85 | 47 | 0.66 | 23.36
DSH048*D | 4 | 1200 | 80 | 71 | 85 | 49.1 | 0.5 | 19.9
DSH048*D | 4 | 1200 | 80 | 59 | 95 | 42.8 | 0.87 | 28.17
DSH048*D | 4 | 1200 | 80 | 63 | 95 | 43.5 | 0.8 | 26.4
DSH048*D | 4 | 1200 | 80 | 67 | 95 | 44.9 | 0.68 | 23.09
DSH048*D | 4 | 1200 | 80 | 71 | 95 | 47 | 0.6 | 19.7
DSH048*D | 4 | 1200 | 80 | 59 | 105 | 40.3 | 0.92 | 27.94
DSH048*D | 4 | 1200 | 80 | 63 | 105 | 40.9 | 0.84 | 26.16
DSH048*D | 4 | 1200 | 80 | 67 | 105 | 42.3 | 0.71 | 22.85
DSH048*D | 4 | 1200 | 80 | 71 | 105 | 44.5 | 0.6 | 19.4
DSH048*D | 4 | 1200 | 80 | 59 | 115 | 37.9 | 1 | 28.73
DSH048*D | 4 | 1200 | 80 | 63 | 115 | 38.6 | 0.93 | 27.27
DSH048*D | 4 | 1200 | 80 | 67 | 115 | 40 | 0.79 | 23.96
DSH048*D | 4 | 1200 | 80 | 71 | 115 | 42.1 | 0.6 | 20.5
DSH048*D | 4 | 1200 | 85 | 59 | 65 | 47.4 | 0.88 | 31.72
DSH048*D | 4 | 1200 | 85 | 63 | 65 | 48 | 0.82 | 29.95
DSH048*D | 4 | 1200 | 85 | 67 | 65 | 49.4 | 0.71 | 26.64
DSH048*D | 4 | 1200 | 85 | 71 | 65 | 51.6 | 0.6 | 23.2
DSH048*D | 4 | 1200 | 85 | 59 | 75 | 47 | 0.89 | 31.68
DSH048*D | 4 | 1200 | 85 | 63 | 75 | 47.6 | 0.83 | 29.9
DSH048*D | 4 | 1200 | 85 | 67 | 75 | 49 | 0.72 | 26.59
DSH048*D | 4 | 1200 | 85 | 71 | 75 | 51.2 | 0.6 | 23.2
DSH048*D | 4 | 1200 | 85 | 59 | 85 | 45.7 | 0.92 | 31.92
DSH048*D | 4 | 1200 | 85 | 63 | 85 | 46.4 | 0.86 | 30.15
DSH048*D | 4 | 1200 | 85 | 67 | 85 | 47.8 | 0.74 | 26.84
DSH048*D | 4 | 1200 | 85 | 71 | 85 | 49.9 | 0.6 | 23.4
DSH048*D | 4 | 1200 | 85 | 59 | 95 | 43.6 | 0.96 | 31.66
DSH048*D | 4 | 1200 | 85 | 63 | 95 | 44.3 | 0.89 | 29.88
DSH048*D | 4 | 1200 | 85 | 67 | 95 | 45.7 | 0.77 | 26.57
DSH048*D | 4 | 1200 | 85 | 71 | 95 | 47.8 | 0.6 | 23.1
DSH048*D | 4 | 1200 | 85 | 59 | 105 | 41.1 | 1 | 31.11
DSH048*D | 4 | 1200 | 85 | 63 | 105 | 41.7 | 0.94 | 29.65
DSH048*D | 4 | 1200 | 85 | 67 | 105 | 43.1 | 0.81 | 26.33
DSH048*D | 4 | 1200 | 85 | 71 | 105 | 45.3 | 0.7 | 22.9
DSH048*D | 4 | 1200 | 85 | 59 | 115 | 38.7 | 1 | 29.33
DSH048*D | 4 | 1200 | 85 | 63 | 115 | 39.4 | 1 | 29.83
DSH048*D | 4 | 1200 | 85 | 67 | 115 | 40.8 | 0.89 | 27.44
DSH048*D | 4 | 1200 | 85 | 71 | 115 | 42.9 | 0.7 | 24
DSH048*D | 4 | 1580 | 70 | 59 | 65 | 47.2 | 0.67 | 18.11
DSH048*D | 4 | 1580 | 70 | 63 | 65 | 47.9 | 0.59 | 16.33
DSH048*D | 4 | 1580 | 70 | 67 | 65 | 49.3 | 0.46 | 13.02
DSH048*D | 4 | 1580 | 70 | 59 | 75 | 46.8 | 0.67 | 18.06
DSH048*D | 4 | 1580 | 70 | 63 | 75 | 47.4 | 0.6 | 16.29
DSH048*D | 4 | 1580 | 70 | 67 | 75 | 48.8 | 0.46 | 12.97
DSH048*D | 4 | 1580 | 70 | 59 | 85 | 45.6 | 0.7 | 18.31
DSH048*D | 4 | 1580 | 70 | 63 | 85 | 46.2 | 0.62 | 16.54
DSH048*D | 4 | 1580 | 70 | 67 | 85 | 47.6 | 0.48 | 13.22
DSH048*D | 4 | 1580 | 70 | 59 | 95 | 43.5 | 0.72 | 18.04
DSH048*D | 4 | 1580 | 70 | 63 | 95 | 44.1 | 0.64 | 16.27
DSH048*D | 4 | 1580 | 70 | 67 | 95 | 45.5 | 0.49 | 12.96
DSH048*D | 4 | 1580 | 70 | 59 | 105 | 40.9 | 0.76 | 17.81
DSH048*D | 4 | 1580 | 70 | 63 | 105 | 41.5 | 0.67 | 16.03
DSH048*D | 4 | 1580 | 70 | 67 | 105 | 42.9 | 0.51 | 12.72
DSH048*D | 4 | 1580 | 70 | 59 | 115 | 38.5 | 0.85 | 18.92
DSH048*D | 4 | 1580 | 70 | 63 | 115 | 39.2 | 0.76 | 17.14
DSH048*D | 4 | 1580 | 70 | 67 | 115 | 40.6 | 0.59 | 13.83
DSH048*D | 4 | 1580 | 75 | 59 | 65 | 47.4 | 0.81 | 22.01
DSH048*D | 4 | 1580 | 75 | 63 | 65 | 48.1 | 0.73 | 20.23
DSH048*D | 4 | 1580 | 75 | 67 | 65 | 49.5 | 0.59 | 16.92
DSH048*D | 4 | 1580 | 75 | 71 | 65 | 51.6 | 0.5 | 13.5
DSH048*D | 4 | 1580 | 75 | 59 | 75 | 47 | 0.81 | 21.96
DSH048*D | 4 | 1580 | 75 | 63 | 75 | 47.7 | 0.74 | 20.19
DSH048*D | 4 | 1580 | 75 | 67 | 75 | 49.1 | 0.6 | 16.87
DSH048*D | 4 | 1580 | 75 | 71 | 75 | 51.2 | 0.5 | 13.4
DSH048*D | 4 | 1580 | 75 | 59 | 85 | 45.8 | 0.84 | 22.21
DSH048*D | 4 | 1580 | 75 | 63 | 85 | 46.5 | 0.76 | 20.44
DSH048*D | 4 | 1580 | 75 | 67 | 85 | 47.9 | 0.62 | 17.12
DSH048*D | 4 | 1580 | 75 | 71 | 85 | 50 | 0.5 | 13.7
DSH048*D | 4 | 1580 | 75 | 59 | 95 | 43.7 | 0.87 | 21.94
DSH048*D | 4 | 1580 | 75 | 63 | 95 | 44.4 | 0.79 | 20.17
DSH048*D | 4 | 1580 | 75 | 67 | 95 | 45.8 | 0.64 | 16.86
DSH048*D | 4 | 1580 | 75 | 71 | 95 | 47.9 | 0.5 | 13.4
DSH048*D | 4 | 1580 | 75 | 59 | 105 | 41.1 | 0.92 | 21.71
DSH048*D | 4 | 1580 | 75 | 63 | 105 | 41.8 | 0.83 | 19.93
DSH048*D | 4 | 1580 | 75 | 67 | 105 | 43.2 | 0.67 | 16.62
DSH048*D | 4 | 1580 | 75 | 71 | 105 | 45.3 | 0.5 | 13.2
DSH048*D | 4 | 1580 | 75 | 59 | 115 | 38.8 | 1 | 22.31
DSH048*D | 4 | 1580 | 75 | 63 | 115 | 39.4 | 0.93 | 21.04
DSH048*D | 4 | 1580 | 75 | 67 | 115 | 40.8 | 0.75 | 17.73
DSH048*D | 4 | 1580 | 75 | 71 | 115 | 43 | 0.6 | 14.3
DSH048*D | 4 | 1580 | 80 | 59 | 65 | 47.7 | 0.95 | 25.94
DSH048*D | 4 | 1580 | 80 | 63 | 65 | 48.3 | 0.87 | 24.16
DSH048*D | 4 | 1580 | 80 | 67 | 65 | 49.7 | 0.73 | 20.85
DSH048*D | 4 | 1580 | 80 | 71 | 65 | 51.9 | 0.6 | 17.4
DSH048*D | 4 | 1580 | 80 | 59 | 75 | 47.3 | 0.95 | 25.89
DSH048*D | 4 | 1580 | 80 | 63 | 75 | 47.9 | 0.87 | 24.11
DSH048*D | 4 | 1580 | 80 | 67 | 75 | 49.3 | 0.73 | 20.8
DSH048*D | 4 | 1580 | 80 | 71 | 75 | 51.5 | 0.6 | 17.4
DSH048*D | 4 | 1580 | 80 | 59 | 85 | 46 | 0.99 | 26.14
DSH048*D | 4 | 1580 | 80 | 63 | 85 | 46.7 | 0.91 | 24.36
DSH048*D | 4 | 1580 | 80 | 67 | 85 | 48.1 | 0.76 | 21.05
DSH048*D | 4 | 1580 | 80 | 71 | 85 | 50.2 | 0.6 | 17.6
DSH048*D | 4 | 1580 | 80 | 59 | 95 | 43.9 | 1 | 25.28
DSH048*D | 4 | 1580 | 80 | 63 | 95 | 44.6 | 0.94 | 24.09
DSH048*D | 4 | 1580 | 80 | 67 | 95 | 46 | 0.79 | 20.78
DSH048*D | 4 | 1580 | 80 | 71 | 95 | 48.1 | 0.6 | 17.4
DSH048*D | 4 | 1580 | 80 | 59 | 105 | 41.4 | 1 | 23.8
DSH048*D | 4 | 1580 | 80 | 63 | 105 | 42 | 0.99 | 23.86
DSH048*D | 4 | 1580 | 80 | 67 | 105 | 43.4 | 0.82 | 20.55
DSH048*D | 4 | 1580 | 80 | 71 | 105 | 45.6 | 0.7 | 17.1
DSH048*D | 4 | 1580 | 80 | 59 | 115 | 39 | 1 | 22.45
DSH048*D | 4 | 1580 | 80 | 63 | 115 | 39.7 | 1 | 22.83
DSH048*D | 4 | 1580 | 80 | 67 | 115 | 41.1 | 0.92 | 21.66
DSH048*D | 4 | 1580 | 80 | 71 | 115 | 43.2 | 0.7 | 18.2
DSH048*D | 4 | 1580 | 85 | 59 | 65 | 48.5 | 1 | 27.89
DSH048*D | 4 | 1580 | 85 | 63 | 65 | 49.1 | 0.98 | 27.64
DSH048*D | 4 | 1580 | 85 | 67 | 65 | 50.5 | 0.84 | 24.33
DSH048*D | 4 | 1580 | 85 | 71 | 65 | 52.7 | 0.7 | 20.9
DSH048*D | 4 | 1580 | 85 | 59 | 75 | 48.1 | 1 | 27.65
DSH048*D | 4 | 1580 | 85 | 63 | 75 | 48.7 | 0.98 | 27.6
DSH048*D | 4 | 1580 | 85 | 67 | 75 | 50.1 | 0.84 | 24.28
DSH048*D | 4 | 1580 | 85 | 71 | 75 | 52.2 | 0.7 | 20.9
DSH048*D | 4 | 1580 | 85 | 59 | 85 | 46.8 | 1 | 26.95
DSH048*D | 4 | 1580 | 85 | 63 | 85 | 47.5 | 1 | 27.33
DSH048*D | 4 | 1580 | 85 | 67 | 85 | 48.9 | 0.87 | 24.53
DSH048*D | 4 | 1580 | 85 | 71 | 85 | 51 | 0.7 | 21.1
DSH048*D | 4 | 1580 | 85 | 59 | 95 | 44.7 | 1 | 25.74
DSH048*D | 4 | 1580 | 85 | 63 | 95 | 45.4 | 1 | 26.12
DSH048*D | 4 | 1580 | 85 | 67 | 95 | 46.8 | 0.9 | 24.27
DSH048*D | 4 | 1580 | 85 | 71 | 95 | 48.9 | 0.7 | 20.8
DSH048*D | 4 | 1580 | 85 | 59 | 105 | 42.2 | 1 | 24.26
DSH048*D | 4 | 1580 | 85 | 63 | 105 | 42.8 | 1 | 24.64
DSH048*D | 4 | 1580 | 85 | 67 | 105 | 44.2 | 0.94 | 24.03
DSH048*D | 4 | 1580 | 85 | 71 | 105 | 46.4 | 0.8 | 20.6
DSH048*D | 4 | 1580 | 85 | 59 | 115 | 39.8 | 1 | 22.91
DSH048*D | 4 | 1580 | 85 | 63 | 115 | 40.5 | 1 | 23.29
DSH048*D | 4 | 1580 | 85 | 67 | 115 | 41.9 | 1 | 24.09
DSH048*D | 4 | 1580 | 85 | 71 | 115 | 44 | 0.9 | 21.7
DSH048*D | 4 | 1800 | 70 | 59 | 65 | 48 | 0.71 | 17.11
DSH048*D | 4 | 1800 | 70 | 63 | 65 | 48.7 | 0.62 | 15.34
DSH048*D | 4 | 1800 | 70 | 67 | 65 | 50.1 | 0.48 | 12.03
DSH048*D | 4 | 1800 | 70 | 59 | 75 | 47.6 | 0.71 | 17.06
DSH048*D | 4 | 1800 | 70 | 63 | 75 | 48.3 | 0.63 | 15.29
DSH048*D | 4 | 1800 | 70 | 67 | 75 | 49.7 | 0.48 | 11.98
DSH048*D | 4 | 1800 | 70 | 59 | 85 | 46.4 | 0.74 | 17.31
DSH048*D | 4 | 1800 | 70 | 63 | 85 | 47.1 | 0.65 | 15.54
DSH048*D | 4 | 1800 | 70 | 67 | 85 | 48.4 | 0.5 | 12.23
DSH048*D | 4 | 1800 | 70 | 59 | 95 | 44.3 | 0.76 | 17.04
DSH048*D | 4 | 1800 | 70 | 63 | 95 | 44.9 | 0.67 | 15.27
DSH048*D | 4 | 1800 | 70 | 67 | 95 | 46.3 | 0.51 | 11.96
DSH048*D | 4 | 1800 | 70 | 59 | 105 | 41.7 | 0.8 | 16.81
DSH048*D | 4 | 1800 | 70 | 63 | 105 | 42.4 | 0.7 | 15.03
DSH048*D | 4 | 1800 | 70 | 67 | 105 | 43.8 | 0.53 | 11.72
DSH048*D | 4 | 1800 | 70 | 59 | 115 | 39.4 | 0.9 | 17.92
DSH048*D | 4 | 1800 | 70 | 63 | 115 | 40 | 0.8 | 16.14
DSH048*D | 4 | 1800 | 70 | 67 | 115 | 41.4 | 0.61 | 12.83
DSH048*D | 4 | 1800 | 75 | 59 | 65 | 48.3 | 0.86 | 21.01
DSH048*D | 4 | 1800 | 75 | 63 | 65 | 48.9 | 0.78 | 19.24
DSH048*D | 4 | 1800 | 75 | 67 | 65 | 50.3 | 0.63 | 15.93
DSH048*D | 4 | 1800 | 75 | 71 | 65 | 52.5 | 0.5 | 12.5
DSH048*D | 4 | 1800 | 75 | 59 | 75 | 47.9 | 0.87 | 20.96
DSH048*D | 4 | 1800 | 75 | 63 | 75 | 48.5 | 0.78 | 19.19
DSH048*D | 4 | 1800 | 75 | 67 | 75 | 49.9 | 0.63 | 15.88
DSH048*D | 4 | 1800 | 75 | 71 | 75 | 52 | 0.5 | 12.4
DSH048*D | 4 | 1800 | 75 | 59 | 85 | 46.6 | 0.9 | 21.21
DSH048*D | 4 | 1800 | 75 | 63 | 85 | 47.3 | 0.81 | 19.44
DSH048*D | 4 | 1800 | 75 | 67 | 85 | 48.7 | 0.66 | 16.13
DSH048*D | 4 | 1800 | 75 | 71 | 85 | 50.8 | 0.5 | 12.7
DSH048*D | 4 | 1800 | 75 | 59 | 95 | 44.5 | 0.93 | 20.94
DSH048*D | 4 | 1800 | 75 | 63 | 95 | 45.2 | 0.84 | 19.17
DSH048*D | 4 | 1800 | 75 | 67 | 95 | 46.6 | 0.67 | 15.86
DSH048*D | 4 | 1800 | 75 | 71 | 95 | 48.7 | 0.5 | 12.4
DSH048*D | 4 | 1800 | 75 | 59 | 105 | 42 | 0.98 | 20.71
DSH048*D | 4 | 1800 | 75 | 63 | 105 | 42.6 | 0.88 | 18.93
DSH048*D | 4 | 1800 | 75 | 67 | 105 | 44 | 0.7 | 15.62
DSH048*D | 4 | 1800 | 75 | 71 | 105 | 46.2 | 0.5 | 12.2
DSH048*D | 4 | 1800 | 75 | 59 | 115 | 39.6 | 1 | 20.01
DSH048*D | 4 | 1800 | 75 | 63 | 115 | 40.3 | 0.99 | 20.04
DSH048*D | 4 | 1800 | 75 | 67 | 115 | 41.7 | 0.79 | 16.73
DSH048*D | 4 | 1800 | 75 | 71 | 115 | 43.8 | 0.6 | 13.3
DSH048*D | 4 | 1800 | 80 | 59 | 65 | 48.5 | 1 | 24.5
DSH048*D | 4 | 1800 | 80 | 63 | 65 | 49.2 | 0.93 | 23.16
DSH048*D | 4 | 1800 | 80 | 67 | 65 | 50.6 | 0.78 | 19.85
DSH048*D | 4 | 1800 | 80 | 71 | 65 | 52.7 | 0.6 | 16.4
DSH048*D | 4 | 1800 | 80 | 59 | 75 | 48.1 | 1 | 24.29
DSH048*D | 4 | 1800 | 80 | 63 | 75 | 48.8 | 0.94 | 23.12
DSH048*D | 4 | 1800 | 80 | 67 | 75 | 50.2 | 0.78 | 19.8
DSH048*D | 4 | 1800 | 80 | 71 | 75 | 52.3 | 0.6 | 16.4
DSH048*D | 4 | 1800 | 80 | 59 | 85 | 46.9 | 1 | 23.67
DSH048*D | 4 | 1800 | 80 | 63 | 85 | 47.5 | 0.97 | 23.36
DSH048*D | 4 | 1800 | 80 | 67 | 85 | 48.9 | 0.81 | 20.05
DSH048*D | 4 | 1800 | 80 | 71 | 85 | 51.1 | 0.6 | 16.6
DSH048*D | 4 | 1800 | 80 | 59 | 95 | 44.8 | 1 | 22.61
DSH048*D | 4 | 1800 | 80 | 63 | 95 | 45.4 | 1 | 22.95
DSH048*D | 4 | 1800 | 80 | 67 | 95 | 46.8 | 0.84 | 19.79
DSH048*D | 4 | 1800 | 80 | 71 | 95 | 49 | 0.7 | 16.4
DSH048*D | 4 | 1800 | 80 | 59 | 105 | 42.2 | 1 | 21.31
DSH048*D | 4 | 1800 | 80 | 63 | 105 | 42.9 | 1 | 21.65
DSH048*D | 4 | 1800 | 80 | 67 | 105 | 44.3 | 0.87 | 19.55
DSH048*D | 4 | 1800 | 80 | 71 | 105 | 46.4 | 0.7 | 16.1
DSH048*D | 4 | 1800 | 80 | 59 | 115 | 39.9 | 1 | 20.13
DSH048*D | 4 | 1800 | 80 | 63 | 115 | 40.5 | 1 | 20.46
DSH048*D | 4 | 1800 | 80 | 67 | 115 | 41.9 | 0.98 | 20.66
DSH048*D | 4 | 1800 | 80 | 71 | 115 | 44.1 | 0.8 | 17.2
DSH048*D | 4 | 1800 | 85 | 59 | 65 | 49.3 | 1 | 24.9
DSH048*D | 4 | 1800 | 85 | 63 | 65 | 50 | 1 | 25.23
DSH048*D | 4 | 1800 | 85 | 67 | 65 | 51.4 | 0.9 | 23.33
DSH048*D | 4 | 1800 | 85 | 71 | 65 | 53.5 | 0.7 | 19.9
DSH048*D | 4 | 1800 | 85 | 59 | 75 | 48.9 | 1 | 24.69
DSH048*D | 4 | 1800 | 85 | 63 | 75 | 49.5 | 1 | 25.02
DSH048*D | 4 | 1800 | 85 | 67 | 75 | 50.9 | 0.91 | 23.29
DSH048*D | 4 | 1800 | 85 | 71 | 75 | 53.1 | 0.7 | 19.9
DSH048*D | 4 | 1800 | 85 | 59 | 85 | 47.7 | 1 | 24.07
DSH048*D | 4 | 1800 | 85 | 63 | 85 | 48.3 | 1 | 24.41
DSH048*D | 4 | 1800 | 85 | 67 | 85 | 49.7 | 0.94 | 23.54
DSH048*D | 4 | 1800 | 85 | 71 | 85 | 51.9 | 0.8 | 20.1
DSH048*D | 4 | 1800 | 85 | 59 | 95 | 45.6 | 1 | 23.01
DSH048*D | 4 | 1800 | 85 | 63 | 95 | 46.2 | 1 | 23.34
DSH048*D | 4 | 1800 | 85 | 67 | 95 | 47.6 | 0.97 | 23.27
DSH048*D | 4 | 1800 | 85 | 71 | 95 | 49.8 | 0.8 | 19.8
DSH048*D | 4 | 1800 | 85 | 59 | 105 | 43 | 1 | 21.71
DSH048*D | 4 | 1800 | 85 | 63 | 105 | 43.7 | 1 | 22.05
DSH048*D | 4 | 1800 | 85 | 67 | 105 | 45.1 | 1 | 22.75
DSH048*D | 4 | 1800 | 85 | 71 | 105 | 47.2 | 0.8 | 19.6
DSH048*D | 4 | 1800 | 85 | 59 | 115 | 40.6 | 1 | 20.53
DSH048*D | 4 | 1800 | 85 | 63 | 115 | 41.3 | 1 | 20.86
DSH048*D | 4 | 1800 | 85 | 67 | 115 | 42.7 | 1 | 21.57
DSH048*D | 4 | 1800 | 85 | 71 | 115 | 44.8 | 0.9 | 20.7
DSH060*D | 5 | 1500 | 70 | 59 | 65 | 57.8 | 0.59 | 20.85
DSH060*D | 5 | 1500 | 70 | 63 | 65 | 58.7 | 0.53 | 18.99
DSH060*D | 5 | 1500 | 70 | 67 | 65 | 60.4 | 0.42 | 15.53
DSH060*D | 5 | 1500 | 70 | 59 | 75 | 57.3 | 0.6 | 20.8
DSH060*D | 5 | 1500 | 70 | 63 | 75 | 58.1 | 0.54 | 18.94
DSH060*D | 5 | 1500 | 70 | 67 | 75 | 59.9 | 0.43 | 15.48
DSH060*D | 5 | 1500 | 70 | 59 | 85 | 55.8 | 0.62 | 21.06
DSH060*D | 5 | 1500 | 70 | 63 | 85 | 56.6 | 0.56 | 19.2
DSH060*D | 5 | 1500 | 70 | 67 | 85 | 58.4 | 0.44 | 15.74
DSH060*D | 5 | 1500 | 70 | 59 | 95 | 53.2 | 0.64 | 20.78
DSH060*D | 5 | 1500 | 70 | 63 | 95 | 54 | 0.58 | 18.92
DSH060*D | 5 | 1500 | 70 | 67 | 95 | 55.7 | 0.46 | 15.46
DSH060*D | 5 | 1500 | 70 | 59 | 105 | 49.9 | 0.68 | 20.53
DSH060*D | 5 | 1500 | 70 | 63 | 105 | 50.8 | 0.61 | 18.67
DSH060*D | 5 | 1500 | 70 | 67 | 105 | 52.5 | 0.48 | 15.21
DSH060*D | 5 | 1500 | 70 | 59 | 115 | 47 | 0.76 | 21.69
DSH060*D | 5 | 1500 | 70 | 63 | 115 | 47.8 | 0.68 | 19.84
DSH060*D | 5 | 1500 | 70 | 67 | 115 | 49.6 | 0.54 | 16.37
DSH060*D | 5 | 1500 | 75 | 59 | 65 | 58.1 | 0.71 | 24.93
DSH060*D | 5 | 1500 | 75 | 63 | 65 | 59 | 0.65 | 23.07
DSH060*D | 5 | 1500 | 75 | 67 | 65 | 60.7 | 0.53 | 19.61
DSH060*D | 5 | 1500 | 75 | 71 | 65 | 63.4 | 0.4 | 16
DSH060*D | 5 | 1500 | 75 | 59 | 75 | 57.6 | 0.71 | 24.88
DSH060*D | 5 | 1500 | 75 | 63 | 75 | 58.4 | 0.65 | 23.02
DSH060*D | 5 | 1500 | 75 | 67 | 75 | 60.2 | 0.54 | 19.56
DSH060*D | 5 | 1500 | 75 | 71 | 75 | 62.9 | 0.4 | 16
DSH060*D | 5 | 1500 | 75 | 59 | 85 | 56.1 | 0.74 | 25.14
DSH060*D | 5 | 1500 | 75 | 63 | 85 | 56.9 | 0.67 | 23.28
DSH060*D | 5 | 1500 | 75 | 67 | 85 | 58.7 | 0.56 | 19.82
DSH060*D | 5 | 1500 | 75 | 71 | 85 | 61.3 | 0.4 | 16.2
DSH060*D | 5 | 1500 | 75 | 59 | 95 | 53.5 | 0.77 | 24.86
DSH060*D | 5 | 1500 | 75 | 63 | 95 | 54.3 | 0.7 | 23
DSH060*D | 5 | 1500 | 75 | 67 | 95 | 56 | 0.58 | 19.54
DSH060*D | 5 | 1500 | 75 | 71 | 95 | 58.7 | 0.4 | 15.9
DSH060*D | 5 | 1500 | 75 | 59 | 105 | 50.3 | 0.81 | 24.61
DSH060*D | 5 | 1500 | 75 | 63 | 105 | 51.1 | 0.74 | 22.76
DSH060*D | 5 | 1500 | 75 | 67 | 105 | 52.8 | 0.6 | 19.29
DSH060*D | 5 | 1500 | 75 | 71 | 105 | 55.5 | 0.5 | 15.7
DSH060*D | 5 | 1500 | 75 | 59 | 115 | 47.3 | 0.9 | 25.77
DSH060*D | 5 | 1500 | 75 | 63 | 115 | 48.1 | 0.82 | 23.92
DSH060*D | 5 | 1500 | 75 | 67 | 115 | 49.9 | 0.68 | 20.45
DSH060*D | 5 | 1500 | 75 | 71 | 115 | 52.6 | 0.5 | 16.9
DSH060*D | 5 | 1500 | 80 | 59 | 65 | 58.4 | 0.82 | 29.04
DSH060*D | 5 | 1500 | 80 | 63 | 65 | 59.3 | 0.76 | 27.18
DSH060*D | 5 | 1500 | 80 | 67 | 65 | 61 | 0.64 | 23.72
DSH060*D | 5 | 1500 | 80 | 71 | 65 | 63.7 | 0.5 | 20.1
DSH060*D | 5 | 1500 | 80 | 59 | 75 | 57.9 | 0.83 | 28.99
DSH060*D | 5 | 1500 | 80 | 63 | 75 | 58.7 | 0.76 | 27.13
DSH060*D | 5 | 1500 | 80 | 67 | 75 | 60.5 | 0.65 | 23.67
DSH060*D | 5 | 1500 | 80 | 71 | 75 | 63.2 | 0.5 | 20.1
DSH060*D | 5 | 1500 | 80 | 59 | 85 | 56.4 | 0.86 | 29.25
DSH060*D | 5 | 1500 | 80 | 63 | 85 | 57.2 | 0.79 | 27.39
DSH060*D | 5 | 1500 | 80 | 67 | 85 | 59 | 0.67 | 23.93
DSH060*D | 5 | 1500 | 80 | 71 | 85 | 61.6 | 0.5 | 20.3
DSH060*D | 5 | 1500 | 80 | 59 | 95 | 53.8 | 0.89 | 28.97
DSH060*D | 5 | 1500 | 80 | 63 | 95 | 54.6 | 0.82 | 27.11
DSH060*D | 5 | 1500 | 80 | 67 | 95 | 56.3 | 0.69 | 23.65
DSH060*D | 5 | 1500 | 80 | 71 | 95 | 59 | 0.6 | 20.1
DSH060*D | 5 | 1500 | 80 | 59 | 105 | 50.6 | 0.94 | 28.72
DSH060*D | 5 | 1500 | 80 | 63 | 105 | 51.4 | 0.86 | 26.86
DSH060*D | 5 | 1500 | 80 | 67 | 105 | 53.1 | 0.73 | 23.4
DSH060*D | 5 | 1500 | 80 | 71 | 105 | 55.8 | 0.6 | 19.8
DSH060*D | 5 | 1500 | 80 | 59 | 115 | 47.6 | 1 | 28.86
DSH060*D | 5 | 1500 | 80 | 63 | 115 | 48.4 | 0.95 | 28.03
DSH060*D | 5 | 1500 | 80 | 67 | 115 | 50.2 | 0.81 | 24.56
DSH060*D | 5 | 1500 | 80 | 71 | 115 | 52.9 | 0.7 | 21
DSH060*D | 5 | 1500 | 85 | 59 | 65 | 59.4 | 0.91 | 32.68
DSH060*D | 5 | 1500 | 85 | 63 | 65 | 60.3 | 0.84 | 30.83
DSH060*D | 5 | 1500 | 85 | 67 | 65 | 62 | 0.73 | 27.36
DSH060*D | 5 | 1500 | 85 | 71 | 65 | 64.7 | 0.6 | 23.8
DSH060*D | 5 | 1500 | 85 | 59 | 75 | 58.9 | 0.91 | 32.63
DSH060*D | 5 | 1500 | 85 | 63 | 75 | 59.7 | 0.85 | 30.78
DSH060*D | 5 | 1500 | 85 | 67 | 75 | 61.5 | 0.73 | 27.31
DSH060*D | 5 | 1500 | 85 | 71 | 75 | 64.2 | 0.6 | 23.7
DSH060*D | 5 | 1500 | 85 | 59 | 85 | 57.4 | 0.95 | 32.89
DSH060*D | 5 | 1500 | 85 | 63 | 85 | 58.2 | 0.88 | 31.04
DSH060*D | 5 | 1500 | 85 | 67 | 85 | 60 | 0.76 | 27.57
DSH060*D | 5 | 1500 | 85 | 71 | 85 | 62.6 | 0.6 | 24
DSH060*D | 5 | 1500 | 85 | 59 | 95 | 54.8 | 0.98 | 32.61
DSH060*D | 5 | 1500 | 85 | 63 | 95 | 55.6 | 0.91 | 30.76
DSH060*D | 5 | 1500 | 85 | 67 | 95 | 57.3 | 0.79 | 27.29
DSH060*D | 5 | 1500 | 85 | 71 | 95 | 60 | 0.7 | 23.7
DSH060*D | 5 | 1500 | 85 | 59 | 105 | 51.5 | 1 | 31.24
DSH060*D | 5 | 1500 | 85 | 63 | 105 | 52.4 | 0.96 | 30.51
DSH060*D | 5 | 1500 | 85 | 67 | 105 | 54.1 | 0.82 | 27.04
DSH060*D | 5 | 1500 | 85 | 71 | 105 | 56.8 | 0.7 | 23.5
DSH060*D | 5 | 1500 | 85 | 59 | 115 | 48.6 | 1 | 29.46
DSH060*D | 5 | 1500 | 85 | 63 | 115 | 49.4 | 1 | 29.96
DSH060*D | 5 | 1500 | 85 | 67 | 115 | 51.2 | 0.91 | 28.2
DSH060*D | 5 | 1500 | 85 | 71 | 115 | 53.9 | 0.8 | 24.6
DSH060*D | 5 | 1870 | 70 | 59 | 65 | 59 | 0.66 | 18.95
DSH060*D | 5 | 1870 | 70 | 63 | 65 | 59.8 | 0.59 | 17.09
DSH060*D | 5 | 1870 | 70 | 67 | 65 | 61.6 | 0.46 | 13.63
DSH060*D | 5 | 1870 | 70 | 59 | 75 | 58.5 | 0.66 | 18.9
DSH060*D | 5 | 1870 | 70 | 63 | 75 | 59.3 | 0.59 | 17.04
DSH060*D | 5 | 1870 | 70 | 67 | 75 | 61 | 0.46 | 13.58
DSH060*D | 5 | 1870 | 70 | 59 | 85 | 56.9 | 0.69 | 19.16
DSH060*D | 5 | 1870 | 70 | 63 | 85 | 57.8 | 0.62 | 17.3
DSH060*D | 5 | 1870 | 70 | 67 | 85 | 59.5 | 0.48 | 13.84
DSH060*D | 5 | 1870 | 70 | 59 | 95 | 54.3 | 0.71 | 18.88
DSH060*D | 5 | 1870 | 70 | 63 | 95 | 55.1 | 0.63 | 17.02
DSH060*D | 5 | 1870 | 70 | 67 | 95 | 56.9 | 0.49 | 13.56
DSH060*D | 5 | 1870 | 70 | 59 | 105 | 51.1 | 0.75 | 18.63
DSH060*D | 5 | 1870 | 70 | 63 | 105 | 51.9 | 0.66 | 16.78
DSH060*D | 5 | 1870 | 70 | 67 | 105 | 53.7 | 0.51 | 13.31
DSH060*D | 5 | 1870 | 70 | 59 | 115 | 48.2 | 0.85 | 19.79
DSH060*D | 5 | 1870 | 70 | 63 | 115 | 49 | 0.75 | 17.94
DSH060*D | 5 | 1870 | 70 | 67 | 115 | 50.7 | 0.59 | 14.47
DSH060*D | 5 | 1870 | 75 | 59 | 65 | 59.3 | 0.8 | 23.03
DSH060*D | 5 | 1870 | 75 | 63 | 65 | 60.1 | 0.72 | 21.17
DSH060*D | 5 | 1870 | 75 | 67 | 65 | 61.9 | 0.59 | 17.71
DSH060*D | 5 | 1870 | 75 | 71 | 65 | 64.5 | 0.4 | 14.1
DSH060*D | 5 | 1870 | 75 | 59 | 75 | 58.8 | 0.8 | 22.98
DSH060*D | 5 | 1870 | 75 | 63 | 75 | 59.6 | 0.73 | 21.12
DSH060*D | 5 | 1870 | 75 | 67 | 75 | 61.4 | 0.59 | 17.66
DSH060*D | 5 | 1870 | 75 | 71 | 75 | 64 | 0.5 | 14.1
DSH060*D | 5 | 1870 | 75 | 59 | 85 | 57.3 | 0.84 | 23.24
DSH060*D | 5 | 1870 | 75 | 63 | 85 | 58.1 | 0.76 | 21.38
DSH060*D | 5 | 1870 | 75 | 67 | 85 | 59.8 | 0.62 | 17.92
DSH060*D | 5 | 1870 | 75 | 71 | 85 | 62.5 | 0.5 | 14.3
DSH060*D | 5 | 1870 | 75 | 59 | 95 | 54.6 | 0.86 | 22.96
DSH060*D | 5 | 1870 | 75 | 63 | 95 | 55.4 | 0.78 | 21.1
DSH060*D | 5 | 1870 | 75 | 67 | 95 | 57.2 | 0.63 | 17.64
DSH060*D | 5 | 1870 | 75 | 71 | 95 | 59.9 | 0.5 | 14
DSH060*D | 5 | 1870 | 75 | 59 | 105 | 51.4 | 0.91 | 22.71
DSH060*D | 5 | 1870 | 75 | 63 | 105 | 52.2 | 0.82 | 20.86
DSH060*D | 5 | 1870 | 75 | 67 | 105 | 54 | 0.66 | 17.39
DSH060*D | 5 | 1870 | 75 | 71 | 105 | 56.7 | 0.5 | 13.8
DSH060*D | 5 | 1870 | 75 | 59 | 115 | 48.5 | 1 | 23.57
DSH060*D | 5 | 1870 | 75 | 63 | 115 | 49.3 | 0.92 | 22.02
DSH060*D | 5 | 1870 | 75 | 67 | 115 | 51.1 | 0.75 | 18.55
DSH060*D | 5 | 1870 | 75 | 71 | 115 | 53.7 | 0.6 | 15
DSH060*D | 5 | 1870 | 80 | 59 | 65 | 59.6 | 0.94 | 27.14
DSH060*D | 5 | 1870 | 80 | 63 | 65 | 60.4 | 0.86 | 25.28
DSH060*D | 5 | 1870 | 80 | 67 | 65 | 62.2 | 0.72 | 21.82
DSH060*D | 5 | 1870 | 80 | 71 | 65 | 64.8 | 0.6 | 18.2
DSH060*D | 5 | 1870 | 80 | 59 | 75 | 59.1 | 0.94 | 27.09
DSH060*D | 5 | 1870 | 80 | 63 | 75 | 59.9 | 0.87 | 25.23
DSH060*D | 5 | 1870 | 80 | 67 | 75 | 61.7 | 0.73 | 21.77
DSH060*D | 5 | 1870 | 80 | 71 | 75 | 64.3 | 0.6 | 18.2
DSH060*D | 5 | 1870 | 80 | 59 | 85 | 57.6 | 0.98 | 27.35
DSH060*D | 5 | 1870 | 80 | 63 | 85 | 58.4 | 0.9 | 25.49
DSH060*D | 5 | 1870 | 80 | 67 | 85 | 60.1 | 0.75 | 22.03
DSH060*D | 5 | 1870 | 80 | 71 | 85 | 62.8 | 0.6 | 18.4
DSH060*D | 5 | 1870 | 80 | 59 | 95 | 54.9 | 1 | 26.7
DSH060*D | 5 | 1870 | 80 | 63 | 95 | 55.8 | 0.93 | 25.21
DSH060*D | 5 | 1870 | 80 | 67 | 95 | 57.5 | 0.78 | 21.75
DSH060*D | 5 | 1870 | 80 | 71 | 95 | 60.2 | 0.6 | 18.2
DSH060*D | 5 | 1870 | 80 | 59 | 105 | 51.7 | 1 | 25.14
DSH060*D | 5 | 1870 | 80 | 63 | 105 | 52.5 | 0.98 | 24.96
DSH060*D | 5 | 1870 | 80 | 67 | 105 | 54.3 | 0.81 | 21.5
DSH060*D | 5 | 1870 | 80 | 71 | 105 | 57 | 0.6 | 17.9
DSH060*D | 5 | 1870 | 80 | 59 | 115 | 48.8 | 1 | 23.71
DSH060*D | 5 | 1870 | 80 | 63 | 115 | 49.6 | 1 | 24.12
DSH060*D | 5 | 1870 | 80 | 67 | 115 | 51.4 | 0.91 | 22.66
DSH060*D | 5 | 1870 | 80 | 71 | 115 | 54 | 0.7 | 19.1
DSH060*D | 5 | 1870 | 85 | 59 | 65 | 60.6 | 1 | 29.46
DSH060*D | 5 | 1870 | 85 | 63 | 65 | 61.4 | 0.97 | 28.93
DSH060*D | 5 | 1870 | 85 | 67 | 65 | 63.2 | 0.83 | 25.46
DSH060*D | 5 | 1870 | 85 | 71 | 65 | 65.8 | 0.7 | 21.9
DSH060*D | 5 | 1870 | 85 | 59 | 75 | 60.1 | 1 | 29.2
DSH060*D | 5 | 1870 | 85 | 63 | 75 | 60.9 | 0.98 | 28.88
DSH060*D | 5 | 1870 | 85 | 67 | 75 | 62.6 | 0.83 | 25.41
DSH060*D | 5 | 1870 | 85 | 71 | 75 | 65.3 | 0.7 | 21.8
DSH060*D | 5 | 1870 | 85 | 59 | 85 | 58.5 | 1 | 28.46
DSH060*D | 5 | 1870 | 85 | 63 | 85 | 59.4 | 1 | 28.86
DSH060*D | 5 | 1870 | 85 | 67 | 85 | 61.1 | 0.86 | 25.67
DSH060*D | 5 | 1870 | 85 | 71 | 85 | 63.8 | 0.7 | 22.1
DSH060*D | 5 | 1870 | 85 | 59 | 95 | 55.9 | 1 | 27.18
DSH060*D | 5 | 1870 | 85 | 63 | 95 | 56.7 | 1 | 27.58
DSH060*D | 5 | 1870 | 85 | 67 | 95 | 58.5 | 0.89 | 25.39
DSH060*D | 5 | 1870 | 85 | 71 | 95 | 61.2 | 0.7 | 21.8
DSH060*D | 5 | 1870 | 85 | 59 | 105 | 52.7 | 1 | 25.62
DSH060*D | 5 | 1870 | 85 | 63 | 105 | 53.5 | 1 | 26.02
DSH060*D | 5 | 1870 | 85 | 67 | 105 | 55.3 | 0.94 | 25.14
DSH060*D | 5 | 1870 | 85 | 71 | 105 | 57.9 | 0.8 | 21.6
DSH060*D | 5 | 1870 | 85 | 59 | 115 | 49.8 | 1 | 24.19
DSH060*D | 5 | 1870 | 85 | 63 | 115 | 50.6 | 1 | 24.6
DSH060*D | 5 | 1870 | 85 | 67 | 115 | 52.3 | 1 | 25.45
DSH060*D | 5 | 1870 | 85 | 71 | 115 | 55 | 0.8 | 22.7
DSH060*D | 5 | 2250 | 70 | 59 | 65 | 60.6 | 0.71 | 17.47
DSH060*D | 5 | 2250 | 70 | 63 | 65 | 61.4 | 0.63 | 15.62
DSH060*D | 5 | 2250 | 70 | 67 | 65 | 63.2 | 0.48 | 12.15
DSH060*D | 5 | 2250 | 70 | 59 | 75 | 60.1 | 0.72 | 17.42
DSH060*D | 5 | 2250 | 70 | 63 | 75 | 60.9 | 0.63 | 15.57
DSH060*D | 5 | 2250 | 70 | 67 | 75 | 62.6 | 0.48 | 12.1
DSH060*D | 5 | 2250 | 70 | 59 | 85 | 58.5 | 0.75 | 17.68
DSH060*D | 5 | 2250 | 70 | 63 | 85 | 59.4 | 0.66 | 15.83
DSH060*D | 5 | 2250 | 70 | 67 | 85 | 61.1 | 0.5 | 12.36
DSH060*D | 5 | 2250 | 70 | 59 | 95 | 55.9 | 0.77 | 17.4
DSH060*D | 5 | 2250 | 70 | 63 | 95 | 56.7 | 0.68 | 15.55
DSH060*D | 5 | 2250 | 70 | 67 | 95 | 58.5 | 0.51 | 12.08
DSH060*D | 5 | 2250 | 70 | 59 | 105 | 52.7 | 0.81 | 17.15
DSH060*D | 5 | 2250 | 70 | 63 | 105 | 53.5 | 0.71 | 15.3
DSH060*D | 5 | 2250 | 70 | 67 | 105 | 55.3 | 0.53 | 11.83
DSH060*D | 5 | 2250 | 70 | 59 | 115 | 49.8 | 0.91 | 18.32
DSH060*D | 5 | 2250 | 70 | 63 | 115 | 50.6 | 0.81 | 16.46
DSH060*D | 5 | 2250 | 70 | 67 | 115 | 52.3 | 0.61 | 12.99
DSH060*D | 5 | 2250 | 75 | 59 | 65 | 60.9 | 0.88 | 21.55
DSH060*D | 5 | 2250 | 75 | 63 | 65 | 61.7 | 0.79 | 19.7
DSH060*D | 5 | 2250 | 75 | 67 | 65 | 63.5 | 0.63 | 16.23
DSH060*D | 5 | 2250 | 75 | 71 | 65 | 66.1 | 0.5 | 12.6
DSH060*D | 5 | 2250 | 75 | 59 | 75 | 60.4 | 0.88 | 21.5
DSH060*D | 5 | 2250 | 75 | 63 | 75 | 61.2 | 0.79 | 19.65
DSH060*D | 5 | 2250 | 75 | 67 | 75 | 62.9 | 0.64 | 16.18
DSH060*D | 5 | 2250 | 75 | 71 | 75 | 65.6 | 0.5 | 12.6
DSH060*D | 5 | 2250 | 75 | 59 | 85 | 58.8 | 0.92 | 21.76
DSH060*D | 5 | 2250 | 75 | 63 | 85 | 59.7 | 0.83 | 19.91
DSH060*D | 5 | 2250 | 75 | 67 | 85 | 61.4 | 0.66 | 16.44
DSH060*D | 5 | 2250 | 75 | 71 | 85 | 64.1 | 0.5 | 12.9
DSH060*D | 5 | 2250 | 75 | 59 | 95 | 56.2 | 0.95 | 21.48
DSH060*D | 5 | 2250 | 75 | 63 | 95 | 57 | 0.85 | 19.63
DSH060*D | 5 | 2250 | 75 | 67 | 95 | 58.8 | 0.68 | 16.16
DSH060*D | 5 | 2250 | 75 | 71 | 95 | 61.5 | 0.5 | 12.6
DSH060*D | 5 | 2250 | 75 | 59 | 105 | 53 | 0.99 | 21.24
DSH060*D | 5 | 2250 | 75 | 63 | 105 | 53.8 | 0.89 | 19.38
DSH060*D | 5 | 2250 | 75 | 67 | 105 | 55.6 | 0.71 | 15.91
DSH060*D | 5 | 2250 | 75 | 71 | 105 | 58.2 | 0.5 | 12.3
DSH060*D | 5 | 2250 | 75 | 59 | 115 | 50.1 | 1 | 20.23
DSH060*D | 5 | 2250 | 75 | 63 | 115 | 50.9 | 1 | 20.54
DSH060*D | 5 | 2250 | 75 | 67 | 115 | 52.6 | 0.8 | 17.08
DSH060*D | 5 | 2250 | 75 | 71 | 115 | 55.3 | 0.6 | 13.5
DSH060*D | 5 | 2250 | 80 | 59 | 65 | 61.2 | 1 | 24.73
DSH060*D | 5 | 2250 | 80 | 63 | 65 | 62 | 0.95 | 23.81
DSH060*D | 5 | 2250 | 80 | 67 | 65 | 63.8 | 0.79 | 20.34
DSH060*D | 5 | 2250 | 80 | 71 | 65 | 66.4 | 0.6 | 16.7
DSH060*D | 5 | 2250 | 80 | 59 | 75 | 60.7 | 1 | 24.52
DSH060*D | 5 | 2250 | 80 | 63 | 75 | 61.5 | 0.96 | 23.75
DSH060*D | 5 | 2250 | 80 | 67 | 75 | 63.2 | 0.79 | 20.29
DSH060*D | 5 | 2250 | 80 | 71 | 75 | 65.9 | 0.6 | 16.7
DSH060*D | 5 | 2250 | 80 | 59 | 85 | 59.1 | 1 | 23.9
DSH060*D | 5 | 2250 | 80 | 63 | 85 | 60 | 0.99 | 24.02
DSH060*D | 5 | 2250 | 80 | 67 | 85 | 61.7 | 0.82 | 20.55
DSH060*D | 5 | 2250 | 80 | 71 | 85 | 64.4 | 0.7 | 17
DSH060*D | 5 | 2250 | 80 | 59 | 95 | 56.5 | 1 | 22.84
DSH060*D | 5 | 2250 | 80 | 63 | 95 | 57.3 | 1 | 23.17
DSH060*D | 5 | 2250 | 80 | 67 | 95 | 59.1 | 0.85 | 20.27
DSH060*D | 5 | 2250 | 80 | 71 | 95 | 61.8 | 0.7 | 16.7
DSH060*D | 5 | 2250 | 80 | 59 | 105 | 53.3 | 1 | 21.54
DSH060*D | 5 | 2250 | 80 | 63 | 105 | 54.1 | 1 | 21.87
DSH060*D | 5 | 2250 | 80 | 67 | 105 | 55.9 | 0.89 | 20.02
DSH060*D | 5 | 2250 | 80 | 71 | 105 | 58.6 | 0.7 | 16.4
DSH060*D | 5 | 2250 | 80 | 59 | 115 | 50.4 | 1 | 20.35
DSH060*D | 5 | 2250 | 80 | 63 | 115 | 51.2 | 1 | 20.69
DSH060*D | 5 | 2250 | 80 | 67 | 115 | 52.9 | 0.99 | 21.18
DSH060*D | 5 | 2250 | 80 | 71 | 115 | 55.6 | 0.8 | 17.6
DSH060*D | 5 | 2250 | 85 | 59 | 65 | 62.2 | 1 | 25.12
DSH060*D | 5 | 2250 | 85 | 63 | 65 | 63 | 1 | 25.46
DSH060*D | 5 | 2250 | 85 | 67 | 65 | 64.8 | 0.92 | 23.98
DSH060*D | 5 | 2250 | 85 | 71 | 65 | 67.4 | 0.7 | 20.4
DSH060*D | 5 | 2250 | 85 | 59 | 75 | 61.7 | 1 | 24.91
DSH060*D | 5 | 2250 | 85 | 63 | 75 | 62.5 | 1 | 25.25
DSH060*D | 5 | 2250 | 85 | 67 | 75 | 64.2 | 0.92 | 23.93
DSH060*D | 5 | 2250 | 85 | 71 | 75 | 66.9 | 0.8 | 20.3
DSH060*D | 5 | 2250 | 85 | 59 | 85 | 60.1 | 1 | 24.3
DSH060*D | 5 | 2250 | 85 | 63 | 85 | 61 | 1 | 24.63
DSH060*D | 5 | 2250 | 85 | 67 | 85 | 62.7 | 0.95 | 24.19
DSH060*D | 5 | 2250 | 85 | 71 | 85 | 65.4 | 0.8 | 20.6
DSH060*D | 5 | 2250 | 85 | 59 | 95 | 57.5 | 1 | 23.23
DSH060*D | 5 | 2250 | 85 | 63 | 95 | 58.3 | 1 | 23.57
DSH060*D | 5 | 2250 | 85 | 67 | 95 | 60.1 | 0.99 | 23.91
DSH060*D | 5 | 2250 | 85 | 71 | 95 | 62.7 | 0.8 | 20.3
DSH060*D | 5 | 2250 | 85 | 59 | 105 | 54.3 | 1 | 21.94
DSH060*D | 5 | 2250 | 85 | 63 | 105 | 55.1 | 1 | 22.27
DSH060*D | 5 | 2250 | 85 | 67 | 105 | 56.9 | 1 | 22.98
DSH060*D | 5 | 2250 | 85 | 71 | 105 | 59.5 | 0.8 | 20.1
DSH060*D | 5 | 2250 | 85 | 59 | 115 | 51.4 | 1 | 20.75
DSH060*D | 5 | 2250 | 85 | 63 | 115 | 52.2 | 1 | 21.09
DSH060*D | 5 | 2250 | 85 | 67 | 115 | 53.9 | 1 | 21.79
DSH060*D | 5 | 2250 | 85 | 71 | 115 | 56.6 | 0.9 | 21.2
DSH072*D | 6 | 1800 | 70 | 59 | 65 | 68.1 | 0.59 | 20.27
DSH072*D | 6 | 1800 | 70 | 63 | 65 | 69.1 | 0.53 | 18.51
DSH072*D | 6 | 1800 | 70 | 67 | 65 | 71.2 | 0.42 | 15.23
DSH072*D | 6 | 1800 | 70 | 59 | 75 | 67.5 | 0.59 | 20.22
DSH072*D | 6 | 1800 | 70 | 63 | 75 | 68.5 | 0.53 | 18.46
DSH072*D | 6 | 1800 | 70 | 67 | 75 | 70.6 | 0.43 | 15.18
DSH072*D | 6 | 1800 | 70 | 59 | 85 | 65.7 | 0.62 | 20.46
DSH072*D | 6 | 1800 | 70 | 63 | 85 | 66.7 | 0.56 | 18.71
DSH072*D | 6 | 1800 | 70 | 67 | 85 | 68.7 | 0.44 | 15.43
DSH072*D | 6 | 1800 | 70 | 59 | 95 | 62.6 | 0.64 | 20.2
DSH072*D | 6 | 1800 | 70 | 63 | 95 | 63.6 | 0.57 | 18.44
DSH072*D | 6 | 1800 | 70 | 67 | 95 | 65.6 | 0.46 | 15.16
DSH072*D | 6 | 1800 | 70 | 59 | 105 | 58.8 | 0.67 | 19.96
DSH072*D | 6 | 1800 | 70 | 63 | 105 | 59.8 | 0.6 | 18.21
DSH072*D | 6 | 1800 | 70 | 67 | 105 | 61.8 | 0.48 | 14.93
DSH072*D | 6 | 1800 | 70 | 59 | 115 | 55.3 | 0.75 | 21.06
DSH072*D | 6 | 1800 | 70 | 63 | 115 | 56.3 | 0.68 | 19.31
DSH072*D | 6 | 1800 | 70 | 67 | 115 | 58.4 | 0.54 | 16.03
DSH072*D | 6 | 1800 | 75 | 59 | 65 | 68.5 | 0.7 | 24.13
DSH072*D | 6 | 1800 | 75 | 63 | 65 | 69.5 | 0.64 | 22.37
DSH072*D | 6 | 1800 | 75 | 67 | 65 | 71.5 | 0.53 | 19.09
DSH072*D | 6 | 1800 | 75 | 71 | 65 | 74.7 | 0.4 | 15.7
DSH072*D | 6 | 1800 | 75 | 59 | 75 | 67.9 | 0.7 | 24.08
DSH072*D | 6 | 1800 | 75 | 63 | 75 | 68.8 | 0.64 | 22.32
DSH072*D | 6 | 1800 | 75 | 67 | 75 | 70.9 | 0.53 | 19.04
DSH072*D | 6 | 1800 | 75 | 71 | 75 | 74.1 | 0.4 | 15.6
DSH072*D | 6 | 1800 | 75 | 59 | 85 | 66.1 | 0.73 | 24.33
DSH072*D | 6 | 1800 | 75 | 63 | 85 | 67 | 0.67 | 22.57
DSH072*D | 6 | 1800 | 75 | 67 | 85 | 69.1 | 0.55 | 19.29
DSH072*D | 6 | 1800 | 75 | 71 | 85 | 72.3 | 0.4 | 15.9
DSH072*D | 6 | 1800 | 75 | 59 | 95 | 63 | 0.76 | 24.06
DSH072*D | 6 | 1800 | 75 | 63 | 95 | 63.9 | 0.69 | 22.31
DSH072*D | 6 | 1800 | 75 | 67 | 95 | 66 | 0.57 | 19.02
DSH072*D | 6 | 1800 | 75 | 71 | 95 | 69.2 | 0.4 | 15.6
DSH072*D | 6 | 1800 | 75 | 59 | 105 | 59.2 | 0.8 | 23.83
DSH072*D | 6 | 1800 | 75 | 63 | 105 | 60.1 | 0.73 | 22.07
DSH072*D | 6 | 1800 | 75 | 67 | 105 | 62.2 | 0.6 | 18.79
DSH072*D | 6 | 1800 | 75 | 71 | 105 | 65.4 | 0.5 | 15.4
DSH072*D | 6 | 1800 | 75 | 59 | 115 | 55.7 | 0.89 | 24.93
DSH072*D | 6 | 1800 | 75 | 63 | 115 | 56.7 | 0.81 | 23.17
DSH072*D | 6 | 1800 | 75 | 67 | 115 | 58.7 | 0.67 | 19.89
DSH072*D | 6 | 1800 | 75 | 71 | 115 | 61.9 | 0.5 | 16.5
DSH072*D | 6 | 1800 | 80 | 59 | 65 | 68.8 | 0.81 | 28.02
DSH072*D | 6 | 1800 | 80 | 63 | 65 | 69.8 | 0.74 | 26.26
DSH072*D | 6 | 1800 | 80 | 67 | 65 | 71.9 | 0.63 | 22.98
DSH072*D | 6 | 1800 | 80 | 71 | 65 | 75 | 0.5 | 19.6
DSH072*D | 6 | 1800 | 80 | 59 | 75 | 68.2 | 0.81 | 27.97
DSH072*D | 6 | 1800 | 80 | 63 | 75 | 69.2 | 0.75 | 26.21
DSH072*D | 6 | 1800 | 80 | 67 | 75 | 71.3 | 0.64 | 22.93
DSH072*D | 6 | 1800 | 80 | 71 | 75 | 74.4 | 0.5 | 19.5
DSH072*D | 6 | 1800 | 80 | 59 | 85 | 66.4 | 0.84 | 28.22
DSH072*D | 6 | 1800 | 80 | 63 | 85 | 67.4 | 0.78 | 26.46
DSH072*D | 6 | 1800 | 80 | 67 | 85 | 69.5 | 0.66 | 23.18
DSH072*D | 6 | 1800 | 80 | 71 | 85 | 72.6 | 0.5 | 19.8
DSH072*D | 6 | 1800 | 80 | 59 | 95 | 63.3 | 0.87 | 27.95
DSH072*D | 6 | 1800 | 80 | 63 | 95 | 64.3 | 0.81 | 26.2
DSH072*D | 6 | 1800 | 80 | 67 | 95 | 66.4 | 0.68 | 22.91
DSH072*D | 6 | 1800 | 80 | 71 | 95 | 69.5 | 0.6 | 19.5
DSH072*D | 6 | 1800 | 80 | 59 | 105 | 59.5 | 0.92 | 27.72
DSH072*D | 6 | 1800 | 80 | 63 | 105 | 60.5 | 0.85 | 25.96
DSH072*D | 6 | 1800 | 80 | 67 | 105 | 62.6 | 0.72 | 22.68
DSH072*D | 6 | 1800 | 80 | 71 | 105 | 65.7 | 0.6 | 19.3
DSH072*D | 6 | 1800 | 80 | 59 | 115 | 56 | 1 | 28.31
DSH072*D | 6 | 1800 | 80 | 63 | 115 | 57 | 0.94 | 27.06
DSH072*D | 6 | 1800 | 80 | 67 | 115 | 59.1 | 0.8 | 23.78
DSH072*D | 6 | 1800 | 80 | 71 | 115 | 62.2 | 0.6 | 20.4
DSH072*D | 6 | 1800 | 85 | 59 | 65 | 70 | 0.89 | 31.47
DSH072*D | 6 | 1800 | 85 | 63 | 65 | 71 | 0.83 | 29.71
DSH072*D | 6 | 1800 | 85 | 67 | 65 | 73.1 | 0.72 | 26.43
DSH072*D | 6 | 1800 | 85 | 71 | 65 | 76.2 | 0.6 | 23
DSH072*D | 6 | 1800 | 85 | 59 | 75 | 69.4 | 0.9 | 31.42
DSH072*D | 6 | 1800 | 85 | 63 | 75 | 70.4 | 0.83 | 29.66
DSH072*D | 6 | 1800 | 85 | 67 | 75 | 72.4 | 0.72 | 26.38
DSH072*D | 6 | 1800 | 85 | 71 | 75 | 75.6 | 0.6 | 23
DSH072*D | 6 | 1800 | 85 | 59 | 85 | 67.6 | 0.93 | 31.67
DSH072*D | 6 | 1800 | 85 | 63 | 85 | 68.6 | 0.86 | 29.91
DSH072*D | 6 | 1800 | 85 | 67 | 85 | 70.6 | 0.75 | 26.63
DSH072*D | 6 | 1800 | 85 | 71 | 85 | 73.8 | 0.6 | 23.2
DSH072*D | 6 | 1800 | 85 | 59 | 95 | 64.5 | 0.96 | 31.4
DSH072*D | 6 | 1800 | 85 | 63 | 95 | 65.5 | 0.9 | 29.65
DSH072*D | 6 | 1800 | 85 | 67 | 95 | 67.5 | 0.77 | 26.37
DSH072*D | 6 | 1800 | 85 | 71 | 95 | 70.7 | 0.6 | 23
DSH072*D | 6 | 1800 | 85 | 59 | 105 | 60.7 | 1 | 30.65
DSH072*D | 6 | 1800 | 85 | 63 | 105 | 61.7 | 0.94 | 29.41
DSH072*D | 6 | 1800 | 85 | 67 | 105 | 63.7 | 0.81 | 26.13
DSH072*D | 6 | 1800 | 85 | 71 | 105 | 66.9 | 0.7 | 22.7
DSH072*D | 6 | 1800 | 85 | 59 | 115 | 57.2 | 1 | 28.9
DSH072*D | 6 | 1800 | 85 | 63 | 115 | 58.2 | 1 | 29.39
DSH072*D | 6 | 1800 | 85 | 67 | 115 | 60.3 | 0.89 | 27.23
DSH072*D | 6 | 1800 | 85 | 71 | 115 | 63.4 | 0.7 | 23.8
DSH072*D | 6 | 2380 | 70 | 59 | 65 | 69.8 | 0.67 | 17.94
DSH072*D | 6 | 2380 | 70 | 63 | 65 | 70.8 | 0.6 | 16.18
DSH072*D | 6 | 2380 | 70 | 67 | 65 | 72.8 | 0.46 | 12.9
DSH072*D | 6 | 2380 | 70 | 59 | 75 | 69.2 | 0.68 | 17.89
DSH072*D | 6 | 2380 | 70 | 63 | 75 | 70.1 | 0.6 | 16.14
DSH072*D | 6 | 2380 | 70 | 67 | 75 | 72.2 | 0.47 | 12.86
DSH072*D | 6 | 2380 | 70 | 59 | 85 | 67.3 | 0.71 | 18.14
DSH072*D | 6 | 2380 | 70 | 63 | 85 | 68.3 | 0.63 | 16.38
DSH072*D | 6 | 2380 | 70 | 67 | 85 | 70.4 | 0.49 | 13.1
DSH072*D | 6 | 2380 | 70 | 59 | 95 | 64.2 | 0.73 | 17.88
DSH072*D | 6 | 2380 | 70 | 63 | 95 | 65.2 | 0.65 | 16.12
DSH072*D | 6 | 2380 | 70 | 67 | 95 | 67.3 | 0.5 | 12.84
DSH072*D | 6 | 2380 | 70 | 59 | 105 | 60.4 | 0.76 | 17.64
DSH072*D | 6 | 2380 | 70 | 63 | 105 | 61.4 | 0.68 | 15.88
DSH072*D | 6 | 2380 | 70 | 67 | 105 | 63.5 | 0.52 | 12.6
DSH072*D | 6 | 2380 | 70 | 59 | 115 | 57 | 0.86 | 18.74
DSH072*D | 6 | 2380 | 70 | 63 | 115 | 57.9 | 0.77 | 16.98
DSH072*D | 6 | 2380 | 70 | 67 | 115 | 60 | 0.6 | 13.7
DSH072*D | 6 | 2380 | 75 | 59 | 65 | 70.1 | 0.81 | 21.81
DSH072*D | 6 | 2380 | 75 | 63 | 65 | 71.1 | 0.74 | 20.05
DSH072*D | 6 | 2380 | 75 | 67 | 65 | 73.2 | 0.6 | 16.77
DSH072*D | 6 | 2380 | 75 | 71 | 65 | 76.3 | 0.5 | 13.4
DSH072*D | 6 | 2380 | 75 | 59 | 75 | 69.5 | 0.82 | 21.76
DSH072*D | 6 | 2380 | 75 | 63 | 75 | 70.5 | 0.74 | 20
DSH072*D | 6 | 2380 | 75 | 67 | 75 | 72.6 | 0.6 | 16.72
DSH072*D | 6 | 2380 | 75 | 71 | 75 | 75.7 | 0.5 | 13.3
DSH072*D | 6 | 2380 | 75 | 59 | 85 | 67.7 | 0.85 | 22.01
DSH072*D | 6 | 2380 | 75 | 63 | 85 | 68.7 | 0.77 | 20.25
DSH072*D | 6 | 2380 | 75 | 67 | 85 | 70.7 | 0.63 | 16.97
DSH072*D | 6 | 2380 | 75 | 71 | 85 | 73.9 | 0.5 | 13.6
DSH072*D | 6 | 2380 | 75 | 59 | 95 | 64.6 | 0.88 | 21.74
DSH072*D | 6 | 2380 | 75 | 63 | 95 | 65.6 | 0.8 | 19.98
DSH072*D | 6 | 2380 | 75 | 67 | 95 | 67.6 | 0.65 | 16.7
DSH072*D | 6 | 2380 | 75 | 71 | 95 | 70.8 | 0.5 | 13.3
DSH072*D | 6 | 2380 | 75 | 59 | 105 | 60.8 | 0.93 | 21.51
DSH072*D | 6 | 2380 | 75 | 63 | 105 | 61.8 | 0.84 | 19.75
DSH072*D | 6 | 2380 | 75 | 67 | 105 | 63.8 | 0.68 | 16.47
DSH072*D | 6 | 2380 | 75 | 71 | 105 | 67 | 0.5 | 13.1
DSH072*D | 6 | 2380 | 75 | 59 | 115 | 57.3 | 1 | 21.9
DSH072*D | 6 | 2380 | 75 | 63 | 115 | 58.3 | 0.94 | 20.85
DSH072*D | 6 | 2380 | 75 | 67 | 115 | 60.4 | 0.76 | 17.57
DSH072*D | 6 | 2380 | 75 | 71 | 115 | 63.5 | 0.6 | 14.2
DSH072*D | 6 | 2380 | 80 | 59 | 65 | 70.5 | 0.95 | 25.7
DSH072*D | 6 | 2380 | 80 | 63 | 65 | 71.5 | 0.88 | 23.94
DSH072*D | 6 | 2380 | 80 | 67 | 65 | 73.5 | 0.74 | 20.66
DSH072*D | 6 | 2380 | 80 | 71 | 65 | 76.7 | 0.6 | 17.3
DSH072*D | 6 | 2380 | 80 | 59 | 75 | 69.9 | 0.96 | 25.65
DSH072*D | 6 | 2380 | 80 | 63 | 75 | 70.8 | 0.88 | 23.89
DSH072*D | 6 | 2380 | 80 | 67 | 75 | 72.9 | 0.74 | 20.61
DSH072*D | 6 | 2380 | 80 | 71 | 75 | 76.1 | 0.6 | 17.2
DSH072*D | 6 | 2380 | 80 | 59 | 85 | 68.1 | 1 | 25.9
DSH072*D | 6 | 2380 | 80 | 63 | 85 | 69 | 0.92 | 24.14
DSH072*D | 6 | 2380 | 80 | 67 | 85 | 71.1 | 0.77 | 20.86
DSH072*D | 6 | 2380 | 80 | 71 | 85 | 74.3 | 0.6 | 17.5
DSH072*D | 6 | 2380 | 80 | 59 | 95 | 65 | 1 | 24.81
DSH072*D | 6 | 2380 | 80 | 63 | 95 | 65.9 | 0.95 | 23.87
DSH072*D | 6 | 2380 | 80 | 67 | 95 | 68 | 0.79 | 20.59
DSH072*D | 6 | 2380 | 80 | 71 | 95 | 71.2 | 0.6 | 17.2
DSH072*D | 6 | 2380 | 80 | 59 | 105 | 61.2 | 1 | 23.36
DSH072*D | 6 | 2380 | 80 | 63 | 105 | 62.1 | 1 | 23.64
DSH072*D | 6 | 2380 | 80 | 67 | 105 | 64.2 | 0.83 | 20.36
DSH072*D | 6 | 2380 | 80 | 71 | 105 | 67.4 | 0.7 | 17
DSH072*D | 6 | 2380 | 80 | 59 | 115 | 57.7 | 1 | 22.04
DSH072*D | 6 | 2380 | 80 | 63 | 115 | 58.7 | 1 | 22.41
DSH072*D | 6 | 2380 | 80 | 67 | 115 | 60.7 | 0.92 | 21.46
DSH072*D | 6 | 2380 | 80 | 71 | 115 | 63.9 | 0.7 | 18.1
DSH072*D | 6 | 2380 | 85 | 59 | 65 | 71.7 | 1 | 27.37
DSH072*D | 6 | 2380 | 85 | 63 | 65 | 72.6 | 0.99 | 27.39
DSH072*D | 6 | 2380 | 85 | 67 | 65 | 74.7 | 0.84 | 24.11
DSH072*D | 6 | 2380 | 85 | 71 | 65 | 77.9 | 0.7 | 20.7
DSH072*D | 6 | 2380 | 85 | 59 | 75 | 71 | 1 | 27.13
DSH072*D | 6 | 2380 | 85 | 63 | 75 | 72 | 0.99 | 27.34
DSH072*D | 6 | 2380 | 85 | 67 | 75 | 74.1 | 0.85 | 24.06
DSH072*D | 6 | 2380 | 85 | 71 | 75 | 77.2 | 0.7 | 20.7
DSH072*D | 6 | 2380 | 85 | 59 | 85 | 69.2 | 1 | 26.44
DSH072*D | 6 | 2380 | 85 | 63 | 85 | 70.2 | 1 | 26.82
DSH072*D | 6 | 2380 | 85 | 67 | 85 | 72.3 | 0.88 | 24.31
DSH072*D | 6 | 2380 | 85 | 71 | 85 | 75.4 | 0.7 | 20.9
DSH072*D | 6 | 2380 | 85 | 59 | 95 | 66.1 | 1 | 25.26
DSH072*D | 6 | 2380 | 85 | 63 | 95 | 67.1 | 1 | 25.63
DSH072*D | 6 | 2380 | 85 | 67 | 95 | 69.2 | 0.91 | 24.04
DSH072*D | 6 | 2380 | 85 | 71 | 95 | 72.3 | 0.7 | 20.6
DSH072*D | 6 | 2380 | 85 | 59 | 105 | 62.3 | 1 | 23.81
DSH072*D | 6 | 2380 | 85 | 63 | 105 | 63.3 | 1 | 24.18
DSH072*D | 6 | 2380 | 85 | 67 | 105 | 65.4 | 0.95 | 23.81
DSH072*D | 6 | 2380 | 85 | 71 | 105 | 68.5 | 0.8 | 20.4
DSH072*D | 6 | 2380 | 85 | 59 | 115 | 58.9 | 1 | 22.48
DSH072*D | 6 | 2380 | 85 | 63 | 115 | 59.8 | 1 | 22.85
DSH072*D | 6 | 2380 | 85 | 67 | 115 | 61.9 | 1 | 23.64
DSH072*D | 6 | 2380 | 85 | 71 | 115 | 65.1 | 0.9 | 21.5
DSH072*D | 6 | 2700 | 70 | 59 | 65 | 71 | 0.71 | 16.99
DSH072*D | 6 | 2700 | 70 | 63 | 65 | 71.9 | 0.63 | 15.23
DSH072*D | 6 | 2700 | 70 | 67 | 65 | 74 | 0.48 | 11.95
DSH072*D | 6 | 2700 | 70 | 59 | 75 | 70.3 | 0.72 | 16.94
DSH072*D | 6 | 2700 | 70 | 63 | 75 | 71.3 | 0.63 | 15.18
DSH072*D | 6 | 2700 | 70 | 67 | 75 | 73.4 | 0.48 | 11.9
DSH072*D | 6 | 2700 | 70 | 59 | 85 | 68.5 | 0.74 | 17.18
DSH072*D | 6 | 2700 | 70 | 63 | 85 | 69.5 | 0.66 | 15.43
DSH072*D | 6 | 2700 | 70 | 67 | 85 | 71.6 | 0.5 | 12.15
DSH072*D | 6 | 2700 | 70 | 59 | 95 | 65.4 | 0.77 | 16.92
DSH072*D | 6 | 2700 | 70 | 63 | 95 | 66.4 | 0.68 | 15.16
DSH072*D | 6 | 2700 | 70 | 67 | 95 | 68.5 | 0.52 | 11.88
DSH072*D | 6 | 2700 | 70 | 59 | 105 | 61.6 | 0.8 | 16.68
DSH072*D | 6 | 2700 | 70 | 63 | 105 | 62.6 | 0.71 | 14.93
DSH072*D | 6 | 2700 | 70 | 67 | 105 | 64.7 | 0.53 | 11.65
DSH072*D | 6 | 2700 | 70 | 59 | 115 | 58.2 | 0.91 | 17.79
DSH072*D | 6 | 2700 | 70 | 63 | 115 | 59.1 | 0.81 | 16.03
DSH072*D | 6 | 2700 | 70 | 67 | 115 | 61.2 | 0.62 | 12.75
DSH072*D | 6 | 2700 | 75 | 59 | 65 | 71.3 | 0.87 | 20.85
DSH072*D | 6 | 2700 | 75 | 63 | 65 | 72.3 | 0.78 | 19.09
DSH072*D | 6 | 2700 | 75 | 67 | 65 | 74.4 | 0.63 | 15.81
DSH072*D | 6 | 2700 | 75 | 71 | 65 | 77.5 | 0.5 | 12.4
DSH072*D | 6 | 2700 | 75 | 59 | 75 | 70.7 | 0.87 | 20.8
DSH072*D | 6 | 2700 | 75 | 63 | 75 | 71.7 | 0.79 | 19.04
DSH072*D | 6 | 2700 | 75 | 67 | 75 | 73.7 | 0.63 | 15.76
DSH072*D | 6 | 2700 | 75 | 71 | 75 | 76.9 | 0.5 | 12.4
DSH072*D | 6 | 2700 | 75 | 59 | 85 | 68.9 | 0.91 | 21.05
DSH072*D | 6 | 2700 | 75 | 63 | 85 | 69.9 | 0.82 | 19.29
DSH072*D | 6 | 2700 | 75 | 67 | 85 | 71.9 | 0.66 | 16.01
DSH072*D | 6 | 2700 | 75 | 71 | 85 | 75.1 | 0.5 | 12.6
DSH072*D | 6 | 2700 | 75 | 59 | 95 | 65.8 | 0.94 | 20.78
DSH072*D | 6 | 2700 | 75 | 63 | 95 | 66.8 | 0.85 | 19.03
DSH072*D | 6 | 2700 | 75 | 67 | 95 | 68.8 | 0.68 | 15.74
DSH072*D | 6 | 2700 | 75 | 71 | 95 | 72 | 0.5 | 12.3
DSH072*D | 6 | 2700 | 75 | 59 | 105 | 62 | 0.98 | 20.55
DSH072*D | 6 | 2700 | 75 | 63 | 105 | 63 | 0.89 | 18.79
DSH072*D | 6 | 2700 | 75 | 67 | 105 | 65 | 0.71 | 15.51
DSH072*D | 6 | 2700 | 75 | 71 | 105 | 68.2 | 0.5 | 12.1
DSH072*D | 6 | 2700 | 75 | 59 | 115 | 58.5 | 1 | 19.7
DSH072*D | 6 | 2700 | 75 | 63 | 115 | 59.5 | 0.99 | 19.89
DSH072*D | 6 | 2700 | 75 | 67 | 115 | 61.6 | 0.8 | 16.61
DSH072*D | 6 | 2700 | 75 | 71 | 115 | 64.7 | 0.6 | 13.2
DSH072*D | 6 | 2700 | 80 | 59 | 65 | 71.7 | 1 | 24.13
DSH072*D | 6 | 2700 | 80 | 63 | 65 | 72.6 | 0.94 | 22.98
DSH072*D | 6 | 2700 | 80 | 67 | 65 | 74.7 | 0.78 | 19.7
DSH072*D | 6 | 2700 | 80 | 71 | 65 | 77.9 | 0.6 | 16.3
DSH072*D | 6 | 2700 | 80 | 59 | 75 | 71.1 | 1 | 23.92
DSH072*D | 6 | 2700 | 80 | 63 | 75 | 72 | 0.95 | 22.93
DSH072*D | 6 | 2700 | 80 | 67 | 75 | 74.1 | 0.79 | 19.65
DSH072*D | 6 | 2700 | 80 | 71 | 75 | 77.3 | 0.6 | 16.3
DSH072*D | 6 | 2700 | 80 | 59 | 85 | 69.2 | 1 | 23.32
DSH072*D | 6 | 2700 | 80 | 63 | 85 | 70.2 | 0.98 | 23.18
DSH072*D | 6 | 2700 | 80 | 67 | 85 | 72.3 | 0.82 | 19.9
DSH072*D | 6 | 2700 | 80 | 71 | 85 | 75.4 | 0.6 | 16.5
DSH072*D | 6 | 2700 | 80 | 59 | 95 | 66.1 | 1 | 22.27
DSH072*D | 6 | 2700 | 80 | 63 | 95 | 67.1 | 1 | 22.6
DSH072*D | 6 | 2700 | 80 | 67 | 95 | 69.2 | 0.84 | 19.64
DSH072*D | 6 | 2700 | 80 | 71 | 95 | 72.3 | 0.7 | 16.2
DSH072*D | 6 | 2700 | 80 | 59 | 105 | 62.3 | 1 | 20.99
DSH072*D | 6 | 2700 | 80 | 63 | 105 | 63.3 | 1 | 21.32
DSH072*D | 6 | 2700 | 80 | 67 | 105 | 65.4 | 0.88 | 19.4
DSH072*D | 6 | 2700 | 80 | 71 | 105 | 68.5 | 0.7 | 16
DSH072*D | 6 | 2700 | 80 | 59 | 115 | 58.9 | 1 | 19.82
DSH072*D | 6 | 2700 | 80 | 63 | 115 | 59.8 | 1 | 20.15
DSH072*D | 6 | 2700 | 80 | 67 | 115 | 61.9 | 0.98 | 20.5
DSH072*D | 6 | 2700 | 80 | 71 | 115 | 65.1 | 0.8 | 17.1
DSH072*D | 6 | 2700 | 85 | 59 | 65 | 72.8 | 1 | 24.52
DSH072*D | 6 | 2700 | 85 | 63 | 65 | 73.8 | 1 | 24.85
DSH072*D | 6 | 2700 | 85 | 67 | 65 | 75.9 | 0.91 | 23.15
DSH072*D | 6 | 2700 | 85 | 71 | 65 | 79 | 0.7 | 19.8
DSH072*D | 6 | 2700 | 85 | 59 | 75 | 72.2 | 1 | 24.32
DSH072*D | 6 | 2700 | 85 | 63 | 75 | 73.2 | 1 | 24.65
DSH072*D | 6 | 2700 | 85 | 67 | 75 | 75.3 | 0.91 | 23.1
DSH072*D | 6 | 2700 | 85 | 71 | 75 | 78.4 | 0.7 | 19.7
DSH072*D | 6 | 2700 | 85 | 59 | 85 | 70.4 | 1 | 23.71
DSH072*D | 6 | 2700 | 85 | 63 | 85 | 71.4 | 1 | 24.04
DSH072*D | 6 | 2700 | 85 | 67 | 85 | 73.5 | 0.94 | 23.35
DSH072*D | 6 | 2700 | 85 | 71 | 85 | 76.6 | 0.8 | 20
DSH072*D | 6 | 2700 | 85 | 59 | 95 | 67.3 | 1 | 22.66
DSH072*D | 6 | 2700 | 85 | 63 | 95 | 68.3 | 1 | 22.99
DSH072*D | 6 | 2700 | 85 | 67 | 95 | 70.3 | 0.97 | 23.09
DSH072*D | 6 | 2700 | 85 | 71 | 95 | 73.5 | 0.8 | 19.7
DSH072*D | 6 | 2700 | 85 | 59 | 105 | 63.5 | 1 | 21.38
DSH072*D | 6 | 2700 | 85 | 63 | 105 | 64.5 | 1 | 21.71
DSH072*D | 6 | 2700 | 85 | 67 | 105 | 66.5 | 1 | 22.41
DSH072*D | 6 | 2700 | 85 | 71 | 105 | 69.7 | 0.8 | 19.5
DSH072*D | 6 | 2700 | 85 | 59 | 115 | 60 | 1 | 20.21
DSH072*D | 6 | 2700 | 85 | 63 | 115 | 61 | 1 | 20.54
DSH072*D | 6 | 2700 | 85 | 67 | 115 | 63.1 | 1 | 21.24
DSH072*D | 6 | 2700 | 85 | 71 | 115 | 66.2 | 0.9 | 20.6
DSH090* | 7.5 | 2625 | 70 | 59 | 65 | 87 | 0.62 | 18.82
DSH090* | 7.5 | 2625 | 70 | 63 | 65 | 88.3 | 0.56 | 17.08
DSH090* | 7.5 | 2625 | 70 | 67 | 65 | 90.9 | 0.44 | 13.83
DSH090* | 7.5 | 2625 | 70 | 59 | 75 | 86.3 | 0.63 | 18.77
DSH090* | 7.5 | 2625 | 70 | 63 | 75 | 87.5 | 0.56 | 17.03
DSH090* | 7.5 | 2625 | 70 | 67 | 75 | 90.1 | 0.44 | 13.78
DSH090* | 7.5 | 2625 | 70 | 59 | 85 | 84 | 0.65 | 19.02
DSH090* | 7.5 | 2625 | 70 | 63 | 85 | 85.2 | 0.59 | 17.28
DSH090* | 7.5 | 2625 | 70 | 67 | 85 | 87.8 | 0.46 | 14.03
DSH090* | 7.5 | 2625 | 70 | 59 | 95 | 80 | 0.68 | 18.75
DSH090* | 7.5 | 2625 | 70 | 63 | 95 | 81.3 | 0.6 | 17.01
DSH090* | 7.5 | 2625 | 70 | 67 | 95 | 83.9 | 0.47 | 13.76
DSH090* | 7.5 | 2625 | 70 | 59 | 105 | 75.2 | 0.71 | 18.52
DSH090* | 7.5 | 2625 | 70 | 63 | 105 | 76.5 | 0.63 | 16.78
DSH090* | 7.5 | 2625 | 70 | 67 | 105 | 79.1 | 0.49 | 13.53
DSH090* | 7.5 | 2625 | 70 | 59 | 115 | 70.9 | 0.8 | 19.61
DSH090* | 7.5 | 2625 | 70 | 63 | 115 | 72.1 | 0.72 | 17.87
DSH090* | 7.5 | 2625 | 70 | 67 | 115 | 74.7 | 0.57 | 14.62
DSH090* | 7.5 | 2625 | 75 | 59 | 65 | 87.5 | 0.75 | 22.65
DSH090* | 7.5 | 2625 | 75 | 63 | 65 | 88.8 | 0.68 | 20.9
DSH090* | 7.5 | 2625 | 75 | 67 | 65 | 91.4 | 0.56 | 17.66
DSH090* | 7.5 | 2625 | 75 | 71 | 65 | 95.4 | 0.4 | 14.3
DSH090* | 7.5 | 2625 | 75 | 59 | 75 | 86.8 | 0.75 | 22.6
DSH090* | 7.5 | 2625 | 75 | 63 | 75 | 88 | 0.68 | 20.86
DSH090* | 7.5 | 2625 | 75 | 67 | 75 | 90.6 | 0.56 | 17.61
DSH090* | 7.5 | 2625 | 75 | 71 | 75 | 94.6 | 0.4 | 14.2
DSH090* | 7.5 | 2625 | 75 | 59 | 85 | 84.5 | 0.78 | 22.84
DSH090* | 7.5 | 2625 | 75 | 63 | 85 | 85.7 | 0.71 | 21.1
DSH090* | 7.5 | 2625 | 75 | 67 | 85 | 88.3 | 0.58 | 17.85
DSH090* | 7.5 | 2625 | 75 | 71 | 85 | 92.3 | 0.5 | 14.5
DSH090* | 7.5 | 2625 | 75 | 59 | 95 | 80.5 | 0.81 | 22.58
DSH090* | 7.5 | 2625 | 75 | 63 | 95 | 81.8 | 0.74 | 20.84
DSH090* | 7.5 | 2625 | 75 | 67 | 95 | 84.4 | 0.6 | 17.59
DSH090* | 7.5 | 2625 | 75 | 71 | 95 | 88.4 | 0.5 | 14.2
DSH090* | 7.5 | 2625 | 75 | 59 | 105 | 75.7 | 0.85 | 22.35
DSH090* | 7.5 | 2625 | 75 | 63 | 105 | 77 | 0.77 | 20.61
DSH090* | 7.5 | 2625 | 75 | 67 | 105 | 79.6 | 0.63 | 17.36
DSH090* | 7.5 | 2625 | 75 | 71 | 105 | 83.6 | 0.5 | 14
DSH090* | 7.5 | 2625 | 75 | 59 | 115 | 71.4 | 0.95 | 23.44
DSH090* | 7.5 | 2625 | 75 | 63 | 115 | 72.6 | 0.86 | 21.7
DSH090* | 7.5 | 2625 | 75 | 67 | 115 | 75.2 | 0.71 | 18.45
DSH090* | 7.5 | 2625 | 75 | 71 | 115 | 79.2 | 0.5 | 15.1
DSH090* | 7.5 | 2625 | 80 | 59 | 65 | 88 | 0.87 | 26.5
DSH090* | 7.5 | 2625 | 80 | 63 | 65 | 89.2 | 0.8 | 24.76
DSH090* | 7.5 | 2625 | 80 | 67 | 65 | 91.8 | 0.68 | 21.51
DSH090* | 7.5 | 2625 | 80 | 71 | 65 | 95.8 | 0.5 | 18.1
DSH090* | 7.5 | 2625 | 80 | 59 | 75 | 87.2 | 0.88 | 26.45
DSH090* | 7.5 | 2625 | 80 | 63 | 75 | 88.5 | 0.81 | 24.71
DSH090* | 7.5 | 2625 | 80 | 67 | 75 | 91.1 | 0.68 | 21.46
DSH090* | 7.5 | 2625 | 80 | 71 | 75 | 95.1 | 0.5 | 18.1
DSH090* | 7.5 | 2625 | 80 | 59 | 85 | 84.9 | 0.91 | 26.7
DSH090* | 7.5 | 2625 | 80 | 63 | 85 | 86.2 | 0.84 | 24.95
DSH090* | 7.5 | 2625 | 80 | 67 | 85 | 88.8 | 0.71 | 21.71
DSH090* | 7.5 | 2625 | 80 | 71 | 85 | 92.8 | 0.6 | 18.3
DSH090* | 7.5 | 2625 | 80 | 59 | 95 | 81 | 0.94 | 26.43
DSH090* | 7.5 | 2625 | 80 | 63 | 95 | 82.2 | 0.87 | 24.69
DSH090* | 7.5 | 2625 | 80 | 67 | 95 | 84.9 | 0.73 | 21.44
DSH090* | 7.5 | 2625 | 80 | 71 | 95 | 88.8 | 0.6 | 18.1
DSH090* | 7.5 | 2625 | 80 | 59 | 105 | 76.2 | 0.99 | 26.2
DSH090* | 7.5 | 2625 | 80 | 63 | 105 | 77.4 | 0.91 | 24.46
DSH090* | 7.5 | 2625 | 80 | 67 | 105 | 80 | 0.77 | 21.21
DSH090* | 7.5 | 2625 | 80 | 71 | 105 | 84 | 0.6 | 17.8
DSH090* | 7.5 | 2625 | 80 | 59 | 115 | 71.8 | 1 | 24.87
DSH090* | 7.5 | 2625 | 80 | 63 | 115 | 73 | 1 | 25.3
DSH090* | 7.5 | 2625 | 80 | 67 | 115 | 75.7 | 0.85 | 22.3
DSH090* | 7.5 | 2625 | 80 | 71 | 115 | 79.7 | 0.7 | 18.9
DSH090* | 7.5 | 2625 | 85 | 59 | 65 | 89.5 | 0.97 | 29.91
DSH090* | 7.5 | 2625 | 85 | 63 | 65 | 90.7 | 0.9 | 28.17
DSH090* | 7.5 | 2625 | 85 | 67 | 65 | 93.3 | 0.77 | 24.92
DSH090* | 7.5 | 2625 | 85 | 71 | 65 | 97.3 | 0.6 | 21.6
DSH090* | 7.5 | 2625 | 85 | 59 | 75 | 88.7 | 0.97 | 29.87
DSH090* | 7.5 | 2625 | 85 | 63 | 75 | 89.9 | 0.9 | 28.13
DSH090* | 7.5 | 2625 | 85 | 67 | 75 | 92.5 | 0.78 | 24.88
DSH090* | 7.5 | 2625 | 85 | 71 | 75 | 96.5 | 0.6 | 21.5
DSH090* | 7.5 | 2625 | 85 | 59 | 85 | 86.4 | 1 | 29.92
DSH090* | 7.5 | 2625 | 85 | 63 | 85 | 87.6 | 0.93 | 28.37
DSH090* | 7.5 | 2625 | 85 | 67 | 85 | 90.3 | 0.8 | 25.12
DSH090* | 7.5 | 2625 | 85 | 71 | 85 | 94.2 | 0.7 | 21.8
DSH090* | 7.5 | 2625 | 85 | 59 | 95 | 82.5 | 1 | 28.56
DSH090* | 7.5 | 2625 | 85 | 63 | 95 | 83.7 | 0.97 | 28.11
DSH090* | 7.5 | 2625 | 85 | 67 | 95 | 86.3 | 0.83 | 24.86
DSH090* | 7.5 | 2625 | 85 | 71 | 95 | 90.3 | 0.7 | 21.5
DSH090* | 7.5 | 2625 | 85 | 59 | 105 | 77.7 | 1 | 26.9
DSH090* | 7.5 | 2625 | 85 | 63 | 105 | 78.9 | 1 | 27.33
DSH090* | 7.5 | 2625 | 85 | 67 | 105 | 81.5 | 0.87 | 24.63
DSH090* | 7.5 | 2625 | 85 | 71 | 105 | 85.5 | 0.7 | 21.3
DSH090* | 7.5 | 2625 | 85 | 59 | 115 | 73.3 | 1 | 25.38
DSH090* | 7.5 | 2625 | 85 | 63 | 115 | 74.5 | 1 | 25.81
DSH090* | 7.5 | 2625 | 85 | 67 | 115 | 77.1 | 0.96 | 25.72
DSH090* | 7.5 | 2625 | 85 | 71 | 115 | 81.1 | 0.8 | 22.4
DSH090* | 7.5 | 3000 | 70 | 59 | 65 | 88.6 | 0.66 | 17.77
DSH090* | 7.5 | 3000 | 70 | 63 | 65 | 89.9 | 0.59 | 16.03
DSH090* | 7.5 | 3000 | 70 | 67 | 65 | 92.5 | 0.46 | 12.78
DSH090* | 7.5 | 3000 | 70 | 59 | 75 | 87.9 | 0.67 | 17.72
DSH090* | 7.5 | 3000 | 70 | 63 | 75 | 89.1 | 0.59 | 15.98
DSH090* | 7.5 | 3000 | 70 | 67 | 75 | 91.7 | 0.46 | 12.73
DSH090* | 7.5 | 3000 | 70 | 59 | 85 | 85.6 | 0.69 | 17.96
DSH090* | 7.5 | 3000 | 70 | 63 | 85 | 86.8 | 0.62 | 16.22
DSH090* | 7.5 | 3000 | 70 | 67 | 85 | 89.4 | 0.48 | 12.97
DSH090* | 7.5 | 3000 | 70 | 59 | 95 | 81.6 | 0.72 | 17.7
DSH090* | 7.5 | 3000 | 70 | 63 | 95 | 82.9 | 0.64 | 15.96
DSH090* | 7.5 | 3000 | 70 | 67 | 95 | 85.5 | 0.49 | 12.71
DSH090* | 7.5 | 3000 | 70 | 59 | 105 | 76.8 | 0.75 | 17.47
DSH090* | 7.5 | 3000 | 70 | 63 | 105 | 78.1 | 0.66 | 15.73
DSH090* | 7.5 | 3000 | 70 | 67 | 105 | 80.7 | 0.51 | 12.48
DSH090* | 7.5 | 3000 | 70 | 59 | 115 | 72.5 | 0.85 | 18.56
DSH090* | 7.5 | 3000 | 70 | 63 | 115 | 73.7 | 0.75 | 16.82
DSH090* | 7.5 | 3000 | 70 | 67 | 115 | 76.3 | 0.59 | 13.57
DSH090* | 7.5 | 3000 | 75 | 59 | 65 | 88.7 | 0.8 | 21.59
DSH090* | 7.5 | 3000 | 75 | 63 | 65 | 89.9 | 0.73 | 19.85
DSH090* | 7.5 | 3000 | 75 | 67 | 65 | 92.5 | 0.59 | 16.6
DSH090* | 7.5 | 3000 | 75 | 71 | 65 | 96.5 | 0.5 | 13.2
DSH090* | 7.5 | 3000 | 75 | 59 | 75 | 87.9 | 0.81 | 21.55
DSH090* | 7.5 | 3000 | 75 | 63 | 75 | 89.1 | 0.73 | 19.81
DSH090* | 7.5 | 3000 | 75 | 67 | 75 | 91.8 | 0.6 | 16.56
DSH090* | 7.5 | 3000 | 75 | 71 | 75 | 95.8 | 0.5 | 13.2
DSH090* | 7.5 | 3000 | 75 | 59 | 85 | 85.6 | 0.84 | 21.79
DSH090* | 7.5 | 3000 | 75 | 63 | 85 | 86.9 | 0.76 | 20.05
DSH090* | 7.5 | 3000 | 75 | 67 | 85 | 89.5 | 0.62 | 16.8
DSH090* | 7.5 | 3000 | 75 | 71 | 85 | 93.5 | 0.5 | 13.4
DSH090* | 7.5 | 3000 | 75 | 59 | 95 | 81.7 | 0.87 | 21.53
DSH090* | 7.5 | 3000 | 75 | 63 | 95 | 82.9 | 0.79 | 19.79
DSH090* | 7.5 | 3000 | 75 | 67 | 95 | 85.5 | 0.64 | 16.54
DSH090* | 7.5 | 3000 | 75 | 71 | 95 | 89.5 | 0.5 | 13.2
DSH090* | 7.5 | 3000 | 75 | 59 | 105 | 76.9 | 0.91 | 21.3
DSH090* | 7.5 | 3000 | 75 | 63 | 105 | 78.1 | 0.83 | 19.56
DSH090* | 7.5 | 3000 | 75 | 67 | 105 | 80.7 | 0.67 | 16.31
DSH090* | 7.5 | 3000 | 75 | 71 | 105 | 84.7 | 0.5 | 12.9
DSH090* | 7.5 | 3000 | 75 | 59 | 115 | 72.5 | 1 | 21.97
DSH090* | 7.5 | 3000 | 75 | 63 | 115 | 73.7 | 0.92 | 20.65
DSH090* | 7.5 | 3000 | 75 | 67 | 115 | 76.4 | 0.75 | 17.4
DSH090* | 7.5 | 3000 | 75 | 71 | 115 | 80.3 | 0.6 | 14
DSH090* | 7.5 | 3000 | 80 | 59 | 65 | 89.1 | 0.94 | 25.45
DSH090* | 7.5 | 3000 | 80 | 63 | 65 | 90.4 | 0.87 | 23.71
DSH090* | 7.5 | 3000 | 80 | 67 | 65 | 93 | 0.73 | 20.46
DSH090* | 7.5 | 3000 | 80 | 71 | 65 | 97 | 0.6 | 17.1
DSH090* | 7.5 | 3000 | 80 | 59 | 75 | 88.4 | 0.95 | 25.4
DSH090* | 7.5 | 3000 | 80 | 63 | 75 | 89.6 | 0.87 | 23.66
DSH090* | 7.5 | 3000 | 80 | 67 | 75 | 92.2 | 0.73 | 20.41
DSH090* | 7.5 | 3000 | 80 | 71 | 75 | 96.2 | 0.6 | 17
DSH090* | 7.5 | 3000 | 80 | 59 | 85 | 86.1 | 0.98 | 25.64
DSH090* | 7.5 | 3000 | 80 | 63 | 85 | 87.3 | 0.9 | 23.9
DSH090* | 7.5 | 3000 | 80 | 67 | 85 | 89.9 | 0.76 | 20.65
DSH090* | 7.5 | 3000 | 80 | 71 | 85 | 93.9 | 0.6 | 17.3
DSH090* | 7.5 | 3000 | 80 | 59 | 95 | 82.1 | 1 | 24.89
DSH090* | 7.5 | 3000 | 80 | 63 | 95 | 83.4 | 0.94 | 23.64
DSH090* | 7.5 | 3000 | 80 | 67 | 95 | 86 | 0.78 | 20.39
DSH090* | 7.5 | 3000 | 80 | 71 | 95 | 90 | 0.6 | 17
DSH090* | 7.5 | 3000 | 80 | 59 | 105 | 77.3 | 1 | 23.44
DSH090* | 7.5 | 3000 | 80 | 63 | 105 | 78.6 | 0.98 | 23.41
DSH090* | 7.5 | 3000 | 80 | 67 | 105 | 81.2 | 0.82 | 20.16
DSH090* | 7.5 | 3000 | 80 | 71 | 105 | 85.2 | 0.7 | 16.8
DSH090* | 7.5 | 3000 | 80 | 59 | 115 | 73 | 1 | 22.11
DSH090* | 7.5 | 3000 | 80 | 63 | 115 | 74.2 | 1 | 22.48
DSH090* | 7.5 | 3000 | 80 | 67 | 115 | 76.8 | 0.91 | 21.25
DSH090* | 7.5 | 3000 | 80 | 71 | 115 | 80.8 | 0.7 | 17.9
DSH090* | 7.5 | 3000 | 85 | 59 | 65 | 90.6 | 1 | 27.46
DSH090* | 7.5 | 3000 | 85 | 63 | 65 | 91.9 | 0.97 | 27.12
DSH090* | 7.5 | 3000 | 85 | 67 | 65 | 94.5 | 0.83 | 23.87
DSH090* | 7.5 | 3000 | 85 | 71 | 65 | 98.5 | 0.7 | 20.5
DSH090* | 7.5 | 3000 | 85 | 59 | 75 | 89.8 | 1 | 27.22
DSH090* | 7.5 | 3000 | 85 | 63 | 75 | 91.1 | 0.98 | 27.08
DSH090* | 7.5 | 3000 | 85 | 67 | 75 | 93.7 | 0.84 | 23.83
DSH090* | 7.5 | 3000 | 85 | 71 | 75 | 97.7 | 0.7 | 20.5
DSH090* | 7.5 | 3000 | 85 | 59 | 85 | 87.6 | 1 | 26.53
DSH090* | 7.5 | 3000 | 85 | 63 | 85 | 88.8 | 1 | 26.91
DSH090* | 7.5 | 3000 | 85 | 67 | 85 | 91.4 | 0.87 | 24.07
DSH090* | 7.5 | 3000 | 85 | 71 | 85 | 95.4 | 0.7 | 20.7
DSH090* | 7.5 | 3000 | 85 | 59 | 95 | 83.6 | 1 | 25.34
DSH090* | 7.5 | 3000 | 85 | 63 | 95 | 84.9 | 1 | 25.72
DSH090* | 7.5 | 3000 | 85 | 67 | 95 | 87.5 | 0.9 | 23.81
DSH090* | 7.5 | 3000 | 85 | 71 | 95 | 91.5 | 0.7 | 20.4
DSH090* | 7.5 | 3000 | 85 | 59 | 105 | 78.8 | 1 | 23.88
DSH090* | 7.5 | 3000 | 85 | 63 | 105 | 80.1 | 1 | 24.26
DSH090* | 7.5 | 3000 | 85 | 67 | 105 | 82.7 | 0.94 | 23.58
DSH090* | 7.5 | 3000 | 85 | 71 | 105 | 86.7 | 0.8 | 20.2
DSH090* | 7.5 | 3000 | 85 | 59 | 115 | 74.4 | 1 | 22.56
DSH090* | 7.5 | 3000 | 85 | 63 | 115 | 75.7 | 1 | 22.93
DSH090* | 7.5 | 3000 | 85 | 67 | 115 | 78.3 | 1 | 23.72
DSH090* | 7.5 | 3000 | 85 | 71 | 115 | 82.3 | 0.9 | 21.3
DSH090* | 7.5 | 3375 | 70 | 59 | 65 | 90 | 0.7 | 16.88
DSH090* | 7.5 | 3375 | 70 | 63 | 65 | 91.3 | 0.62 | 15.14
DSH090* | 7.5 | 3375 | 70 | 67 | 65 | 93.9 | 0.47 | 11.89
DSH090* | 7.5 | 3375 | 70 | 59 | 75 | 89.2 | 0.7 | 16.83
DSH090* | 7.5 | 3375 | 70 | 63 | 75 | 90.5 | 0.62 | 15.09
DSH090* | 7.5 | 3375 | 70 | 67 | 75 | 93.1 | 0.47 | 11.84
DSH090* | 7.5 | 3375 | 70 | 59 | 85 | 87 | 0.73 | 17.08
DSH090* | 7.5 | 3375 | 70 | 63 | 85 | 88.2 | 0.65 | 15.34
DSH090* | 7.5 | 3375 | 70 | 67 | 85 | 90.8 | 0.49 | 12.09
DSH090* | 7.5 | 3375 | 70 | 59 | 95 | 83 | 0.75 | 16.82
DSH090* | 7.5 | 3375 | 70 | 63 | 95 | 84.3 | 0.66 | 15.08
DSH090* | 7.5 | 3375 | 70 | 67 | 95 | 86.9 | 0.51 | 11.83
DSH090* | 7.5 | 3375 | 70 | 59 | 105 | 78.2 | 0.79 | 16.58
DSH090* | 7.5 | 3375 | 70 | 63 | 105 | 79.5 | 0.69 | 14.84
DSH090* | 7.5 | 3375 | 70 | 67 | 105 | 82.1 | 0.52 | 11.59
DSH090* | 7.5 | 3375 | 70 | 59 | 115 | 73.8 | 0.89 | 17.67
DSH090* | 7.5 | 3375 | 70 | 63 | 115 | 75.1 | 0.79 | 15.93
DSH090* | 7.5 | 3375 | 70 | 67 | 115 | 77.7 | 0.61 | 12.68
DSH090* | 7.5 | 3375 | 75 | 59 | 65 | 90.1 | 0.85 | 20.71
DSH090* | 7.5 | 3375 | 75 | 63 | 65 | 91.3 | 0.77 | 18.97
DSH090* | 7.5 | 3375 | 75 | 67 | 65 | 93.9 | 0.62 | 15.72
DSH090* | 7.5 | 3375 | 75 | 71 | 65 | 97.9 | 0.5 | 12.4
DSH090* | 7.5 | 3375 | 75 | 59 | 75 | 89.3 | 0.86 | 20.66
DSH090* | 7.5 | 3375 | 75 | 63 | 75 | 90.5 | 0.78 | 18.92
DSH090* | 7.5 | 3375 | 75 | 67 | 75 | 93.1 | 0.62 | 15.67
DSH090* | 7.5 | 3375 | 75 | 71 | 75 | 97.1 | 0.5 | 12.3
DSH090* | 7.5 | 3375 | 75 | 59 | 85 | 87 | 0.89 | 20.91
DSH090* | 7.5 | 3375 | 75 | 63 | 85 | 88.2 | 0.81 | 19.17
DSH090* | 7.5 | 3375 | 75 | 67 | 85 | 90.9 | 0.65 | 15.92
DSH090* | 7.5 | 3375 | 75 | 71 | 85 | 94.8 | 0.5 | 12.5
DSH090* | 7.5 | 3375 | 75 | 59 | 95 | 83.1 | 0.92 | 20.64
DSH090* | 7.5 | 3375 | 75 | 63 | 95 | 84.3 | 0.83 | 18.9
DSH090* | 7.5 | 3375 | 75 | 67 | 95 | 86.9 | 0.67 | 15.65
DSH090* | 7.5 | 3375 | 75 | 71 | 95 | 90.9 | 0.5 | 12.3
DSH090* | 7.5 | 3375 | 75 | 59 | 105 | 78.3 | 0.97 | 20.41
DSH090* | 7.5 | 3375 | 75 | 63 | 105 | 79.5 | 0.87 | 18.67
DSH090* | 7.5 | 3375 | 75 | 67 | 105 | 82.1 | 0.7 | 15.42
DSH090* | 7.5 | 3375 | 75 | 71 | 105 | 86.1 | 0.5 | 12.1
DSH090* | 7.5 | 3375 | 75 | 59 | 115 | 73.9 | 1 | 19.9
DSH090* | 7.5 | 3375 | 75 | 63 | 115 | 75.1 | 0.98 | 19.76
DSH090* | 7.5 | 3375 | 75 | 67 | 115 | 77.7 | 0.79 | 16.51
DSH090* | 7.5 | 3375 | 75 | 71 | 115 | 81.7 | 0.6 | 13.1
DSH090* | 7.5 | 3375 | 80 | 59 | 65 | 90.5 | 1 | 24.38
DSH090* | 7.5 | 3375 | 80 | 63 | 65 | 91.8 | 0.92 | 22.82
DSH090* | 7.5 | 3375 | 80 | 67 | 65 | 94.4 | 0.77 | 19.57
DSH090* | 7.5 | 3375 | 80 | 71 | 65 | 98.4 | 0.6 | 16.2
DSH090* | 7.5 | 3375 | 80 | 59 | 75 | 89.7 | 1 | 24.17
DSH090* | 7.5 | 3375 | 80 | 63 | 75 | 91 | 0.93 | 22.77
DSH090* | 7.5 | 3375 | 80 | 67 | 75 | 93.6 | 0.77 | 19.52
DSH090* | 7.5 | 3375 | 80 | 71 | 75 | 97.6 | 0.6 | 16.2
DSH090* | 7.5 | 3375 | 80 | 59 | 85 | 87.5 | 1 | 23.56
DSH090* | 7.5 | 3375 | 80 | 63 | 85 | 88.7 | 0.96 | 23.02
DSH090* | 7.5 | 3375 | 80 | 67 | 85 | 91.3 | 0.8 | 19.77
DSH090* | 7.5 | 3375 | 80 | 71 | 85 | 95.3 | 0.6 | 16.4
DSH090* | 7.5 | 3375 | 80 | 59 | 95 | 83.5 | 1 | 22.5
DSH090* | 7.5 | 3375 | 80 | 63 | 95 | 84.8 | 1 | 22.76
DSH090* | 7.5 | 3375 | 80 | 67 | 95 | 87.4 | 0.83 | 19.51
DSH090* | 7.5 | 3375 | 80 | 71 | 95 | 91.4 | 0.7 | 16.1
DSH090* | 7.5 | 3375 | 80 | 59 | 105 | 78.7 | 1 | 21.21
DSH090* | 7.5 | 3375 | 80 | 63 | 105 | 80 | 1 | 21.54
DSH090* | 7.5 | 3375 | 80 | 67 | 105 | 82.6 | 0.87 | 19.27
DSH090* | 7.5 | 3375 | 80 | 71 | 105 | 86.6 | 0.7 | 15.9
DSH090* | 7.5 | 3375 | 80 | 59 | 115 | 74.3 | 1 | 20.02
DSH090* | 7.5 | 3375 | 80 | 63 | 115 | 75.6 | 1 | 20.36
DSH090* | 7.5 | 3375 | 80 | 67 | 115 | 78.2 | 0.97 | 20.36
DSH090* | 7.5 | 3375 | 80 | 71 | 115 | 82.2 | 0.8 | 17
DSH090* | 7.5 | 3375 | 85 | 59 | 65 | 92 | 1 | 24.78
DSH090* | 7.5 | 3375 | 85 | 63 | 65 | 93.2 | 1 | 25.11
DSH090* | 7.5 | 3375 | 85 | 67 | 65 | 95.9 | 0.89 | 22.99
DSH090* | 7.5 | 3375 | 85 | 71 | 65 | 99.8 | 0.7 | 19.6
DSH090* | 7.5 | 3375 | 85 | 59 | 75 | 91.2 | 1 | 24.57
DSH090* | 7.5 | 3375 | 85 | 63 | 75 | 92.5 | 1 | 24.9
DSH090* | 7.5 | 3375 | 85 | 67 | 75 | 95.1 | 0.9 | 22.94
DSH090* | 7.5 | 3375 | 85 | 71 | 75 | 99.1 | 0.7 | 19.6
DSH090* | 7.5 | 3375 | 85 | 59 | 85 | 88.9 | 1 | 23.96
DSH090* | 7.5 | 3375 | 85 | 63 | 85 | 90.2 | 1 | 24.29
DSH090* | 7.5 | 3375 | 85 | 67 | 85 | 92.8 | 0.93 | 23.19
DSH090* | 7.5 | 3375 | 85 | 71 | 85 | 96.8 | 0.8 | 19.8
DSH090* | 7.5 | 3375 | 85 | 59 | 95 | 85 | 1 | 22.9
DSH090* | 7.5 | 3375 | 85 | 63 | 95 | 86.2 | 1 | 23.23
DSH090* | 7.5 | 3375 | 85 | 67 | 95 | 88.9 | 0.96 | 22.92
DSH090* | 7.5 | 3375 | 85 | 71 | 95 | 92.8 | 0.8 | 19.6
DSH090* | 7.5 | 3375 | 85 | 59 | 105 | 80.2 | 1 | 21.6
DSH090* | 7.5 | 3375 | 85 | 63 | 105 | 81.4 | 1 | 21.94
DSH090* | 7.5 | 3375 | 85 | 67 | 105 | 84.1 | 1 | 22.64
DSH090* | 7.5 | 3375 | 85 | 71 | 105 | 88 | 0.8 | 19.3
DSH090* | 7.5 | 3375 | 85 | 59 | 115 | 75.8 | 1 | 20.42
DSH090* | 7.5 | 3375 | 85 | 63 | 115 | 77.1 | 1 | 20.75
DSH090* | 7.5 | 3375 | 85 | 67 | 115 | 79.7 | 1 | 21.46
DSH090* | 7.5 | 3375 | 85 | 71 | 115 | 83.7 | 0.9 | 20.4
DSH102* | 8.5 | 2625 | 70 | 59 | 65 | 99.3 | 0.61 | 21.03
DSH102* | 8.5 | 2625 | 70 | 63 | 65 | 100.7 | 0.55 | 19.09
DSH102* | 8.5 | 2625 | 70 | 67 | 65 | 103.6 | 0.43 | 15.46
DSH102* | 8.5 | 2625 | 70 | 59 | 75 | 98.4 | 0.62 | 20.98
DSH102* | 8.5 | 2625 | 70 | 63 | 75 | 99.8 | 0.55 | 19.04
DSH102* | 8.5 | 2625 | 70 | 67 | 75 | 102.8 | 0.43 | 15.4
DSH102* | 8.5 | 2625 | 70 | 59 | 85 | 95.8 | 0.64 | 21.25
DSH102* | 8.5 | 2625 | 70 | 63 | 85 | 97.2 | 0.57 | 19.31
DSH102* | 8.5 | 2625 | 70 | 67 | 85 | 100.2 | 0.45 | 15.68
DSH102* | 8.5 | 2625 | 70 | 59 | 95 | 91.3 | 0.66 | 20.96
DSH102* | 8.5 | 2625 | 70 | 63 | 95 | 92.7 | 0.59 | 19.02
DSH102* | 8.5 | 2625 | 70 | 67 | 95 | 95.7 | 0.46 | 15.38
DSH102* | 8.5 | 2625 | 70 | 59 | 105 | 85.8 | 0.7 | 20.7
DSH102* | 8.5 | 2625 | 70 | 63 | 105 | 87.2 | 0.62 | 18.76
DSH102* | 8.5 | 2625 | 70 | 67 | 105 | 90.2 | 0.48 | 15.12
DSH102* | 8.5 | 2625 | 70 | 59 | 115 | 80.8 | 0.78 | 21.92
DSH102* | 8.5 | 2625 | 70 | 63 | 115 | 82.2 | 0.7 | 19.97
DSH102* | 8.5 | 2625 | 70 | 67 | 115 | 85.2 | 0.55 | 16.34
DSH102* | 8.5 | 2625 | 75 | 59 | 65 | 99.8 | 0.73 | 25.31
DSH102* | 8.5 | 2625 | 75 | 63 | 65 | 101.2 | 0.67 | 23.37
DSH102* | 8.5 | 2625 | 75 | 67 | 65 | 104.1 | 0.55 | 19.73
DSH102* | 8.5 | 2625 | 75 | 71 | 65 | 108.7 | 0.4 | 16
DSH102* | 8.5 | 2625 | 75 | 59 | 75 | 98.9 | 0.74 | 25.26
DSH102* | 8.5 | 2625 | 75 | 63 | 75 | 100.3 | 0.67 | 23.31
DSH102* | 8.5 | 2625 | 75 | 67 | 75 | 103.3 | 0.55 | 19.68
DSH102* | 8.5 | 2625 | 75 | 71 | 75 | 107.8 | 0.4 | 15.9
DSH102* | 8.5 | 2625 | 75 | 59 | 85 | 96.3 | 0.77 | 25.53
DSH102* | 8.5 | 2625 | 75 | 63 | 85 | 97.7 | 0.7 | 23.59
DSH102* | 8.5 | 2625 | 75 | 67 | 85 | 100.7 | 0.57 | 19.95
DSH102* | 8.5 | 2625 | 75 | 71 | 85 | 105.2 | 0.4 | 16.2
DSH102* | 8.5 | 2625 | 75 | 59 | 95 | 91.8 | 0.79 | 25.24
DSH102* | 8.5 | 2625 | 75 | 63 | 95 | 93.2 | 0.72 | 23.29
DSH102* | 8.5 | 2625 | 75 | 67 | 95 | 96.2 | 0.59 | 19.66
DSH102* | 8.5 | 2625 | 75 | 71 | 95 | 100.7 | 0.5 | 15.9
DSH102* | 8.5 | 2625 | 75 | 59 | 105 | 86.3 | 0.84 | 24.98
DSH102* | 8.5 | 2625 | 75 | 63 | 105 | 87.7 | 0.76 | 23.03
DSH102* | 8.5 | 2625 | 75 | 67 | 105 | 90.7 | 0.62 | 19.4
DSH102* | 8.5 | 2625 | 75 | 71 | 105 | 95.2 | 0.5 | 15.6
DSH102* | 8.5 | 2625 | 75 | 59 | 115 | 81.3 | 0.93 | 26.2
DSH102* | 8.5 | 2625 | 75 | 63 | 115 | 82.7 | 0.85 | 24.25
DSH102* | 8.5 | 2625 | 75 | 67 | 115 | 85.7 | 0.69 | 20.62
DSH102* | 8.5 | 2625 | 75 | 71 | 115 | 90.3 | 0.5 | 16.9
DSH102* | 8.5 | 2625 | 80 | 59 | 65 | 100.3 | 0.85 | 29.62
DSH102* | 8.5 | 2625 | 80 | 63 | 65 | 101.7 | 0.79 | 27.67
DSH102* | 8.5 | 2625 | 80 | 67 | 65 | 104.7 | 0.66 | 24.04
DSH102* | 8.5 | 2625 | 80 | 71 | 65 | 109.2 | 0.5 | 20.3
DSH102* | 8.5 | 2625 | 80 | 59 | 75 | 99.4 | 0.86 | 29.56
DSH102* | 8.5 | 2625 | 80 | 63 | 75 | 100.8 | 0.79 | 27.62
DSH102* | 8.5 | 2625 | 80 | 67 | 75 | 103.8 | 0.67 | 23.99
DSH102* | 8.5 | 2625 | 80 | 71 | 75 | 108.3 | 0.5 | 20.2
DSH102* | 8.5 | 2625 | 80 | 59 | 85 | 96.8 | 0.89 | 29.84
DSH102* | 8.5 | 2625 | 80 | 63 | 85 | 98.2 | 0.82 | 27.89
DSH102* | 8.5 | 2625 | 80 | 67 | 85 | 101.2 | 0.69 | 24.26
DSH102* | 8.5 | 2625 | 80 | 71 | 85 | 105.7 | 0.6 | 20.5
DSH102* | 8.5 | 2625 | 80 | 59 | 95 | 92.3 | 0.92 | 29.54
DSH102* | 8.5 | 2625 | 80 | 63 | 95 | 93.7 | 0.85 | 27.6
DSH102* | 8.5 | 2625 | 80 | 67 | 95 | 96.7 | 0.72 | 23.97
DSH102* | 8.5 | 2625 | 80 | 71 | 95 | 101.2 | 0.6 | 20.2
DSH102* | 8.5 | 2625 | 80 | 59 | 105 | 86.8 | 0.97 | 29.28
DSH102* | 8.5 | 2625 | 80 | 63 | 105 | 88.2 | 0.89 | 27.34
DSH102* | 8.5 | 2625 | 80 | 67 | 105 | 91.2 | 0.75 | 23.71
DSH102* | 8.5 | 2625 | 80 | 71 | 105 | 95.8 | 0.6 | 19.9
DSH102* | 8.5 | 2625 | 80 | 59 | 115 | 81.8 | 1 | 28.34
DSH102* | 8.5 | 2625 | 80 | 63 | 115 | 83.2 | 0.99 | 28.56
DSH102* | 8.5 | 2625 | 80 | 67 | 115 | 86.2 | 0.83 | 24.93
DSH102* | 8.5 | 2625 | 80 | 71 | 115 | 90.8 | 0.7 | 21.2
DSH102* | 8.5 | 2625 | 85 | 59 | 65 | 102 | 0.95 | 33.44
DSH102* | 8.5 | 2625 | 85 | 63 | 65 | 103.4 | 0.88 | 31.49
DSH102* | 8.5 | 2625 | 85 | 67 | 65 | 106.3 | 0.76 | 27.86
DSH102* | 8.5 | 2625 | 85 | 71 | 65 | 110.9 | 0.6 | 24.1
DSH102* | 8.5 | 2625 | 85 | 59 | 75 | 101.1 | 0.95 | 33.38
DSH102* | 8.5 | 2625 | 85 | 63 | 75 | 102.5 | 0.89 | 31.44
DSH102* | 8.5 | 2625 | 85 | 67 | 75 | 105.5 | 0.76 | 27.81
DSH102* | 8.5 | 2625 | 85 | 71 | 75 | 110 | 0.6 | 24
DSH102* | 8.5 | 2625 | 85 | 59 | 85 | 98.5 | 0.99 | 33.66
DSH102* | 8.5 | 2625 | 85 | 63 | 85 | 99.9 | 0.92 | 31.71
DSH102* | 8.5 | 2625 | 85 | 67 | 85 | 102.8 | 0.79 | 28.08
DSH102* | 8.5 | 2625 | 85 | 71 | 85 | 107.4 | 0.7 | 24.3
DSH102* | 8.5 | 2625 | 85 | 59 | 95 | 94 | 1 | 32.55
DSH102* | 8.5 | 2625 | 85 | 63 | 95 | 95.4 | 0.95 | 31.42
DSH102* | 8.5 | 2625 | 85 | 67 | 95 | 98.4 | 0.82 | 27.79
DSH102* | 8.5 | 2625 | 85 | 71 | 95 | 102.9 | 0.7 | 24
DSH102* | 8.5 | 2625 | 85 | 59 | 105 | 88.5 | 1 | 30.65
DSH102* | 8.5 | 2625 | 85 | 63 | 105 | 89.9 | 1 | 31.14
DSH102* | 8.5 | 2625 | 85 | 67 | 105 | 92.9 | 0.86 | 27.53
DSH102* | 8.5 | 2625 | 85 | 71 | 105 | 97.4 | 0.7 | 23.8
DSH102* | 8.5 | 2625 | 85 | 59 | 115 | 83.5 | 1 | 28.92
DSH102* | 8.5 | 2625 | 85 | 63 | 115 | 84.9 | 1 | 29.41
DSH102* | 8.5 | 2625 | 85 | 67 | 115 | 87.9 | 0.94 | 28.74
DSH102* | 8.5 | 2625 | 85 | 71 | 115 | 92.4 | 0.8 | 25
DSH102* | 8.5 | 3000 | 70 | 59 | 65 | 100.6 | 0.65 | 19.86
DSH102* | 8.5 | 3000 | 70 | 63 | 65 | 102 | 0.58 | 17.91
DSH102* | 8.5 | 3000 | 70 | 67 | 65 | 105 | 0.45 | 14.28
DSH102* | 8.5 | 3000 | 70 | 59 | 75 | 99.7 | 0.66 | 19.81
DSH102* | 8.5 | 3000 | 70 | 63 | 75 | 101.1 | 0.58 | 17.86
DSH102* | 8.5 | 3000 | 70 | 67 | 75 | 104.1 | 0.45 | 14.23
DSH102* | 8.5 | 3000 | 70 | 59 | 85 | 97.1 | 0.68 | 20.08
DSH102* | 8.5 | 3000 | 70 | 63 | 85 | 98.5 | 0.61 | 18.13
DSH102* | 8.5 | 3000 | 70 | 67 | 85 | 101.5 | 0.47 | 14.5
DSH102* | 8.5 | 3000 | 70 | 59 | 95 | 92.6 | 0.71 | 19.79
DSH102* | 8.5 | 3000 | 70 | 63 | 95 | 94 | 0.63 | 17.84
DSH102* | 8.5 | 3000 | 70 | 67 | 95 | 97 | 0.48 | 14.21
DSH102* | 8.5 | 3000 | 70 | 59 | 105 | 87.1 | 0.74 | 19.53
DSH102* | 8.5 | 3000 | 70 | 63 | 105 | 88.5 | 0.66 | 17.58
DSH102* | 8.5 | 3000 | 70 | 67 | 105 | 91.5 | 0.5 | 13.95
DSH102* | 8.5 | 3000 | 70 | 59 | 115 | 82.1 | 0.83 | 20.74
DSH102* | 8.5 | 3000 | 70 | 63 | 115 | 83.5 | 0.74 | 18.8
DSH102* | 8.5 | 3000 | 70 | 67 | 115 | 86.5 | 0.58 | 15.17
DSH102* | 8.5 | 3000 | 75 | 59 | 65 | 101.1 | 0.79 | 24.14
DSH102* | 8.5 | 3000 | 75 | 63 | 65 | 102.5 | 0.71 | 22.19
DSH102* | 8.5 | 3000 | 75 | 67 | 65 | 105.5 | 0.58 | 18.56
DSH102* | 8.5 | 3000 | 75 | 71 | 65 | 110 | 0.4 | 14.8
DSH102* | 8.5 | 3000 | 75 | 59 | 75 | 100.2 | 0.79 | 24.08
DSH102* | 8.5 | 3000 | 75 | 63 | 75 | 101.6 | 0.72 | 22.14
DSH102* | 8.5 | 3000 | 75 | 67 | 75 | 104.6 | 0.58 | 18.51
DSH102* | 8.5 | 3000 | 75 | 71 | 75 | 109.1 | 0.4 | 14.7
DSH102* | 8.5 | 3000 | 75 | 59 | 85 | 97.6 | 0.82 | 24.36
DSH102* | 8.5 | 3000 | 75 | 63 | 85 | 99 | 0.75 | 22.41
DSH102* | 8.5 | 3000 | 75 | 67 | 85 | 102 | 0.61 | 18.78
DSH102* | 8.5 | 3000 | 75 | 71 | 85 | 106.5 | 0.5 | 15
DSH102* | 8.5 | 3000 | 75 | 59 | 95 | 93.1 | 0.85 | 24.06
DSH102* | 8.5 | 3000 | 75 | 63 | 95 | 94.5 | 0.77 | 22.12
DSH102* | 8.5 | 3000 | 75 | 67 | 95 | 97.5 | 0.63 | 18.49
DSH102* | 8.5 | 3000 | 75 | 71 | 95 | 102 | 0.5 | 14.7
DSH102* | 8.5 | 3000 | 75 | 59 | 105 | 87.6 | 0.9 | 23.8
DSH102* | 8.5 | 3000 | 75 | 63 | 105 | 89 | 0.81 | 21.86
DSH102* | 8.5 | 3000 | 75 | 67 | 105 | 92 | 0.65 | 18.23
DSH102* | 8.5 | 3000 | 75 | 71 | 105 | 96.6 | 0.5 | 14.5
DSH102* | 8.5 | 3000 | 75 | 59 | 115 | 82.6 | 1 | 25.02
DSH102* | 8.5 | 3000 | 75 | 63 | 115 | 84 | 0.91 | 23.08
DSH102* | 8.5 | 3000 | 75 | 67 | 115 | 87 | 0.74 | 19.44
DSH102* | 8.5 | 3000 | 75 | 71 | 115 | 91.6 | 0.6 | 15.7
DSH102* | 8.5 | 3000 | 80 | 59 | 65 | 101.6 | 0.92 | 28.44
DSH102* | 8.5 | 3000 | 80 | 63 | 65 | 103 | 0.85 | 26.5
DSH102* | 8.5 | 3000 | 80 | 67 | 65 | 106 | 0.71 | 22.87
DSH102* | 8.5 | 3000 | 80 | 71 | 65 | 110.5 | 0.6 | 19.1
DSH102* | 8.5 | 3000 | 80 | 59 | 75 | 100.7 | 0.93 | 28.39
DSH102* | 8.5 | 3000 | 80 | 63 | 75 | 102.1 | 0.85 | 26.44
DSH102* | 8.5 | 3000 | 80 | 67 | 75 | 105.1 | 0.72 | 22.81
DSH102* | 8.5 | 3000 | 80 | 71 | 75 | 109.6 | 0.6 | 19
DSH102* | 8.5 | 3000 | 80 | 59 | 85 | 98.1 | 0.96 | 28.66
DSH102* | 8.5 | 3000 | 80 | 63 | 85 | 99.5 | 0.89 | 26.72
DSH102* | 8.5 | 3000 | 80 | 67 | 85 | 102.5 | 0.74 | 23.09
DSH102* | 8.5 | 3000 | 80 | 71 | 85 | 107 | 0.6 | 19.3
DSH102* | 8.5 | 3000 | 80 | 59 | 95 | 93.6 | 1 | 28.37
DSH102* | 8.5 | 3000 | 80 | 63 | 95 | 95 | 0.92 | 26.42
DSH102* | 8.5 | 3000 | 80 | 67 | 95 | 98 | 0.77 | 22.79
DSH102* | 8.5 | 3000 | 80 | 71 | 95 | 102.5 | 0.6 | 19
DSH102* | 8.5 | 3000 | 80 | 59 | 105 | 88.1 | 1 | 26.71
DSH102* | 8.5 | 3000 | 80 | 63 | 105 | 89.5 | 0.96 | 26.16
DSH102* | 8.5 | 3000 | 80 | 67 | 105 | 92.5 | 0.8 | 22.53
DSH102* | 8.5 | 3000 | 80 | 71 | 105 | 97.1 | 0.6 | 18.8
DSH102* | 8.5 | 3000 | 80 | 59 | 115 | 83.1 | 1 | 25.19
DSH102* | 8.5 | 3000 | 80 | 63 | 115 | 84.5 | 1 | 25.62
DSH102* | 8.5 | 3000 | 80 | 67 | 115 | 87.5 | 0.9 | 23.75
DSH102* | 8.5 | 3000 | 80 | 71 | 115 | 92.1 | 0.7 | 20
DSH102* | 8.5 | 3000 | 85 | 59 | 65 | 103.3 | 1 | 31.29
DSH102* | 8.5 | 3000 | 85 | 63 | 65 | 104.7 | 0.96 | 30.32
DSH102* | 8.5 | 3000 | 85 | 67 | 65 | 107.7 | 0.82 | 26.68
DSH102* | 8.5 | 3000 | 85 | 71 | 65 | 112.2 | 0.7 | 22.9
DSH102* | 8.5 | 3000 | 85 | 59 | 75 | 102.4 | 1 | 31.02
DSH102* | 8.5 | 3000 | 85 | 63 | 75 | 103.8 | 0.96 | 30.26
DSH102* | 8.5 | 3000 | 85 | 67 | 75 | 106.8 | 0.82 | 26.63
DSH102* | 8.5 | 3000 | 85 | 71 | 75 | 111.3 | 0.7 | 22.9
DSH102* | 8.5 | 3000 | 85 | 59 | 85 | 99.8 | 1 | 30.23
DSH102* | 8.5 | 3000 | 85 | 63 | 85 | 101.2 | 1 | 30.54
DSH102* | 8.5 | 3000 | 85 | 67 | 85 | 104.2 | 0.85 | 26.9
DSH102* | 8.5 | 3000 | 85 | 71 | 85 | 108.7 | 0.7 | 23.1
DSH102* | 8.5 | 3000 | 85 | 59 | 95 | 95.3 | 1 | 28.88
DSH102* | 8.5 | 3000 | 85 | 63 | 95 | 96.7 | 1 | 29.3
DSH102* | 8.5 | 3000 | 85 | 67 | 95 | 99.7 | 0.88 | 26.61
DSH102* | 8.5 | 3000 | 85 | 71 | 95 | 104.2 | 0.7 | 22.8
DSH102* | 8.5 | 3000 | 85 | 59 | 105 | 89.8 | 1 | 27.22
DSH102* | 8.5 | 3000 | 85 | 63 | 105 | 91.2 | 1 | 27.64
DSH102* | 8.5 | 3000 | 85 | 67 | 105 | 94.2 | 0.92 | 26.35
DSH102* | 8.5 | 3000 | 85 | 71 | 105 | 98.8 | 0.8 | 22.6
DSH102* | 8.5 | 3000 | 85 | 59 | 115 | 84.8 | 1 | 25.7
DSH102* | 8.5 | 3000 | 85 | 63 | 115 | 86.2 | 1 | 26.13
DSH102* | 8.5 | 3000 | 85 | 67 | 115 | 89.2 | 1 | 27.03
DSH102* | 8.5 | 3000 | 85 | 71 | 115 | 93.8 | 0.8 | 23.8
DSH102* | 8.5 | 3375 | 70 | 59 | 65 | 102.1 | 0.69 | 18.87
DSH102* | 8.5 | 3375 | 70 | 63 | 65 | 103.6 | 0.61 | 16.92
DSH102* | 8.5 | 3375 | 70 | 67 | 65 | 106.5 | 0.46 | 13.29
DSH102* | 8.5 | 3375 | 70 | 59 | 75 | 101.3 | 0.69 | 18.82
DSH102* | 8.5 | 3375 | 70 | 63 | 75 | 102.7 | 0.61 | 16.87
DSH102* | 8.5 | 3375 | 70 | 67 | 75 | 105.6 | 0.47 | 13.24
DSH102* | 8.5 | 3375 | 70 | 59 | 85 | 98.6 | 0.72 | 19.09
DSH102* | 8.5 | 3375 | 70 | 63 | 85 | 100.1 | 0.64 | 17.14
DSH102* | 8.5 | 3375 | 70 | 67 | 85 | 103 | 0.49 | 13.51
DSH102* | 8.5 | 3375 | 70 | 59 | 95 | 94.2 | 0.74 | 18.8
DSH102* | 8.5 | 3375 | 70 | 63 | 95 | 95.6 | 0.65 | 16.85
DSH102* | 8.5 | 3375 | 70 | 67 | 95 | 98.6 | 0.5 | 13.22
DSH102* | 8.5 | 3375 | 70 | 59 | 105 | 88.7 | 0.78 | 18.54
DSH102* | 8.5 | 3375 | 70 | 63 | 105 | 90.1 | 0.68 | 16.59
DSH102* | 8.5 | 3375 | 70 | 67 | 105 | 93.1 | 0.52 | 12.96
DSH102* | 8.5 | 3375 | 70 | 59 | 115 | 83.7 | 0.88 | 19.75
DSH102* | 8.5 | 3375 | 70 | 63 | 115 | 85.1 | 0.78 | 17.81
DSH102* | 8.5 | 3375 | 70 | 67 | 115 | 88.1 | 0.6 | 14.18
DSH102* | 8.5 | 3375 | 75 | 59 | 65 | 102.6 | 0.84 | 23.15
DSH102* | 8.5 | 3375 | 75 | 63 | 65 | 104.1 | 0.76 | 21.2
DSH102* | 8.5 | 3375 | 75 | 67 | 65 | 107 | 0.61 | 17.57
DSH102* | 8.5 | 3375 | 75 | 71 | 65 | 111.6 | 0.5 | 13.8
DSH102* | 8.5 | 3375 | 75 | 59 | 75 | 101.8 | 0.84 | 23.09
DSH102* | 8.5 | 3375 | 75 | 63 | 75 | 103.2 | 0.76 | 21.15
DSH102* | 8.5 | 3375 | 75 | 67 | 75 | 106.1 | 0.61 | 17.52
DSH102* | 8.5 | 3375 | 75 | 71 | 75 | 110.7 | 0.5 | 13.8
DSH102* | 8.5 | 3375 | 75 | 59 | 85 | 99.1 | 0.87 | 23.37
DSH102* | 8.5 | 3375 | 75 | 63 | 85 | 100.6 | 0.79 | 21.42
DSH102* | 8.5 | 3375 | 75 | 67 | 85 | 103.5 | 0.64 | 17.79
DSH102* | 8.5 | 3375 | 75 | 71 | 85 | 108.1 | 0.5 | 14
DSH102* | 8.5 | 3375 | 75 | 59 | 95 | 94.7 | 0.9 | 23.07
DSH102* | 8.5 | 3375 | 75 | 63 | 95 | 96.1 | 0.82 | 21.13
DSH102* | 8.5 | 3375 | 75 | 67 | 95 | 99.1 | 0.66 | 17.5
DSH102* | 8.5 | 3375 | 75 | 71 | 95 | 103.6 | 0.5 | 13.7
DSH102* | 8.5 | 3375 | 75 | 59 | 105 | 89.2 | 0.95 | 22.81
DSH102* | 8.5 | 3375 | 75 | 63 | 105 | 90.6 | 0.86 | 20.87
DSH102* | 8.5 | 3375 | 75 | 67 | 105 | 93.6 | 0.68 | 17.24
DSH102* | 8.5 | 3375 | 75 | 71 | 105 | 98.1 | 0.5 | 13.5
DSH102* | 8.5 | 3375 | 75 | 59 | 115 | 84.2 | 1 | 22.68
DSH102* | 8.5 | 3375 | 75 | 63 | 115 | 85.6 | 0.96 | 22.09
DSH102* | 8.5 | 3375 | 75 | 67 | 115 | 88.6 | 0.77 | 18.45
DSH102* | 8.5 | 3375 | 75 | 71 | 115 | 93.1 | 0.6 | 14.7
DSH102* | 8.5 | 3375 | 80 | 59 | 65 | 103.2 | 0.99 | 27.45
DSH102* | 8.5 | 3375 | 80 | 63 | 65 | 104.6 | 0.91 | 25.51
DSH102* | 8.5 | 3375 | 80 | 67 | 65 | 107.5 | 0.76 | 21.88
DSH102* | 8.5 | 3375 | 80 | 71 | 65 | 112.1 | 0.6 | 18.1
DSH102* | 8.5 | 3375 | 80 | 59 | 75 | 102.3 | 0.99 | 27.4
DSH102* | 8.5 | 3375 | 80 | 63 | 75 | 103.7 | 0.91 | 25.45
DSH102* | 8.5 | 3375 | 80 | 67 | 75 | 106.7 | 0.76 | 21.82
DSH102* | 8.5 | 3375 | 80 | 71 | 75 | 111.2 | 0.6 | 18.1
DSH102* | 8.5 | 3375 | 80 | 59 | 85 | 99.7 | 1 | 26.85
DSH102* | 8.5 | 3375 | 80 | 63 | 85 | 101.1 | 0.95 | 25.73
DSH102* | 8.5 | 3375 | 80 | 67 | 85 | 104.1 | 0.79 | 22.1
DSH102* | 8.5 | 3375 | 80 | 71 | 85 | 108.6 | 0.6 | 18.3
DSH102* | 8.5 | 3375 | 80 | 59 | 95 | 95.2 | 1 | 25.64
DSH102* | 8.5 | 3375 | 80 | 63 | 95 | 96.6 | 0.98 | 25.43
DSH102* | 8.5 | 3375 | 80 | 67 | 95 | 99.6 | 0.81 | 21.8
DSH102* | 8.5 | 3375 | 80 | 71 | 95 | 104.1 | 0.6 | 18
DSH102* | 8.5 | 3375 | 80 | 59 | 105 | 89.7 | 1 | 24.16
DSH102* | 8.5 | 3375 | 80 | 63 | 105 | 91.1 | 1 | 24.54
DSH102* | 8.5 | 3375 | 80 | 67 | 105 | 94.1 | 0.85 | 21.54
DSH102* | 8.5 | 3375 | 80 | 71 | 105 | 98.6 | 0.7 | 17.8
DSH102* | 8.5 | 3375 | 80 | 59 | 115 | 84.7 | 1 | 22.82
DSH102* | 8.5 | 3375 | 80 | 63 | 115 | 86.1 | 1 | 23.2
DSH102* | 8.5 | 3375 | 80 | 67 | 115 | 89.1 | 0.95 | 22.76
DSH102* | 8.5 | 3375 | 80 | 71 | 115 | 93.7 | 0.8 | 19
DSH102* | 8.5 | 3375 | 85 | 59 | 65 | 104.8 | 1 | 28.24
DSH102* | 8.5 | 3375 | 85 | 63 | 65 | 106.2 | 1 | 28.62
DSH102* | 8.5 | 3375 | 85 | 67 | 65 | 109.2 | 0.87 | 25.69
DSH102* | 8.5 | 3375 | 85 | 71 | 65 | 113.8 | 0.7 | 21.9
DSH102* | 8.5 | 3375 | 85 | 59 | 75 | 103.9 | 1 | 28
DSH102* | 8.5 | 3375 | 85 | 63 | 75 | 105.4 | 1 | 28.38
DSH102* | 8.5 | 3375 | 85 | 67 | 75 | 108.3 | 0.88 | 25.64
DSH102* | 8.5 | 3375 | 85 | 71 | 75 | 112.9 | 0.7 | 21.9
DSH102* | 8.5 | 3375 | 85 | 59 | 85 | 101.3 | 1 | 27.3
DSH102* | 8.5 | 3375 | 85 | 63 | 85 | 102.8 | 1 | 27.68
DSH102* | 8.5 | 3375 | 85 | 67 | 85 | 105.7 | 0.91 | 25.92
DSH102* | 8.5 | 3375 | 85 | 71 | 85 | 110.3 | 0.7 | 22.2
DSH102* | 8.5 | 3375 | 85 | 59 | 95 | 96.9 | 1 | 26.09
DSH102* | 8.5 | 3375 | 85 | 63 | 95 | 98.3 | 1 | 26.47
DSH102* | 8.5 | 3375 | 85 | 67 | 95 | 101.3 | 0.94 | 25.62
DSH102* | 8.5 | 3375 | 85 | 71 | 95 | 105.8 | 0.8 | 21.9
DSH102* | 8.5 | 3375 | 85 | 59 | 105 | 91.4 | 1 | 24.62
DSH102* | 8.5 | 3375 | 85 | 63 | 105 | 92.8 | 1 | 25
DSH102* | 8.5 | 3375 | 85 | 67 | 105 | 95.8 | 0.98 | 25.36
DSH102* | 8.5 | 3375 | 85 | 71 | 105 | 100.3 | 0.8 | 21.6
DSH102* | 8.5 | 3375 | 85 | 59 | 115 | 86.4 | 1 | 23.27
DSH102* | 8.5 | 3375 | 85 | 63 | 115 | 87.8 | 1 | 23.65
DSH102* | 8.5 | 3375 | 85 | 67 | 115 | 90.8 | 1 | 24.45
DSH102* | 8.5 | 3375 | 85 | 71 | 115 | 95.3 | 0.9 | 22.8
DSH120* | 10 | 3325 | 70 | 59 | 65 | 117.4 | 0.62 | 19.83
DSH120* | 10 | 3325 | 70 | 63 | 65 | 119 | 0.55 | 18.01
DSH120* | 10 | 3325 | 70 | 67 | 65 | 122.6 | 0.44 | 14.6
DSH120* | 10 | 3325 | 70 | 59 | 75 | 116.3 | 0.62 | 19.78
DSH120* | 10 | 3325 | 70 | 63 | 75 | 118 | 0.56 | 17.96
DSH120* | 10 | 3325 | 70 | 67 | 75 | 121.5 | 0.44 | 14.55
DSH120* | 10 | 3325 | 70 | 59 | 85 | 113.2 | 0.65 | 20.04
DSH120* | 10 | 3325 | 70 | 63 | 85 | 114.9 | 0.58 | 18.21
DSH120* | 10 | 3325 | 70 | 67 | 85 | 118.4 | 0.46 | 14.81
DSH120* | 10 | 3325 | 70 | 59 | 95 | 107.9 | 0.67 | 19.76
DSH120* | 10 | 3325 | 70 | 63 | 95 | 109.6 | 0.6 | 17.94
DSH120* | 10 | 3325 | 70 | 67 | 95 | 113.1 | 0.47 | 14.53
DSH120* | 10 | 3325 | 70 | 59 | 105 | 101.4 | 0.7 | 19.52
DSH120* | 10 | 3325 | 70 | 63 | 105 | 103.1 | 0.63 | 17.69
DSH120* | 10 | 3325 | 70 | 67 | 105 | 106.6 | 0.49 | 14.29
DSH120* | 10 | 3325 | 70 | 59 | 115 | 95.5 | 0.79 | 20.66
DSH120* | 10 | 3325 | 70 | 63 | 115 | 97.2 | 0.71 | 18.84
DSH120* | 10 | 3325 | 70 | 67 | 115 | 100.7 | 0.56 | 15.43
DSH120* | 10 | 3325 | 75 | 59 | 65 | 118 | 0.74 | 23.84
DSH120* | 10 | 3325 | 75 | 63 | 65 | 119.6 | 0.67 | 22.02
DSH120* | 10 | 3325 | 75 | 67 | 65 | 123.2 | 0.55 | 18.61
DSH120* | 10 | 3325 | 75 | 71 | 65 | 128.5 | 0.4 | 15.1
DSH120* | 10 | 3325 | 75 | 59 | 75 | 116.9 | 0.74 | 23.79
DSH120* | 10 | 3325 | 75 | 63 | 75 | 118.6 | 0.68 | 21.97
DSH120* | 10 | 3325 | 75 | 67 | 75 | 122.1 | 0.56 | 18.56
DSH120* | 10 | 3325 | 75 | 71 | 75 | 127.5 | 0.4 | 15
DSH120* | 10 | 3325 | 75 | 59 | 85 | 113.8 | 0.77 | 24.05
DSH120* | 10 | 3325 | 75 | 63 | 85 | 115.5 | 0.7 | 22.22
DSH120* | 10 | 3325 | 75 | 67 | 85 | 119 | 0.58 | 18.82
DSH120* | 10 | 3325 | 75 | 71 | 85 | 124.4 | 0.4 | 15.3
DSH120* | 10 | 3325 | 75 | 59 | 95 | 108.5 | 0.8 | 23.77
DSH120* | 10 | 3325 | 75 | 63 | 95 | 110.2 | 0.73 | 21.95
DSH120* | 10 | 3325 | 75 | 67 | 95 | 113.7 | 0.6 | 18.54
DSH120* | 10 | 3325 | 75 | 71 | 95 | 119.1 | 0.5 | 15
DSH120* | 10 | 3325 | 75 | 59 | 105 | 102 | 0.84 | 23.53
DSH120* | 10 | 3325 | 75 | 63 | 105 | 103.7 | 0.77 | 21.7
DSH120* | 10 | 3325 | 75 | 67 | 105 | 107.2 | 0.62 | 18.3
DSH120* | 10 | 3325 | 75 | 71 | 105 | 112.6 | 0.5 | 14.8
DSH120* | 10 | 3325 | 75 | 59 | 115 | 96.1 | 0.94 | 24.67
DSH120* | 10 | 3325 | 75 | 63 | 115 | 97.8 | 0.85 | 22.85
DSH120* | 10 | 3325 | 75 | 67 | 115 | 101.3 | 0.7 | 19.44
DSH120* | 10 | 3325 | 75 | 71 | 115 | 106.7 | 0.5 | 15.9
DSH120* | 10 | 3325 | 80 | 59 | 65 | 118.6 | 0.86 | 27.88
DSH120* | 10 | 3325 | 80 | 63 | 65 | 120.2 | 0.79 | 26.05
DSH120* | 10 | 3325 | 80 | 67 | 65 | 123.8 | 0.67 | 22.65
DSH120* | 10 | 3325 | 80 | 71 | 65 | 129.1 | 0.5 | 19.1
DSH120* | 10 | 3325 | 80 | 59 | 75 | 117.5 | 0.87 | 27.83
DSH120* | 10 | 3325 | 80 | 63 | 75 | 119.2 | 0.8 | 26
DSH120* | 10 | 3325 | 80 | 67 | 75 | 122.7 | 0.67 | 22.6
DSH120* | 10 | 3325 | 80 | 71 | 75 | 128.1 | 0.5 | 19.1
DSH120* | 10 | 3325 | 80 | 59 | 85 | 114.4 | 0.9 | 28.08
DSH120* | 10 | 3325 | 80 | 63 | 85 | 116.1 | 0.83 | 26.26
DSH120* | 10 | 3325 | 80 | 67 | 85 | 119.6 | 0.7 | 22.85
DSH120* | 10 | 3325 | 80 | 71 | 85 | 125 | 0.6 | 19.3
DSH120* | 10 | 3325 | 80 | 59 | 95 | 109.1 | 0.93 | 27.81
DSH120* | 10 | 3325 | 80 | 63 | 95 | 110.8 | 0.86 | 25.98
DSH120* | 10 | 3325 | 80 | 67 | 95 | 114.3 | 0.72 | 22.58
DSH120* | 10 | 3325 | 80 | 71 | 95 | 119.7 | 0.6 | 19.1
DSH120* | 10 | 3325 | 80 | 59 | 105 | 102.6 | 0.98 | 27.56
DSH120* | 10 | 3325 | 80 | 63 | 105 | 104.3 | 0.9 | 25.74
DSH120* | 10 | 3325 | 80 | 67 | 105 | 107.8 | 0.76 | 22.34
DSH120* | 10 | 3325 | 80 | 71 | 105 | 113.2 | 0.6 | 18.8
DSH120* | 10 | 3325 | 80 | 59 | 115 | 96.7 | 1 | 26.45
DSH120* | 10 | 3325 | 80 | 63 | 115 | 98.4 | 1 | 26.88
DSH120* | 10 | 3325 | 80 | 67 | 115 | 101.9 | 0.84 | 23.48
DSH120* | 10 | 3325 | 80 | 71 | 115 | 107.3 | 0.7 | 19.9
DSH120* | 10 | 3325 | 85 | 59 | 65 | 120.6 | 0.95 | 31.46
DSH120* | 10 | 3325 | 85 | 63 | 65 | 122.2 | 0.89 | 29.63
DSH120* | 10 | 3325 | 85 | 67 | 65 | 125.7 | 0.76 | 26.23
DSH120* | 10 | 3325 | 85 | 71 | 65 | 131.1 | 0.6 | 22.7
DSH120* | 10 | 3325 | 85 | 59 | 75 | 119.5 | 0.96 | 31.41
DSH120* | 10 | 3325 | 85 | 63 | 75 | 121.2 | 0.89 | 29.58
DSH120* | 10 | 3325 | 85 | 67 | 75 | 124.7 | 0.77 | 26.18
DSH120* | 10 | 3325 | 85 | 71 | 75 | 130.1 | 0.6 | 22.7
DSH120* | 10 | 3325 | 85 | 59 | 85 | 116.4 | 0.99 | 31.66
DSH120* | 10 | 3325 | 85 | 63 | 85 | 118.1 | 0.92 | 29.84
DSH120* | 10 | 3325 | 85 | 67 | 85 | 121.6 | 0.8 | 26.43
DSH120* | 10 | 3325 | 85 | 71 | 85 | 127 | 0.7 | 22.9
DSH120* | 10 | 3325 | 85 | 59 | 95 | 111.1 | 1 | 30.38
DSH120* | 10 | 3325 | 85 | 63 | 95 | 112.8 | 0.96 | 29.56
DSH120* | 10 | 3325 | 85 | 67 | 95 | 116.3 | 0.82 | 26.16
DSH120* | 10 | 3325 | 85 | 71 | 95 | 121.7 | 0.7 | 22.6
DSH120* | 10 | 3325 | 85 | 59 | 105 | 104.6 | 1 | 28.61
DSH120* | 10 | 3325 | 85 | 63 | 105 | 106.3 | 1 | 29.06
DSH120* | 10 | 3325 | 85 | 67 | 105 | 109.8 | 0.86 | 25.92
DSH120* | 10 | 3325 | 85 | 71 | 105 | 115.2 | 0.7 | 22.4
DSH120* | 10 | 3325 | 85 | 59 | 115 | 98.7 | 1 | 26.99
DSH120* | 10 | 3325 | 85 | 63 | 115 | 100.4 | 1 | 27.45
DSH120* | 10 | 3325 | 85 | 67 | 115 | 103.9 | 0.95 | 27.06
DSH120* | 10 | 3325 | 85 | 71 | 115 | 109.3 | 0.8 | 23.5
DSH120* | 10 | 3850 | 70 | 59 | 65 | 119 | 0.66 | 18.62
DSH120* | 10 | 3850 | 70 | 63 | 65 | 120.7 | 0.59 | 16.79
DSH120* | 10 | 3850 | 70 | 67 | 65 | 124.2 | 0.46 | 13.39
DSH120* | 10 | 3850 | 70 | 59 | 75 | 118 | 0.67 | 18.57
DSH120* | 10 | 3850 | 70 | 63 | 75 | 119.6 | 0.59 | 16.74
DSH120* | 10 | 3850 | 70 | 67 | 75 | 123.2 | 0.46 | 13.34
DSH120* | 10 | 3850 | 70 | 59 | 85 | 114.9 | 0.69 | 18.82
DSH120* | 10 | 3850 | 70 | 63 | 85 | 116.6 | 0.62 | 17
DSH120* | 10 | 3850 | 70 | 67 | 85 | 120.1 | 0.48 | 13.59
DSH120* | 10 | 3850 | 70 | 59 | 95 | 109.6 | 0.72 | 18.55
DSH120* | 10 | 3850 | 70 | 63 | 95 | 111.3 | 0.64 | 16.72
DSH120* | 10 | 3850 | 70 | 67 | 95 | 114.8 | 0.49 | 13.32
DSH120* | 10 | 3850 | 70 | 59 | 105 | 103.1 | 0.75 | 18.3
DSH120* | 10 | 3850 | 70 | 63 | 105 | 104.8 | 0.67 | 16.48
DSH120* | 10 | 3850 | 70 | 67 | 105 | 108.3 | 0.51 | 13.08
DSH120* | 10 | 3850 | 70 | 59 | 115 | 97.2 | 0.85 | 19.45
DSH120* | 10 | 3850 | 70 | 63 | 115 | 98.9 | 0.75 | 17.62
DSH120* | 10 | 3850 | 70 | 67 | 115 | 102.4 | 0.59 | 14.22
DSH120* | 10 | 3850 | 75 | 59 | 65 | 119.6 | 0.8 | 22.63
DSH120* | 10 | 3850 | 75 | 63 | 65 | 121.3 | 0.73 | 20.8
DSH120* | 10 | 3850 | 75 | 67 | 65 | 124.8 | 0.59 | 17.4
DSH120* | 10 | 3850 | 75 | 71 | 65 | 130.2 | 0.5 | 13.9
DSH120* | 10 | 3850 | 75 | 59 | 75 | 118.6 | 0.81 | 22.58
DSH120* | 10 | 3850 | 75 | 63 | 75 | 120.2 | 0.73 | 20.75
DSH120* | 10 | 3850 | 75 | 67 | 75 | 123.8 | 0.59 | 17.35
DSH120* | 10 | 3850 | 75 | 71 | 75 | 129.2 | 0.5 | 13.8
DSH120* | 10 | 3850 | 75 | 59 | 85 | 115.5 | 0.84 | 22.83
DSH120* | 10 | 3850 | 75 | 63 | 85 | 117.2 | 0.76 | 21.01
DSH120* | 10 | 3850 | 75 | 67 | 85 | 120.7 | 0.62 | 17.6
DSH120* | 10 | 3850 | 75 | 71 | 85 | 126.1 | 0.5 | 14.1
DSH120* | 10 | 3850 | 75 | 59 | 95 | 110.2 | 0.87 | 22.56
DSH120* | 10 | 3850 | 75 | 63 | 95 | 111.9 | 0.78 | 20.73
DSH120* | 10 | 3850 | 75 | 67 | 95 | 115.4 | 0.64 | 17.33
DSH120* | 10 | 3850 | 75 | 71 | 95 | 120.8 | 0.5 | 13.8
DSH120* | 10 | 3850 | 75 | 59 | 105 | 103.7 | 0.91 | 22.31
DSH120* | 10 | 3850 | 75 | 63 | 105 | 105.4 | 0.82 | 20.49
DSH120* | 10 | 3850 | 75 | 67 | 105 | 108.9 | 0.66 | 17.09
DSH120* | 10 | 3850 | 75 | 71 | 105 | 114.3 | 0.5 | 13.6
DSH120* | 10 | 3850 | 75 | 59 | 115 | 97.8 | 1 | 23.09
DSH120* | 10 | 3850 | 75 | 63 | 115 | 99.5 | 0.92 | 21.63
DSH120* | 10 | 3850 | 75 | 67 | 115 | 103 | 0.75 | 18.23
DSH120* | 10 | 3850 | 75 | 71 | 115 | 108.4 | 0.6 | 14.7
DSH120* | 10 | 3850 | 80 | 59 | 65 | 120.2 | 0.94 | 26.66
DSH120* | 10 | 3850 | 80 | 63 | 65 | 121.9 | 0.86 | 24.84
DSH120* | 10 | 3850 | 80 | 67 | 65 | 125.4 | 0.72 | 21.43
DSH120* | 10 | 3850 | 80 | 71 | 65 | 130.8 | 0.6 | 17.9
DSH120* | 10 | 3850 | 80 | 59 | 75 | 119.2 | 0.95 | 26.61
DSH120* | 10 | 3850 | 80 | 63 | 75 | 120.9 | 0.87 | 24.79
DSH120* | 10 | 3850 | 80 | 67 | 75 | 124.4 | 0.73 | 21.38
DSH120* | 10 | 3850 | 80 | 71 | 75 | 129.8 | 0.6 | 17.9
DSH120* | 10 | 3850 | 80 | 59 | 85 | 116.1 | 0.98 | 26.87
DSH120* | 10 | 3850 | 80 | 63 | 85 | 117.8 | 0.9 | 25.05
DSH120* | 10 | 3850 | 80 | 67 | 85 | 121.3 | 0.76 | 21.64
DSH120* | 10 | 3850 | 80 | 71 | 85 | 126.7 | 0.6 | 18.1
DSH120* | 10 | 3850 | 80 | 59 | 95 | 110.8 | 1 | 26.16
DSH120* | 10 | 3850 | 80 | 63 | 95 | 112.5 | 0.93 | 24.77
DSH120* | 10 | 3850 | 80 | 67 | 95 | 116 | 0.78 | 21.37
DSH120* | 10 | 3850 | 80 | 71 | 95 | 121.4 | 0.6 | 17.8
DSH120* | 10 | 3850 | 80 | 59 | 105 | 104.3 | 1 | 24.63
DSH120* | 10 | 3850 | 80 | 63 | 105 | 106 | 0.98 | 24.53
DSH120* | 10 | 3850 | 80 | 67 | 105 | 109.5 | 0.82 | 21.12
DSH120* | 10 | 3850 | 80 | 71 | 105 | 114.9 | 0.6 | 17.6
DSH120* | 10 | 3850 | 80 | 59 | 115 | 98.4 | 1 | 23.24
DSH120* | 10 | 3850 | 80 | 63 | 115 | 100.1 | 1 | 23.63
DSH120* | 10 | 3850 | 80 | 67 | 115 | 103.6 | 0.91 | 22.26
DSH120* | 10 | 3850 | 80 | 71 | 115 | 109 | 0.7 | 18.7
DSH120* | 10 | 3850 | 85 | 59 | 65 | 122.2 | 1 | 28.86
DSH120* | 10 | 3850 | 85 | 63 | 65 | 123.9 | 0.97 | 28.42
DSH120* | 10 | 3850 | 85 | 67 | 65 | 127.4 | 0.83 | 25.01
DSH120* | 10 | 3850 | 85 | 71 | 65 | 132.8 | 0.7 | 21.5
DSH120* | 10 | 3850 | 85 | 59 | 75 | 121.2 | 1 | 28.61
DSH120* | 10 | 3850 | 85 | 63 | 75 | 122.8 | 0.98 | 28.37
DSH120* | 10 | 3850 | 85 | 67 | 75 | 126.4 | 0.84 | 24.96
DSH120* | 10 | 3850 | 85 | 71 | 75 | 131.8 | 0.7 | 21.4
DSH120* | 10 | 3850 | 85 | 59 | 85 | 118.1 | 1 | 27.89
DSH120* | 10 | 3850 | 85 | 63 | 85 | 119.8 | 1 | 28.28
DSH120* | 10 | 3850 | 85 | 67 | 85 | 123.3 | 0.87 | 25.22
DSH120* | 10 | 3850 | 85 | 71 | 85 | 128.7 | 0.7 | 21.7
DSH120* | 10 | 3850 | 85 | 59 | 95 | 112.8 | 1 | 26.63
DSH120* | 10 | 3850 | 85 | 63 | 95 | 114.5 | 1 | 27.03
DSH120* | 10 | 3850 | 85 | 67 | 95 | 118 | 0.9 | 24.95
DSH120* | 10 | 3850 | 85 | 71 | 95 | 123.4 | 0.7 | 21.4
DSH120* | 10 | 3850 | 85 | 59 | 105 | 106.3 | 1 | 25.1
DSH120* | 10 | 3850 | 85 | 63 | 105 | 108 | 1 | 25.5
DSH120* | 10 | 3850 | 85 | 67 | 105 | 111.5 | 0.94 | 24.7
DSH120* | 10 | 3850 | 85 | 71 | 105 | 116.9 | 0.8 | 21.2
DSH120* | 10 | 3850 | 85 | 59 | 115 | 100.4 | 1 | 23.71
DSH120* | 10 | 3850 | 85 | 63 | 115 | 102.1 | 1 | 24.1
DSH120* | 10 | 3850 | 85 | 67 | 115 | 105.6 | 1 | 24.93
DSH120* | 10 | 3850 | 85 | 71 | 115 | 111 | 0.9 | 22.3
DSH120* | 10 | 4275 | 70 | 59 | 65 | 120.7 | 0.69 | 17.79
DSH120* | 10 | 4275 | 70 | 63 | 65 | 122.3 | 0.61 | 15.97
DSH120* | 10 | 4275 | 70 | 67 | 65 | 125.9 | 0.47 | 12.56
DSH120* | 10 | 4275 | 70 | 59 | 75 | 119.6 | 0.7 | 17.74
DSH120* | 10 | 4275 | 70 | 63 | 75 | 121.3 | 0.62 | 15.92
DSH120* | 10 | 4275 | 70 | 67 | 75 | 124.8 | 0.47 | 12.51
DSH120* | 10 | 4275 | 70 | 59 | 85 | 116.5 | 0.73 | 18
DSH120* | 10 | 4275 | 70 | 63 | 85 | 118.2 | 0.64 | 16.17
DSH120* | 10 | 4275 | 70 | 67 | 85 | 121.7 | 0.49 | 12.77
DSH120* | 10 | 4275 | 70 | 59 | 95 | 111.2 | 0.75 | 17.72
DSH120* | 10 | 4275 | 70 | 63 | 95 | 112.9 | 0.66 | 15.9
DSH120* | 10 | 4275 | 70 | 67 | 95 | 116.4 | 0.5 | 12.49
DSH120* | 10 | 4275 | 70 | 59 | 105 | 104.7 | 0.78 | 17.48
DSH120* | 10 | 4275 | 70 | 63 | 105 | 106.4 | 0.69 | 15.66
DSH120* | 10 | 4275 | 70 | 67 | 105 | 109.9 | 0.52 | 12.25
DSH120* | 10 | 4275 | 70 | 59 | 115 | 98.8 | 0.89 | 18.62
DSH120* | 10 | 4275 | 70 | 63 | 115 | 100.5 | 0.79 | 16.8
DSH120* | 10 | 4275 | 70 | 67 | 115 | 104 | 0.61 | 13.39
DSH120* | 10 | 4275 | 75 | 59 | 65 | 121.3 | 0.85 | 21.8
DSH120* | 10 | 4275 | 75 | 63 | 65 | 122.9 | 0.76 | 19.98
DSH120* | 10 | 4275 | 75 | 67 | 65 | 126.5 | 0.62 | 16.57
DSH120* | 10 | 4275 | 75 | 71 | 65 | 131.8 | 0.5 | 13
DSH120* | 10 | 4275 | 75 | 59 | 75 | 120.2 | 0.85 | 21.75
DSH120* | 10 | 4275 | 75 | 63 | 75 | 121.9 | 0.77 | 19.93
DSH120* | 10 | 4275 | 75 | 67 | 75 | 125.4 | 0.62 | 16.52
DSH120* | 10 | 4275 | 75 | 71 | 75 | 130.8 | 0.5 | 13
DSH120* | 10 | 4275 | 75 | 59 | 85 | 117.1 | 0.88 | 22.01
DSH120* | 10 | 4275 | 75 | 63 | 85 | 118.8 | 0.8 | 20.18
DSH120* | 10 | 4275 | 75 | 67 | 85 | 122.3 | 0.65 | 16.78
DSH120* | 10 | 4275 | 75 | 71 | 85 | 127.7 | 0.5 | 13.3
DSH120* | 10 | 4275 | 75 | 59 | 95 | 111.8 | 0.91 | 21.73
DSH120* | 10 | 4275 | 75 | 63 | 95 | 113.5 | 0.82 | 19.91
DSH120* | 10 | 4275 | 75 | 67 | 95 | 117 | 0.66 | 16.5
DSH120* | 10 | 4275 | 75 | 71 | 95 | 122.4 | 0.5 | 13
DSH120* | 10 | 4275 | 75 | 59 | 105 | 105.3 | 0.96 | 21.49
DSH120* | 10 | 4275 | 75 | 63 | 105 | 107 | 0.86 | 19.66
DSH120* | 10 | 4275 | 75 | 67 | 105 | 110.5 | 0.69 | 16.26
DSH120* | 10 | 4275 | 75 | 71 | 105 | 115.9 | 0.5 | 12.7
DSH120* | 10 | 4275 | 75 | 59 | 115 | 99.4 | 1 | 21.14
DSH120* | 10 | 4275 | 75 | 63 | 115 | 101.1 | 0.97 | 20.81
DSH120* | 10 | 4275 | 75 | 67 | 115 | 104.6 | 0.78 | 17.4
DSH120* | 10 | 4275 | 75 | 71 | 115 | 110 | 0.6 | 13.9
DSH120* | 10 | 4275 | 80 | 59 | 65 | 121.9 | 1 | 25.84
DSH120* | 10 | 4275 | 80 | 63 | 65 | 123.5 | 0.91 | 24.01
DSH120* | 10 | 4275 | 80 | 67 | 65 | 127.1 | 0.76 | 20.61
DSH120* | 10 | 4275 | 80 | 71 | 65 | 132.5 | 0.6 | 17.1
DSH120* | 10 | 4275 | 80 | 59 | 75 | 120.8 | 1 | 25.69
DSH120* | 10 | 4275 | 80 | 63 | 75 | 122.5 | 0.92 | 23.96
DSH120* | 10 | 4275 | 80 | 67 | 75 | 126 | 0.77 | 20.56
DSH120* | 10 | 4275 | 80 | 71 | 75 | 131.4 | 0.6 | 17
DSH120* | 10 | 4275 | 80 | 59 | 85 | 117.7 | 1 | 25.04
DSH120* | 10 | 4275 | 80 | 63 | 85 | 119.4 | 0.95 | 24.22
DSH120* | 10 | 4275 | 80 | 67 | 85 | 122.9 | 0.8 | 20.81
DSH120* | 10 | 4275 | 80 | 71 | 85 | 128.3 | 0.6 | 17.3
DSH120* | 10 | 4275 | 80 | 59 | 95 | 112.4 | 1 | 23.91
DSH120* | 10 | 4275 | 80 | 63 | 95 | 114.1 | 0.99 | 23.94
DSH120* | 10 | 4275 | 80 | 67 | 95 | 117.6 | 0.82 | 20.54
DSH120* | 10 | 4275 | 80 | 71 | 95 | 123 | 0.7 | 17
DSH120* | 10 | 4275 | 80 | 59 | 105 | 106 | 1 | 22.53
DSH120* | 10 | 4275 | 80 | 63 | 105 | 107.6 | 1 | 22.89
DSH120* | 10 | 4275 | 80 | 67 | 105 | 111.1 | 0.86 | 20.3
DSH120* | 10 | 4275 | 80 | 71 | 105 | 116.5 | 0.7 | 16.8
DSH120* | 10 | 4275 | 80 | 59 | 115 | 100 | 1 | 21.27
DSH120* | 10 | 4275 | 80 | 63 | 115 | 101.7 | 1 | 21.63
DSH120* | 10 | 4275 | 80 | 67 | 115 | 105.2 | 0.96 | 21.44
DSH120* | 10 | 4275 | 80 | 71 | 115 | 110.6 | 0.8 | 17.9
DSH120* | 10 | 4275 | 85 | 59 | 65 | 123.9 | 1 | 26.34
DSH120* | 10 | 4275 | 85 | 63 | 65 | 125.5 | 1 | 26.69
DSH120* | 10 | 4275 | 85 | 67 | 65 | 129.1 | 0.88 | 24.19
DSH120* | 10 | 4275 | 85 | 71 | 65 | 134.4 | 0.7 | 20.7
DSH120* | 10 | 4275 | 85 | 59 | 75 | 122.8 | 1 | 26.11
DSH120* | 10 | 4275 | 85 | 63 | 75 | 124.5 | 1 | 26.47
DSH120* | 10 | 4275 | 85 | 67 | 75 | 128 | 0.89 | 24.14
DSH120* | 10 | 4275 | 85 | 71 | 75 | 133.4 | 0.7 | 20.6
DSH120* | 10 | 4275 | 85 | 59 | 85 | 119.7 | 1 | 25.46
DSH120* | 10 | 4275 | 85 | 63 | 85 | 121.4 | 1 | 25.81
DSH120* | 10 | 4275 | 85 | 67 | 85 | 124.9 | 0.92 | 24.4
DSH120* | 10 | 4275 | 85 | 71 | 85 | 130.3 | 0.8 | 20.9
DSH120* | 10 | 4275 | 85 | 59 | 95 | 114.4 | 1 | 24.33
DSH120* | 10 | 4275 | 85 | 63 | 95 | 116.1 | 1 | 24.69
DSH120* | 10 | 4275 | 85 | 67 | 95 | 119.6 | 0.95 | 24.12
DSH120* | 10 | 4275 | 85 | 71 | 95 | 125 | 0.8 | 20.6
DSH120* | 10 | 4275 | 85 | 59 | 105 | 107.9 | 1 | 22.95
DSH120* | 10 | 4275 | 85 | 63 | 105 | 109.6 | 1 | 23.31
DSH120* | 10 | 4275 | 85 | 67 | 105 | 113.1 | 0.99 | 23.88
DSH120* | 10 | 4275 | 85 | 71 | 105 | 118.5 | 0.8 | 20.3
DSH120* | 10 | 4275 | 85 | 59 | 115 | 102 | 1 | 21.7
DSH120* | 10 | 4275 | 85 | 63 | 115 | 103.7 | 1 | 22.05
DSH120* | 10 | 4275 | 85 | 67 | 115 | 107.2 | 1 | 22.8
DSH120* | 10 | 4275 | 85 | 71 | 115 | 112.6 | 0.9 | 21.5
DSH150* | 12.5 | 3750 | 70 | 59 | 65 | 144.97 | 0.59 | 20.62
DSH150* | 12.5 | 3750 | 70 | 63 | 65 | 147.03 | 0.53 | 18.75
DSH150* | 12.5 | 3750 | 70 | 67 | 65 | 151.37 | 0.42 | 15.26
DSH150* | 12.5 | 3750 | 70 | 59 | 75 | 143.67 | 0.59 | 20.57
DSH150* | 12.5 | 3750 | 70 | 63 | 75 | 145.72 | 0.53 | 18.7
DSH150* | 12.5 | 3750 | 70 | 67 | 75 | 150.07 | 0.42 | 15.21
DSH150* | 12.5 | 3750 | 70 | 59 | 85 | 139.87 | 0.61 | 20.83
DSH150* | 12.5 | 3750 | 70 | 63 | 85 | 141.92 | 0.55 | 18.96
DSH150* | 12.5 | 3750 | 70 | 67 | 85 | 146.27 | 0.44 | 15.47
DSH150* | 12.5 | 3750 | 70 | 59 | 95 | 133.33 | 0.64 | 20.55
DSH150* | 12.5 | 3750 | 70 | 63 | 95 | 135.39 | 0.57 | 18.68
DSH150* | 12.5 | 3750 | 70 | 67 | 95 | 139.73 | 0.45 | 15.19
DSH150* | 12.5 | 3750 | 70 | 59 | 105 | 125.35 | 0.67 | 20.3
DSH150* | 12.5 | 3750 | 70 | 63 | 105 | 127.4 | 0.6 | 18.43
DSH150* | 12.5 | 3750 | 70 | 67 | 105 | 131.75 | 0.47 | 14.94
DSH150* | 12.5 | 3750 | 70 | 59 | 115 | 118.05 | 0.75 | 21.47
DSH150* | 12.5 | 3750 | 70 | 63 | 115 | 120.11 | 0.67 | 19.6
DSH150* | 12.5 | 3750 | 70 | 67 | 115 | 124.45 | 0.53 | 16.11
DSH150* | 12.5 | 3750 | 75 | 59 | 65 | 145.06 | 0.7 | 24.73
DSH150* | 12.5 | 3750 | 75 | 63 | 65 | 147.11 | 0.64 | 22.86
DSH150* | 12.5 | 3750 | 75 | 67 | 65 | 151.46 | 0.53 | 19.37
DSH150* | 12.5 | 3750 | 75 | 71 | 65 | 158.1 | 0.41 | 15.75
DSH150* | 12.5 | 3750 | 75 | 59 | 75 | 143.75 | 0.71 | 24.68
DSH150* | 12.5 | 3750 | 75 | 63 | 75 | 145.81 | 0.65 | 22.81
DSH150* | 12.5 | 3750 | 75 | 67 | 75 | 150.15 | 0.53 | 19.32
DSH150* | 12.5 | 3750 | 75 | 71 | 75 | 156.79 | 0.41 | 15.7
DSH150* | 12.5 | 3750 | 75 | 59 | 85 | 139.95 | 0.74 | 24.95
DSH150* | 12.5 | 3750 | 75 | 63 | 85 | 142.01 | 0.67 | 23.07
DSH150* | 12.5 | 3750 | 75 | 67 | 85 | 146.36 | 0.55 | 19.58
DSH150* | 12.5 | 3750 | 75 | 71 | 85 | 152.99 | 0.43 | 15.96
DSH150* | 12.5 | 3750 | 75 | 59 | 95 | 133.42 | 0.76 | 24.66
DSH150* | 12.5 | 3750 | 75 | 63 | 95 | 135.47 | 0.69 | 22.79
DSH150* | 12.5 | 3750 | 75 | 67 | 95 | 139.82 | 0.57 | 19.3
DSH150* | 12.5 | 3750 | 75 | 71 | 95 | 146.46 | 0.44 | 15.68
DSH150* | 12.5 | 3750 | 75 | 59 | 105 | 125.43 | 0.8 | 24.41
DSH150* | 12.5 | 3750 | 75 | 63 | 105 | 127.48 | 0.73 | 22.54
DSH150* | 12.5 | 3750 | 75 | 67 | 105 | 131.83 | 0.6 | 19.05
DSH150* | 12.5 | 3750 | 75 | 71 | 105 | 138.47 | 0.46 | 15.43
DSH150* | 12.5 | 3750 | 75 | 59 | 115 | 118.14 | 0.89 | 25.58
DSH150* | 12.5 | 3750 | 75 | 63 | 115 | 120.19 | 0.81 | 23.71
DSH150* | 12.5 | 3750 | 75 | 67 | 115 | 124.54 | 0.67 | 20.22
DSH150* | 12.5 | 3750 | 75 | 71 | 115 | 131.18 | 0.52 | 16.6
DSH150* | 12.5 | 3750 | 80 | 59 | 65 | 145.81 | 0.82 | 28.87
DSH150* | 12.5 | 3750 | 80 | 63 | 65 | 147.86 | 0.75 | 27
DSH150* | 12.5 | 3750 | 80 | 67 | 65 | 152.21 | 0.64 | 23.51
DSH150* | 12.5 | 3750 | 80 | 71 | 65 | 158.85 | 0.52 | 19.89
DSH150* | 12.5 | 3750 | 80 | 59 | 75 | 144.51 | 0.82 | 28.82
DSH150* | 12.5 | 3750 | 80 | 63 | 75 | 146.56 | 0.76 | 26.95
DSH150* | 12.5 | 3750 | 80 | 67 | 75 | 150.91 | 0.64 | 23.46
DSH150* | 12.5 | 3750 | 80 | 71 | 75 | 157.55 | 0.52 | 19.84
DSH150* | 12.5 | 3750 | 80 | 59 | 85 | 140.71 | 0.85 | 29.09
DSH150* | 12.5 | 3750 | 80 | 63 | 85 | 142.76 | 0.79 | 27.22
DSH150* | 12.5 | 3750 | 80 | 67 | 85 | 147.11 | 0.67 | 23.72
DSH150* | 12.5 | 3750 | 80 | 71 | 85 | 153.75 | 0.54 | 20.1
DSH150* | 12.5 | 3750 | 80 | 59 | 95 | 134.17 | 0.89 | 28.8
DSH150* | 12.5 | 3750 | 80 | 63 | 95 | 136.23 | 0.82 | 26.93
DSH150* | 12.5 | 3750 | 80 | 67 | 95 | 140.57 | 0.69 | 23.44
DSH150* | 12.5 | 3750 | 80 | 71 | 95 | 147.21 | 0.56 | 19.82
DSH150* | 12.5 | 3750 | 80 | 59 | 105 | 126.18 | 0.93 | 28.55
DSH150* | 12.5 | 3750 | 80 | 63 | 105 | 128.24 | 0.86 | 26.68
DSH150* | 12.5 | 3750 | 80 | 67 | 105 | 132.58 | 0.72 | 23.19
DSH150* | 12.5 | 3750 | 80 | 71 | 105 | 139.22 | 0.58 | 19.57
DSH150* | 12.5 | 3750 | 80 | 59 | 115 | 118.89 | 1 | 28.82
DSH150* | 12.5 | 3750 | 80 | 63 | 115 | 120.95 | 0.95 | 27.85
DSH150* | 12.5 | 3750 | 80 | 67 | 115 | 125.29 | 0.8 | 24.36
DSH150* | 12.5 | 3750 | 80 | 71 | 115 | 131.93 | 0.65 | 20.74
DSH150* | 12.5 | 3750 | 85 | 59 | 65 | 148.26 | 0.91 | 32.55
DSH150* | 12.5 | 3750 | 85 | 63 | 65 | 150.32 | 0.84 | 30.68
DSH150* | 12.5 | 3750 | 85 | 67 | 65 | 154.66 | 0.73 | 27.18
DSH150* | 12.5 | 3750 | 85 | 71 | 65 | 161.3 | 0.6 | 23.56
DSH150* | 12.5 | 3750 | 85 | 59 | 75 | 146.96 | 0.91 | 32.5
DSH150* | 12.5 | 3750 | 85 | 63 | 75 | 149.01 | 0.85 | 30.63
DSH150* | 12.5 | 3750 | 85 | 67 | 75 | 153.36 | 0.73 | 27.13
DSH150* | 12.5 | 3750 | 85 | 71 | 75 | 160 | 0.61 | 23.51
DSH150* | 12.5 | 3750 | 85 | 59 | 85 | 143.16 | 0.94 | 32.76
DSH150* | 12.5 | 3750 | 85 | 63 | 85 | 145.21 | 0.88 | 30.89
DSH150* | 12.5 | 3750 | 85 | 67 | 85 | 149.56 | 0.76 | 27.4
DSH150* | 12.5 | 3750 | 85 | 71 | 85 | 156.2 | 0.63 | 23.78
DSH150* | 12.5 | 3750 | 85 | 59 | 95 | 136.62 | 0.98 | 32.48
DSH150* | 12.5 | 3750 | 85 | 63 | 95 | 138.68 | 0.91 | 30.61
DSH150* | 12.5 | 3750 | 85 | 67 | 95 | 143.02 | 0.78 | 27.11
DSH150* | 12.5 | 3750 | 85 | 71 | 95 | 149.66 | 0.65 | 23.49
DSH150* | 12.5 | 3750 | 85 | 59 | 105 | 128.64 | 1 | 31.18
DSH150* | 12.5 | 3750 | 85 | 63 | 105 | 130.69 | 0.96 | 30.36
DSH150* | 12.5 | 3750 | 85 | 67 | 105 | 135.04 | 0.82 | 26.86
DSH150* | 12.5 | 3750 | 85 | 71 | 105 | 141.67 | 0.68 | 23.24
DSH150* | 12.5 | 3750 | 85 | 59 | 115 | 121.34 | 1 | 29.42
DSH150* | 12.5 | 3750 | 85 | 63 | 115 | 123.4 | 1 | 29.91
DSH150* | 12.5 | 3750 | 85 | 67 | 115 | 127.74 | 0.91 | 28.03
DSH150* | 12.5 | 3750 | 85 | 71 | 115 | 134.38 | 0.75 | 24.42
DSH150* | 12.5 | 4300 | 70 | 59 | 65 | 147.4 | 0.61 | 19.1
DSH150* | 12.5 | 4300 | 70 | 63 | 65 | 149.45 | 0.55 | 17.23
DSH150* | 12.5 | 4300 | 70 | 67 | 65 | 153.8 | 0.42 | 13.73
DSH150* | 12.5 | 4300 | 70 | 59 | 75 | 146.09 | 0.62 | 19.05
DSH150* | 12.5 | 4300 | 70 | 63 | 75 | 148.15 | 0.55 | 17.18
DSH150* | 12.5 | 4300 | 70 | 67 | 75 | 152.5 | 0.42 | 13.68
DSH150* | 12.5 | 4300 | 70 | 59 | 85 | 142.3 | 0.64 | 19.31
DSH150* | 12.5 | 4300 | 70 | 63 | 85 | 144.35 | 0.57 | 17.44
DSH150* | 12.5 | 4300 | 70 | 67 | 85 | 148.7 | 0.44 | 13.95
DSH150* | 12.5 | 4300 | 70 | 59 | 95 | 135.76 | 0.66 | 19.03
DSH150* | 12.5 | 4300 | 70 | 63 | 95 | 137.81 | 0.59 | 17.16
DSH150* | 12.5 | 4300 | 70 | 67 | 95 | 142.16 | 0.45 | 13.66
DSH150* | 12.5 | 4300 | 70 | 59 | 105 | 127.77 | 0.7 | 18.78
DSH150* | 12.5 | 4300 | 70 | 63 | 105 | 129.83 | 0.62 | 16.91
DSH150* | 12.5 | 4300 | 70 | 67 | 105 | 134.17 | 0.47 | 13.41
DSH150* | 12.5 | 4300 | 70 | 59 | 115 | 120.48 | 0.78 | 19.95
DSH150* | 12.5 | 4300 | 70 | 63 | 115 | 122.53 | 0.7 | 18.08
DSH150* | 12.5 | 4300 | 70 | 67 | 115 | 126.88 | 0.54 | 14.59
DSH150* | 12.5 | 4300 | 75 | 59 | 65 | 147.48 | 0.74 | 23.21
DSH150* | 12.5 | 4300 | 75 | 63 | 65 | 149.54 | 0.68 | 21.34
DSH150* | 12.5 | 4300 | 75 | 67 | 65 | 153.88 | 0.55 | 17.85
DSH150* | 12.5 | 4300 | 75 | 71 | 65 | 160.52 | 0.42 | 14.23
DSH150* | 12.5 | 4300 | 75 | 59 | 75 | 146.18 | 0.75 | 23.16
DSH150* | 12.5 | 4300 | 75 | 63 | 75 | 148.23 | 0.68 | 21.29
DSH150* | 12.5 | 4300 | 75 | 67 | 75 | 152.58 | 0.55 | 17.8
DSH150* | 12.5 | 4300 | 75 | 71 | 75 | 159.22 | 0.42 | 14.18
DSH150* | 12.5 | 4300 | 75 | 59 | 85 | 142.38 | 0.78 | 23.42
DSH150* | 12.5 | 4300 | 75 | 63 | 85 | 144.44 | 0.71 | 21.55
DSH150* | 12.5 | 4300 | 75 | 67 | 85 | 148.78 | 0.57 | 18.06
DSH150* | 12.5 | 4300 | 75 | 71 | 85 | 155.42 | 0.44 | 14.44
DSH150* | 12.5 | 4300 | 75 | 59 | 95 | 135.84 | 0.81 | 23.14
DSH150* | 12.5 | 4300 | 75 | 63 | 95 | 137.9 | 0.73 | 21.27
DSH150* | 12.5 | 4300 | 75 | 67 | 95 | 142.25 | 0.59 | 17.78
DSH150* | 12.5 | 4300 | 75 | 71 | 95 | 148.88 | 0.45 | 14.16
DSH150* | 12.5 | 4300 | 75 | 59 | 105 | 127.86 | 0.85 | 22.89
DSH150* | 12.5 | 4300 | 75 | 63 | 105 | 129.91 | 0.77 | 21.02
DSH150* | 12.5 | 4300 | 75 | 67 | 105 | 134.26 | 0.62 | 17.53
DSH150* | 12.5 | 4300 | 75 | 71 | 105 | 140.9 | 0.47 | 13.91
DSH150* | 12.5 | 4300 | 75 | 59 | 115 | 120.56 | 0.94 | 24.06
DSH150* | 12.5 | 4300 | 75 | 63 | 115 | 122.62 | 0.86 | 22.19
DSH150* | 12.5 | 4300 | 75 | 67 | 115 | 126.96 | 0.7 | 18.7
DSH150* | 12.5 | 4300 | 75 | 71 | 115 | 133.6 | 0.53 | 15.08
DSH150* | 12.5 | 4300 | 80 | 59 | 65 | 148.24 | 0.87 | 27.35
DSH150* | 12.5 | 4300 | 80 | 63 | 65 | 150.29 | 0.8 | 25.48
DSH150* | 12.5 | 4300 | 80 | 67 | 65 | 154.64 | 0.67 | 21.99
DSH150* | 12.5 | 4300 | 80 | 71 | 65 | 161.28 | 0.54 | 18.37
DSH150* | 12.5 | 4300 | 80 | 59 | 75 | 146.93 | 0.88 | 27.3
DSH150* | 12.5 | 4300 | 80 | 63 | 75 | 148.99 | 0.81 | 25.43
DSH150* | 12.5 | 4300 | 80 | 67 | 75 | 153.33 | 0.68 | 21.94
DSH150* | 12.5 | 4300 | 80 | 71 | 75 | 159.97 | 0.54 | 18.32
DSH150* | 12.5 | 4300 | 80 | 59 | 85 | 143.13 | 0.91 | 27.56
DSH150* | 12.5 | 4300 | 80 | 63 | 85 | 145.19 | 0.84 | 25.69
DSH150* | 12.5 | 4300 | 80 | 67 | 85 | 149.54 | 0.7 | 22.2
DSH150* | 12.5 | 4300 | 80 | 71 | 85 | 156.17 | 0.56 | 18.58
DSH150* | 12.5 | 4300 | 80 | 59 | 95 | 136.6 | 0.94 | 27.28
DSH150* | 12.5 | 4300 | 80 | 63 | 95 | 138.65 | 0.87 | 25.41
DSH150* | 12.5 | 4300 | 80 | 67 | 95 | 143 | 0.72 | 21.92
DSH150* | 12.5 | 4300 | 80 | 71 | 95 | 149.64 | 0.58 | 18.3
DSH150* | 12.5 | 4300 | 80 | 59 | 105 | 128.61 | 0.99 | 27.03
DSH150* | 12.5 | 4300 | 80 | 63 | 105 | 130.67 | 0.91 | 25.16
DSH150* | 12.5 | 4300 | 80 | 67 | 105 | 135.01 | 0.76 | 21.67
DSH150* | 12.5 | 4300 | 80 | 71 | 105 | 141.65 | 0.6 | 18.05
DSH150* | 12.5 | 4300 | 80 | 59 | 115 | 121.32 | 1 | 25.65
DSH150* | 12.5 | 4300 | 80 | 63 | 115 | 123.37 | 1 | 26.08
DSH150* | 12.5 | 4300 | 80 | 67 | 115 | 127.72 | 0.85 | 22.84
DSH150* | 12.5 | 4300 | 80 | 71 | 115 | 134.36 | 0.68 | 19.22
DSH150* | 12.5 | 4300 | 85 | 59 | 65 | 150.69 | 0.97 | 31.02
DSH150* | 12.5 | 4300 | 85 | 63 | 65 | 152.74 | 0.9 | 29.15
DSH150* | 12.5 | 4300 | 85 | 67 | 65 | 157.09 | 0.77 | 25.66
DSH150* | 12.5 | 4300 | 85 | 71 | 65 | 163.73 | 0.64 | 22.04
DSH150* | 12.5 | 4300 | 85 | 59 | 75 | 149.38 | 0.98 | 30.97
DSH150* | 12.5 | 4300 | 85 | 63 | 75 | 151.44 | 0.91 | 29.1
DSH150* | 12.5 | 4300 | 85 | 67 | 75 | 155.79 | 0.78 | 25.61
DSH150* | 12.5 | 4300 | 85 | 71 | 75 | 162.42 | 0.64 | 21.99
DSH150* | 12.5 | 4300 | 85 | 59 | 85 | 145.59 | 1 | 30.78
DSH150* | 12.5 | 4300 | 85 | 63 | 85 | 147.64 | 0.94 | 29.37
DSH150* | 12.5 | 4300 | 85 | 67 | 85 | 151.99 | 0.81 | 25.87
DSH150* | 12.5 | 4300 | 85 | 71 | 85 | 158.63 | 0.66 | 22.25
DSH150* | 12.5 | 4300 | 85 | 59 | 95 | 139.05 | 1 | 29.4
DSH150* | 12.5 | 4300 | 85 | 63 | 95 | 141.1 | 0.97 | 29.08
DSH150* | 12.5 | 4300 | 85 | 67 | 95 | 145.45 | 0.83 | 25.59
DSH150* | 12.5 | 4300 | 85 | 71 | 95 | 152.09 | 0.68 | 21.97
DSH150* | 12.5 | 4300 | 85 | 59 | 105 | 131.06 | 1 | 27.71
DSH150* | 12.5 | 4300 | 85 | 63 | 105 | 133.12 | 1 | 28.14
DSH150* | 12.5 | 4300 | 85 | 67 | 105 | 137.46 | 0.87 | 25.34
DSH150* | 12.5 | 4300 | 85 | 71 | 105 | 144.1 | 0.71 | 21.72
DSH150* | 12.5 | 4300 | 85 | 59 | 115 | 123.77 | 1 | 26.17
DSH150* | 12.5 | 4300 | 85 | 63 | 115 | 125.82 | 1 | 26.6
DSH150* | 12.5 | 4300 | 85 | 67 | 115 | 130.17 | 0.96 | 26.51
DSH150* | 12.5 | 4300 | 85 | 71 | 115 | 136.81 | 0.79 | 22.89
DSH150* | 12.5 | 6250 | 70 | 59 | 65 | 156.33 | 0.72 | 16.4
DSH150* | 12.5 | 6250 | 70 | 63 | 65 | 158.38 | 0.63 | 14.53
DSH150* | 12.5 | 6250 | 70 | 67 | 65 | 162.73 | 0.47 | 11.03
DSH150* | 12.5 | 6250 | 70 | 59 | 75 | 155.03 | 0.72 | 16.34
DSH150* | 12.5 | 6250 | 70 | 63 | 75 | 157.08 | 0.63 | 14.47
DSH150* | 12.5 | 6250 | 70 | 67 | 75 | 161.43 | 0.47 | 10.98
DSH150* | 12.5 | 6250 | 70 | 59 | 85 | 151.23 | 0.76 | 16.61
DSH150* | 12.5 | 6250 | 70 | 63 | 85 | 153.28 | 0.66 | 14.74
DSH150* | 12.5 | 6250 | 70 | 67 | 85 | 157.63 | 0.49 | 11.24
DSH150* | 12.5 | 6250 | 70 | 59 | 95 | 144.69 | 0.78 | 16.33
DSH150* | 12.5 | 6250 | 70 | 63 | 95 | 146.75 | 0.68 | 14.45
DSH150* | 12.5 | 6250 | 70 | 67 | 95 | 151.09 | 0.5 | 10.96
DSH150* | 12.5 | 6250 | 70 | 59 | 105 | 136.7 | 0.81 | 16.08
DSH150* | 12.5 | 6250 | 70 | 63 | 105 | 138.76 | 0.7 | 14.2
DSH150* | 12.5 | 6250 | 70 | 67 | 105 | 143.1 | 0.51 | 10.71
DSH150* | 12.5 | 6250 | 70 | 59 | 115 | 129.41 | 0.92 | 17.25
DSH150* | 12.5 | 6250 | 70 | 63 | 115 | 131.47 | 0.8 | 15.38
DSH150* | 12.5 | 6250 | 70 | 67 | 115 | 135.81 | 0.6 | 11.88
DSH150* | 12.5 | 6250 | 75 | 59 | 65 | 156.41 | 0.9 | 20.51
DSH150* | 12.5 | 6250 | 75 | 63 | 65 | 158.47 | 0.81 | 18.64
DSH150* | 12.5 | 6250 | 75 | 67 | 65 | 162.82 | 0.64 | 15.15
DSH150* | 12.5 | 6250 | 75 | 71 | 65 | 169.45 | 0.47 | 11.53
DSH150* | 12.5 | 6250 | 75 | 59 | 75 | 155.11 | 0.91 | 20.46
DSH150* | 12.5 | 6250 | 75 | 63 | 75 | 157.17 | 0.81 | 18.59
DSH150* | 12.5 | 6250 | 75 | 67 | 75 | 161.51 | 0.64 | 15.09
DSH150* | 12.5 | 6250 | 75 | 71 | 75 | 168.15 | 0.47 | 11.48
DSH150* | 12.5 | 6250 | 75 | 59 | 85 | 151.31 | 0.94 | 20.72
DSH150* | 12.5 | 6250 | 75 | 63 | 85 | 153.37 | 0.84 | 18.85
DSH150* | 12.5 | 6250 | 75 | 67 | 85 | 157.71 | 0.67 | 15.36
DSH150* | 12.5 | 6250 | 75 | 71 | 85 | 164.35 | 0.49 | 11.74
DSH150* | 12.5 | 6250 | 75 | 59 | 95 | 144.78 | 0.97 | 20.44
DSH150* | 12.5 | 6250 | 75 | 63 | 95 | 146.83 | 0.87 | 18.57
DSH150* | 12.5 | 6250 | 75 | 67 | 95 | 151.18 | 0.69 | 15.08
DSH150* | 12.5 | 6250 | 75 | 71 | 95 | 157.82 | 0.5 | 11.46
DSH150* | 12.5 | 6250 | 75 | 59 | 105 | 136.79 | 1 | 19.9
DSH150* | 12.5 | 6250 | 75 | 63 | 105 | 138.84 | 0.91 | 18.32
DSH150* | 12.5 | 6250 | 75 | 67 | 105 | 143.19 | 0.71 | 14.83
DSH150* | 12.5 | 6250 | 75 | 71 | 105 | 149.83 | 0.51 | 11.21
DSH150* | 12.5 | 6250 | 75 | 59 | 115 | 129.5 | 1 | 18.84
DSH150* | 12.5 | 6250 | 75 | 63 | 115 | 131.55 | 1 | 19.13
DSH150* | 12.5 | 6250 | 75 | 67 | 115 | 135.9 | 0.81 | 16
DSH150* | 12.5 | 6250 | 75 | 71 | 115 | 142.54 | 0.6 | 12.38
DSH150* | 12.5 | 6250 | 80 | 59 | 65 | 157.17 | 1 | 22.86
DSH150* | 12.5 | 6250 | 80 | 63 | 65 | 159.22 | 0.98 | 22.78
DSH150* | 12.5 | 6250 | 80 | 67 | 65 | 163.57 | 0.81 | 19.29
DSH150* | 12.5 | 6250 | 80 | 71 | 65 | 170.21 | 0.63 | 15.67
DSH150* | 12.5 | 6250 | 80 | 59 | 75 | 155.87 | 1 | 22.67
DSH150* | 12.5 | 6250 | 80 | 63 | 75 | 157.92 | 0.99 | 22.73
DSH150* | 12.5 | 6250 | 80 | 67 | 75 | 162.27 | 0.81 | 19.24
DSH150* | 12.5 | 6250 | 80 | 71 | 75 | 168.91 | 0.64 | 15.62
DSH150* | 12.5 | 6250 | 80 | 59 | 85 | 152.07 | 1 | 22.12
DSH150* | 12.5 | 6250 | 80 | 63 | 85 | 154.12 | 1 | 22.42
DSH150* | 12.5 | 6250 | 80 | 67 | 85 | 158.47 | 0.85 | 19.5
DSH150* | 12.5 | 6250 | 80 | 71 | 85 | 165.11 | 0.66 | 15.88
DSH150* | 12.5 | 6250 | 80 | 59 | 95 | 145.53 | 1 | 21.17
DSH150* | 12.5 | 6250 | 80 | 63 | 95 | 147.59 | 1 | 21.47
DSH150* | 12.5 | 6250 | 80 | 67 | 95 | 151.93 | 0.87 | 19.22
DSH150* | 12.5 | 6250 | 80 | 71 | 95 | 158.57 | 0.68 | 15.6
DSH150* | 12.5 | 6250 | 80 | 59 | 105 | 137.54 | 1 | 20.01
DSH150* | 12.5 | 6250 | 80 | 63 | 105 | 139.6 | 1 | 20.31
DSH150* | 12.5 | 6250 | 80 | 67 | 105 | 143.94 | 0.91 | 18.97
DSH150* | 12.5 | 6250 | 80 | 71 | 105 | 150.58 | 0.7 | 15.35
DSH150* | 12.5 | 6250 | 80 | 59 | 115 | 130.25 | 1 | 18.95
DSH150* | 12.5 | 6250 | 80 | 63 | 115 | 132.3 | 1 | 19.24
DSH150* | 12.5 | 6250 | 80 | 67 | 115 | 136.65 | 1 | 19.88
DSH150* | 12.5 | 6250 | 80 | 71 | 115 | 143.29 | 0.79 | 16.52
DSH150* | 12.5 | 6250 | 85 | 59 | 65 | 159.62 | 1 | 23.22
DSH150* | 12.5 | 6250 | 85 | 63 | 65 | 161.67 | 1 | 23.52
DSH150* | 12.5 | 6250 | 85 | 67 | 65 | 166.02 | 0.95 | 22.96
DSH150* | 12.5 | 6250 | 85 | 71 | 65 | 172.66 | 0.77 | 19.34
DSH150* | 12.5 | 6250 | 85 | 59 | 75 | 158.32 | 1 | 23.03
DSH150* | 12.5 | 6250 | 85 | 63 | 75 | 160.37 | 1 | 23.33
DSH150* | 12.5 | 6250 | 85 | 67 | 75 | 164.72 | 0.96 | 22.91
DSH150* | 12.5 | 6250 | 85 | 71 | 75 | 171.36 | 0.77 | 19.29
DSH150* | 12.5 | 6250 | 85 | 59 | 85 | 154.52 | 1 | 22.48
DSH150* | 12.5 | 6250 | 85 | 63 | 85 | 156.57 | 1 | 22.77
DSH150* | 12.5 | 6250 | 85 | 67 | 85 | 160.92 | 0.99 | 23.17
DSH150* | 12.5 | 6250 | 85 | 71 | 85 | 167.56 | 0.8 | 19.55
DSH150* | 12.5 | 6250 | 85 | 59 | 95 | 147.98 | 1 | 21.52
DSH150* | 12.5 | 6250 | 85 | 63 | 95 | 150.04 | 1 | 21.82
DSH150* | 12.5 | 6250 | 85 | 67 | 95 | 154.38 | 1 | 22.46
DSH150* | 12.5 | 6250 | 85 | 71 | 95 | 161.02 | 0.82 | 19.27
DSH150* | 12.5 | 6250 | 85 | 59 | 105 | 139.99 | 1 | 20.36
DSH150* | 12.5 | 6250 | 85 | 63 | 105 | 142.05 | 1 | 20.66
DSH150* | 12.5 | 6250 | 85 | 67 | 105 | 146.39 | 1 | 21.29
DSH150* | 12.5 | 6250 | 85 | 71 | 105 | 153.03 | 0.85 | 19.02
DSH150* | 12.5 | 6250 | 85 | 59 | 115 | 132.7 | 1 | 19.3
DSH150* | 12.5 | 6250 | 85 | 63 | 115 | 134.76 | 1 | 19.6
DSH150* | 12.5 | 6250 | 85 | 67 | 115 | 139.1 | 1 | 20.23
DSH150* | 12.5 | 6250 | 85 | 71 | 115 | 145.74 | 0.95 | 20.19
DSH180* | 15 | 6000 | 70 | 59 | 65 | 181.5 | 0.59 | 16.19
DSH180* | 15 | 6000 | 70 | 63 | 65 | 184.1 | 0.51 | 14.1
DSH180* | 15 | 6000 | 70 | 67 | 65 | 189.6 | 0.36 | 10.26
DSH180* | 15 | 6000 | 70 | 59 | 75 | 179.9 | 0.6 | 16.23
DSH180* | 15 | 6000 | 70 | 63 | 75 | 182.5 | 0.51 | 14.16
DSH180* | 15 | 6000 | 70 | 67 | 75 | 188 | 0.36 | 10.36
DSH180* | 15 | 6000 | 70 | 59 | 85 | 175.1 | 0.62 | 16.52
DSH180* | 15 | 6000 | 70 | 63 | 85 | 177.7 | 0.54 | 14.53
DSH180* | 15 | 6000 | 70 | 67 | 85 | 183.2 | 0.39 | 10.86
DSH180* | 15 | 6000 | 70 | 59 | 95 | 166.9 | 1 | 25.29
DSH180* | 15 | 6000 | 70 | 63 | 95 | 169.5 | 0.56 | 14.4
DSH180* | 15 | 6000 | 70 | 67 | 95 | 175 | 0.41 | 10.94
DSH180* | 15 | 6000 | 70 | 59 | 105 | 156.8 | 1 | 23.76
DSH180* | 15 | 6000 | 70 | 63 | 105 | 159.4 | 0.58 | 14.13
DSH180* | 15 | 6000 | 70 | 67 | 105 | 164.9 | 0.44 | 10.91
DSH180* | 15 | 6000 | 70 | 59 | 115 | 147.7 | 1 | 22.37
DSH180* | 15 | 6000 | 70 | 63 | 115 | 150.2 | 0.64 | 14.6
DSH180* | 15 | 6000 | 70 | 67 | 115 | 155.7 | 0.49 | 11.63
DSH180* | 15 | 6000 | 70 | 59 | 125 | 142.7 | 1 | 21.6
DSH180* | 15 | 6000 | 70 | 63 | 125 | 145.3 | 1 | 22
DSH180* | 15 | 6000 | 70 | 67 | 125 | 150.8 | 0.62 | 14.2
DSH180* | 15 | 6000 | 75 | 59 | 65 | 181.6 | 0.73 | 20.08
DSH180* | 15 | 6000 | 75 | 63 | 65 | 184.2 | 0.65 | 18.04
DSH180* | 15 | 6000 | 75 | 67 | 65 | 189.7 | 0.5 | 14.32
DSH180* | 15 | 6000 | 75 | 71 | 65 | 198.1 | 0.34 | 10.3
DSH180* | 15 | 6000 | 75 | 59 | 75 | 180 | 1 | 27.27
DSH180* | 15 | 6000 | 75 | 63 | 75 | 182.6 | 0.65 | 18.07
DSH180* | 15 | 6000 | 75 | 67 | 75 | 188.1 | 0.5 | 14.39
DSH180* | 15 | 6000 | 75 | 71 | 75 | 196.4 | 0.35 | 10.4
DSH180* | 15 | 6000 | 75 | 59 | 85 | 175.2 | 1 | 26.55
DSH180* | 15 | 6000 | 75 | 63 | 85 | 177.8 | 0.68 | 18.34
DSH180* | 15 | 6000 | 75 | 67 | 85 | 183.3 | 0.53 | 14.78
DSH180* | 15 | 6000 | 75 | 71 | 85 | 191.6 | 0.38 | 10.9
DSH180* | 15 | 6000 | 75 | 59 | 95 | 167 | 1 | 25.3
DSH180* | 15 | 6000 | 75 | 63 | 95 | 169.6 | 0.7 | 18.03
DSH180* | 15 | 6000 | 75 | 67 | 95 | 175.1 | 0.55 | 14.69
DSH180* | 15 | 6000 | 75 | 71 | 95 | 183.4 | 0.4 | 11
DSH180* | 15 | 6000 | 75 | 59 | 105 | 156.9 | 1 | 23.78
DSH180* | 15 | 6000 | 75 | 63 | 105 | 159.5 | 0.73 | 17.55
DSH180* | 15 | 6000 | 75 | 67 | 105 | 165 | 0.58 | 14.45
DSH180* | 15 | 6000 | 75 | 71 | 105 | 173.4 | 0.42 | 11.1
DSH180* | 15 | 6000 | 75 | 59 | 115 | 147.8 | 1 | 22.39
DSH180* | 15 | 6000 | 75 | 63 | 115 | 150.4 | 1 | 22.78
DSH180* | 15 | 6000 | 75 | 67 | 115 | 155.8 | 0.63 | 14.97
DSH180* | 15 | 6000 | 75 | 71 | 115 | 164.2 | 0.48 | 11.9
DSH180* | 15 | 6000 | 75 | 59 | 125 | 142.8 | 1 | 21.6
DSH180* | 15 | 6000 | 75 | 63 | 125 | 145.4 | 1 | 22
DSH180* | 15 | 6000 | 75 | 67 | 125 | 150.9 | 0.76 | 17.5
DSH180* | 15 | 6000 | 75 | 71 | 125 | 159.2 | 0.61 | 14.7
DSH180* | 15 | 6000 | 80 | 59 | 65 | 182.6 | 1 | 27.67
DSH180* | 15 | 6000 | 80 | 63 | 65 | 185.2 | 0.78 | 21.98
DSH180* | 15 | 6000 | 80 | 67 | 65 | 190.7 | 0.64 | 18.35
DSH180* | 15 | 6000 | 80 | 71 | 65 | 199 | 0.48 | 14.4
DSH180* | 15 | 6000 | 80 | 59 | 75 | 181 | 1 | 27.42
DSH180* | 15 | 6000 | 80 | 63 | 75 | 183.5 | 0.79 | 21.98
DSH180* | 15 | 6000 | 80 | 67 | 75 | 189 | 0.64 | 18.39
DSH180* | 15 | 6000 | 80 | 71 | 75 | 197.4 | 0.49 | 14.5
DSH180* | 15 | 6000 | 80 | 59 | 85 | 176.2 | 1 | 26.69
DSH180* | 15 | 6000 | 80 | 63 | 85 | 178.8 | 0.82 | 22.15
DSH180* | 15 | 6000 | 80 | 67 | 85 | 184.2 | 0.67 | 18.69
DSH180* | 15 | 6000 | 80 | 71 | 85 | 192.6 | 0.51 | 15
DSH180* | 15 | 6000 | 80 | 59 | 95 | 167.9 | 1 | 25.45
DSH180* | 15 | 6000 | 80 | 63 | 95 | 170.5 | 1 | 25.84
DSH180* | 15 | 6000 | 80 | 67 | 95 | 176 | 0.69 | 18.42
DSH180* | 15 | 6000 | 80 | 71 | 95 | 184.4 | 0.53 | 14.9
DSH180* | 15 | 6000 | 80 | 59 | 105 | 157.9 | 1 | 23.92
DSH180* | 15 | 6000 | 80 | 63 | 105 | 160.5 | 1 | 24.32
DSH180* | 15 | 6000 | 80 | 67 | 105 | 166 | 0.71 | 17.98
DSH180* | 15 | 6000 | 80 | 71 | 105 | 174.3 | 0.56 | 14.8
DSH180* | 15 | 6000 | 80 | 59 | 115 | 148.7 | 1 | 22.53
DSH180* | 15 | 6000 | 80 | 63 | 115 | 151.3 | 1 | 22.92
DSH180* | 15 | 6000 | 80 | 67 | 115 | 156.8 | 0.77 | 18.32
DSH180* | 15 | 6000 | 80 | 71 | 115 | 165.1 | 0.61 | 15.4
DSH180* | 15 | 6000 | 80 | 59 | 125 | 143.8 | 1 | 21.8
DSH180* | 15 | 6000 | 80 | 63 | 125 | 146.4 | 1 | 22.2
DSH180* | 15 | 6000 | 80 | 67 | 125 | 151.8 | 1 | 23
DSH180* | 15 | 6000 | 80 | 71 | 125 | 160.2 | 0.74 | 18.1
DSH180* | 15 | 6000 | 85 | 59 | 65 | 185.7 | 1 | 28.13
DSH180* | 15 | 6000 | 85 | 63 | 65 | 188.3 | 0.89 | 25.51
DSH180* | 15 | 6000 | 85 | 67 | 65 | 193.7 | 0.75 | 21.9
DSH180* | 15 | 6000 | 85 | 71 | 65 | 202.1 | 0.59 | 18.1
DSH180* | 15 | 6000 | 85 | 59 | 75 | 184 | 1 | 27.89
DSH180* | 15 | 6000 | 85 | 63 | 75 | 186.6 | 1 | 28.28
DSH180* | 15 | 6000 | 85 | 67 | 75 | 192.1 | 0.75 | 21.91
DSH180* | 15 | 6000 | 85 | 71 | 75 | 200.5 | 0.6 | 18.1
DSH180* | 15 | 6000 | 85 | 59 | 85 | 179.3 | 1 | 27.16
DSH180* | 15 | 6000 | 85 | 63 | 85 | 181.8 | 1 | 27.55
DSH180* | 15 | 6000 | 85 | 67 | 85 | 187.3 | 0.78 | 22.14
DSH180* | 15 | 6000 | 85 | 71 | 85 | 195.7 | 0.62 | 18.5
DSH180* | 15 | 6000 | 85 | 59 | 95 | 171 | 1 | 25.91
DSH180* | 15 | 6000 | 85 | 63 | 95 | 173.6 | 1 | 26.31
DSH180* | 15 | 6000 | 85 | 67 | 95 | 179.1 | 0.8 | 21.75
DSH180* | 15 | 6000 | 85 | 71 | 95 | 187.4 | 0.65 | 18.3
DSH180* | 15 | 6000 | 85 | 59 | 105 | 161 | 1 | 24.39
DSH180* | 15 | 6000 | 85 | 63 | 105 | 163.6 | 1 | 24.78
DSH180* | 15 | 6000 | 85 | 67 | 105 | 169 | 1 | 25.61
DSH180* | 15 | 6000 | 85 | 71 | 105 | 177.4 | 0.67 | 18
DSH180* | 15 | 6000 | 85 | 59 | 115 | 151.8 | 1 | 23
DSH180* | 15 | 6000 | 85 | 63 | 115 | 154.4 | 1 | 23.39
DSH180* | 15 | 6000 | 85 | 67 | 115 | 159.9 | 1 | 24.22
DSH180* | 15 | 6000 | 85 | 71 | 115 | 168.2 | 0.73 | 18.5
DSH180* | 15 | 6000 | 85 | 59 | 125 | 146.9 | 1 | 22.3
DSH180* | 15 | 6000 | 85 | 63 | 125 | 149.4 | 1 | 22.6
DSH180* | 15 | 6000 | 85 | 67 | 125 | 154.9 | 1 | 23.5
DSH180* | 15 | 6000 | 85 | 71 | 125 | 163.3 | 1 | 24.7
DSH180* | 15 | 6000 | 90 | 59 | 65 | 189.4 | 1 | 28.7
DSH180* | 15 | 6000 | 90 | 63 | 65 | 192 | 1 | 29.1
DSH180* | 15 | 6000 | 90 | 67 | 65 | 197.5 | 0.83 | 24.8
DSH180* | 15 | 6000 | 90 | 71 | 65 | 205.8 | 0.67 | 21
DSH180* | 15 | 6000 | 90 | 59 | 75 | 187.8 | 1 | 28.5
DSH180* | 15 | 6000 | 90 | 63 | 75 | 190.4 | 1 | 28.8
DSH180* | 15 | 6000 | 90 | 67 | 75 | 195.8 | 0.84 | 24.8
DSH180* | 15 | 6000 | 90 | 71 | 75 | 204.2 | 0.68 | 21
DSH180* | 15 | 6000 | 90 | 59 | 85 | 183 | 1 | 27.7
DSH180* | 15 | 6000 | 90 | 63 | 85 | 185.6 | 1 | 28.1
DSH180* | 15 | 6000 | 90 | 67 | 85 | 191.1 | 1 | 28.9
DSH180* | 15 | 6000 | 90 | 71 | 85 | 199.4 | 0.71 | 21.4
DSH180* | 15 | 6000 | 90 | 59 | 95 | 174.8 | 1 | 26.5
DSH180* | 15 | 6000 | 90 | 63 | 95 | 177.4 | 1 | 26.9
DSH180* | 15 | 6000 | 90 | 67 | 95 | 182.8 | 1 | 27.7
DSH180* | 15 | 6000 | 90 | 71 | 95 | 191.2 | 0.73 | 21.1
DSH180* | 15 | 6000 | 90 | 59 | 105 | 164.7 | 1 | 25
DSH180* | 15 | 6000 | 90 | 63 | 105 | 167.3 | 1 | 25.3
DSH180* | 15 | 6000 | 90 | 67 | 105 | 172.8 | 1 | 26.2
DSH180* | 15 | 6000 | 90 | 71 | 105 | 181.1 | 0.75 | 20.7
DSH180* | 15 | 6000 | 90 | 59 | 115 | 155.5 | 1 | 23.6
DSH180* | 15 | 6000 | 90 | 63 | 115 | 158.1 | 1 | 24
DSH180* | 15 | 6000 | 90 | 67 | 115 | 163.6 | 1 | 24.8
DSH180* | 15 | 6000 | 90 | 71 | 115 | 172 | 1 | 26.1
DSH180* | 15 | 6000 | 90 | 59 | 125 | 150.6 | 1 | 22.8
DSH180* | 15 | 6000 | 90 | 63 | 125 | 153.2 | 1 | 23.2
DSH180* | 15 | 6000 | 90 | 67 | 125 | 158.6 | 1 | 24
DSH180* | 15 | 6000 | 90 | 71 | 125 | 167 | 1 | 25.3
DSH180* | 15 | 6600 | 70 | 59 | 65 | 182.8 | 0.65 | 16.38
DSH180* | 15 | 6600 | 70 | 63 | 65 | 185.4 | 0.57 | 14.48
DSH180* | 15 | 6600 | 70 | 67 | 65 | 190.9 | 0.42 | 11.01
DSH180* | 15 | 6600 | 70 | 59 | 75 | 181.2 | 0.66 | 16.4
DSH180* | 15 | 6600 | 70 | 63 | 75 | 183.8 | 0.57 | 14.53
DSH180* | 15 | 6600 | 70 | 67 | 75 | 189.2 | 0.43 | 11.1
DSH180* | 15 | 6600 | 70 | 59 | 85 | 176.4 | 0.68 | 16.63
DSH180* | 15 | 6600 | 70 | 63 | 85 | 179 | 0.6 | 14.83
DSH180* | 15 | 6600 | 70 | 67 | 85 | 184.5 | 0.45 | 11.51
DSH180* | 15 | 6600 | 70 | 59 | 95 | 168.2 | 1 | 23.16
DSH180* | 15 | 6600 | 70 | 63 | 95 | 170.8 | 0.62 | 14.64
DSH180* | 15 | 6600 | 70 | 67 | 95 | 176.2 | 0.47 | 11.52
DSH180* | 15 | 6600 | 70 | 59 | 105 | 158.1 | 1 | 21.78
DSH180* | 15 | 6600 | 70 | 63 | 105 | 160.7 | 0.65 | 14.32
DSH180* | 15 | 6600 | 70 | 67 | 105 | 166.2 | 0.5 | 11.41
DSH180* | 15 | 6600 | 70 | 59 | 115 | 148.9 | 1 | 20.51
DSH180* | 15 | 6600 | 70 | 63 | 115 | 151.5 | 0.7 | 14.67
DSH180* | 15 | 6600 | 70 | 67 | 115 | 157 | 0.55 | 12
DSH180* | 15 | 6600 | 70 | 59 | 125 | 144 | 1 | 19.8
DSH180* | 15 | 6600 | 70 | 63 | 125 | 146.6 | 1 | 20.2
DSH180* | 15 | 6600 | 70 | 67 | 125 | 152 | 0.68 | 14.3
DSH180* | 15 | 6600 | 75 | 59 | 65 | 182.9 | 0.79 | 19.94
DSH180* | 15 | 6600 | 75 | 63 | 65 | 185.5 | 0.71 | 18.1
DSH180* | 15 | 6600 | 75 | 67 | 65 | 191 | 0.56 | 14.73
DSH180* | 15 | 6600 | 75 | 71 | 65 | 199.3 | 0.4 | 11.1
DSH180* | 15 | 6600 | 75 | 59 | 75 | 181.3 | 1 | 24.97
DSH180* | 15 | 6600 | 75 | 63 | 75 | 183.9 | 0.72 | 18.11
DSH180* | 15 | 6600 | 75 | 67 | 75 | 189.3 | 0.57 | 14.78
DSH180* | 15 | 6600 | 75 | 71 | 75 | 197.7 | 0.41 | 11.2
DSH180* | 15 | 6600 | 75 | 59 | 85 | 176.5 | 1 | 24.31
DSH180* | 15 | 6600 | 75 | 63 | 85 | 179.1 | 0.74 | 18.32
DSH180* | 15 | 6600 | 75 | 67 | 85 | 184.6 | 0.59 | 15.11
DSH180* | 15 | 6600 | 75 | 71 | 85 | 192.9 | 0.44 | 11.6
DSH180* | 15 | 6600 | 75 | 59 | 95 | 168.3 | 1 | 23.18
DSH180* | 15 | 6600 | 75 | 63 | 95 | 170.9 | 0.76 | 17.97
DSH180* | 15 | 6600 | 75 | 67 | 95 | 176.3 | 0.62 | 14.95
DSH180* | 15 | 6600 | 75 | 71 | 95 | 184.7 | 0.46 | 11.7
DSH180* | 15 | 6600 | 75 | 59 | 105 | 158.2 | 1 | 21.79
DSH180* | 15 | 6600 | 75 | 63 | 105 | 160.8 | 0.79 | 17.45
DSH180* | 15 | 6600 | 75 | 67 | 105 | 166.3 | 0.64 | 14.65
DSH180* | 15 | 6600 | 75 | 71 | 105 | 174.6 | 0.48 | 11.6
DSH180* | 15 | 6600 | 75 | 59 | 115 | 149 | 1 | 20.53
DSH180* | 15 | 6600 | 75 | 63 | 115 | 151.6 | 1 | 20.89
DSH180* | 15 | 6600 | 75 | 67 | 115 | 157.1 | 0.7 | 15.06
DSH180* | 15 | 6600 | 75 | 71 | 115 | 165.5 | 0.54 | 12.3
DSH180* | 15 | 6600 | 75 | 59 | 125 | 144.1 | 1 | 19.8
DSH180* | 15 | 6600 | 75 | 63 | 125 | 146.7 | 1 | 20.2
DSH180* | 15 | 6600 | 75 | 67 | 125 | 152.2 | 0.83 | 17.3
DSH180* | 15 | 6600 | 75 | 71 | 125 | 160.5 | 0.67 | 14.8
DSH180* | 15 | 6600 | 80 | 59 | 65 | 183.9 | 1 | 25.33
DSH180* | 15 | 6600 | 80 | 63 | 65 | 186.5 | 0.85 | 21.71
DSH180* | 15 | 6600 | 80 | 67 | 65 | 191.9 | 0.7 | 18.43
DSH180* | 15 | 6600 | 80 | 71 | 65 | 200.3 | 0.54 | 14.9
DSH180* | 15 | 6600 | 80 | 59 | 75 | 182.2 | 1 | 25.1
DSH180* | 15 | 6600 | 80 | 63 | 75 | 184.8 | 0.85 | 21.69
DSH180* | 15 | 6600 | 80 | 67 | 75 | 190.3 | 0.7 | 18.45
DSH180* | 15 | 6600 | 80 | 71 | 75 | 198.6 | 0.55 | 15
DSH180* | 15 | 6600 | 80 | 59 | 85 | 177.5 | 1 | 24.44
DSH180* | 15 | 6600 | 80 | 63 | 85 | 180 | 0.88 | 21.81
DSH180* | 15 | 6600 | 80 | 67 | 85 | 185.5 | 0.73 | 18.69
DSH180* | 15 | 6600 | 80 | 71 | 85 | 193.9 | 0.58 | 15.4
DSH180* | 15 | 6600 | 80 | 59 | 95 | 169.2 | 1 | 23.31
DSH180* | 15 | 6600 | 80 | 63 | 95 | 171.8 | 1 | 23.67
DSH180* | 15 | 6600 | 80 | 67 | 95 | 177.3 | 0.75 | 18.38
DSH180* | 15 | 6600 | 80 | 71 | 95 | 185.6 | 0.6 | 15.2
DSH180* | 15 | 6600 | 80 | 59 | 105 | 159.2 | 1 | 21.92
DSH180* | 15 | 6600 | 80 | 63 | 105 | 161.8 | 1 | 22.28
DSH180* | 15 | 6600 | 80 | 67 | 105 | 167.2 | 0.78 | 17.89
DSH180* | 15 | 6600 | 80 | 71 | 105 | 175.6 | 0.62 | 15
DSH180* | 15 | 6600 | 80 | 59 | 115 | 150 | 1 | 20.66
DSH180* | 15 | 6600 | 80 | 63 | 115 | 152.6 | 1 | 21.02
DSH180* | 15 | 6600 | 80 | 67 | 115 | 158 | 0.83 | 18.14
DSH180* | 15 | 6600 | 80 | 71 | 115 | 166.4 | 0.68 | 15.5
DSH180* | 15 | 6600 | 80 | 59 | 125 | 145 | 1 | 20
DSH180* | 15 | 6600 | 80 | 63 | 125 | 147.6 | 1 | 20.3
DSH180* | 15 | 6600 | 80 | 67 | 125 | 153.1 | 1 | 21.1
DSH180* | 15 | 6600 | 80 | 71 | 125 | 161.5 | 0.81 | 17.9
DSH180* | 15 | 6600 | 85 | 59 | 65 | 187 | 1 | 25.75
DSH180* | 15 | 6600 | 85 | 63 | 65 | 189.5 | 0.96 | 24.96
DSH180* | 15 | 6600 | 85 | 67 | 65 | 195 | 0.81 | 21.7
DSH180* | 15 | 6600 | 85 | 71 | 65 | 203.4 | 0.65 | 18.3
DSH180* | 15 | 6600 | 85 | 59 | 75 | 185.3 | 1 | 25.53
DSH180* | 15 | 6600 | 85 | 63 | 75 | 187.9 | 1 | 25.88
DSH180* | 15 | 6600 | 85 | 67 | 75 | 193.4 | 0.81 | 21.7
DSH180* | 15 | 6600 | 85 | 71 | 75 | 201.7 | 0.66 | 18.3
DSH180* | 15 | 6600 | 85 | 59 | 85 | 180.5 | 1 | 24.87
DSH180* | 15 | 6600 | 85 | 63 | 85 | 183.1 | 1 | 25.22
DSH180* | 15 | 6600 | 85 | 67 | 85 | 188.6 | 0.84 | 21.87
DSH180* | 15 | 6600 | 85 | 71 | 85 | 197 | 0.69 | 18.6
DSH180* | 15 | 6600 | 85 | 59 | 95 | 172.3 | 1 | 23.73
DSH180* | 15 | 6600 | 85 | 63 | 95 | 174.9 | 1 | 24.09
DSH180* | 15 | 6600 | 85 | 67 | 95 | 180.4 | 0.86 | 21.45
DSH180* | 15 | 6600 | 85 | 71 | 95 | 188.7 | 0.71 | 18.4
DSH180* | 15 | 6600 | 85 | 59 | 105 | 162.3 | 1 | 22.35
DSH180* | 15 | 6600 | 85 | 63 | 105 | 164.8 | 1 | 22.71
DSH180* | 15 | 6600 | 85 | 67 | 105 | 170.3 | 1 | 23.46
DSH180* | 15 | 6600 | 85 | 71 | 105 | 178.7 | 0.73 | 18
DSH180* | 15 | 6600 | 85 | 59 | 115 | 153.1 | 1 | 21.09
DSH180* | 15 | 6600 | 85 | 63 | 115 | 155.7 | 1 | 21.44
DSH180* | 15 | 6600 | 85 | 67 | 115 | 161.1 | 1 | 22.19
DSH180* | 15 | 6600 | 85 | 71 | 115 | 169.5 | 0.79 | 18.4
DSH180* | 15 | 6600 | 85 | 59 | 125 | 148.1 | 1 | 20.4
DSH180* | 15 | 6600 | 85 | 63 | 125 | 150.7 | 1 | 20.8
DSH180* | 15 | 6600 | 85 | 67 | 125 | 156.2 | 1 | 21.5
DSH180* | 15 | 6600 | 85 | 71 | 125 | 164.5 | 1 | 22.7
DSH180* | 15 | 6600 | 90 | 59 | 65 | 190.7 | 1 | 26.3
DSH180* | 15 | 6600 | 90 | 63 | 65 | 193.3 | 1 | 26.6
DSH180* | 15 | 6600 | 90 | 67 | 65 | 198.8 | 0.89 | 24.4
DSH180* | 15 | 6600 | 90 | 71 | 65 | 207.1 | 0.74 | 21
DSH180* | 15 | 6600 | 90 | 59 | 75 | 189.1 | 1 | 26
DSH180* | 15 | 6600 | 90 | 63 | 75 | 191.6 | 1 | 26.4
DSH180* | 15 | 6600 | 90 | 67 | 75 | 197.1 | 0.9 | 24.4
DSH180* | 15 | 6600 | 90 | 71 | 75 | 205.5 | 0.74 | 21
DSH180* | 15 | 6600 | 90 | 59 | 85 | 184.3 | 1 | 25.4
DSH180* | 15 | 6600 | 90 | 63 | 85 | 186.9 | 1 | 25.7
DSH180* | 15 | 6600 | 90 | 67 | 85 | 192.3 | 1 | 26.5
DSH180* | 15 | 6600 | 90 | 71 | 85 | 200.7 | 0.77 | 21.3
DSH180* | 15 | 6600 | 90 | 59 | 95 | 176 | 1 | 24.2
DSH180* | 15 | 6600 | 90 | 63 | 95 | 178.6 | 1 | 24.6
DSH180* | 15 | 6600 | 90 | 67 | 95 | 184.1 | 1 | 25.4
DSH180* | 15 | 6600 | 90 | 71 | 95 | 192.5 | 0.79 | 21
DSH180* | 15 | 6600 | 90 | 59 | 105 | 166 | 1 | 22.9
DSH180* | 15 | 6600 | 90 | 63 | 105 | 168.6 | 1 | 23.2
DSH180* | 15 | 6600 | 90 | 67 | 105 | 174 | 1 | 24
DSH180* | 15 | 6600 | 90 | 71 | 105 | 182.4 | 0.82 | 20.5
DSH180* | 15 | 6600 | 90 | 59 | 115 | 156.8 | 1 | 21.6
DSH180* | 15 | 6600 | 90 | 63 | 115 | 159.4 | 1 | 22
DSH180* | 15 | 6600 | 90 | 67 | 115 | 164.9 | 1 | 22.7
DSH180* | 15 | 6600 | 90 | 71 | 115 | 173.2 | 1 | 23.9
DSH180* | 15 | 6600 | 90 | 59 | 125 | 151.9 | 1 | 20.9
DSH180* | 15 | 6600 | 90 | 63 | 125 | 154.5 | 1 | 21.3
DSH180* | 15 | 6600 | 90 | 67 | 125 | 159.9 | 1 | 22
DSH180* | 15 | 6600 | 90 | 71 | 125 | 168.3 | 1 | 23.2
DSH180* | 15 | 7200 | 70 | 59 | 65 | 184.2 | 0.7 | 16.23
DSH180* | 15 | 7200 | 70 | 63 | 65 | 186.8 | 0.61 | 14.5
DSH180* | 15 | 7200 | 70 | 67 | 65 | 192.3 | 0.47 | 11.32
DSH180* | 15 | 7200 | 70 | 59 | 75 | 182.6 | 0.7 | 16.25
DSH180* | 15 | 7200 | 70 | 63 | 75 | 185.2 | 0.62 | 14.53
DSH180* | 15 | 7200 | 70 | 67 | 75 | 190.6 | 0.47 | 11.39
DSH180* | 15 | 7200 | 70 | 59 | 85 | 177.8 | 0.73 | 16.44
DSH180* | 15 | 7200 | 70 | 63 | 85 | 180.4 | 0.65 | 14.78
DSH180* | 15 | 7200 | 70 | 67 | 85 | 185.9 | 0.5 | 11.75
DSH180* | 15 | 7200 | 70 | 59 | 95 | 169.6 | 1 | 21.41
DSH180* | 15 | 7200 | 70 | 63 | 95 | 172.2 | 0.67 | 14.57
DSH180* | 15 | 7200 | 70 | 67 | 95 | 177.6 | 0.52 | 11.71
DSH180* | 15 | 7200 | 70 | 59 | 105 | 159.5 | 1 | 20.14
DSH180* | 15 | 7200 | 70 | 63 | 105 | 162.1 | 0.69 | 14.21
DSH180* | 15 | 7200 | 70 | 67 | 105 | 167.6 | 0.55 | 11.55
DSH180* | 15 | 7200 | 70 | 59 | 115 | 150.3 | 1 | 18.98
DSH180* | 15 | 7200 | 70 | 63 | 115 | 152.9 | 0.75 | 14.49
DSH180* | 15 | 7200 | 70 | 67 | 115 | 158.4 | 0.6 | 12.05
DSH180* | 15 | 7200 | 70 | 59 | 125 | 145.4 | 1 | 18.4
DSH180* | 15 | 7200 | 70 | 63 | 125 | 148 | 1 | 18.7
DSH180* | 15 | 7200 | 70 | 67 | 125 | 153.5 | 0.73 | 14.2
DSH180* | 15 | 7200 | 75 | 59 | 65 | 184.3 | 0.84 | 19.53
DSH180* | 15 | 7200 | 75 | 63 | 65 | 186.9 | 0.76 | 17.84
DSH180* | 15 | 7200 | 75 | 67 | 65 | 192.4 | 0.61 | 14.76
DSH180* | 15 | 7200 | 75 | 71 | 65 | 200.8 | 0.45 | 11.4
DSH180* | 15 | 7200 | 75 | 59 | 75 | 182.7 | 1 | 23.07
DSH180* | 15 | 7200 | 75 | 63 | 75 | 185.3 | 0.76 | 17.84
DSH180* | 15 | 7200 | 75 | 67 | 75 | 190.8 | 0.61 | 14.8
DSH180* | 15 | 7200 | 75 | 71 | 75 | 199.1 | 0.46 | 11.5
DSH180* | 15 | 7200 | 75 | 59 | 85 | 177.9 | 1 | 22.46
DSH180* | 15 | 7200 | 75 | 63 | 85 | 180.5 | 0.79 | 18
DSH180* | 15 | 7200 | 75 | 67 | 85 | 186 | 0.64 | 15.07
DSH180* | 15 | 7200 | 75 | 71 | 85 | 194.3 | 0.49 | 11.9
DSH180* | 15 | 7200 | 75 | 59 | 95 | 169.7 | 1 | 21.43
DSH180* | 15 | 7200 | 75 | 63 | 95 | 172.3 | 0.81 | 17.65
DSH180* | 15 | 7200 | 75 | 67 | 95 | 177.7 | 0.66 | 14.88
DSH180* | 15 | 7200 | 75 | 71 | 95 | 186.1 | 0.51 | 11.9
DSH180* | 15 | 7200 | 75 | 59 | 105 | 159.6 | 1 | 20.16
DSH180* | 15 | 7200 | 75 | 63 | 105 | 162.2 | 1 | 20.48
DSH180* | 15 | 7200 | 75 | 67 | 105 | 167.7 | 0.69 | 14.55
DSH180* | 15 | 7200 | 75 | 71 | 105 | 176 | 0.53 | 11.8
DSH180* | 15 | 7200 | 75 | 59 | 115 | 150.5 | 1 | 19
DSH180* | 15 | 7200 | 75 | 63 | 115 | 153 | 1 | 19.32
DSH180* | 15 | 7200 | 75 | 67 | 115 | 158.5 | 0.74 | 14.88
DSH180* | 15 | 7200 | 75 | 71 | 115 | 166.9 | 0.59 | 12.4
DSH180* | 15 | 7200 | 75 | 59 | 125 | 145.5 | 1 | 18.4
DSH180* | 15 | 7200 | 75 | 63 | 125 | 148.1 | 1 | 18.7
DSH180* | 15 | 7200 | 75 | 67 | 125 | 153.6 | 1 | 19.4
DSH180* | 15 | 7200 | 75 | 71 | 125 | 161.9 | 0.72 | 14.7
DSH180* | 15 | 7200 | 80 | 59 | 65 | 185.3 | 1 | 23.39
DSH180* | 15 | 7200 | 80 | 63 | 65 | 187.9 | 0.89 | 21.18
DSH180* | 15 | 7200 | 80 | 67 | 65 | 193.3 | 0.74 | 18.18
DSH180* | 15 | 7200 | 80 | 71 | 65 | 201.7 | 0.59 | 15
DSH180* | 15 | 7200 | 80 | 59 | 75 | 183.6 | 1 | 23.19
DSH180* | 15 | 7200 | 80 | 63 | 75 | 186.2 | 0.9 | 21.16
DSH180* | 15 | 7200 | 80 | 67 | 75 | 191.7 | 0.75 | 18.19
DSH180* | 15 | 7200 | 80 | 71 | 75 | 200.1 | 0.6 | 15
DSH180* | 15 | 7200 | 80 | 59 | 85 | 178.9 | 1 | 22.58
DSH180* | 15 | 7200 | 80 | 63 | 85 | 181.5 | 0.93 | 21.24
DSH180* | 15 | 7200 | 80 | 67 | 85 | 186.9 | 0.78 | 18.38
DSH180* | 15 | 7200 | 80 | 71 | 85 | 195.3 | 0.62 | 15.4
DSH180* | 15 | 7200 | 80 | 59 | 95 | 170.6 | 1 | 21.55
DSH180* | 15 | 7200 | 80 | 63 | 95 | 173.2 | 1 | 21.87
DSH180* | 15 | 7200 | 80 | 67 | 95 | 178.7 | 0.8 | 18.05
DSH180* | 15 | 7200 | 80 | 71 | 95 | 187.1 | 0.64 | 15.2
DSH180* | 15 | 7200 | 80 | 59 | 105 | 160.6 | 1 | 20.28
DSH180* | 15 | 7200 | 80 | 63 | 105 | 163.2 | 1 | 20.6
DSH180* | 15 | 7200 | 80 | 67 | 105 | 168.6 | 0.82 | 17.55
DSH180* | 15 | 7200 | 80 | 71 | 105 | 177 | 0.67 | 14.9
DSH180* | 15 | 7200 | 80 | 59 | 115 | 151.4 | 1 | 19.12
DSH180* | 15 | 7200 | 80 | 63 | 115 | 154 | 1 | 19.44
DSH180* | 15 | 7200 | 80 | 67 | 115 | 159.5 | 0.88 | 17.73
DSH180* | 15 | 7200 | 80 | 71 | 115 | 167.8 | 0.72 | 15.3
DSH180* | 15 | 7200 | 80 | 59 | 125 | 146.5 | 1 | 18.5
DSH180* | 15 | 7200 | 80 | 63 | 125 | 149 | 1 | 18.8
DSH180* | 15 | 7200 | 80 | 67 | 125 | 154.5 | 1 | 19.5
DSH180* | 15 | 7200 | 80 | 71 | 125 | 162.9 | 0.85 | 17.6
DSH180* | 15 | 7200 | 85 | 59 | 65 | 188.4 | 1 | 23.78
DSH180* | 15 | 7200 | 85 | 63 | 65 | 191 | 1 | 24.11
DSH180* | 15 | 7200 | 85 | 67 | 65 | 196.4 | 0.86 | 21.21
DSH180* | 15 | 7200 | 85 | 71 | 65 | 204.8 | 0.7 | 18.1
DSH180* | 15 | 7200 | 85 | 59 | 75 | 186.7 | 1 | 23.58
DSH180* | 15 | 7200 | 85 | 63 | 75 | 189.3 | 1 | 23.9
DSH180* | 15 | 7200 | 85 | 67 | 75 | 194.8 | 0.86 | 21.21
DSH180* | 15 | 7200 | 85 | 71 | 75 | 203.1 | 0.71 | 18.1
DSH180* | 15 | 7200 | 85 | 59 | 85 | 182 | 1 | 22.97
DSH180* | 15 | 7200 | 85 | 63 | 85 | 184.5 | 1 | 23.3
DSH180* | 15 | 7200 | 85 | 67 | 85 | 190 | 0.89 | 21.34
DSH180* | 15 | 7200 | 85 | 71 | 85 | 198.4 | 0.73 | 18.4
DSH180* | 15 | 7200 | 85 | 59 | 95 | 173.7 | 1 | 21.93
DSH180* | 15 | 7200 | 85 | 63 | 95 | 176.3 | 1 | 22.26
DSH180* | 15 | 7200 | 85 | 67 | 95 | 181.8 | 0.91 | 20.91
DSH180* | 15 | 7200 | 85 | 71 | 95 | 190.1 | 0.75 | 18.1
DSH180* | 15 | 7200 | 85 | 59 | 105 | 163.7 | 1 | 20.67
DSH180* | 15 | 7200 | 85 | 63 | 105 | 166.3 | 1 | 20.99
DSH180* | 15 | 7200 | 85 | 67 | 105 | 171.7 | 1 | 21.68
DSH180* | 15 | 7200 | 85 | 71 | 105 | 180.1 | 0.78 | 17.7
DSH180* | 15 | 7200 | 85 | 59 | 115 | 154.5 | 1 | 19.51
DSH180* | 15 | 7200 | 85 | 63 | 115 | 157.1 | 1 | 19.83
DSH180* | 15 | 7200 | 85 | 67 | 115 | 162.5 | 1 | 20.52
DSH180* | 15 | 7200 | 85 | 71 | 115 | 170.9 | 0.83 | 18
DSH180* | 15 | 7200 | 85 | 59 | 125 | 149.5 | 1 | 18.9
DSH180* | 15 | 7200 | 85 | 63 | 125 | 152.1 | 1 | 19.2
DSH180* | 15 | 7200 | 85 | 67 | 125 | 157.6 | 1 | 19.9
DSH180* | 15 | 7200 | 85 | 71 | 125 | 166 | 1 | 21
DSH180* | 15 | 7200 | 90 | 59 | 65 | 192.1 | 1 | 24.3
DSH180* | 15 | 7200 | 90 | 63 | 65 | 194.7 | 1 | 24.6
DSH180* | 15 | 7200 | 90 | 67 | 65 | 200.2 | 0.94 | 23.7
DSH180* | 15 | 7200 | 90 | 71 | 65 | 208.5 | 0.78 | 20.6
DSH180* | 15 | 7200 | 90 | 59 | 75 | 190.5 | 1 | 24
DSH180* | 15 | 7200 | 90 | 63 | 75 | 193.1 | 1 | 24.4
DSH180* | 15 | 7200 | 90 | 67 | 75 | 198.5 | 0.95 | 23.7
DSH180* | 15 | 7200 | 90 | 71 | 75 | 206.9 | 0.79 | 20.6
DSH180* | 15 | 7200 | 90 | 59 | 85 | 185.7 | 1 | 23.4
DSH180* | 15 | 7200 | 90 | 63 | 85 | 188.3 | 1 | 23.8
DSH180* | 15 | 7200 | 90 | 67 | 85 | 193.7 | 1 | 24.5
DSH180* | 15 | 7200 | 90 | 71 | 85 | 202.1 | 0.82 | 20.9
DSH180* | 15 | 7200 | 90 | 59 | 95 | 177.5 | 1 | 22.4
DSH180* | 15 | 7200 | 90 | 63 | 95 | 180 | 1 | 22.7
DSH180* | 15 | 7200 | 90 | 67 | 95 | 185.5 | 1 | 23.4
DSH180* | 15 | 7200 | 90 | 71 | 95 | 193.9 | 0.84 | 20.5
DSH180* | 15 | 7200 | 90 | 59 | 105 | 167.4 | 1 | 21.1
DSH180* | 15 | 7200 | 90 | 63 | 105 | 170 | 1 | 21.5
DSH180* | 15 | 7200 | 90 | 67 | 105 | 175.5 | 1 | 22.2
DSH180* | 15 | 7200 | 90 | 71 | 105 | 183.8 | 0.86 | 20
DSH180* | 15 | 7200 | 90 | 59 | 115 | 158.2 | 1 | 20
DSH180* | 15 | 7200 | 90 | 63 | 115 | 160.8 | 1 | 20.3
DSH180* | 15 | 7200 | 90 | 67 | 115 | 166.3 | 1 | 21
DSH180* | 15 | 7200 | 90 | 71 | 115 | 174.6 | 1 | 22.1
DSH180* | 15 | 7200 | 90 | 59 | 125 | 153.3 | 1 | 19.4
DSH180* | 15 | 7200 | 90 | 63 | 125 | 155.9 | 1 | 19.7
DSH180* | 15 | 7200 | 90 | 67 | 125 | 161.3 | 1 | 20.4
DSH180* | 15 | 7200 | 90 | 71 | 125 | 169.7 | 1 | 21.4
DSH180* | 15 | 7400 | 70 | 59 | 65 | 184.7 | 0.71 | 16.13
DSH180* | 15 | 7400 | 70 | 63 | 65 | 187.3 | 0.63 | 14.44
DSH180* | 15 | 7400 | 70 | 67 | 65 | 192.8 | 0.48 | 11.36
DSH180* | 15 | 7400 | 70 | 59 | 75 | 183.1 | 0.72 | 16.14
DSH180* | 15 | 7400 | 70 | 63 | 75 | 185.7 | 0.63 | 14.47
DSH180* | 15 | 7400 | 70 | 67 | 75 | 191.2 | 0.49 | 11.42
DSH180* | 15 | 7400 | 70 | 59 | 85 | 178.3 | 0.75 | 16.32
DSH180* | 15 | 7400 | 70 | 63 | 85 | 180.9 | 0.66 | 14.71
DSH180* | 15 | 7400 | 70 | 67 | 85 | 186.4 | 0.51 | 11.76
DSH180* | 15 | 7400 | 70 | 59 | 95 | 170.1 | 1 | 20.9
DSH180* | 15 | 7400 | 70 | 63 | 95 | 172.7 | 0.68 | 14.49
DSH180* | 15 | 7400 | 70 | 67 | 95 | 178.1 | 0.53 | 11.71
DSH180* | 15 | 7400 | 70 | 59 | 105 | 160 | 1 | 19.66
DSH180* | 15 | 7400 | 70 | 63 | 105 | 162.6 | 0.71 | 14.13
DSH180* | 15 | 7400 | 70 | 67 | 105 | 168.1 | 0.56 | 11.55
DSH180* | 15 | 7400 | 70 | 59 | 115 | 150.9 | 1 | 18.53
DSH180* | 15 | 7400 | 70 | 63 | 115 | 153.4 | 0.76 | 14.39
DSH180* | 15 | 7400 | 70 | 67 | 115 | 158.9 | 0.62 | 12.01
DSH180* | 15 | 7400 | 70 | 59 | 125 | 145.9 | 1 | 17.9
DSH180* | 15 | 7400 | 70 | 63 | 125 | 148.5 | 1 | 18.2
DSH180* | 15 | 7400 | 70 | 67 | 125 | 154 | 0.74 | 14.1
DSH180* | 15 | 7400 | 75 | 59 | 65 | 184.8 | 0.85 | 19.35
DSH180* | 15 | 7400 | 75 | 63 | 65 | 187.4 | 0.77 | 17.7
DSH180* | 15 | 7400 | 75 | 67 | 65 | 192.9 | 0.62 | 14.71
DSH180* | 15 | 7400 | 75 | 71 | 65 | 201.3 | 0.46 | 11.5
DSH180* | 15 | 7400 | 75 | 59 | 75 | 183.2 | 1 | 22.51
DSH180* | 15 | 7400 | 75 | 63 | 75 | 185.8 | 0.78 | 17.7
DSH180* | 15 | 7400 | 75 | 67 | 75 | 191.3 | 0.63 | 14.74
DSH180* | 15 | 7400 | 75 | 71 | 75 | 199.6 | 0.47 | 11.6
DSH180* | 15 | 7400 | 75 | 59 | 85 | 178.4 | 1 | 21.92
DSH180* | 15 | 7400 | 75 | 63 | 85 | 181 | 0.8 | 17.86
DSH180* | 15 | 7400 | 75 | 67 | 85 | 186.5 | 0.65 | 15
DSH180* | 15 | 7400 | 75 | 71 | 85 | 194.8 | 0.5 | 11.9
DSH180* | 15 | 7400 | 75 | 59 | 95 | 170.2 | 1 | 20.91
DSH180* | 15 | 7400 | 75 | 63 | 95 | 172.8 | 0.82 | 17.5
DSH180* | 15 | 7400 | 75 | 67 | 95 | 178.3 | 0.68 | 14.8
DSH180* | 15 | 7400 | 75 | 71 | 95 | 186.6 | 0.52 | 11.9
DSH180* | 15 | 7400 | 75 | 59 | 105 | 160.1 | 1 | 19.67
DSH180* | 15 | 7400 | 75 | 63 | 105 | 162.7 | 1 | 19.99
DSH180* | 15 | 7400 | 75 | 67 | 105 | 168.2 | 0.7 | 14.47
DSH180* | 15 | 7400 | 75 | 71 | 105 | 176.6 | 0.54 | 11.8
DSH180* | 15 | 7400 | 75 | 59 | 115 | 151 | 1 | 18.55
DSH180* | 15 | 7400 | 75 | 63 | 115 | 153.5 | 1 | 18.86
DSH180* | 15 | 7400 | 75 | 67 | 115 | 159 | 0.76 | 14.78
DSH180* | 15 | 7400 | 75 | 71 | 115 | 167.4 | 0.6 | 12.3
DSH180* | 15 | 7400 | 75 | 59 | 125 | 146 | 1 | 17.9
DSH180* | 15 | 7400 | 75 | 63 | 125 | 148.6 | 1 | 18.3
DSH180* | 15 | 7400 | 75 | 67 | 125 | 154.1 | 1 | 18.9
DSH180* | 15 | 7400 | 75 | 71 | 125 | 162.4 | 0.73 | 14.6
DSH180* | 15 | 7400 | 80 | 59 | 65 | 185.8 | 1 | 22.82
DSH180* | 15 | 7400 | 80 | 63 | 65 | 188.4 | 0.91 | 20.96
DSH180* | 15 | 7400 | 80 | 67 | 65 | 193.9 | 0.76 | 18.04
DSH180* | 15 | 7400 | 80 | 71 | 65 | 202.2 | 0.6 | 14.9
DSH180* | 15 | 7400 | 80 | 59 | 75 | 184.2 | 1 | 22.62
DSH180* | 15 | 7400 | 80 | 63 | 75 | 186.7 | 0.91 | 20.94
DSH180* | 15 | 7400 | 80 | 67 | 75 | 192.2 | 0.76 | 18.05
DSH180* | 15 | 7400 | 80 | 71 | 75 | 200.6 | 0.61 | 15
DSH180* | 15 | 7400 | 80 | 59 | 85 | 179.4 | 1 | 22.04
DSH180* | 15 | 7400 | 80 | 63 | 85 | 182 | 0.94 | 21.01
DSH180* | 15 | 7400 | 80 | 67 | 85 | 187.4 | 0.79 | 18.23
DSH180* | 15 | 7400 | 80 | 71 | 85 | 195.8 | 0.64 | 15.3
DSH180* | 15 | 7400 | 80 | 59 | 95 | 171.1 | 1 | 21.03
DSH180* | 15 | 7400 | 80 | 63 | 95 | 173.7 | 1 | 21.34
DSH180* | 15 | 7400 | 80 | 67 | 95 | 179.2 | 0.81 | 17.9
DSH180* | 15 | 7400 | 80 | 71 | 95 | 187.6 | 0.66 | 15.1
DSH180* | 15 | 7400 | 80 | 59 | 105 | 161.1 | 1 | 19.79
DSH180* | 15 | 7400 | 80 | 63 | 105 | 163.7 | 1 | 20.11
DSH180* | 15 | 7400 | 80 | 67 | 105 | 169.1 | 0.84 | 17.4
DSH180* | 15 | 7400 | 80 | 71 | 105 | 177.5 | 0.68 | 14.9
DSH180* | 15 | 7400 | 80 | 59 | 115 | 151.9 | 1 | 18.66
DSH180* | 15 | 7400 | 80 | 63 | 115 | 154.5 | 1 | 18.98
DSH180* | 15 | 7400 | 80 | 67 | 115 | 160 | 0.89 | 17.56
DSH180* | 15 | 7400 | 80 | 71 | 115 | 168.3 | 0.74 | 15.2
DSH180* | 15 | 7400 | 80 | 59 | 125 | 147 | 1 | 18.1
DSH180* | 15 | 7400 | 80 | 63 | 125 | 149.5 | 1 | 18.4
DSH180* | 15 | 7400 | 80 | 67 | 125 | 155 | 1 | 19
DSH180* | 15 | 7400 | 80 | 71 | 125 | 163.4 | 0.87 | 17.4
DSH180* | 15 | 7400 | 85 | 59 | 65 | 188.9 | 1 | 23.2
DSH180* | 15 | 7400 | 85 | 63 | 65 | 191.5 | 1 | 23.52
DSH180* | 15 | 7400 | 85 | 67 | 65 | 196.9 | 0.87 | 21.01
DSH180* | 15 | 7400 | 85 | 71 | 65 | 205.3 | 0.71 | 18
DSH180* | 15 | 7400 | 85 | 59 | 75 | 187.2 | 1 | 23
DSH180* | 15 | 7400 | 85 | 63 | 75 | 189.8 | 1 | 23.32
DSH180* | 15 | 7400 | 85 | 67 | 75 | 195.3 | 0.88 | 21
DSH180* | 15 | 7400 | 85 | 71 | 75 | 203.7 | 0.72 | 18
DSH180* | 15 | 7400 | 85 | 59 | 85 | 182.5 | 1 | 22.42
DSH180* | 15 | 7400 | 85 | 63 | 85 | 185 | 1 | 22.73
DSH180* | 15 | 7400 | 85 | 67 | 85 | 190.5 | 0.9 | 21.13
DSH180* | 15 | 7400 | 85 | 71 | 85 | 198.9 | 0.75 | 18.2
DSH180* | 15 | 7400 | 85 | 59 | 95 | 174.2 | 1 | 21.4
DSH180* | 15 | 7400 | 85 | 63 | 95 | 176.8 | 1 | 21.72
DSH180* | 15 | 7400 | 85 | 67 | 95 | 182.3 | 0.92 | 20.69
DSH180* | 15 | 7400 | 85 | 71 | 95 | 190.6 | 0.77 | 18
DSH180* | 15 | 7400 | 85 | 59 | 105 | 164.2 | 1 | 20.17
DSH180* | 15 | 7400 | 85 | 63 | 105 | 166.8 | 1 | 20.49
DSH180* | 15 | 7400 | 85 | 67 | 105 | 172.2 | 1 | 21.16
DSH180* | 15 | 7400 | 85 | 71 | 105 | 180.6 | 0.79 | 17.6
DSH180* | 15 | 7400 | 85 | 59 | 115 | 155 | 1 | 19.04
DSH180* | 15 | 7400 | 85 | 63 | 115 | 157.6 | 1 | 19.36
DSH180* | 15 | 7400 | 85 | 67 | 115 | 163.1 | 1 | 20.03
DSH180* | 15 | 7400 | 85 | 71 | 115 | 171.4 | 0.85 | 17.9
DSH180* | 15 | 7400 | 85 | 59 | 125 | 150 | 1 | 18.4
DSH180* | 15 | 7400 | 85 | 63 | 125 | 152.6 | 1 | 18.8
DSH180* | 15 | 7400 | 85 | 67 | 125 | 158.1 | 1 | 19.4
DSH180* | 15 | 7400 | 85 | 71 | 125 | 166.5 | 1 | 20.4
DSH180* | 15 | 7400 | 90 | 59 | 65 | 192.6 | 1 | 23.7
DSH180* | 15 | 7400 | 90 | 63 | 65 | 195.2 | 1 | 24
DSH180* | 15 | 7400 | 90 | 67 | 65 | 200.7 | 0.95 | 23.5
DSH180* | 15 | 7400 | 90 | 71 | 65 | 209 | 0.8 | 20.4
DSH180* | 15 | 7400 | 90 | 59 | 75 | 191 | 1 | 23.5
DSH180* | 15 | 7400 | 90 | 63 | 75 | 193.6 | 1 | 23.8
DSH180* | 15 | 7400 | 90 | 67 | 75 | 199 | 0.96 | 23.4
DSH180* | 15 | 7400 | 90 | 71 | 75 | 207.4 | 0.8 | 20.5
DSH180* | 15 | 7400 | 90 | 59 | 85 | 186.2 | 1 | 22.9
DSH180* | 15 | 7400 | 90 | 63 | 85 | 188.8 | 1 | 23.2
DSH180* | 15 | 7400 | 90 | 67 | 85 | 194.3 | 1 | 23.9
DSH180* | 15 | 7400 | 90 | 71 | 85 | 202.6 | 0.83 | 20.7
DSH180* | 15 | 7400 | 90 | 59 | 95 | 178 | 1 | 21.9
DSH180* | 15 | 7400 | 90 | 63 | 95 | 180.6 | 1 | 22.2
DSH180* | 15 | 7400 | 90 | 67 | 95 | 186 | 1 | 22.9
DSH180* | 15 | 7400 | 90 | 71 | 95 | 194.4 | 0.85 | 20.3
DSH180* | 15 | 7400 | 90 | 59 | 105 | 167.9 | 1 | 20.6
DSH180* | 15 | 7400 | 90 | 63 | 105 | 170.5 | 1 | 20.9
DSH180* | 15 | 7400 | 90 | 67 | 105 | 176 | 1 | 21.6
DSH180* | 15 | 7400 | 90 | 71 | 105 | 184.3 | 0.88 | 19.8
DSH180* | 15 | 7400 | 90 | 59 | 115 | 158.7 | 1 | 19.5
DSH180* | 15 | 7400 | 90 | 63 | 115 | 161.3 | 1 | 19.8
DSH180* | 15 | 7400 | 90 | 67 | 115 | 166.8 | 1 | 20.5
DSH180* | 15 | 7400 | 90 | 71 | 115 | 175.1 | 1 | 21.5
DSH180* | 15 | 7400 | 90 | 59 | 125 | 153.8 | 1 | 18.9
DSH180* | 15 | 7400 | 90 | 63 | 125 | 156.4 | 1 | 19.2
DSH180* | 15 | 7400 | 90 | 67 | 125 | 161.8 | 1 | 19.9
DSH180* | 15 | 7400 | 90 | 71 | 125 | 170.2 | 1 | 20.9
DSH180* | 15 | 7700 | 70 | 59 | 65 | 185.5 | 0.73 | 15.95
DSH180* | 15 | 7700 | 70 | 63 | 65 | 188.1 | 0.64 | 14.32
DSH180* | 15 | 7700 | 70 | 67 | 65 | 193.6 | 0.5 | 11.35
DSH180* | 15 | 7700 | 70 | 59 | 75 | 183.9 | 0.73 | 15.95
DSH180* | 15 | 7700 | 70 | 63 | 75 | 186.5 | 0.65 | 14.35
DSH180* | 15 | 7700 | 70 | 67 | 75 | 192 | 0.5 | 11.41
DSH180* | 15 | 7700 | 70 | 59 | 85 | 179.1 | 1 | 21.15
DSH180* | 15 | 7700 | 70 | 63 | 85 | 181.7 | 0.68 | 14.57
DSH180* | 15 | 7700 | 70 | 67 | 85 | 187.2 | 0.53 | 11.73
DSH180* | 15 | 7700 | 70 | 59 | 95 | 170.9 | 1 | 20.18
DSH180* | 15 | 7700 | 70 | 63 | 95 | 173.5 | 0.7 | 14.34
DSH180* | 15 | 7700 | 70 | 67 | 95 | 178.9 | 0.55 | 11.66
DSH180* | 15 | 7700 | 70 | 59 | 105 | 160.8 | 1 | 18.99
DSH180* | 15 | 7700 | 70 | 63 | 105 | 163.4 | 0.72 | 13.98
DSH180* | 15 | 7700 | 70 | 67 | 105 | 168.9 | 0.58 | 11.49
DSH180* | 15 | 7700 | 70 | 59 | 115 | 151.7 | 1 | 17.9
DSH180* | 15 | 7700 | 70 | 63 | 115 | 154.2 | 0.78 | 14.22
DSH180* | 15 | 7700 | 70 | 67 | 115 | 159.7 | 0.63 | 11.93
DSH180* | 15 | 7700 | 70 | 59 | 125 | 146.7 | 1 | 17.3
DSH180* | 15 | 7700 | 70 | 63 | 125 | 149.3 | 1 | 17.6
DSH180* | 15 | 7700 | 70 | 67 | 125 | 154.8 | 0.76 | 13.9
DSH180* | 15 | 7700 | 75 | 59 | 65 | 185.6 | 0.87 | 19.05
DSH180* | 15 | 7700 | 75 | 63 | 65 | 188.2 | 0.79 | 17.47
DSH180* | 15 | 7700 | 75 | 67 | 65 | 193.7 | 0.64 | 14.58
DSH180* | 15 | 7700 | 75 | 71 | 65 | 202.1 | 0.48 | 11.5
DSH180* | 15 | 7700 | 75 | 59 | 75 | 184 | 1 | 21.72
DSH180* | 15 | 7700 | 75 | 63 | 75 | 186.6 | 0.79 | 17.46
DSH180* | 15 | 7700 | 75 | 67 | 75 | 192.1 | 0.64 | 14.61
DSH180* | 15 | 7700 | 75 | 71 | 75 | 200.4 | 0.49 | 11.6
DSH180* | 15 | 7700 | 75 | 59 | 85 | 179.2 | 1 | 21.16
DSH180* | 15 | 7700 | 75 | 63 | 85 | 181.8 | 0.82 | 17.6
DSH180* | 15 | 7700 | 75 | 67 | 85 | 187.3 | 0.67 | 14.86
DSH180* | 15 | 7700 | 75 | 71 | 85 | 195.6 | 0.52 | 11.9
DSH180* | 15 | 7700 | 75 | 59 | 95 | 171 | 1 | 20.19
DSH180* | 15 | 7700 | 75 | 63 | 95 | 173.6 | 0.84 | 17.24
DSH180* | 15 | 7700 | 75 | 67 | 95 | 179.1 | 0.69 | 14.65
DSH180* | 15 | 7700 | 75 | 71 | 95 | 187.4 | 0.54 | 11.9
DSH180* | 15 | 7700 | 75 | 59 | 105 | 160.9 | 1 | 19
DSH180* | 15 | 7700 | 75 | 63 | 105 | 163.5 | 1 | 19.31
DSH180* | 15 | 7700 | 75 | 67 | 105 | 169 | 0.72 | 14.31
DSH180* | 15 | 7700 | 75 | 71 | 105 | 177.4 | 0.56 | 11.7
DSH180* | 15 | 7700 | 75 | 59 | 115 | 151.8 | 1 | 17.92
DSH180* | 15 | 7700 | 75 | 63 | 115 | 154.3 | 1 | 18.22
DSH180* | 15 | 7700 | 75 | 67 | 115 | 159.8 | 0.77 | 14.6
DSH180* | 15 | 7700 | 75 | 71 | 115 | 168.2 | 0.62 | 12.3
DSH180* | 15 | 7700 | 75 | 59 | 125 | 146.8 | 1 | 17.3
DSH180* | 15 | 7700 | 75 | 63 | 125 | 149.4 | 1 | 17.6
DSH180* | 15 | 7700 | 75 | 67 | 125 | 154.9 | 1 | 18.3
DSH180* | 15 | 7700 | 75 | 71 | 125 | 163.2 | 0.75 | 14.4
DSH180* | 15 | 7700 | 80 | 59 | 65 | 186.6 | 1 | 22.03
DSH180* | 15 | 7700 | 80 | 63 | 65 | 189.2 | 0.92 | 20.62
DSH180* | 15 | 7700 | 80 | 67 | 65 | 194.6 | 0.77 | 17.81
DSH180* | 15 | 7700 | 80 | 71 | 65 | 203 | 0.62 | 14.8
DSH180* | 15 | 7700 | 80 | 59 | 75 | 185 | 1 | 21.84
DSH180* | 15 | 7700 | 80 | 63 | 75 | 187.5 | 0.93 | 20.59
DSH180* | 15 | 7700 | 80 | 67 | 75 | 193 | 0.78 | 17.81
DSH180* | 15 | 7700 | 80 | 71 | 75 | 201.4 | 0.63 | 14.9
DSH180* | 15 | 7700 | 80 | 59 | 85 | 180.2 | 1 | 21.27
DSH180* | 15 | 7700 | 80 | 63 | 85 | 182.8 | 1 | 21.58
DSH180* | 15 | 7700 | 80 | 67 | 85 | 188.2 | 0.81 | 17.98
DSH180* | 15 | 7700 | 80 | 71 | 85 | 196.6 | 0.65 | 15.1
DSH180* | 15 | 7700 | 80 | 59 | 95 | 171.9 | 1 | 20.3
DSH180* | 15 | 7700 | 80 | 63 | 95 | 174.5 | 1 | 20.61
DSH180* | 15 | 7700 | 80 | 67 | 95 | 180 | 0.83 | 17.64
DSH180* | 15 | 7700 | 80 | 71 | 95 | 188.4 | 0.67 | 15
DSH180* | 15 | 7700 | 80 | 59 | 105 | 161.9 | 1 | 19.11
DSH180* | 15 | 7700 | 80 | 63 | 105 | 164.5 | 1 | 19.42
DSH180* | 15 | 7700 | 80 | 67 | 105 | 169.9 | 0.85 | 17.14
DSH180* | 15 | 7700 | 80 | 71 | 105 | 178.3 | 0.7 | 14.7
DSH180* | 15 | 7700 | 80 | 59 | 115 | 152.7 | 1 | 18.03
DSH180* | 15 | 7700 | 80 | 63 | 115 | 155.3 | 1 | 18.33
DSH180* | 15 | 7700 | 80 | 67 | 115 | 160.8 | 1 | 18.98
DSH180* | 15 | 7700 | 80 | 71 | 115 | 169.1 | 0.75 | 15.1
DSH180* | 15 | 7700 | 80 | 59 | 125 | 147.8 | 1 | 17.4
DSH180* | 15 | 7700 | 80 | 63 | 125 | 150.3 | 1 | 17.8
DSH180* | 15 | 7700 | 80 | 67 | 125 | 155.8 | 1 | 18.4
DSH180* | 15 | 7700 | 80 | 71 | 125 | 164.2 | 0.88 | 17.1
DSH180* | 15 | 7700 | 85 | 59 | 65 | 189.7 | 1 | 22.39
DSH180* | 15 | 7700 | 85 | 63 | 65 | 192.3 | 1 | 22.7
DSH180* | 15 | 7700 | 85 | 67 | 65 | 197.7 | 0.89 | 20.67
DSH180* | 15 | 7700 | 85 | 71 | 65 | 206.1 | 0.73 | 17.7
DSH180* | 15 | 7700 | 85 | 59 | 75 | 188 | 1 | 22.2
DSH180* | 15 | 7700 | 85 | 63 | 75 | 190.6 | 1 | 22.51
DSH180* | 15 | 7700 | 85 | 67 | 75 | 196.1 | 0.89 | 20.66
DSH180* | 15 | 7700 | 85 | 71 | 75 | 204.5 | 0.74 | 17.8
DSH180* | 15 | 7700 | 85 | 59 | 85 | 183.3 | 1 | 21.64
DSH180* | 15 | 7700 | 85 | 63 | 85 | 185.8 | 1 | 21.94
DSH180* | 15 | 7700 | 85 | 67 | 85 | 191.3 | 0.92 | 20.77
DSH180* | 15 | 7700 | 85 | 71 | 85 | 199.7 | 0.76 | 18
DSH180* | 15 | 7700 | 85 | 59 | 95 | 175 | 1 | 20.66
DSH180* | 15 | 7700 | 85 | 63 | 95 | 177.6 | 1 | 20.97
DSH180* | 15 | 7700 | 85 | 67 | 95 | 183.1 | 0.94 | 20.34
DSH180* | 15 | 7700 | 85 | 71 | 95 | 191.4 | 0.78 | 17.7
DSH180* | 15 | 7700 | 85 | 59 | 105 | 165 | 1 | 19.48
DSH180* | 15 | 7700 | 85 | 63 | 105 | 167.6 | 1 | 19.78
DSH180* | 15 | 7700 | 85 | 67 | 105 | 173 | 1 | 20.43
DSH180* | 15 | 7700 | 85 | 71 | 105 | 181.4 | 0.81 | 17.3
DSH180* | 15 | 7700 | 85 | 59 | 115 | 155.8 | 1 | 18.39
DSH180* | 15 | 7700 | 85 | 63 | 115 | 158.4 | 1 | 18.7
DSH180* | 15 | 7700 | 85 | 67 | 115 | 163.9 | 1 | 19.34
DSH180* | 15 | 7700 | 85 | 71 | 115 | 172.2 | 0.87 | 17.6
DSH180* | 15 | 7700 | 85 | 59 | 125 | 150.8 | 1 | 17.8
DSH180* | 15 | 7700 | 85 | 63 | 125 | 153.4 | 1 | 18.1
DSH180* | 15 | 7700 | 85 | 67 | 125 | 158.9 | 1 | 18.8
DSH180* | 15 | 7700 | 85 | 71 | 125 | 167.3 | 1 | 19.7
DSH180* | 15 | 7700 | 90 | 59 | 65 | 193.4 | 1 | 22.8
DSH180* | 15 | 7700 | 90 | 63 | 65 | 196 | 1 | 23.1
DSH180* | 15 | 7700 | 90 | 67 | 65 | 201.5 | 0.97 | 23.1
DSH180* | 15 | 7700 | 90 | 71 | 65 | 209.8 | 0.81 | 20.1
DSH180* | 15 | 7700 | 90 | 59 | 75 | 191.8 | 1 | 22.6
DSH180* | 15 | 7700 | 90 | 63 | 75 | 194.4 | 1 | 22.9
DSH180* | 15 | 7700 | 90 | 67 | 75 | 199.8 | 0.98 | 23
DSH180* | 15 | 7700 | 90 | 71 | 75 | 208.2 | 0.82 | 20.2
DSH180* | 15 | 7700 | 90 | 59 | 85 | 187 | 1 | 22.1
DSH180* | 15 | 7700 | 90 | 63 | 85 | 189.6 | 1 | 22.4
DSH180* | 15 | 7700 | 90 | 67 | 85 | 195 | 1 | 23
DSH180* | 15 | 7700 | 90 | 71 | 85 | 203.4 | 0.85 | 20.3
DSH180* | 15 | 7700 | 90 | 59 | 95 | 178.8 | 1 | 21.1
DSH180* | 15 | 7700 | 90 | 63 | 95 | 181.4 | 1 | 21.4
DSH180* | 15 | 7700 | 90 | 67 | 95 | 186.8 | 1 | 22.1
DSH180* | 15 | 7700 | 90 | 71 | 95 | 195.2 | 0.87 | 20
DSH180* | 15 | 7700 | 90 | 59 | 105 | 168.7 | 1 | 19.9
DSH180* | 15 | 7700 | 90 | 63 | 105 | 171.3 | 1 | 20.2
DSH180* | 15 | 7700 | 90 | 67 | 105 | 176.8 | 1 | 20.9
DSH180* | 15 | 7700 | 90 | 71 | 105 | 185.1 | 0.89 | 19.5
DSH180* | 15 | 7700 | 90 | 59 | 115 | 159.5 | 1 | 18.8
DSH180* | 15 | 7700 | 90 | 63 | 115 | 162.1 | 1 | 19.1
DSH180* | 15 | 7700 | 90 | 67 | 115 | 167.6 | 1 | 19.8
DSH180* | 15 | 7700 | 90 | 71 | 115 | 175.9 | 1 | 20.8
DSH180* | 15 | 7700 | 90 | 59 | 125 | 154.6 | 1 | 18.3
DSH180* | 15 | 7700 | 90 | 63 | 125 | 157.2 | 1 | 18.6
DSH180* | 15 | 7700 | 90 | 67 | 125 | 162.6 | 1 | 19.2
DSH180* | 15 | 7700 | 90 | 71 | 125 | 171 | 1 | 20.2
DSH240* | 20 | 6000 | 70 | 59 | 65 | 229.5 | 0.58 | 20.08
DSH240* | 20 | 6000 | 70 | 63 | 65 | 232.8 | 0.5 | 17.76
DSH240* | 20 | 6000 | 70 | 67 | 65 | 239.7 | 0.37 | 13.5
DSH240* | 20 | 6000 | 70 | 59 | 75 | 227.5 | 0.58 | 20.11
DSH240* | 20 | 6000 | 70 | 63 | 75 | 230.7 | 0.51 | 17.81
DSH240* | 20 | 6000 | 70 | 67 | 75 | 237.6 | 0.38 | 13.6
DSH240* | 20 | 6000 | 70 | 59 | 85 | 221.5 | 0.61 | 20.39
DSH240* | 20 | 6000 | 70 | 63 | 85 | 224.7 | 0.53 | 18.18
DSH240* | 20 | 6000 | 70 | 67 | 85 | 231.6 | 0.4 | 14.11
DSH240* | 20 | 6000 | 70 | 59 | 95 | 211.1 | 0.63 | 20.04
DSH240* | 20 | 6000 | 70 | 63 | 95 | 214.4 | 0.55 | 17.95
DSH240* | 20 | 6000 | 70 | 67 | 95 | 221.3 | 0.42 | 14.12
DSH240* | 20 | 6000 | 70 | 59 | 105 | 198.5 | 1 | 30.08
DSH240* | 20 | 6000 | 70 | 63 | 105 | 201.8 | 0.57 | 17.55
DSH240* | 20 | 6000 | 70 | 67 | 105 | 208.6 | 0.44 | 13.99
DSH240* | 20 | 6000 | 70 | 59 | 115 | 187 | 1 | 28.33
DSH240* | 20 | 6000 | 70 | 63 | 115 | 190.2 | 0.62 | 17.99
DSH240* | 20 | 6000 | 70 | 67 | 115 | 197.1 | 0.49 | 14.71
DSH240* | 20 | 6000 | 70 | 59 | 125 | 180.8 | 1 | 27.4
DSH240* | 20 | 6000 | 70 | 63 | 125 | 184 | 0.74 | 20.6
DSH240* | 20 | 6000 | 70 | 67 | 125 | 190.9 | 0.61 | 17.6
DSH240* | 20 | 6000 | 75 | 59 | 65 | 229.7 | 0.7 | 24.45
DSH240* | 20 | 6000 | 75 | 63 | 65 | 232.9 | 0.63 | 22.19
DSH240* | 20 | 6000 | 75 | 67 | 65 | 239.8 | 0.5 | 18.06
DSH240* | 20 | 6000 | 75 | 71 | 65 | 250.3 | 0.36 | 13.6
DSH240* | 20 | 6000 | 75 | 59 | 75 | 227.6 | 0.71 | 24.44
DSH240* | 20 | 6000 | 75 | 63 | 75 | 230.9 | 0.63 | 22.2
DSH240* | 20 | 6000 | 75 | 67 | 75 | 237.7 | 0.5 | 18.12
DSH240* | 20 | 6000 | 75 | 71 | 75 | 248.2 | 0.36 | 13.7
DSH240* | 20 | 6000 | 75 | 59 | 85 | 221.6 | 1 | 33.58
DSH240* | 20 | 6000 | 75 | 63 | 85 | 224.9 | 0.66 | 22.45
DSH240* | 20 | 6000 | 75 | 67 | 85 | 231.7 | 0.53 | 18.52
DSH240* | 20 | 6000 | 75 | 71 | 85 | 242.2 | 0.39 | 14.3
DSH240* | 20 | 6000 | 75 | 59 | 95 | 211.3 | 1 | 32.01
DSH240* | 20 | 6000 | 75 | 63 | 95 | 214.5 | 0.68 | 22.04
DSH240* | 20 | 6000 | 75 | 67 | 95 | 221.4 | 0.55 | 18.33
DSH240* | 20 | 6000 | 75 | 71 | 95 | 231.9 | 0.41 | 14.3
DSH240* | 20 | 6000 | 75 | 59 | 105 | 198.7 | 1 | 30.1
DSH240* | 20 | 6000 | 75 | 63 | 105 | 201.9 | 0.7 | 21.4
DSH240* | 20 | 6000 | 75 | 67 | 105 | 208.8 | 0.57 | 17.96
DSH240* | 20 | 6000 | 75 | 71 | 105 | 219.3 | 0.43 | 14.3
DSH240* | 20 | 6000 | 75 | 59 | 115 | 187.1 | 1 | 28.35
DSH240* | 20 | 6000 | 75 | 63 | 115 | 190.4 | 0.75 | 21.61
DSH240* | 20 | 6000 | 75 | 67 | 115 | 197.2 | 0.62 | 18.46
DSH240* | 20 | 6000 | 75 | 71 | 115 | 207.7 | 0.48 | 15.1
DSH240* | 20 | 6000 | 75 | 59 | 125 | 180.9 | 1 | 27.4
DSH240* | 20 | 6000 | 75 | 63 | 125 | 184.2 | 1 | 27.9
DSH240* | 20 | 6000 | 75 | 67 | 125 | 191 | 0.73 | 21.2
DSH240* | 20 | 6000 | 75 | 71 | 125 | 201.5 | 0.59 | 18.1
DSH240* | 20 | 6000 | 80 | 59 | 65 | 230.9 | 0.82 | 28.83
DSH240* | 20 | 6000 | 80 | 63 | 65 | 234.1 | 0.75 | 26.62
DSH240* | 20 | 6000 | 80 | 67 | 65 | 241 | 0.62 | 22.59
DSH240* | 20 | 6000 | 80 | 71 | 65 | 251.5 | 0.48 | 18.3
DSH240* | 20 | 6000 | 80 | 59 | 75 | 228.8 | 1 | 34.67
DSH240* | 20 | 6000 | 80 | 63 | 75 | 232.1 | 0.76 | 26.6
DSH240* | 20 | 6000 | 80 | 67 | 75 | 238.9 | 0.62 | 22.62
DSH240* | 20 | 6000 | 80 | 71 | 75 | 249.4 | 0.49 | 18.4
DSH240* | 20 | 6000 | 80 | 59 | 85 | 222.8 | 1 | 33.76
DSH240* | 20 | 6000 | 80 | 63 | 85 | 226 | 0.78 | 26.74
DSH240* | 20 | 6000 | 80 | 67 | 85 | 232.9 | 0.65 | 22.91
DSH240* | 20 | 6000 | 80 | 71 | 85 | 243.4 | 0.51 | 18.8
DSH240* | 20 | 6000 | 80 | 59 | 95 | 212.5 | 1 | 32.19
DSH240* | 20 | 6000 | 80 | 63 | 95 | 215.7 | 0.8 | 26.14
DSH240* | 20 | 6000 | 80 | 67 | 95 | 222.6 | 0.67 | 22.53
DSH240* | 20 | 6000 | 80 | 71 | 95 | 233.1 | 0.53 | 18.7
DSH240* | 20 | 6000 | 80 | 59 | 105 | 199.8 | 1 | 30.28
DSH240* | 20 | 6000 | 80 | 63 | 105 | 203.1 | 1 | 30.77
DSH240* | 20 | 6000 | 80 | 67 | 105 | 210 | 0.69 | 21.94
DSH240* | 20 | 6000 | 80 | 71 | 105 | 220.5 | 0.55 | 18.4
DSH240* | 20 | 6000 | 80 | 59 | 115 | 188.3 | 1 | 28.53
DSH240* | 20 | 6000 | 80 | 63 | 115 | 191.6 | 1 | 29.03
DSH240* | 20 | 6000 | 80 | 67 | 115 | 198.4 | 0.74 | 22.23
DSH240* | 20 | 6000 | 80 | 71 | 115 | 208.9 | 0.6 | 19
DSH240* | 20 | 6000 | 80 | 59 | 125 | 182.1 | 1 | 27.6
DSH240* | 20 | 6000 | 80 | 63 | 125 | 185.4 | 1 | 28.1
DSH240* | 20 | 6000 | 80 | 67 | 125 | 192.2 | 0.85 | 24.9
DSH240* | 20 | 6000 | 80 | 71 | 125 | 202.7 | 0.72 | 22
DSH240* | 20 | 6000 | 85 | 59 | 65 | 234.7 | 1 | 35.57
DSH240* | 20 | 6000 | 85 | 63 | 65 | 238 | 0.85 | 30.6
DSH240* | 20 | 6000 | 85 | 67 | 65 | 244.9 | 0.72 | 26.6
DSH240* | 20 | 6000 | 85 | 71 | 65 | 255.3 | 0.58 | 22.4
DSH240* | 20 | 6000 | 85 | 59 | 75 | 232.7 | 1 | 35.25
DSH240* | 20 | 6000 | 85 | 63 | 75 | 235.9 | 0.85 | 30.55
DSH240* | 20 | 6000 | 85 | 67 | 75 | 242.8 | 0.72 | 26.6
DSH240* | 20 | 6000 | 85 | 71 | 75 | 253.3 | 0.58 | 22.4
DSH240* | 20 | 6000 | 85 | 59 | 85 | 226.7 | 1 | 34.34
DSH240* | 20 | 6000 | 85 | 63 | 85 | 229.9 | 1 | 34.84
DSH240* | 20 | 6000 | 85 | 67 | 85 | 236.8 | 0.75 | 26.82
DSH240* | 20 | 6000 | 85 | 71 | 85 | 247.3 | 0.61 | 22.8
DSH240* | 20 | 6000 | 85 | 59 | 95 | 216.3 | 1 | 32.78
DSH240* | 20 | 6000 | 85 | 63 | 95 | 219.6 | 1 | 33.27
DSH240* | 20 | 6000 | 85 | 67 | 95 | 226.5 | 0.77 | 26.3
DSH240* | 20 | 6000 | 85 | 71 | 95 | 237 | 0.63 | 22.5
DSH240* | 20 | 6000 | 85 | 59 | 105 | 203.7 | 1 | 30.87
DSH240* | 20 | 6000 | 85 | 63 | 105 | 207 | 1 | 31.36
DSH240* | 20 | 6000 | 85 | 67 | 105 | 213.8 | 0.79 | 25.52
DSH240* | 20 | 6000 | 85 | 71 | 105 | 224.3 | 0.65 | 22.1
DSH240* | 20 | 6000 | 85 | 59 | 115 | 192.2 | 1 | 29.12
DSH240* | 20 | 6000 | 85 | 63 | 115 | 195.4 | 1 | 29.61
DSH240* | 20 | 6000 | 85 | 67 | 115 | 202.3 | 0.84 | 25.68
DSH240* | 20 | 6000 | 85 | 71 | 115 | 212.8 | 0.7 | 22.5
DSH240* | 20 | 6000 | 85 | 59 | 125 | 186 | 1 | 28.2
DSH240* | 20 | 6000 | 85 | 63 | 125 | 189.2 | 1 | 28.7
DSH240* | 20 | 6000 | 85 | 67 | 125 | 196.1 | 1 | 29.7
DSH240* | 20 | 6000 | 85 | 71 | 125 | 206.6 | 0.81 | 25.5
DSH240* | 20 | 6000 | 90 | 59 | 65 | 230.9 | 0.82 | 28.83
DSH240* | 20 | 6000 | 90 | 63 | 65 | 234.1 | 0.75 | 26.62
DSH240* | 20 | 6000 | 90 | 67 | 65 | 241 | 0.62 | 22.59
DSH240* | 20 | 6000 | 90 | 71 | 65 | 251.5 | 0.48 | 18.3
DSH240* | 20 | 6000 | 90 | 59 | 75 | 228.8 | 1 | 34.67
DSH240* | 20 | 6000 | 90 | 63 | 75 | 232.1 | 0.76 | 26.6
DSH240* | 20 | 6000 | 90 | 67 | 75 | 238.9 | 0.62 | 22.62
DSH240* | 20 | 6000 | 90 | 71 | 75 | 249.4 | 0.49 | 18.4
DSH240* | 20 | 6000 | 90 | 59 | 85 | 222.8 | 1 | 33.76
DSH240* | 20 | 6000 | 90 | 63 | 85 | 226 | 0.78 | 26.74
DSH240* | 20 | 6000 | 90 | 67 | 85 | 232.9 | 0.65 | 22.91
DSH240* | 20 | 6000 | 90 | 71 | 85 | 243.4 | 0.51 | 18.8
DSH240* | 20 | 6000 | 90 | 59 | 95 | 212.5 | 1 | 32.19
DSH240* | 20 | 6000 | 90 | 63 | 95 | 215.7 | 0.8 | 26.14
DSH240* | 20 | 6000 | 90 | 67 | 95 | 222.6 | 0.67 | 22.53
DSH240* | 20 | 6000 | 90 | 71 | 95 | 233.1 | 0.53 | 18.7
DSH240* | 20 | 6000 | 90 | 59 | 105 | 199.8 | 1 | 30.28
DSH240* | 20 | 6000 | 90 | 63 | 105 | 203.1 | 1 | 30.77
DSH240* | 20 | 6000 | 90 | 67 | 105 | 210 | 0.69 | 21.94
DSH240* | 20 | 6000 | 90 | 71 | 105 | 220.5 | 0.55 | 18.4
DSH240* | 20 | 6000 | 90 | 59 | 115 | 188.3 | 1 | 28.53
DSH240* | 20 | 6000 | 90 | 63 | 115 | 191.6 | 1 | 29.03
DSH240* | 20 | 6000 | 90 | 67 | 115 | 198.4 | 0.74 | 22.23
DSH240* | 20 | 6000 | 90 | 71 | 115 | 208.9 | 0.6 | 19
DSH240* | 20 | 6000 | 90 | 59 | 125 | 190.7 | 1 | 28.9
DSH240* | 20 | 6000 | 90 | 63 | 125 | 193.9 | 1 | 29.4
DSH240* | 20 | 6000 | 90 | 67 | 125 | 200.8 | 1 | 30.4
DSH240* | 20 | 6000 | 90 | 71 | 125 | 211.3 | 1 | 32
DSH240* | 20 | 6500 | 70 | 59 | 65 | 231.2 | 0.62 | 19.93
DSH240* | 20 | 6500 | 70 | 63 | 65 | 234.4 | 0.54 | 17.79
DSH240* | 20 | 6500 | 70 | 67 | 65 | 241.3 | 0.41 | 13.87
DSH240* | 20 | 6500 | 70 | 59 | 75 | 229.1 | 0.62 | 19.94
DSH240* | 20 | 6500 | 70 | 63 | 75 | 232.3 | 0.55 | 17.83
DSH240* | 20 | 6500 | 70 | 67 | 75 | 239.2 | 0.42 | 13.95
DSH240* | 20 | 6500 | 70 | 59 | 85 | 223.1 | 0.65 | 20.18
DSH240* | 20 | 6500 | 70 | 63 | 85 | 226.3 | 0.57 | 18.14
DSH240* | 20 | 6500 | 70 | 67 | 85 | 233.2 | 0.44 | 14.39
DSH240* | 20 | 6500 | 70 | 59 | 95 | 212.8 | 0.67 | 19.81
DSH240* | 20 | 6500 | 70 | 63 | 95 | 216 | 0.59 | 17.88
DSH240* | 20 | 6500 | 70 | 67 | 95 | 222.9 | 0.46 | 14.35
DSH240* | 20 | 6500 | 70 | 59 | 105 | 200.1 | 1 | 27.99
DSH240* | 20 | 6500 | 70 | 63 | 105 | 203.4 | 0.61 | 17.44
DSH240* | 20 | 6500 | 70 | 67 | 105 | 210.3 | 0.48 | 14.16
DSH240* | 20 | 6500 | 70 | 59 | 115 | 188.6 | 1 | 26.38
DSH240* | 20 | 6500 | 70 | 63 | 115 | 191.9 | 0.66 | 17.79
DSH240* | 20 | 6500 | 70 | 67 | 115 | 198.7 | 0.53 | 14.78
DSH240* | 20 | 6500 | 70 | 59 | 125 | 182.4 | 1 | 25.5
DSH240* | 20 | 6500 | 70 | 63 | 125 | 185.6 | 0.78 | 20.2
DSH240* | 20 | 6500 | 70 | 67 | 125 | 192.5 | 0.65 | 17.4
DSH240* | 20 | 6500 | 75 | 59 | 65 | 231.3 | 0.74 | 23.99
DSH240* | 20 | 6500 | 75 | 63 | 65 | 234.5 | 0.67 | 21.91
DSH240* | 20 | 6500 | 75 | 67 | 65 | 241.4 | 0.54 | 18.1
DSH240* | 20 | 6500 | 75 | 71 | 65 | 251.9 | 0.4 | 14
DSH240* | 20 | 6500 | 75 | 59 | 75 | 229.2 | 0.75 | 23.97
DSH240* | 20 | 6500 | 75 | 63 | 75 | 232.5 | 0.67 | 21.91
DSH240* | 20 | 6500 | 75 | 67 | 75 | 239.3 | 0.54 | 18.15
DSH240* | 20 | 6500 | 75 | 71 | 75 | 249.8 | 0.4 | 14.1
DSH240* | 20 | 6500 | 75 | 59 | 85 | 223.2 | 1 | 31.22
DSH240* | 20 | 6500 | 75 | 63 | 85 | 226.5 | 0.7 | 22.11
DSH240* | 20 | 6500 | 75 | 67 | 85 | 233.3 | 0.57 | 18.49
DSH240* | 20 | 6500 | 75 | 71 | 85 | 243.8 | 0.43 | 14.6
DSH240* | 20 | 6500 | 75 | 59 | 95 | 212.9 | 1 | 29.78
DSH240* | 20 | 6500 | 75 | 63 | 95 | 216.1 | 0.72 | 21.68
DSH240* | 20 | 6500 | 75 | 67 | 95 | 223 | 0.59 | 18.26
DSH240* | 20 | 6500 | 75 | 71 | 95 | 233.5 | 0.45 | 14.6
DSH240* | 20 | 6500 | 75 | 59 | 105 | 200.3 | 1 | 28.01
DSH240* | 20 | 6500 | 75 | 63 | 105 | 203.5 | 0.74 | 21.02
DSH240* | 20 | 6500 | 75 | 67 | 105 | 210.4 | 0.61 | 17.86
DSH240* | 20 | 6500 | 75 | 71 | 105 | 220.9 | 0.47 | 14.5
DSH240* | 20 | 6500 | 75 | 59 | 115 | 188.8 | 1 | 26.4
DSH240* | 20 | 6500 | 75 | 63 | 115 | 192 | 0.79 | 21.17
DSH240* | 20 | 6500 | 75 | 67 | 115 | 198.9 | 0.66 | 18.27
DSH240* | 20 | 6500 | 75 | 71 | 115 | 209.4 | 0.52 | 15.2
DSH240* | 20 | 6500 | 75 | 59 | 125 | 182.5 | 1 | 25.5
DSH240* | 20 | 6500 | 75 | 63 | 125 | 185.8 | 1 | 26
DSH240* | 20 | 6500 | 75 | 67 | 125 | 192.7 | 0.77 | 20.8
DSH240* | 20 | 6500 | 75 | 71 | 125 | 203.1 | 0.63 | 18
DSH240* | 20 | 6500 | 80 | 59 | 65 | 232.5 | 0.86 | 28.07
DSH240* | 20 | 6500 | 80 | 63 | 65 | 235.7 | 0.79 | 26.03
DSH240* | 20 | 6500 | 80 | 67 | 65 | 242.6 | 0.66 | 22.32
DSH240* | 20 | 6500 | 80 | 71 | 65 | 253.1 | 0.52 | 18.4
DSH240* | 20 | 6500 | 80 | 59 | 75 | 230.4 | 1 | 32.23
DSH240* | 20 | 6500 | 80 | 63 | 75 | 233.7 | 0.8 | 26
DSH240* | 20 | 6500 | 80 | 67 | 75 | 240.5 | 0.66 | 22.34
DSH240* | 20 | 6500 | 80 | 71 | 75 | 251 | 0.53 | 18.4
DSH240* | 20 | 6500 | 80 | 59 | 85 | 224.4 | 1 | 31.39
DSH240* | 20 | 6500 | 80 | 63 | 85 | 227.7 | 0.82 | 26.1
DSH240* | 20 | 6500 | 80 | 67 | 85 | 234.5 | 0.69 | 22.58
DSH240* | 20 | 6500 | 80 | 71 | 85 | 245 | 0.55 | 18.8
DSH240* | 20 | 6500 | 80 | 59 | 95 | 214.1 | 1 | 29.94
DSH240* | 20 | 6500 | 80 | 63 | 95 | 217.3 | 0.84 | 25.49
DSH240* | 20 | 6500 | 80 | 67 | 95 | 224.2 | 0.71 | 22.17
DSH240* | 20 | 6500 | 80 | 71 | 95 | 234.7 | 0.57 | 18.7
DSH240* | 20 | 6500 | 80 | 59 | 105 | 201.5 | 1 | 28.18
DSH240* | 20 | 6500 | 80 | 63 | 105 | 204.7 | 1 | 28.63
DSH240* | 20 | 6500 | 80 | 67 | 105 | 211.6 | 0.73 | 21.56
DSH240* | 20 | 6500 | 80 | 71 | 105 | 222.1 | 0.59 | 18.3
DSH240* | 20 | 6500 | 80 | 59 | 115 | 189.9 | 1 | 26.57
DSH240* | 20 | 6500 | 80 | 63 | 115 | 193.2 | 1 | 27.02
DSH240* | 20 | 6500 | 80 | 67 | 115 | 200.1 | 0.78 | 21.78
DSH240* | 20 | 6500 | 80 | 71 | 115 | 210.5 | 0.64 | 18.8
DSH240* | 20 | 6500 | 80 | 59 | 125 | 183.7 | 1 | 25.7
DSH240* | 20 | 6500 | 80 | 63 | 125 | 187 | 1 | 26.2
DSH240* | 20 | 6500 | 80 | 67 | 125 | 193.8 | 0.89 | 24.2
DSH240* | 20 | 6500 | 80 | 71 | 125 | 204.3 | 0.75 | 21.6
DSH240* | 20 | 6500 | 85 | 59 | 65 | 236.4 | 1 | 33.06
DSH240* | 20 | 6500 | 85 | 63 | 65 | 239.6 | 0.89 | 29.75
DSH240* | 20 | 6500 | 85 | 67 | 65 | 246.5 | 0.76 | 26.07
DSH240* | 20 | 6500 | 85 | 71 | 65 | 257 | 0.62 | 22.2
DSH240* | 20 | 6500 | 85 | 59 | 75 | 234.3 | 1 | 32.77
DSH240* | 20 | 6500 | 85 | 63 | 75 | 237.5 | 0.89 | 29.7
DSH240* | 20 | 6500 | 85 | 67 | 75 | 244.4 | 0.76 | 26.06
DSH240* | 20 | 6500 | 85 | 71 | 75 | 254.9 | 0.62 | 22.2
DSH240* | 20 | 6500 | 85 | 59 | 85 | 228.3 | 1 | 31.93
DSH240* | 20 | 6500 | 85 | 63 | 85 | 231.5 | 1 | 32.38
DSH240* | 20 | 6500 | 85 | 67 | 85 | 238.4 | 0.79 | 26.23
DSH240* | 20 | 6500 | 85 | 71 | 85 | 248.9 | 0.65 | 22.6
DSH240* | 20 | 6500 | 85 | 59 | 95 | 218 | 1 | 30.48
DSH240* | 20 | 6500 | 85 | 63 | 95 | 221.2 | 1 | 30.94
DSH240* | 20 | 6500 | 85 | 67 | 95 | 228.1 | 0.81 | 25.69
DSH240* | 20 | 6500 | 85 | 71 | 95 | 238.6 | 0.67 | 22.2
DSH240* | 20 | 6500 | 85 | 59 | 105 | 205.3 | 1 | 28.72
DSH240* | 20 | 6500 | 85 | 63 | 105 | 208.6 | 1 | 29.17
DSH240* | 20 | 6500 | 85 | 67 | 105 | 215.5 | 0.83 | 24.92
DSH240* | 20 | 6500 | 85 | 71 | 105 | 225.9 | 0.69 | 21.7
DSH240* | 20 | 6500 | 85 | 59 | 115 | 193.8 | 1 | 27.11
DSH240* | 20 | 6500 | 85 | 63 | 115 | 197.1 | 1 | 27.56
DSH240* | 20 | 6500 | 85 | 67 | 115 | 203.9 | 1 | 28.52
DSH240* | 20 | 6500 | 85 | 71 | 115 | 214.4 | 0.74 | 22.1
DSH240* | 20 | 6500 | 85 | 59 | 125 | 187.6 | 1 | 26.2
DSH240* | 20 | 6500 | 85 | 63 | 125 | 190.8 | 1 | 26.7
DSH240* | 20 | 6500 | 85 | 67 | 125 | 197.7 | 1 | 27.7
DSH240* | 20 | 6500 | 85 | 71 | 125 | 208.2 | 0.85 | 24.8
DSH240* | 20 | 6500 | 90 | 59 | 65 | 232.5 | 0.86 | 28.07
DSH240* | 20 | 6500 | 90 | 63 | 65 | 235.7 | 0.79 | 26.03
DSH240* | 20 | 6500 | 90 | 67 | 65 | 242.6 | 0.66 | 22.32
DSH240* | 20 | 6500 | 90 | 71 | 65 | 253.1 | 0.52 | 18.4
DSH240* | 20 | 6500 | 90 | 59 | 75 | 230.4 | 1 | 32.23
DSH240* | 20 | 6500 | 90 | 63 | 75 | 233.7 | 0.8 | 26
DSH240* | 20 | 6500 | 90 | 67 | 75 | 240.5 | 0.66 | 22.34
DSH240* | 20 | 6500 | 90 | 71 | 75 | 251 | 0.53 | 18.4
DSH240* | 20 | 6500 | 90 | 59 | 85 | 224.4 | 1 | 31.39
DSH240* | 20 | 6500 | 90 | 63 | 85 | 227.7 | 0.82 | 26.1
DSH240* | 20 | 6500 | 90 | 67 | 85 | 234.5 | 0.69 | 22.58
DSH240* | 20 | 6500 | 90 | 71 | 85 | 245 | 0.55 | 18.8
DSH240* | 20 | 6500 | 90 | 59 | 95 | 214.1 | 1 | 29.94
DSH240* | 20 | 6500 | 90 | 63 | 95 | 217.3 | 0.84 | 25.49
DSH240* | 20 | 6500 | 90 | 67 | 95 | 224.2 | 0.71 | 22.17
DSH240* | 20 | 6500 | 90 | 71 | 95 | 234.7 | 0.57 | 18.7
DSH240* | 20 | 6500 | 90 | 59 | 105 | 201.5 | 1 | 28.18
DSH240* | 20 | 6500 | 90 | 63 | 105 | 204.7 | 1 | 28.63
DSH240* | 20 | 6500 | 90 | 67 | 105 | 211.6 | 0.73 | 21.56
DSH240* | 20 | 6500 | 90 | 71 | 105 | 222.1 | 0.59 | 18.3
DSH240* | 20 | 6500 | 90 | 59 | 115 | 189.9 | 1 | 26.57
DSH240* | 20 | 6500 | 90 | 63 | 115 | 193.2 | 1 | 27.02
DSH240* | 20 | 6500 | 90 | 67 | 115 | 200.1 | 0.78 | 21.78
DSH240* | 20 | 6500 | 90 | 71 | 115 | 210.5 | 0.64 | 18.8
DSH240* | 20 | 6500 | 90 | 59 | 125 | 192.3 | 1 | 26.9
DSH240* | 20 | 6500 | 90 | 63 | 125 | 195.5 | 1 | 27.3
DSH240* | 20 | 6500 | 90 | 67 | 125 | 202.4 | 1 | 28.3
DSH240* | 20 | 6500 | 90 | 71 | 125 | 212.9 | 1 | 29.8
DSH240* | 20 | 7000 | 70 | 59 | 65 | 232.9 | 0.65 | 19.55
DSH240* | 20 | 7000 | 70 | 63 | 65 | 236.2 | 0.57 | 17.56
DSH240* | 20 | 7000 | 70 | 67 | 65 | 243.1 | 0.44 | 13.91
DSH240* | 20 | 7000 | 70 | 59 | 75 | 230.9 | 0.65 | 19.56
DSH240* | 20 | 7000 | 70 | 63 | 75 | 234.1 | 0.58 | 17.59
DSH240* | 20 | 7000 | 70 | 67 | 75 | 241 | 0.45 | 13.99
DSH240* | 20 | 7000 | 70 | 59 | 85 | 224.9 | 0.68 | 19.76
DSH240* | 20 | 7000 | 70 | 63 | 85 | 228.1 | 0.6 | 17.86
DSH240* | 20 | 7000 | 70 | 67 | 85 | 235 | 0.47 | 14.38
DSH240* | 20 | 7000 | 70 | 59 | 95 | 214.6 | 0.7 | 19.38
DSH240* | 20 | 7000 | 70 | 63 | 95 | 217.8 | 0.62 | 17.58
DSH240* | 20 | 7000 | 70 | 67 | 95 | 224.7 | 0.49 | 14.3
DSH240* | 20 | 7000 | 70 | 59 | 105 | 201.9 | 1 | 26.23
DSH240* | 20 | 7000 | 70 | 63 | 105 | 205.2 | 0.64 | 17.14
DSH240* | 20 | 7000 | 70 | 67 | 105 | 212 | 0.51 | 14.09
DSH240* | 20 | 7000 | 70 | 59 | 115 | 190.4 | 1 | 24.73
DSH240* | 20 | 7000 | 70 | 63 | 115 | 193.7 | 0.69 | 17.43
DSH240* | 20 | 7000 | 70 | 67 | 115 | 200.5 | 0.56 | 14.62
DSH240* | 20 | 7000 | 70 | 59 | 125 | 184.2 | 1 | 23.9
DSH240* | 20 | 7000 | 70 | 63 | 125 | 187.4 | 1 | 24.3
DSH240* | 20 | 7000 | 70 | 67 | 125 | 194.3 | 0.68 | 17.1
DSH240* | 20 | 7000 | 75 | 59 | 65 | 233.1 | 0.77 | 23.35
DSH240* | 20 | 7000 | 75 | 63 | 65 | 236.3 | 0.7 | 21.41
DSH240* | 20 | 7000 | 75 | 67 | 65 | 243.2 | 0.57 | 17.88
DSH240* | 20 | 7000 | 75 | 71 | 65 | 253.7 | 0.43 | 14.1
DSH240* | 20 | 7000 | 75 | 59 | 75 | 231 | 0.78 | 23.33
DSH240* | 20 | 7000 | 75 | 63 | 75 | 234.3 | 0.7 | 21.41
DSH240* | 20 | 7000 | 75 | 67 | 75 | 241.1 | 0.57 | 17.92
DSH240* | 20 | 7000 | 75 | 71 | 75 | 251.6 | 0.43 | 14.2
DSH240* | 20 | 7000 | 75 | 59 | 85 | 225 | 1 | 29.22
DSH240* | 20 | 7000 | 75 | 63 | 85 | 228.3 | 0.73 | 21.58
DSH240* | 20 | 7000 | 75 | 67 | 85 | 235.1 | 0.6 | 18.21
DSH240* | 20 | 7000 | 75 | 71 | 85 | 245.6 | 0.46 | 14.6
DSH240* | 20 | 7000 | 75 | 59 | 95 | 214.7 | 1 | 27.88
DSH240* | 20 | 7000 | 75 | 63 | 95 | 217.9 | 0.75 | 21.14
DSH240* | 20 | 7000 | 75 | 67 | 95 | 224.8 | 0.62 | 17.96
DSH240* | 20 | 7000 | 75 | 71 | 95 | 235.3 | 0.48 | 14.6
DSH240* | 20 | 7000 | 75 | 59 | 105 | 202.1 | 1 | 26.24
DSH240* | 20 | 7000 | 75 | 63 | 105 | 205.3 | 0.77 | 20.49
DSH240* | 20 | 7000 | 75 | 67 | 105 | 212.2 | 0.64 | 17.55
DSH240* | 20 | 7000 | 75 | 71 | 105 | 222.7 | 0.5 | 14.4
DSH240* | 20 | 7000 | 75 | 59 | 115 | 190.5 | 1 | 24.75
DSH240* | 20 | 7000 | 75 | 63 | 115 | 193.8 | 0.82 | 20.59
DSH240* | 20 | 7000 | 75 | 67 | 115 | 200.7 | 0.69 | 17.89
DSH240* | 20 | 7000 | 75 | 71 | 115 | 211.1 | 0.55 | 15
DSH240* | 20 | 7000 | 75 | 59 | 125 | 184.3 | 1 | 23.9
DSH240* | 20 | 7000 | 75 | 63 | 125 | 187.6 | 1 | 24.4
DSH240* | 20 | 7000 | 75 | 67 | 125 | 194.4 | 0.8 | 20.2
DSH240* | 20 | 7000 | 75 | 71 | 125 | 204.9 | 0.66 | 17.6
DSH240* | 20 | 7000 | 80 | 59 | 65 | 234.3 | 1 | 30.43
DSH240* | 20 | 7000 | 80 | 63 | 65 | 237.5 | 0.82 | 25.27
DSH240* | 20 | 7000 | 80 | 67 | 65 | 244.4 | 0.69 | 21.83
DSH240* | 20 | 7000 | 80 | 71 | 65 | 254.9 | 0.55 | 18.2
DSH240* | 20 | 7000 | 80 | 59 | 75 | 232.2 | 1 | 30.16
DSH240* | 20 | 7000 | 80 | 63 | 75 | 235.5 | 0.83 | 25.24
DSH240* | 20 | 7000 | 80 | 67 | 75 | 242.3 | 0.69 | 21.84
DSH240* | 20 | 7000 | 80 | 71 | 75 | 252.8 | 0.56 | 18.2
DSH240* | 20 | 7000 | 80 | 59 | 85 | 226.2 | 1 | 29.38
DSH240* | 20 | 7000 | 80 | 63 | 85 | 229.5 | 0.85 | 25.32
DSH240* | 20 | 7000 | 80 | 67 | 85 | 236.3 | 0.72 | 22.04
DSH240* | 20 | 7000 | 80 | 71 | 85 | 246.8 | 0.58 | 18.6
DSH240* | 20 | 7000 | 80 | 59 | 95 | 215.9 | 1 | 28.04
DSH240* | 20 | 7000 | 80 | 63 | 95 | 219.1 | 0.87 | 24.72
DSH240* | 20 | 7000 | 80 | 67 | 95 | 226 | 0.74 | 21.63
DSH240* | 20 | 7000 | 80 | 71 | 95 | 236.5 | 0.6 | 18.4
DSH240* | 20 | 7000 | 80 | 59 | 105 | 203.3 | 1 | 26.4
DSH240* | 20 | 7000 | 80 | 63 | 105 | 206.5 | 1 | 26.82
DSH240* | 20 | 7000 | 80 | 67 | 105 | 213.4 | 0.76 | 21.02
DSH240* | 20 | 7000 | 80 | 71 | 105 | 223.9 | 0.62 | 18
DSH240* | 20 | 7000 | 80 | 59 | 115 | 191.7 | 1 | 24.9
DSH240* | 20 | 7000 | 80 | 63 | 115 | 195 | 1 | 25.32
DSH240* | 20 | 7000 | 80 | 67 | 115 | 201.8 | 0.81 | 21.19
DSH240* | 20 | 7000 | 80 | 71 | 115 | 212.3 | 0.67 | 18.5
DSH240* | 20 | 7000 | 80 | 59 | 125 | 185.5 | 1 | 24.1
DSH240* | 20 | 7000 | 80 | 63 | 125 | 188.8 | 1 | 24.5
DSH240* | 20 | 7000 | 80 | 67 | 125 | 195.6 | 1 | 25.4
DSH240* | 20 | 7000 | 80 | 71 | 125 | 206.1 | 0.78 | 21
DSH240* | 20 | 7000 | 85 | 59 | 65 | 238.1 | 1 | 30.93
DSH240* | 20 | 7000 | 85 | 63 | 65 | 241.4 | 0.92 | 28.77
DSH240* | 20 | 7000 | 85 | 67 | 65 | 248.3 | 0.79 | 25.34
DSH240* | 20 | 7000 | 85 | 71 | 65 | 258.8 | 0.65 | 21.8
DSH240* | 20 | 7000 | 85 | 59 | 75 | 236.1 | 1 | 30.66
DSH240* | 20 | 7000 | 85 | 63 | 75 | 239.3 | 0.92 | 28.71
DSH240* | 20 | 7000 | 85 | 67 | 75 | 246.2 | 0.79 | 25.33
DSH240* | 20 | 7000 | 85 | 71 | 75 | 256.7 | 0.65 | 21.8
DSH240* | 20 | 7000 | 85 | 59 | 85 | 230.1 | 1 | 29.88
DSH240* | 20 | 7000 | 85 | 63 | 85 | 233.3 | 1 | 30.3
DSH240* | 20 | 7000 | 85 | 67 | 85 | 240.2 | 0.82 | 25.47
DSH240* | 20 | 7000 | 85 | 71 | 85 | 250.7 | 0.68 | 22.1
DSH240* | 20 | 7000 | 85 | 59 | 95 | 219.8 | 1 | 28.54
DSH240* | 20 | 7000 | 85 | 63 | 95 | 223 | 1 | 28.96
DSH240* | 20 | 7000 | 85 | 67 | 95 | 229.9 | 0.84 | 24.94
DSH240* | 20 | 7000 | 85 | 71 | 95 | 240.4 | 0.7 | 21.7
DSH240* | 20 | 7000 | 85 | 59 | 105 | 207.1 | 1 | 26.9
DSH240* | 20 | 7000 | 85 | 63 | 105 | 210.4 | 1 | 27.32
DSH240* | 20 | 7000 | 85 | 67 | 105 | 217.2 | 0.86 | 24.17
DSH240* | 20 | 7000 | 85 | 71 | 105 | 227.7 | 0.72 | 21.2
DSH240* | 20 | 7000 | 85 | 59 | 115 | 195.6 | 1 | 25.4
DSH240* | 20 | 7000 | 85 | 63 | 115 | 198.9 | 1 | 25.83
DSH240* | 20 | 7000 | 85 | 67 | 115 | 205.7 | 1 | 26.72
DSH240* | 20 | 7000 | 85 | 71 | 115 | 216.2 | 0.77 | 21.6
DSH240* | 20 | 7000 | 85 | 59 | 125 | 189.4 | 1 | 24.6
DSH240* | 20 | 7000 | 85 | 63 | 125 | 192.6 | 1 | 25
DSH240* | 20 | 7000 | 85 | 67 | 125 | 199.5 | 1 | 25.9
DSH240* | 20 | 7000 | 85 | 71 | 125 | 210 | 0.88 | 24.1
DSH240* | 20 | 7000 | 90 | 59 | 65 | 234.3 | 1 | 30.43
DSH240* | 20 | 7000 | 90 | 63 | 65 | 237.5 | 0.82 | 25.27
DSH240* | 20 | 7000 | 90 | 67 | 65 | 244.4 | 0.69 | 21.83
DSH240* | 20 | 7000 | 90 | 71 | 65 | 254.9 | 0.55 | 18.2
DSH240* | 20 | 7000 | 90 | 59 | 75 | 232.2 | 1 | 30.16
DSH240* | 20 | 7000 | 90 | 63 | 75 | 235.5 | 0.83 | 25.24
DSH240* | 20 | 7000 | 90 | 67 | 75 | 242.3 | 0.69 | 21.84
DSH240* | 20 | 7000 | 90 | 71 | 75 | 252.8 | 0.56 | 18.2
DSH240* | 20 | 7000 | 90 | 59 | 85 | 226.2 | 1 | 29.38
DSH240* | 20 | 7000 | 90 | 63 | 85 | 229.5 | 0.85 | 25.32
DSH240* | 20 | 7000 | 90 | 67 | 85 | 236.3 | 0.72 | 22.04
DSH240* | 20 | 7000 | 90 | 71 | 85 | 246.8 | 0.58 | 18.6
DSH240* | 20 | 7000 | 90 | 59 | 95 | 215.9 | 1 | 28.04
DSH240* | 20 | 7000 | 90 | 63 | 95 | 219.1 | 0.87 | 24.72
DSH240* | 20 | 7000 | 90 | 67 | 95 | 226 | 0.74 | 21.63
DSH240* | 20 | 7000 | 90 | 71 | 95 | 236.5 | 0.6 | 18.4
DSH240* | 20 | 7000 | 90 | 59 | 105 | 203.3 | 1 | 26.4
DSH240* | 20 | 7000 | 90 | 63 | 105 | 206.5 | 1 | 26.82
DSH240* | 20 | 7000 | 90 | 67 | 105 | 213.4 | 0.76 | 21.02
DSH240* | 20 | 7000 | 90 | 71 | 105 | 223.9 | 0.62 | 18
DSH240* | 20 | 7000 | 90 | 59 | 115 | 191.7 | 1 | 24.9
DSH240* | 20 | 7000 | 90 | 63 | 115 | 195 | 1 | 25.32
DSH240* | 20 | 7000 | 90 | 67 | 115 | 201.8 | 0.81 | 21.19
DSH240* | 20 | 7000 | 90 | 71 | 115 | 212.3 | 0.67 | 18.5
DSH240* | 20 | 7000 | 90 | 59 | 125 | 194.1 | 1 | 25.2
DSH240* | 20 | 7000 | 90 | 63 | 125 | 197.3 | 1 | 25.6
DSH240* | 20 | 7000 | 90 | 67 | 125 | 204.2 | 1 | 26.5
DSH240* | 20 | 7000 | 90 | 71 | 125 | 214.7 | 1 | 27.9
DSH240* | 20 | 7500 | 70 | 59 | 65 | 234.9 | 0.67 | 19.02
DSH240* | 20 | 7500 | 70 | 63 | 65 | 238.2 | 0.59 | 17.15
DSH240* | 20 | 7500 | 70 | 67 | 65 | 245.1 | 0.46 | 13.74
DSH240* | 20 | 7500 | 70 | 59 | 75 | 232.9 | 0.67 | 19.02
DSH240* | 20 | 7500 | 70 | 63 | 75 | 236.1 | 0.6 | 17.17
DSH240* | 20 | 7500 | 70 | 67 | 75 | 243 | 0.47 | 13.8
DSH240* | 20 | 7500 | 70 | 59 | 85 | 226.9 | 0.7 | 19.2
DSH240* | 20 | 7500 | 70 | 63 | 85 | 230.1 | 0.62 | 17.42
DSH240* | 20 | 7500 | 70 | 67 | 85 | 237 | 0.49 | 14.16
DSH240* | 20 | 7500 | 70 | 59 | 95 | 216.5 | 0.72 | 18.82
DSH240* | 20 | 7500 | 70 | 63 | 95 | 219.8 | 0.64 | 17.14
DSH240* | 20 | 7500 | 70 | 67 | 95 | 226.7 | 0.51 | 14.06
DSH240* | 20 | 7500 | 70 | 59 | 105 | 203.9 | 1 | 24.72
DSH240* | 20 | 7500 | 70 | 63 | 105 | 207.2 | 0.66 | 16.69
DSH240* | 20 | 7500 | 70 | 67 | 105 | 214 | 0.53 | 13.83
DSH240* | 20 | 7500 | 70 | 59 | 115 | 192.4 | 1 | 23.32
DSH240* | 20 | 7500 | 70 | 63 | 115 | 195.6 | 0.71 | 16.95
DSH240* | 20 | 7500 | 70 | 67 | 115 | 202.5 | 0.58 | 14.31
DSH240* | 20 | 7500 | 70 | 59 | 125 | 186.2 | 1 | 22.6
DSH240* | 20 | 7500 | 70 | 63 | 125 | 189.4 | 1 | 23
DSH240* | 20 | 7500 | 70 | 67 | 125 | 196.3 | 0.7 | 16.6
DSH240* | 20 | 7500 | 75 | 59 | 65 | 235.1 | 0.79 | 22.6
DSH240* | 20 | 7500 | 75 | 63 | 65 | 238.3 | 0.72 | 20.78
DSH240* | 20 | 7500 | 75 | 67 | 65 | 245.2 | 0.59 | 17.47
DSH240* | 20 | 7500 | 75 | 71 | 65 | 255.7 | 0.45 | 13.9
DSH240* | 20 | 7500 | 75 | 59 | 75 | 233 | 0.8 | 22.57
DSH240* | 20 | 7500 | 75 | 63 | 75 | 236.3 | 0.73 | 20.77
DSH240* | 20 | 7500 | 75 | 67 | 75 | 243.1 | 0.59 | 17.5
DSH240* | 20 | 7500 | 75 | 71 | 75 | 253.6 | 0.46 | 14
DSH240* | 20 | 7500 | 75 | 59 | 85 | 227 | 1 | 27.52
DSH240* | 20 | 7500 | 75 | 63 | 85 | 230.3 | 0.75 | 20.92
DSH240* | 20 | 7500 | 75 | 67 | 85 | 237.1 | 0.62 | 17.76
DSH240* | 20 | 7500 | 75 | 71 | 85 | 247.6 | 0.48 | 14.4
DSH240* | 20 | 7500 | 75 | 59 | 95 | 216.7 | 1 | 26.26
DSH240* | 20 | 7500 | 75 | 63 | 95 | 219.9 | 0.77 | 20.49
DSH240* | 20 | 7500 | 75 | 67 | 95 | 226.8 | 0.64 | 17.51
DSH240* | 20 | 7500 | 75 | 71 | 95 | 237.3 | 0.5 | 14.3
DSH240* | 20 | 7500 | 75 | 59 | 105 | 204.1 | 1 | 24.73
DSH240* | 20 | 7500 | 75 | 63 | 105 | 207.3 | 0.79 | 19.85
DSH240* | 20 | 7500 | 75 | 67 | 105 | 214.2 | 0.66 | 17.09
DSH240* | 20 | 7500 | 75 | 71 | 105 | 224.7 | 0.52 | 14.2
DSH240* | 20 | 7500 | 75 | 59 | 115 | 192.5 | 1 | 23.34
DSH240* | 20 | 7500 | 75 | 63 | 115 | 195.8 | 1 | 23.73
DSH240* | 20 | 7500 | 75 | 67 | 115 | 202.6 | 0.71 | 17.4
DSH240* | 20 | 7500 | 75 | 71 | 115 | 213.1 | 0.57 | 14.7
DSH240* | 20 | 7500 | 75 | 59 | 125 | 186.3 | 1 | 22.6
DSH240* | 20 | 7500 | 75 | 63 | 125 | 189.6 | 1 | 23
DSH240* | 20 | 7500 | 75 | 67 | 125 | 196.4 | 0.82 | 19.6
DSH240* | 20 | 7500 | 75 | 71 | 125 | 206.9 | 0.68 | 17.2
DSH240* | 20 | 7500 | 80 | 59 | 65 | 236.3 | 1 | 28.64
DSH240* | 20 | 7500 | 80 | 63 | 65 | 239.5 | 0.84 | 24.41
DSH240* | 20 | 7500 | 80 | 67 | 65 | 246.4 | 0.71 | 21.19
DSH240* | 20 | 7500 | 80 | 71 | 65 | 256.9 | 0.57 | 17.8
DSH240* | 20 | 7500 | 80 | 59 | 75 | 234.2 | 1 | 28.39
DSH240* | 20 | 7500 | 80 | 63 | 75 | 237.5 | 0.85 | 24.38
DSH240* | 20 | 7500 | 80 | 67 | 75 | 244.3 | 0.72 | 21.19
DSH240* | 20 | 7500 | 80 | 71 | 75 | 254.8 | 0.58 | 17.8
DSH240* | 20 | 7500 | 80 | 59 | 85 | 228.2 | 1 | 27.66
DSH240* | 20 | 7500 | 80 | 63 | 85 | 231.5 | 0.87 | 24.44
DSH240* | 20 | 7500 | 80 | 67 | 85 | 238.3 | 0.74 | 21.37
DSH240* | 20 | 7500 | 80 | 71 | 85 | 248.8 | 0.6 | 18.1
DSH240* | 20 | 7500 | 80 | 59 | 95 | 217.9 | 1 | 26.41
DSH240* | 20 | 7500 | 80 | 63 | 95 | 221.1 | 0.89 | 23.86
DSH240* | 20 | 7500 | 80 | 67 | 95 | 228 | 0.76 | 20.97
DSH240* | 20 | 7500 | 80 | 71 | 95 | 238.5 | 0.62 | 17.9
DSH240* | 20 | 7500 | 80 | 59 | 105 | 205.2 | 1 | 24.88
DSH240* | 20 | 7500 | 80 | 63 | 105 | 208.5 | 1 | 25.27
DSH240* | 20 | 7500 | 80 | 67 | 105 | 215.4 | 0.78 | 20.36
DSH240* | 20 | 7500 | 80 | 71 | 105 | 225.9 | 0.64 | 17.6
DSH240* | 20 | 7500 | 80 | 59 | 115 | 193.7 | 1 | 23.48
DSH240* | 20 | 7500 | 80 | 63 | 115 | 197 | 1 | 23.88
DSH240* | 20 | 7500 | 80 | 67 | 115 | 203.8 | 0.83 | 20.51
DSH240* | 20 | 7500 | 80 | 71 | 115 | 214.3 | 0.69 | 18
DSH240* | 20 | 7500 | 80 | 59 | 125 | 187.5 | 1 | 22.7
DSH240* | 20 | 7500 | 80 | 63 | 125 | 190.8 | 1 | 23.1
DSH240* | 20 | 7500 | 80 | 67 | 125 | 197.6 | 1 | 24
DSH240* | 20 | 7500 | 80 | 71 | 125 | 208.1 | 0.81 | 20.3
DSH240* | 20 | 7500 | 85 | 59 | 65 | 240.1 | 1 | 29.11
DSH240* | 20 | 7500 | 85 | 63 | 65 | 243.4 | 0.94 | 27.71
DSH240* | 20 | 7500 | 85 | 67 | 65 | 250.3 | 0.81 | 24.5
DSH240* | 20 | 7500 | 85 | 71 | 65 | 260.7 | 0.67 | 21.1
DSH240* | 20 | 7500 | 85 | 59 | 75 | 238.1 | 1 | 28.86
DSH240* | 20 | 7500 | 85 | 63 | 75 | 241.3 | 0.95 | 27.65
DSH240* | 20 | 7500 | 85 | 67 | 75 | 248.2 | 0.81 | 24.48
DSH240* | 20 | 7500 | 85 | 71 | 75 | 258.7 | 0.68 | 21.2
DSH240* | 20 | 7500 | 85 | 59 | 85 | 232.1 | 1 | 28.13
DSH240* | 20 | 7500 | 85 | 63 | 85 | 235.3 | 1 | 28.52
DSH240* | 20 | 7500 | 85 | 67 | 85 | 242.2 | 0.84 | 24.6
DSH240* | 20 | 7500 | 85 | 71 | 85 | 252.7 | 0.7 | 21.4
DSH240* | 20 | 7500 | 85 | 59 | 95 | 221.7 | 1 | 26.88
DSH240* | 20 | 7500 | 85 | 63 | 95 | 225 | 1 | 27.27
DSH240* | 20 | 7500 | 85 | 67 | 95 | 231.9 | 0.86 | 24.08
DSH240* | 20 | 7500 | 85 | 71 | 95 | 242.4 | 0.72 | 21.1
DSH240* | 20 | 7500 | 85 | 59 | 105 | 209.1 | 1 | 25.35
DSH240* | 20 | 7500 | 85 | 63 | 105 | 212.4 | 1 | 25.74
DSH240* | 20 | 7500 | 85 | 67 | 105 | 219.2 | 0.88 | 23.34
DSH240* | 20 | 7500 | 85 | 71 | 105 | 229.7 | 0.74 | 20.6
DSH240* | 20 | 7500 | 85 | 59 | 115 | 197.6 | 1 | 23.95
DSH240* | 20 | 7500 | 85 | 63 | 115 | 200.8 | 1 | 24.34
DSH240* | 20 | 7500 | 85 | 67 | 115 | 207.7 | 1 | 25.18
DSH240* | 20 | 7500 | 85 | 71 | 115 | 218.2 | 0.79 | 20.9
DSH240* | 20 | 7500 | 85 | 59 | 125 | 191.4 | 1 | 23.2
DSH240* | 20 | 7500 | 85 | 63 | 125 | 194.6 | 1 | 23.6
DSH240* | 20 | 7500 | 85 | 67 | 125 | 201.5 | 1 | 24.4
DSH240* | 20 | 7500 | 85 | 71 | 125 | 212 | 0.9 | 23.2
DSH240* | 20 | 7500 | 90 | 59 | 65 | 236.3 | 1 | 28.64
DSH240* | 20 | 7500 | 90 | 63 | 65 | 239.5 | 0.84 | 24.41
DSH240* | 20 | 7500 | 90 | 67 | 65 | 246.4 | 0.71 | 21.19
DSH240* | 20 | 7500 | 90 | 71 | 65 | 256.9 | 0.57 | 17.8
DSH240* | 20 | 7500 | 90 | 59 | 75 | 234.2 | 1 | 28.39
DSH240* | 20 | 7500 | 90 | 63 | 75 | 237.5 | 0.85 | 24.38
DSH240* | 20 | 7500 | 90 | 67 | 75 | 244.3 | 0.72 | 21.19
DSH240* | 20 | 7500 | 90 | 71 | 75 | 254.8 | 0.58 | 17.8
DSH240* | 20 | 7500 | 90 | 59 | 85 | 228.2 | 1 | 27.66
DSH240* | 20 | 7500 | 90 | 63 | 85 | 231.5 | 0.87 | 24.44
DSH240* | 20 | 7500 | 90 | 67 | 85 | 238.3 | 0.74 | 21.37
DSH240* | 20 | 7500 | 90 | 71 | 85 | 248.8 | 0.6 | 18.1
DSH240* | 20 | 7500 | 90 | 59 | 95 | 217.9 | 1 | 26.41
DSH240* | 20 | 7500 | 90 | 63 | 95 | 221.1 | 0.89 | 23.86
DSH240* | 20 | 7500 | 90 | 67 | 95 | 228 | 0.76 | 20.97
DSH240* | 20 | 7500 | 90 | 71 | 95 | 238.5 | 0.62 | 17.9
DSH240* | 20 | 7500 | 90 | 59 | 105 | 205.2 | 1 | 24.88
DSH240* | 20 | 7500 | 90 | 63 | 105 | 208.5 | 1 | 25.27
DSH240* | 20 | 7500 | 90 | 67 | 105 | 215.4 | 0.78 | 20.36
DSH240* | 20 | 7500 | 90 | 71 | 105 | 225.9 | 0.64 | 17.6
DSH240* | 20 | 7500 | 90 | 59 | 115 | 193.7 | 1 | 23.48
DSH240* | 20 | 7500 | 90 | 63 | 115 | 197 | 1 | 23.88
DSH240* | 20 | 7500 | 90 | 67 | 115 | 203.8 | 0.83 | 20.51
DSH240* | 20 | 7500 | 90 | 71 | 115 | 214.3 | 0.69 | 18
DSH240* | 20 | 7500 | 90 | 59 | 125 | 196.1 | 1 | 23.8
DSH240* | 20 | 7500 | 90 | 63 | 125 | 199.3 | 1 | 24.2
DSH240* | 20 | 7500 | 90 | 67 | 125 | 206.2 | 1 | 25
DSH240* | 20 | 7500 | 90 | 71 | 125 | 216.7 | 1 | 26.3
DSH240* | 20 | 8000 | 70 | 59 | 65 | 237.2 | 0.68 | 18.38
DSH240* | 20 | 8000 | 70 | 63 | 65 | 240.4 | 0.61 | 16.61
DSH240* | 20 | 8000 | 70 | 67 | 65 | 247.3 | 0.48 | 13.39
DSH240* | 20 | 8000 | 70 | 59 | 75 | 235.1 | 0.69 | 18.38
DSH240* | 20 | 8000 | 70 | 63 | 75 | 238.3 | 0.61 | 16.63
DSH240* | 20 | 8000 | 70 | 67 | 75 | 245.2 | 0.48 | 13.45
DSH240* | 20 | 8000 | 70 | 59 | 85 | 229.1 | 0.71 | 18.54
DSH240* | 20 | 8000 | 70 | 63 | 85 | 232.3 | 0.64 | 16.86
DSH240* | 20 | 8000 | 70 | 67 | 85 | 239.2 | 0.51 | 13.78
DSH240* | 20 | 8000 | 70 | 59 | 95 | 218.8 | 1 | 24.86
DSH240* | 20 | 8000 | 70 | 63 | 95 | 222 | 0.66 | 16.58
DSH240* | 20 | 8000 | 70 | 67 | 95 | 228.9 | 0.53 | 13.68
DSH240* | 20 | 8000 | 70 | 59 | 105 | 206.1 | 1 | 23.42
DSH240* | 20 | 8000 | 70 | 63 | 105 | 209.4 | 0.68 | 16.15
DSH240* | 20 | 8000 | 70 | 67 | 105 | 216.3 | 0.55 | 13.45
DSH240* | 20 | 8000 | 70 | 59 | 115 | 194.6 | 1 | 22.11
DSH240* | 20 | 8000 | 70 | 63 | 115 | 197.9 | 0.73 | 16.38
DSH240* | 20 | 8000 | 70 | 67 | 115 | 204.7 | 0.6 | 13.89
DSH240* | 20 | 8000 | 70 | 59 | 125 | 188.4 | 1 | 21.4
DSH240* | 20 | 8000 | 70 | 63 | 125 | 191.6 | 1 | 21.8
DSH240* | 20 | 8000 | 70 | 67 | 125 | 198.5 | 0.71 | 16.1
DSH240* | 20 | 8000 | 75 | 59 | 65 | 237.3 | 0.81 | 21.77
DSH240* | 20 | 8000 | 75 | 63 | 65 | 240.5 | 0.73 | 20.05
DSH240* | 20 | 8000 | 75 | 67 | 65 | 247.4 | 0.6 | 16.92
DSH240* | 20 | 8000 | 75 | 71 | 65 | 257.9 | 0.46 | 13.6
DSH240* | 20 | 8000 | 75 | 59 | 75 | 235.2 | 0.81 | 21.74
DSH240* | 20 | 8000 | 75 | 63 | 75 | 238.5 | 0.74 | 20.04
DSH240* | 20 | 8000 | 75 | 67 | 75 | 245.3 | 0.61 | 16.95
DSH240* | 20 | 8000 | 75 | 71 | 75 | 255.8 | 0.47 | 13.6
DSH240* | 20 | 8000 | 75 | 59 | 85 | 229.2 | 1 | 26.05
DSH240* | 20 | 8000 | 75 | 63 | 85 | 232.5 | 0.76 | 20.18
DSH240* | 20 | 8000 | 75 | 67 | 85 | 239.3 | 0.63 | 17.19
DSH240* | 20 | 8000 | 75 | 71 | 85 | 249.8 | 0.49 | 14
DSH240* | 20 | 8000 | 75 | 59 | 95 | 218.9 | 1 | 24.87
DSH240* | 20 | 8000 | 75 | 63 | 95 | 222.1 | 0.78 | 19.76
DSH240* | 20 | 8000 | 75 | 67 | 95 | 229 | 0.65 | 16.94
DSH240* | 20 | 8000 | 75 | 71 | 95 | 239.5 | 0.51 | 13.9
DSH240* | 20 | 8000 | 75 | 59 | 105 | 206.3 | 1 | 23.44
DSH240* | 20 | 8000 | 75 | 63 | 105 | 209.5 | 0.8 | 19.14
DSH240* | 20 | 8000 | 75 | 67 | 105 | 216.4 | 0.67 | 16.54
DSH240* | 20 | 8000 | 75 | 71 | 105 | 226.9 | 0.53 | 13.8
DSH240* | 20 | 8000 | 75 | 59 | 115 | 194.7 | 1 | 22.13
DSH240* | 20 | 8000 | 75 | 63 | 115 | 198 | 1 | 22.5
DSH240* | 20 | 8000 | 75 | 67 | 115 | 204.9 | 0.72 | 16.82
DSH240* | 20 | 8000 | 75 | 71 | 115 | 215.4 | 0.58 | 14.3
DSH240* | 20 | 8000 | 75 | 59 | 125 | 188.5 | 1 | 21.4
DSH240* | 20 | 8000 | 75 | 63 | 125 | 191.8 | 1 | 21.8
DSH240* | 20 | 8000 | 75 | 67 | 125 | 198.6 | 0.84 | 18.9
DSH240* | 20 | 8000 | 75 | 71 | 125 | 209.1 | 0.7 | 16.6
DSH240* | 20 | 8000 | 80 | 59 | 65 | 238.5 | 1 | 27.1
DSH240* | 20 | 8000 | 80 | 63 | 65 | 241.7 | 0.86 | 23.49
DSH240* | 20 | 8000 | 80 | 67 | 65 | 248.6 | 0.72 | 20.44
DSH240* | 20 | 8000 | 80 | 71 | 65 | 259.1 | 0.58 | 17.2
DSH240* | 20 | 8000 | 80 | 59 | 75 | 236.4 | 1 | 26.87
DSH240* | 20 | 8000 | 80 | 63 | 75 | 239.7 | 0.86 | 23.45
DSH240* | 20 | 8000 | 80 | 67 | 75 | 246.5 | 0.73 | 20.44
DSH240* | 20 | 8000 | 80 | 71 | 75 | 257 | 0.59 | 17.3
DSH240* | 20 | 8000 | 80 | 59 | 85 | 230.4 | 1 | 26.18
DSH240* | 20 | 8000 | 80 | 63 | 85 | 233.7 | 0.89 | 23.51
DSH240* | 20 | 8000 | 80 | 67 | 85 | 240.5 | 0.75 | 20.61
DSH240* | 20 | 8000 | 80 | 71 | 85 | 251 | 0.62 | 17.5
DSH240* | 20 | 8000 | 80 | 59 | 95 | 220.1 | 1 | 25.01
DSH240* | 20 | 8000 | 80 | 63 | 95 | 223.3 | 1 | 25.38
DSH240* | 20 | 8000 | 80 | 67 | 95 | 230.2 | 0.77 | 20.21
DSH240* | 20 | 8000 | 80 | 71 | 95 | 240.7 | 0.63 | 17.3
DSH240* | 20 | 8000 | 80 | 59 | 105 | 207.5 | 1 | 23.58
DSH240* | 20 | 8000 | 80 | 63 | 105 | 210.7 | 1 | 23.94
DSH240* | 20 | 8000 | 80 | 67 | 105 | 217.6 | 0.79 | 19.64
DSH240* | 20 | 8000 | 80 | 71 | 105 | 228.1 | 0.66 | 17
DSH240* | 20 | 8000 | 80 | 59 | 115 | 195.9 | 1 | 22.27
DSH240* | 20 | 8000 | 80 | 63 | 115 | 199.2 | 1 | 22.63
DSH240* | 20 | 8000 | 80 | 67 | 115 | 206.1 | 0.84 | 19.77
DSH240* | 20 | 8000 | 80 | 71 | 115 | 216.5 | 0.71 | 17.4
DSH240* | 20 | 8000 | 80 | 59 | 125 | 189.7 | 1 | 21.6
DSH240* | 20 | 8000 | 80 | 63 | 125 | 193 | 1 | 21.9
DSH240* | 20 | 8000 | 80 | 67 | 125 | 199.8 | 1 | 22.7
DSH240* | 20 | 8000 | 80 | 71 | 125 | 210.3 | 0.82 | 19.6
DSH240* | 20 | 8000 | 85 | 59 | 65 | 242.4 | 1 | 27.54
DSH240* | 20 | 8000 | 85 | 63 | 65 | 245.6 | 0.95 | 26.61
DSH240* | 20 | 8000 | 85 | 67 | 65 | 252.5 | 0.82 | 23.58
DSH240* | 20 | 8000 | 85 | 71 | 65 | 263 | 0.68 | 20.4
DSH240* | 20 | 8000 | 85 | 59 | 75 | 240.3 | 1 | 27.31
DSH240* | 20 | 8000 | 85 | 63 | 75 | 243.5 | 0.96 | 26.55
DSH240* | 20 | 8000 | 85 | 67 | 75 | 250.4 | 0.83 | 23.56
DSH240* | 20 | 8000 | 85 | 71 | 75 | 260.9 | 0.69 | 20.4
DSH240* | 20 | 8000 | 85 | 59 | 85 | 234.3 | 1 | 26.62
DSH240* | 20 | 8000 | 85 | 63 | 85 | 237.5 | 1 | 26.99
DSH240* | 20 | 8000 | 85 | 67 | 85 | 244.4 | 0.85 | 23.67
DSH240* | 20 | 8000 | 85 | 71 | 85 | 254.9 | 0.71 | 20.7
DSH240* | 20 | 8000 | 85 | 59 | 95 | 224 | 1 | 25.45
DSH240* | 20 | 8000 | 85 | 63 | 95 | 227.2 | 1 | 25.82
DSH240* | 20 | 8000 | 85 | 67 | 95 | 234.1 | 0.87 | 23.17
DSH240* | 20 | 8000 | 85 | 71 | 95 | 244.6 | 0.73 | 20.4
DSH240* | 20 | 8000 | 85 | 59 | 105 | 211.3 | 1 | 24.02
DSH240* | 20 | 8000 | 85 | 63 | 105 | 214.6 | 1 | 24.38
DSH240* | 20 | 8000 | 85 | 67 | 105 | 221.5 | 0.89 | 22.46
DSH240* | 20 | 8000 | 85 | 71 | 105 | 231.9 | 0.75 | 19.9
DSH240* | 20 | 8000 | 85 | 59 | 115 | 199.8 | 1 | 22.71
DSH240* | 20 | 8000 | 85 | 63 | 115 | 203.1 | 1 | 23.07
DSH240* | 20 | 8000 | 85 | 67 | 115 | 209.9 | 1 | 23.86
DSH240* | 20 | 8000 | 85 | 71 | 115 | 220.4 | 0.8 | 20.1
DSH240* | 20 | 8000 | 85 | 59 | 125 | 193.6 | 1 | 22
DSH240* | 20 | 8000 | 85 | 63 | 125 | 196.8 | 1 | 22.4
DSH240* | 20 | 8000 | 85 | 67 | 125 | 203.7 | 1 | 23.1
DSH240* | 20 | 8000 | 85 | 71 | 125 | 214.2 | 0.92 | 22.4
DSH240* | 20 | 8000 | 90 | 59 | 65 | 238.5 | 1 | 27.1
DSH240* | 20 | 8000 | 90 | 63 | 65 | 241.7 | 0.86 | 23.49
DSH240* | 20 | 8000 | 90 | 67 | 65 | 248.6 | 0.72 | 20.44
DSH240* | 20 | 8000 | 90 | 71 | 65 | 259.1 | 0.58 | 17.2
DSH240* | 20 | 8000 | 90 | 59 | 75 | 236.4 | 1 | 26.87
DSH240* | 20 | 8000 | 90 | 63 | 75 | 239.7 | 0.86 | 23.45
DSH240* | 20 | 8000 | 90 | 67 | 75 | 246.5 | 0.73 | 20.44
DSH240* | 20 | 8000 | 90 | 71 | 75 | 257 | 0.59 | 17.3
DSH240* | 20 | 8000 | 90 | 59 | 85 | 230.4 | 1 | 26.18
DSH240* | 20 | 8000 | 90 | 63 | 85 | 233.7 | 0.89 | 23.51
DSH240* | 20 | 8000 | 90 | 67 | 85 | 240.5 | 0.75 | 20.61
DSH240* | 20 | 8000 | 90 | 71 | 85 | 251 | 0.62 | 17.5
DSH240* | 20 | 8000 | 90 | 59 | 95 | 220.1 | 1 | 25.01
DSH240* | 20 | 8000 | 90 | 63 | 95 | 223.3 | 1 | 25.38
DSH240* | 20 | 8000 | 90 | 67 | 95 | 230.2 | 0.77 | 20.21
DSH240* | 20 | 8000 | 90 | 71 | 95 | 240.7 | 0.63 | 17.3
DSH240* | 20 | 8000 | 90 | 59 | 105 | 207.5 | 1 | 23.58
DSH240* | 20 | 8000 | 90 | 63 | 105 | 210.7 | 1 | 23.94
DSH240* | 20 | 8000 | 90 | 67 | 105 | 217.6 | 0.79 | 19.64
DSH240* | 20 | 8000 | 90 | 71 | 105 | 228.1 | 0.66 | 17
DSH240* | 20 | 8000 | 90 | 59 | 115 | 195.9 | 1 | 22.27
DSH240* | 20 | 8000 | 90 | 63 | 115 | 199.2 | 1 | 22.63
DSH240* | 20 | 8000 | 90 | 67 | 115 | 206.1 | 0.84 | 19.77
DSH240* | 20 | 8000 | 90 | 71 | 115 | 216.5 | 0.71 | 17.4
DSH240* | 20 | 8000 | 90 | 59 | 125 | 198.3 | 1 | 22.5
DSH240* | 20 | 8000 | 90 | 63 | 125 | 201.5 | 1 | 22.9
DSH240* | 20 | 8000 | 90 | 67 | 125 | 208.4 | 1 | 23.7
DSH240* | 20 | 8000 | 90 | 71 | 125 | 218.9 | 1 | 24.9
DHH036* | 3 | 900 | 70 | 59 | 65 | 35.1 | 0.58 | 20.5
DHH036* | 3 | 900 | 70 | 63 | 65 | 35.6 | 0.52 | 18.7
DHH036* | 3 | 900 | 70 | 67 | 65 | 36.7 | 0.41 | 15.33
DHH036* | 3 | 900 | 70 | 59 | 75 | 34.8 | 0.58 | 20.45
DHH036* | 3 | 900 | 70 | 63 | 75 | 35.3 | 0.52 | 18.65
DHH036* | 3 | 900 | 70 | 67 | 75 | 36.4 | 0.42 | 15.28
DHH036* | 3 | 900 | 70 | 59 | 85 | 33.9 | 0.6 | 20.71
DHH036* | 3 | 900 | 70 | 63 | 85 | 34.4 | 0.54 | 18.9
DHH036* | 3 | 900 | 70 | 67 | 85 | 35.5 | 0.43 | 15.53
DHH036* | 3 | 900 | 70 | 59 | 95 | 32.3 | 0.63 | 20.43
DHH036* | 3 | 900 | 70 | 63 | 95 | 32.8 | 0.56 | 18.63
DHH036* | 3 | 900 | 70 | 67 | 95 | 33.9 | 0.45 | 15.26
DHH036* | 3 | 900 | 70 | 59 | 105 | 30.3 | 0.66 | 20.19
DHH036* | 3 | 900 | 70 | 63 | 105 | 30.8 | 0.59 | 18.39
DHH036* | 3 | 900 | 70 | 67 | 105 | 31.9 | 0.47 | 15.02
DHH036* | 3 | 900 | 70 | 59 | 115 | 28.6 | 0.74 | 21.32
DHH036* | 3 | 900 | 70 | 63 | 115 | 29.1 | 0.66 | 19.52
DHH036* | 3 | 900 | 70 | 67 | 115 | 30.1 | 0.53 | 16.15
DHH036* | 3 | 900 | 75 | 59 | 65 | 35.3 | 0.69 | 24.47
DHH036* | 3 | 900 | 75 | 63 | 65 | 35.8 | 0.63 | 22.67
DHH036* | 3 | 900 | 75 | 67 | 65 | 36.9 | 0.52 | 19.3
DHH036* | 3 | 900 | 75 | 71 | 65 | 38.5 | 0.4 | 15.8
DHH036* | 3 | 900 | 75 | 59 | 75 | 35 | 0.69 | 24.42
DHH036* | 3 | 900 | 75 | 63 | 75 | 35.5 | 0.63 | 22.62
DHH036* | 3 | 900 | 75 | 67 | 75 | 36.6 | 0.52 | 19.25
DHH036* | 3 | 900 | 75 | 71 | 75 | 38.2 | 0.4 | 15.8
DHH036* | 3 | 900 | 75 | 59 | 85 | 34.1 | 0.72 | 24.68
DHH036* | 3 | 900 | 75 | 63 | 85 | 34.6 | 0.65 | 22.87
DHH036* | 3 | 900 | 75 | 67 | 85 | 35.6 | 0.54 | 19.5
DHH036* | 3 | 900 | 75 | 71 | 85 | 37.3 | 0.4 | 16
DHH036* | 3 | 900 | 75 | 59 | 95 | 32.5 | 0.74 | 24.4
DHH036* | 3 | 900 | 75 | 63 | 95 | 33 | 0.68 | 22.6
DHH036* | 3 | 900 | 75 | 67 | 95 | 34 | 0.56 | 19.23
DHH036* | 3 | 900 | 75 | 71 | 95 | 35.7 | 0.4 | 15.7
DHH036* | 3 | 900 | 75 | 59 | 105 | 30.5 | 0.78 | 24.16
DHH036* | 3 | 900 | 75 | 63 | 105 | 31 | 0.71 | 22.36
DHH036* | 3 | 900 | 75 | 67 | 105 | 32.1 | 0.59 | 18.99
DHH036* | 3 | 900 | 75 | 71 | 105 | 33.7 | 0.5 | 15.5
DHH036* | 3 | 900 | 75 | 59 | 115 | 28.7 | 0.87 | 25.29
DHH036* | 3 | 900 | 75 | 63 | 115 | 29.2 | 0.8 | 23.49
DHH036* | 3 | 900 | 75 | 67 | 115 | 30.3 | 0.66 | 20.12
DHH036* | 3 | 900 | 75 | 71 | 115 | 31.9 | 0.5 | 16.6
DHH036* | 3 | 900 | 80 | 59 | 65 | 35.5 | 0.79 | 28.47
DHH036* | 3 | 900 | 80 | 63 | 65 | 36 | 0.73 | 26.66
DHH036* | 3 | 900 | 80 | 67 | 65 | 37.1 | 0.62 | 23.29
DHH036* | 3 | 900 | 80 | 71 | 65 | 38.7 | 0.5 | 19.8
DHH036* | 3 | 900 | 80 | 59 | 75 | 35.2 | 0.8 | 28.42
DHH036* | 3 | 900 | 80 | 63 | 75 | 35.7 | 0.74 | 26.61
DHH036* | 3 | 900 | 80 | 67 | 75 | 36.8 | 0.63 | 23.24
DHH036* | 3 | 900 | 80 | 71 | 75 | 38.4 | 0.5 | 19.8
DHH036* | 3 | 900 | 80 | 59 | 85 | 34.3 | 0.83 | 28.67
DHH036* | 3 | 900 | 80 | 63 | 85 | 34.8 | 0.77 | 26.87
DHH036* | 3 | 900 | 80 | 67 | 85 | 35.8 | 0.65 | 23.5
DHH036* | 3 | 900 | 80 | 71 | 85 | 37.5 | 0.5 | 20
DHH036* | 3 | 900 | 80 | 59 | 95 | 32.7 | 0.86 | 28.4
DHH036* | 3 | 900 | 80 | 63 | 95 | 33.2 | 0.79 | 26.6
DHH036* | 3 | 900 | 80 | 67 | 95 | 34.2 | 0.67 | 23.22
DHH036* | 3 | 900 | 80 | 71 | 95 | 35.9 | 0.5 | 19.7
DHH036* | 3 | 900 | 80 | 59 | 105 | 30.7 | 0.91 | 28.16
DHH036* | 3 | 900 | 80 | 63 | 105 | 31.2 | 0.84 | 26.35
DHH036* | 3 | 900 | 80 | 67 | 105 | 32.3 | 0.7 | 22.98
DHH036* | 3 | 900 | 80 | 71 | 105 | 33.9 | 0.6 | 19.5
DHH036* | 3 | 900 | 80 | 59 | 115 | 28.9 | 1 | 29.22
DHH036* | 3 | 900 | 80 | 63 | 115 | 29.4 | 0.92 | 27.49
DHH036* | 3 | 900 | 80 | 67 | 115 | 30.5 | 0.78 | 24.11
DHH036* | 3 | 900 | 80 | 71 | 115 | 32.1 | 0.6 | 20.6
DHH036* | 3 | 900 | 85 | 59 | 65 | 36.1 | 0.88 | 32.01
DHH036* | 3 | 900 | 85 | 63 | 65 | 36.6 | 0.82 | 30.21
DHH036* | 3 | 900 | 85 | 67 | 65 | 37.7 | 0.71 | 26.84
DHH036* | 3 | 900 | 85 | 71 | 65 | 39.3 | 0.6 | 23.3
DHH036* | 3 | 900 | 85 | 59 | 75 | 35.8 | 0.88 | 31.96
DHH036* | 3 | 900 | 85 | 63 | 75 | 36.3 | 0.82 | 30.16
DHH036* | 3 | 900 | 85 | 67 | 75 | 37.4 | 0.71 | 26.79
DHH036* | 3 | 900 | 85 | 71 | 75 | 39 | 0.6 | 23.3
DHH036* | 3 | 900 | 85 | 59 | 85 | 34.9 | 0.91 | 32.22
DHH036* | 3 | 900 | 85 | 63 | 85 | 35.4 | 0.85 | 30.41
DHH036* | 3 | 900 | 85 | 67 | 85 | 36.4 | 0.73 | 27.04
DHH036* | 3 | 900 | 85 | 71 | 85 | 38.1 | 0.6 | 23.5
DHH036* | 3 | 900 | 85 | 59 | 95 | 33.3 | 0.95 | 31.95
DHH036* | 3 | 900 | 85 | 63 | 95 | 33.8 | 0.88 | 30.14
DHH036* | 3 | 900 | 85 | 67 | 95 | 34.8 | 0.76 | 26.77
DHH036* | 3 | 900 | 85 | 71 | 95 | 36.5 | 0.6 | 23.3
DHH036* | 3 | 900 | 85 | 59 | 105 | 31.3 | 1 | 31.63
DHH036* | 3 | 900 | 85 | 63 | 105 | 31.8 | 0.93 | 29.9
DHH036* | 3 | 900 | 85 | 67 | 105 | 32.9 | 0.8 | 26.53
DHH036* | 3 | 900 | 85 | 71 | 105 | 34.5 | 0.7 | 23
DHH036* | 3 | 900 | 85 | 59 | 115 | 29.5 | 1 | 29.83
DHH036* | 3 | 900 | 85 | 63 | 115 | 30 | 1 | 30.33
DHH036* | 3 | 900 | 85 | 67 | 115 | 31.1 | 0.88 | 27.66
DHH036* | 3 | 900 | 85 | 71 | 115 | 32.7 | 0.7 | 24.2
DHH036* | 3 | 1150 | 70 | 59 | 65 | 35.9 | 0.65 | 18.43
DHH036* | 3 | 1150 | 70 | 63 | 65 | 36.4 | 0.58 | 16.63
DHH036* | 3 | 1150 | 70 | 67 | 65 | 37.5 | 0.45 | 13.26
DHH036* | 3 | 1150 | 70 | 59 | 75 | 35.6 | 0.65 | 18.38
DHH036* | 3 | 1150 | 70 | 63 | 75 | 36.1 | 0.58 | 16.58
DHH036* | 3 | 1150 | 70 | 67 | 75 | 37.2 | 0.45 | 13.21
DHH036* | 3 | 1150 | 70 | 59 | 85 | 34.7 | 0.68 | 18.64
DHH036* | 3 | 1150 | 70 | 63 | 85 | 35.2 | 0.61 | 16.83
DHH036* | 3 | 1150 | 70 | 67 | 85 | 36.2 | 0.47 | 13.46
DHH036* | 3 | 1150 | 70 | 59 | 95 | 33.1 | 0.7 | 18.36
DHH036* | 3 | 1150 | 70 | 63 | 95 | 33.6 | 0.62 | 16.56
DHH036* | 3 | 1150 | 70 | 67 | 95 | 34.6 | 0.48 | 13.19
DHH036* | 3 | 1150 | 70 | 59 | 105 | 31.1 | 0.74 | 18.12
DHH036* | 3 | 1150 | 70 | 63 | 105 | 31.6 | 0.65 | 16.32
DHH036* | 3 | 1150 | 70 | 67 | 105 | 32.7 | 0.5 | 12.95
DHH036* | 3 | 1150 | 70 | 59 | 115 | 29.3 | 0.83 | 19.25
DHH036* | 3 | 1150 | 70 | 63 | 115 | 29.8 | 0.74 | 17.45
DHH036* | 3 | 1150 | 70 | 67 | 115 | 30.9 | 0.58 | 14.08
DHH036* | 3 | 1150 | 75 | 59 | 65 | 36.1 | 0.79 | 22.4
DHH036* | 3 | 1150 | 75 | 63 | 65 | 36.6 | 0.71 | 20.6
DHH036* | 3 | 1150 | 75 | 67 | 65 | 37.7 | 0.58 | 17.23
DHH036* | 3 | 1150 | 75 | 71 | 65 | 39.3 | 0.4 | 13.7
DHH036* | 3 | 1150 | 75 | 59 | 75 | 35.8 | 0.79 | 22.35
DHH036* | 3 | 1150 | 75 | 63 | 75 | 36.3 | 0.72 | 20.55
DHH036* | 3 | 1150 | 75 | 67 | 75 | 37.3 | 0.58 | 17.18
DHH036* | 3 | 1150 | 75 | 71 | 75 | 39 | 0.4 | 13.7
DHH036* | 3 | 1150 | 75 | 59 | 85 | 34.8 | 0.82 | 22.61
DHH036* | 3 | 1150 | 75 | 63 | 85 | 35.4 | 0.74 | 20.8
DHH036* | 3 | 1150 | 75 | 67 | 85 | 36.4 | 0.61 | 17.43
DHH036* | 3 | 1150 | 75 | 71 | 85 | 38 | 0.5 | 13.9
DHH036* | 3 | 1150 | 75 | 59 | 95 | 33.2 | 0.85 | 22.33
DHH036* | 3 | 1150 | 75 | 63 | 95 | 33.8 | 0.77 | 20.53
DHH036* | 3 | 1150 | 75 | 67 | 95 | 34.8 | 0.62 | 17.16
DHH036* | 3 | 1150 | 75 | 71 | 95 | 36.4 | 0.5 | 13.7
DHH036* | 3 | 1150 | 75 | 59 | 105 | 31.3 | 0.89 | 22.09
DHH036* | 3 | 1150 | 75 | 63 | 105 | 31.8 | 0.81 | 20.29
DHH036* | 3 | 1150 | 75 | 67 | 105 | 32.9 | 0.65 | 16.92
DHH036* | 3 | 1150 | 75 | 71 | 105 | 34.5 | 0.5 | 13.4
DHH036* | 3 | 1150 | 75 | 59 | 115 | 29.5 | 1 | 23.22
DHH036* | 3 | 1150 | 75 | 63 | 115 | 30 | 0.9 | 21.42
DHH036* | 3 | 1150 | 75 | 67 | 115 | 31.1 | 0.73 | 18.05
DHH036* | 3 | 1150 | 75 | 71 | 115 | 32.7 | 0.6 | 14.6
DHH036* | 3 | 1150 | 80 | 59 | 65 | 36.3 | 0.92 | 26.4
DHH036* | 3 | 1150 | 80 | 63 | 65 | 36.8 | 0.85 | 24.59
DHH036* | 3 | 1150 | 80 | 67 | 65 | 37.8 | 0.71 | 21.22
DHH036* | 3 | 1150 | 80 | 71 | 65 | 39.5 | 0.6 | 17.7
DHH036* | 3 | 1150 | 80 | 59 | 75 | 36 | 0.93 | 26.35
DHH036* | 3 | 1150 | 80 | 63 | 75 | 36.5 | 0.85 | 24.54
DHH036* | 3 | 1150 | 80 | 67 | 75 | 37.5 | 0.71 | 21.17
DHH036* | 3 | 1150 | 80 | 71 | 75 | 39.2 | 0.6 | 17.7
DHH036* | 3 | 1150 | 80 | 59 | 85 | 35 | 0.96 | 26.6
DHH036* | 3 | 1150 | 80 | 63 | 85 | 35.5 | 0.88 | 24.8
DHH036* | 3 | 1150 | 80 | 67 | 85 | 36.6 | 0.74 | 21.43
DHH036* | 3 | 1150 | 80 | 71 | 85 | 38.2 | 0.6 | 17.9
DHH036* | 3 | 1150 | 80 | 59 | 95 | 33.4 | 1 | 26.33
DHH036* | 3 | 1150 | 80 | 63 | 95 | 33.9 | 0.91 | 24.53
DHH036* | 3 | 1150 | 80 | 67 | 95 | 35 | 0.76 | 21.15
DHH036* | 3 | 1150 | 80 | 71 | 95 | 36.6 | 0.6 | 17.7
DHH036* | 3 | 1150 | 80 | 59 | 105 | 31.5 | 1 | 24.88
DHH036* | 3 | 1150 | 80 | 63 | 105 | 32 | 0.96 | 24.28
DHH036* | 3 | 1150 | 80 | 67 | 105 | 33 | 0.8 | 20.91
DHH036* | 3 | 1150 | 80 | 71 | 105 | 34.7 | 0.6 | 17.4
DHH036* | 3 | 1150 | 80 | 59 | 115 | 29.7 | 1 | 23.47
DHH036* | 3 | 1150 | 80 | 63 | 115 | 30.2 | 1 | 23.87
DHH036* | 3 | 1150 | 80 | 67 | 115 | 31.3 | 0.89 | 22.04
DHH036* | 3 | 1150 | 80 | 71 | 115 | 32.9 | 0.7 | 18.6
DHH036* | 3 | 1150 | 85 | 59 | 65 | 36.9 | 1 | 29.16
DHH036* | 3 | 1150 | 85 | 63 | 65 | 37.4 | 0.95 | 28.14
DHH036* | 3 | 1150 | 85 | 67 | 65 | 38.4 | 0.81 | 24.77
DHH036* | 3 | 1150 | 85 | 71 | 65 | 40.1 | 0.7 | 21.3
DHH036* | 3 | 1150 | 85 | 59 | 75 | 36.6 | 1 | 28.9
DHH036* | 3 | 1150 | 85 | 63 | 75 | 37.1 | 0.96 | 28.09
DHH036* | 3 | 1150 | 85 | 67 | 75 | 38.1 | 0.82 | 24.72
DHH036* | 3 | 1150 | 85 | 71 | 75 | 39.8 | 0.7 | 21.2
DHH036* | 3 | 1150 | 85 | 59 | 85 | 35.6 | 1 | 28.17
DHH036* | 3 | 1150 | 85 | 63 | 85 | 36.1 | 0.99 | 28.34
DHH036* | 3 | 1150 | 85 | 67 | 85 | 37.2 | 0.85 | 24.97
DHH036* | 3 | 1150 | 85 | 71 | 85 | 38.8 | 0.7 | 21.5
DHH036* | 3 | 1150 | 85 | 59 | 95 | 34 | 1 | 26.9
DHH036* | 3 | 1150 | 85 | 63 | 95 | 34.5 | 1 | 27.3
DHH036* | 3 | 1150 | 85 | 67 | 95 | 35.6 | 0.88 | 24.7
DHH036* | 3 | 1150 | 85 | 71 | 95 | 37.2 | 0.7 | 21.2
DHH036* | 3 | 1150 | 85 | 59 | 105 | 32.1 | 1 | 25.36
DHH036* | 3 | 1150 | 85 | 63 | 105 | 32.6 | 1 | 25.76
DHH036* | 3 | 1150 | 85 | 67 | 105 | 33.6 | 0.92 | 24.46
DHH036* | 3 | 1150 | 85 | 71 | 105 | 35.3 | 0.8 | 21
DHH036* | 3 | 1150 | 85 | 59 | 115 | 30.3 | 1 | 23.95
DHH036* | 3 | 1150 | 85 | 63 | 115 | 30.8 | 1 | 24.34
DHH036* | 3 | 1150 | 85 | 67 | 115 | 31.9 | 1 | 25.19
DHH036* | 3 | 1150 | 85 | 71 | 115 | 33.5 | 0.8 | 22.1
DHH036* | 3 | 1500 | 70 | 59 | 65 | 37.5 | 0.72 | 16.37
DHH036* | 3 | 1500 | 70 | 63 | 65 | 38 | 0.63 | 14.56
DHH036* | 3 | 1500 | 70 | 67 | 65 | 39 | 0.47 | 11.19
DHH036* | 3 | 1500 | 70 | 59 | 75 | 37.2 | 0.72 | 16.32
DHH036* | 3 | 1500 | 70 | 63 | 75 | 37.7 | 0.64 | 14.51
DHH036* | 3 | 1500 | 70 | 67 | 75 | 38.7 | 0.47 | 11.14
DHH036* | 3 | 1500 | 70 | 59 | 85 | 36.2 | 0.75 | 16.57
DHH036* | 3 | 1500 | 70 | 63 | 85 | 36.7 | 0.66 | 14.77
DHH036* | 3 | 1500 | 70 | 67 | 85 | 37.8 | 0.5 | 11.39
DHH036* | 3 | 1500 | 70 | 59 | 95 | 34.6 | 0.78 | 16.3
DHH036* | 3 | 1500 | 70 | 63 | 95 | 35.1 | 0.68 | 14.49
DHH036* | 3 | 1500 | 70 | 67 | 95 | 36.2 | 0.51 | 11.12
DHH036* | 3 | 1500 | 70 | 59 | 105 | 32.7 | 0.81 | 16.06
DHH036* | 3 | 1500 | 70 | 63 | 105 | 33.2 | 0.71 | 14.25
DHH036* | 3 | 1500 | 70 | 67 | 105 | 34.2 | 0.52 | 10.88
DHH036* | 3 | 1500 | 70 | 59 | 115 | 30.9 | 0.92 | 17.19
DHH036* | 3 | 1500 | 70 | 63 | 115 | 31.4 | 0.81 | 15.38
DHH036* | 3 | 1500 | 70 | 67 | 115 | 32.5 | 0.61 | 12.01
DHH036* | 3 | 1500 | 75 | 59 | 65 | 37.7 | 0.89 | 20.34
DHH036* | 3 | 1500 | 75 | 63 | 65 | 38.2 | 0.8 | 18.53
DHH036* | 3 | 1500 | 75 | 67 | 65 | 39.2 | 0.64 | 15.16
DHH036* | 3 | 1500 | 75 | 71 | 65 | 40.9 | 0.5 | 11.7
DHH036* | 3 | 1500 | 75 | 59 | 75 | 37.3 | 0.9 | 20.29
DHH036* | 3 | 1500 | 75 | 63 | 75 | 37.9 | 0.81 | 18.48
DHH036* | 3 | 1500 | 75 | 67 | 75 | 38.9 | 0.64 | 15.11
DHH036* | 3 | 1500 | 75 | 71 | 75 | 40.5 | 0.5 | 11.6
DHH036* | 3 | 1500 | 75 | 59 | 85 | 36.4 | 0.93 | 20.54
DHH036* | 3 | 1500 | 75 | 63 | 85 | 36.9 | 0.84 | 18.74
DHH036* | 3 | 1500 | 75 | 67 | 85 | 38 | 0.67 | 15.36
DHH036* | 3 | 1500 | 75 | 71 | 85 | 39.6 | 0.5 | 11.9
DHH036* | 3 | 1500 | 75 | 59 | 95 | 34.8 | 0.96 | 20.27
DHH036* | 3 | 1500 | 75 | 63 | 95 | 35.3 | 0.86 | 18.46
DHH036* | 3 | 1500 | 75 | 67 | 95 | 36.4 | 0.68 | 15.09
DHH036* | 3 | 1500 | 75 | 71 | 95 | 38 | 0.5 | 11.6
DHH036* | 3 | 1500 | 75 | 59 | 105 | 32.9 | 1 | 19.92
DHH036* | 3 | 1500 | 75 | 63 | 105 | 33.4 | 0.9 | 18.22
DHH036* | 3 | 1500 | 75 | 67 | 105 | 34.4 | 0.71 | 14.85
DHH036* | 3 | 1500 | 75 | 71 | 105 | 36.1 | 0.5 | 11.4
DHH036* | 3 | 1500 | 75 | 59 | 115 | 31.1 | 1 | 18.84
DHH036* | 3 | 1500 | 75 | 63 | 115 | 31.6 | 1 | 19.14
DHH036* | 3 | 1500 | 75 | 67 | 115 | 32.6 | 0.81 | 15.98
DHH036* | 3 | 1500 | 75 | 71 | 115 | 34.3 | 0.6 | 12.5
DHH036* | 3 | 1500 | 80 | 59 | 65 | 37.9 | 1 | 22.94
DHH036* | 3 | 1500 | 80 | 63 | 65 | 38.4 | 0.97 | 22.53
DHH036* | 3 | 1500 | 80 | 67 | 65 | 39.4 | 0.8 | 19.16
DHH036* | 3 | 1500 | 80 | 71 | 65 | 41 | 0.6 | 15.7
DHH036* | 3 | 1500 | 80 | 59 | 75 | 37.5 | 1 | 22.75
DHH036* | 3 | 1500 | 80 | 63 | 75 | 38 | 0.98 | 22.48
DHH036* | 3 | 1500 | 80 | 67 | 75 | 39.1 | 0.81 | 19.11
DHH036* | 3 | 1500 | 80 | 71 | 75 | 40.7 | 0.6 | 15.6
DHH036* | 3 | 1500 | 80 | 59 | 85 | 36.6 | 1 | 22.18
DHH036* | 3 | 1500 | 80 | 63 | 85 | 37.1 | 1 | 22.49
DHH036* | 3 | 1500 | 80 | 67 | 85 | 38.2 | 0.84 | 19.36
DHH036* | 3 | 1500 | 80 | 71 | 85 | 39.8 | 0.7 | 15.9
DHH036* | 3 | 1500 | 80 | 59 | 95 | 35 | 1 | 21.21
DHH036* | 3 | 1500 | 80 | 63 | 95 | 35.5 | 1 | 21.52
DHH036* | 3 | 1500 | 80 | 67 | 95 | 36.6 | 0.86 | 19.09
DHH036* | 3 | 1500 | 80 | 71 | 95 | 38.2 | 0.7 | 15.6
DHH036* | 3 | 1500 | 80 | 59 | 105 | 33 | 1 | 20.03
DHH036* | 3 | 1500 | 80 | 63 | 105 | 33.6 | 1 | 20.33
DHH036* | 3 | 1500 | 80 | 67 | 105 | 34.6 | 0.9 | 18.85
DHH036* | 3 | 1500 | 80 | 71 | 105 | 36.2 | 0.7 | 15.4
DHH036* | 3 | 1500 | 80 | 59 | 115 | 31.3 | 1 | 18.95
DHH036* | 3 | 1500 | 80 | 63 | 115 | 31.8 | 1 | 19.25
DHH036* | 3 | 1500 | 80 | 67 | 115 | 32.8 | 1 | 19.9
DHH036* | 3 | 1500 | 80 | 71 | 115 | 34.5 | 0.8 | 16.5
DHH036* | 3 | 1500 | 85 | 59 | 65 | 38.5 | 1 | 23.3
DHH036* | 3 | 1500 | 85 | 63 | 65 | 39 | 1 | 23.61
DHH036* | 3 | 1500 | 85 | 67 | 65 | 40 | 0.94 | 22.7
DHH036* | 3 | 1500 | 85 | 71 | 65 | 41.6 | 0.8 | 19.2
DHH036* | 3 | 1500 | 85 | 59 | 75 | 38.1 | 1 | 23.11
DHH036* | 3 | 1500 | 85 | 63 | 75 | 38.6 | 1 | 23.42
DHH036* | 3 | 1500 | 85 | 67 | 75 | 39.7 | 0.94 | 22.65
DHH036* | 3 | 1500 | 85 | 71 | 75 | 41.3 | 0.8 | 19.2
DHH036* | 3 | 1500 | 85 | 59 | 85 | 37.2 | 1 | 22.55
DHH036* | 3 | 1500 | 85 | 63 | 85 | 37.7 | 1 | 22.85
DHH036* | 3 | 1500 | 85 | 67 | 85 | 38.8 | 0.97 | 22.91
DHH036* | 3 | 1500 | 85 | 71 | 85 | 40.4 | 0.8 | 19.4
DHH036* | 3 | 1500 | 85 | 59 | 95 | 35.6 | 1 | 21.58
DHH036* | 3 | 1500 | 85 | 63 | 95 | 36.1 | 1 | 21.88
DHH036* | 3 | 1500 | 85 | 67 | 95 | 37.2 | 1 | 22.53
DHH036* | 3 | 1500 | 85 | 71 | 95 | 38.8 | 0.8 | 19.1
DHH036* | 3 | 1500 | 85 | 59 | 105 | 33.6 | 1 | 20.39
DHH036* | 3 | 1500 | 85 | 63 | 105 | 34.2 | 1 | 20.7
DHH036* | 3 | 1500 | 85 | 67 | 105 | 35.2 | 1 | 21.34
DHH036* | 3 | 1500 | 85 | 71 | 105 | 36.8 | 0.8 | 18.9
DHH036* | 3 | 1500 | 85 | 59 | 115 | 31.9 | 1 | 19.31
DHH036* | 3 | 1500 | 85 | 63 | 115 | 32.4 | 1 | 19.62
DHH036* | 3 | 1500 | 85 | 67 | 115 | 33.4 | 1 | 20.26
DHH036* | 3 | 1500 | 85 | 71 | 115 | 35.1 | 0.9 | 20
DHH048* | 4 | 1200 | 70 | 59 | 65 | 48.391 | 0.58 | 21.26
DHH048* | 4 | 1200 | 70 | 63 | 65 | 49.08 | 0.52 | 19.39
DHH048* | 4 | 1200 | 70 | 67 | 65 | 50.539 | 0.42 | 15.92
DHH048* | 4 | 1200 | 70 | 59 | 75 | 47.953 | 0.58 | 21.21
DHH048* | 4 | 1200 | 70 | 63 | 75 | 48.643 | 0.52 | 19.34
DHH048* | 4 | 1200 | 70 | 67 | 75 | 50.102 | 0.42 | 15.86
DHH048* | 4 | 1200 | 70 | 59 | 85 | 46.678 | 0.61 | 21.47
DHH048* | 4 | 1200 | 70 | 63 | 85 | 47.368 | 0.55 | 19.61
DHH048* | 4 | 1200 | 70 | 67 | 85 | 48.827 | 0.44 | 16.13
DHH048* | 4 | 1200 | 70 | 59 | 95 | 44.484 | 0.63 | 21.19
DHH048* | 4 | 1200 | 70 | 63 | 95 | 45.174 | 0.56 | 19.32
DHH048* | 4 | 1200 | 70 | 67 | 95 | 46.633 | 0.45 | 15.85
DHH048* | 4 | 1200 | 70 | 59 | 105 | 41.803 | 0.66 | 20.94
DHH048* | 4 | 1200 | 70 | 63 | 105 | 42.493 | 0.59 | 19.08
DHH048* | 4 | 1200 | 70 | 67 | 105 | 43.951 | 0.47 | 15.6
DHH048* | 4 | 1200 | 70 | 59 | 115 | 39.355 | 0.74 | 22.1
DHH048* | 4 | 1200 | 70 | 63 | 115 | 40.045 | 0.67 | 20.24
DHH048* | 4 | 1200 | 70 | 67 | 115 | 41.504 | 0.53 | 16.76
DHH048* | 4 | 1200 | 75 | 59 | 65 | 48.4 | 0.69 | 25.35
DHH048* | 4 | 1200 | 75 | 63 | 65 | 49.1 | 0.63 | 23.49
DHH048* | 4 | 1200 | 75 | 67 | 65 | 50.6 | 0.52 | 20.01
DHH048* | 4 | 1200 | 75 | 71 | 65 | 52.8 | 0.4 | 16.4
DHH048* | 4 | 1200 | 75 | 59 | 75 | 48 | 0.7 | 25.3
DHH048* | 4 | 1200 | 75 | 63 | 75 | 48.7 | 0.64 | 23.44
DHH048* | 4 | 1200 | 75 | 67 | 75 | 50.1 | 0.53 | 19.96
DHH048* | 4 | 1200 | 75 | 71 | 75 | 52.4 | 0.4 | 16.4
DHH048* | 4 | 1200 | 75 | 59 | 85 | 46.7 | 0.72 | 25.56
DHH048* | 4 | 1200 | 75 | 63 | 85 | 47.4 | 0.66 | 23.7
DHH048* | 4 | 1200 | 75 | 67 | 85 | 48.9 | 0.55 | 20.22
DHH048* | 4 | 1200 | 75 | 71 | 85 | 51.1 | 0.4 | 16.6
DHH048* | 4 | 1200 | 75 | 59 | 95 | 44.5 | 0.75 | 25.28
DHH048* | 4 | 1200 | 75 | 63 | 95 | 45.2 | 0.68 | 23.42
DHH048* | 4 | 1200 | 75 | 67 | 95 | 46.7 | 0.56 | 19.94
DHH048* | 4 | 1200 | 75 | 71 | 95 | 48.9 | 0.4 | 16.3
DHH048* | 4 | 1200 | 75 | 59 | 105 | 41.8 | 0.79 | 25.03
DHH048* | 4 | 1200 | 75 | 63 | 105 | 42.5 | 0.72 | 23.17
DHH048* | 4 | 1200 | 75 | 67 | 105 | 44 | 0.59 | 19.69
DHH048* | 4 | 1200 | 75 | 71 | 105 | 46.2 | 0.5 | 16.1
DHH048* | 4 | 1200 | 75 | 59 | 115 | 39.4 | 0.88 | 26.2
DHH048* | 4 | 1200 | 75 | 63 | 115 | 40.1 | 0.8 | 24.34
DHH048* | 4 | 1200 | 75 | 67 | 115 | 41.5 | 0.66 | 20.86
DHH048* | 4 | 1200 | 75 | 71 | 115 | 43.8 | 0.5 | 17.3
DHH048* | 4 | 1200 | 80 | 59 | 65 | 48.7 | 0.8 | 29.48
DHH048* | 4 | 1200 | 80 | 63 | 65 | 49.4 | 0.74 | 27.61
DHH048* | 4 | 1200 | 80 | 67 | 65 | 50.8 | 0.63 | 24.14
DHH048* | 4 | 1200 | 80 | 71 | 65 | 53 | 0.5 | 20.5
DHH048* | 4 | 1200 | 80 | 59 | 75 | 48.2 | 0.81 | 29.43
DHH048* | 4 | 1200 | 80 | 63 | 75 | 48.9 | 0.74 | 27.56
DHH048* | 4 | 1200 | 80 | 67 | 75 | 50.4 | 0.63 | 24.09
DHH048* | 4 | 1200 | 80 | 71 | 75 | 52.6 | 0.5 | 20.5
DHH048* | 4 | 1200 | 80 | 59 | 85 | 47 | 0.83 | 29.69
DHH048* | 4 | 1200 | 80 | 63 | 85 | 47.6 | 0.77 | 27.83
DHH048* | 4 | 1200 | 80 | 67 | 85 | 49.1 | 0.65 | 24.35
DHH048* | 4 | 1200 | 80 | 71 | 85 | 51.3 | 0.5 | 20.7
DHH048* | 4 | 1200 | 80 | 59 | 95 | 44.8 | 0.87 | 29.41
DHH048* | 4 | 1200 | 80 | 63 | 95 | 45.5 | 0.8 | 27.54
DHH048* | 4 | 1200 | 80 | 67 | 95 | 46.9 | 0.68 | 24.07
DHH048* | 4 | 1200 | 80 | 71 | 95 | 49.1 | 0.5 | 20.5
DHH048* | 4 | 1200 | 80 | 59 | 105 | 42.1 | 0.91 | 29.16
DHH048* | 4 | 1200 | 80 | 63 | 105 | 42.8 | 0.84 | 27.3
DHH048* | 4 | 1200 | 80 | 67 | 105 | 44.2 | 0.71 | 23.82
DHH048* | 4 | 1200 | 80 | 71 | 105 | 46.5 | 0.6 | 20.2
DHH048* | 4 | 1200 | 80 | 59 | 115 | 39.6 | 1 | 30.03
DHH048* | 4 | 1200 | 80 | 63 | 115 | 40.3 | 0.93 | 28.46
DHH048* | 4 | 1200 | 80 | 67 | 115 | 41.8 | 0.79 | 24.98
DHH048* | 4 | 1200 | 80 | 71 | 115 | 44 | 0.6 | 21.4
DHH048* | 4 | 1200 | 85 | 59 | 65 | 49.5 | 0.88 | 33.13
DHH048* | 4 | 1200 | 85 | 63 | 65 | 50.2 | 0.82 | 31.27
DHH048* | 4 | 1200 | 85 | 67 | 65 | 51.6 | 0.71 | 27.79
DHH048* | 4 | 1200 | 85 | 71 | 65 | 53.9 | 0.6 | 24.2
DHH048* | 4 | 1200 | 85 | 59 | 75 | 49.1 | 0.89 | 33.08
DHH048* | 4 | 1200 | 85 | 63 | 75 | 49.7 | 0.83 | 31.22
DHH048* | 4 | 1200 | 85 | 67 | 75 | 51.2 | 0.72 | 27.74
DHH048* | 4 | 1200 | 85 | 71 | 75 | 53.4 | 0.6 | 24.1
DHH048* | 4 | 1200 | 85 | 59 | 85 | 47.8 | 0.92 | 33.35
DHH048* | 4 | 1200 | 85 | 63 | 85 | 48.5 | 0.86 | 31.48
DHH048* | 4 | 1200 | 85 | 67 | 85 | 49.9 | 0.74 | 28
DHH048* | 4 | 1200 | 85 | 71 | 85 | 52.2 | 0.6 | 24.4
DHH048* | 4 | 1200 | 85 | 59 | 95 | 45.6 | 0.96 | 33.06
DHH048* | 4 | 1200 | 85 | 63 | 95 | 46.3 | 0.89 | 31.2
DHH048* | 4 | 1200 | 85 | 67 | 95 | 47.7 | 0.77 | 27.72
DHH048* | 4 | 1200 | 85 | 71 | 95 | 50 | 0.6 | 24.1
DHH048* | 4 | 1200 | 85 | 59 | 105 | 42.9 | 1 | 32.51
DHH048* | 4 | 1200 | 85 | 63 | 105 | 43.6 | 0.94 | 30.95
DHH048* | 4 | 1200 | 85 | 67 | 105 | 45.1 | 0.8 | 27.47
DHH048* | 4 | 1200 | 85 | 71 | 105 | 47.3 | 0.7 | 23.9
DHH048* | 4 | 1200 | 85 | 59 | 115 | 40.5 | 1 | 30.65
DHH048* | 4 | 1200 | 85 | 63 | 115 | 41.1 | 1 | 31.17
DHH048* | 4 | 1200 | 85 | 67 | 115 | 42.6 | 0.89 | 28.64
DHH048* | 4 | 1200 | 85 | 71 | 115 | 44.8 | 0.7 | 25
DHH048* | 4 | 1550 | 70 | 59 | 65 | 49.476 | 0.66 | 19.02
DHH048* | 4 | 1550 | 70 | 63 | 65 | 50.166 | 0.58 | 17.16
DHH048* | 4 | 1550 | 70 | 67 | 65 | 51.625 | 0.45 | 13.68
DHH048* | 4 | 1550 | 70 | 59 | 75 | 49.039 | 0.66 | 18.97
DHH048* | 4 | 1550 | 70 | 63 | 75 | 49.729 | 0.59 | 17.11
DHH048* | 4 | 1550 | 70 | 67 | 75 | 51.187 | 0.45 | 13.63
DHH048* | 4 | 1550 | 70 | 59 | 85 | 47.764 | 0.69 | 19.23
DHH048* | 4 | 1550 | 70 | 63 | 85 | 48.453 | 0.61 | 17.37
DHH048* | 4 | 1550 | 70 | 67 | 85 | 49.912 | 0.47 | 13.89
DHH048* | 4 | 1550 | 70 | 59 | 95 | 45.57 | 0.71 | 18.95
DHH048* | 4 | 1550 | 70 | 63 | 95 | 46.259 | 0.63 | 17.09
DHH048* | 4 | 1550 | 70 | 67 | 95 | 47.718 | 0.49 | 13.61
DHH048* | 4 | 1550 | 70 | 59 | 105 | 42.888 | 0.74 | 18.7
DHH048* | 4 | 1550 | 70 | 63 | 105 | 43.578 | 0.66 | 16.84
DHH048* | 4 | 1550 | 70 | 67 | 105 | 45.037 | 0.51 | 13.36
DHH048* | 4 | 1550 | 70 | 59 | 115 | 40.441 | 0.84 | 19.87
DHH048* | 4 | 1550 | 70 | 63 | 115 | 41.13 | 0.75 | 18
DHH048* | 4 | 1550 | 70 | 67 | 115 | 42.589 | 0.58 | 14.52
DHH048* | 4 | 1550 | 75 | 59 | 65 | 49.5 | 0.8 | 23.12
DHH048* | 4 | 1550 | 75 | 63 | 65 | 50.2 | 0.72 | 21.25
DHH048* | 4 | 1550 | 75 | 67 | 65 | 51.7 | 0.59 | 17.77
DHH048* | 4 | 1550 | 75 | 71 | 65 | 53.9 | 0.4 | 14.2
DHH048* | 4 | 1550 | 75 | 59 | 75 | 49.1 | 0.8 | 23.06
DHH048* | 4 | 1550 | 75 | 63 | 75 | 49.8 | 0.73 | 21.2
DHH048* | 4 | 1550 | 75 | 67 | 75 | 51.2 | 0.59 | 17.72
DHH048* | 4 | 1550 | 75 | 71 | 75 | 53.4 | 0.5 | 14.1
DHH048* | 4 | 1550 | 75 | 59 | 85 | 47.8 | 0.83 | 23.33
DHH048* | 4 | 1550 | 75 | 63 | 85 | 48.5 | 0.75 | 21.46
DHH048* | 4 | 1550 | 75 | 67 | 85 | 49.9 | 0.61 | 17.98
DHH048* | 4 | 1550 | 75 | 71 | 85 | 52.2 | 0.5 | 14.4
DHH048* | 4 | 1550 | 75 | 59 | 95 | 45.6 | 0.86 | 23.05
DHH048* | 4 | 1550 | 75 | 63 | 95 | 46.3 | 0.78 | 21.18
DHH048* | 4 | 1550 | 75 | 67 | 95 | 47.7 | 0.63 | 17.7
DHH048* | 4 | 1550 | 75 | 71 | 95 | 50 | 0.5 | 14.1
DHH048* | 4 | 1550 | 75 | 59 | 105 | 42.9 | 0.91 | 22.8
DHH048* | 4 | 1550 | 75 | 63 | 105 | 43.6 | 0.82 | 20.93
DHH048* | 4 | 1550 | 75 | 67 | 105 | 45.1 | 0.66 | 17.45
DHH048* | 4 | 1550 | 75 | 71 | 105 | 47.3 | 0.5 | 13.9
DHH048* | 4 | 1550 | 75 | 59 | 115 | 40.5 | 1 | 23.74
DHH048* | 4 | 1550 | 75 | 63 | 115 | 41.2 | 0.92 | 22.1
DHH048* | 4 | 1550 | 75 | 67 | 115 | 42.6 | 0.74 | 18.62
DHH048* | 4 | 1550 | 75 | 71 | 115 | 44.8 | 0.6 | 15
DHH048* | 4 | 1550 | 80 | 59 | 65 | 49.8 | 0.93 | 27.24
DHH048* | 4 | 1550 | 80 | 63 | 65 | 50.4 | 0.86 | 25.38
DHH048* | 4 | 1550 | 80 | 67 | 65 | 51.9 | 0.72 | 21.9
DHH048* | 4 | 1550 | 80 | 71 | 65 | 54.1 | 0.6 | 18.3
DHH048* | 4 | 1550 | 80 | 59 | 75 | 49.3 | 0.94 | 27.19
DHH048* | 4 | 1550 | 80 | 63 | 75 | 50 | 0.86 | 25.33
DHH048* | 4 | 1550 | 80 | 67 | 75 | 51.5 | 0.72 | 21.85
DHH048* | 4 | 1550 | 80 | 71 | 75 | 53.7 | 0.6 | 18.2
DHH048* | 4 | 1550 | 80 | 59 | 85 | 48 | 0.97 | 27.45
DHH048* | 4 | 1550 | 80 | 63 | 85 | 48.7 | 0.9 | 25.59
DHH048* | 4 | 1550 | 80 | 67 | 85 | 50.2 | 0.75 | 22.11
DHH048* | 4 | 1550 | 80 | 71 | 85 | 52.4 | 0.6 | 18.5
DHH048* | 4 | 1550 | 80 | 59 | 95 | 45.9 | 1 | 26.89
DHH048* | 4 | 1550 | 80 | 63 | 95 | 46.5 | 0.93 | 25.31
DHH048* | 4 | 1550 | 80 | 67 | 95 | 48 | 0.78 | 21.83
DHH048* | 4 | 1550 | 80 | 71 | 95 | 50.2 | 0.6 | 18.2
DHH048* | 4 | 1550 | 80 | 59 | 105 | 43.2 | 1 | 25.32
DHH048* | 4 | 1550 | 80 | 63 | 105 | 43.9 | 0.97 | 25.06
DHH048* | 4 | 1550 | 80 | 67 | 105 | 45.3 | 0.81 | 21.58
DHH048* | 4 | 1550 | 80 | 71 | 105 | 47.5 | 0.6 | 18
DHH048* | 4 | 1550 | 80 | 59 | 115 | 40.7 | 1 | 23.88
DHH048* | 4 | 1550 | 80 | 63 | 115 | 41.4 | 1 | 24.29
DHH048* | 4 | 1550 | 80 | 67 | 115 | 42.9 | 0.9 | 22.75
DHH048* | 4 | 1550 | 80 | 71 | 115 | 45.1 | 0.7 | 19.1
DHH048* | 4 | 1550 | 85 | 59 | 65 | 50.6 | 1 | 29.67
DHH048* | 4 | 1550 | 85 | 63 | 65 | 51.3 | 0.97 | 29.03
DHH048* | 4 | 1550 | 85 | 67 | 65 | 52.7 | 0.83 | 25.56
DHH048* | 4 | 1550 | 85 | 71 | 65 | 55 | 0.7 | 22
DHH048* | 4 | 1550 | 85 | 59 | 75 | 50.1 | 1 | 29.41
DHH048* | 4 | 1550 | 85 | 63 | 75 | 50.8 | 0.97 | 28.98
DHH048* | 4 | 1550 | 85 | 67 | 75 | 52.3 | 0.83 | 25.5
DHH048* | 4 | 1550 | 85 | 71 | 75 | 54.5 | 0.7 | 21.9
DHH048* | 4 | 1550 | 85 | 59 | 85 | 48.9 | 1 | 28.66
DHH048* | 4 | 1550 | 85 | 63 | 85 | 49.6 | 1 | 29.07
DHH048* | 4 | 1550 | 85 | 67 | 85 | 51 | 0.86 | 25.77
DHH048* | 4 | 1550 | 85 | 71 | 85 | 53.2 | 0.7 | 22.2
DHH048* | 4 | 1550 | 85 | 59 | 95 | 46.7 | 1 | 27.37
DHH048* | 4 | 1550 | 85 | 63 | 95 | 47.4 | 1 | 27.78
DHH048* | 4 | 1550 | 85 | 67 | 95 | 48.8 | 0.89 | 25.49
DHH048* | 4 | 1550 | 85 | 71 | 95 | 51.1 | 0.7 | 21.9
DHH048* | 4 | 1550 | 85 | 59 | 105 | 44 | 1 | 25.8
DHH048* | 4 | 1550 | 85 | 63 | 105 | 44.7 | 1 | 26.21
DHH048* | 4 | 1550 | 85 | 67 | 105 | 46.1 | 0.93 | 25.24
DHH048* | 4 | 1550 | 85 | 71 | 105 | 48.4 | 0.8 | 21.6
DHH048* | 4 | 1550 | 85 | 59 | 115 | 41.5 | 1 | 24.37
DHH048* | 4 | 1550 | 85 | 63 | 115 | 42.2 | 1 | 24.77
DHH048* | 4 | 1550 | 85 | 67 | 115 | 43.7 | 1 | 25.63
DHH048* | 4 | 1550 | 85 | 71 | 115 | 45.9 | 0.8 | 22.8
DHH048* | 4 | 2000 | 70 | 59 | 65 | 51.508 | 0.72 | 16.97
DHH048* | 4 | 2000 | 70 | 63 | 65 | 52.197 | 0.64 | 15.11
DHH048* | 4 | 2000 | 70 | 67 | 65 | 53.656 | 0.48 | 11.63
DHH048* | 4 | 2000 | 70 | 59 | 75 | 51.07 | 0.73 | 16.92
DHH048* | 4 | 2000 | 70 | 63 | 75 | 51.76 | 0.64 | 15.06
DHH048* | 4 | 2000 | 70 | 67 | 75 | 53.219 | 0.48 | 11.58
DHH048* | 4 | 2000 | 70 | 59 | 85 | 49.795 | 0.76 | 17.19
DHH048* | 4 | 2000 | 70 | 63 | 85 | 50.485 | 0.67 | 15.32
DHH048* | 4 | 2000 | 70 | 67 | 85 | 51.944 | 0.5 | 11.84
DHH048* | 4 | 2000 | 70 | 59 | 95 | 47.601 | 0.78 | 16.9
DHH048* | 4 | 2000 | 70 | 63 | 95 | 48.291 | 0.69 | 15.04
DHH048* | 4 | 2000 | 70 | 67 | 95 | 49.75 | 0.51 | 11.56
DHH048* | 4 | 2000 | 70 | 59 | 105 | 44.92 | 0.82 | 16.66
DHH048* | 4 | 2000 | 70 | 63 | 105 | 45.61 | 0.71 | 14.79
DHH048* | 4 | 2000 | 70 | 67 | 105 | 47.068 | 0.53 | 11.31
DHH048* | 4 | 2000 | 70 | 59 | 115 | 42.472 | 0.92 | 17.82
DHH048* | 4 | 2000 | 70 | 63 | 115 | 43.162 | 0.81 | 15.96
DHH048* | 4 | 2000 | 70 | 67 | 115 | 44.621 | 0.62 | 12.48
DHH048* | 4 | 2000 | 75 | 59 | 65 | 51.5 | 0.9 | 21.07
DHH048* | 4 | 2000 | 75 | 63 | 65 | 52.2 | 0.81 | 19.21
DHH048* | 4 | 2000 | 75 | 67 | 65 | 53.7 | 0.64 | 15.73
DHH048* | 4 | 2000 | 75 | 71 | 65 | 55.9 | 0.5 | 12.1
DHH048* | 4 | 2000 | 75 | 59 | 75 | 51.1 | 0.9 | 21.02
DHH048* | 4 | 2000 | 75 | 63 | 75 | 51.8 | 0.81 | 19.16
DHH048* | 4 | 2000 | 75 | 67 | 75 | 53.2 | 0.65 | 15.68
DHH048* | 4 | 2000 | 75 | 71 | 75 | 55.5 | 0.5 | 12.1
DHH048* | 4 | 2000 | 75 | 59 | 85 | 49.8 | 0.94 | 21.28
DHH048* | 4 | 2000 | 75 | 63 | 85 | 50.5 | 0.85 | 19.42
DHH048* | 4 | 2000 | 75 | 67 | 85 | 52 | 0.67 | 15.94
DHH048* | 4 | 2000 | 75 | 71 | 85 | 54.2 | 0.5 | 12.3
DHH048* | 4 | 2000 | 75 | 59 | 95 | 47.6 | 0.97 | 21
DHH048* | 4 | 2000 | 75 | 63 | 95 | 48.3 | 0.87 | 19.14
DHH048* | 4 | 2000 | 75 | 67 | 95 | 49.8 | 0.69 | 15.66
DHH048* | 4 | 2000 | 75 | 71 | 95 | 52 | 0.5 | 12.1
DHH048* | 4 | 2000 | 75 | 59 | 105 | 44.9 | 1 | 20.43
DHH048* | 4 | 2000 | 75 | 63 | 105 | 45.6 | 0.91 | 18.89
DHH048* | 4 | 2000 | 75 | 67 | 105 | 47.1 | 0.72 | 15.41
DHH048* | 4 | 2000 | 75 | 71 | 105 | 49.3 | 0.5 | 11.8
DHH048* | 4 | 2000 | 75 | 59 | 115 | 42.5 | 1 | 19.32
DHH048* | 4 | 2000 | 75 | 63 | 115 | 43.2 | 1 | 19.63
DHH048* | 4 | 2000 | 75 | 67 | 115 | 44.6 | 0.82 | 16.58
DHH048* | 4 | 2000 | 75 | 71 | 115 | 46.9 | 0.6 | 13
DHH048* | 4 | 2000 | 80 | 59 | 65 | 51.8 | 1 | 23.54
DHH048* | 4 | 2000 | 80 | 63 | 65 | 52.5 | 0.98 | 23.33
DHH048* | 4 | 2000 | 80 | 67 | 65 | 53.9 | 0.81 | 19.85
DHH048* | 4 | 2000 | 80 | 71 | 65 | 56.2 | 0.6 | 16.2
DHH048* | 4 | 2000 | 80 | 59 | 75 | 51.4 | 1 | 23.34
DHH048* | 4 | 2000 | 80 | 63 | 75 | 52 | 0.98 | 23.28
DHH048* | 4 | 2000 | 80 | 67 | 75 | 53.5 | 0.81 | 19.8
DHH048* | 4 | 2000 | 80 | 71 | 75 | 55.7 | 0.6 | 16.2
DHH048* | 4 | 2000 | 80 | 59 | 85 | 50.1 | 1 | 22.76
DHH048* | 4 | 2000 | 80 | 63 | 85 | 50.8 | 1 | 23.08
DHH048* | 4 | 2000 | 80 | 67 | 85 | 52.2 | 0.85 | 20.06
DHH048* | 4 | 2000 | 80 | 71 | 85 | 54.5 | 0.7 | 16.5
DHH048* | 4 | 2000 | 80 | 59 | 95 | 47.9 | 1 | 21.76
DHH048* | 4 | 2000 | 80 | 63 | 95 | 48.6 | 1 | 22.08
DHH048* | 4 | 2000 | 80 | 67 | 95 | 50 | 0.87 | 19.78
DHH048* | 4 | 2000 | 80 | 71 | 95 | 52.3 | 0.7 | 16.2
DHH048* | 4 | 2000 | 80 | 59 | 105 | 45.2 | 1 | 20.55
DHH048* | 4 | 2000 | 80 | 63 | 105 | 45.9 | 1 | 20.86
DHH048* | 4 | 2000 | 80 | 67 | 105 | 47.3 | 0.91 | 19.53
DHH048* | 4 | 2000 | 80 | 71 | 105 | 49.6 | 0.7 | 15.9
DHH048* | 4 | 2000 | 80 | 59 | 115 | 42.8 | 1 | 19.43
DHH048* | 4 | 2000 | 80 | 63 | 115 | 43.4 | 1 | 19.75
DHH048* | 4 | 2000 | 80 | 67 | 115 | 44.9 | 1 | 20.41
DHH048* | 4 | 2000 | 80 | 71 | 115 | 47.1 | 0.8 | 17.1
DHH048* | 4 | 2000 | 85 | 59 | 65 | 52.6 | 1 | 23.91
DHH048* | 4 | 2000 | 85 | 63 | 65 | 53.3 | 1 | 24.23
DHH048* | 4 | 2000 | 85 | 67 | 65 | 54.8 | 0.94 | 23.51
DHH048* | 4 | 2000 | 85 | 71 | 65 | 57 | 0.8 | 19.9
DHH048* | 4 | 2000 | 85 | 59 | 75 | 52.2 | 1 | 23.72
DHH048* | 4 | 2000 | 85 | 63 | 75 | 52.9 | 1 | 24.03
DHH048* | 4 | 2000 | 85 | 67 | 75 | 54.3 | 0.95 | 23.46
DHH048* | 4 | 2000 | 85 | 71 | 75 | 56.6 | 0.8 | 19.9
DHH048* | 4 | 2000 | 85 | 59 | 85 | 50.9 | 1 | 23.14
DHH048* | 4 | 2000 | 85 | 63 | 85 | 51.6 | 1 | 23.45
DHH048* | 4 | 2000 | 85 | 67 | 85 | 53 | 0.98 | 23.72
DHH048* | 4 | 2000 | 85 | 71 | 85 | 55.3 | 0.8 | 20.1
DHH048* | 4 | 2000 | 85 | 59 | 95 | 48.7 | 1 | 22.14
DHH048* | 4 | 2000 | 85 | 63 | 95 | 49.4 | 1 | 22.45
DHH048* | 4 | 2000 | 85 | 67 | 95 | 50.9 | 1 | 23.12
DHH048* | 4 | 2000 | 85 | 71 | 95 | 53.1 | 0.8 | 19.8
DHH048* | 4 | 2000 | 85 | 59 | 105 | 46 | 1 | 20.92
DHH048* | 4 | 2000 | 85 | 63 | 105 | 46.7 | 1 | 21.23
DHH048* | 4 | 2000 | 85 | 67 | 105 | 48.2 | 1 | 21.9
DHH048* | 4 | 2000 | 85 | 71 | 105 | 50.4 | 0.9 | 19.6
DHH048* | 4 | 2000 | 85 | 59 | 115 | 43.6 | 1 | 19.81
DHH048* | 4 | 2000 | 85 | 63 | 115 | 44.3 | 1 | 20.12
DHH048* | 4 | 2000 | 85 | 67 | 115 | 45.7 | 1 | 20.78
DHH048* | 4 | 2000 | 85 | 71 | 115 | 48 | 1 | 20.8
DHH060* | 5 | 1500 | 70 | 59 | 65 | 60.2 | 0.57 | 20.93
DHH060* | 5 | 1500 | 70 | 63 | 65 | 61 | 0.52 | 19.1
DHH060* | 5 | 1500 | 70 | 67 | 65 | 62.9 | 0.41 | 15.68
DHH060* | 5 | 1500 | 70 | 59 | 75 | 59.6 | 0.58 | 20.88
DHH060* | 5 | 1500 | 70 | 63 | 75 | 60.5 | 0.52 | 19.05
DHH060* | 5 | 1500 | 70 | 67 | 75 | 62.3 | 0.41 | 15.63
DHH060* | 5 | 1500 | 70 | 59 | 85 | 58 | 0.6 | 21.13
DHH060* | 5 | 1500 | 70 | 63 | 85 | 58.9 | 0.54 | 19.3
DHH060* | 5 | 1500 | 70 | 67 | 85 | 60.7 | 0.43 | 15.89
DHH060* | 5 | 1500 | 70 | 59 | 95 | 55.3 | 0.62 | 20.86
DHH060* | 5 | 1500 | 70 | 63 | 95 | 56.2 | 0.56 | 19.03
DHH060* | 5 | 1500 | 70 | 67 | 95 | 58 | 0.44 | 15.61
DHH060* | 5 | 1500 | 70 | 59 | 105 | 51.9 | 0.65 | 20.61
DHH060* | 5 | 1500 | 70 | 63 | 105 | 52.8 | 0.59 | 18.78
DHH060* | 5 | 1500 | 70 | 67 | 105 | 54.6 | 0.46 | 15.37
DHH060* | 5 | 1500 | 70 | 59 | 115 | 48.9 | 0.73 | 21.76
DHH060* | 5 | 1500 | 70 | 63 | 115 | 49.7 | 0.66 | 19.93
DHH060* | 5 | 1500 | 70 | 67 | 115 | 51.6 | 0.53 | 16.51
DHH060* | 5 | 1500 | 75 | 59 | 65 | 60.5 | 0.68 | 24.95
DHH060* | 5 | 1500 | 75 | 63 | 65 | 61.4 | 0.62 | 23.12
DHH060* | 5 | 1500 | 75 | 67 | 65 | 63.2 | 0.51 | 19.7
DHH060* | 5 | 1500 | 75 | 71 | 65 | 66 | 0.4 | 16.2
DHH060* | 5 | 1500 | 75 | 59 | 75 | 60 | 0.69 | 24.9
DHH060* | 5 | 1500 | 75 | 63 | 75 | 60.8 | 0.63 | 23.07
DHH060* | 5 | 1500 | 75 | 67 | 75 | 62.6 | 0.52 | 19.65
DHH060* | 5 | 1500 | 75 | 71 | 75 | 65.4 | 0.4 | 16.1
DHH060* | 5 | 1500 | 75 | 59 | 85 | 58.4 | 0.71 | 25.15
DHH060* | 5 | 1500 | 75 | 63 | 85 | 59.2 | 0.65 | 23.33
DHH060* | 5 | 1500 | 75 | 67 | 85 | 61 | 0.54 | 19.91
DHH060* | 5 | 1500 | 75 | 71 | 85 | 63.8 | 0.4 | 16.4
DHH060* | 5 | 1500 | 75 | 59 | 95 | 55.6 | 0.74 | 24.88
DHH060* | 5 | 1500 | 75 | 63 | 95 | 56.5 | 0.67 | 23.05
DHH060* | 5 | 1500 | 75 | 67 | 95 | 58.3 | 0.56 | 19.63
DHH060* | 5 | 1500 | 75 | 71 | 95 | 61.1 | 0.4 | 16.1
DHH060* | 5 | 1500 | 75 | 59 | 105 | 52.3 | 0.78 | 24.63
DHH060* | 5 | 1500 | 75 | 63 | 105 | 53.1 | 0.71 | 22.8
DHH060* | 5 | 1500 | 75 | 67 | 105 | 54.9 | 0.58 | 19.39
DHH060* | 5 | 1500 | 75 | 71 | 105 | 57.7 | 0.5 | 15.9
DHH060* | 5 | 1500 | 75 | 59 | 115 | 49.2 | 0.86 | 25.78
DHH060* | 5 | 1500 | 75 | 63 | 115 | 50.1 | 0.79 | 23.95
DHH060* | 5 | 1500 | 75 | 67 | 115 | 51.9 | 0.65 | 20.54
DHH060* | 5 | 1500 | 75 | 71 | 115 | 54.7 | 0.5 | 17
DHH060* | 5 | 1500 | 80 | 59 | 65 | 60.8 | 0.79 | 28.99
DHH060* | 5 | 1500 | 80 | 63 | 65 | 61.7 | 0.73 | 27.17
DHH060* | 5 | 1500 | 80 | 67 | 65 | 63.5 | 0.62 | 23.75
DHH060* | 5 | 1500 | 80 | 71 | 65 | 66.3 | 0.5 | 20.2
DHH060* | 5 | 1500 | 80 | 59 | 75 | 60.3 | 0.79 | 28.94
DHH060* | 5 | 1500 | 80 | 63 | 75 | 61.1 | 0.73 | 27.12
DHH060* | 5 | 1500 | 80 | 67 | 75 | 63 | 0.62 | 23.7
DHH060* | 5 | 1500 | 80 | 71 | 75 | 65.7 | 0.5 | 20.2
DHH060* | 5 | 1500 | 80 | 59 | 85 | 58.7 | 0.82 | 29.2
DHH060* | 5 | 1500 | 80 | 63 | 85 | 59.5 | 0.76 | 27.37
DHH060* | 5 | 1500 | 80 | 67 | 85 | 61.4 | 0.64 | 23.96
DHH060* | 5 | 1500 | 80 | 71 | 85 | 64.1 | 0.5 | 20.4
DHH060* | 5 | 1500 | 80 | 59 | 95 | 55.9 | 0.85 | 28.93
DHH060* | 5 | 1500 | 80 | 63 | 95 | 56.8 | 0.79 | 27.1
DHH060* | 5 | 1500 | 80 | 67 | 95 | 58.6 | 0.67 | 23.68
DHH060* | 5 | 1500 | 80 | 71 | 95 | 61.4 | 0.5 | 20.1
DHH060* | 5 | 1500 | 80 | 59 | 105 | 52.6 | 0.9 | 28.68
DHH060* | 5 | 1500 | 80 | 63 | 105 | 53.4 | 0.83 | 26.85
DHH060* | 5 | 1500 | 80 | 67 | 105 | 55.3 | 0.7 | 23.44
DHH060* | 5 | 1500 | 80 | 71 | 105 | 58.1 | 0.6 | 19.9
DHH060* | 5 | 1500 | 80 | 59 | 115 | 49.5 | 0.99 | 29.83
DHH060* | 5 | 1500 | 80 | 63 | 115 | 50.4 | 0.92 | 28
DHH060* | 5 | 1500 | 80 | 67 | 115 | 52.2 | 0.78 | 24.58
DHH060* | 5 | 1500 | 80 | 71 | 115 | 55 | 0.6 | 21
DHH060* | 5 | 1500 | 85 | 59 | 65 | 61.8 | 0.87 | 32.59
DHH060* | 5 | 1500 | 85 | 63 | 65 | 62.7 | 0.81 | 30.76
DHH060* | 5 | 1500 | 85 | 67 | 65 | 64.5 | 0.7 | 27.34
DHH060* | 5 | 1500 | 85 | 71 | 65 | 67.3 | 0.6 | 23.8
DHH060* | 5 | 1500 | 85 | 59 | 75 | 61.3 | 0.88 | 32.54
DHH060* | 5 | 1500 | 85 | 63 | 75 | 62.2 | 0.82 | 30.71
DHH060* | 5 | 1500 | 85 | 67 | 75 | 64 | 0.7 | 27.29
DHH060* | 5 | 1500 | 85 | 71 | 75 | 66.8 | 0.6 | 23.8
DHH060* | 5 | 1500 | 85 | 59 | 85 | 59.7 | 0.91 | 32.79
DHH060* | 5 | 1500 | 85 | 63 | 85 | 60.6 | 0.84 | 30.96
DHH060* | 5 | 1500 | 85 | 67 | 85 | 62.4 | 0.73 | 27.55
DHH060* | 5 | 1500 | 85 | 71 | 85 | 65.2 | 0.6 | 24
DHH060* | 5 | 1500 | 85 | 59 | 95 | 57 | 0.94 | 32.52
DHH060* | 5 | 1500 | 85 | 63 | 95 | 57.8 | 0.88 | 30.69
DHH060* | 5 | 1500 | 85 | 67 | 95 | 59.6 | 0.75 | 27.27
DHH060* | 5 | 1500 | 85 | 71 | 95 | 62.4 | 0.6 | 23.7
DHH060* | 5 | 1500 | 85 | 59 | 105 | 53.6 | 0.99 | 32.27
DHH060* | 5 | 1500 | 85 | 63 | 105 | 54.5 | 0.92 | 30.44
DHH060* | 5 | 1500 | 85 | 67 | 105 | 56.3 | 0.79 | 27.03
DHH060* | 5 | 1500 | 85 | 71 | 105 | 59.1 | 0.7 | 23.5
DHH060* | 5 | 1500 | 85 | 59 | 115 | 50.5 | 1 | 30.64
DHH060* | 5 | 1500 | 85 | 63 | 115 | 51.4 | 1 | 31.16
DHH060* | 5 | 1500 | 85 | 67 | 115 | 53.2 | 0.87 | 28.17
DHH060* | 5 | 1500 | 85 | 71 | 115 | 56 | 0.7 | 24.6
DHH060* | 5 | 1950 | 70 | 59 | 65 | 61.6 | 0.65 | 18.67
DHH060* | 5 | 1950 | 70 | 63 | 65 | 62.4 | 0.58 | 16.84
DHH060* | 5 | 1950 | 70 | 67 | 65 | 64.3 | 0.45 | 13.43
DHH060* | 5 | 1950 | 70 | 59 | 75 | 61 | 0.65 | 18.62
DHH060* | 5 | 1950 | 70 | 63 | 75 | 61.9 | 0.58 | 16.79
DHH060* | 5 | 1950 | 70 | 67 | 75 | 63.7 | 0.45 | 13.38
DHH060* | 5 | 1950 | 70 | 59 | 85 | 59.4 | 0.68 | 18.88
DHH060* | 5 | 1950 | 70 | 63 | 85 | 60.3 | 0.61 | 17.05
DHH060* | 5 | 1950 | 70 | 67 | 85 | 62.1 | 0.47 | 13.63
DHH060* | 5 | 1950 | 70 | 59 | 95 | 56.7 | 0.7 | 18.6
DHH060* | 5 | 1950 | 70 | 63 | 95 | 57.5 | 0.63 | 16.77
DHH060* | 5 | 1950 | 70 | 67 | 95 | 59.4 | 0.48 | 13.36
DHH060* | 5 | 1950 | 70 | 59 | 105 | 53.3 | 0.74 | 18.36
DHH060* | 5 | 1950 | 70 | 63 | 105 | 54.2 | 0.65 | 16.53
DHH060* | 5 | 1950 | 70 | 67 | 105 | 56 | 0.5 | 13.11
DHH060* | 5 | 1950 | 70 | 59 | 115 | 50.3 | 0.83 | 19.5
DHH060* | 5 | 1950 | 70 | 63 | 115 | 51.1 | 0.74 | 17.67
DHH060* | 5 | 1950 | 70 | 67 | 115 | 53 | 0.58 | 14.26
DHH060* | 5 | 1950 | 75 | 59 | 65 | 61.9 | 0.79 | 22.69
DHH060* | 5 | 1950 | 75 | 63 | 65 | 62.7 | 0.71 | 20.86
DHH060* | 5 | 1950 | 75 | 67 | 65 | 64.6 | 0.58 | 17.45
DHH060* | 5 | 1950 | 75 | 71 | 65 | 67.4 | 0.4 | 13.9
DHH060* | 5 | 1950 | 75 | 59 | 75 | 61.3 | 0.79 | 22.64
DHH060* | 5 | 1950 | 75 | 63 | 75 | 62.2 | 0.72 | 20.81
DHH060* | 5 | 1950 | 75 | 67 | 75 | 64 | 0.58 | 17.4
DHH060* | 5 | 1950 | 75 | 71 | 75 | 66.8 | 0.4 | 13.9
DHH060* | 5 | 1950 | 75 | 59 | 85 | 59.7 | 0.82 | 22.9
DHH060* | 5 | 1950 | 75 | 63 | 85 | 60.6 | 0.75 | 21.07
DHH060* | 5 | 1950 | 75 | 67 | 85 | 62.4 | 0.61 | 17.65
DHH060* | 5 | 1950 | 75 | 71 | 85 | 65.2 | 0.5 | 14.1
DHH060* | 5 | 1950 | 75 | 59 | 95 | 57 | 0.85 | 22.62
DHH060* | 5 | 1950 | 75 | 63 | 95 | 57.9 | 0.77 | 20.79
DHH060* | 5 | 1950 | 75 | 67 | 95 | 59.7 | 0.62 | 17.38
DHH060* | 5 | 1950 | 75 | 71 | 95 | 62.5 | 0.5 | 13.8
DHH060* | 5 | 1950 | 75 | 59 | 105 | 53.6 | 0.89 | 22.38
DHH060* | 5 | 1950 | 75 | 63 | 105 | 54.5 | 0.81 | 20.55
DHH060* | 5 | 1950 | 75 | 67 | 105 | 56.3 | 0.65 | 17.13
DHH060* | 5 | 1950 | 75 | 71 | 105 | 59.1 | 0.5 | 13.6
DHH060* | 5 | 1950 | 75 | 59 | 115 | 50.6 | 1 | 23.52
DHH060* | 5 | 1950 | 75 | 63 | 115 | 51.4 | 0.9 | 21.69
DHH060* | 5 | 1950 | 75 | 67 | 115 | 53.3 | 0.74 | 18.28
DHH060* | 5 | 1950 | 75 | 71 | 115 | 56.1 | 0.6 | 14.7
DHH060* | 5 | 1950 | 80 | 59 | 65 | 62.2 | 0.92 | 26.74
DHH060* | 5 | 1950 | 80 | 63 | 65 | 63.1 | 0.85 | 24.91
DHH060* | 5 | 1950 | 80 | 67 | 65 | 64.9 | 0.71 | 21.49
DHH060* | 5 | 1950 | 80 | 71 | 65 | 67.7 | 0.6 | 18
DHH060* | 5 | 1950 | 80 | 59 | 75 | 61.7 | 0.93 | 26.69
DHH060* | 5 | 1950 | 80 | 63 | 75 | 62.5 | 0.85 | 24.86
DHH060* | 5 | 1950 | 80 | 67 | 75 | 64.3 | 0.71 | 21.44
DHH060* | 5 | 1950 | 80 | 71 | 75 | 67.1 | 0.6 | 17.9
DHH060* | 5 | 1950 | 80 | 59 | 85 | 60.1 | 0.96 | 26.94
DHH060* | 5 | 1950 | 80 | 63 | 85 | 60.9 | 0.88 | 25.12
DHH060* | 5 | 1950 | 80 | 67 | 85 | 62.7 | 0.74 | 21.7
DHH060* | 5 | 1950 | 80 | 71 | 85 | 65.5 | 0.6 | 18.2
DHH060* | 5 | 1950 | 80 | 59 | 95 | 57.3 | 1 | 26.67
DHH060* | 5 | 1950 | 80 | 63 | 95 | 58.2 | 0.92 | 24.84
DHH060* | 5 | 1950 | 80 | 67 | 95 | 60 | 0.77 | 21.43
DHH060* | 5 | 1950 | 80 | 71 | 95 | 62.8 | 0.6 | 17.9
DHH060* | 5 | 1950 | 80 | 59 | 105 | 54 | 1 | 25.16
DHH060* | 5 | 1950 | 80 | 63 | 105 | 54.8 | 0.96 | 24.6
DHH060* | 5 | 1950 | 80 | 67 | 105 | 56.6 | 0.8 | 21.18
DHH060* | 5 | 1950 | 80 | 71 | 105 | 59.4 | 0.6 | 17.6
DHH060* | 5 | 1950 | 80 | 59 | 115 | 50.9 | 1 | 23.73
DHH060* | 5 | 1950 | 80 | 63 | 115 | 51.8 | 1 | 24.13
DHH060* | 5 | 1950 | 80 | 67 | 115 | 53.6 | 0.89 | 22.33
DHH060* | 5 | 1950 | 80 | 71 | 115 | 56.4 | 0.7 | 18.8
DHH060* | 5 | 1950 | 85 | 59 | 65 | 63.2 | 1 | 29.48
DHH060* | 5 | 1950 | 85 | 63 | 65 | 64.1 | 0.95 | 28.5
DHH060* | 5 | 1950 | 85 | 67 | 65 | 65.9 | 0.82 | 25.08
DHH060* | 5 | 1950 | 85 | 71 | 65 | 68.7 | 0.7 | 21.5
DHH060* | 5 | 1950 | 85 | 59 | 75 | 62.7 | 1 | 29.22
DHH060* | 5 | 1950 | 85 | 63 | 75 | 63.5 | 0.96 | 28.45
DHH060* | 5 | 1950 | 85 | 67 | 75 | 65.4 | 0.82 | 25.03
DHH060* | 5 | 1950 | 85 | 71 | 75 | 68.2 | 0.7 | 21.5
DHH060* | 5 | 1950 | 85 | 59 | 85 | 61.1 | 1 | 28.48
DHH060* | 5 | 1950 | 85 | 63 | 85 | 61.9 | 0.99 | 28.71
DHH060* | 5 | 1950 | 85 | 67 | 85 | 63.8 | 0.85 | 25.29
DHH060* | 5 | 1950 | 85 | 71 | 85 | 66.6 | 0.7 | 21.8
DHH060* | 5 | 1950 | 85 | 59 | 95 | 58.3 | 1 | 27.2
DHH060* | 5 | 1950 | 85 | 63 | 95 | 59.2 | 1 | 27.6
DHH060* | 5 | 1950 | 85 | 67 | 95 | 61 | 0.88 | 25.02
DHH060* | 5 | 1950 | 85 | 71 | 95 | 63.8 | 0.7 | 21.5
DHH060* | 5 | 1950 | 85 | 59 | 105 | 55 | 1 | 25.64
DHH060* | 5 | 1950 | 85 | 63 | 105 | 55.9 | 1 | 26.04
DHH060* | 5 | 1950 | 85 | 67 | 105 | 57.7 | 0.92 | 24.77
DHH060* | 5 | 1950 | 85 | 71 | 105 | 60.5 | 0.8 | 21.2
DHH060* | 5 | 1950 | 85 | 59 | 115 | 51.9 | 1 | 24.21
DHH060* | 5 | 1950 | 85 | 63 | 115 | 52.8 | 1 | 24.61
DHH060* | 5 | 1950 | 85 | 67 | 115 | 54.6 | 1 | 25.46
DHH060* | 5 | 1950 | 85 | 71 | 115 | 57.4 | 0.8 | 22.4
DHH060* | 5 | 2500 | 70 | 59 | 65 | 64 | 0.72 | 16.71
DHH060* | 5 | 2500 | 70 | 63 | 65 | 64.9 | 0.63 | 14.88
DHH060* | 5 | 2500 | 70 | 67 | 65 | 66.7 | 0.47 | 11.47
DHH060* | 5 | 2500 | 70 | 59 | 75 | 63.5 | 0.72 | 16.66
DHH060* | 5 | 2500 | 70 | 63 | 75 | 64.3 | 0.63 | 14.83
DHH060* | 5 | 2500 | 70 | 67 | 75 | 66.2 | 0.47 | 11.42
DHH060* | 5 | 2500 | 70 | 59 | 85 | 61.9 | 0.75 | 16.92
DHH060* | 5 | 2500 | 70 | 63 | 85 | 62.7 | 0.66 | 15.09
DHH060* | 5 | 2500 | 70 | 67 | 85 | 64.6 | 0.5 | 11.68
DHH060* | 5 | 2500 | 70 | 59 | 95 | 59.1 | 0.77 | 16.64
DHH060* | 5 | 2500 | 70 | 63 | 95 | 60 | 0.68 | 14.82
DHH060* | 5 | 2500 | 70 | 67 | 95 | 61.8 | 0.51 | 11.4
DHH060* | 5 | 2500 | 70 | 59 | 105 | 55.8 | 0.81 | 16.4
DHH060* | 5 | 2500 | 70 | 63 | 105 | 56.6 | 0.71 | 14.57
DHH060* | 5 | 2500 | 70 | 67 | 105 | 58.5 | 0.52 | 11.16
DHH060* | 5 | 2500 | 70 | 59 | 115 | 52.7 | 0.92 | 17.55
DHH060* | 5 | 2500 | 70 | 63 | 115 | 53.6 | 0.81 | 15.72
DHH060* | 5 | 2500 | 70 | 67 | 115 | 55.4 | 0.61 | 12.3
DHH060* | 5 | 2500 | 75 | 59 | 65 | 64.3 | 0.89 | 20.73
DHH060* | 5 | 2500 | 75 | 63 | 65 | 65.2 | 0.8 | 18.91
DHH060* | 5 | 2500 | 75 | 67 | 65 | 67 | 0.64 | 15.49
DHH060* | 5 | 2500 | 75 | 71 | 65 | 69.8 | 0.5 | 12
DHH060* | 5 | 2500 | 75 | 59 | 75 | 63.8 | 0.89 | 20.68
DHH060* | 5 | 2500 | 75 | 63 | 75 | 64.6 | 0.8 | 18.86
DHH060* | 5 | 2500 | 75 | 67 | 75 | 66.5 | 0.64 | 15.44
DHH060* | 5 | 2500 | 75 | 71 | 75 | 69.3 | 0.5 | 11.9
DHH060* | 5 | 2500 | 75 | 59 | 85 | 62.2 | 0.93 | 20.94
DHH060* | 5 | 2500 | 75 | 63 | 85 | 63.1 | 0.83 | 19.11
DHH060* | 5 | 2500 | 75 | 67 | 85 | 64.9 | 0.67 | 15.7
DHH060* | 5 | 2500 | 75 | 71 | 85 | 67.7 | 0.5 | 12.2
DHH060* | 5 | 2500 | 75 | 59 | 95 | 59.4 | 0.96 | 20.67
DHH060* | 5 | 2500 | 75 | 63 | 95 | 60.3 | 0.86 | 18.84
DHH060* | 5 | 2500 | 75 | 67 | 95 | 62.1 | 0.68 | 15.42
DHH060* | 5 | 2500 | 75 | 71 | 95 | 64.9 | 0.5 | 11.9
DHH060* | 5 | 2500 | 75 | 59 | 105 | 56.1 | 1 | 20.4
DHH060* | 5 | 2500 | 75 | 63 | 105 | 57 | 0.9 | 18.59
DHH060* | 5 | 2500 | 75 | 67 | 105 | 58.8 | 0.71 | 15.18
DHH060* | 5 | 2500 | 75 | 71 | 105 | 61.6 | 0.5 | 11.6
DHH060* | 5 | 2500 | 75 | 59 | 115 | 53 | 1 | 19.29
DHH060* | 5 | 2500 | 75 | 63 | 115 | 53.9 | 1 | 19.6
DHH060* | 5 | 2500 | 75 | 67 | 115 | 55.7 | 0.81 | 16.32
DHH060* | 5 | 2500 | 75 | 71 | 115 | 58.5 | 0.6 | 12.8
DHH060* | 5 | 2500 | 80 | 59 | 65 | 64.6 | 1 | 23.51
DHH060* | 5 | 2500 | 80 | 63 | 65 | 65.5 | 0.96 | 22.95
DHH060* | 5 | 2500 | 80 | 67 | 65 | 67.3 | 0.8 | 19.54
DHH060* | 5 | 2500 | 80 | 71 | 65 | 70.1 | 0.6 | 16
DHH060* | 5 | 2500 | 80 | 59 | 75 | 64.1 | 1 | 23.31
DHH060* | 5 | 2500 | 80 | 63 | 75 | 65 | 0.97 | 22.9
DHH060* | 5 | 2500 | 80 | 67 | 75 | 66.8 | 0.8 | 19.49
DHH060* | 5 | 2500 | 80 | 71 | 75 | 69.6 | 0.6 | 16
DHH060* | 5 | 2500 | 80 | 59 | 85 | 62.5 | 1 | 22.73
DHH060* | 5 | 2500 | 80 | 63 | 85 | 63.4 | 1 | 23.04
DHH060* | 5 | 2500 | 80 | 67 | 85 | 65.2 | 0.83 | 19.75
DHH060* | 5 | 2500 | 80 | 71 | 85 | 68 | 0.7 | 16.2
DHH060* | 5 | 2500 | 80 | 59 | 95 | 59.8 | 1 | 21.73
DHH060* | 5 | 2500 | 80 | 63 | 95 | 60.6 | 1 | 22.05
DHH060* | 5 | 2500 | 80 | 67 | 95 | 62.5 | 0.86 | 19.47
DHH060* | 5 | 2500 | 80 | 71 | 95 | 65.2 | 0.7 | 15.9
DHH060* | 5 | 2500 | 80 | 59 | 105 | 56.4 | 1 | 20.51
DHH060* | 5 | 2500 | 80 | 63 | 105 | 57.3 | 1 | 20.83
DHH060* | 5 | 2500 | 80 | 67 | 105 | 59.1 | 0.89 | 19.23
DHH060* | 5 | 2500 | 80 | 71 | 105 | 61.9 | 0.7 | 15.7
DHH060* | 5 | 2500 | 80 | 59 | 115 | 53.4 | 1 | 19.4
DHH060* | 5 | 2500 | 80 | 63 | 115 | 54.2 | 1 | 19.71
DHH060* | 5 | 2500 | 80 | 67 | 115 | 56 | 1 | 20.37
DHH060* | 5 | 2500 | 80 | 71 | 115 | 58.8 | 0.8 | 16.8
DHH060* | 5 | 2500 | 85 | 59 | 65 | 65.7 | 1 | 23.88
DHH060* | 5 | 2500 | 85 | 63 | 65 | 66.5 | 1 | 24.2
DHH060* | 5 | 2500 | 85 | 67 | 65 | 68.4 | 0.93 | 23.13
DHH060* | 5 | 2500 | 85 | 71 | 65 | 71.1 | 0.8 | 19.6
DHH060* | 5 | 2500 | 85 | 59 | 75 | 65.1 | 1 | 23.68
DHH060* | 5 | 2500 | 85 | 63 | 75 | 66 | 1 | 24
DHH060* | 5 | 2500 | 85 | 67 | 75 | 67.8 | 0.94 | 23.08
DHH060* | 5 | 2500 | 85 | 71 | 75 | 70.6 | 0.8 | 19.5
DHH060* | 5 | 2500 | 85 | 59 | 85 | 63.5 | 1 | 23.1
DHH060* | 5 | 2500 | 85 | 63 | 85 | 64.4 | 1 | 23.42
DHH060* | 5 | 2500 | 85 | 67 | 85 | 66.2 | 0.97 | 23.34
DHH060* | 5 | 2500 | 85 | 71 | 85 | 69 | 0.8 | 19.8
DHH060* | 5 | 2500 | 85 | 59 | 95 | 60.8 | 1 | 22.11
DHH060* | 5 | 2500 | 85 | 63 | 95 | 61.7 | 1 | 22.42
DHH060* | 5 | 2500 | 85 | 67 | 95 | 63.5 | 1 | 23.06
DHH060* | 5 | 2500 | 85 | 71 | 95 | 66.3 | 0.8 | 19.5
DHH060* | 5 | 2500 | 85 | 59 | 105 | 57.4 | 1 | 20.89
DHH060* | 5 | 2500 | 85 | 63 | 105 | 58.3 | 1 | 21.2
DHH060* | 5 | 2500 | 85 | 67 | 105 | 60.1 | 1 | 21.86
DHH060* | 5 | 2500 | 85 | 71 | 105 | 62.9 | 0.8 | 19.3
DHH060* | 5 | 2500 | 85 | 59 | 115 | 54.4 | 1 | 19.78
DHH060* | 5 | 2500 | 85 | 63 | 115 | 55.2 | 1 | 20.09
DHH060* | 5 | 2500 | 85 | 67 | 115 | 57.1 | 1 | 20.75
DHH060* | 5 | 2500 | 85 | 71 | 115 | 59.9 | 0.9 | 20.4
DHH072* | 6 | 1800 | 70 | 59 | 65 | 69.5 | 0.59 | 20.61
DHH072* | 6 | 1800 | 70 | 63 | 65 | 70.5 | 0.53 | 18.76
DHH072* | 6 | 1800 | 70 | 67 | 65 | 72.6 | 0.42 | 15.3
DHH072* | 6 | 1800 | 70 | 59 | 75 | 68.9 | 0.59 | 20.56
DHH072* | 6 | 1800 | 70 | 63 | 75 | 69.9 | 0.53 | 18.71
DHH072* | 6 | 1800 | 70 | 67 | 75 | 72 | 0.42 | 15.25
DHH072* | 6 | 1800 | 70 | 59 | 85 | 67 | 0.61 | 20.82
DHH072* | 6 | 1800 | 70 | 63 | 85 | 68 | 0.55 | 18.97
DHH072* | 6 | 1800 | 70 | 67 | 85 | 70.1 | 0.44 | 15.51
DHH072* | 6 | 1800 | 70 | 59 | 95 | 63.9 | 0.64 | 20.54
DHH072* | 6 | 1800 | 70 | 63 | 95 | 64.9 | 0.57 | 18.69
DHH072* | 6 | 1800 | 70 | 67 | 95 | 67 | 0.45 | 15.23
DHH072* | 6 | 1800 | 70 | 59 | 105 | 60 | 0.67 | 20.29
DHH072* | 6 | 1800 | 70 | 63 | 105 | 61 | 0.6 | 18.44
DHH072* | 6 | 1800 | 70 | 67 | 105 | 63.1 | 0.47 | 14.99
DHH072* | 6 | 1800 | 70 | 59 | 115 | 56.5 | 0.75 | 21.45
DHH072* | 6 | 1800 | 70 | 63 | 115 | 57.5 | 0.67 | 19.6
DHH072* | 6 | 1800 | 70 | 67 | 115 | 59.6 | 0.54 | 16.14
DHH072* | 6 | 1800 | 75 | 59 | 65 | 69.9 | 0.7 | 24.68
DHH072* | 6 | 1800 | 75 | 63 | 65 | 70.9 | 0.64 | 22.83
DHH072* | 6 | 1800 | 75 | 67 | 65 | 73 | 0.53 | 19.37
DHH072* | 6 | 1800 | 75 | 71 | 65 | 76.2 | 0.4 | 15.8
DHH072* | 6 | 1800 | 75 | 59 | 75 | 69.2 | 0.7 | 24.63
DHH072* | 6 | 1800 | 75 | 63 | 75 | 70.2 | 0.64 | 22.78
DHH072* | 6 | 1800 | 75 | 67 | 75 | 72.3 | 0.53 | 19.32
DHH072* | 6 | 1800 | 75 | 71 | 75 | 75.5 | 0.4 | 15.7
DHH072* | 6 | 1800 | 75 | 59 | 85 | 67.4 | 0.73 | 24.89
DHH072* | 6 | 1800 | 75 | 63 | 85 | 68.4 | 0.67 | 23.04
DHH072* | 6 | 1800 | 75 | 67 | 85 | 70.5 | 0.55 | 19.58
DHH072* | 6 | 1800 | 75 | 71 | 85 | 73.7 | 0.4 | 16
DHH072* | 6 | 1800 | 75 | 59 | 95 | 64.3 | 0.76 | 24.61
DHH072* | 6 | 1800 | 75 | 63 | 95 | 65.2 | 0.69 | 22.76
DHH072* | 6 | 1800 | 75 | 67 | 95 | 67.3 | 0.57 | 19.3
DHH072* | 6 | 1800 | 75 | 71 | 95 | 70.5 | 0.4 | 15.7
DHH072* | 6 | 1800 | 75 | 59 | 105 | 60.4 | 0.8 | 24.36
DHH072* | 6 | 1800 | 75 | 63 | 105 | 61.4 | 0.73 | 22.51
DHH072* | 6 | 1800 | 75 | 67 | 105 | 63.5 | 0.59 | 19.06
DHH072* | 6 | 1800 | 75 | 71 | 105 | 66.7 | 0.5 | 15.5
DHH072* | 6 | 1800 | 75 | 59 | 115 | 56.9 | 0.89 | 25.52
DHH072* | 6 | 1800 | 75 | 63 | 115 | 57.9 | 0.81 | 23.67
DHH072* | 6 | 1800 | 75 | 67 | 115 | 60 | 0.67 | 20.21
DHH072* | 6 | 1800 | 75 | 71 | 115 | 63.2 | 0.5 | 16.6
DHH072* | 6 | 1800 | 80 | 59 | 65 | 70.2 | 0.81 | 28.78
DHH072* | 6 | 1800 | 80 | 63 | 65 | 71.2 | 0.75 | 26.93
DHH072* | 6 | 1800 | 80 | 67 | 65 | 73.3 | 0.63 | 23.47
DHH072* | 6 | 1800 | 80 | 71 | 65 | 76.5 | 0.5 | 19.9
DHH072* | 6 | 1800 | 80 | 59 | 75 | 69.6 | 0.82 | 28.73
DHH072* | 6 | 1800 | 80 | 63 | 75 | 70.6 | 0.75 | 26.88
DHH072* | 6 | 1800 | 80 | 67 | 75 | 72.7 | 0.64 | 23.42
DHH072* | 6 | 1800 | 80 | 71 | 75 | 75.9 | 0.5 | 19.8
DHH072* | 6 | 1800 | 80 | 59 | 85 | 67.8 | 0.85 | 28.99
DHH072* | 6 | 1800 | 80 | 63 | 85 | 68.8 | 0.78 | 27.14
DHH072* | 6 | 1800 | 80 | 67 | 85 | 70.9 | 0.66 | 23.68
DHH072* | 6 | 1800 | 80 | 71 | 85 | 74.1 | 0.5 | 20.1
DHH072* | 6 | 1800 | 80 | 59 | 95 | 64.6 | 0.88 | 28.71
DHH072* | 6 | 1800 | 80 | 63 | 95 | 65.6 | 0.81 | 26.86
DHH072* | 6 | 1800 | 80 | 67 | 95 | 67.7 | 0.68 | 23.4
DHH072* | 6 | 1800 | 80 | 71 | 95 | 70.9 | 0.6 | 19.8
DHH072* | 6 | 1800 | 80 | 59 | 105 | 60.8 | 0.93 | 28.46
DHH072* | 6 | 1800 | 80 | 63 | 105 | 61.8 | 0.85 | 26.61
DHH072* | 6 | 1800 | 80 | 67 | 105 | 63.9 | 0.72 | 23.15
DHH072* | 6 | 1800 | 80 | 71 | 105 | 67.1 | 0.6 | 19.6
DHH072* | 6 | 1800 | 80 | 59 | 115 | 57.2 | 1 | 28.91
DHH072* | 6 | 1800 | 80 | 63 | 115 | 58.2 | 0.94 | 27.77
DHH072* | 6 | 1800 | 80 | 67 | 115 | 60.3 | 0.8 | 24.31
DHH072* | 6 | 1800 | 80 | 71 | 115 | 63.5 | 0.6 | 20.7
DHH072* | 6 | 1800 | 85 | 59 | 65 | 71.4 | 0.9 | 32.41
DHH072* | 6 | 1800 | 85 | 63 | 65 | 72.4 | 0.84 | 30.56
DHH072* | 6 | 1800 | 85 | 67 | 65 | 74.5 | 0.72 | 27.1
DHH072* | 6 | 1800 | 85 | 71 | 65 | 77.7 | 0.6 | 23.5
DHH072* | 6 | 1800 | 85 | 59 | 75 | 70.8 | 0.91 | 32.36
DHH072* | 6 | 1800 | 85 | 63 | 75 | 71.8 | 0.84 | 30.51
DHH072* | 6 | 1800 | 85 | 67 | 75 | 73.9 | 0.73 | 27.05
DHH072* | 6 | 1800 | 85 | 71 | 75 | 77.1 | 0.6 | 23.5
DHH072* | 6 | 1800 | 85 | 59 | 85 | 69 | 0.94 | 32.62
DHH072* | 6 | 1800 | 85 | 63 | 85 | 69.9 | 0.87 | 30.77
DHH072* | 6 | 1800 | 85 | 67 | 85 | 72 | 0.75 | 27.31
DHH072* | 6 | 1800 | 85 | 71 | 85 | 75.2 | 0.6 | 23.7
DHH072* | 6 | 1800 | 85 | 59 | 95 | 65.8 | 0.97 | 32.34
DHH072* | 6 | 1800 | 85 | 63 | 95 | 66.8 | 0.9 | 30.49
DHH072* | 6 | 1800 | 85 | 67 | 95 | 68.9 | 0.78 | 27.03
DHH072* | 6 | 1800 | 85 | 71 | 95 | 72.1 | 0.6 | 23.5
DHH072* | 6 | 1800 | 85 | 59 | 105 | 61.9 | 1 | 31.29
DHH072* | 6 | 1800 | 85 | 63 | 105 | 62.9 | 0.95 | 30.24
DHH072* | 6 | 1800 | 85 | 67 | 105 | 65 | 0.82 | 26.79
DHH072* | 6 | 1800 | 85 | 71 | 105 | 68.2 | 0.7 | 23.2
DHH072* | 6 | 1800 | 85 | 59 | 115 | 58.4 | 1 | 29.51
DHH072* | 6 | 1800 | 85 | 63 | 115 | 59.4 | 1 | 30.01
DHH072* | 6 | 1800 | 85 | 67 | 115 | 61.5 | 0.9 | 27.95
DHH072* | 6 | 1800 | 85 | 71 | 115 | 64.7 | 0.7 | 24.4
DHH072* | 6 | 2200 | 70 | 59 | 65 | 70.8 | 0.65 | 18.9
DHH072* | 6 | 2200 | 70 | 63 | 65 | 71.8 | 0.57 | 17.05
DHH072* | 6 | 2200 | 70 | 67 | 65 | 73.9 | 0.45 | 13.59
DHH072* | 6 | 2200 | 70 | 59 | 75 | 70.2 | 0.65 | 18.85
DHH072* | 6 | 2200 | 70 | 63 | 75 | 71.2 | 0.58 | 16.99
DHH072* | 6 | 2200 | 70 | 67 | 75 | 73.3 | 0.45 | 13.54
DHH072* | 6 | 2200 | 70 | 59 | 85 | 68.3 | 0.68 | 19.11
DHH072* | 6 | 2200 | 70 | 63 | 85 | 69.3 | 0.6 | 17.25
DHH072* | 6 | 2200 | 70 | 67 | 85 | 71.4 | 0.47 | 13.8
DHH072* | 6 | 2200 | 70 | 59 | 95 | 65.2 | 0.7 | 18.83
DHH072* | 6 | 2200 | 70 | 63 | 95 | 66.2 | 0.62 | 16.98
DHH072* | 6 | 2200 | 70 | 67 | 95 | 68.3 | 0.48 | 13.52
DHH072* | 6 | 2200 | 70 | 59 | 105 | 61.3 | 0.73 | 18.58
DHH072* | 6 | 2200 | 70 | 63 | 105 | 62.3 | 0.65 | 16.73
DHH072* | 6 | 2200 | 70 | 67 | 105 | 64.4 | 0.5 | 13.27
DHH072* | 6 | 2200 | 70 | 59 | 115 | 57.8 | 0.83 | 19.74
DHH072* | 6 | 2200 | 70 | 63 | 115 | 58.8 | 0.74 | 17.89
DHH072* | 6 | 2200 | 70 | 67 | 115 | 60.9 | 0.57 | 14.43
DHH072* | 6 | 2200 | 75 | 59 | 65 | 71.2 | 0.78 | 22.97
DHH072* | 6 | 2200 | 75 | 63 | 65 | 72.2 | 0.71 | 21.12
DHH072* | 6 | 2200 | 75 | 67 | 65 | 74.3 | 0.58 | 17.66
DHH072* | 6 | 2200 | 75 | 71 | 65 | 77.5 | 0.4 | 14.1
DHH072* | 6 | 2200 | 75 | 59 | 75 | 70.5 | 0.79 | 22.92
DHH072* | 6 | 2200 | 75 | 63 | 75 | 71.5 | 0.71 | 21.06
DHH072* | 6 | 2200 | 75 | 67 | 75 | 73.6 | 0.58 | 17.61
DHH072* | 6 | 2200 | 75 | 71 | 75 | 76.8 | 0.4 | 14
DHH072* | 6 | 2200 | 75 | 59 | 85 | 68.7 | 0.82 | 23.18
DHH072* | 6 | 2200 | 75 | 63 | 85 | 69.7 | 0.74 | 21.32
DHH072* | 6 | 2200 | 75 | 67 | 85 | 71.8 | 0.6 | 17.87
DHH072* | 6 | 2200 | 75 | 71 | 85 | 75 | 0.5 | 14.3
DHH072* | 6 | 2200 | 75 | 59 | 95 | 65.5 | 0.85 | 22.9
DHH072* | 6 | 2200 | 75 | 63 | 95 | 66.5 | 0.77 | 21.05
DHH072* | 6 | 2200 | 75 | 67 | 95 | 68.6 | 0.62 | 17.59
DHH072* | 6 | 2200 | 75 | 71 | 95 | 71.8 | 0.5 | 14
DHH072* | 6 | 2200 | 75 | 59 | 105 | 61.7 | 0.89 | 22.65
DHH072* | 6 | 2200 | 75 | 63 | 105 | 62.7 | 0.8 | 20.8
DHH072* | 6 | 2200 | 75 | 67 | 105 | 64.8 | 0.65 | 17.34
DHH072* | 6 | 2200 | 75 | 71 | 105 | 68 | 0.5 | 13.8
DHH072* | 6 | 2200 | 75 | 59 | 115 | 58.2 | 0.99 | 23.81
DHH072* | 6 | 2200 | 75 | 63 | 115 | 59.2 | 0.9 | 21.96
DHH072* | 6 | 2200 | 75 | 67 | 115 | 61.3 | 0.73 | 18.5
DHH072* | 6 | 2200 | 75 | 71 | 115 | 64.5 | 0.6 | 14.9
DHH072* | 6 | 2200 | 80 | 59 | 65 | 71.5 | 0.92 | 27.06
DHH072* | 6 | 2200 | 80 | 63 | 65 | 72.5 | 0.84 | 25.21
DHH072* | 6 | 2200 | 80 | 67 | 65 | 74.6 | 0.71 | 21.76
DHH072* | 6 | 2200 | 80 | 71 | 65 | 77.8 | 0.6 | 18.2
DHH072* | 6 | 2200 | 80 | 59 | 75 | 70.9 | 0.92 | 27.01
DHH072* | 6 | 2200 | 80 | 63 | 75 | 71.9 | 0.85 | 25.16
DHH072* | 6 | 2200 | 80 | 67 | 75 | 74 | 0.71 | 21.71
DHH072* | 6 | 2200 | 80 | 71 | 75 | 77.2 | 0.6 | 18.1
DHH072* | 6 | 2200 | 80 | 59 | 85 | 69.1 | 0.96 | 27.27
DHH072* | 6 | 2200 | 80 | 63 | 85 | 70.1 | 0.88 | 25.42
DHH072* | 6 | 2200 | 80 | 67 | 85 | 72.2 | 0.74 | 21.97
DHH072* | 6 | 2200 | 80 | 71 | 85 | 75.4 | 0.6 | 18.4
DHH072* | 6 | 2200 | 80 | 59 | 95 | 65.9 | 0.99 | 26.99
DHH072* | 6 | 2200 | 80 | 63 | 95 | 66.9 | 0.91 | 25.14
DHH072* | 6 | 2200 | 80 | 67 | 95 | 69 | 0.76 | 21.69
DHH072* | 6 | 2200 | 80 | 71 | 95 | 72.2 | 0.6 | 18.1
DHH072* | 6 | 2200 | 80 | 59 | 105 | 62.1 | 1 | 25.64
DHH072* | 6 | 2200 | 80 | 63 | 105 | 63 | 0.96 | 24.9
DHH072* | 6 | 2200 | 80 | 67 | 105 | 65.1 | 0.8 | 21.44
DHH072* | 6 | 2200 | 80 | 71 | 105 | 68.3 | 0.6 | 17.9
DHH072* | 6 | 2200 | 80 | 59 | 115 | 58.5 | 1 | 24.19
DHH072* | 6 | 2200 | 80 | 63 | 115 | 59.5 | 1 | 24.6
DHH072* | 6 | 2200 | 80 | 67 | 115 | 61.6 | 0.89 | 22.6
DHH072* | 6 | 2200 | 80 | 71 | 115 | 64.8 | 0.7 | 19
DHH072* | 6 | 2200 | 85 | 59 | 65 | 72.7 | 1 | 30.05
DHH072* | 6 | 2200 | 85 | 63 | 65 | 73.7 | 0.95 | 28.85
DHH072* | 6 | 2200 | 85 | 67 | 65 | 75.8 | 0.81 | 25.39
DHH072* | 6 | 2200 | 85 | 71 | 65 | 79 | 0.7 | 21.8
DHH072* | 6 | 2200 | 85 | 59 | 75 | 72.1 | 1 | 29.79
DHH072* | 6 | 2200 | 85 | 63 | 75 | 73.1 | 0.95 | 28.8
DHH072* | 6 | 2200 | 85 | 67 | 75 | 75.2 | 0.82 | 25.34
DHH072* | 6 | 2200 | 85 | 71 | 75 | 78.4 | 0.7 | 21.8
DHH072* | 6 | 2200 | 85 | 59 | 85 | 70.2 | 1 | 29.03
DHH072* | 6 | 2200 | 85 | 63 | 85 | 71.2 | 0.99 | 29.06
DHH072* | 6 | 2200 | 85 | 67 | 85 | 73.3 | 0.84 | 25.6
DHH072* | 6 | 2200 | 85 | 71 | 85 | 76.5 | 0.7 | 22
DHH072* | 6 | 2200 | 85 | 59 | 95 | 67.1 | 1 | 27.72
DHH072* | 6 | 2200 | 85 | 63 | 95 | 68.1 | 1 | 28.13
DHH072* | 6 | 2200 | 85 | 67 | 95 | 70.2 | 0.87 | 25.32
DHH072* | 6 | 2200 | 85 | 71 | 95 | 73.4 | 0.7 | 21.7
DHH072* | 6 | 2200 | 85 | 59 | 105 | 63.2 | 1 | 26.13
DHH072* | 6 | 2200 | 85 | 63 | 105 | 64.2 | 1 | 26.54
DHH072* | 6 | 2200 | 85 | 67 | 105 | 66.3 | 0.91 | 25.07
DHH072* | 6 | 2200 | 85 | 71 | 105 | 69.5 | 0.7 | 21.5
DHH072* | 6 | 2200 | 85 | 59 | 115 | 59.7 | 1 | 24.68
DHH072* | 6 | 2200 | 85 | 63 | 115 | 60.7 | 1 | 25.09
DHH072* | 6 | 2200 | 85 | 67 | 115 | 62.8 | 1 | 25.95
DHH072* | 6 | 2200 | 85 | 71 | 115 | 66 | 0.8 | 22.7
DHH072* | 6 | 3000 | 70 | 59 | 65 | 74.7 | 0.73 | 16.41
DHH072* | 6 | 3000 | 70 | 63 | 65 | 75.7 | 0.64 | 14.56
DHH072* | 6 | 3000 | 70 | 67 | 65 | 77.8 | 0.47 | 11.11
DHH072* | 6 | 3000 | 70 | 59 | 75 | 74 | 0.73 | 16.36
DHH072* | 6 | 3000 | 70 | 63 | 75 | 75 | 0.64 | 14.51
DHH072* | 6 | 3000 | 70 | 67 | 75 | 77.1 | 0.47 | 11.06
DHH072* | 6 | 3000 | 70 | 59 | 85 | 72.2 | 0.76 | 16.62
DHH072* | 6 | 3000 | 70 | 63 | 85 | 73.2 | 0.67 | 14.77
DHH072* | 6 | 3000 | 70 | 67 | 85 | 75.3 | 0.5 | 11.32
DHH072* | 6 | 3000 | 70 | 59 | 95 | 69.1 | 0.78 | 16.35
DHH072* | 6 | 3000 | 70 | 63 | 95 | 70 | 0.68 | 14.49
DHH072* | 6 | 3000 | 70 | 67 | 95 | 72.1 | 0.5 | 11.04
DHH072* | 6 | 3000 | 70 | 59 | 105 | 65.2 | 0.81 | 16.1
DHH072* | 6 | 3000 | 70 | 63 | 105 | 66.2 | 0.71 | 14.25
DHH072* | 6 | 3000 | 70 | 67 | 105 | 68.3 | 0.52 | 10.79
DHH072* | 6 | 3000 | 70 | 59 | 115 | 61.7 | 0.92 | 17.26
DHH072* | 6 | 3000 | 70 | 63 | 115 | 62.7 | 0.81 | 15.41
DHH072* | 6 | 3000 | 70 | 67 | 115 | 64.8 | 0.61 | 11.95
DHH072* | 6 | 3000 | 75 | 59 | 65 | 75 | 0.9 | 20.48
DHH072* | 6 | 3000 | 75 | 63 | 65 | 76 | 0.81 | 18.63
DHH072* | 6 | 3000 | 75 | 67 | 65 | 78.1 | 0.64 | 15.18
DHH072* | 6 | 3000 | 75 | 71 | 65 | 81.3 | 0.5 | 11.6
DHH072* | 6 | 3000 | 75 | 59 | 75 | 74.4 | 0.91 | 20.43
DHH072* | 6 | 3000 | 75 | 63 | 75 | 75.4 | 0.81 | 18.58
DHH072* | 6 | 3000 | 75 | 67 | 75 | 77.5 | 0.64 | 15.13
DHH072* | 6 | 3000 | 75 | 71 | 75 | 80.7 | 0.5 | 11.5
DHH072* | 6 | 3000 | 75 | 59 | 85 | 72.6 | 0.94 | 20.69
DHH072* | 6 | 3000 | 75 | 63 | 85 | 73.6 | 0.85 | 18.84
DHH072* | 6 | 3000 | 75 | 67 | 85 | 75.7 | 0.67 | 15.39
DHH072* | 6 | 3000 | 75 | 71 | 85 | 78.9 | 0.5 | 11.8
DHH072* | 6 | 3000 | 75 | 59 | 95 | 69.4 | 0.97 | 20.41
DHH072* | 6 | 3000 | 75 | 63 | 95 | 70.4 | 0.87 | 18.56
DHH072* | 6 | 3000 | 75 | 67 | 95 | 72.5 | 0.69 | 15.11
DHH072* | 6 | 3000 | 75 | 71 | 95 | 75.7 | 0.5 | 11.5
DHH072* | 6 | 3000 | 75 | 59 | 105 | 65.6 | 1 | 19.87
DHH072* | 6 | 3000 | 75 | 63 | 105 | 66.6 | 0.91 | 18.32
DHH072* | 6 | 3000 | 75 | 67 | 105 | 68.7 | 0.71 | 14.86
DHH072* | 6 | 3000 | 75 | 71 | 105 | 71.9 | 0.5 | 11.3
DHH072* | 6 | 3000 | 75 | 59 | 115 | 62 | 1 | 18.8
DHH072* | 6 | 3000 | 75 | 63 | 115 | 63 | 1 | 19.1
DHH072* | 6 | 3000 | 75 | 67 | 115 | 65.1 | 0.81 | 16.02
DHH072* | 6 | 3000 | 75 | 71 | 115 | 68.3 | 0.6 | 12.4
DHH072* | 6 | 3000 | 80 | 59 | 65 | 75.4 | 1 | 22.85
DHH072* | 6 | 3000 | 80 | 63 | 65 | 76.4 | 0.98 | 22.73
DHH072* | 6 | 3000 | 80 | 67 | 65 | 78.5 | 0.81 | 19.27
DHH072* | 6 | 3000 | 80 | 71 | 65 | 81.7 | 0.6 | 15.7
DHH072* | 6 | 3000 | 80 | 59 | 75 | 74.8 | 1 | 22.66
DHH072* | 6 | 3000 | 80 | 63 | 75 | 75.8 | 0.99 | 22.68
DHH072* | 6 | 3000 | 80 | 67 | 75 | 77.9 | 0.81 | 19.22
DHH072* | 6 | 3000 | 80 | 71 | 75 | 81.1 | 0.6 | 15.6
DHH072* | 6 | 3000 | 80 | 59 | 85 | 72.9 | 1 | 22.1
DHH072* | 6 | 3000 | 80 | 63 | 85 | 73.9 | 1 | 22.4
DHH072* | 6 | 3000 | 80 | 67 | 85 | 76 | 0.85 | 19.48
DHH072* | 6 | 3000 | 80 | 71 | 85 | 79.2 | 0.7 | 15.9
DHH072* | 6 | 3000 | 80 | 59 | 95 | 69.8 | 1 | 21.15
DHH072* | 6 | 3000 | 80 | 63 | 95 | 70.8 | 1 | 21.45
DHH072* | 6 | 3000 | 80 | 67 | 95 | 72.9 | 0.87 | 19.21
DHH072* | 6 | 3000 | 80 | 71 | 95 | 76.1 | 0.7 | 15.6
DHH072* | 6 | 3000 | 80 | 59 | 105 | 65.9 | 1 | 19.98
DHH072* | 6 | 3000 | 80 | 63 | 105 | 66.9 | 1 | 20.28
DHH072* | 6 | 3000 | 80 | 67 | 105 | 69 | 0.91 | 18.96
DHH072* | 6 | 3000 | 80 | 71 | 105 | 72.2 | 0.7 | 15.4
DHH072* | 6 | 3000 | 80 | 59 | 115 | 62.4 | 1 | 18.91
DHH072* | 6 | 3000 | 80 | 63 | 115 | 63.4 | 1 | 19.21
DHH072* | 6 | 3000 | 80 | 67 | 115 | 65.5 | 1 | 19.85
DHH072* | 6 | 3000 | 80 | 71 | 115 | 68.7 | 0.8 | 16.5
DHH072* | 6 | 3000 | 85 | 59 | 65 | 76.6 | 1 | 23.21
DHH072* | 6 | 3000 | 85 | 63 | 65 | 77.6 | 1 | 23.51
DHH072* | 6 | 3000 | 85 | 67 | 65 | 79.7 | 0.95 | 22.91
DHH072* | 6 | 3000 | 85 | 71 | 65 | 82.9 | 0.8 | 19.3
DHH072* | 6 | 3000 | 85 | 59 | 75 | 76 | 1 | 23.02
DHH072* | 6 | 3000 | 85 | 63 | 75 | 76.9 | 1 | 23.32
DHH072* | 6 | 3000 | 85 | 67 | 75 | 79 | 0.95 | 22.86
DHH072* | 6 | 3000 | 85 | 71 | 75 | 82.2 | 0.8 | 19.3
DHH072* | 6 | 3000 | 85 | 59 | 85 | 74.1 | 1 | 22.46
DHH072* | 6 | 3000 | 85 | 63 | 85 | 75.1 | 1 | 22.76
DHH072* | 6 | 3000 | 85 | 67 | 85 | 77.2 | 0.99 | 23.12
DHH072* | 6 | 3000 | 85 | 71 | 85 | 80.4 | 0.8 | 19.5
DHH072* | 6 | 3000 | 85 | 59 | 95 | 71 | 1 | 21.5
DHH072* | 6 | 3000 | 85 | 63 | 95 | 72 | 1 | 21.8
DHH072* | 6 | 3000 | 85 | 67 | 95 | 74.1 | 1 | 22.44
DHH072* | 6 | 3000 | 85 | 71 | 95 | 77.3 | 0.8 | 19.3
DHH072* | 6 | 3000 | 85 | 59 | 105 | 67.1 | 1 | 20.34
DHH072* | 6 | 3000 | 85 | 63 | 105 | 68.1 | 1 | 20.64
DHH072* | 6 | 3000 | 85 | 67 | 105 | 70.2 | 1 | 21.27
DHH072* | 6 | 3000 | 85 | 71 | 105 | 73.4 | 0.9 | 19
DHH072* | 6 | 3000 | 85 | 59 | 115 | 63.6 | 1 | 19.27
DHH072* | 6 | 3000 | 85 | 63 | 115 | 64.6 | 1 | 19.57
DHH072* | 6 | 3000 | 85 | 67 | 115 | 66.7 | 1 | 20.21
DHH072* | 6 | 3000 | 85 | 71 | 115 | 69.9 | 1 | 20.2
DVH090* | 7.5 | 2550 | 70 | 57 | 23 | 92.3 | 0.86 | 28.38
DVH090* | 7.5 | 2550 | 70 | 61 | 23 | 100.8 | 0.67 | 24.1
DVH090* | 7.5 | 2550 | 70 | 64 | 23 | 108.8 | 0.52 | 20.14
DVH090* | 7.5 | 2550 | 70 | 67 | 23 | 114.6 | 0.41 | 16.83
DVH090* | 7.5 | 2550 | 70 | 57 | 30 | 92.2 | 0.86 | 28.31
DVH090* | 7.5 | 2550 | 70 | 61 | 30 | 100.6 | 0.67 | 24.06
DVH090* | 7.5 | 2550 | 70 | 64 | 30 | 108.6 | 0.52 | 20.11
DVH090* | 7.5 | 2550 | 70 | 67 | 30 | 114.4 | 0.41 | 16.79
DVH090* | 7.5 | 2550 | 70 | 57 | 40 | 91.9 | 0.86 | 28.24
DVH090* | 7.5 | 2550 | 70 | 61 | 40 | 100.3 | 0.67 | 23.99
DVH090* | 7.5 | 2550 | 70 | 64 | 40 | 108.3 | 0.52 | 20.04
DVH090* | 7.5 | 2550 | 70 | 67 | 40 | 114 | 0.41 | 16.76
DVH090* | 7.5 | 2550 | 70 | 57 | 50 | 91.6 | 0.86 | 28.13
DVH090* | 7.5 | 2550 | 70 | 61 | 50 | 100 | 0.67 | 23.92
DVH090* | 7.5 | 2550 | 70 | 64 | 50 | 107.9 | 0.52 | 20
DVH090* | 7.5 | 2550 | 70 | 67 | 50 | 113.7 | 0.41 | 16.68
DVH090* | 7.5 | 2550 | 70 | 57 | 54 | 91.5 | 0.86 | 28.09
DVH090* | 7.5 | 2550 | 70 | 61 | 54 | 99.9 | 0.67 | 23.89
DVH090* | 7.5 | 2550 | 70 | 64 | 54 | 107.8 | 0.52 | 19.96
DVH090* | 7.5 | 2550 | 70 | 67 | 54 | 113.6 | 0.41 | 16.68
DVH090* | 7.5 | 2550 | 70 | 57 | 58 | 91.1 | 0.86 | 27.99
DVH090* | 7.5 | 2550 | 70 | 61 | 58 | 99.5 | 0.67 | 23.78
DVH090* | 7.5 | 2550 | 70 | 64 | 58 | 107.3 | 0.52 | 19.89
DVH090* | 7.5 | 2550 | 70 | 67 | 58 | 113.1 | 0.41 | 16.61
DVH090* | 7.5 | 2550 | 70 | 57 | 62 | 90.1 | 0.86 | 27.7
DVH090* | 7.5 | 2550 | 70 | 61 | 62 | 98.3 | 0.67 | 23.57
DVH090* | 7.5 | 2550 | 70 | 64 | 62 | 105.8 | 0.52 | 19.75
DVH090* | 7.5 | 2550 | 70 | 67 | 62 | 111.5 | 0.42 | 16.51
DVH090* | 7.5 | 2550 | 70 | 57 | 66 | 89 | 0.87 | 27.45
DVH090* | 7.5 | 2550 | 70 | 61 | 66 | 97.1 | 0.67 | 23.35
DVH090* | 7.5 | 2550 | 70 | 64 | 66 | 104.3 | 0.53 | 19.61
DVH090* | 7.5 | 2550 | 70 | 67 | 66 | 109.8 | 0.42 | 16.36
DVH090* | 7.5 | 2550 | 70 | 57 | 70 | 87.9 | 0.87 | 27.24
DVH090* | 7.5 | 2550 | 70 | 61 | 70 | 96 | 0.68 | 23.14
DVH090* | 7.5 | 2550 | 70 | 64 | 70 | 102.7 | 0.53 | 19.47
DVH090* | 7.5 | 2550 | 70 | 67 | 70 | 108.2 | 0.42 | 16.26
DVH090* | 7.5 | 2550 | 70 | 57 | 72 | 87.4 | 0.87 | 27.09
DVH090* | 7.5 | 2550 | 70 | 61 | 72 | 95.4 | 0.68 | 23.03
DVH090* | 7.5 | 2550 | 70 | 64 | 72 | 101.9 | 0.53 | 19.39
DVH090* | 7.5 | 2550 | 70 | 67 | 72 | 107.4 | 0.42 | 16.19
DVH090* | 7.5 | 2550 | 70 | 57 | 75 | 86.6 | 0.87 | 26.92
DVH090* | 7.5 | 2550 | 70 | 61 | 75 | 94.5 | 0.68 | 22.85
DVH090* | 7.5 | 2550 | 70 | 64 | 75 | 100.8 | 0.54 | 19.29
DVH090* | 7.5 | 2550 | 70 | 67 | 75 | 106.2 | 0.43 | 16.11
DVH090* | 7.5 | 2550 | 70 | 57 | 79 | 85.5 | 0.87 | 26.67
DVH090* | 7.5 | 2550 | 70 | 61 | 79 | 93.3 | 0.68 | 22.64
DVH090* | 7.5 | 2550 | 70 | 64 | 79 | 99.2 | 0.54 | 19.11
DVH090* | 7.5 | 2550 | 70 | 67 | 79 | 104.6 | 0.43 | 15.97
DVH090* | 7.5 | 2550 | 70 | 57 | 83 | 84.4 | 0.88 | 26.42
DVH090* | 7.5 | 2550 | 70 | 61 | 83 | 92.2 | 0.68 | 22.42
DVH090* | 7.5 | 2550 | 70 | 64 | 83 | 97.7 | 0.54 | 18.97
DVH090* | 7.5 | 2550 | 70 | 67 | 83 | 102.9 | 0.43 | 15.86
DVH090* | 7.5 | 2550 | 70 | 57 | 87 | 83.3 | 0.88 | 26.13
DVH090* | 7.5 | 2550 | 70 | 61 | 87 | 91 | 0.68 | 22.21
DVH090* | 7.5 | 2550 | 70 | 64 | 87 | 96.2 | 0.55 | 18.82
DVH090* | 7.5 | 2550 | 70 | 67 | 87 | 101.3 | 0.44 | 15.72
DVH090* | 7.5 | 2550 | 70 | 57 | 91 | 82.3 | 0.88 | 25.88
DVH090* | 7.5 | 2550 | 70 | 61 | 91 | 89.8 | 0.69 | 22
DVH090* | 7.5 | 2550 | 70 | 64 | 91 | 94.6 | 0.55 | 18.65
DVH090* | 7.5 | 2550 | 70 | 67 | 91 | 99.7 | 0.44 | 15.58
DVH090* | 7.5 | 2550 | 70 | 57 | 93 | 81.7 | 0.88 | 25.78
DVH090* | 7.5 | 2550 | 70 | 61 | 93 | 89.2 | 0.69 | 21.89
DVH090* | 7.5 | 2550 | 70 | 64 | 93 | 93.8 | 0.56 | 18.57
DVH090* | 7.5 | 2550 | 70 | 67 | 93 | 98.9 | 0.44 | 15.51
DVH090* | 7.5 | 2550 | 70 | 57 | 95 | 81.2 | 0.89 | 25.63
DVH090* | 7.5 | 2550 | 70 | 61 | 95 | 88.6 | 0.69 | 21.78
DVH090* | 7.5 | 2550 | 70 | 64 | 95 | 93.1 | 0.56 | 18.47
DVH090* | 7.5 | 2550 | 70 | 67 | 95 | 98.1 | 0.44 | 15.44
DVH090* | 7.5 | 2550 | 70 | 57 | 99 | 80.1 | 0.89 | 25.38
DVH090* | 7.5 | 2550 | 70 | 61 | 99 | 87.5 | 0.69 | 21.57
DVH090* | 7.5 | 2550 | 70 | 64 | 99 | 91.5 | 0.56 | 18.29
DVH090* | 7.5 | 2550 | 70 | 67 | 99 | 96.4 | 0.45 | 15.29
DVH090* | 7.5 | 2550 | 70 | 57 | 103 | 79 | 0.89 | 25.1
DVH090* | 7.5 | 2550 | 70 | 61 | 103 | 86.3 | 0.69 | 21.32
DVH090* | 7.5 | 2550 | 70 | 64 | 103 | 90 | 0.56 | 18.11
DVH090* | 7.5 | 2550 | 70 | 67 | 103 | 94.8 | 0.45 | 15.15
DVH090* | 7.5 | 2550 | 70 | 57 | 106 | 78.2 | 0.89 | 24.92
DVH090* | 7.5 | 2550 | 70 | 61 | 106 | 85.4 | 0.7 | 21.18
DVH090* | 7.5 | 2550 | 70 | 64 | 106 | 88.8 | 0.57 | 18
DVH090* | 7.5 | 2550 | 70 | 67 | 106 | 93.6 | 0.45 | 15.01
DVH090* | 7.5 | 2550 | 70 | 57 | 110 | 77.2 | 0.9 | 24.63
DVH090* | 7.5 | 2550 | 70 | 61 | 110 | 84.2 | 0.7 | 20.93
DVH090* | 7.5 | 2550 | 70 | 64 | 110 | 87.3 | 0.57 | 17.79
DVH090* | 7.5 | 2550 | 70 | 67 | 110 | 92 | 0.45 | 14.87
DVH090* | 7.5 | 2550 | 70 | 57 | 115 | 75.8 | 0.9 | 24.31
DVH090* | 7.5 | 2550 | 70 | 61 | 115 | 82.8 | 0.7 | 20.64
DVH090* | 7.5 | 2550 | 70 | 64 | 115 | 85.4 | 0.58 | 17.58
DVH090* | 7.5 | 2550 | 70 | 67 | 115 | 89.9 | 0.46 | 14.69
DVH090* | 7.5 | 2550 | 70 | 57 | 118 | 75 | 0.9 | 24.1
DVH090* | 7.5 | 2550 | 70 | 61 | 118 | 81.9 | 0.7 | 20.46
DVH090* | 7.5 | 2550 | 70 | 64 | 118 | 84.2 | 0.58 | 17.43
DVH090* | 7.5 | 2550 | 70 | 67 | 118 | 88.7 | 0.46 | 14.55
DVH090* | 7.5 | 2550 | 75 | 57 | 23 | 95 | 1 | 33.87
DVH090* | 7.5 | 2550 | 75 | 61 | 23 | 99.7 | 0.83 | 29.41
DVH090* | 7.5 | 2550 | 75 | 64 | 23 | 108.8 | 0.66 | 25.67
DVH090* | 7.5 | 2550 | 75 | 67 | 23 | 114.6 | 0.55 | 22.39
DVH090* | 7.5 | 2550 | 75 | 70 | 23 | 121.9 | 0.45 | 19.36
DVH090* | 7.5 | 2550 | 75 | 72 | 23 | 126.2 | 0.37 | 16.86
DVH090* | 7.5 | 2550 | 75 | 57 | 30 | 94.8 | 1 | 33.8
DVH090* | 7.5 | 2550 | 75 | 61 | 30 | 99.5 | 0.83 | 29.34
DVH090* | 7.5 | 2550 | 75 | 64 | 30 | 108.6 | 0.66 | 25.63
DVH090* | 7.5 | 2550 | 75 | 67 | 30 | 114.4 | 0.55 | 22.35
DVH090* | 7.5 | 2550 | 75 | 70 | 30 | 121.6 | 0.45 | 19.32
DVH090* | 7.5 | 2550 | 75 | 72 | 30 | 126 | 0.38 | 16.86
DVH090* | 7.5 | 2550 | 75 | 57 | 40 | 94.5 | 1 | 33.69
DVH090* | 7.5 | 2550 | 75 | 61 | 40 | 99.2 | 0.83 | 29.27
DVH090* | 7.5 | 2550 | 75 | 64 | 40 | 108.3 | 0.66 | 25.56
DVH090* | 7.5 | 2550 | 75 | 67 | 40 | 114 | 0.55 | 22.28
DVH090* | 7.5 | 2550 | 75 | 70 | 40 | 121.3 | 0.45 | 19.25
DVH090* | 7.5 | 2550 | 75 | 72 | 40 | 125.6 | 0.38 | 16.79
DVH090* | 7.5 | 2550 | 75 | 57 | 50 | 94.3 | 1 | 33.62
DVH090* | 7.5 | 2550 | 75 | 61 | 50 | 98.9 | 0.83 | 29.16
DVH090* | 7.5 | 2550 | 75 | 64 | 50 | 107.9 | 0.66 | 25.49
DVH090* | 7.5 | 2550 | 75 | 67 | 50 | 113.7 | 0.55 | 22.21
DVH090* | 7.5 | 2550 | 75 | 70 | 50 | 120.9 | 0.45 | 19.22
DVH090* | 7.5 | 2550 | 75 | 72 | 50 | 125.2 | 0.38 | 16.76
DVH090* | 7.5 | 2550 | 75 | 57 | 54 | 94.1 | 1 | 33.55
DVH090* | 7.5 | 2550 | 75 | 61 | 54 | 98.8 | 0.83 | 29.13
DVH090* | 7.5 | 2550 | 75 | 64 | 54 | 107.8 | 0.66 | 25.45
DVH090* | 7.5 | 2550 | 75 | 67 | 54 | 113.6 | 0.55 | 22.21
DVH090* | 7.5 | 2550 | 75 | 70 | 54 | 120.8 | 0.45 | 19.18
DVH090* | 7.5 | 2550 | 75 | 72 | 54 | 125.1 | 0.37 | 16.72
DVH090* | 7.5 | 2550 | 75 | 57 | 58 | 93.8 | 1 | 33.44
DVH090* | 7.5 | 2550 | 75 | 61 | 58 | 98.4 | 0.83 | 29.02
DVH090* | 7.5 | 2550 | 75 | 64 | 58 | 107.3 | 0.66 | 25.35
DVH090* | 7.5 | 2550 | 75 | 67 | 58 | 113.1 | 0.55 | 22.1
DVH090* | 7.5 | 2550 | 75 | 70 | 58 | 120.3 | 0.45 | 19.11
DVH090* | 7.5 | 2550 | 75 | 72 | 58 | 124.6 | 0.37 | 16.65
DVH090* | 7.5 | 2550 | 75 | 57 | 62 | 92.7 | 1 | 33.05
DVH090* | 7.5 | 2550 | 75 | 61 | 62 | 97.2 | 0.83 | 28.73
DVH090* | 7.5 | 2550 | 75 | 64 | 62 | 105.8 | 0.67 | 25.13
DVH090* | 7.5 | 2550 | 75 | 67 | 62 | 111.5 | 0.55 | 21.93
DVH090* | 7.5 | 2550 | 75 | 70 | 62 | 118.5 | 0.45 | 18.97
DVH090* | 7.5 | 2550 | 75 | 72 | 62 | 122.8 | 0.38 | 16.54
DVH090* | 7.5 | 2550 | 75 | 57 | 66 | 91.6 | 1 | 32.66
DVH090* | 7.5 | 2550 | 75 | 61 | 66 | 96.1 | 0.83 | 28.48
DVH090* | 7.5 | 2550 | 75 | 64 | 66 | 104.3 | 0.67 | 24.99
DVH090* | 7.5 | 2550 | 75 | 67 | 66 | 109.8 | 0.56 | 21.78
DVH090* | 7.5 | 2550 | 75 | 70 | 66 | 116.8 | 0.45 | 18.82
DVH090* | 7.5 | 2550 | 75 | 72 | 66 | 121 | 0.38 | 16.43
DVH090* | 7.5 | 2550 | 75 | 57 | 70 | 90.5 | 1 | 32.26
DVH090* | 7.5 | 2550 | 75 | 61 | 70 | 94.9 | 0.83 | 28.2
DVH090* | 7.5 | 2550 | 75 | 64 | 70 | 102.7 | 0.68 | 24.78
DVH090* | 7.5 | 2550 | 75 | 67 | 70 | 108.2 | 0.56 | 21.64
DVH090* | 7.5 | 2550 | 75 | 70 | 70 | 115.1 | 0.46 | 18.68
DVH090* | 7.5 | 2550 | 75 | 72 | 70 | 119.2 | 0.38 | 16.29
DVH090* | 7.5 | 2550 | 75 | 57 | 72 | 89.9 | 1 | 32.05
DVH090* | 7.5 | 2550 | 75 | 61 | 72 | 94.3 | 0.84 | 28.09
DVH090* | 7.5 | 2550 | 75 | 64 | 72 | 101.9 | 0.68 | 24.71
DVH090* | 7.5 | 2550 | 75 | 67 | 72 | 107.4 | 0.56 | 21.57
DVH090* | 7.5 | 2550 | 75 | 70 | 72 | 114.2 | 0.46 | 18.61
DVH090* | 7.5 | 2550 | 75 | 72 | 72 | 118.3 | 0.39 | 16.26
DVH090* | 7.5 | 2550 | 75 | 57 | 75 | 89.1 | 1 | 31.76
DVH090* | 7.5 | 2550 | 75 | 61 | 75 | 93.5 | 0.84 | 27.88
DVH090* | 7.5 | 2550 | 75 | 64 | 75 | 100.8 | 0.68 | 24.56
DVH090* | 7.5 | 2550 | 75 | 67 | 75 | 106.2 | 0.57 | 21.43
DVH090* | 7.5 | 2550 | 75 | 70 | 75 | 112.9 | 0.46 | 18.5
DVH090* | 7.5 | 2550 | 75 | 72 | 75 | 116.9 | 0.39 | 16.15
DVH090* | 7.5 | 2550 | 75 | 57 | 79 | 88 | 1 | 31.37
DVH090* | 7.5 | 2550 | 75 | 61 | 79 | 92.3 | 0.84 | 27.63
DVH090* | 7.5 | 2550 | 75 | 64 | 79 | 99.2 | 0.69 | 24.39
DVH090* | 7.5 | 2550 | 75 | 67 | 79 | 104.6 | 0.57 | 21.25
DVH090* | 7.5 | 2550 | 75 | 70 | 79 | 111.2 | 0.46 | 18.36
DVH090* | 7.5 | 2550 | 75 | 72 | 79 | 115.2 | 0.39 | 16.01
DVH090* | 7.5 | 2550 | 75 | 57 | 83 | 86.9 | 1 | 30.98
DVH090* | 7.5 | 2550 | 75 | 61 | 83 | 91.1 | 0.84 | 27.38
DVH090* | 7.5 | 2550 | 75 | 64 | 83 | 97.7 | 0.69 | 24.17
DVH090* | 7.5 | 2550 | 75 | 67 | 83 | 102.9 | 0.58 | 21.11
DVH090* | 7.5 | 2550 | 75 | 70 | 83 | 109.4 | 0.47 | 18.22
DVH090* | 7.5 | 2550 | 75 | 72 | 83 | 113.4 | 0.39 | 15.9
DVH090* | 7.5 | 2550 | 75 | 57 | 87 | 85.8 | 1 | 30.59
DVH090* | 7.5 | 2550 | 75 | 61 | 87 | 90 | 0.84 | 27.09
DVH090* | 7.5 | 2550 | 75 | 64 | 87 | 96.2 | 0.7 | 23.96
DVH090* | 7.5 | 2550 | 75 | 67 | 87 | 101.3 | 0.58 | 20.93
DVH090* | 7.5 | 2550 | 75 | 70 | 87 | 107.7 | 0.47 | 18.07
DVH090* | 7.5 | 2550 | 75 | 72 | 87 | 111.6 | 0.4 | 15.76
DVH090* | 7.5 | 2550 | 75 | 57 | 91 | 84.7 | 1 | 30.2
DVH090* | 7.5 | 2550 | 75 | 61 | 91 | 88.8 | 0.85 | 26.84
DVH090* | 7.5 | 2550 | 75 | 64 | 91 | 94.6 | 0.7 | 23.74
DVH090* | 7.5 | 2550 | 75 | 67 | 91 | 99.7 | 0.58 | 20.71
DVH090* | 7.5 | 2550 | 75 | 70 | 91 | 106 | 0.47 | 17.9
DVH090* | 7.5 | 2550 | 75 | 72 | 91 | 109.8 | 0.4 | 15.61
DVH090* | 7.5 | 2550 | 75 | 57 | 93 | 84.1 | 1 | 29.98
DVH090* | 7.5 | 2550 | 75 | 61 | 93 | 88.2 | 0.85 | 26.7
DVH090* | 7.5 | 2550 | 75 | 64 | 93 | 93.8 | 0.71 | 23.64
DVH090* | 7.5 | 2550 | 75 | 67 | 93 | 98.9 | 0.59 | 20.64
DVH090* | 7.5 | 2550 | 75 | 70 | 93 | 105.1 | 0.48 | 17.83
DVH090* | 7.5 | 2550 | 75 | 72 | 93 | 108.9 | 0.4 | 15.54
DVH090* | 7.5 | 2550 | 75 | 57 | 95 | 83.6 | 1 | 29.8
DVH090* | 7.5 | 2550 | 75 | 61 | 95 | 87.7 | 0.85 | 26.56
DVH090* | 7.5 | 2550 | 75 | 64 | 95 | 93.1 | 0.71 | 23.53
DVH090* | 7.5 | 2550 | 75 | 67 | 95 | 98.1 | 0.59 | 20.53
DVH090* | 7.5 | 2550 | 75 | 70 | 95 | 104.3 | 0.48 | 17.75
DVH090* | 7.5 | 2550 | 75 | 72 | 95 | 108 | 0.4 | 15.47
DVH090* | 7.5 | 2550 | 75 | 57 | 99 | 82.5 | 1 | 29.41
DVH090* | 7.5 | 2550 | 75 | 61 | 99 | 86.5 | 0.85 | 26.31
DVH090* | 7.5 | 2550 | 75 | 64 | 99 | 91.5 | 0.71 | 23.32
DVH090* | 7.5 | 2550 | 75 | 67 | 99 | 96.4 | 0.59 | 20.36
DVH090* | 7.5 | 2550 | 75 | 70 | 99 | 102.5 | 0.48 | 17.58
DVH090* | 7.5 | 2550 | 75 | 72 | 99 | 106.2 | 0.4 | 15.33
DVH090* | 7.5 | 2550 | 75 | 57 | 103 | 81.3 | 1 | 28.98
DVH090* | 7.5 | 2550 | 75 | 61 | 103 | 85.3 | 0.86 | 26.02
DVH090* | 7.5 | 2550 | 75 | 64 | 103 | 90 | 0.72 | 23.1
DVH090* | 7.5 | 2550 | 75 | 67 | 103 | 94.8 | 0.6 | 20.14
DVH090* | 7.5 | 2550 | 75 | 70 | 103 | 100.8 | 0.48 | 17.4
DVH090* | 7.5 | 2550 | 75 | 72 | 103 | 104.4 | 0.41 | 15.19
DVH090* | 7.5 | 2550 | 75 | 57 | 106 | 80.5 | 1 | 28.7
DVH090* | 7.5 | 2550 | 75 | 61 | 106 | 84.5 | 0.86 | 25.81
DVH090* | 7.5 | 2550 | 75 | 64 | 106 | 88.8 | 0.72 | 22.92
DVH090* | 7.5 | 2550 | 75 | 67 | 106 | 93.6 | 0.6 | 20
DVH090* | 7.5 | 2550 | 75 | 70 | 106 | 99.5 | 0.49 | 17.29
DVH090* | 7.5 | 2550 | 75 | 72 | 106 | 103.1 | 0.41 | 15.08
DVH090* | 7.5 | 2550 | 75 | 57 | 110 | 79.4 | 1 | 28.31
DVH090* | 7.5 | 2550 | 75 | 61 | 110 | 83.3 | 0.86 | 25.53
DVH090* | 7.5 | 2550 | 75 | 64 | 110 | 87.3 | 0.73 | 22.67
DVH090* | 7.5 | 2550 | 75 | 67 | 110 | 92 | 0.6 | 19.79
DVH090* | 7.5 | 2550 | 75 | 70 | 110 | 97.8 | 0.49 | 17.11
DVH090* | 7.5 | 2550 | 75 | 72 | 110 | 101.3 | 0.41 | 14.9
DVH090* | 7.5 | 2550 | 75 | 57 | 115 | 78 | 1 | 27.81
DVH090* | 7.5 | 2550 | 75 | 61 | 115 | 81.9 | 0.86 | 25.17
DVH090* | 7.5 | 2550 | 75 | 64 | 115 | 85.4 | 0.74 | 22.39
DVH090* | 7.5 | 2550 | 75 | 67 | 115 | 89.9 | 0.61 | 19.54
DVH090* | 7.5 | 2550 | 75 | 70 | 115 | 95.6 | 0.49 | 16.86
DVH090* | 7.5 | 2550 | 75 | 72 | 115 | 99 | 0.42 | 14.72
DVH090* | 7.5 | 2550 | 75 | 57 | 118 | 77.2 | 1 | 27.52
DVH090* | 7.5 | 2550 | 75 | 61 | 118 | 81 | 0.87 | 24.99
DVH090* | 7.5 | 2550 | 75 | 64 | 118 | 84.2 | 0.74 | 22.17
DVH090* | 7.5 | 2550 | 75 | 67 | 118 | 88.7 | 0.61 | 19.36
DVH090* | 7.5 | 2550 | 75 | 70 | 118 | 94.3 | 0.5 | 16.72
DVH090* | 7.5 | 2550 | 75 | 72 | 118 | 97.7 | 0.42 | 14.58
DVH090* | 7.5 | 2550 | 80 | 57 | 23 | 100.8 | 1 | 35.94
DVH090* | 7.5 | 2550 | 80 | 61 | 23 | 100.8 | 1 | 35.94
DVH090* | 7.5 | 2550 | 80 | 64 | 23 | 108.8 | 0.8 | 31.12
DVH090* | 7.5 | 2550 | 80 | 67 | 23 | 114.6 | 0.68 | 27.91
DVH090* | 7.5 | 2550 | 80 | 70 | 23 | 121.9 | 0.58 | 24.99
DVH090* | 7.5 | 2550 | 80 | 72 | 23 | 126.2 | 0.5 | 22.46
DVH090* | 7.5 | 2550 | 80 | 75 | 23 | 132.7 | 0.41 | 19.43
DVH090* | 7.5 | 2550 | 80 | 57 | 30 | 100.6 | 1 | 35.86
DVH090* | 7.5 | 2550 | 80 | 61 | 30 | 100.6 | 1 | 35.86
DVH090* | 7.5 | 2550 | 80 | 64 | 30 | 108.6 | 0.8 | 31.05
DVH090* | 7.5 | 2550 | 80 | 67 | 30 | 114.4 | 0.68 | 27.84
DVH090* | 7.5 | 2550 | 80 | 70 | 30 | 121.6 | 0.57 | 24.92
DVH090* | 7.5 | 2550 | 80 | 72 | 30 | 126 | 0.5 | 22.42
DVH090* | 7.5 | 2550 | 80 | 75 | 30 | 132.5 | 0.41 | 19.43
DVH090* | 7.5 | 2550 | 80 | 57 | 40 | 100.3 | 1 | 35.76
DVH090* | 7.5 | 2550 | 80 | 61 | 40 | 100.3 | 1 | 35.76
DVH090* | 7.5 | 2550 | 80 | 64 | 40 | 108.3 | 0.8 | 30.94
DVH090* | 7.5 | 2550 | 80 | 67 | 40 | 114 | 0.68 | 27.77
DVH090* | 7.5 | 2550 | 80 | 70 | 40 | 121.3 | 0.57 | 24.85
DVH090* | 7.5 | 2550 | 80 | 72 | 40 | 125.6 | 0.5 | 22.35
DVH090* | 7.5 | 2550 | 80 | 75 | 40 | 132.3 | 0.41 | 19.39
DVH090* | 7.5 | 2550 | 80 | 57 | 50 | 100 | 1 | 35.65
DVH090* | 7.5 | 2550 | 80 | 61 | 50 | 100 | 1 | 35.65
DVH090* | 7.5 | 2550 | 80 | 64 | 50 | 107.9 | 0.8 | 30.87
DVH090* | 7.5 | 2550 | 80 | 67 | 50 | 113.7 | 0.68 | 27.66
DVH090* | 7.5 | 2550 | 80 | 70 | 50 | 120.9 | 0.57 | 24.78
DVH090* | 7.5 | 2550 | 80 | 72 | 50 | 125.2 | 0.5 | 22.28
DVH090* | 7.5 | 2550 | 80 | 75 | 50 | 132.1 | 0.41 | 19.36
DVH090* | 7.5 | 2550 | 80 | 57 | 54 | 99.9 | 1 | 35.61
DVH090* | 7.5 | 2550 | 80 | 61 | 54 | 99.9 | 1 | 35.61
DVH090* | 7.5 | 2550 | 80 | 64 | 54 | 107.8 | 0.8 | 30.84
DVH090* | 7.5 | 2550 | 80 | 67 | 54 | 113.6 | 0.68 | 27.66
DVH090* | 7.5 | 2550 | 80 | 70 | 54 | 120.8 | 0.57 | 24.74
DVH090* | 7.5 | 2550 | 80 | 72 | 54 | 125.1 | 0.5 | 22.28
DVH090* | 7.5 | 2550 | 80 | 75 | 54 | 132 | 0.41 | 19.32
DVH090* | 7.5 | 2550 | 80 | 57 | 58 | 99.5 | 1 | 35.47
DVH090* | 7.5 | 2550 | 80 | 61 | 58 | 99.5 | 1 | 35.47
DVH090* | 7.5 | 2550 | 80 | 64 | 58 | 107.3 | 0.8 | 30.7
DVH090* | 7.5 | 2550 | 80 | 67 | 58 | 113.1 | 0.68 | 27.52
DVH090* | 7.5 | 2550 | 80 | 70 | 58 | 120.3 | 0.57 | 24.63
DVH090* | 7.5 | 2550 | 80 | 72 | 58 | 124.6 | 0.5 | 22.17
DVH090* | 7.5 | 2550 | 80 | 75 | 58 | 131.2 | 0.41 | 19.22
DVH090* | 7.5 | 2550 | 80 | 57 | 62 | 98.3 | 1 | 35.04
DVH090* | 7.5 | 2550 | 80 | 61 | 62 | 98.3 | 1 | 35.04
DVH090* | 7.5 | 2550 | 80 | 64 | 62 | 105.8 | 0.81 | 30.48
DVH090* | 7.5 | 2550 | 80 | 67 | 62 | 111.5 | 0.69 | 27.34
DVH090* | 7.5 | 2550 | 80 | 70 | 62 | 118.5 | 0.58 | 24.46
DVH090* | 7.5 | 2550 | 80 | 72 | 62 | 122.8 | 0.5 | 22
DVH090* | 7.5 | 2550 | 80 | 75 | 62 | 129.4 | 0.41 | 19
DVH090* | 7.5 | 2550 | 80 | 57 | 66 | 97.1 | 1 | 34.62
DVH090* | 7.5 | 2550 | 80 | 61 | 66 | 97.1 | 1 | 34.62
DVH090* | 7.5 | 2550 | 80 | 64 | 66 | 104.3 | 0.81 | 30.27
DVH090* | 7.5 | 2550 | 80 | 67 | 66 | 109.8 | 0.69 | 27.13
DVH090* | 7.5 | 2550 | 80 | 70 | 66 | 116.8 | 0.58 | 24.31
DVH090* | 7.5 | 2550 | 80 | 72 | 66 | 121 | 0.51 | 21.85
DVH090* | 7.5 | 2550 | 80 | 75 | 66 | 127.6 | 0.41 | 18.79
DVH090* | 7.5 | 2550 | 80 | 57 | 70 | 96 | 1 | 34.22
DVH090* | 7.5 | 2550 | 80 | 61 | 70 | 96 | 1 | 34.22
DVH090* | 7.5 | 2550 | 80 | 64 | 70 | 102.7 | 0.82 | 30.05
DVH090* | 7.5 | 2550 | 80 | 67 | 70 | 108.2 | 0.7 | 26.95
DVH090* | 7.5 | 2550 | 80 | 70 | 70 | 115.1 | 0.59 | 24.14
DVH090* | 7.5 | 2550 | 80 | 72 | 70 | 119.2 | 0.51 | 21.71
DVH090* | 7.5 | 2550 | 80 | 75 | 70 | 125.7 | 0.41 | 18.57
DVH090* | 7.5 | 2550 | 80 | 57 | 72 | 95.4 | 1 | 34.01
DVH090* | 7.5 | 2550 | 80 | 61 | 72 | 95.4 | 1 | 34.01
DVH090* | 7.5 | 2550 | 80 | 64 | 72 | 101.9 | 0.82 | 29.95
DVH090* | 7.5 | 2550 | 80 | 67 | 72 | 107.4 | 0.7 | 26.84
DVH090* | 7.5 | 2550 | 80 | 70 | 72 | 114.2 | 0.59 | 24.03
DVH090* | 7.5 | 2550 | 80 | 72 | 72 | 118.3 | 0.51 | 21.6
DVH090* | 7.5 | 2550 | 80 | 75 | 72 | 124.8 | 0.42 | 18.47
DVH090* | 7.5 | 2550 | 80 | 57 | 75 | 94.5 | 1 | 33.69
DVH090* | 7.5 | 2550 | 80 | 61 | 75 | 94.5 | 1 | 33.69
DVH090* | 7.5 | 2550 | 80 | 64 | 75 | 100.8 | 0.83 | 29.77
DVH090* | 7.5 | 2550 | 80 | 67 | 75 | 106.2 | 0.71 | 26.7
DVH090* | 7.5 | 2550 | 80 | 70 | 75 | 112.9 | 0.59 | 23.89
DVH090* | 7.5 | 2550 | 80 | 72 | 75 | 116.9 | 0.52 | 21.5
DVH090* | 7.5 | 2550 | 80 | 75 | 75 | 123.4 | 0.42 | 18.29
DVH090* | 7.5 | 2550 | 80 | 57 | 79 | 93.3 | 1 | 33.26
DVH090* | 7.5 | 2550 | 80 | 61 | 79 | 93.3 | 1 | 33.26
DVH090* | 7.5 | 2550 | 80 | 64 | 79 | 99.2 | 0.83 | 29.52
DVH090* | 7.5 | 2550 | 80 | 67 | 79 | 104.6 | 0.71 | 26.49
DVH090* | 7.5 | 2550 | 80 | 70 | 79 | 111.2 | 0.6 | 23.71
DVH090* | 7.5 | 2550 | 80 | 72 | 79 | 115.2 | 0.52 | 21.32
DVH090* | 7.5 | 2550 | 80 | 75 | 79 | 121.6 | 0.42 | 18.07
DVH090* | 7.5 | 2550 | 80 | 57 | 83 | 92.2 | 1 | 32.87
DVH090* | 7.5 | 2550 | 80 | 61 | 83 | 92.2 | 1 | 32.87
DVH090* | 7.5 | 2550 | 80 | 64 | 83 | 97.7 | 0.84 | 29.27
DVH090* | 7.5 | 2550 | 80 | 67 | 83 | 102.9 | 0.72 | 26.27
DVH090* | 7.5 | 2550 | 80 | 70 | 83 | 109.4 | 0.6 | 23.53
DVH090* | 7.5 | 2550 | 80 | 72 | 83 | 113.4 | 0.52 | 21.14
DVH090* | 7.5 | 2550 | 80 | 75 | 83 | 119.8 | 0.42 | 17.86
DVH090* | 7.5 | 2550 | 80 | 57 | 87 | 91 | 1 | 32.44
DVH090* | 7.5 | 2550 | 80 | 61 | 87 | 91 | 1 | 32.44
DVH090* | 7.5 | 2550 | 80 | 64 | 87 | 96.2 | 0.85 | 29.06
DVH090* | 7.5 | 2550 | 80 | 67 | 87 | 101.3 | 0.72 | 26.06
DVH090* | 7.5 | 2550 | 80 | 70 | 87 | 107.7 | 0.61 | 23.32
DVH090* | 7.5 | 2550 | 80 | 72 | 87 | 111.6 | 0.53 | 20.96
DVH090* | 7.5 | 2550 | 80 | 75 | 87 | 117.9 | 0.42 | 17.65
DVH090* | 7.5 | 2550 | 80 | 57 | 91 | 89.8 | 1 | 32.01
DVH090* | 7.5 | 2550 | 80 | 61 | 91 | 89.8 | 1 | 32.01
DVH090* | 7.5 | 2550 | 80 | 64 | 91 | 94.6 | 0.85 | 28.77
DVH090* | 7.5 | 2550 | 80 | 67 | 91 | 99.7 | 0.73 | 25.81
DVH090* | 7.5 | 2550 | 80 | 70 | 91 | 106 | 0.61 | 23.1
DVH090* | 7.5 | 2550 | 80 | 72 | 91 | 109.8 | 0.53 | 20.78
DVH090* | 7.5 | 2550 | 80 | 75 | 91 | 116.1 | 0.42 | 17.43
DVH090* | 7.5 | 2550 | 80 | 57 | 93 | 89.2 | 1 | 31.8
DVH090* | 7.5 | 2550 | 80 | 61 | 93 | 89.2 | 1 | 31.8
DVH090* | 7.5 | 2550 | 80 | 64 | 93 | 93.8 | 0.86 | 28.66
DVH090* | 7.5 | 2550 | 80 | 67 | 93 | 98.9 | 0.73 | 25.7
DVH090* | 7.5 | 2550 | 80 | 70 | 93 | 105.1 | 0.61 | 22.99
DVH090* | 7.5 | 2550 | 80 | 72 | 93 | 108.9 | 0.53 | 20.71
DVH090* | 7.5 | 2550 | 80 | 75 | 93 | 115.2 | 0.42 | 17.33
DVH090* | 7.5 | 2550 | 80 | 57 | 95 | 88.6 | 1 | 31.59
DVH090* | 7.5 | 2550 | 80 | 61 | 95 | 88.6 | 1 | 31.59
DVH090* | 7.5 | 2550 | 80 | 64 | 95 | 93.1 | 0.86 | 28.52
DVH090* | 7.5 | 2550 | 80 | 67 | 95 | 98.1 | 0.73 | 25.6
DVH090* | 7.5 | 2550 | 80 | 70 | 95 | 104.3 | 0.62 | 22.92
DVH090* | 7.5 | 2550 | 80 | 72 | 95 | 108 | 0.54 | 20.61
DVH090* | 7.5 | 2550 | 80 | 75 | 95 | 114.3 | 0.42 | 17.22
DVH090* | 7.5 | 2550 | 80 | 57 | 99 | 87.5 | 1 | 31.19
DVH090* | 7.5 | 2550 | 80 | 61 | 99 | 87.5 | 1 | 31.19
DVH090* | 7.5 | 2550 | 80 | 64 | 99 | 91.5 | 0.87 | 28.27
DVH090* | 7.5 | 2550 | 80 | 67 | 99 | 96.4 | 0.74 | 25.35
DVH090* | 7.5 | 2550 | 80 | 70 | 99 | 102.5 | 0.62 | 22.67
DVH090* | 7.5 | 2550 | 80 | 72 | 99 | 106.2 | 0.54 | 20.39
DVH090* | 7.5 | 2550 | 80 | 75 | 99 | 112.4 | 0.42 | 16.97
DVH090* | 7.5 | 2550 | 80 | 57 | 103 | 86.3 | 1 | 30.77
DVH090* | 7.5 | 2550 | 80 | 61 | 103 | 86.3 | 1 | 30.77
DVH090* | 7.5 | 2550 | 80 | 64 | 103 | 90 | 0.87 | 27.99
DVH090* | 7.5 | 2550 | 80 | 67 | 103 | 94.8 | 0.74 | 25.1
DVH090* | 7.5 | 2550 | 80 | 70 | 103 | 100.8 | 0.62 | 22.46
DVH090* | 7.5 | 2550 | 80 | 72 | 103 | 104.4 | 0.54 | 20.21
DVH090* | 7.5 | 2550 | 80 | 75 | 103 | 110.6 | 0.42 | 16.76
DVH090* | 7.5 | 2550 | 80 | 57 | 106 | 85.4 | 1 | 30.45
DVH090* | 7.5 | 2550 | 80 | 61 | 106 | 85.4 | 1 | 30.45
DVH090* | 7.5 | 2550 | 80 | 64 | 106 | 88.8 | 0.88 | 27.77
DVH090* | 7.5 | 2550 | 80 | 67 | 106 | 93.6 | 0.75 | 24.92
DVH090* | 7.5 | 2550 | 80 | 70 | 106 | 99.5 | 0.63 | 22.32
DVH090* | 7.5 | 2550 | 80 | 72 | 106 | 103.1 | 0.55 | 20.07
DVH090* | 7.5 | 2550 | 80 | 75 | 106 | 109.2 | 0.43 | 16.58
DVH090* | 7.5 | 2550 | 80 | 57 | 110 | 84.2 | 1 | 30.02
DVH090* | 7.5 | 2550 | 80 | 61 | 110 | 84.2 | 1 | 30.02
DVH090* | 7.5 | 2550 | 80 | 64 | 110 | 87.3 | 0.88 | 27.49
DVH090* | 7.5 | 2550 | 80 | 67 | 110 | 92 | 0.75 | 24.63
DVH090* | 7.5 | 2550 | 80 | 70 | 110 | 97.8 | 0.63 | 22.07
DVH090* | 7.5 | 2550 | 80 | 72 | 110 | 101.3 | 0.55 | 19.86
DVH090* | 7.5 | 2550 | 80 | 75 | 110 | 107.4 | 0.43 | 16.36
DVH090* | 7.5 | 2550 | 80 | 57 | 115 | 82.8 | 1 | 29.52
DVH090* | 7.5 | 2550 | 80 | 61 | 115 | 82.8 | 1 | 29.52
DVH090* | 7.5 | 2550 | 80 | 64 | 115 | 85.4 | 0.89 | 27.13
DVH090* | 7.5 | 2550 | 80 | 67 | 115 | 89.9 | 0.76 | 24.31
DVH090* | 7.5 | 2550 | 80 | 70 | 115 | 95.6 | 0.64 | 21.78
DVH090* | 7.5 | 2550 | 80 | 72 | 115 | 99 | 0.55 | 19.57
DVH090* | 7.5 | 2550 | 80 | 75 | 115 | 105.1 | 0.43 | 16.08
DVH090* | 7.5 | 2550 | 80 | 57 | 118 | 81.9 | 1 | 29.2
DVH090* | 7.5 | 2550 | 80 | 61 | 118 | 81.9 | 1 | 29.2
DVH090* | 7.5 | 2550 | 80 | 64 | 118 | 84.2 | 0.9 | 26.88
DVH090* | 7.5 | 2550 | 80 | 67 | 118 | 88.7 | 0.76 | 24.1
DVH090* | 7.5 | 2550 | 80 | 70 | 118 | 94.3 | 0.64 | 21.6
DVH090* | 7.5 | 2550 | 80 | 72 | 118 | 97.7 | 0.56 | 19.43
DVH090* | 7.5 | 2550 | 80 | 75 | 118 | 103.7 | 0.43 | 15.9
DVH090* | 7.5 | 2550 | 85 | 57 | 23 | 106.7 | 1 | 38.04
DVH090* | 7.5 | 2550 | 85 | 61 | 23 | 106.7 | 1 | 38.04
DVH090* | 7.5 | 2550 | 85 | 64 | 23 | 110 | 0.91 | 35.61
DVH090* | 7.5 | 2550 | 85 | 67 | 23 | 114.6 | 0.82 | 33.3
DVH090* | 7.5 | 2550 | 85 | 70 | 23 | 121.9 | 0.7 | 30.55
DVH090* | 7.5 | 2550 | 85 | 72 | 23 | 126.2 | 0.62 | 27.99
DVH090* | 7.5 | 2550 | 85 | 75 | 23 | 132.7 | 0.53 | 25.1
DVH090* | 7.5 | 2550 | 85 | 57 | 30 | 106.5 | 1 | 37.97
DVH090* | 7.5 | 2550 | 85 | 61 | 30 | 106.5 | 1 | 37.97
DVH090* | 7.5 | 2550 | 85 | 64 | 30 | 109.8 | 0.91 | 35.54
DVH090* | 7.5 | 2550 | 85 | 67 | 30 | 114.4 | 0.81 | 33.23
DVH090* | 7.5 | 2550 | 85 | 70 | 30 | 121.6 | 0.7 | 30.48
DVH090* | 7.5 | 2550 | 85 | 72 | 30 | 126 | 0.62 | 27.95
DVH090* | 7.5 | 2550 | 85 | 75 | 30 | 132.5 | 0.53 | 25.06
DVH090* | 7.5 | 2550 | 85 | 57 | 40 | 106.1 | 1 | 37.83
DVH090* | 7.5 | 2550 | 85 | 61 | 40 | 106.2 | 1 | 37.86
DVH090* | 7.5 | 2550 | 85 | 64 | 40 | 109.5 | 0.91 | 35.44
DVH090* | 7.5 | 2550 | 85 | 67 | 40 | 114 | 0.82 | 33.16
DVH090* | 7.5 | 2550 | 85 | 70 | 40 | 121.3 | 0.7 | 30.37
DVH090* | 7.5 | 2550 | 85 | 72 | 40 | 125.6 | 0.62 | 27.84
DVH090* | 7.5 | 2550 | 85 | 75 | 40 | 132.3 | 0.53 | 25.03
DVH090* | 7.5 | 2550 | 85 | 57 | 50 | 105.8 | 1 | 37.72
DVH090* | 7.5 | 2550 | 85 | 61 | 50 | 105.8 | 1 | 37.72
DVH090* | 7.5 | 2550 | 85 | 64 | 50 | 109.2 | 0.91 | 35.33
DVH090* | 7.5 | 2550 | 85 | 67 | 50 | 113.7 | 0.82 | 33.05
DVH090* | 7.5 | 2550 | 85 | 70 | 50 | 120.9 | 0.7 | 30.3
DVH090* | 7.5 | 2550 | 85 | 72 | 50 | 125.2 | 0.62 | 27.77
DVH090* | 7.5 | 2550 | 85 | 75 | 50 | 132.1 | 0.53 | 24.99
DVH090* | 7.5 | 2550 | 85 | 57 | 54 | 105.7 | 1 | 37.68
DVH090* | 7.5 | 2550 | 85 | 61 | 54 | 105.7 | 1 | 37.68
DVH090* | 7.5 | 2550 | 85 | 64 | 54 | 109.1 | 0.91 | 35.29
DVH090* | 7.5 | 2550 | 85 | 67 | 54 | 113.6 | 0.82 | 33.01
DVH090* | 7.5 | 2550 | 85 | 70 | 54 | 120.8 | 0.7 | 30.27
DVH090* | 7.5 | 2550 | 85 | 72 | 54 | 125.1 | 0.62 | 27.74
DVH090* | 7.5 | 2550 | 85 | 75 | 54 | 132 | 0.53 | 24.99
DVH090* | 7.5 | 2550 | 85 | 57 | 58 | 105.3 | 1 | 37.54
DVH090* | 7.5 | 2550 | 85 | 61 | 58 | 105.3 | 1 | 37.54
DVH090* | 7.5 | 2550 | 85 | 64 | 58 | 108.6 | 0.91 | 35.15
DVH090* | 7.5 | 2550 | 85 | 67 | 58 | 113.1 | 0.82 | 32.87
DVH090* | 7.5 | 2550 | 85 | 70 | 58 | 120.3 | 0.7 | 30.12
DVH090* | 7.5 | 2550 | 85 | 72 | 58 | 124.6 | 0.62 | 27.63
DVH090* | 7.5 | 2550 | 85 | 75 | 58 | 131.2 | 0.53 | 24.85
DVH090* | 7.5 | 2550 | 85 | 57 | 62 | 104.1 | 1 | 37.11
DVH090* | 7.5 | 2550 | 85 | 61 | 62 | 104.1 | 1 | 37.11
DVH090* | 7.5 | 2550 | 85 | 64 | 62 | 107 | 0.91 | 34.9
DVH090* | 7.5 | 2550 | 85 | 67 | 62 | 111.5 | 0.82 | 32.62
DVH090* | 7.5 | 2550 | 85 | 70 | 62 | 118.5 | 0.71 | 29.91
DVH090* | 7.5 | 2550 | 85 | 72 | 62 | 122.8 | 0.63 | 27.42
DVH090* | 7.5 | 2550 | 85 | 75 | 62 | 129.4 | 0.53 | 24.53
DVH090* | 7.5 | 2550 | 85 | 57 | 66 | 102.8 | 1 | 36.65
DVH090* | 7.5 | 2550 | 85 | 61 | 66 | 102.8 | 1 | 36.65
DVH090* | 7.5 | 2550 | 85 | 64 | 66 | 105.5 | 0.92 | 34.65
DVH090* | 7.5 | 2550 | 85 | 67 | 66 | 109.8 | 0.83 | 32.41
DVH090* | 7.5 | 2550 | 85 | 70 | 66 | 116.8 | 0.71 | 29.7
DVH090* | 7.5 | 2550 | 85 | 72 | 66 | 121 | 0.63 | 27.24
DVH090* | 7.5 | 2550 | 85 | 75 | 66 | 127.6 | 0.53 | 24.24
DVH090* | 7.5 | 2550 | 85 | 57 | 70 | 101.6 | 1 | 36.22
DVH090* | 7.5 | 2550 | 85 | 61 | 70 | 101.6 | 1 | 36.22
DVH090* | 7.5 | 2550 | 85 | 64 | 70 | 103.9 | 0.93 | 34.4
DVH090* | 7.5 | 2550 | 85 | 67 | 70 | 108.2 | 0.83 | 32.16
DVH090* | 7.5 | 2550 | 85 | 70 | 70 | 115.1 | 0.72 | 29.48
DVH090* | 7.5 | 2550 | 85 | 72 | 70 | 119.2 | 0.64 | 27.02
DVH090* | 7.5 | 2550 | 85 | 75 | 70 | 125.7 | 0.54 | 23.99
DVH090* | 7.5 | 2550 | 85 | 57 | 72 | 100.9 | 1 | 35.97
DVH090* | 7.5 | 2550 | 85 | 61 | 72 | 101 | 1 | 36.01
DVH090* | 7.5 | 2550 | 85 | 64 | 72 | 103.1 | 0.93 | 34.26
DVH090* | 7.5 | 2550 | 85 | 67 | 72 | 107.4 | 0.84 | 32.05
DVH090* | 7.5 | 2550 | 85 | 70 | 72 | 114.2 | 0.72 | 29.38
DVH090* | 7.5 | 2550 | 85 | 72 | 72 | 118.3 | 0.64 | 26.92
DVH090* | 7.5 | 2550 | 85 | 75 | 72 | 124.8 | 0.54 | 23.85
DVH090* | 7.5 | 2550 | 85 | 57 | 75 | 100 | 1 | 35.65
DVH090* | 7.5 | 2550 | 85 | 61 | 75 | 100 | 1 | 35.65
DVH090* | 7.5 | 2550 | 85 | 64 | 75 | 102 | 0.94 | 34.08
DVH090* | 7.5 | 2550 | 85 | 67 | 75 | 106.2 | 0.84 | 31.87
DVH090* | 7.5 | 2550 | 85 | 70 | 75 | 112.9 | 0.73 | 29.2
DVH090* | 7.5 | 2550 | 85 | 72 | 75 | 116.9 | 0.64 | 26.77
DVH090* | 7.5 | 2550 | 85 | 75 | 75 | 123.4 | 0.54 | 23.64
DVH090* | 7.5 | 2550 | 85 | 57 | 79 | 98.8 | 1 | 35.22
DVH090* | 7.5 | 2550 | 85 | 61 | 79 | 98.8 | 1 | 35.22
DVH090* | 7.5 | 2550 | 85 | 64 | 79 | 100.4 | 0.94 | 33.8
DVH090* | 7.5 | 2550 | 85 | 67 | 79 | 104.6 | 0.85 | 31.62
DVH090* | 7.5 | 2550 | 85 | 70 | 79 | 111.2 | 0.73 | 28.98
DVH090* | 7.5 | 2550 | 85 | 72 | 79 | 115.2 | 0.65 | 26.56
DVH090* | 7.5 | 2550 | 85 | 75 | 79 | 121.6 | 0.54 | 23.35
DVH090* | 7.5 | 2550 | 85 | 57 | 83 | 97.5 | 1 | 34.76
DVH090* | 7.5 | 2550 | 85 | 61 | 83 | 97.5 | 1 | 34.76
DVH090* | 7.5 | 2550 | 85 | 64 | 83 | 98.8 | 0.95 | 33.51
DVH090* | 7.5 | 2550 | 85 | 67 | 83 | 102.9 | 0.85 | 31.34
DVH090* | 7.5 | 2550 | 85 | 70 | 83 | 109.4 | 0.74 | 28.73
DVH090* | 7.5 | 2550 | 85 | 72 | 83 | 113.4 | 0.65 | 26.35
DVH090* | 7.5 | 2550 | 85 | 75 | 83 | 119.8 | 0.54 | 23.07
DVH090* | 7.5 | 2550 | 85 | 57 | 87 | 96.3 | 1 | 34.33
DVH090* | 7.5 | 2550 | 85 | 61 | 87 | 96.3 | 1 | 34.33
DVH090* | 7.5 | 2550 | 85 | 64 | 87 | 97.3 | 0.96 | 33.23
DVH090* | 7.5 | 2550 | 85 | 67 | 87 | 101.3 | 0.86 | 31.09
DVH090* | 7.5 | 2550 | 85 | 70 | 87 | 107.7 | 0.74 | 28.52
DVH090* | 7.5 | 2550 | 85 | 72 | 87 | 111.6 | 0.66 | 26.13
DVH090* | 7.5 | 2550 | 85 | 75 | 87 | 117.9 | 0.54 | 22.78
DVH090* | 7.5 | 2550 | 85 | 57 | 91 | 95.1 | 1 | 33.9
DVH090* | 7.5 | 2550 | 85 | 61 | 91 | 95.1 | 1 | 33.9
DVH090* | 7.5 | 2550 | 85 | 64 | 91 | 95.7 | 0.97 | 32.94
DVH090* | 7.5 | 2550 | 85 | 67 | 91 | 99.7 | 0.87 | 30.8
DVH090* | 7.5 | 2550 | 85 | 70 | 91 | 106 | 0.75 | 28.27
DVH090* | 7.5 | 2550 | 85 | 72 | 91 | 109.8 | 0.66 | 25.88
DVH090* | 7.5 | 2550 | 85 | 75 | 91 | 116.1 | 0.54 | 22.5
DVH090* | 7.5 | 2550 | 85 | 57 | 93 | 94.4 | 1 | 33.65
DVH090* | 7.5 | 2550 | 85 | 61 | 93 | 94.4 | 1 | 33.65
DVH090* | 7.5 | 2550 | 85 | 64 | 93 | 94.9 | 0.97 | 32.8
DVH090* | 7.5 | 2550 | 85 | 67 | 93 | 98.9 | 0.87 | 30.66
DVH090* | 7.5 | 2550 | 85 | 70 | 93 | 105.1 | 0.75 | 28.13
DVH090* | 7.5 | 2550 | 85 | 72 | 93 | 108.9 | 0.66 | 25.78
DVH090* | 7.5 | 2550 | 85 | 75 | 93 | 115.2 | 0.54 | 22.35
DVH090* | 7.5 | 2550 | 85 | 57 | 95 | 93.8 | 1 | 33.44
DVH090* | 7.5 | 2550 | 85 | 61 | 95 | 93.8 | 1 | 33.44
DVH090* | 7.5 | 2550 | 85 | 64 | 95 | 94.1 | 0.97 | 32.66
DVH090* | 7.5 | 2550 | 85 | 67 | 95 | 98.1 | 0.87 | 30.55
DVH090* | 7.5 | 2550 | 85 | 70 | 95 | 104.3 | 0.75 | 27.99
DVH090* | 7.5 | 2550 | 85 | 72 | 95 | 108 | 0.67 | 25.67
DVH090* | 7.5 | 2550 | 85 | 75 | 95 | 114.3 | 0.55 | 22.21
DVH090* | 7.5 | 2550 | 85 | 57 | 99 | 92.6 | 1 | 33.01
DVH090* | 7.5 | 2550 | 85 | 61 | 99 | 92.6 | 1 | 33.01
DVH090* | 7.5 | 2550 | 85 | 64 | 99 | 92.6 | 1 | 33.01
DVH090* | 7.5 | 2550 | 85 | 67 | 99 | 96.4 | 0.88 | 30.23
DVH090* | 7.5 | 2550 | 85 | 70 | 99 | 102.5 | 0.76 | 27.74
DVH090* | 7.5 | 2550 | 85 | 72 | 99 | 106.2 | 0.67 | 25.42
DVH090* | 7.5 | 2550 | 85 | 75 | 99 | 112.4 | 0.55 | 21.93
DVH090* | 7.5 | 2550 | 85 | 57 | 103 | 91.3 | 1 | 32.55
DVH090* | 7.5 | 2550 | 85 | 61 | 103 | 91.3 | 1 | 32.55
DVH090* | 7.5 | 2550 | 85 | 64 | 103 | 91 | 1 | 32.44
DVH090* | 7.5 | 2550 | 85 | 67 | 103 | 94.8 | 0.89 | 29.95
DVH090* | 7.5 | 2550 | 85 | 70 | 103 | 100.8 | 0.76 | 27.45
DVH090* | 7.5 | 2550 | 85 | 72 | 103 | 104.4 | 0.68 | 25.17
DVH090* | 7.5 | 2550 | 85 | 75 | 103 | 110.6 | 0.55 | 21.64
DVH090* | 7.5 | 2550 | 85 | 57 | 106 | 90.4 | 1 | 32.23
DVH090* | 7.5 | 2550 | 85 | 61 | 106 | 90.4 | 1 | 32.23
DVH090* | 7.5 | 2550 | 85 | 64 | 106 | 89.9 | 1 | 32.05
DVH090* | 7.5 | 2550 | 85 | 67 | 106 | 93.6 | 0.89 | 29.73
DVH090* | 7.5 | 2550 | 85 | 70 | 106 | 99.5 | 0.77 | 27.27
DVH090* | 7.5 | 2550 | 85 | 72 | 106 | 103.1 | 0.68 | 24.99
DVH090* | 7.5 | 2550 | 85 | 75 | 106 | 109.2 | 0.55 | 21.43
DVH090* | 7.5 | 2550 | 85 | 57 | 110 | 89.2 | 1 | 31.8
DVH090* | 7.5 | 2550 | 85 | 61 | 110 | 89.2 | 1 | 31.8
DVH090* | 7.5 | 2550 | 85 | 64 | 110 | 88.3 | 1 | 31.48
DVH090* | 7.5 | 2550 | 85 | 67 | 110 | 92 | 0.9 | 29.41
DVH090* | 7.5 | 2550 | 85 | 70 | 110 | 97.8 | 0.77 | 26.99
DVH090* | 7.5 | 2550 | 85 | 72 | 110 | 101.3 | 0.69 | 24.74
DVH090* | 7.5 | 2550 | 85 | 75 | 110 | 107.4 | 0.55 | 21.11
DVH090* | 7.5 | 2550 | 85 | 57 | 115 | 87.6 | 1 | 31.23
DVH090* | 7.5 | 2550 | 85 | 61 | 115 | 87.6 | 1 | 31.23
DVH090* | 7.5 | 2550 | 85 | 64 | 115 | 86.3 | 1 | 30.77
DVH090* | 7.5 | 2550 | 85 | 67 | 115 | 89.9 | 0.91 | 29.02
DVH090* | 7.5 | 2550 | 85 | 70 | 115 | 95.6 | 0.78 | 26.63
DVH090* | 7.5 | 2550 | 85 | 72 | 115 | 99 | 0.69 | 24.39
DVH090* | 7.5 | 2550 | 85 | 75 | 115 | 105.1 | 0.55 | 20.75
DVH090* | 7.5 | 2550 | 85 | 57 | 118 | 86.7 | 1 | 30.91
DVH090* | 7.5 | 2550 | 85 | 61 | 118 | 86.7 | 1 | 30.91
DVH090* | 7.5 | 2550 | 85 | 64 | 118 | 85.2 | 1 | 30.37
DVH090* | 7.5 | 2550 | 85 | 67 | 118 | 88.7 | 0.91 | 28.77
DVH090* | 7.5 | 2550 | 85 | 70 | 118 | 94.3 | 0.78 | 26.38
DVH090* | 7.5 | 2550 | 85 | 72 | 118 | 97.7 | 0.69 | 24.21
DVH090* | 7.5 | 2550 | 85 | 75 | 118 | 103.7 | 0.56 | 20.53
DVH090* | 7.5 | 2950 | 70 | 57 | 23 | 95 | 0.89 | 25.92
DVH090* | 7.5 | 2950 | 70 | 61 | 23 | 103.7 | 0.69 | 22.03
DVH090* | 7.5 | 2950 | 70 | 64 | 23 | 111.9 | 0.53 | 18.4
DVH090* | 7.5 | 2950 | 70 | 67 | 23 | 117.9 | 0.42 | 15.38
DVH090* | 7.5 | 2950 | 70 | 57 | 30 | 94.8 | 0.89 | 25.86
DVH090* | 7.5 | 2950 | 70 | 61 | 30 | 103.5 | 0.69 | 21.97
DVH090* | 7.5 | 2950 | 70 | 64 | 30 | 111.7 | 0.53 | 18.37
DVH090* | 7.5 | 2950 | 70 | 67 | 30 | 117.7 | 0.42 | 15.35
DVH090* | 7.5 | 2950 | 70 | 57 | 40 | 94.5 | 0.89 | 25.79
DVH090* | 7.5 | 2950 | 70 | 61 | 40 | 103.2 | 0.69 | 21.91
DVH090* | 7.5 | 2950 | 70 | 64 | 40 | 111.4 | 0.53 | 18.31
DVH090* | 7.5 | 2950 | 70 | 67 | 40 | 117.3 | 0.42 | 15.32
DVH090* | 7.5 | 2950 | 70 | 57 | 50 | 94.2 | 0.89 | 25.7
DVH090* | 7.5 | 2950 | 70 | 61 | 50 | 102.9 | 0.69 | 21.85
DVH090* | 7.5 | 2950 | 70 | 64 | 50 | 111.1 | 0.53 | 18.27
DVH090* | 7.5 | 2950 | 70 | 67 | 50 | 117 | 0.42 | 15.25
DVH090* | 7.5 | 2950 | 70 | 57 | 54 | 94.1 | 0.89 | 25.67
DVH090* | 7.5 | 2950 | 70 | 61 | 54 | 102.7 | 0.69 | 21.82
DVH090* | 7.5 | 2950 | 70 | 64 | 54 | 110.9 | 0.53 | 18.24
DVH090* | 7.5 | 2950 | 70 | 67 | 54 | 116.9 | 0.42 | 15.22
DVH090* | 7.5 | 2950 | 70 | 57 | 58 | 93.8 | 0.88 | 25.58
DVH090* | 7.5 | 2950 | 70 | 61 | 58 | 102.4 | 0.69 | 21.73
DVH090* | 7.5 | 2950 | 70 | 64 | 58 | 110.4 | 0.53 | 18.15
DVH090* | 7.5 | 2950 | 70 | 67 | 58 | 116.3 | 0.42 | 15.16
DVH090* | 7.5 | 2950 | 70 | 57 | 62 | 92.7 | 0.89 | 25.3
DVH090* | 7.5 | 2950 | 70 | 61 | 62 | 101.1 | 0.69 | 21.51
DVH090* | 7.5 | 2950 | 70 | 64 | 62 | 108.9 | 0.54 | 18.03
DVH090* | 7.5 | 2950 | 70 | 67 | 62 | 114.7 | 0.43 | 15.07
DVH090* | 7.5 | 2950 | 70 | 57 | 66 | 91.5 | 0.89 | 25.08
DVH090* | 7.5 | 2950 | 70 | 61 | 66 | 99.9 | 0.69 | 21.33
DVH090* | 7.5 | 2950 | 70 | 64 | 66 | 107.3 | 0.54 | 17.9
DVH090* | 7.5 | 2950 | 70 | 67 | 66 | 113 | 0.43 | 14.95
DVH090* | 7.5 | 2950 | 70 | 57 | 70 | 90.4 | 0.89 | 24.87
DVH090* | 7.5 | 2950 | 70 | 61 | 70 | 98.7 | 0.7 | 21.14
DVH090* | 7.5 | 2950 | 70 | 64 | 70 | 105.7 | 0.55 | 17.78
DVH090* | 7.5 | 2950 | 70 | 67 | 70 | 111.3 | 0.43 | 14.85
DVH090* | 7.5 | 2950 | 70 | 57 | 72 | 89.9 | 0.89 | 24.75
DVH090* | 7.5 | 2950 | 70 | 61 | 72 | 98.1 | 0.7 | 21.05
DVH090* | 7.5 | 2950 | 70 | 64 | 72 | 104.9 | 0.55 | 17.72
DVH090* | 7.5 | 2950 | 70 | 67 | 72 | 110.5 | 0.43 | 14.79
DVH090* | 7.5 | 2950 | 70 | 57 | 75 | 89.1 | 0.9 | 24.59
DVH090* | 7.5 | 2950 | 70 | 61 | 75 | 97.2 | 0.7 | 20.89
DVH090* | 7.5 | 2950 | 70 | 64 | 75 | 103.7 | 0.55 | 17.6
DVH090* | 7.5 | 2950 | 70 | 67 | 75 | 109.2 | 0.44 | 14.7
DVH090* | 7.5 | 2950 | 70 | 57 | 79 | 88 | 0.9 | 24.35
DVH090* | 7.5 | 2950 | 70 | 61 | 79 | 96 | 0.7 | 20.68
DVH090* | 7.5 | 2950 | 70 | 64 | 79 | 102.1 | 0.56 | 17.47
DVH090* | 7.5 | 2950 | 70 | 67 | 79 | 107.6 | 0.44 | 14.61
DVH090* | 7.5 | 2950 | 70 | 57 | 83 | 86.8 | 0.9 | 24.13
DVH090* | 7.5 | 2950 | 70 | 61 | 83 | 94.8 | 0.7 | 20.49
DVH090* | 7.5 | 2950 | 70 | 64 | 83 | 100.5 | 0.56 | 17.32
DVH090* | 7.5 | 2950 | 70 | 67 | 83 | 105.9 | 0.44 | 14.48
DVH090* | 7.5 | 2950 | 70 | 57 | 87 | 85.7 | 0.9 | 23.88
DVH090* | 7.5 | 2950 | 70 | 61 | 87 | 93.6 | 0.7 | 20.31
DVH090* | 7.5 | 2950 | 70 | 64 | 87 | 98.9 | 0.56 | 17.2
DVH090* | 7.5 | 2950 | 70 | 67 | 87 | 104.2 | 0.45 | 14.36
DVH090* | 7.5 | 2950 | 70 | 57 | 91 | 84.6 | 0.91 | 23.64
DVH090* | 7.5 | 2950 | 70 | 61 | 91 | 92.4 | 0.71 | 20.09
DVH090* | 7.5 | 2950 | 70 | 64 | 91 | 97.3 | 0.57 | 17.04
DVH090* | 7.5 | 2950 | 70 | 67 | 91 | 102.5 | 0.45 | 14.24
DVH090* | 7.5 | 2950 | 70 | 57 | 93 | 84.1 | 0.91 | 23.54
DVH090* | 7.5 | 2950 | 70 | 61 | 93 | 91.8 | 0.71 | 20
DVH090* | 7.5 | 2950 | 70 | 64 | 93 | 96.5 | 0.57 | 16.95
DVH090* | 7.5 | 2950 | 70 | 67 | 93 | 101.7 | 0.45 | 14.18
DVH090* | 7.5 | 2950 | 70 | 57 | 95 | 83.5 | 0.91 | 23.42
DVH090* | 7.5 | 2950 | 70 | 61 | 95 | 91.2 | 0.71 | 19.91
DVH090* | 7.5 | 2950 | 70 | 64 | 95 | 95.8 | 0.57 | 16.89
DVH090* | 7.5 | 2950 | 70 | 67 | 95 | 100.9 | 0.45 | 14.11
DVH090* | 7.5 | 2950 | 70 | 57 | 99 | 82.4 | 0.91 | 23.17
DVH090* | 7.5 | 2950 | 70 | 61 | 99 | 90 | 0.71 | 19.69
DVH090* | 7.5 | 2950 | 70 | 64 | 99 | 94.2 | 0.58 | 16.73
DVH090* | 7.5 | 2950 | 70 | 67 | 99 | 99.2 | 0.46 | 13.96
DVH090* | 7.5 | 2950 | 70 | 57 | 103 | 81.3 | 0.92 | 22.93
DVH090* | 7.5 | 2950 | 70 | 61 | 103 | 88.8 | 0.71 | 19.48
DVH090* | 7.5 | 2950 | 70 | 64 | 103 | 92.6 | 0.58 | 16.55
DVH090* | 7.5 | 2950 | 70 | 67 | 103 | 97.5 | 0.46 | 13.84
DVH090* | 7.5 | 2950 | 70 | 57 | 106 | 80.5 | 0.92 | 22.74
DVH090* | 7.5 | 2950 | 70 | 61 | 106 | 87.9 | 0.71 | 19.32
DVH090* | 7.5 | 2950 | 70 | 64 | 106 | 91.4 | 0.58 | 16.43
DVH090* | 7.5 | 2950 | 70 | 67 | 106 | 96.3 | 0.46 | 13.71
DVH090* | 7.5 | 2950 | 70 | 57 | 110 | 79.4 | 0.92 | 22.5
DVH090* | 7.5 | 2950 | 70 | 61 | 110 | 86.7 | 0.72 | 19.14
DVH090* | 7.5 | 2950 | 70 | 64 | 110 | 89.8 | 0.59 | 16.27
DVH090* | 7.5 | 2950 | 70 | 67 | 110 | 94.6 | 0.47 | 13.59
DVH090* | 7.5 | 2950 | 70 | 57 | 115 | 78 | 0.92 | 22.19
DVH090* | 7.5 | 2950 | 70 | 61 | 115 | 85.2 | 0.72 | 18.86
DVH090* | 7.5 | 2950 | 70 | 64 | 115 | 87.8 | 0.59 | 16.06
DVH090* | 7.5 | 2950 | 70 | 67 | 115 | 92.5 | 0.47 | 13.41
DVH090* | 7.5 | 2950 | 70 | 57 | 118 | 77.2 | 0.92 | 22
DVH090* | 7.5 | 2950 | 70 | 61 | 118 | 84.3 | 0.72 | 18.71
DVH090* | 7.5 | 2950 | 70 | 64 | 118 | 86.6 | 0.6 | 15.9
DVH090* | 7.5 | 2950 | 70 | 67 | 118 | 91.3 | 0.47 | 13.28
DVH090* | 7.5 | 2950 | 75 | 57 | 23 | 97.8 | 1 | 30.14
DVH090* | 7.5 | 2950 | 75 | 61 | 23 | 102.6 | 0.85 | 26.87
DVH090* | 7.5 | 2950 | 75 | 64 | 23 | 111.9 | 0.68 | 23.45
DVH090* | 7.5 | 2950 | 75 | 67 | 23 | 117.9 | 0.56 | 20.46
DVH090* | 7.5 | 2950 | 75 | 70 | 23 | 125.4 | 0.46 | 17.69
DVH090* | 7.5 | 2950 | 75 | 72 | 23 | 129.9 | 0.38 | 15.41
DVH090* | 7.5 | 2950 | 75 | 57 | 30 | 97.6 | 1 | 30.08
DVH090* | 7.5 | 2950 | 75 | 61 | 30 | 102.4 | 0.85 | 26.81
DVH090* | 7.5 | 2950 | 75 | 64 | 30 | 111.7 | 0.68 | 23.42
DVH090* | 7.5 | 2950 | 75 | 67 | 30 | 117.7 | 0.56 | 20.43
DVH090* | 7.5 | 2950 | 75 | 70 | 30 | 125.1 | 0.46 | 17.66
DVH090* | 7.5 | 2950 | 75 | 72 | 30 | 129.6 | 0.39 | 15.38
DVH090* | 7.5 | 2950 | 75 | 57 | 40 | 97.3 | 1 | 29.98
DVH090* | 7.5 | 2950 | 75 | 61 | 40 | 102 | 0.85 | 26.72
DVH090* | 7.5 | 2950 | 75 | 64 | 40 | 111.4 | 0.68 | 23.33
DVH090* | 7.5 | 2950 | 75 | 67 | 40 | 117.3 | 0.56 | 20.37
DVH090* | 7.5 | 2950 | 75 | 70 | 40 | 124.8 | 0.46 | 17.6
DVH090* | 7.5 | 2950 | 75 | 72 | 40 | 129.2 | 0.39 | 15.35
DVH090* | 7.5 | 2950 | 75 | 57 | 50 | 97 | 1 | 29.89
DVH090* | 7.5 | 2950 | 75 | 61 | 50 | 101.7 | 0.85 | 26.66
DVH090* | 7.5 | 2950 | 75 | 64 | 50 | 111.1 | 0.68 | 23.27
DVH090* | 7.5 | 2950 | 75 | 67 | 50 | 117 | 0.56 | 20.31
DVH090* | 7.5 | 2950 | 75 | 70 | 50 | 124.4 | 0.46 | 17.53
DVH090* | 7.5 | 2950 | 75 | 72 | 50 | 128.9 | 0.38 | 15.29
DVH090* | 7.5 | 2950 | 75 | 57 | 54 | 96.9 | 1 | 29.86
DVH090* | 7.5 | 2950 | 75 | 61 | 54 | 101.6 | 0.85 | 26.63
DVH090* | 7.5 | 2950 | 75 | 64 | 54 | 110.9 | 0.68 | 23.24
DVH090* | 7.5 | 2950 | 75 | 67 | 54 | 116.9 | 0.56 | 20.28
DVH090* | 7.5 | 2950 | 75 | 70 | 54 | 124.3 | 0.46 | 17.53
DVH090* | 7.5 | 2950 | 75 | 72 | 54 | 128.7 | 0.39 | 15.29
DVH090* | 7.5 | 2950 | 75 | 57 | 58 | 96.5 | 1 | 29.74
DVH090* | 7.5 | 2950 | 75 | 61 | 58 | 101.2 | 0.85 | 26.5
DVH090* | 7.5 | 2950 | 75 | 64 | 58 | 110.4 | 0.68 | 23.14
DVH090* | 7.5 | 2950 | 75 | 67 | 58 | 116.3 | 0.56 | 20.18
DVH090* | 7.5 | 2950 | 75 | 70 | 58 | 123.7 | 0.46 | 17.44
DVH090* | 7.5 | 2950 | 75 | 72 | 58 | 128.1 | 0.39 | 15.22
DVH090* | 7.5 | 2950 | 75 | 57 | 62 | 95.4 | 1 | 29.4
DVH090* | 7.5 | 2950 | 75 | 61 | 62 | 100 | 0.85 | 26.22
DVH090* | 7.5 | 2950 | 75 | 64 | 62 | 108.9 | 0.68 | 22.96
DVH090* | 7.5 | 2950 | 75 | 67 | 62 | 114.7 | 0.57 | 20.03
DVH090* | 7.5 | 2950 | 75 | 70 | 62 | 121.9 | 0.46 | 17.32
DVH090* | 7.5 | 2950 | 75 | 72 | 62 | 126.3 | 0.39 | 15.1
DVH090* | 7.5 | 2950 | 75 | 57 | 66 | 94.2 | 1 | 29.03
DVH090* | 7.5 | 2950 | 75 | 61 | 66 | 98.8 | 0.85 | 26.01
DVH090* | 7.5 | 2950 | 75 | 64 | 66 | 107.3 | 0.69 | 22.8
DVH090* | 7.5 | 2950 | 75 | 67 | 66 | 113 | 0.57 | 19.91
DVH090* | 7.5 | 2950 | 75 | 70 | 66 | 120.2 | 0.46 | 17.2
DVH090* | 7.5 | 2950 | 75 | 72 | 66 | 124.5 | 0.39 | 15.01
DVH090* | 7.5 | 2950 | 75 | 57 | 70 | 93.1 | 1 | 28.69
DVH090* | 7.5 | 2950 | 75 | 61 | 70 | 97.6 | 0.86 | 25.76
DVH090* | 7.5 | 2950 | 75 | 64 | 70 | 105.7 | 0.7 | 22.65
DVH090* | 7.5 | 2950 | 75 | 67 | 70 | 111.3 | 0.58 | 19.75
DVH090* | 7.5 | 2950 | 75 | 70 | 70 | 118.4 | 0.47 | 17.07
DVH090* | 7.5 | 2950 | 75 | 72 | 70 | 122.6 | 0.39 | 14.88
DVH090* | 7.5 | 2950 | 75 | 57 | 72 | 92.5 | 1 | 28.51
DVH090* | 7.5 | 2950 | 75 | 61 | 72 | 97.1 | 0.86 | 25.67
DVH090* | 7.5 | 2950 | 75 | 64 | 72 | 104.9 | 0.7 | 22.56
DVH090* | 7.5 | 2950 | 75 | 67 | 72 | 110.5 | 0.58 | 19.69
DVH090* | 7.5 | 2950 | 75 | 70 | 72 | 117.5 | 0.47 | 17.01
DVH090* | 7.5 | 2950 | 75 | 72 | 72 | 121.7 | 0.4 | 14.82
DVH090* | 7.5 | 2950 | 75 | 57 | 75 | 91.7 | 1 | 28.26
DVH090* | 7.5 | 2950 | 75 | 61 | 75 | 96.2 | 0.86 | 25.49
DVH090* | 7.5 | 2950 | 75 | 64 | 75 | 103.7 | 0.7 | 22.43
DVH090* | 7.5 | 2950 | 75 | 67 | 75 | 109.2 | 0.58 | 19.57
DVH090* | 7.5 | 2950 | 75 | 70 | 75 | 116.2 | 0.47 | 16.92
DVH090* | 7.5 | 2950 | 75 | 72 | 75 | 120.3 | 0.4 | 14.76
DVH090* | 7.5 | 2950 | 75 | 57 | 79 | 90.5 | 1 | 27.89
DVH090* | 7.5 | 2950 | 75 | 61 | 79 | 95 | 0.86 | 25.24
DVH090* | 7.5 | 2950 | 75 | 64 | 79 | 102.1 | 0.71 | 22.25
DVH090* | 7.5 | 2950 | 75 | 67 | 79 | 107.6 | 0.59 | 19.41
DVH090* | 7.5 | 2950 | 75 | 70 | 79 | 114.4 | 0.48 | 16.8
DVH090* | 7.5 | 2950 | 75 | 72 | 79 | 118.5 | 0.4 | 14.64
DVH090* | 7.5 | 2950 | 75 | 57 | 83 | 89.4 | 1 | 27.55
DVH090* | 7.5 | 2950 | 75 | 61 | 83 | 93.8 | 0.86 | 24.99
DVH090* | 7.5 | 2950 | 75 | 64 | 83 | 100.5 | 0.71 | 22.06
DVH090* | 7.5 | 2950 | 75 | 67 | 83 | 105.9 | 0.59 | 19.26
DVH090* | 7.5 | 2950 | 75 | 70 | 83 | 112.6 | 0.48 | 16.64
DVH090* | 7.5 | 2950 | 75 | 72 | 83 | 116.6 | 0.4 | 14.51
DVH090* | 7.5 | 2950 | 75 | 57 | 87 | 88.2 | 1 | 27.18
DVH090* | 7.5 | 2950 | 75 | 61 | 87 | 92.6 | 0.87 | 24.75
DVH090* | 7.5 | 2950 | 75 | 64 | 87 | 98.9 | 0.72 | 21.88
DVH090* | 7.5 | 2950 | 75 | 67 | 87 | 104.2 | 0.6 | 19.11
DVH090* | 7.5 | 2950 | 75 | 70 | 87 | 110.8 | 0.48 | 16.52
DVH090* | 7.5 | 2950 | 75 | 72 | 87 | 114.8 | 0.41 | 14.39
DVH090* | 7.5 | 2950 | 75 | 57 | 91 | 87.1 | 1 | 26.84
DVH090* | 7.5 | 2950 | 75 | 61 | 91 | 91.4 | 0.87 | 24.5
DVH090* | 7.5 | 2950 | 75 | 64 | 91 | 97.3 | 0.72 | 21.69
DVH090* | 7.5 | 2950 | 75 | 67 | 91 | 102.5 | 0.6 | 18.92
DVH090* | 7.5 | 2950 | 75 | 70 | 91 | 109 | 0.49 | 16.36
DVH090* | 7.5 | 2950 | 75 | 72 | 91 | 112.9 | 0.41 | 14.27
DVH090* | 7.5 | 2950 | 75 | 57 | 93 | 86.5 | 1 | 26.66
DVH090* | 7.5 | 2950 | 75 | 61 | 93 | 90.8 | 0.87 | 24.38
DVH090* | 7.5 | 2950 | 75 | 64 | 93 | 96.5 | 0.73 | 21.6
DVH090* | 7.5 | 2950 | 75 | 67 | 93 | 101.7 | 0.6 | 18.86
DVH090* | 7.5 | 2950 | 75 | 70 | 93 | 108.2 | 0.49 | 16.3
DVH090* | 7.5 | 2950 | 75 | 72 | 93 | 112 | 0.41 | 14.21
DVH090* | 7.5 | 2950 | 75 | 57 | 95 | 86 | 1 | 26.5
DVH090* | 7.5 | 2950 | 75 | 61 | 95 | 90.2 | 0.87 | 24.25
DVH090* | 7.5 | 2950 | 75 | 64 | 95 | 95.8 | 0.73 | 21.51
DVH090* | 7.5 | 2950 | 75 | 67 | 95 | 100.9 | 0.6 | 18.77
DVH090* | 7.5 | 2950 | 75 | 70 | 95 | 107.3 | 0.49 | 16.21
DVH090* | 7.5 | 2950 | 75 | 72 | 95 | 111.1 | 0.41 | 14.14
DVH090* | 7.5 | 2950 | 75 | 57 | 99 | 84.8 | 1 | 26.13
DVH090* | 7.5 | 2950 | 75 | 61 | 99 | 89 | 0.88 | 24.01
DVH090* | 7.5 | 2950 | 75 | 64 | 99 | 94.2 | 0.73 | 21.29
DVH090* | 7.5 | 2950 | 75 | 67 | 99 | 99.2 | 0.61 | 18.58
DVH090* | 7.5 | 2950 | 75 | 70 | 99 | 105.5 | 0.49 | 16.06
DVH090* | 7.5 | 2950 | 75 | 72 | 99 | 109.3 | 0.42 | 13.99
DVH090* | 7.5 | 2950 | 75 | 57 | 103 | 83.7 | 1 | 25.79
DVH090* | 7.5 | 2950 | 75 | 61 | 103 | 87.8 | 0.88 | 23.76
DVH090* | 7.5 | 2950 | 75 | 64 | 103 | 92.6 | 0.74 | 21.11
DVH090* | 7.5 | 2950 | 75 | 67 | 103 | 97.5 | 0.61 | 18.4
DVH090* | 7.5 | 2950 | 75 | 70 | 103 | 103.7 | 0.5 | 15.9
DVH090* | 7.5 | 2950 | 75 | 72 | 103 | 107.4 | 0.42 | 13.87
DVH090* | 7.5 | 2950 | 75 | 57 | 106 | 82.8 | 1 | 25.52
DVH090* | 7.5 | 2950 | 75 | 61 | 106 | 86.9 | 0.88 | 23.57
DVH090* | 7.5 | 2950 | 75 | 64 | 106 | 91.4 | 0.74 | 20.92
DVH090* | 7.5 | 2950 | 75 | 67 | 106 | 96.3 | 0.62 | 18.27
DVH090* | 7.5 | 2950 | 75 | 70 | 106 | 102.4 | 0.5 | 15.78
DVH090* | 7.5 | 2950 | 75 | 72 | 106 | 106 | 0.42 | 13.78
DVH090* | 7.5 | 2950 | 75 | 57 | 110 | 81.7 | 1 | 25.18
DVH090* | 7.5 | 2950 | 75 | 61 | 110 | 85.7 | 0.88 | 23.33
DVH090* | 7.5 | 2950 | 75 | 64 | 110 | 89.8 | 0.75 | 20.71
DVH090* | 7.5 | 2950 | 75 | 67 | 110 | 94.6 | 0.62 | 18.09
DVH090* | 7.5 | 2950 | 75 | 70 | 110 | 100.6 | 0.5 | 15.62
DVH090* | 7.5 | 2950 | 75 | 72 | 110 | 104.2 | 0.42 | 13.62
DVH090* | 7.5 | 2950 | 75 | 57 | 115 | 80.3 | 1 | 24.75
DVH090* | 7.5 | 2950 | 75 | 61 | 115 | 84.2 | 0.89 | 23.02
DVH090* | 7.5 | 2950 | 75 | 64 | 115 | 87.8 | 0.76 | 20.43
DVH090* | 7.5 | 2950 | 75 | 67 | 115 | 92.5 | 0.63 | 17.84
DVH090* | 7.5 | 2950 | 75 | 70 | 115 | 98.4 | 0.51 | 15.41
DVH090* | 7.5 | 2950 | 75 | 72 | 115 | 101.9 | 0.43 | 13.44
DVH090* | 7.5 | 2950 | 75 | 57 | 118 | 79.4 | 1 | 24.47
DVH090* | 7.5 | 2950 | 75 | 61 | 118 | 83.3 | 0.89 | 22.8
DVH090* | 7.5 | 2950 | 75 | 64 | 118 | 86.6 | 0.76 | 20.28
DVH090* | 7.5 | 2950 | 75 | 67 | 118 | 91.3 | 0.63 | 17.69
DVH090* | 7.5 | 2950 | 75 | 70 | 118 | 97 | 0.51 | 15.29
DVH090* | 7.5 | 2950 | 75 | 72 | 118 | 100.5 | 0.43 | 13.31
DVH090* | 7.5 | 2950 | 80 | 57 | 23 | 103.7 | 1 | 31.96
DVH090* | 7.5 | 2950 | 80 | 61 | 23 | 103.7 | 1 | 31.96
DVH090* | 7.5 | 2950 | 80 | 64 | 23 | 111.9 | 0.82 | 28.41
DVH090* | 7.5 | 2950 | 80 | 67 | 23 | 117.9 | 0.7 | 25.49
DVH090* | 7.5 | 2950 | 80 | 70 | 23 | 125.4 | 0.59 | 22.84
DVH090* | 7.5 | 2950 | 80 | 72 | 23 | 129.9 | 0.51 | 20.52
DVH090* | 7.5 | 2950 | 80 | 75 | 23 | 136.5 | 0.42 | 17.75
DVH090* | 7.5 | 2950 | 80 | 57 | 30 | 103.5 | 1 | 31.9
DVH090* | 7.5 | 2950 | 80 | 61 | 30 | 103.5 | 1 | 31.9
DVH090* | 7.5 | 2950 | 80 | 64 | 30 | 111.7 | 0.82 | 28.35
DVH090* | 7.5 | 2950 | 80 | 67 | 30 | 117.7 | 0.7 | 25.42
DVH090* | 7.5 | 2950 | 80 | 70 | 30 | 125.1 | 0.59 | 22.77
DVH090* | 7.5 | 2950 | 80 | 72 | 30 | 129.6 | 0.51 | 20.49
DVH090* | 7.5 | 2950 | 80 | 75 | 30 | 136.3 | 0.42 | 17.72
DVH090* | 7.5 | 2950 | 80 | 57 | 40 | 103.2 | 1 | 31.8
DVH090* | 7.5 | 2950 | 80 | 61 | 40 | 103.2 | 1 | 31.8
DVH090* | 7.5 | 2950 | 80 | 64 | 40 | 111.4 | 0.82 | 28.29
DVH090* | 7.5 | 2950 | 80 | 67 | 40 | 117.3 | 0.7 | 25.36
DVH090* | 7.5 | 2950 | 80 | 70 | 40 | 124.8 | 0.59 | 22.71
DVH090* | 7.5 | 2950 | 80 | 72 | 40 | 129.2 | 0.51 | 20.43
DVH090* | 7.5 | 2950 | 80 | 75 | 40 | 136.1 | 0.42 | 17.72
DVH090* | 7.5 | 2950 | 80 | 57 | 50 | 102.9 | 1 | 31.71
DVH090* | 7.5 | 2950 | 80 | 61 | 50 | 102.9 | 1 | 31.71
DVH090* | 7.5 | 2950 | 80 | 64 | 50 | 111.1 | 0.82 | 28.2
DVH090* | 7.5 | 2950 | 80 | 67 | 50 | 117 | 0.7 | 25.3
DVH090* | 7.5 | 2950 | 80 | 70 | 50 | 124.4 | 0.59 | 22.65
DVH090* | 7.5 | 2950 | 80 | 72 | 50 | 128.9 | 0.51 | 20.37
DVH090* | 7.5 | 2950 | 80 | 75 | 50 | 135.9 | 0.42 | 17.69
DVH090* | 7.5 | 2950 | 80 | 57 | 54 | 102.7 | 1 | 31.65
DVH090* | 7.5 | 2950 | 80 | 61 | 54 | 102.7 | 1 | 31.65
DVH090* | 7.5 | 2950 | 80 | 64 | 54 | 110.9 | 0.82 | 28.17
DVH090* | 7.5 | 2950 | 80 | 67 | 54 | 116.9 | 0.7 | 25.27
DVH090* | 7.5 | 2950 | 80 | 70 | 54 | 124.3 | 0.59 | 22.62
DVH090* | 7.5 | 2950 | 80 | 72 | 54 | 128.7 | 0.51 | 20.34
DVH090* | 7.5 | 2950 | 80 | 75 | 54 | 135.8 | 0.42 | 17.66
DVH090* | 7.5 | 2950 | 80 | 57 | 58 | 102.4 | 1 | 31.56
DVH090* | 7.5 | 2950 | 80 | 61 | 58 | 102.4 | 1 | 31.56
DVH090* | 7.5 | 2950 | 80 | 64 | 58 | 110.4 | 0.82 | 28.04
DVH090* | 7.5 | 2950 | 80 | 67 | 58 | 116.3 | 0.7 | 25.15
DVH090* | 7.5 | 2950 | 80 | 70 | 58 | 123.7 | 0.59 | 22.53
DVH090* | 7.5 | 2950 | 80 | 72 | 58 | 128.1 | 0.51 | 20.25
DVH090* | 7.5 | 2950 | 80 | 75 | 58 | 135 | 0.42 | 17.57
DVH090* | 7.5 | 2950 | 80 | 57 | 62 | 101.1 | 1 | 31.16
DVH090* | 7.5 | 2950 | 80 | 61 | 62 | 101.1 | 1 | 31.16
DVH090* | 7.5 | 2950 | 80 | 64 | 62 | 108.9 | 0.83 | 27.83
DVH090* | 7.5 | 2950 | 80 | 67 | 62 | 114.7 | 0.71 | 24.96
DVH090* | 7.5 | 2950 | 80 | 70 | 62 | 121.9 | 0.59 | 22.34
DVH090* | 7.5 | 2950 | 80 | 72 | 62 | 126.3 | 0.52 | 20.09
DVH090* | 7.5 | 2950 | 80 | 75 | 62 | 133.1 | 0.42 | 17.35
DVH090* | 7.5 | 2950 | 80 | 57 | 66 | 99.9 | 1 | 30.79
DVH090* | 7.5 | 2950 | 80 | 61 | 66 | 99.9 | 1 | 30.79
DVH090* | 7.5 | 2950 | 80 | 64 | 66 | 107.3 | 0.84 | 27.64
DVH090* | 7.5 | 2950 | 80 | 67 | 66 | 113 | 0.71 | 24.78
DVH090* | 7.5 | 2950 | 80 | 70 | 66 | 120.2 | 0.6 | 22.19
DVH090* | 7.5 | 2950 | 80 | 72 | 66 | 124.5 | 0.52 | 19.97
DVH090* | 7.5 | 2950 | 80 | 75 | 66 | 131.2 | 0.42 | 17.16
DVH090* | 7.5 | 2950 | 80 | 57 | 70 | 98.7 | 1 | 30.42
DVH090* | 7.5 | 2950 | 80 | 61 | 70 | 98.7 | 1 | 30.42
DVH090* | 7.5 | 2950 | 80 | 64 | 70 | 105.7 | 0.84 | 27.46
DVH090* | 7.5 | 2950 | 80 | 67 | 70 | 111.3 | 0.72 | 24.62
DVH090* | 7.5 | 2950 | 80 | 70 | 70 | 118.4 | 0.6 | 22.03
DVH090* | 7.5 | 2950 | 80 | 72 | 70 | 122.6 | 0.52 | 19.82
DVH090* | 7.5 | 2950 | 80 | 75 | 70 | 129.4 | 0.43 | 16.95
DVH090* | 7.5 | 2950 | 80 | 57 | 72 | 98.1 | 1 | 30.23
DVH090* | 7.5 | 2950 | 80 | 61 | 72 | 98.1 | 1 | 30.23
DVH090* | 7.5 | 2950 | 80 | 64 | 72 | 104.9 | 0.85 | 27.33
DVH090* | 7.5 | 2950 | 80 | 67 | 72 | 110.5 | 0.72 | 24.53
DVH090* | 7.5 | 2950 | 80 | 70 | 72 | 117.5 | 0.61 | 21.97
DVH090* | 7.5 | 2950 | 80 | 72 | 72 | 121.7 | 0.53 | 19.75
DVH090* | 7.5 | 2950 | 80 | 75 | 72 | 128.4 | 0.43 | 16.86
DVH090* | 7.5 | 2950 | 80 | 57 | 75 | 97.2 | 1 | 29.95
DVH090* | 7.5 | 2950 | 80 | 61 | 75 | 97.2 | 1 | 29.95
DVH090* | 7.5 | 2950 | 80 | 64 | 75 | 103.7 | 0.85 | 27.18
DVH090* | 7.5 | 2950 | 80 | 67 | 75 | 109.2 | 0.72 | 24.38
DVH090* | 7.5 | 2950 | 80 | 70 | 75 | 116.2 | 0.61 | 21.82
DVH090* | 7.5 | 2950 | 80 | 72 | 75 | 120.3 | 0.53 | 19.63
DVH090* | 7.5 | 2950 | 80 | 75 | 75 | 127 | 0.43 | 16.7
DVH090* | 7.5 | 2950 | 80 | 57 | 79 | 96 | 1 | 29.58
DVH090* | 7.5 | 2950 | 80 | 61 | 79 | 96 | 1 | 29.58
DVH090* | 7.5 | 2950 | 80 | 64 | 79 | 102.1 | 0.86 | 26.96
DVH090* | 7.5 | 2950 | 80 | 67 | 79 | 107.6 | 0.73 | 24.19
DVH090* | 7.5 | 2950 | 80 | 70 | 79 | 114.4 | 0.61 | 21.66
DVH090* | 7.5 | 2950 | 80 | 72 | 79 | 118.5 | 0.53 | 19.48
DVH090* | 7.5 | 2950 | 80 | 75 | 79 | 125.1 | 0.43 | 16.52
DVH090* | 7.5 | 2950 | 80 | 57 | 83 | 94.8 | 1 | 29.21
DVH090* | 7.5 | 2950 | 80 | 61 | 83 | 94.8 | 1 | 29.21
DVH090* | 7.5 | 2950 | 80 | 64 | 83 | 100.5 | 0.86 | 26.75
DVH090* | 7.5 | 2950 | 80 | 67 | 83 | 105.9 | 0.74 | 24.01
DVH090* | 7.5 | 2950 | 80 | 70 | 83 | 112.6 | 0.62 | 21.48
DVH090* | 7.5 | 2950 | 80 | 72 | 83 | 116.6 | 0.54 | 19.32
DVH090* | 7.5 | 2950 | 80 | 75 | 83 | 123.2 | 0.43 | 16.33
DVH090* | 7.5 | 2950 | 80 | 57 | 87 | 93.6 | 1 | 28.84
DVH090* | 7.5 | 2950 | 80 | 61 | 87 | 93.6 | 1 | 28.84
DVH090* | 7.5 | 2950 | 80 | 64 | 87 | 98.9 | 0.87 | 26.53
DVH090* | 7.5 | 2950 | 80 | 67 | 87 | 104.2 | 0.74 | 23.79
DVH090* | 7.5 | 2950 | 80 | 70 | 87 | 110.8 | 0.62 | 21.29
DVH090* | 7.5 | 2950 | 80 | 72 | 87 | 114.8 | 0.54 | 19.17
DVH090* | 7.5 | 2950 | 80 | 75 | 87 | 121.3 | 0.43 | 16.12
DVH090* | 7.5 | 2950 | 80 | 57 | 91 | 92.4 | 1 | 28.47
DVH090* | 7.5 | 2950 | 80 | 61 | 91 | 92.4 | 1 | 28.47
DVH090* | 7.5 | 2950 | 80 | 64 | 91 | 97.3 | 0.88 | 26.29
DVH090* | 7.5 | 2950 | 80 | 67 | 91 | 102.5 | 0.75 | 23.57
DVH090* | 7.5 | 2950 | 80 | 70 | 91 | 109 | 0.63 | 21.11
DVH090* | 7.5 | 2950 | 80 | 72 | 91 | 112.9 | 0.55 | 18.98
DVH090* | 7.5 | 2950 | 80 | 75 | 91 | 119.4 | 0.43 | 15.93
DVH090* | 7.5 | 2950 | 80 | 57 | 93 | 91.8 | 1 | 28.29
DVH090* | 7.5 | 2950 | 80 | 61 | 93 | 91.8 | 1 | 28.29
DVH090* | 7.5 | 2950 | 80 | 64 | 93 | 96.5 | 0.88 | 26.16
DVH090* | 7.5 | 2950 | 80 | 67 | 93 | 101.7 | 0.75 | 23.48
DVH090* | 7.5 | 2950 | 80 | 70 | 93 | 108.2 | 0.63 | 21.02
DVH090* | 7.5 | 2950 | 80 | 72 | 93 | 112 | 0.55 | 18.92
DVH090* | 7.5 | 2950 | 80 | 75 | 93 | 118.5 | 0.43 | 15.81
DVH090* | 7.5 | 2950 | 80 | 57 | 95 | 91.2 | 1 | 28.1
DVH090* | 7.5 | 2950 | 80 | 61 | 95 | 91.2 | 1 | 28.1
DVH090* | 7.5 | 2950 | 80 | 64 | 95 | 95.8 | 0.88 | 26.07
DVH090* | 7.5 | 2950 | 80 | 67 | 95 | 100.9 | 0.75 | 23.36
DVH090* | 7.5 | 2950 | 80 | 70 | 95 | 107.3 | 0.63 | 20.92
DVH090* | 7.5 | 2950 | 80 | 72 | 95 | 111.1 | 0.55 | 18.83
DVH090* | 7.5 | 2950 | 80 | 75 | 95 | 117.6 | 0.43 | 15.72
DVH090* | 7.5 | 2950 | 80 | 57 | 99 | 90 | 1 | 27.73
DVH090* | 7.5 | 2950 | 80 | 61 | 99 | 90 | 1 | 27.73
DVH090* | 7.5 | 2950 | 80 | 64 | 99 | 94.2 | 0.89 | 25.82
DVH090* | 7.5 | 2950 | 80 | 67 | 99 | 99.2 | 0.76 | 23.14
DVH090* | 7.5 | 2950 | 80 | 70 | 99 | 105.5 | 0.64 | 20.74
DVH090* | 7.5 | 2950 | 80 | 72 | 99 | 109.3 | 0.55 | 18.64
DVH090* | 7.5 | 2950 | 80 | 75 | 99 | 115.7 | 0.43 | 15.5
DVH090* | 7.5 | 2950 | 80 | 57 | 103 | 88.8 | 1 | 27.37
DVH090* | 7.5 | 2950 | 80 | 61 | 103 | 88.8 | 1 | 27.37
DVH090* | 7.5 | 2950 | 80 | 64 | 103 | 92.6 | 0.9 | 25.55
DVH090* | 7.5 | 2950 | 80 | 67 | 103 | 97.5 | 0.76 | 22.93
DVH090* | 7.5 | 2950 | 80 | 70 | 103 | 103.7 | 0.64 | 20.52
DVH090* | 7.5 | 2950 | 80 | 72 | 103 | 107.4 | 0.56 | 18.46
DVH090* | 7.5 | 2950 | 80 | 75 | 103 | 113.8 | 0.44 | 15.32
DVH090* | 7.5 | 2950 | 80 | 57 | 106 | 87.9 | 1 | 27.09
DVH090* | 7.5 | 2950 | 80 | 61 | 106 | 87.9 | 1 | 27.09
DVH090* | 7.5 | 2950 | 80 | 64 | 106 | 91.4 | 0.9 | 25.36
DVH090* | 7.5 | 2950 | 80 | 67 | 106 | 96.3 | 0.77 | 22.74
DVH090* | 7.5 | 2950 | 80 | 70 | 106 | 102.4 | 0.65 | 20.37
DVH090* | 7.5 | 2950 | 80 | 72 | 106 | 106 | 0.56 | 18.34
DVH090* | 7.5 | 2950 | 80 | 75 | 106 | 112.4 | 0.44 | 15.13
DVH090* | 7.5 | 2950 | 80 | 57 | 110 | 86.7 | 1 | 26.72
DVH090* | 7.5 | 2950 | 80 | 61 | 110 | 86.7 | 1 | 26.72
DVH090* | 7.5 | 2950 | 80 | 64 | 110 | 89.8 | 0.91 | 25.12
DVH090* | 7.5 | 2950 | 80 | 67 | 110 | 94.6 | 0.77 | 22.53
DVH090* | 7.5 | 2950 | 80 | 70 | 110 | 100.6 | 0.65 | 20.15
DVH090* | 7.5 | 2950 | 80 | 72 | 110 | 104.2 | 0.56 | 18.12
DVH090* | 7.5 | 2950 | 80 | 75 | 110 | 110.5 | 0.44 | 14.95
DVH090* | 7.5 | 2950 | 80 | 57 | 115 | 85.2 | 1 | 26.26
DVH090* | 7.5 | 2950 | 80 | 61 | 115 | 85.2 | 1 | 26.26
DVH090* | 7.5 | 2950 | 80 | 64 | 115 | 87.8 | 0.92 | 24.78
DVH090* | 7.5 | 2950 | 80 | 67 | 115 | 92.5 | 0.78 | 22.22
DVH090* | 7.5 | 2950 | 80 | 70 | 115 | 98.4 | 0.66 | 19.88
DVH090* | 7.5 | 2950 | 80 | 72 | 115 | 101.9 | 0.57 | 17.9
DVH090* | 7.5 | 2950 | 80 | 75 | 115 | 108.1 | 0.44 | 14.67
DVH090* | 7.5 | 2950 | 80 | 57 | 118 | 84.3 | 1 | 25.98
DVH090* | 7.5 | 2950 | 80 | 61 | 118 | 84.3 | 1 | 25.98
DVH090* | 7.5 | 2950 | 80 | 64 | 118 | 86.6 | 0.92 | 24.56
DVH090* | 7.5 | 2950 | 80 | 67 | 118 | 91.3 | 0.78 | 22.03
DVH090* | 7.5 | 2950 | 80 | 70 | 118 | 97 | 0.66 | 19.72
DVH090* | 7.5 | 2950 | 80 | 72 | 118 | 100.5 | 0.57 | 17.75
DVH090* | 7.5 | 2950 | 80 | 75 | 118 | 106.7 | 0.44 | 14.51
DVH090* | 7.5 | 2950 | 85 | 57 | 23 | 109.8 | 1 | 33.84
DVH090* | 7.5 | 2950 | 85 | 61 | 23 | 109.8 | 1 | 33.84
DVH090* | 7.5 | 2950 | 85 | 64 | 23 | 113.2 | 0.93 | 32.54
DVH090* | 7.5 | 2950 | 85 | 67 | 23 | 117.9 | 0.84 | 30.42
DVH090* | 7.5 | 2950 | 85 | 70 | 23 | 125.4 | 0.72 | 27.89
DVH090* | 7.5 | 2950 | 85 | 72 | 23 | 129.9 | 0.64 | 25.58
DVH090* | 7.5 | 2950 | 85 | 75 | 23 | 136.5 | 0.55 | 22.93
DVH090* | 7.5 | 2950 | 85 | 57 | 30 | 109.5 | 1 | 33.74
DVH090* | 7.5 | 2950 | 85 | 61 | 30 | 109.5 | 1 | 33.74
DVH090* | 7.5 | 2950 | 85 | 64 | 30 | 113 | 0.93 | 32.48
DVH090* | 7.5 | 2950 | 85 | 67 | 30 | 117.7 | 0.84 | 30.35
DVH090* | 7.5 | 2950 | 85 | 70 | 30 | 125.1 | 0.72 | 27.83
DVH090* | 7.5 | 2950 | 85 | 72 | 30 | 129.6 | 0.64 | 25.52
DVH090* | 7.5 | 2950 | 85 | 75 | 30 | 136.3 | 0.55 | 22.9
DVH090* | 7.5 | 2950 | 85 | 57 | 40 | 109.2 | 1 | 33.65
DVH090* | 7.5 | 2950 | 85 | 61 | 40 | 109.2 | 1 | 33.65
DVH090* | 7.5 | 2950 | 85 | 64 | 40 | 112.7 | 0.93 | 32.36
DVH090* | 7.5 | 2950 | 85 | 67 | 40 | 117.3 | 0.84 | 30.26
DVH090* | 7.5 | 2950 | 85 | 70 | 40 | 124.8 | 0.72 | 27.77
DVH090* | 7.5 | 2950 | 85 | 72 | 40 | 129.2 | 0.64 | 25.45
DVH090* | 7.5 | 2950 | 85 | 75 | 40 | 136.1 | 0.55 | 22.87
DVH090* | 7.5 | 2950 | 85 | 57 | 50 | 108.9 | 1 | 33.56
DVH090* | 7.5 | 2950 | 85 | 61 | 50 | 108.9 | 1 | 33.56
DVH090* | 7.5 | 2950 | 85 | 64 | 50 | 112.3 | 0.93 | 32.27
DVH090* | 7.5 | 2950 | 85 | 67 | 50 | 117 | 0.84 | 30.17
DVH090* | 7.5 | 2950 | 85 | 70 | 50 | 124.4 | 0.72 | 27.67
DVH090* | 7.5 | 2950 | 85 | 72 | 50 | 128.9 | 0.64 | 25.36
DVH090* | 7.5 | 2950 | 85 | 75 | 50 | 135.9 | 0.55 | 22.84
DVH090* | 7.5 | 2950 | 85 | 57 | 54 | 108.7 | 1 | 33.5
DVH090* | 7.5 | 2950 | 85 | 61 | 54 | 108.7 | 1 | 33.5
DVH090* | 7.5 | 2950 | 85 | 64 | 54 | 112.2 | 0.93 | 32.23
DVH090* | 7.5 | 2950 | 85 | 67 | 54 | 116.9 | 0.84 | 30.14
DVH090* | 7.5 | 2950 | 85 | 70 | 54 | 124.3 | 0.72 | 27.64
DVH090* | 7.5 | 2950 | 85 | 72 | 54 | 128.7 | 0.64 | 25.33
DVH090* | 7.5 | 2950 | 85 | 75 | 54 | 135.8 | 0.54 | 22.8
DVH090* | 7.5 | 2950 | 85 | 57 | 58 | 108.3 | 1 | 33.37
DVH090* | 7.5 | 2950 | 85 | 61 | 58 | 108.3 | 1 | 33.37
DVH090* | 7.5 | 2950 | 85 | 64 | 58 | 111.7 | 0.93 | 32.11
DVH090* | 7.5 | 2950 | 85 | 67 | 58 | 116.3 | 0.84 | 30.02
DVH090* | 7.5 | 2950 | 85 | 70 | 58 | 123.7 | 0.72 | 27.52
DVH090* | 7.5 | 2950 | 85 | 72 | 58 | 128.1 | 0.64 | 25.24
DVH090* | 7.5 | 2950 | 85 | 75 | 58 | 135 | 0.55 | 22.68
DVH090* | 7.5 | 2950 | 85 | 57 | 62 | 107 | 1 | 32.97
DVH090* | 7.5 | 2950 | 85 | 61 | 62 | 107.1 | 1 | 33
DVH090* | 7.5 | 2950 | 85 | 64 | 62 | 110.1 | 0.94 | 31.86
DVH090* | 7.5 | 2950 | 85 | 67 | 62 | 114.7 | 0.84 | 29.8
DVH090* | 7.5 | 2950 | 85 | 70 | 62 | 121.9 | 0.73 | 27.33
DVH090* | 7.5 | 2950 | 85 | 72 | 62 | 126.3 | 0.64 | 25.05
DVH090* | 7.5 | 2950 | 85 | 75 | 62 | 133.1 | 0.55 | 22.4
DVH090* | 7.5 | 2950 | 85 | 57 | 66 | 105.8 | 1 | 32.6
DVH090* | 7.5 | 2950 | 85 | 61 | 66 | 105.8 | 1 | 32.6
DVH090* | 7.5 | 2950 | 85 | 64 | 66 | 108.5 | 0.95 | 31.65
DVH090* | 7.5 | 2950 | 85 | 67 | 66 | 113 | 0.85 | 29.58
DVH090* | 7.5 | 2950 | 85 | 70 | 66 | 120.2 | 0.73 | 27.15
DVH090* | 7.5 | 2950 | 85 | 72 | 66 | 124.5 | 0.65 | 24.87
DVH090* | 7.5 | 2950 | 85 | 75 | 66 | 131.2 | 0.55 | 22.16
DVH090* | 7.5 | 2950 | 85 | 57 | 70 | 104.5 | 1 | 32.2
DVH090* | 7.5 | 2950 | 85 | 61 | 70 | 104.5 | 1 | 32.2
DVH090* | 7.5 | 2950 | 85 | 64 | 70 | 106.9 | 0.95 | 31.43
DVH090* | 7.5 | 2950 | 85 | 67 | 70 | 111.3 | 0.86 | 29.37
DVH090* | 7.5 | 2950 | 85 | 70 | 70 | 118.4 | 0.74 | 26.93
DVH090* | 7.5 | 2950 | 85 | 72 | 70 | 122.6 | 0.65 | 24.68
DVH090* | 7.5 | 2950 | 85 | 75 | 70 | 129.4 | 0.55 | 21.91
DVH090* | 7.5 | 2950 | 85 | 57 | 72 | 103.9 | 1 | 32.02
DVH090* | 7.5 | 2950 | 85 | 61 | 72 | 103.9 | 1 | 32.02
DVH090* | 7.5 | 2950 | 85 | 64 | 72 | 106.1 | 0.96 | 31.31
DVH090* | 7.5 | 2950 | 85 | 67 | 72 | 110.5 | 0.86 | 29.28
DVH090* | 7.5 | 2950 | 85 | 70 | 72 | 117.5 | 0.74 | 26.84
DVH090* | 7.5 | 2950 | 85 | 72 | 72 | 121.7 | 0.66 | 24.59
DVH090* | 7.5 | 2950 | 85 | 75 | 72 | 128.4 | 0.55 | 21.79
DVH090* | 7.5 | 2950 | 85 | 57 | 75 | 102.9 | 1 | 31.71
DVH090* | 7.5 | 2950 | 85 | 61 | 75 | 102.9 | 1 | 31.71
DVH090* | 7.5 | 2950 | 85 | 64 | 75 | 104.9 | 0.96 | 31.12
DVH090* | 7.5 | 2950 | 85 | 67 | 75 | 109.2 | 0.86 | 29.09
DVH090* | 7.5 | 2950 | 85 | 70 | 75 | 116.2 | 0.75 | 26.69
DVH090* | 7.5 | 2950 | 85 | 72 | 75 | 120.3 | 0.66 | 24.47
DVH090* | 7.5 | 2950 | 85 | 75 | 75 | 127 | 0.55 | 21.6
DVH090* | 7.5 | 2950 | 85 | 57 | 79 | 101.6 | 1 | 31.31
DVH090* | 7.5 | 2950 | 85 | 61 | 79 | 101.6 | 1 | 31.31
DVH090* | 7.5 | 2950 | 85 | 64 | 79 | 103.3 | 0.97 | 30.88
DVH090* | 7.5 | 2950 | 85 | 67 | 79 | 107.6 | 0.87 | 28.88
DVH090* | 7.5 | 2950 | 85 | 70 | 79 | 114.4 | 0.75 | 26.47
DVH090* | 7.5 | 2950 | 85 | 72 | 79 | 118.5 | 0.66 | 24.28
DVH090* | 7.5 | 2950 | 85 | 75 | 79 | 125.1 | 0.55 | 21.33
DVH090* | 7.5 | 2950 | 85 | 57 | 83 | 100.3 | 1 | 30.91
DVH090* | 7.5 | 2950 | 85 | 61 | 83 | 100.3 | 1 | 30.91
DVH090* | 7.5 | 2950 | 85 | 64 | 83 | 101.7 | 0.98 | 30.63
DVH090* | 7.5 | 2950 | 85 | 67 | 83 | 105.9 | 0.88 | 28.63
DVH090* | 7.5 | 2950 | 85 | 70 | 83 | 112.6 | 0.76 | 26.26
DVH090* | 7.5 | 2950 | 85 | 72 | 83 | 116.6 | 0.67 | 24.07
DVH090* | 7.5 | 2950 | 85 | 75 | 83 | 123.2 | 0.56 | 21.08
DVH090* | 7.5 | 2950 | 85 | 57 | 87 | 99.1 | 1 | 30.54
DVH090* | 7.5 | 2950 | 85 | 61 | 87 | 99.1 | 1 | 30.54
DVH090* | 7.5 | 2950 | 85 | 64 | 87 | 100.1 | 0.98 | 30.35
DVH090* | 7.5 | 2950 | 85 | 67 | 87 | 104.2 | 0.88 | 28.41
DVH090* | 7.5 | 2950 | 85 | 70 | 87 | 110.8 | 0.76 | 26.04
DVH090* | 7.5 | 2950 | 85 | 72 | 87 | 114.8 | 0.68 | 23.88
DVH090* | 7.5 | 2950 | 85 | 75 | 87 | 121.3 | 0.56 | 20.83
DVH090* | 7.5 | 2950 | 85 | 57 | 91 | 97.8 | 1 | 30.14
DVH090* | 7.5 | 2950 | 85 | 61 | 91 | 97.8 | 1 | 30.14
DVH090* | 7.5 | 2950 | 85 | 64 | 91 | 98.5 | 0.99 | 30.11
DVH090* | 7.5 | 2950 | 85 | 67 | 91 | 102.5 | 0.89 | 28.14
DVH090* | 7.5 | 2950 | 85 | 70 | 91 | 109 | 0.77 | 25.82
DVH090* | 7.5 | 2950 | 85 | 72 | 91 | 112.9 | 0.68 | 23.67
DVH090* | 7.5 | 2950 | 85 | 75 | 91 | 119.4 | 0.56 | 20.55
DVH090* | 7.5 | 2950 | 85 | 57 | 93 | 97.2 | 1 | 29.95
DVH090* | 7.5 | 2950 | 85 | 61 | 93 | 97.2 | 1 | 29.95
DVH090* | 7.5 | 2950 | 85 | 64 | 93 | 97.7 | 0.99 | 29.95
DVH090* | 7.5 | 2950 | 85 | 67 | 93 | 101.7 | 0.89 | 28.01
DVH090* | 7.5 | 2950 | 85 | 70 | 93 | 108.2 | 0.77 | 25.7
DVH090* | 7.5 | 2950 | 85 | 72 | 93 | 112 | 0.68 | 23.54
DVH090* | 7.5 | 2950 | 85 | 75 | 93 | 118.5 | 0.56 | 20.43
DVH090* | 7.5 | 2950 | 85 | 57 | 95 | 96.5 | 1 | 29.74
DVH090* | 7.5 | 2950 | 85 | 61 | 95 | 96.5 | 1 | 29.74
DVH090* | 7.5 | 2950 | 85 | 64 | 95 | 96.9 | 1 | 29.83
DVH090* | 7.5 | 2950 | 85 | 67 | 95 | 100.9 | 0.9 | 27.89
DVH090* | 7.5 | 2950 | 85 | 70 | 95 | 107.3 | 0.77 | 25.58
DVH090* | 7.5 | 2950 | 85 | 72 | 95 | 111.1 | 0.68 | 23.45
DVH090* | 7.5 | 2950 | 85 | 75 | 95 | 117.6 | 0.56 | 20.31
DVH090* | 7.5 | 2950 | 85 | 57 | 99 | 95.2 | 1 | 29.34
DVH090* | 7.5 | 2950 | 85 | 61 | 99 | 95.2 | 1 | 29.34
DVH090* | 7.5 | 2950 | 85 | 64 | 99 | 95.3 | 1 | 29.37
DVH090* | 7.5 | 2950 | 85 | 67 | 99 | 99.2 | 0.9 | 27.64
DVH090* | 7.5 | 2950 | 85 | 70 | 99 | 105.5 | 0.78 | 25.33
DVH090* | 7.5 | 2950 | 85 | 72 | 99 | 109.3 | 0.69 | 23.24
DVH090* | 7.5 | 2950 | 85 | 75 | 99 | 115.7 | 0.56 | 20.03
DVH090* | 7.5 | 2950 | 85 | 57 | 103 | 94 | 1 | 28.97
DVH090* | 7.5 | 2950 | 85 | 61 | 103 | 94 | 1 | 28.97
DVH090* | 7.5 | 2950 | 85 | 64 | 103 | 93.6 | 1 | 28.84
DVH090* | 7.5 | 2950 | 85 | 67 | 103 | 97.5 | 0.91 | 27.37
DVH090* | 7.5 | 2950 | 85 | 70 | 103 | 103.7 | 0.78 | 25.08
DVH090* | 7.5 | 2950 | 85 | 72 | 103 | 107.4 | 0.69 | 22.99
DVH090* | 7.5 | 2950 | 85 | 75 | 103 | 113.8 | 0.56 | 19.75
DVH090* | 7.5 | 2950 | 85 | 57 | 106 | 93 | 1 | 28.66
DVH090* | 7.5 | 2950 | 85 | 61 | 106 | 93 | 1 | 28.66
DVH090* | 7.5 | 2950 | 85 | 64 | 106 | 92.4 | 1 | 28.47
DVH090* | 7.5 | 2950 | 85 | 67 | 106 | 96.3 | 0.91 | 27.15
DVH090* | 7.5 | 2950 | 85 | 70 | 106 | 102.4 | 0.79 | 24.9
DVH090* | 7.5 | 2950 | 85 | 72 | 106 | 106 | 0.7 | 22.84
DVH090* | 7.5 | 2950 | 85 | 75 | 106 | 112.4 | 0.56 | 19.57
DVH090* | 7.5 | 2950 | 85 | 57 | 110 | 91.7 | 1 | 28.26
DVH090* | 7.5 | 2950 | 85 | 61 | 110 | 91.7 | 1 | 28.26
DVH090* | 7.5 | 2950 | 85 | 64 | 110 | 90.8 | 1 | 27.98
DVH090* | 7.5 | 2950 | 85 | 67 | 110 | 94.6 | 0.92 | 26.87
DVH090* | 7.5 | 2950 | 85 | 70 | 110 | 100.6 | 0.8 | 24.65
DVH090* | 7.5 | 2950 | 85 | 72 | 110 | 104.2 | 0.7 | 22.59
DVH090* | 7.5 | 2950 | 85 | 75 | 110 | 110.5 | 0.57 | 19.29
DVH090* | 7.5 | 2950 | 85 | 57 | 115 | 90.1 | 1 | 27.77
DVH090* | 7.5 | 2950 | 85 | 61 | 115 | 90.1 | 1 | 27.77
DVH090* | 7.5 | 2950 | 85 | 64 | 115 | 88.8 | 1 | 27.37
DVH090* | 7.5 | 2950 | 85 | 67 | 115 | 92.5 | 0.93 | 26.5
DVH090* | 7.5 | 2950 | 85 | 70 | 115 | 98.4 | 0.8 | 24.31
DVH090* | 7.5 | 2950 | 85 | 72 | 115 | 101.9 | 0.71 | 22.28
DVH090* | 7.5 | 2950 | 85 | 75 | 115 | 108.1 | 0.57 | 18.95
DVH090* | 7.5 | 2950 | 85 | 57 | 118 | 89.2 | 1 | 27.49
DVH090* | 7.5 | 2950 | 85 | 61 | 118 | 89.2 | 1 | 27.49
DVH090* | 7.5 | 2950 | 85 | 64 | 118 | 87.6 | 1 | 27
DVH090* | 7.5 | 2950 | 85 | 67 | 118 | 91.3 | 0.93 | 26.29
DVH090* | 7.5 | 2950 | 85 | 70 | 118 | 97 | 0.81 | 24.1
DVH090* | 7.5 | 2950 | 85 | 72 | 118 | 100.5 | 0.71 | 22.1
DVH090* | 7.5 | 2950 | 85 | 75 | 118 | 106.7 | 0.57 | 18.74
DVH090* | 7.5 | 3350 | 70 | 57 | 23 | 96.9 | 0.91 | 23.88
DVH090* | 7.5 | 3350 | 70 | 61 | 23 | 105.8 | 0.71 | 20.3
DVH090* | 7.5 | 3350 | 70 | 64 | 23 | 114.2 | 0.55 | 16.96
DVH090* | 7.5 | 3350 | 70 | 67 | 23 | 120.3 | 0.43 | 14.17
DVH090* | 7.5 | 3350 | 70 | 57 | 30 | 96.7 | 0.91 | 23.83
DVH090* | 7.5 | 3350 | 70 | 61 | 30 | 105.6 | 0.71 | 20.24
DVH090* | 7.5 | 3350 | 70 | 64 | 30 | 114 | 0.55 | 16.93
DVH090* | 7.5 | 3350 | 70 | 67 | 30 | 120.1 | 0.43 | 14.14
DVH090* | 7.5 | 3350 | 70 | 57 | 40 | 96.4 | 0.91 | 23.74
DVH090* | 7.5 | 3350 | 70 | 61 | 40 | 105.3 | 0.71 | 20.19
DVH090* | 7.5 | 3350 | 70 | 64 | 40 | 113.6 | 0.55 | 16.88
DVH090* | 7.5 | 3350 | 70 | 67 | 40 | 119.7 | 0.43 | 14.11
DVH090* | 7.5 | 3350 | 70 | 57 | 50 | 96.1 | 0.91 | 23.69
DVH090* | 7.5 | 3350 | 70 | 61 | 50 | 105 | 0.71 | 20.14
DVH090* | 7.5 | 3350 | 70 | 64 | 50 | 113.3 | 0.55 | 16.82
DVH090* | 7.5 | 3350 | 70 | 67 | 50 | 119.4 | 0.43 | 14.06
DVH090* | 7.5 | 3350 | 70 | 57 | 54 | 96 | 0.91 | 23.66
DVH090* | 7.5 | 3350 | 70 | 61 | 54 | 104.8 | 0.71 | 20.11
DVH090* | 7.5 | 3350 | 70 | 64 | 54 | 113.2 | 0.55 | 16.8
DVH090* | 7.5 | 3350 | 70 | 67 | 54 | 119.2 | 0.43 | 14.03
DVH090* | 7.5 | 3350 | 70 | 57 | 58 | 95.7 | 0.91 | 23.55
DVH090* | 7.5 | 3350 | 70 | 61 | 58 | 104.4 | 0.71 | 20.03
DVH090* | 7.5 | 3350 | 70 | 64 | 58 | 112.7 | 0.55 | 16.74
DVH090* | 7.5 | 3350 | 70 | 67 | 58 | 118.7 | 0.43 | 13.98
DVH090* | 7.5 | 3350 | 70 | 57 | 62 | 94.5 | 0.91 | 23.34
DVH090* | 7.5 | 3350 | 70 | 61 | 62 | 103.2 | 0.71 | 19.81
DVH090* | 7.5 | 3350 | 70 | 64 | 62 | 111.1 | 0.55 | 16.61
DVH090* | 7.5 | 3350 | 70 | 67 | 62 | 117 | 0.44 | 13.87
DVH090* | 7.5 | 3350 | 70 | 57 | 66 | 93.4 | 0.91 | 23.12
DVH090* | 7.5 | 3350 | 70 | 61 | 66 | 102 | 0.71 | 19.65
DVH090* | 7.5 | 3350 | 70 | 64 | 66 | 109.4 | 0.56 | 16.5
DVH090* | 7.5 | 3350 | 70 | 67 | 66 | 115.3 | 0.44 | 13.79
DVH090* | 7.5 | 3350 | 70 | 57 | 70 | 92.3 | 0.91 | 22.9
DVH090* | 7.5 | 3350 | 70 | 61 | 70 | 100.7 | 0.71 | 19.46
DVH090* | 7.5 | 3350 | 70 | 64 | 70 | 107.8 | 0.56 | 16.39
DVH090* | 7.5 | 3350 | 70 | 67 | 70 | 113.6 | 0.44 | 13.68
DVH090* | 7.5 | 3350 | 70 | 57 | 72 | 91.7 | 0.92 | 22.8
DVH090* | 7.5 | 3350 | 70 | 61 | 72 | 100.1 | 0.71 | 19.38
DVH090* | 7.5 | 3350 | 70 | 64 | 72 | 107 | 0.56 | 16.31
DVH090* | 7.5 | 3350 | 70 | 67 | 72 | 112.7 | 0.45 | 13.62
DVH090* | 7.5 | 3350 | 70 | 57 | 75 | 90.9 | 0.92 | 22.66
DVH090* | 7.5 | 3350 | 70 | 61 | 75 | 99.2 | 0.71 | 19.24
DVH090* | 7.5 | 3350 | 70 | 64 | 75 | 105.8 | 0.57 | 16.23
DVH090* | 7.5 | 3350 | 70 | 67 | 75 | 111.5 | 0.45 | 13.54
DVH090* | 7.5 | 3350 | 70 | 57 | 79 | 89.7 | 0.92 | 22.44
DVH090* | 7.5 | 3350 | 70 | 61 | 79 | 98 | 0.72 | 19.08
DVH090* | 7.5 | 3350 | 70 | 64 | 79 | 104.2 | 0.57 | 16.09
DVH090* | 7.5 | 3350 | 70 | 67 | 79 | 109.8 | 0.45 | 13.46
DVH090* | 7.5 | 3350 | 70 | 57 | 83 | 88.6 | 0.92 | 22.23
DVH090* | 7.5 | 3350 | 70 | 61 | 83 | 96.7 | 0.72 | 18.89
DVH090* | 7.5 | 3350 | 70 | 64 | 83 | 102.6 | 0.57 | 15.96
DVH090* | 7.5 | 3350 | 70 | 67 | 83 | 108 | 0.46 | 13.35
DVH090* | 7.5 | 3350 | 70 | 57 | 87 | 87.5 | 0.93 | 22.01
DVH090* | 7.5 | 3350 | 70 | 61 | 87 | 95.5 | 0.72 | 18.7
DVH090* | 7.5 | 3350 | 70 | 64 | 87 | 100.9 | 0.58 | 15.82
DVH090* | 7.5 | 3350 | 70 | 67 | 87 | 106.3 | 0.46 | 13.22
DVH090* | 7.5 | 3350 | 70 | 57 | 91 | 86.4 | 0.93 | 21.79
DVH090* | 7.5 | 3350 | 70 | 61 | 91 | 94.3 | 0.72 | 18.51
DVH090* | 7.5 | 3350 | 70 | 64 | 91 | 99.3 | 0.58 | 15.69
DVH090* | 7.5 | 3350 | 70 | 67 | 91 | 104.6 | 0.46 | 13.11
DVH090* | 7.5 | 3350 | 70 | 57 | 93 | 85.8 | 0.93 | 21.68
DVH090* | 7.5 | 3350 | 70 | 61 | 93 | 93.7 | 0.72 | 18.43
DVH090* | 7.5 | 3350 | 70 | 64 | 93 | 98.5 | 0.58 | 15.63
DVH090* | 7.5 | 3350 | 70 | 67 | 93 | 103.8 | 0.46 | 13.05
DVH090* | 7.5 | 3350 | 70 | 57 | 95 | 85.2 | 0.93 | 21.57
DVH090* | 7.5 | 3350 | 70 | 61 | 95 | 93 | 0.73 | 18.32
DVH090* | 7.5 | 3350 | 70 | 64 | 95 | 97.7 | 0.59 | 15.55
DVH090* | 7.5 | 3350 | 70 | 67 | 95 | 102.9 | 0.47 | 13
DVH090* | 7.5 | 3350 | 70 | 57 | 99 | 84.1 | 0.94 | 21.36
DVH090* | 7.5 | 3350 | 70 | 61 | 99 | 91.8 | 0.73 | 18.15
DVH090* | 7.5 | 3350 | 70 | 64 | 99 | 96.1 | 0.59 | 15.41
DVH090* | 7.5 | 3350 | 70 | 67 | 99 | 101.2 | 0.47 | 12.86
DVH090* | 7.5 | 3350 | 70 | 57 | 103 | 83 | 0.94 | 21.14
DVH090* | 7.5 | 3350 | 70 | 61 | 103 | 90.6 | 0.73 | 17.96
DVH090* | 7.5 | 3350 | 70 | 64 | 103 | 94.5 | 0.59 | 15.25
DVH090* | 7.5 | 3350 | 70 | 67 | 103 | 99.5 | 0.47 | 12.75
DVH090* | 7.5 | 3350 | 70 | 57 | 106 | 82.1 | 0.94 | 20.95
DVH090* | 7.5 | 3350 | 70 | 61 | 106 | 89.7 | 0.73 | 17.8
DVH090* | 7.5 | 3350 | 70 | 64 | 106 | 93.2 | 0.6 | 15.14
DVH090* | 7.5 | 3350 | 70 | 67 | 106 | 98.2 | 0.47 | 12.65
DVH090* | 7.5 | 3350 | 70 | 57 | 110 | 81 | 0.94 | 20.73
DVH090* | 7.5 | 3350 | 70 | 61 | 110 | 88.4 | 0.73 | 17.61
DVH090* | 7.5 | 3350 | 70 | 64 | 110 | 91.6 | 0.6 | 14.98
DVH090* | 7.5 | 3350 | 70 | 67 | 110 | 96.5 | 0.48 | 12.51
DVH090* | 7.5 | 3350 | 70 | 57 | 115 | 79.6 | 0.95 | 20.46
DVH090* | 7.5 | 3350 | 70 | 61 | 115 | 86.9 | 0.74 | 17.37
DVH090* | 7.5 | 3350 | 70 | 64 | 115 | 89.6 | 0.61 | 14.79
DVH090* | 7.5 | 3350 | 70 | 67 | 115 | 94.4 | 0.48 | 12.35
DVH090* | 7.5 | 3350 | 70 | 57 | 118 | 78.7 | 0.95 | 20.27
DVH090* | 7.5 | 3350 | 70 | 61 | 118 | 86 | 0.74 | 17.23
DVH090* | 7.5 | 3350 | 70 | 64 | 118 | 88.4 | 0.61 | 14.65
DVH090* | 7.5 | 3350 | 70 | 67 | 118 | 93.1 | 0.48 | 12.24
DVH090* | 7.5 | 3350 | 75 | 57 | 23 | 99.8 | 1 | 27.08
DVH090* | 7.5 | 3350 | 75 | 61 | 23 | 104.7 | 0.87 | 24.75
DVH090* | 7.5 | 3350 | 75 | 64 | 23 | 114.2 | 0.7 | 21.6
DVH090* | 7.5 | 3350 | 75 | 67 | 23 | 120.3 | 0.58 | 18.86
DVH090* | 7.5 | 3350 | 75 | 70 | 23 | 127.9 | 0.47 | 16.28
DVH090* | 7.5 | 3350 | 75 | 72 | 23 | 132.5 | 0.4 | 14.22
DVH090* | 7.5 | 3350 | 75 | 57 | 30 | 99.6 | 1 | 27.03
DVH090* | 7.5 | 3350 | 75 | 61 | 30 | 104.4 | 0.87 | 24.69
DVH090* | 7.5 | 3350 | 75 | 64 | 30 | 114 | 0.7 | 21.57
DVH090* | 7.5 | 3350 | 75 | 67 | 30 | 120.1 | 0.58 | 18.81
DVH090* | 7.5 | 3350 | 75 | 70 | 30 | 127.7 | 0.47 | 16.26
DVH090* | 7.5 | 3350 | 75 | 72 | 30 | 132.2 | 0.39 | 14.17
DVH090* | 7.5 | 3350 | 75 | 57 | 40 | 99.3 | 1 | 26.95
DVH090* | 7.5 | 3350 | 75 | 61 | 40 | 104.1 | 0.87 | 24.61
DVH090* | 7.5 | 3350 | 75 | 64 | 40 | 113.6 | 0.7 | 21.49
DVH090* | 7.5 | 3350 | 75 | 67 | 40 | 119.7 | 0.58 | 18.75
DVH090* | 7.5 | 3350 | 75 | 70 | 40 | 127.3 | 0.47 | 16.2
DVH090* | 7.5 | 3350 | 75 | 72 | 40 | 131.9 | 0.39 | 14.14
DVH090* | 7.5 | 3350 | 75 | 57 | 50 | 98.9 | 1 | 26.84
DVH090* | 7.5 | 3350 | 75 | 61 | 50 | 103.8 | 0.87 | 24.56
DVH090* | 7.5 | 3350 | 75 | 64 | 50 | 113.3 | 0.7 | 21.44
DVH090* | 7.5 | 3350 | 75 | 67 | 50 | 119.4 | 0.58 | 18.7
DVH090* | 7.5 | 3350 | 75 | 70 | 50 | 126.9 | 0.47 | 16.17
DVH090* | 7.5 | 3350 | 75 | 72 | 50 | 131.5 | 0.39 | 14.08
DVH090* | 7.5 | 3350 | 75 | 57 | 54 | 98.8 | 1 | 26.81
DVH090* | 7.5 | 3350 | 75 | 61 | 54 | 103.7 | 0.87 | 24.53
DVH090* | 7.5 | 3350 | 75 | 64 | 54 | 113.2 | 0.7 | 21.41
DVH090* | 7.5 | 3350 | 75 | 67 | 54 | 119.2 | 0.58 | 18.7
DVH090* | 7.5 | 3350 | 75 | 70 | 54 | 126.8 | 0.47 | 16.15
DVH090* | 7.5 | 3350 | 75 | 72 | 54 | 131.3 | 0.4 | 14.08
DVH090* | 7.5 | 3350 | 75 | 57 | 58 | 98.5 | 1 | 26.73
DVH090* | 7.5 | 3350 | 75 | 61 | 58 | 103.3 | 0.87 | 24.42
DVH090* | 7.5 | 3350 | 75 | 64 | 58 | 112.7 | 0.7 | 21.33
DVH090* | 7.5 | 3350 | 75 | 67 | 58 | 118.7 | 0.58 | 18.62
DVH090* | 7.5 | 3350 | 75 | 70 | 58 | 126.2 | 0.47 | 16.07
DVH090* | 7.5 | 3350 | 75 | 72 | 58 | 130.8 | 0.4 | 14.03
DVH090* | 7.5 | 3350 | 75 | 57 | 62 | 97.3 | 1 | 26.4
DVH090* | 7.5 | 3350 | 75 | 61 | 62 | 102.1 | 0.87 | 24.18
DVH090* | 7.5 | 3350 | 75 | 64 | 62 | 111.1 | 0.7 | 21.17
DVH090* | 7.5 | 3350 | 75 | 67 | 62 | 117 | 0.58 | 18.48
DVH090* | 7.5 | 3350 | 75 | 70 | 62 | 124.4 | 0.47 | 15.96
DVH090* | 7.5 | 3350 | 75 | 72 | 62 | 128.9 | 0.4 | 13.92
DVH090* | 7.5 | 3350 | 75 | 57 | 66 | 96.1 | 1 | 26.08
DVH090* | 7.5 | 3350 | 75 | 61 | 66 | 100.9 | 0.88 | 23.96
DVH090* | 7.5 | 3350 | 75 | 64 | 66 | 109.4 | 0.71 | 21.03
DVH090* | 7.5 | 3350 | 75 | 67 | 66 | 115.3 | 0.59 | 18.34
DVH090* | 7.5 | 3350 | 75 | 70 | 66 | 122.6 | 0.48 | 15.85
DVH090* | 7.5 | 3350 | 75 | 72 | 66 | 127 | 0.4 | 13.81
DVH090* | 7.5 | 3350 | 75 | 57 | 70 | 95 | 1 | 25.78
DVH090* | 7.5 | 3350 | 75 | 61 | 70 | 99.6 | 0.88 | 23.74
DVH090* | 7.5 | 3350 | 75 | 64 | 70 | 107.8 | 0.71 | 20.87
DVH090* | 7.5 | 3350 | 75 | 67 | 70 | 113.6 | 0.59 | 18.21
DVH090* | 7.5 | 3350 | 75 | 70 | 70 | 120.8 | 0.48 | 15.74
DVH090* | 7.5 | 3350 | 75 | 72 | 70 | 125.1 | 0.4 | 13.73
DVH090* | 7.5 | 3350 | 75 | 57 | 72 | 94.4 | 1 | 25.62
DVH090* | 7.5 | 3350 | 75 | 61 | 72 | 99 | 0.88 | 23.64
DVH090* | 7.5 | 3350 | 75 | 64 | 72 | 107 | 0.72 | 20.79
DVH090* | 7.5 | 3350 | 75 | 67 | 72 | 112.7 | 0.59 | 18.13
DVH090* | 7.5 | 3350 | 75 | 70 | 72 | 119.9 | 0.48 | 15.69
DVH090* | 7.5 | 3350 | 75 | 72 | 72 | 124.2 | 0.41 | 13.68
DVH090* | 7.5 | 3350 | 75 | 57 | 75 | 93.5 | 1 | 25.37
DVH090* | 7.5 | 3350 | 75 | 61 | 75 | 98.1 | 0.88 | 23.47
DVH090* | 7.5 | 3350 | 75 | 64 | 75 | 105.8 | 0.72 | 20.68
DVH090* | 7.5 | 3350 | 75 | 67 | 75 | 111.5 | 0.6 | 18.05
DVH090* | 7.5 | 3350 | 75 | 70 | 75 | 118.5 | 0.48 | 15.58
DVH090* | 7.5 | 3350 | 75 | 72 | 75 | 122.8 | 0.41 | 13.6
DVH090* | 7.5 | 3350 | 75 | 57 | 79 | 92.4 | 1 | 25.07
DVH090* | 7.5 | 3350 | 75 | 61 | 79 | 96.9 | 0.88 | 23.26
DVH090* | 7.5 | 3350 | 75 | 64 | 79 | 104.2 | 0.73 | 20.52
DVH090* | 7.5 | 3350 | 75 | 67 | 79 | 109.8 | 0.6 | 17.88
DVH090* | 7.5 | 3350 | 75 | 70 | 79 | 116.7 | 0.49 | 15.47
DVH090* | 7.5 | 3350 | 75 | 72 | 79 | 120.9 | 0.41 | 13.49
DVH090* | 7.5 | 3350 | 75 | 57 | 83 | 91.2 | 1 | 24.75
DVH090* | 7.5 | 3350 | 75 | 61 | 83 | 95.7 | 0.89 | 23.04
DVH090* | 7.5 | 3350 | 75 | 64 | 83 | 102.6 | 0.73 | 20.35
DVH090* | 7.5 | 3350 | 75 | 67 | 83 | 108 | 0.61 | 17.75
DVH090* | 7.5 | 3350 | 75 | 70 | 83 | 114.9 | 0.49 | 15.33
DVH090* | 7.5 | 3350 | 75 | 72 | 83 | 119 | 0.41 | 13.38
DVH090* | 7.5 | 3350 | 75 | 57 | 87 | 90 | 1 | 24.42
DVH090* | 7.5 | 3350 | 75 | 61 | 87 | 94.5 | 0.89 | 22.82
DVH090* | 7.5 | 3350 | 75 | 64 | 87 | 100.9 | 0.74 | 20.16
DVH090* | 7.5 | 3350 | 75 | 67 | 87 | 106.3 | 0.61 | 17.61
DVH090* | 7.5 | 3350 | 75 | 70 | 87 | 113.1 | 0.5 | 15.2
DVH090* | 7.5 | 3350 | 75 | 72 | 87 | 117.1 | 0.42 | 13.27
DVH090* | 7.5 | 3350 | 75 | 57 | 91 | 88.9 | 1 | 24.12
DVH090* | 7.5 | 3350 | 75 | 61 | 91 | 93.2 | 0.89 | 22.58
DVH090* | 7.5 | 3350 | 75 | 64 | 91 | 99.3 | 0.74 | 20
DVH090* | 7.5 | 3350 | 75 | 67 | 91 | 104.6 | 0.61 | 17.45
DVH090* | 7.5 | 3350 | 75 | 70 | 91 | 111.3 | 0.5 | 15.09
DVH090* | 7.5 | 3350 | 75 | 72 | 91 | 115.2 | 0.42 | 13.13
DVH090* | 7.5 | 3350 | 75 | 57 | 93 | 88.3 | 1 | 23.96
DVH090* | 7.5 | 3350 | 75 | 61 | 93 | 92.6 | 0.89 | 22.47
DVH090* | 7.5 | 3350 | 75 | 64 | 93 | 98.5 | 0.75 | 19.92
DVH090* | 7.5 | 3350 | 75 | 67 | 93 | 103.8 | 0.62 | 17.37
DVH090* | 7.5 | 3350 | 75 | 70 | 93 | 110.4 | 0.5 | 15.01
DVH090* | 7.5 | 3350 | 75 | 72 | 93 | 114.3 | 0.42 | 13.08
DVH090* | 7.5 | 3350 | 75 | 57 | 95 | 87.7 | 1 | 23.8
DVH090* | 7.5 | 3350 | 75 | 61 | 95 | 92 | 0.9 | 22.36
DVH090* | 7.5 | 3350 | 75 | 64 | 95 | 97.7 | 0.75 | 19.81
DVH090* | 7.5 | 3350 | 75 | 67 | 95 | 102.9 | 0.62 | 17.29
DVH090* | 7.5 | 3350 | 75 | 70 | 95 | 109.4 | 0.5 | 14.95
DVH090* | 7.5 | 3350 | 75 | 72 | 95 | 113.4 | 0.42 | 13.03
DVH090* | 7.5 | 3350 | 75 | 57 | 99 | 86.6 | 1 | 23.5
DVH090* | 7.5 | 3350 | 75 | 61 | 99 | 90.8 | 0.9 | 22.14
DVH090* | 7.5 | 3350 | 75 | 64 | 99 | 96.1 | 0.75 | 19.62
DVH090* | 7.5 | 3350 | 75 | 67 | 99 | 101.2 | 0.62 | 17.12
DVH090* | 7.5 | 3350 | 75 | 70 | 99 | 107.6 | 0.51 | 14.79
DVH090* | 7.5 | 3350 | 75 | 72 | 99 | 111.5 | 0.43 | 12.92
DVH090* | 7.5 | 3350 | 75 | 57 | 103 | 85.4 | 1 | 23.18
DVH090* | 7.5 | 3350 | 75 | 61 | 103 | 89.6 | 0.9 | 21.9
DVH090* | 7.5 | 3350 | 75 | 64 | 103 | 94.5 | 0.76 | 19.43
DVH090* | 7.5 | 3350 | 75 | 67 | 103 | 99.5 | 0.63 | 16.96
DVH090* | 7.5 | 3350 | 75 | 70 | 103 | 105.8 | 0.51 | 14.65
DVH090* | 7.5 | 3350 | 75 | 72 | 103 | 109.6 | 0.43 | 12.78
DVH090* | 7.5 | 3350 | 75 | 57 | 106 | 84.5 | 1 | 22.93
DVH090* | 7.5 | 3350 | 75 | 61 | 106 | 88.7 | 0.9 | 21.74
DVH090* | 7.5 | 3350 | 75 | 64 | 106 | 93.2 | 0.76 | 19.29
DVH090* | 7.5 | 3350 | 75 | 67 | 106 | 98.2 | 0.63 | 16.82
DVH090* | 7.5 | 3350 | 75 | 70 | 106 | 104.5 | 0.51 | 14.55
DVH090* | 7.5 | 3350 | 75 | 72 | 106 | 108.2 | 0.43 | 12.67
DVH090* | 7.5 | 3350 | 75 | 57 | 110 | 83.4 | 1 | 22.63
DVH090* | 7.5 | 3350 | 75 | 61 | 110 | 87.5 | 0.91 | 21.49
DVH090* | 7.5 | 3350 | 75 | 64 | 110 | 91.6 | 0.77 | 19.08
DVH090* | 7.5 | 3350 | 75 | 67 | 110 | 96.5 | 0.64 | 16.66
DVH090* | 7.5 | 3350 | 75 | 70 | 110 | 102.6 | 0.52 | 14.38
DVH090* | 7.5 | 3350 | 75 | 72 | 110 | 106.3 | 0.44 | 12.56
DVH090* | 7.5 | 3350 | 75 | 57 | 115 | 81.9 | 1 | 22.23
DVH090* | 7.5 | 3350 | 75 | 61 | 115 | 85.9 | 0.91 | 21.19
DVH090* | 7.5 | 3350 | 75 | 64 | 115 | 89.6 | 0.77 | 18.83
DVH090* | 7.5 | 3350 | 75 | 67 | 115 | 94.4 | 0.64 | 16.45
DVH090* | 7.5 | 3350 | 75 | 70 | 115 | 100.4 | 0.52 | 14.19
DVH090* | 7.5 | 3350 | 75 | 72 | 115 | 104 | 0.44 | 12.37
DVH090* | 7.5 | 3350 | 75 | 57 | 118 | 81 | 1 | 21.98
DVH090* | 7.5 | 3350 | 75 | 61 | 118 | 85 | 0.91 | 21.03
DVH090* | 7.5 | 3350 | 75 | 64 | 118 | 88.4 | 0.78 | 18.67
DVH090* | 7.5 | 3350 | 75 | 67 | 118 | 93.1 | 0.64 | 16.28
DVH090* | 7.5 | 3350 | 75 | 70 | 118 | 99 | 0.52 | 14.08
DVH090* | 7.5 | 3350 | 75 | 72 | 118 | 102.6 | 0.44 | 12.29
DVH090* | 7.5 | 3350 | 80 | 57 | 23 | 105.8 | 1 | 28.71
DVH090* | 7.5 | 3350 | 80 | 61 | 23 | 105.8 | 1 | 28.71
DVH090* | 7.5 | 3350 | 80 | 64 | 23 | 114.2 | 0.85 | 26.19
DVH090* | 7.5 | 3350 | 80 | 67 | 23 | 120.3 | 0.72 | 23.47
DVH090* | 7.5 | 3350 | 80 | 70 | 23 | 127.9 | 0.61 | 21.03
DVH090* | 7.5 | 3350 | 80 | 72 | 23 | 132.5 | 0.53 | 18.91
DVH090* | 7.5 | 3350 | 80 | 75 | 23 | 139.3 | 0.43 | 16.36
DVH090* | 7.5 | 3350 | 80 | 57 | 30 | 105.6 | 1 | 28.66
DVH090* | 7.5 | 3350 | 80 | 61 | 30 | 105.6 | 1 | 28.66
DVH090* | 7.5 | 3350 | 80 | 64 | 30 | 114 | 0.84 | 26.13
DVH090* | 7.5 | 3350 | 80 | 67 | 30 | 120.1 | 0.72 | 23.45
DVH090* | 7.5 | 3350 | 80 | 70 | 30 | 127.7 | 0.61 | 20.98
DVH090* | 7.5 | 3350 | 80 | 72 | 30 | 132.2 | 0.53 | 18.89
DVH090* | 7.5 | 3350 | 80 | 75 | 30 | 139.1 | 0.43 | 16.34
DVH090* | 7.5 | 3350 | 80 | 57 | 40 | 105.3 | 1 | 28.58
DVH090* | 7.5 | 3350 | 80 | 61 | 40 | 105.3 | 1 | 28.58
DVH090* | 7.5 | 3350 | 80 | 64 | 40 | 113.6 | 0.85 | 26.05
DVH090* | 7.5 | 3350 | 80 | 67 | 40 | 119.7 | 0.72 | 23.36
DVH090* | 7.5 | 3350 | 80 | 70 | 40 | 127.3 | 0.61 | 20.92
DVH090* | 7.5 | 3350 | 80 | 72 | 40 | 131.9 | 0.53 | 18.81
DVH090* | 7.5 | 3350 | 80 | 75 | 40 | 138.9 | 0.43 | 16.31
DVH090* | 7.5 | 3350 | 80 | 57 | 50 | 105 | 1 | 28.49
DVH090* | 7.5 | 3350 | 80 | 61 | 50 | 105 | 1 | 28.49
DVH090* | 7.5 | 3350 | 80 | 64 | 50 | 113.3 | 0.84 | 25.97
DVH090* | 7.5 | 3350 | 80 | 67 | 50 | 119.4 | 0.72 | 23.31
DVH090* | 7.5 | 3350 | 80 | 70 | 50 | 126.9 | 0.61 | 20.87
DVH090* | 7.5 | 3350 | 80 | 72 | 50 | 131.5 | 0.53 | 18.75
DVH090* | 7.5 | 3350 | 80 | 75 | 50 | 138.6 | 0.43 | 16.28
DVH090* | 7.5 | 3350 | 80 | 57 | 54 | 104.8 | 1 | 28.44
DVH090* | 7.5 | 3350 | 80 | 61 | 54 | 104.8 | 1 | 28.44
DVH090* | 7.5 | 3350 | 80 | 64 | 54 | 113.2 | 0.84 | 25.94
DVH090* | 7.5 | 3350 | 80 | 67 | 54 | 119.2 | 0.72 | 23.28
DVH090* | 7.5 | 3350 | 80 | 70 | 54 | 126.8 | 0.61 | 20.84
DVH090* | 7.5 | 3350 | 80 | 72 | 54 | 131.3 | 0.53 | 18.75
DVH090* | 7.5 | 3350 | 80 | 75 | 54 | 138.5 | 0.43 | 16.28
DVH090* | 7.5 | 3350 | 80 | 57 | 58 | 104.4 | 1 | 28.33
DVH090* | 7.5 | 3350 | 80 | 61 | 58 | 104.4 | 1 | 28.33
DVH090* | 7.5 | 3350 | 80 | 64 | 58 | 112.7 | 0.84 | 25.83
DVH090* | 7.5 | 3350 | 80 | 67 | 58 | 118.7 | 0.72 | 23.18
DVH090* | 7.5 | 3350 | 80 | 70 | 58 | 126.2 | 0.61 | 20.76
DVH090* | 7.5 | 3350 | 80 | 72 | 58 | 130.8 | 0.53 | 18.67
DVH090* | 7.5 | 3350 | 80 | 75 | 58 | 137.8 | 0.43 | 16.17
DVH090* | 7.5 | 3350 | 80 | 57 | 62 | 103.2 | 1 | 28.01
DVH090* | 7.5 | 3350 | 80 | 61 | 62 | 103.2 | 1 | 28.01
DVH090* | 7.5 | 3350 | 80 | 64 | 62 | 111.1 | 0.85 | 25.64
DVH090* | 7.5 | 3350 | 80 | 67 | 62 | 117 | 0.72 | 23.01
DVH090* | 7.5 | 3350 | 80 | 70 | 62 | 124.4 | 0.61 | 20.6
DVH090* | 7.5 | 3350 | 80 | 72 | 62 | 128.9 | 0.53 | 18.53
DVH090* | 7.5 | 3350 | 80 | 75 | 62 | 135.8 | 0.43 | 15.98
DVH090* | 7.5 | 3350 | 80 | 57 | 66 | 102 | 1 | 27.68
DVH090* | 7.5 | 3350 | 80 | 61 | 66 | 102 | 1 | 27.68
DVH090* | 7.5 | 3350 | 80 | 64 | 66 | 109.4 | 0.86 | 25.48
DVH090* | 7.5 | 3350 | 80 | 67 | 66 | 115.3 | 0.73 | 22.85
DVH090* | 7.5 | 3350 | 80 | 70 | 66 | 122.6 | 0.62 | 20.46
DVH090* | 7.5 | 3350 | 80 | 72 | 66 | 127 | 0.53 | 18.4
DVH090* | 7.5 | 3350 | 80 | 75 | 66 | 133.9 | 0.43 | 15.79
DVH090* | 7.5 | 3350 | 80 | 57 | 70 | 100.7 | 1 | 27.33
DVH090* | 7.5 | 3350 | 80 | 61 | 70 | 100.7 | 1 | 27.33
DVH090* | 7.5 | 3350 | 80 | 64 | 70 | 107.8 | 0.86 | 25.29
DVH090* | 7.5 | 3350 | 80 | 67 | 70 | 113.6 | 0.74 | 22.69
DVH090* | 7.5 | 3350 | 80 | 70 | 70 | 120.8 | 0.62 | 20.3
DVH090* | 7.5 | 3350 | 80 | 72 | 70 | 125.1 | 0.54 | 18.26
DVH090* | 7.5 | 3350 | 80 | 75 | 70 | 132 | 0.44 | 15.63
DVH090* | 7.5 | 3350 | 80 | 57 | 72 | 100.1 | 1 | 27.16
DVH090* | 7.5 | 3350 | 80 | 61 | 72 | 100.1 | 1 | 27.16
DVH090* | 7.5 | 3350 | 80 | 64 | 72 | 107 | 0.87 | 25.18
DVH090* | 7.5 | 3350 | 80 | 67 | 72 | 112.7 | 0.74 | 22.61
DVH090* | 7.5 | 3350 | 80 | 70 | 72 | 119.9 | 0.62 | 20.24
DVH090* | 7.5 | 3350 | 80 | 72 | 72 | 124.2 | 0.54 | 18.21
DVH090* | 7.5 | 3350 | 80 | 75 | 72 | 131 | 0.44 | 15.55
DVH090* | 7.5 | 3350 | 80 | 57 | 75 | 99.2 | 1 | 26.92
DVH090* | 7.5 | 3350 | 80 | 61 | 75 | 99.2 | 1 | 26.92
DVH090* | 7.5 | 3350 | 80 | 64 | 75 | 105.8 | 0.87 | 25.05
DVH090* | 7.5 | 3350 | 80 | 67 | 75 | 111.5 | 0.74 | 22.47
DVH090* | 7.5 | 3350 | 80 | 70 | 75 | 118.5 | 0.63 | 20.11
DVH090* | 7.5 | 3350 | 80 | 72 | 75 | 122.8 | 0.54 | 18.1
DVH090* | 7.5 | 3350 | 80 | 75 | 75 | 129.6 | 0.44 | 15.41
DVH090* | 7.5 | 3350 | 80 | 57 | 79 | 98 | 1 | 26.59
DVH090* | 7.5 | 3350 | 80 | 61 | 79 | 98 | 1 | 26.59
DVH090* | 7.5 | 3350 | 80 | 64 | 79 | 104.2 | 0.88 | 24.86
DVH090* | 7.5 | 3350 | 80 | 67 | 79 | 109.8 | 0.75 | 22.28
DVH090* | 7.5 | 3350 | 80 | 70 | 79 | 116.7 | 0.63 | 19.95
DVH090* | 7.5 | 3350 | 80 | 72 | 79 | 120.9 | 0.55 | 17.96
DVH090* | 7.5 | 3350 | 80 | 75 | 79 | 127.7 | 0.44 | 15.22
DVH090* | 7.5 | 3350 | 80 | 57 | 83 | 96.7 | 1 | 26.24
DVH090* | 7.5 | 3350 | 80 | 61 | 83 | 96.7 | 1 | 26.24
DVH090* | 7.5 | 3350 | 80 | 64 | 83 | 102.6 | 0.88 | 24.64
DVH090* | 7.5 | 3350 | 80 | 67 | 83 | 108 | 0.75 | 22.12
DVH090* | 7.5 | 3350 | 80 | 70 | 83 | 114.9 | 0.63 | 19.78
DVH090* | 7.5 | 3350 | 80 | 72 | 83 | 119 | 0.55 | 17.8
DVH090* | 7.5 | 3350 | 80 | 75 | 83 | 125.7 | 0.44 | 15.03
DVH090* | 7.5 | 3350 | 80 | 57 | 87 | 95.5 | 1 | 25.92
DVH090* | 7.5 | 3350 | 80 | 61 | 87 | 95.5 | 1 | 25.92
DVH090* | 7.5 | 3350 | 80 | 64 | 87 | 100.9 | 0.89 | 24.45
DVH090* | 7.5 | 3350 | 80 | 67 | 87 | 106.3 | 0.76 | 21.93
DVH090* | 7.5 | 3350 | 80 | 70 | 87 | 113.1 | 0.64 | 19.62
DVH090* | 7.5 | 3350 | 80 | 72 | 87 | 117.1 | 0.56 | 17.67
DVH090* | 7.5 | 3350 | 80 | 75 | 87 | 123.8 | 0.44 | 14.84
DVH090* | 7.5 | 3350 | 80 | 57 | 91 | 94.3 | 1 | 25.59
DVH090* | 7.5 | 3350 | 80 | 61 | 91 | 94.3 | 1 | 25.59
DVH090* | 7.5 | 3350 | 80 | 64 | 91 | 99.3 | 0.9 | 24.23
DVH090* | 7.5 | 3350 | 80 | 67 | 91 | 104.6 | 0.77 | 21.74
DVH090* | 7.5 | 3350 | 80 | 70 | 91 | 111.3 | 0.64 | 19.46
DVH090* | 7.5 | 3350 | 80 | 72 | 91 | 115.2 | 0.56 | 17.5
DVH090* | 7.5 | 3350 | 80 | 75 | 91 | 121.9 | 0.44 | 14.65
DVH090* | 7.5 | 3350 | 80 | 57 | 93 | 93.7 | 1 | 25.43
DVH090* | 7.5 | 3350 | 80 | 61 | 93 | 93.7 | 1 | 25.43
DVH090* | 7.5 | 3350 | 80 | 64 | 93 | 98.5 | 0.9 | 24.12
DVH090* | 7.5 | 3350 | 80 | 67 | 93 | 103.8 | 0.77 | 21.63
DVH090* | 7.5 | 3350 | 80 | 70 | 93 | 110.4 | 0.65 | 19.38
DVH090* | 7.5 | 3350 | 80 | 72 | 93 | 114.3 | 0.56 | 17.42
DVH090* | 7.5 | 3350 | 80 | 75 | 93 | 120.9 | 0.44 | 14.57
DVH090* | 7.5 | 3350 | 80 | 57 | 95 | 93 | 1 | 25.24
DVH090* | 7.5 | 3350 | 80 | 61 | 95 | 93 | 1 | 25.24
DVH090* | 7.5 | 3350 | 80 | 64 | 95 | 97.7 | 0.91 | 24.02
DVH090* | 7.5 | 3350 | 80 | 67 | 95 | 102.9 | 0.77 | 21.52
DVH090* | 7.5 | 3350 | 80 | 70 | 95 | 109.4 | 0.65 | 19.27
DVH090* | 7.5 | 3350 | 80 | 72 | 95 | 113.4 | 0.56 | 17.34
DVH090* | 7.5 | 3350 | 80 | 75 | 95 | 120 | 0.45 | 14.49
DVH090* | 7.5 | 3350 | 80 | 57 | 99 | 91.8 | 1 | 24.91
DVH090* | 7.5 | 3350 | 80 | 61 | 99 | 91.8 | 1 | 24.91
DVH090* | 7.5 | 3350 | 80 | 64 | 99 | 96.1 | 0.91 | 23.77
DVH090* | 7.5 | 3350 | 80 | 67 | 99 | 101.2 | 0.78 | 21.33
DVH090* | 7.5 | 3350 | 80 | 70 | 99 | 107.6 | 0.65 | 19.1
DVH090* | 7.5 | 3350 | 80 | 72 | 99 | 111.5 | 0.57 | 17.18
DVH090* | 7.5 | 3350 | 80 | 75 | 99 | 118 | 0.45 | 14.3
DVH090* | 7.5 | 3350 | 80 | 57 | 103 | 90.6 | 1 | 24.59
DVH090* | 7.5 | 3350 | 80 | 61 | 103 | 90.6 | 1 | 24.59
DVH090* | 7.5 | 3350 | 80 | 64 | 103 | 94.5 | 0.92 | 23.55
DVH090* | 7.5 | 3350 | 80 | 67 | 103 | 99.5 | 0.78 | 21.11
DVH090* | 7.5 | 3350 | 80 | 70 | 103 | 105.8 | 0.66 | 18.91
DVH090* | 7.5 | 3350 | 80 | 72 | 103 | 109.6 | 0.57 | 17.01
DVH090* | 7.5 | 3350 | 80 | 75 | 103 | 116.1 | 0.45 | 14.11
DVH090* | 7.5 | 3350 | 80 | 57 | 106 | 89.7 | 1 | 24.34
DVH090* | 7.5 | 3350 | 80 | 61 | 106 | 89.7 | 1 | 24.34
DVH090* | 7.5 | 3350 | 80 | 64 | 106 | 93.2 | 0.92 | 23.36
DVH090* | 7.5 | 3350 | 80 | 67 | 106 | 98.2 | 0.79 | 20.95
DVH090* | 7.5 | 3350 | 80 | 70 | 106 | 104.5 | 0.66 | 18.78
DVH090* | 7.5 | 3350 | 80 | 72 | 106 | 108.2 | 0.57 | 16.88
DVH090* | 7.5 | 3350 | 80 | 75 | 106 | 114.7 | 0.45 | 13.95
DVH090* | 7.5 | 3350 | 80 | 57 | 110 | 88.4 | 1 | 23.99
DVH090* | 7.5 | 3350 | 80 | 61 | 110 | 88.4 | 1 | 23.99
DVH090* | 7.5 | 3350 | 80 | 64 | 110 | 91.6 | 0.93 | 23.12
DVH090* | 7.5 | 3350 | 80 | 67 | 110 | 96.5 | 0.79 | 20.73
DVH090* | 7.5 | 3350 | 80 | 70 | 110 | 102.6 | 0.67 | 18.59
DVH090* | 7.5 | 3350 | 80 | 72 | 110 | 106.3 | 0.58 | 16.72
DVH090* | 7.5 | 3350 | 80 | 75 | 110 | 112.7 | 0.45 | 13.76
DVH090* | 7.5 | 3350 | 80 | 57 | 115 | 86.9 | 1 | 23.58
DVH090* | 7.5 | 3350 | 80 | 61 | 115 | 86.9 | 1 | 23.58
DVH090* | 7.5 | 3350 | 80 | 64 | 115 | 89.6 | 0.94 | 22.82
DVH090* | 7.5 | 3350 | 80 | 67 | 115 | 94.4 | 0.8 | 20.46
DVH090* | 7.5 | 3350 | 80 | 70 | 115 | 100.4 | 0.67 | 18.32
DVH090* | 7.5 | 3350 | 80 | 72 | 115 | 104 | 0.58 | 16.47
DVH090* | 7.5 | 3350 | 80 | 75 | 115 | 110.3 | 0.45 | 13.51
DVH090* | 7.5 | 3350 | 80 | 57 | 118 | 86 | 1 | 23.34
DVH090* | 7.5 | 3350 | 80 | 61 | 118 | 86 | 1 | 23.34
DVH090* | 7.5 | 3350 | 80 | 64 | 118 | 88.4 | 0.94 | 22.63
DVH090* | 7.5 | 3350 | 80 | 67 | 118 | 93.1 | 0.8 | 20.3
DVH090* | 7.5 | 3350 | 80 | 70 | 118 | 99 | 0.68 | 18.18
DVH090* | 7.5 | 3350 | 80 | 72 | 118 | 102.6 | 0.59 | 16.34
DVH090* | 7.5 | 3350 | 80 | 75 | 118 | 108.9 | 0.45 | 13.38
DVH090* | 7.5 | 3350 | 85 | 57 | 23 | 112 | 1 | 30.39
DVH090* | 7.5 | 3350 | 85 | 61 | 23 | 112 | 1 | 30.39
DVH090* | 7.5 | 3350 | 85 | 64 | 23 | 115.5 | 0.96 | 29.99
DVH090* | 7.5 | 3350 | 85 | 67 | 23 | 120.3 | 0.86 | 28.03
DVH090* | 7.5 | 3350 | 85 | 70 | 23 | 127.9 | 0.74 | 25.7
DVH090* | 7.5 | 3350 | 85 | 72 | 23 | 132.5 | 0.66 | 23.55
DVH090* | 7.5 | 3350 | 85 | 75 | 23 | 139.3 | 0.56 | 21.14
DVH090* | 7.5 | 3350 | 85 | 57 | 30 | 111.8 | 1 | 30.34
DVH090* | 7.5 | 3350 | 85 | 61 | 30 | 111.8 | 1 | 30.34
DVH090* | 7.5 | 3350 | 85 | 64 | 30 | 115.3 | 0.96 | 29.91
DVH090* | 7.5 | 3350 | 85 | 67 | 30 | 120.1 | 0.86 | 27.98
DVH090* | 7.5 | 3350 | 85 | 70 | 30 | 127.7 | 0.74 | 25.64
DVH090* | 7.5 | 3350 | 85 | 72 | 30 | 132.2 | 0.66 | 23.5
DVH090* | 7.5 | 3350 | 85 | 75 | 30 | 139.1 | 0.56 | 21.11
DVH090* | 7.5 | 3350 | 85 | 57 | 40 | 111.4 | 1 | 30.23
DVH090* | 7.5 | 3350 | 85 | 61 | 40 | 111.4 | 1 | 30.23
DVH090* | 7.5 | 3350 | 85 | 64 | 40 | 115 | 0.96 | 29.82
DVH090* | 7.5 | 3350 | 85 | 67 | 40 | 119.7 | 0.86 | 27.9
DVH090* | 7.5 | 3350 | 85 | 70 | 40 | 127.3 | 0.74 | 25.56
DVH090* | 7.5 | 3350 | 85 | 72 | 40 | 131.9 | 0.66 | 23.45
DVH090* | 7.5 | 3350 | 85 | 75 | 40 | 138.9 | 0.56 | 21.06
DVH090* | 7.5 | 3350 | 85 | 57 | 50 | 111.1 | 1 | 30.15
DVH090* | 7.5 | 3350 | 85 | 61 | 50 | 111.1 | 1 | 30.15
DVH090* | 7.5 | 3350 | 85 | 64 | 50 | 114.6 | 0.96 | 29.74
DVH090* | 7.5 | 3350 | 85 | 67 | 50 | 119.4 | 0.86 | 27.82
DVH090* | 7.5 | 3350 | 85 | 70 | 50 | 126.9 | 0.74 | 25.51
DVH090* | 7.5 | 3350 | 85 | 72 | 50 | 131.5 | 0.65 | 23.36
DVH090* | 7.5 | 3350 | 85 | 75 | 50 | 138.6 | 0.56 | 21.03
DVH090* | 7.5 | 3350 | 85 | 57 | 54 | 111 | 1 | 30.12
DVH090* | 7.5 | 3350 | 85 | 61 | 54 | 111 | 1 | 30.12
DVH090* | 7.5 | 3350 | 85 | 64 | 54 | 114.5 | 0.96 | 29.72
DVH090* | 7.5 | 3350 | 85 | 67 | 54 | 119.2 | 0.86 | 27.79
DVH090* | 7.5 | 3350 | 85 | 70 | 54 | 126.8 | 0.74 | 25.48
DVH090* | 7.5 | 3350 | 85 | 72 | 54 | 131.3 | 0.65 | 23.34
DVH090* | 7.5 | 3350 | 85 | 75 | 54 | 138.5 | 0.56 | 21.03
DVH090* | 7.5 | 3350 | 85 | 57 | 58 | 110.5 | 1 | 29.99
DVH090* | 7.5 | 3350 | 85 | 61 | 58 | 110.5 | 1 | 29.99
DVH090* | 7.5 | 3350 | 85 | 64 | 58 | 114 | 0.96 | 29.58
DVH090* | 7.5 | 3350 | 85 | 67 | 58 | 118.7 | 0.86 | 27.65
DVH090* | 7.5 | 3350 | 85 | 70 | 58 | 126.2 | 0.74 | 25.37
DVH090* | 7.5 | 3350 | 85 | 72 | 58 | 130.8 | 0.66 | 23.26
DVH090* | 7.5 | 3350 | 85 | 75 | 58 | 137.8 | 0.56 | 20.9
DVH090* | 7.5 | 3350 | 85 | 57 | 62 | 109.2 | 1 | 29.63
DVH090* | 7.5 | 3350 | 85 | 61 | 62 | 109.2 | 1 | 29.63
DVH090* | 7.5 | 3350 | 85 | 64 | 62 | 112.3 | 0.96 | 29.36
DVH090* | 7.5 | 3350 | 85 | 67 | 62 | 117 | 0.86 | 27.46
DVH090* | 7.5 | 3350 | 85 | 70 | 62 | 124.4 | 0.75 | 25.18
DVH090* | 7.5 | 3350 | 85 | 72 | 62 | 128.9 | 0.66 | 23.07
DVH090* | 7.5 | 3350 | 85 | 75 | 62 | 135.8 | 0.56 | 20.65
DVH090* | 7.5 | 3350 | 85 | 57 | 66 | 107.9 | 1 | 29.28
DVH090* | 7.5 | 3350 | 85 | 61 | 66 | 107.9 | 1 | 29.28
DVH090* | 7.5 | 3350 | 85 | 64 | 66 | 110.7 | 0.97 | 29.15
DVH090* | 7.5 | 3350 | 85 | 67 | 66 | 115.3 | 0.87 | 27.27
DVH090* | 7.5 | 3350 | 85 | 70 | 66 | 122.6 | 0.75 | 24.99
DVH090* | 7.5 | 3350 | 85 | 72 | 66 | 127 | 0.67 | 22.93
DVH090* | 7.5 | 3350 | 85 | 75 | 66 | 133.9 | 0.56 | 20.41
DVH090* | 7.5 | 3350 | 85 | 57 | 70 | 106.6 | 1 | 28.93
DVH090* | 7.5 | 3350 | 85 | 61 | 70 | 106.6 | 1 | 28.93
DVH090* | 7.5 | 3350 | 85 | 64 | 70 | 109.1 | 0.98 | 28.96
DVH090* | 7.5 | 3350 | 85 | 67 | 70 | 113.6 | 0.88 | 27.08
DVH090* | 7.5 | 3350 | 85 | 70 | 70 | 120.8 | 0.76 | 24.83
DVH090* | 7.5 | 3350 | 85 | 72 | 70 | 125.1 | 0.67 | 22.74
DVH090* | 7.5 | 3350 | 85 | 75 | 70 | 132 | 0.56 | 20.19
DVH090* | 7.5 | 3350 | 85 | 57 | 72 | 106 | 1 | 28.77
DVH090* | 7.5 | 3350 | 85 | 61 | 72 | 106 | 1 | 28.77
DVH090* | 7.5 | 3350 | 85 | 64 | 72 | 108.3 | 0.98 | 28.85
DVH090* | 7.5 | 3350 | 85 | 67 | 72 | 112.7 | 0.88 | 26.97
DVH090* | 7.5 | 3350 | 85 | 70 | 72 | 119.9 | 0.76 | 24.72
DVH090* | 7.5 | 3350 | 85 | 72 | 72 | 124.2 | 0.67 | 22.66
DVH090* | 7.5 | 3350 | 85 | 75 | 72 | 131 | 0.56 | 20.08
DVH090* | 7.5 | 3350 | 85 | 57 | 75 | 105 | 1 | 28.49
DVH090* | 7.5 | 3350 | 85 | 61 | 75 | 105 | 1 | 28.49
DVH090* | 7.5 | 3350 | 85 | 64 | 75 | 107 | 0.99 | 28.68
DVH090* | 7.5 | 3350 | 85 | 67 | 75 | 111.5 | 0.89 | 26.81
DVH090* | 7.5 | 3350 | 85 | 70 | 75 | 118.5 | 0.76 | 24.59
DVH090* | 7.5 | 3350 | 85 | 72 | 75 | 122.8 | 0.68 | 22.55
DVH090* | 7.5 | 3350 | 85 | 75 | 75 | 129.6 | 0.57 | 19.89
DVH090* | 7.5 | 3350 | 85 | 57 | 79 | 103.7 | 1 | 28.14
DVH090* | 7.5 | 3350 | 85 | 61 | 79 | 103.7 | 1 | 28.14
DVH090* | 7.5 | 3350 | 85 | 64 | 79 | 105.4 | 0.99 | 28.44
DVH090* | 7.5 | 3350 | 85 | 67 | 79 | 109.8 | 0.89 | 26.59
DVH090* | 7.5 | 3350 | 85 | 70 | 79 | 116.7 | 0.77 | 24.4
DVH090* | 7.5 | 3350 | 85 | 72 | 79 | 120.9 | 0.68 | 22.36
DVH090* | 7.5 | 3350 | 85 | 75 | 79 | 127.7 | 0.57 | 19.65
DVH090* | 7.5 | 3350 | 85 | 57 | 83 | 102.4 | 1 | 27.79
DVH090* | 7.5 | 3350 | 85 | 61 | 83 | 102.4 | 1 | 27.79
DVH090* | 7.5 | 3350 | 85 | 64 | 83 | 103.7 | 1 | 28.22
DVH090* | 7.5 | 3350 | 85 | 67 | 83 | 108 | 0.9 | 26.38
DVH090* | 7.5 | 3350 | 85 | 70 | 83 | 114.9 | 0.78 | 24.21
DVH090* | 7.5 | 3350 | 85 | 72 | 83 | 119 | 0.69 | 22.17
DVH090* | 7.5 | 3350 | 85 | 75 | 83 | 125.7 | 0.57 | 19.43
DVH090* | 7.5 | 3350 | 85 | 57 | 87 | 101.1 | 1 | 27.44
DVH090* | 7.5 | 3350 | 85 | 61 | 87 | 101.1 | 1 | 27.44
DVH090* | 7.5 | 3350 | 85 | 64 | 87 | 102.1 | 1.01 | 27.98
DVH090* | 7.5 | 3350 | 85 | 67 | 87 | 106.3 | 0.91 | 26.16
DVH090* | 7.5 | 3350 | 85 | 70 | 87 | 113.1 | 0.78 | 23.99
DVH090* | 7.5 | 3350 | 85 | 72 | 87 | 117.1 | 0.69 | 21.98
DVH090* | 7.5 | 3350 | 85 | 75 | 87 | 123.8 | 0.57 | 19.19
DVH090* | 7.5 | 3350 | 85 | 57 | 91 | 99.8 | 1 | 27.08
DVH090* | 7.5 | 3350 | 85 | 61 | 91 | 99.8 | 1 | 27.08
DVH090* | 7.5 | 3350 | 85 | 64 | 91 | 100.5 | 1.02 | 27.73
DVH090* | 7.5 | 3350 | 85 | 67 | 91 | 104.6 | 0.91 | 25.94
DVH090* | 7.5 | 3350 | 85 | 70 | 91 | 111.3 | 0.79 | 23.77
DVH090* | 7.5 | 3350 | 85 | 72 | 91 | 115.2 | 0.7 | 21.79
DVH090* | 7.5 | 3350 | 85 | 75 | 91 | 121.9 | 0.57 | 18.94
DVH090* | 7.5 | 3350 | 85 | 57 | 93 | 99.1 | 1 | 26.89
DVH090* | 7.5 | 3350 | 85 | 61 | 93 | 99.1 | 1 | 26.89
DVH090* | 7.5 | 3350 | 85 | 64 | 93 | 99.6 | 1.02 | 27.6
DVH090* | 7.5 | 3350 | 85 | 67 | 93 | 103.8 | 0.92 | 25.81
DVH090* | 7.5 | 3350 | 85 | 70 | 93 | 110.4 | 0.79 | 23.66
DVH090* | 7.5 | 3350 | 85 | 72 | 93 | 114.3 | 0.7 | 21.71
DVH090* | 7.5 | 3350 | 85 | 75 | 93 | 120.9 | 0.57 | 18.83
DVH090* | 7.5 | 3350 | 85 | 57 | 95 | 98.5 | 1 | 26.73
DVH090* | 7.5 | 3350 | 85 | 61 | 95 | 98.5 | 1 | 26.73
DVH090* | 7.5 | 3350 | 85 | 64 | 95 | 98.8 | 1.03 | 27.49
DVH090* | 7.5 | 3350 | 85 | 67 | 95 | 102.9 | 0.92 | 25.7
DVH090* | 7.5 | 3350 | 85 | 70 | 95 | 109.4 | 0.79 | 23.55
DVH090* | 7.5 | 3350 | 85 | 72 | 95 | 113.4 | 0.7 | 21.6
DVH090* | 7.5 | 3350 | 85 | 75 | 95 | 120 | 0.57 | 18.7
DVH090* | 7.5 | 3350 | 85 | 57 | 99 | 97.2 | 1 | 26.38
DVH090* | 7.5 | 3350 | 85 | 61 | 99 | 97.2 | 1 | 26.38
DVH090* | 7.5 | 3350 | 85 | 64 | 99 | 97.2 | 1 | 26.38
DVH090* | 7.5 | 3350 | 85 | 67 | 99 | 101.2 | 0.93 | 25.45
DVH090* | 7.5 | 3350 | 85 | 70 | 99 | 107.6 | 0.8 | 23.34
DVH090* | 7.5 | 3350 | 85 | 72 | 99 | 111.5 | 0.71 | 21.41
DVH090* | 7.5 | 3350 | 85 | 75 | 99 | 118 | 0.58 | 18.45
DVH090* | 7.5 | 3350 | 85 | 57 | 103 | 95.9 | 1 | 26.02
DVH090* | 7.5 | 3350 | 85 | 61 | 103 | 95.9 | 1 | 26.02
DVH090* | 7.5 | 3350 | 85 | 64 | 103 | 95.6 | 1 | 25.94
DVH090* | 7.5 | 3350 | 85 | 67 | 103 | 99.5 | 0.93 | 25.21
DVH090* | 7.5 | 3350 | 85 | 70 | 103 | 105.8 | 0.81 | 23.12
DVH090* | 7.5 | 3350 | 85 | 72 | 103 | 109.6 | 0.71 | 21.19
DVH090* | 7.5 | 3350 | 85 | 75 | 103 | 116.1 | 0.58 | 18.21
DVH090* | 7.5 | 3350 | 85 | 57 | 106 | 94.9 | 1 | 25.75
DVH090* | 7.5 | 3350 | 85 | 61 | 106 | 94.9 | 1 | 25.75
DVH090* | 7.5 | 3350 | 85 | 64 | 106 | 94.3 | 1 | 25.59
DVH090* | 7.5 | 3350 | 85 | 67 | 106 | 98.2 | 0.94 | 25.02
DVH090* | 7.5 | 3350 | 85 | 70 | 106 | 104.5 | 0.81 | 22.93
DVH090* | 7.5 | 3350 | 85 | 72 | 106 | 108.2 | 0.72 | 21.03
DVH090* | 7.5 | 3350 | 85 | 75 | 106 | 114.7 | 0.58 | 18.02
DVH090* | 7.5 | 3350 | 85 | 57 | 110 | 93.6 | 1 | 25.4
DVH090* | 7.5 | 3350 | 85 | 61 | 110 | 93.6 | 1 | 25.4
DVH090* | 7.5 | 3350 | 85 | 64 | 110 | 92.7 | 1 | 25.16
DVH090* | 7.5 | 3350 | 85 | 67 | 110 | 96.5 | 0.95 | 24.75
DVH090* | 7.5 | 3350 | 85 | 70 | 110 | 102.6 | 0.82 | 22.71
DVH090* | 7.5 | 3350 | 85 | 72 | 110 | 106.3 | 0.72 | 20.81
DVH090* | 7.5 | 3350 | 85 | 75 | 110 | 112.7 | 0.58 | 17.77
DVH090* | 7.5 | 3350 | 85 | 57 | 115 | 92 | 1 | 24.97
DVH090* | 7.5 | 3350 | 85 | 61 | 115 | 92 | 1 | 24.97
DVH090* | 7.5 | 3350 | 85 | 64 | 115 | 90.6 | 1 | 24.59
DVH090* | 7.5 | 3350 | 85 | 67 | 115 | 94.4 | 0.95 | 24.42
DVH090* | 7.5 | 3350 | 85 | 70 | 115 | 100.4 | 0.82 | 22.42
DVH090* | 7.5 | 3350 | 85 | 72 | 115 | 104 | 0.73 | 20.54
DVH090* | 7.5 | 3350 | 85 | 75 | 115 | 110.3 | 0.58 | 17.45
DVH090* | 7.5 | 3350 | 85 | 57 | 118 | 91 | 1 | 24.69
DVH090* | 7.5 | 3350 | 85 | 61 | 118 | 91 | 1 | 24.69
DVH090* | 7.5 | 3350 | 85 | 64 | 118 | 89.4 | 1 | 24.26
DVH090* | 7.5 | 3350 | 85 | 67 | 118 | 93.1 | 0.96 | 24.23
DVH090* | 7.5 | 3350 | 85 | 70 | 118 | 99 | 0.83 | 22.23
DVH090* | 7.5 | 3350 | 85 | 72 | 118 | 102.6 | 0.73 | 20.35
DVH090* | 7.5 | 3350 | 85 | 75 | 118 | 108.9 | 0.58 | 17.26
DVH102* | 8.5 | 2700 | 70 | 57 | 23 | 99.4 | 0.85 | 28.59
DVH102* | 8.5 | 2700 | 70 | 61 | 23 | 110.5 | 0.65 | 24.01
DVH102* | 8.5 | 2700 | 70 | 64 | 23 | 116.5 | 0.52 | 20.54
DVH102* | 8.5 | 2700 | 70 | 67 | 23 | 122.7 | 0.41 | 17.07
DVH102* | 8.5 | 2700 | 70 | 57 | 30 | 99.3 | 0.85 | 28.55
DVH102* | 8.5 | 2700 | 70 | 61 | 30 | 110.3 | 0.65 | 23.97
DVH102* | 8.5 | 2700 | 70 | 64 | 30 | 116.3 | 0.52 | 20.51
DVH102* | 8.5 | 2700 | 70 | 67 | 30 | 122.5 | 0.41 | 17.04
DVH102* | 8.5 | 2700 | 70 | 57 | 40 | 99.2 | 0.85 | 28.52
DVH102* | 8.5 | 2700 | 70 | 61 | 40 | 110.1 | 0.64 | 23.91
DVH102* | 8.5 | 2700 | 70 | 64 | 40 | 116 | 0.52 | 20.47
DVH102* | 8.5 | 2700 | 70 | 67 | 40 | 122.2 | 0.41 | 17
DVH102* | 8.5 | 2700 | 70 | 57 | 50 | 99 | 0.85 | 28.48
DVH102* | 8.5 | 2700 | 70 | 61 | 50 | 109.8 | 0.65 | 23.87
DVH102* | 8.5 | 2700 | 70 | 64 | 50 | 115.8 | 0.52 | 20.4
DVH102* | 8.5 | 2700 | 70 | 67 | 50 | 121.9 | 0.41 | 16.97
DVH102* | 8.5 | 2700 | 70 | 57 | 54 | 98.9 | 0.85 | 28.45
DVH102* | 8.5 | 2700 | 70 | 61 | 54 | 109.7 | 0.65 | 23.84
DVH102* | 8.5 | 2700 | 70 | 64 | 54 | 115.7 | 0.52 | 20.4
DVH102* | 8.5 | 2700 | 70 | 67 | 54 | 121.8 | 0.41 | 16.94
DVH102* | 8.5 | 2700 | 70 | 57 | 58 | 98.9 | 0.85 | 28.45
DVH102* | 8.5 | 2700 | 70 | 61 | 58 | 109.6 | 0.65 | 23.84
DVH102* | 8.5 | 2700 | 70 | 64 | 58 | 115.6 | 0.52 | 20.37
DVH102* | 8.5 | 2700 | 70 | 67 | 58 | 121.7 | 0.41 | 16.94
DVH102* | 8.5 | 2700 | 70 | 57 | 62 | 98.3 | 0.85 | 28.28
DVH102* | 8.5 | 2700 | 70 | 61 | 62 | 108.9 | 0.65 | 23.74
DVH102* | 8.5 | 2700 | 70 | 64 | 62 | 114.8 | 0.53 | 20.3
DVH102* | 8.5 | 2700 | 70 | 67 | 62 | 121 | 0.41 | 16.87
DVH102* | 8.5 | 2700 | 70 | 57 | 66 | 97.2 | 0.86 | 28.05
DVH102* | 8.5 | 2700 | 70 | 61 | 66 | 107.4 | 0.65 | 23.57
DVH102* | 8.5 | 2700 | 70 | 64 | 66 | 113.2 | 0.53 | 20.17
DVH102* | 8.5 | 2700 | 70 | 67 | 66 | 119.3 | 0.42 | 16.77
DVH102* | 8.5 | 2700 | 70 | 57 | 70 | 96 | 0.86 | 27.81
DVH102* | 8.5 | 2700 | 70 | 61 | 70 | 105.9 | 0.66 | 23.4
DVH102* | 8.5 | 2700 | 70 | 64 | 70 | 111.6 | 0.53 | 20
DVH102* | 8.5 | 2700 | 70 | 67 | 70 | 117.5 | 0.42 | 16.63
DVH102* | 8.5 | 2700 | 70 | 57 | 72 | 95.5 | 0.86 | 27.68
DVH102* | 8.5 | 2700 | 70 | 61 | 72 | 105.1 | 0.66 | 23.3
DVH102* | 8.5 | 2700 | 70 | 64 | 72 | 110.8 | 0.53 | 19.93
DVH102* | 8.5 | 2700 | 70 | 67 | 72 | 116.7 | 0.42 | 16.57
DVH102* | 8.5 | 2700 | 70 | 57 | 75 | 94.6 | 0.86 | 27.51
DVH102* | 8.5 | 2700 | 70 | 61 | 75 | 104 | 0.66 | 23.16
DVH102* | 8.5 | 2700 | 70 | 64 | 75 | 109.6 | 0.54 | 19.83
DVH102* | 8.5 | 2700 | 70 | 67 | 75 | 115.4 | 0.42 | 16.46
DVH102* | 8.5 | 2700 | 70 | 57 | 79 | 93.5 | 0.87 | 27.24
DVH102* | 8.5 | 2700 | 70 | 61 | 79 | 102.4 | 0.67 | 23
DVH102* | 8.5 | 2700 | 70 | 64 | 79 | 108 | 0.54 | 19.66
DVH102* | 8.5 | 2700 | 70 | 67 | 79 | 113.7 | 0.43 | 16.36
DVH102* | 8.5 | 2700 | 70 | 57 | 83 | 92.4 | 0.87 | 27
DVH102* | 8.5 | 2700 | 70 | 61 | 83 | 100.9 | 0.67 | 22.83
DVH102* | 8.5 | 2700 | 70 | 64 | 83 | 106.3 | 0.55 | 19.53
DVH102* | 8.5 | 2700 | 70 | 67 | 83 | 112 | 0.43 | 16.23
DVH102* | 8.5 | 2700 | 70 | 57 | 87 | 91.2 | 0.87 | 26.73
DVH102* | 8.5 | 2700 | 70 | 61 | 87 | 99.3 | 0.68 | 22.63
DVH102* | 8.5 | 2700 | 70 | 64 | 87 | 104.7 | 0.55 | 19.36
DVH102* | 8.5 | 2700 | 70 | 67 | 87 | 110.3 | 0.43 | 16.09
DVH102* | 8.5 | 2700 | 70 | 57 | 91 | 90.1 | 0.87 | 26.5
DVH102* | 8.5 | 2700 | 70 | 61 | 91 | 97.8 | 0.68 | 22.42
DVH102* | 8.5 | 2700 | 70 | 64 | 91 | 103.1 | 0.55 | 19.19
DVH102* | 8.5 | 2700 | 70 | 67 | 91 | 108.6 | 0.44 | 15.96
DVH102* | 8.5 | 2700 | 70 | 57 | 93 | 89.6 | 0.87 | 26.36
DVH102* | 8.5 | 2700 | 70 | 61 | 93 | 97 | 0.68 | 22.32
DVH102* | 8.5 | 2700 | 70 | 64 | 93 | 102.3 | 0.55 | 19.09
DVH102* | 8.5 | 2700 | 70 | 67 | 93 | 107.7 | 0.44 | 15.86
DVH102* | 8.5 | 2700 | 70 | 57 | 95 | 89 | 0.88 | 26.23
DVH102* | 8.5 | 2700 | 70 | 61 | 95 | 96.3 | 0.68 | 22.19
DVH102* | 8.5 | 2700 | 70 | 64 | 95 | 101.5 | 0.56 | 19.02
DVH102* | 8.5 | 2700 | 70 | 67 | 95 | 106.9 | 0.44 | 15.79
DVH102* | 8.5 | 2700 | 70 | 57 | 99 | 87.9 | 0.88 | 25.96
DVH102* | 8.5 | 2700 | 70 | 61 | 99 | 94.7 | 0.69 | 21.89
DVH102* | 8.5 | 2700 | 70 | 64 | 99 | 99.9 | 0.56 | 18.86
DVH102* | 8.5 | 2700 | 70 | 67 | 99 | 105.2 | 0.44 | 15.66
DVH102* | 8.5 | 2700 | 70 | 57 | 103 | 86.7 | 0.88 | 25.72
DVH102* | 8.5 | 2700 | 70 | 61 | 103 | 93.2 | 0.69 | 21.58
DVH102* | 8.5 | 2700 | 70 | 64 | 103 | 98.3 | 0.56 | 18.65
DVH102* | 8.5 | 2700 | 70 | 67 | 103 | 103.5 | 0.45 | 15.52
DVH102* | 8.5 | 2700 | 70 | 57 | 106 | 85.9 | 0.88 | 25.52
DVH102* | 8.5 | 2700 | 70 | 61 | 106 | 92.1 | 0.69 | 21.38
DVH102* | 8.5 | 2700 | 70 | 64 | 106 | 97 | 0.57 | 18.52
DVH102* | 8.5 | 2700 | 70 | 67 | 106 | 102.2 | 0.45 | 15.39
DVH102* | 8.5 | 2700 | 70 | 57 | 110 | 84.8 | 0.88 | 25.25
DVH102* | 8.5 | 2700 | 70 | 61 | 110 | 90.5 | 0.69 | 21.08
DVH102* | 8.5 | 2700 | 70 | 64 | 110 | 95.4 | 0.57 | 18.35
DVH102* | 8.5 | 2700 | 70 | 67 | 110 | 100.5 | 0.45 | 15.25
DVH102* | 8.5 | 2700 | 70 | 57 | 115 | 83.3 | 0.89 | 24.92
DVH102* | 8.5 | 2700 | 70 | 61 | 115 | 88.6 | 0.69 | 20.71
DVH102* | 8.5 | 2700 | 70 | 64 | 115 | 93.4 | 0.58 | 18.11
DVH102* | 8.5 | 2700 | 70 | 67 | 115 | 98.4 | 0.45 | 15.05
DVH102* | 8.5 | 2700 | 75 | 57 | 23 | 101.9 | 1 | 34.31
DVH102* | 8.5 | 2700 | 75 | 61 | 23 | 110.5 | 0.79 | 29.49
DVH102* | 8.5 | 2700 | 75 | 64 | 23 | 116.5 | 0.67 | 26.09
DVH102* | 8.5 | 2700 | 75 | 67 | 23 | 122.7 | 0.55 | 22.73
DVH102* | 8.5 | 2700 | 75 | 70 | 23 | 129.9 | 0.45 | 19.56
DVH102* | 8.5 | 2700 | 75 | 72 | 23 | 134.4 | 0.38 | 17.04
DVH102* | 8.5 | 2700 | 75 | 57 | 30 | 101.7 | 1 | 34.24
DVH102* | 8.5 | 2700 | 75 | 61 | 30 | 110.3 | 0.79 | 29.46
DVH102* | 8.5 | 2700 | 75 | 64 | 30 | 116.3 | 0.67 | 26.06
DVH102* | 8.5 | 2700 | 75 | 67 | 30 | 122.5 | 0.55 | 22.69
DVH102* | 8.5 | 2700 | 75 | 70 | 30 | 129.7 | 0.45 | 19.56
DVH102* | 8.5 | 2700 | 75 | 72 | 30 | 134.2 | 0.38 | 17
DVH102* | 8.5 | 2700 | 75 | 57 | 40 | 101.6 | 1 | 34.21
DVH102* | 8.5 | 2700 | 75 | 61 | 40 | 110.1 | 0.79 | 29.39
DVH102* | 8.5 | 2700 | 75 | 64 | 40 | 116 | 0.67 | 25.99
DVH102* | 8.5 | 2700 | 75 | 67 | 40 | 122.2 | 0.55 | 22.63
DVH102* | 8.5 | 2700 | 75 | 70 | 40 | 129.4 | 0.45 | 19.49
DVH102* | 8.5 | 2700 | 75 | 72 | 40 | 133.9 | 0.38 | 16.97
DVH102* | 8.5 | 2700 | 75 | 57 | 50 | 101.4 | 1 | 34.14
DVH102* | 8.5 | 2700 | 75 | 61 | 50 | 109.8 | 0.79 | 29.33
DVH102* | 8.5 | 2700 | 75 | 64 | 50 | 115.8 | 0.66 | 25.93
DVH102* | 8.5 | 2700 | 75 | 67 | 50 | 121.9 | 0.55 | 22.59
DVH102* | 8.5 | 2700 | 75 | 70 | 50 | 129.2 | 0.45 | 19.46
DVH102* | 8.5 | 2700 | 75 | 72 | 50 | 133.6 | 0.38 | 16.94
DVH102* | 8.5 | 2700 | 75 | 57 | 54 | 101.3 | 1 | 34.11
DVH102* | 8.5 | 2700 | 75 | 61 | 54 | 109.7 | 0.79 | 29.29
DVH102* | 8.5 | 2700 | 75 | 64 | 54 | 115.7 | 0.67 | 25.93
DVH102* | 8.5 | 2700 | 75 | 67 | 54 | 121.8 | 0.55 | 22.56
DVH102* | 8.5 | 2700 | 75 | 70 | 54 | 129 | 0.45 | 19.46
DVH102* | 8.5 | 2700 | 75 | 72 | 54 | 133.5 | 0.38 | 16.9
DVH102* | 8.5 | 2700 | 75 | 57 | 58 | 101.3 | 1 | 34.11
DVH102* | 8.5 | 2700 | 75 | 61 | 58 | 109.6 | 0.79 | 29.29
DVH102* | 8.5 | 2700 | 75 | 64 | 58 | 115.6 | 0.67 | 25.89
DVH102* | 8.5 | 2700 | 75 | 67 | 58 | 121.7 | 0.55 | 22.53
DVH102* | 8.5 | 2700 | 75 | 70 | 58 | 128.9 | 0.45 | 19.43
DVH102* | 8.5 | 2700 | 75 | 72 | 58 | 133.4 | 0.38 | 16.9
DVH102* | 8.5 | 2700 | 75 | 57 | 62 | 100.7 | 1 | 33.91
DVH102* | 8.5 | 2700 | 75 | 61 | 62 | 108.9 | 0.8 | 29.16
DVH102* | 8.5 | 2700 | 75 | 64 | 62 | 114.8 | 0.67 | 25.79
DVH102* | 8.5 | 2700 | 75 | 67 | 62 | 121 | 0.55 | 22.46
DVH102* | 8.5 | 2700 | 75 | 70 | 62 | 128.1 | 0.45 | 19.36
DVH102* | 8.5 | 2700 | 75 | 72 | 62 | 132.5 | 0.38 | 16.84
DVH102* | 8.5 | 2700 | 75 | 57 | 66 | 99.5 | 1 | 33.5
DVH102* | 8.5 | 2700 | 75 | 61 | 66 | 107.4 | 0.8 | 28.96
DVH102* | 8.5 | 2700 | 75 | 64 | 66 | 113.2 | 0.67 | 25.62
DVH102* | 8.5 | 2700 | 75 | 67 | 66 | 119.3 | 0.55 | 22.29
DVH102* | 8.5 | 2700 | 75 | 70 | 66 | 126.3 | 0.45 | 19.23
DVH102* | 8.5 | 2700 | 75 | 72 | 66 | 130.7 | 0.38 | 16.73
DVH102* | 8.5 | 2700 | 75 | 57 | 70 | 98.4 | 1 | 33.13
DVH102* | 8.5 | 2700 | 75 | 61 | 70 | 105.9 | 0.81 | 28.75
DVH102* | 8.5 | 2700 | 75 | 64 | 70 | 111.6 | 0.68 | 25.42
DVH102* | 8.5 | 2700 | 75 | 67 | 70 | 117.5 | 0.56 | 22.12
DVH102* | 8.5 | 2700 | 75 | 70 | 70 | 124.5 | 0.46 | 19.09
DVH102* | 8.5 | 2700 | 75 | 72 | 70 | 128.8 | 0.38 | 16.6
DVH102* | 8.5 | 2700 | 75 | 57 | 72 | 97.8 | 1 | 32.93
DVH102* | 8.5 | 2700 | 75 | 61 | 72 | 105.1 | 0.81 | 28.65
DVH102* | 8.5 | 2700 | 75 | 64 | 72 | 110.8 | 0.68 | 25.32
DVH102* | 8.5 | 2700 | 75 | 67 | 72 | 116.7 | 0.56 | 22.05
DVH102* | 8.5 | 2700 | 75 | 70 | 72 | 123.6 | 0.46 | 19.02
DVH102* | 8.5 | 2700 | 75 | 72 | 72 | 127.9 | 0.38 | 16.53
DVH102* | 8.5 | 2700 | 75 | 57 | 75 | 96.9 | 1 | 32.63
DVH102* | 8.5 | 2700 | 75 | 61 | 75 | 104 | 0.81 | 28.48
DVH102* | 8.5 | 2700 | 75 | 64 | 75 | 109.6 | 0.68 | 25.19
DVH102* | 8.5 | 2700 | 75 | 67 | 75 | 115.4 | 0.56 | 21.92
DVH102* | 8.5 | 2700 | 75 | 70 | 75 | 122.3 | 0.46 | 18.89
DVH102* | 8.5 | 2700 | 75 | 72 | 75 | 126.5 | 0.39 | 16.43
DVH102* | 8.5 | 2700 | 75 | 57 | 79 | 95.8 | 1 | 32.26
DVH102* | 8.5 | 2700 | 75 | 61 | 79 | 102.4 | 0.82 | 28.28
DVH102* | 8.5 | 2700 | 75 | 64 | 79 | 108 | 0.69 | 24.98
DVH102* | 8.5 | 2700 | 75 | 67 | 79 | 113.7 | 0.57 | 21.75
DVH102* | 8.5 | 2700 | 75 | 70 | 79 | 120.4 | 0.46 | 18.75
DVH102* | 8.5 | 2700 | 75 | 72 | 79 | 124.6 | 0.39 | 16.33
DVH102* | 8.5 | 2700 | 75 | 57 | 83 | 94.6 | 1 | 31.85
DVH102* | 8.5 | 2700 | 75 | 61 | 83 | 100.9 | 0.83 | 28.05
DVH102* | 8.5 | 2700 | 75 | 64 | 83 | 106.3 | 0.69 | 24.78
DVH102* | 8.5 | 2700 | 75 | 67 | 83 | 112 | 0.57 | 21.58
DVH102* | 8.5 | 2700 | 75 | 70 | 83 | 118.6 | 0.47 | 18.62
DVH102* | 8.5 | 2700 | 75 | 72 | 83 | 122.7 | 0.39 | 16.2
DVH102* | 8.5 | 2700 | 75 | 57 | 87 | 93.5 | 1 | 31.48
DVH102* | 8.5 | 2700 | 75 | 61 | 87 | 99.3 | 0.83 | 27.81
DVH102* | 8.5 | 2700 | 75 | 64 | 87 | 104.7 | 0.7 | 24.58
DVH102* | 8.5 | 2700 | 75 | 67 | 87 | 110.3 | 0.58 | 21.41
DVH102* | 8.5 | 2700 | 75 | 70 | 87 | 116.8 | 0.47 | 18.45
DVH102* | 8.5 | 2700 | 75 | 72 | 87 | 120.9 | 0.39 | 16.06
DVH102* | 8.5 | 2700 | 75 | 57 | 91 | 92.3 | 1 | 31.08
DVH102* | 8.5 | 2700 | 75 | 61 | 91 | 97.8 | 0.84 | 27.58
DVH102* | 8.5 | 2700 | 75 | 64 | 91 | 103.1 | 0.7 | 24.38
DVH102* | 8.5 | 2700 | 75 | 67 | 91 | 108.6 | 0.58 | 21.21
DVH102* | 8.5 | 2700 | 75 | 70 | 91 | 115 | 0.47 | 18.28
DVH102* | 8.5 | 2700 | 75 | 72 | 91 | 119 | 0.4 | 15.93
DVH102* | 8.5 | 2700 | 75 | 57 | 93 | 91.7 | 1 | 30.88
DVH102* | 8.5 | 2700 | 75 | 61 | 93 | 97 | 0.84 | 27.44
DVH102* | 8.5 | 2700 | 75 | 64 | 93 | 102.3 | 0.7 | 24.28
DVH102* | 8.5 | 2700 | 75 | 67 | 93 | 107.7 | 0.58 | 21.11
DVH102* | 8.5 | 2700 | 75 | 70 | 93 | 114.1 | 0.47 | 18.22
DVH102* | 8.5 | 2700 | 75 | 72 | 93 | 118.1 | 0.4 | 15.86
DVH102* | 8.5 | 2700 | 75 | 57 | 95 | 91.2 | 1 | 30.71
DVH102* | 8.5 | 2700 | 75 | 61 | 95 | 96.3 | 0.84 | 27.27
DVH102* | 8.5 | 2700 | 75 | 64 | 95 | 101.5 | 0.71 | 24.14
DVH102* | 8.5 | 2700 | 75 | 67 | 95 | 106.9 | 0.58 | 21.04
DVH102* | 8.5 | 2700 | 75 | 70 | 95 | 113.2 | 0.48 | 18.11
DVH102* | 8.5 | 2700 | 75 | 72 | 95 | 117.1 | 0.4 | 15.76
DVH102* | 8.5 | 2700 | 75 | 57 | 99 | 90 | 1 | 30.3
DVH102* | 8.5 | 2700 | 75 | 61 | 99 | 94.7 | 0.84 | 26.9
DVH102* | 8.5 | 2700 | 75 | 64 | 99 | 99.9 | 0.71 | 23.94
DVH102* | 8.5 | 2700 | 75 | 67 | 99 | 105.2 | 0.59 | 20.84
DVH102* | 8.5 | 2700 | 75 | 70 | 99 | 111.4 | 0.48 | 17.95
DVH102* | 8.5 | 2700 | 75 | 72 | 99 | 115.3 | 0.4 | 15.62
DVH102* | 8.5 | 2700 | 75 | 57 | 103 | 88.8 | 1 | 29.9
DVH102* | 8.5 | 2700 | 75 | 61 | 103 | 93.2 | 0.85 | 26.53
DVH102* | 8.5 | 2700 | 75 | 64 | 103 | 98.3 | 0.72 | 23.7
DVH102* | 8.5 | 2700 | 75 | 67 | 103 | 103.5 | 0.59 | 20.64
DVH102* | 8.5 | 2700 | 75 | 70 | 103 | 109.6 | 0.48 | 17.78
DVH102* | 8.5 | 2700 | 75 | 72 | 103 | 113.4 | 0.41 | 15.49
DVH102* | 8.5 | 2700 | 75 | 57 | 106 | 88 | 1 | 29.63
DVH102* | 8.5 | 2700 | 75 | 61 | 106 | 92.1 | 0.85 | 26.26
DVH102* | 8.5 | 2700 | 75 | 64 | 106 | 97 | 0.72 | 23.54
DVH102* | 8.5 | 2700 | 75 | 67 | 106 | 102.2 | 0.6 | 20.51
DVH102* | 8.5 | 2700 | 75 | 70 | 106 | 108.3 | 0.48 | 17.68
DVH102* | 8.5 | 2700 | 75 | 72 | 106 | 112 | 0.41 | 15.35
DVH102* | 8.5 | 2700 | 75 | 57 | 110 | 86.8 | 1 | 29.23
DVH102* | 8.5 | 2700 | 75 | 61 | 110 | 90.5 | 0.85 | 25.89
DVH102* | 8.5 | 2700 | 75 | 64 | 110 | 95.4 | 0.73 | 23.3
DVH102* | 8.5 | 2700 | 75 | 67 | 110 | 100.5 | 0.6 | 20.27
DVH102* | 8.5 | 2700 | 75 | 70 | 110 | 106.4 | 0.49 | 17.47
DVH102* | 8.5 | 2700 | 75 | 72 | 110 | 110.1 | 0.41 | 15.22
DVH102* | 8.5 | 2700 | 75 | 57 | 115 | 85.4 | 1 | 28.75
DVH102* | 8.5 | 2700 | 75 | 61 | 115 | 88.6 | 0.85 | 25.45
DVH102* | 8.5 | 2700 | 75 | 64 | 115 | 93.4 | 0.73 | 23
DVH102* | 8.5 | 2700 | 75 | 67 | 115 | 98.4 | 0.6 | 20.03
DVH102* | 8.5 | 2700 | 75 | 70 | 115 | 104.2 | 0.49 | 17.24
DVH102* | 8.5 | 2700 | 75 | 72 | 115 | 107.8 | 0.41 | 15.02
DVH102* | 8.5 | 2700 | 80 | 57 | 23 | 107.8 | 1 | 36.3
DVH102* | 8.5 | 2700 | 80 | 61 | 23 | 110.5 | 0.92 | 34.11
DVH102* | 8.5 | 2700 | 80 | 64 | 23 | 116.5 | 0.8 | 31.52
DVH102* | 8.5 | 2700 | 80 | 67 | 23 | 122.7 | 0.68 | 28.18
DVH102* | 8.5 | 2700 | 80 | 70 | 23 | 129.9 | 0.58 | 25.22
DVH102* | 8.5 | 2700 | 80 | 72 | 23 | 134.4 | 0.5 | 22.69
DVH102* | 8.5 | 2700 | 80 | 75 | 23 | 142 | 0.41 | 19.7
DVH102* | 8.5 | 2700 | 80 | 57 | 30 | 107.7 | 1 | 36.26
DVH102* | 8.5 | 2700 | 80 | 61 | 30 | 110.3 | 0.92 | 34.07
DVH102* | 8.5 | 2700 | 80 | 64 | 30 | 116.3 | 0.8 | 31.45
DVH102* | 8.5 | 2700 | 80 | 67 | 30 | 122.5 | 0.68 | 28.15
DVH102* | 8.5 | 2700 | 80 | 70 | 30 | 129.7 | 0.58 | 25.19
DVH102* | 8.5 | 2700 | 80 | 72 | 30 | 134.2 | 0.5 | 22.66
DVH102* | 8.5 | 2700 | 80 | 75 | 30 | 141.8 | 0.41 | 19.7
DVH102* | 8.5 | 2700 | 80 | 57 | 40 | 107.5 | 1 | 36.2
DVH102* | 8.5 | 2700 | 80 | 61 | 40 | 110.1 | 0.92 | 33.97
DVH102* | 8.5 | 2700 | 80 | 64 | 40 | 116 | 0.8 | 31.38
DVH102* | 8.5 | 2700 | 80 | 67 | 40 | 122.2 | 0.68 | 28.08
DVH102* | 8.5 | 2700 | 80 | 70 | 40 | 129.4 | 0.58 | 25.15
DVH102* | 8.5 | 2700 | 80 | 72 | 40 | 133.9 | 0.5 | 22.59
DVH102* | 8.5 | 2700 | 80 | 75 | 40 | 141.6 | 0.41 | 19.66
DVH102* | 8.5 | 2700 | 80 | 57 | 50 | 107.4 | 1 | 36.16
DVH102* | 8.5 | 2700 | 80 | 61 | 50 | 109.8 | 0.92 | 33.91
DVH102* | 8.5 | 2700 | 80 | 64 | 50 | 115.8 | 0.8 | 31.31
DVH102* | 8.5 | 2700 | 80 | 67 | 50 | 121.9 | 0.68 | 28.01
DVH102* | 8.5 | 2700 | 80 | 70 | 50 | 129.2 | 0.58 | 25.08
DVH102* | 8.5 | 2700 | 80 | 72 | 50 | 133.6 | 0.5 | 22.56
DVH102* | 8.5 | 2700 | 80 | 75 | 50 | 141.3 | 0.41 | 19.63
DVH102* | 8.5 | 2700 | 80 | 57 | 54 | 107.3 | 1 | 36.13
DVH102* | 8.5 | 2700 | 80 | 61 | 54 | 109.7 | 0.92 | 33.87
DVH102* | 8.5 | 2700 | 80 | 64 | 54 | 115.7 | 0.8 | 31.31
DVH102* | 8.5 | 2700 | 80 | 67 | 54 | 121.8 | 0.68 | 27.98
DVH102* | 8.5 | 2700 | 80 | 70 | 54 | 129 | 0.58 | 25.05
DVH102* | 8.5 | 2700 | 80 | 72 | 54 | 133.5 | 0.5 | 22.53
DVH102* | 8.5 | 2700 | 80 | 75 | 54 | 141.2 | 0.41 | 19.6
DVH102* | 8.5 | 2700 | 80 | 57 | 58 | 107.2 | 1 | 36.09
DVH102* | 8.5 | 2700 | 80 | 61 | 58 | 109.6 | 0.92 | 33.84
DVH102* | 8.5 | 2700 | 80 | 64 | 58 | 115.6 | 0.8 | 31.28
DVH102* | 8.5 | 2700 | 80 | 67 | 58 | 121.7 | 0.68 | 27.98
DVH102* | 8.5 | 2700 | 80 | 70 | 58 | 128.9 | 0.58 | 25.05
DVH102* | 8.5 | 2700 | 80 | 72 | 58 | 133.4 | 0.5 | 22.49
DVH102* | 8.5 | 2700 | 80 | 75 | 58 | 141.1 | 0.41 | 19.6
DVH102* | 8.5 | 2700 | 80 | 57 | 62 | 106.6 | 1 | 35.89
DVH102* | 8.5 | 2700 | 80 | 61 | 62 | 108.9 | 0.92 | 33.74
DVH102* | 8.5 | 2700 | 80 | 64 | 62 | 114.8 | 0.81 | 31.14
DVH102* | 8.5 | 2700 | 80 | 67 | 62 | 121 | 0.68 | 27.85
DVH102* | 8.5 | 2700 | 80 | 70 | 62 | 128.1 | 0.58 | 24.95
DVH102* | 8.5 | 2700 | 80 | 72 | 62 | 132.5 | 0.5 | 22.42
DVH102* | 8.5 | 2700 | 80 | 75 | 62 | 139.6 | 0.41 | 19.39
DVH102* | 8.5 | 2700 | 80 | 57 | 66 | 105.4 | 1 | 35.49
DVH102* | 8.5 | 2700 | 80 | 61 | 66 | 107.4 | 0.93 | 33.5
DVH102* | 8.5 | 2700 | 80 | 64 | 66 | 113.2 | 0.81 | 30.94
DVH102* | 8.5 | 2700 | 80 | 67 | 66 | 119.3 | 0.69 | 27.68
DVH102* | 8.5 | 2700 | 80 | 70 | 66 | 126.3 | 0.58 | 24.78
DVH102* | 8.5 | 2700 | 80 | 72 | 66 | 130.7 | 0.51 | 22.26
DVH102* | 8.5 | 2700 | 80 | 75 | 66 | 137.7 | 0.41 | 19.16
DVH102* | 8.5 | 2700 | 80 | 57 | 70 | 104.2 | 1 | 35.08
DVH102* | 8.5 | 2700 | 80 | 61 | 70 | 105.9 | 0.93 | 33.23
DVH102* | 8.5 | 2700 | 80 | 64 | 70 | 111.6 | 0.82 | 30.71
DVH102* | 8.5 | 2700 | 80 | 67 | 70 | 117.5 | 0.69 | 27.47
DVH102* | 8.5 | 2700 | 80 | 70 | 70 | 124.5 | 0.59 | 24.58
DVH102* | 8.5 | 2700 | 80 | 72 | 70 | 128.8 | 0.51 | 22.09
DVH102* | 8.5 | 2700 | 80 | 75 | 70 | 135.7 | 0.41 | 18.96
DVH102* | 8.5 | 2700 | 80 | 57 | 72 | 103.6 | 1 | 34.88
DVH102* | 8.5 | 2700 | 80 | 61 | 72 | 105.1 | 0.94 | 33.13
DVH102* | 8.5 | 2700 | 80 | 64 | 72 | 110.8 | 0.82 | 30.61
DVH102* | 8.5 | 2700 | 80 | 67 | 72 | 116.7 | 0.7 | 27.37
DVH102* | 8.5 | 2700 | 80 | 70 | 72 | 123.6 | 0.59 | 24.51
DVH102* | 8.5 | 2700 | 80 | 72 | 72 | 127.9 | 0.51 | 22.02
DVH102* | 8.5 | 2700 | 80 | 75 | 72 | 134.8 | 0.42 | 18.86
DVH102* | 8.5 | 2700 | 80 | 57 | 75 | 102.6 | 1 | 34.55
DVH102* | 8.5 | 2700 | 80 | 61 | 75 | 104 | 0.94 | 32.93
DVH102* | 8.5 | 2700 | 80 | 64 | 75 | 109.6 | 0.82 | 30.44
DVH102* | 8.5 | 2700 | 80 | 67 | 75 | 115.4 | 0.7 | 27.21
DVH102* | 8.5 | 2700 | 80 | 70 | 75 | 122.3 | 0.59 | 24.38
DVH102* | 8.5 | 2700 | 80 | 72 | 75 | 126.5 | 0.51 | 21.89
DVH102* | 8.5 | 2700 | 80 | 75 | 75 | 133.3 | 0.42 | 18.69
DVH102* | 8.5 | 2700 | 80 | 57 | 79 | 101.4 | 1 | 34.14
DVH102* | 8.5 | 2700 | 80 | 61 | 79 | 102.4 | 0.95 | 32.69
DVH102* | 8.5 | 2700 | 80 | 64 | 79 | 108 | 0.83 | 30.2
DVH102* | 8.5 | 2700 | 80 | 67 | 79 | 113.7 | 0.71 | 27
DVH102* | 8.5 | 2700 | 80 | 70 | 79 | 120.4 | 0.6 | 24.18
DVH102* | 8.5 | 2700 | 80 | 72 | 79 | 124.6 | 0.52 | 21.72
DVH102* | 8.5 | 2700 | 80 | 75 | 79 | 131.4 | 0.42 | 18.48
DVH102* | 8.5 | 2700 | 80 | 57 | 83 | 100.2 | 1 | 33.74
DVH102* | 8.5 | 2700 | 80 | 61 | 83 | 100.9 | 0.95 | 32.42
DVH102* | 8.5 | 2700 | 80 | 64 | 83 | 106.3 | 0.84 | 29.93
DVH102* | 8.5 | 2700 | 80 | 67 | 83 | 112 | 0.71 | 26.77
DVH102* | 8.5 | 2700 | 80 | 70 | 83 | 118.6 | 0.6 | 23.97
DVH102* | 8.5 | 2700 | 80 | 72 | 83 | 122.7 | 0.52 | 21.55
DVH102* | 8.5 | 2700 | 80 | 75 | 83 | 129.5 | 0.42 | 18.25
DVH102* | 8.5 | 2700 | 80 | 57 | 87 | 99 | 1 | 33.33
DVH102* | 8.5 | 2700 | 80 | 61 | 87 | 99.3 | 0.96 | 32.15
DVH102* | 8.5 | 2700 | 80 | 64 | 87 | 104.7 | 0.84 | 29.7
DVH102* | 8.5 | 2700 | 80 | 67 | 87 | 110.3 | 0.72 | 26.57
DVH102* | 8.5 | 2700 | 80 | 70 | 87 | 116.8 | 0.6 | 23.77
DVH102* | 8.5 | 2700 | 80 | 72 | 87 | 120.9 | 0.53 | 21.38
DVH102* | 8.5 | 2700 | 80 | 75 | 87 | 127.5 | 0.42 | 18.05
DVH102* | 8.5 | 2700 | 80 | 57 | 91 | 97.7 | 1 | 32.9
DVH102* | 8.5 | 2700 | 80 | 61 | 91 | 97.8 | 0.97 | 31.89
DVH102* | 8.5 | 2700 | 80 | 64 | 91 | 103.1 | 0.85 | 29.43
DVH102* | 8.5 | 2700 | 80 | 67 | 91 | 108.6 | 0.72 | 26.33
DVH102* | 8.5 | 2700 | 80 | 70 | 91 | 115 | 0.61 | 23.57
DVH102* | 8.5 | 2700 | 80 | 72 | 91 | 119 | 0.53 | 21.18
DVH102* | 8.5 | 2700 | 80 | 75 | 91 | 125.6 | 0.42 | 17.81
DVH102* | 8.5 | 2700 | 80 | 57 | 93 | 97.1 | 1 | 32.69
DVH102* | 8.5 | 2700 | 80 | 61 | 93 | 97 | 0.97 | 31.72
DVH102* | 8.5 | 2700 | 80 | 64 | 93 | 102.3 | 0.85 | 29.33
DVH102* | 8.5 | 2700 | 80 | 67 | 93 | 107.7 | 0.72 | 26.23
DVH102* | 8.5 | 2700 | 80 | 70 | 93 | 114.1 | 0.61 | 23.47
DVH102* | 8.5 | 2700 | 80 | 72 | 93 | 118.1 | 0.53 | 21.11
DVH102* | 8.5 | 2700 | 80 | 75 | 93 | 124.6 | 0.42 | 17.71
DVH102* | 8.5 | 2700 | 80 | 57 | 95 | 96.5 | 1 | 32.49
DVH102* | 8.5 | 2700 | 80 | 61 | 95 | 96.3 | 1 | 32.42
DVH102* | 8.5 | 2700 | 80 | 64 | 95 | 101.5 | 0.85 | 29.19
DVH102* | 8.5 | 2700 | 80 | 67 | 95 | 106.9 | 0.72 | 26.09
DVH102* | 8.5 | 2700 | 80 | 70 | 95 | 113.2 | 0.61 | 23.37
DVH102* | 8.5 | 2700 | 80 | 72 | 95 | 117.1 | 0.53 | 21.01
DVH102* | 8.5 | 2700 | 80 | 75 | 95 | 123.7 | 0.42 | 17.58
DVH102* | 8.5 | 2700 | 80 | 57 | 99 | 95.3 | 1 | 32.09
DVH102* | 8.5 | 2700 | 80 | 61 | 99 | 94.7 | 1 | 31.89
DVH102* | 8.5 | 2700 | 80 | 64 | 99 | 99.9 | 0.86 | 28.92
DVH102* | 8.5 | 2700 | 80 | 67 | 99 | 105.2 | 0.73 | 25.86
DVH102* | 8.5 | 2700 | 80 | 70 | 99 | 111.4 | 0.62 | 23.16
DVH102* | 8.5 | 2700 | 80 | 72 | 99 | 115.3 | 0.54 | 20.81
DVH102* | 8.5 | 2700 | 80 | 75 | 99 | 121.7 | 0.42 | 17.37
DVH102* | 8.5 | 2700 | 80 | 57 | 103 | 94.1 | 1 | 31.68
DVH102* | 8.5 | 2700 | 80 | 61 | 103 | 93.2 | 1 | 31.38
DVH102* | 8.5 | 2700 | 80 | 64 | 103 | 98.3 | 0.87 | 28.65
DVH102* | 8.5 | 2700 | 80 | 67 | 103 | 103.5 | 0.74 | 25.62
DVH102* | 8.5 | 2700 | 80 | 70 | 103 | 109.6 | 0.62 | 22.93
DVH102* | 8.5 | 2700 | 80 | 72 | 103 | 113.4 | 0.54 | 20.61
DVH102* | 8.5 | 2700 | 80 | 75 | 103 | 119.8 | 0.42 | 17.14
DVH102* | 8.5 | 2700 | 80 | 57 | 106 | 93.1 | 1 | 31.35
DVH102* | 8.5 | 2700 | 80 | 61 | 106 | 92.1 | 1 | 31.01
DVH102* | 8.5 | 2700 | 80 | 64 | 106 | 97 | 0.87 | 28.42
DVH102* | 8.5 | 2700 | 80 | 67 | 106 | 102.2 | 0.74 | 25.42
DVH102* | 8.5 | 2700 | 80 | 70 | 106 | 108.3 | 0.62 | 22.76
DVH102* | 8.5 | 2700 | 80 | 72 | 106 | 112 | 0.54 | 20.47
DVH102* | 8.5 | 2700 | 80 | 75 | 106 | 118.3 | 0.43 | 16.97
DVH102* | 8.5 | 2700 | 80 | 57 | 110 | 91.9 | 1 | 30.94
DVH102* | 8.5 | 2700 | 80 | 61 | 110 | 90.5 | 1 | 30.47
DVH102* | 8.5 | 2700 | 80 | 64 | 110 | 95.4 | 0.88 | 28.15
DVH102* | 8.5 | 2700 | 80 | 67 | 110 | 100.5 | 0.74 | 25.15
DVH102* | 8.5 | 2700 | 80 | 70 | 110 | 106.4 | 0.63 | 22.53
DVH102* | 8.5 | 2700 | 80 | 72 | 110 | 110.1 | 0.55 | 20.27
DVH102* | 8.5 | 2700 | 80 | 75 | 110 | 116.4 | 0.43 | 16.73
DVH102* | 8.5 | 2700 | 80 | 57 | 115 | 90.4 | 1 | 30.44
DVH102* | 8.5 | 2700 | 80 | 61 | 115 | 88.6 | 1 | 29.83
DVH102* | 8.5 | 2700 | 80 | 64 | 115 | 93.4 | 0.88 | 27.78
DVH102* | 8.5 | 2700 | 80 | 67 | 115 | 98.4 | 0.75 | 24.85
DVH102* | 8.5 | 2700 | 80 | 70 | 115 | 104.2 | 0.63 | 22.22
DVH102* | 8.5 | 2700 | 80 | 72 | 115 | 107.8 | 0.55 | 20
DVH102* | 8.5 | 2700 | 80 | 75 | 115 | 114 | 0.43 | 16.43
DVH102* | 8.5 | 2700 | 85 | 57 | 23 | 113.9 | 1 | 38.35
DVH102* | 8.5 | 2700 | 85 | 61 | 23 | 116.7 | 0.92 | 36.03
DVH102* | 8.5 | 2700 | 85 | 64 | 23 | 116.5 | 0.92 | 35.99
DVH102* | 8.5 | 2700 | 85 | 67 | 23 | 122.7 | 0.81 | 33.57
DVH102* | 8.5 | 2700 | 85 | 70 | 23 | 129.9 | 0.7 | 30.74
DVH102* | 8.5 | 2700 | 85 | 72 | 23 | 134.4 | 0.62 | 28.15
DVH102* | 8.5 | 2700 | 85 | 75 | 23 | 142 | 0.53 | 25.35
DVH102* | 8.5 | 2700 | 85 | 57 | 30 | 113.8 | 1 | 38.32
DVH102* | 8.5 | 2700 | 85 | 61 | 30 | 116.5 | 0.92 | 35.99
DVH102* | 8.5 | 2700 | 85 | 64 | 30 | 116.3 | 0.92 | 35.96
DVH102* | 8.5 | 2700 | 85 | 67 | 30 | 122.5 | 0.81 | 33.5
DVH102* | 8.5 | 2700 | 85 | 70 | 30 | 129.7 | 0.7 | 30.71
DVH102* | 8.5 | 2700 | 85 | 72 | 30 | 134.2 | 0.62 | 28.11
DVH102* | 8.5 | 2700 | 85 | 75 | 30 | 141.8 | 0.53 | 25.35
DVH102* | 8.5 | 2700 | 85 | 57 | 40 | 113.6 | 1 | 38.25
DVH102* | 8.5 | 2700 | 85 | 61 | 40 | 116.3 | 0.92 | 35.89
DVH102* | 8.5 | 2700 | 85 | 64 | 40 | 116 | 0.92 | 35.86
DVH102* | 8.5 | 2700 | 85 | 67 | 40 | 122.2 | 0.81 | 33.43
DVH102* | 8.5 | 2700 | 85 | 70 | 40 | 129.4 | 0.7 | 30.64
DVH102* | 8.5 | 2700 | 85 | 72 | 40 | 133.9 | 0.62 | 28.05
DVH102* | 8.5 | 2700 | 85 | 75 | 40 | 141.6 | 0.53 | 25.29
DVH102* | 8.5 | 2700 | 85 | 57 | 50 | 113.4 | 1 | 38.18
DVH102* | 8.5 | 2700 | 85 | 61 | 50 | 116 | 0.92 | 35.82
DVH102* | 8.5 | 2700 | 85 | 64 | 50 | 115.8 | 0.92 | 35.79
DVH102* | 8.5 | 2700 | 85 | 67 | 50 | 121.9 | 0.81 | 33.37
DVH102* | 8.5 | 2700 | 85 | 70 | 50 | 129.2 | 0.7 | 30.57
DVH102* | 8.5 | 2700 | 85 | 72 | 50 | 133.6 | 0.62 | 27.98
DVH102* | 8.5 | 2700 | 85 | 75 | 50 | 141.3 | 0.53 | 25.25
DVH102* | 8.5 | 2700 | 85 | 57 | 54 | 113.4 | 1 | 38.18
DVH102* | 8.5 | 2700 | 85 | 61 | 54 | 115.9 | 0.92 | 35.79
DVH102* | 8.5 | 2700 | 85 | 64 | 54 | 115.7 | 0.92 | 35.76
DVH102* | 8.5 | 2700 | 85 | 67 | 54 | 121.8 | 0.81 | 33.33
DVH102* | 8.5 | 2700 | 85 | 70 | 54 | 129 | 0.7 | 30.54
DVH102* | 8.5 | 2700 | 85 | 72 | 54 | 133.5 | 0.62 | 27.98
DVH102* | 8.5 | 2700 | 85 | 75 | 54 | 141.2 | 0.53 | 25.22
DVH102* | 8.5 | 2700 | 85 | 57 | 58 | 113.3 | 1 | 38.15
DVH102* | 8.5 | 2700 | 85 | 61 | 58 | 115.8 | 0.92 | 35.76
DVH102* | 8.5 | 2700 | 85 | 64 | 58 | 115.6 | 0.92 | 35.72
DVH102* | 8.5 | 2700 | 85 | 67 | 58 | 121.7 | 0.81 | 33.3
DVH102* | 8.5 | 2700 | 85 | 70 | 58 | 128.9 | 0.7 | 30.51
DVH102* | 8.5 | 2700 | 85 | 72 | 58 | 133.4 | 0.62 | 27.95
DVH102* | 8.5 | 2700 | 85 | 75 | 58 | 141.1 | 0.53 | 25.22
DVH102* | 8.5 | 2700 | 85 | 57 | 62 | 112.6 | 1 | 37.91
DVH102* | 8.5 | 2700 | 85 | 61 | 62 | 115.1 | 0.92 | 35.62
DVH102* | 8.5 | 2700 | 85 | 64 | 62 | 114.8 | 0.92 | 35.59
DVH102* | 8.5 | 2700 | 85 | 67 | 62 | 121 | 0.81 | 33.16
DVH102* | 8.5 | 2700 | 85 | 70 | 62 | 128.1 | 0.7 | 30.4
DVH102* | 8.5 | 2700 | 85 | 72 | 62 | 132.5 | 0.62 | 27.85
DVH102* | 8.5 | 2700 | 85 | 75 | 62 | 139.6 | 0.53 | 24.95
DVH102* | 8.5 | 2700 | 85 | 57 | 66 | 111.3 | 1 | 37.47
DVH102* | 8.5 | 2700 | 85 | 61 | 66 | 113.5 | 0.93 | 35.39
DVH102* | 8.5 | 2700 | 85 | 64 | 66 | 113.2 | 0.93 | 35.35
DVH102* | 8.5 | 2700 | 85 | 67 | 66 | 119.3 | 0.82 | 32.96
DVH102* | 8.5 | 2700 | 85 | 70 | 66 | 126.3 | 0.71 | 30.17
DVH102* | 8.5 | 2700 | 85 | 72 | 66 | 130.7 | 0.63 | 27.64
DVH102* | 8.5 | 2700 | 85 | 75 | 66 | 137.7 | 0.53 | 24.68
DVH102* | 8.5 | 2700 | 85 | 57 | 70 | 110 | 1 | 37.04
DVH102* | 8.5 | 2700 | 85 | 61 | 70 | 111.9 | 0.93 | 35.12
DVH102* | 8.5 | 2700 | 85 | 64 | 70 | 111.6 | 0.93 | 35.08
DVH102* | 8.5 | 2700 | 85 | 67 | 70 | 117.5 | 0.83 | 32.73
DVH102* | 8.5 | 2700 | 85 | 70 | 70 | 124.5 | 0.71 | 29.97
DVH102* | 8.5 | 2700 | 85 | 72 | 70 | 128.8 | 0.63 | 27.44
DVH102* | 8.5 | 2700 | 85 | 75 | 70 | 135.7 | 0.53 | 24.41
DVH102* | 8.5 | 2700 | 85 | 57 | 72 | 109.4 | 1 | 36.84
DVH102* | 8.5 | 2700 | 85 | 61 | 72 | 111 | 0.94 | 34.98
DVH102* | 8.5 | 2700 | 85 | 64 | 72 | 110.8 | 0.94 | 34.95
DVH102* | 8.5 | 2700 | 85 | 67 | 72 | 116.7 | 0.83 | 32.59
DVH102* | 8.5 | 2700 | 85 | 70 | 72 | 123.6 | 0.72 | 29.87
DVH102* | 8.5 | 2700 | 85 | 72 | 72 | 127.9 | 0.63 | 27.34
DVH102* | 8.5 | 2700 | 85 | 75 | 72 | 134.8 | 0.53 | 24.28
DVH102* | 8.5 | 2700 | 85 | 57 | 75 | 108.4 | 1 | 36.5
DVH102* | 8.5 | 2700 | 85 | 61 | 75 | 109.8 | 0.94 | 34.78
DVH102* | 8.5 | 2700 | 85 | 64 | 75 | 109.6 | 0.94 | 34.75
DVH102* | 8.5 | 2700 | 85 | 67 | 75 | 115.4 | 0.83 | 32.42
DVH102* | 8.5 | 2700 | 85 | 70 | 75 | 122.3 | 0.72 | 29.7
DVH102* | 8.5 | 2700 | 85 | 72 | 75 | 126.5 | 0.64 | 27.17
DVH102* | 8.5 | 2700 | 85 | 75 | 75 | 133.3 | 0.54 | 24.04
DVH102* | 8.5 | 2700 | 85 | 57 | 79 | 107.1 | 1 | 36.06
DVH102* | 8.5 | 2700 | 85 | 61 | 79 | 108.2 | 0.95 | 34.51
DVH102* | 8.5 | 2700 | 85 | 64 | 79 | 108 | 0.95 | 34.48
DVH102* | 8.5 | 2700 | 85 | 67 | 79 | 113.7 | 0.84 | 32.15
DVH102* | 8.5 | 2700 | 85 | 70 | 79 | 120.4 | 0.73 | 29.46
DVH102* | 8.5 | 2700 | 85 | 72 | 79 | 124.6 | 0.64 | 26.97
DVH102* | 8.5 | 2700 | 85 | 75 | 79 | 131.4 | 0.54 | 23.77
DVH102* | 8.5 | 2700 | 85 | 57 | 83 | 105.8 | 1 | 35.62
DVH102* | 8.5 | 2700 | 85 | 61 | 83 | 106.6 | 0.95 | 34.24
DVH102* | 8.5 | 2700 | 85 | 64 | 83 | 106.3 | 0.96 | 34.21
DVH102* | 8.5 | 2700 | 85 | 67 | 83 | 112 | 0.85 | 31.89
DVH102* | 8.5 | 2700 | 85 | 70 | 83 | 118.6 | 0.73 | 29.23
DVH102* | 8.5 | 2700 | 85 | 72 | 83 | 122.7 | 0.65 | 26.77
DVH102* | 8.5 | 2700 | 85 | 75 | 83 | 129.5 | 0.54 | 23.5
DVH102* | 8.5 | 2700 | 85 | 57 | 87 | 104.6 | 1 | 35.22
DVH102* | 8.5 | 2700 | 85 | 61 | 87 | 105 | 0.96 | 33.97
DVH102* | 8.5 | 2700 | 85 | 64 | 87 | 104.7 | 0.96 | 33.94
DVH102* | 8.5 | 2700 | 85 | 67 | 87 | 110.3 | 0.85 | 31.65
DVH102* | 8.5 | 2700 | 85 | 70 | 87 | 116.8 | 0.74 | 28.99
DVH102* | 8.5 | 2700 | 85 | 72 | 87 | 120.9 | 0.65 | 26.53
DVH102* | 8.5 | 2700 | 85 | 75 | 87 | 127.5 | 0.54 | 23.2
DVH102* | 8.5 | 2700 | 85 | 57 | 91 | 103.3 | 1 | 34.78
DVH102* | 8.5 | 2700 | 85 | 61 | 91 | 103.3 | 0.97 | 33.67
DVH102* | 8.5 | 2700 | 85 | 64 | 91 | 103.1 | 0.97 | 33.64
DVH102* | 8.5 | 2700 | 85 | 67 | 91 | 108.6 | 0.86 | 31.35
DVH102* | 8.5 | 2700 | 85 | 70 | 91 | 115 | 0.74 | 28.72
DVH102* | 8.5 | 2700 | 85 | 72 | 91 | 119 | 0.66 | 26.3
DVH102* | 8.5 | 2700 | 85 | 75 | 91 | 125.6 | 0.54 | 22.93
DVH102* | 8.5 | 2700 | 85 | 57 | 93 | 102.6 | 1 | 34.55
DVH102* | 8.5 | 2700 | 85 | 61 | 93 | 102.5 | 0.97 | 33.54
DVH102* | 8.5 | 2700 | 85 | 64 | 93 | 102.3 | 0.97 | 33.5
DVH102* | 8.5 | 2700 | 85 | 67 | 93 | 107.7 | 0.86 | 31.21
DVH102* | 8.5 | 2700 | 85 | 70 | 93 | 114.1 | 0.74 | 28.59
DVH102* | 8.5 | 2700 | 85 | 72 | 93 | 118.1 | 0.66 | 26.2
DVH102* | 8.5 | 2700 | 85 | 75 | 93 | 124.6 | 0.54 | 22.79
DVH102* | 8.5 | 2700 | 85 | 57 | 95 | 102 | 1 | 34.34
DVH102* | 8.5 | 2700 | 85 | 61 | 95 | 101.7 | 1 | 34.24
DVH102* | 8.5 | 2700 | 85 | 64 | 95 | 101.5 | 1 | 34.18
DVH102* | 8.5 | 2700 | 85 | 67 | 95 | 106.9 | 0.86 | 31.08
DVH102* | 8.5 | 2700 | 85 | 70 | 95 | 113.2 | 0.75 | 28.48
DVH102* | 8.5 | 2700 | 85 | 72 | 95 | 117.1 | 0.66 | 26.06
DVH102* | 8.5 | 2700 | 85 | 75 | 95 | 123.7 | 0.54 | 22.63
DVH102* | 8.5 | 2700 | 85 | 57 | 99 | 100.7 | 1 | 33.91
DVH102* | 8.5 | 2700 | 85 | 61 | 99 | 100.1 | 1 | 33.7
DVH102* | 8.5 | 2700 | 85 | 64 | 99 | 99.9 | 1 | 33.64
DVH102* | 8.5 | 2700 | 85 | 67 | 99 | 105.2 | 0.87 | 30.81
DVH102* | 8.5 | 2700 | 85 | 70 | 99 | 111.4 | 0.75 | 28.22
DVH102* | 8.5 | 2700 | 85 | 72 | 99 | 115.3 | 0.67 | 25.82
DVH102* | 8.5 | 2700 | 85 | 75 | 99 | 121.7 | 0.55 | 22.36
DVH102* | 8.5 | 2700 | 85 | 57 | 103 | 99.4 | 1 | 33.47
DVH102* | 8.5 | 2700 | 85 | 61 | 103 | 98.5 | 1 | 33.16
DVH102* | 8.5 | 2700 | 85 | 64 | 103 | 98.3 | 1 | 33.1
DVH102* | 8.5 | 2700 | 85 | 67 | 103 | 103.5 | 0.88 | 30.51
DVH102* | 8.5 | 2700 | 85 | 70 | 103 | 109.6 | 0.76 | 27.95
DVH102* | 8.5 | 2700 | 85 | 72 | 103 | 113.4 | 0.67 | 25.59
DVH102* | 8.5 | 2700 | 85 | 75 | 103 | 119.8 | 0.55 | 22.05
DVH102* | 8.5 | 2700 | 85 | 57 | 106 | 98.4 | 1 | 33.13
DVH102* | 8.5 | 2700 | 85 | 61 | 106 | 97.2 | 1 | 32.73
DVH102* | 8.5 | 2700 | 85 | 64 | 106 | 97 | 1 | 32.66
DVH102* | 8.5 | 2700 | 85 | 67 | 106 | 102.2 | 0.88 | 30.27
DVH102* | 8.5 | 2700 | 85 | 70 | 106 | 108.3 | 0.76 | 27.74
DVH102* | 8.5 | 2700 | 85 | 72 | 106 | 112 | 0.67 | 25.39
DVH102* | 8.5 | 2700 | 85 | 75 | 106 | 118.3 | 0.55 | 21.85
DVH102* | 8.5 | 2700 | 85 | 57 | 110 | 97.1 | 1 | 32.69
DVH102* | 8.5 | 2700 | 85 | 61 | 110 | 95.6 | 1 | 32.19
DVH102* | 8.5 | 2700 | 85 | 64 | 110 | 95.4 | 1 | 32.12
DVH102* | 8.5 | 2700 | 85 | 67 | 110 | 100.5 | 0.89 | 29.97
DVH102* | 8.5 | 2700 | 85 | 70 | 110 | 106.4 | 0.77 | 27.47
DVH102* | 8.5 | 2700 | 85 | 72 | 110 | 110.1 | 0.68 | 25.15
DVH102* | 8.5 | 2700 | 85 | 75 | 110 | 116.4 | 0.55 | 21.55
DVH102* | 8.5 | 2700 | 85 | 57 | 115 | 95.5 | 1 | 32.15
DVH102* | 8.5 | 2700 | 85 | 61 | 115 | 93.6 | 1 | 31.52
DVH102* | 8.5 | 2700 | 85 | 64 | 115 | 93.4 | 1 | 31.45
DVH102* | 8.5 | 2700 | 85 | 67 | 115 | 98.4 | 0.89 | 29.6
DVH102* | 8.5 | 2700 | 85 | 70 | 115 | 104.2 | 0.77 | 27.1
DVH102* | 8.5 | 2700 | 85 | 72 | 115 | 107.8 | 0.68 | 24.81
DVH102* | 8.5 | 2700 | 85 | 75 | 115 | 114 | 0.55 | 21.18
DVH102* | 8.5 | 3100 | 70 | 57 | 23 | 101.9 | 0.88 | 26.25
DVH102* | 8.5 | 3100 | 70 | 61 | 23 | 113.2 | 0.66 | 22.02
DVH102* | 8.5 | 3100 | 70 | 64 | 23 | 119.3 | 0.54 | 18.86
DVH102* | 8.5 | 3100 | 70 | 67 | 23 | 125.7 | 0.42 | 15.66
DVH102* | 8.5 | 3100 | 70 | 57 | 30 | 101.7 | 0.88 | 26.22
DVH102* | 8.5 | 3100 | 70 | 61 | 30 | 113 | 0.66 | 21.99
DVH102* | 8.5 | 3100 | 70 | 64 | 30 | 119.1 | 0.54 | 18.83
DVH102* | 8.5 | 3100 | 70 | 67 | 30 | 125.5 | 0.42 | 15.63
DVH102* | 8.5 | 3100 | 70 | 57 | 40 | 101.6 | 0.88 | 26.16
DVH102* | 8.5 | 3100 | 70 | 61 | 40 | 112.8 | 0.66 | 21.94
DVH102* | 8.5 | 3100 | 70 | 64 | 40 | 118.9 | 0.54 | 18.77
DVH102* | 8.5 | 3100 | 70 | 67 | 40 | 125.2 | 0.42 | 15.6
DVH102* | 8.5 | 3100 | 70 | 57 | 50 | 101.4 | 0.88 | 26.13
DVH102* | 8.5 | 3100 | 70 | 61 | 50 | 112.5 | 0.66 | 21.91
DVH102* | 8.5 | 3100 | 70 | 64 | 50 | 118.6 | 0.54 | 18.74
DVH102* | 8.5 | 3100 | 70 | 67 | 50 | 124.9 | 0.43 | 15.57
DVH102* | 8.5 | 3100 | 70 | 57 | 54 | 101.4 | 0.88 | 26.1
DVH102* | 8.5 | 3100 | 70 | 61 | 54 | 112.4 | 0.66 | 21.88
DVH102* | 8.5 | 3100 | 70 | 64 | 54 | 118.5 | 0.54 | 18.71
DVH102* | 8.5 | 3100 | 70 | 67 | 54 | 124.8 | 0.42 | 15.54
DVH102* | 8.5 | 3100 | 70 | 57 | 58 | 101.3 | 0.88 | 26.1
DVH102* | 8.5 | 3100 | 70 | 61 | 58 | 112.3 | 0.66 | 21.88
DVH102* | 8.5 | 3100 | 70 | 64 | 58 | 118.4 | 0.54 | 18.71
DVH102* | 8.5 | 3100 | 70 | 67 | 58 | 124.7 | 0.43 | 15.54
DVH102* | 8.5 | 3100 | 70 | 57 | 62 | 100.7 | 0.88 | 25.95
DVH102* | 8.5 | 3100 | 70 | 61 | 62 | 111.6 | 0.67 | 21.79
DVH102* | 8.5 | 3100 | 70 | 64 | 62 | 117.7 | 0.54 | 18.62
DVH102* | 8.5 | 3100 | 70 | 67 | 62 | 123.9 | 0.43 | 15.48
DVH102* | 8.5 | 3100 | 70 | 57 | 66 | 99.5 | 0.88 | 25.75
DVH102* | 8.5 | 3100 | 70 | 61 | 66 | 110 | 0.67 | 21.61
DVH102* | 8.5 | 3100 | 70 | 64 | 66 | 116 | 0.54 | 18.5
DVH102* | 8.5 | 3100 | 70 | 67 | 66 | 122.2 | 0.43 | 15.37
DVH102* | 8.5 | 3100 | 70 | 57 | 70 | 98.4 | 0.88 | 25.51
DVH102* | 8.5 | 3100 | 70 | 61 | 70 | 108.5 | 0.67 | 21.47
DVH102* | 8.5 | 3100 | 70 | 64 | 70 | 114.3 | 0.55 | 18.36
DVH102* | 8.5 | 3100 | 70 | 67 | 70 | 120.4 | 0.43 | 15.25
DVH102* | 8.5 | 3100 | 70 | 57 | 72 | 97.8 | 0.89 | 25.4
DVH102* | 8.5 | 3100 | 70 | 61 | 72 | 107.7 | 0.68 | 21.38
DVH102* | 8.5 | 3100 | 70 | 64 | 72 | 113.5 | 0.55 | 18.3
DVH102* | 8.5 | 3100 | 70 | 67 | 72 | 119.5 | 0.43 | 15.22
DVH102* | 8.5 | 3100 | 70 | 57 | 75 | 96.9 | 0.89 | 25.22
DVH102* | 8.5 | 3100 | 70 | 61 | 75 | 106.5 | 0.68 | 21.26
DVH102* | 8.5 | 3100 | 70 | 64 | 75 | 112.3 | 0.55 | 18.18
DVH102* | 8.5 | 3100 | 70 | 67 | 75 | 118.2 | 0.44 | 15.13
DVH102* | 8.5 | 3100 | 70 | 57 | 79 | 95.8 | 0.89 | 24.99
DVH102* | 8.5 | 3100 | 70 | 61 | 79 | 104.9 | 0.69 | 21.11
DVH102* | 8.5 | 3100 | 70 | 64 | 79 | 110.6 | 0.56 | 18.06
DVH102* | 8.5 | 3100 | 70 | 67 | 79 | 116.5 | 0.44 | 15.01
DVH102* | 8.5 | 3100 | 70 | 57 | 83 | 94.6 | 0.89 | 24.78
DVH102* | 8.5 | 3100 | 70 | 61 | 83 | 103.3 | 0.69 | 20.94
DVH102* | 8.5 | 3100 | 70 | 64 | 83 | 108.9 | 0.56 | 17.92
DVH102* | 8.5 | 3100 | 70 | 67 | 83 | 114.7 | 0.44 | 14.87
DVH102* | 8.5 | 3100 | 70 | 57 | 87 | 93.5 | 0.9 | 24.55
DVH102* | 8.5 | 3100 | 70 | 61 | 87 | 101.8 | 0.7 | 20.76
DVH102* | 8.5 | 3100 | 70 | 64 | 87 | 107.3 | 0.56 | 17.77
DVH102* | 8.5 | 3100 | 70 | 67 | 87 | 113 | 0.45 | 14.75
DVH102* | 8.5 | 3100 | 70 | 57 | 91 | 92.3 | 0.9 | 24.31
DVH102* | 8.5 | 3100 | 70 | 61 | 91 | 100.2 | 0.7 | 20.59
DVH102* | 8.5 | 3100 | 70 | 64 | 91 | 105.6 | 0.57 | 17.6
DVH102* | 8.5 | 3100 | 70 | 67 | 91 | 111.3 | 0.45 | 14.63
DVH102* | 8.5 | 3100 | 70 | 57 | 93 | 91.7 | 0.9 | 24.19
DVH102* | 8.5 | 3100 | 70 | 61 | 93 | 99.4 | 0.7 | 20.5
DVH102* | 8.5 | 3100 | 70 | 64 | 93 | 104.8 | 0.57 | 17.54
DVH102* | 8.5 | 3100 | 70 | 67 | 93 | 110.4 | 0.45 | 14.57
DVH102* | 8.5 | 3100 | 70 | 57 | 95 | 91.2 | 0.9 | 24.08
DVH102* | 8.5 | 3100 | 70 | 61 | 95 | 98.6 | 0.7 | 20.35
DVH102* | 8.5 | 3100 | 70 | 64 | 95 | 104 | 0.57 | 17.45
DVH102* | 8.5 | 3100 | 70 | 67 | 95 | 109.5 | 0.45 | 14.49
DVH102* | 8.5 | 3100 | 70 | 57 | 99 | 90 | 0.9 | 23.84
DVH102* | 8.5 | 3100 | 70 | 61 | 99 | 97.1 | 0.71 | 20.09
DVH102* | 8.5 | 3100 | 70 | 64 | 99 | 102.3 | 0.58 | 17.3
DVH102* | 8.5 | 3100 | 70 | 67 | 99 | 107.8 | 0.45 | 14.37
DVH102* | 8.5 | 3100 | 70 | 57 | 103 | 88.9 | 0.9 | 23.58
DVH102* | 8.5 | 3100 | 70 | 61 | 103 | 95.5 | 0.71 | 19.82
DVH102* | 8.5 | 3100 | 70 | 64 | 103 | 100.7 | 0.58 | 17.13
DVH102* | 8.5 | 3100 | 70 | 67 | 103 | 106 | 0.46 | 14.22
DVH102* | 8.5 | 3100 | 70 | 57 | 106 | 88 | 0.91 | 23.4
DVH102* | 8.5 | 3100 | 70 | 61 | 106 | 94.3 | 0.71 | 19.62
DVH102* | 8.5 | 3100 | 70 | 64 | 106 | 99.4 | 0.58 | 17.01
DVH102* | 8.5 | 3100 | 70 | 67 | 106 | 104.7 | 0.46 | 14.13
DVH102* | 8.5 | 3100 | 70 | 57 | 110 | 86.8 | 0.91 | 23.17
DVH102* | 8.5 | 3100 | 70 | 61 | 110 | 92.7 | 0.71 | 19.35
DVH102* | 8.5 | 3100 | 70 | 64 | 110 | 97.7 | 0.59 | 16.83
DVH102* | 8.5 | 3100 | 70 | 67 | 110 | 103 | 0.46 | 13.99
DVH102* | 8.5 | 3100 | 70 | 57 | 115 | 85.4 | 0.91 | 22.87
DVH102* | 8.5 | 3100 | 70 | 61 | 115 | 90.8 | 0.71 | 19
DVH102* | 8.5 | 3100 | 70 | 64 | 115 | 95.7 | 0.59 | 16.6
DVH102* | 8.5 | 3100 | 70 | 67 | 115 | 100.8 | 0.47 | 13.81
DVH102* | 8.5 | 3100 | 75 | 57 | 23 | 104.3 | 1 | 30.59
DVH102* | 8.5 | 3100 | 75 | 61 | 23 | 113.2 | 0.82 | 27.07
DVH102* | 8.5 | 3100 | 75 | 64 | 23 | 119.3 | 0.68 | 23.93
DVH102* | 8.5 | 3100 | 75 | 67 | 23 | 125.7 | 0.57 | 20.85
DVH102* | 8.5 | 3100 | 75 | 70 | 23 | 133.1 | 0.46 | 17.98
DVH102* | 8.5 | 3100 | 75 | 72 | 23 | 137.7 | 0.39 | 15.63
DVH102* | 8.5 | 3100 | 75 | 57 | 30 | 104.2 | 1 | 30.56
DVH102* | 8.5 | 3100 | 75 | 61 | 30 | 113 | 0.82 | 27.04
DVH102* | 8.5 | 3100 | 75 | 64 | 30 | 119.1 | 0.68 | 23.9
DVH102* | 8.5 | 3100 | 75 | 67 | 30 | 125.5 | 0.57 | 20.82
DVH102* | 8.5 | 3100 | 75 | 70 | 30 | 132.9 | 0.46 | 17.95
DVH102* | 8.5 | 3100 | 75 | 72 | 30 | 137.5 | 0.39 | 15.6
DVH102* | 8.5 | 3100 | 75 | 57 | 40 | 104.1 | 1 | 30.53
DVH102* | 8.5 | 3100 | 75 | 61 | 40 | 112.8 | 0.82 | 26.98
DVH102* | 8.5 | 3100 | 75 | 64 | 40 | 118.9 | 0.68 | 23.84
DVH102* | 8.5 | 3100 | 75 | 67 | 40 | 125.2 | 0.57 | 20.76
DVH102* | 8.5 | 3100 | 75 | 70 | 40 | 132.6 | 0.46 | 17.89
DVH102* | 8.5 | 3100 | 75 | 72 | 40 | 137.2 | 0.39 | 15.57
DVH102* | 8.5 | 3100 | 75 | 57 | 50 | 103.9 | 1 | 30.47
DVH102* | 8.5 | 3100 | 75 | 61 | 50 | 112.5 | 0.82 | 26.92
DVH102* | 8.5 | 3100 | 75 | 64 | 50 | 118.6 | 0.68 | 23.78
DVH102* | 8.5 | 3100 | 75 | 67 | 50 | 124.9 | 0.57 | 20.73
DVH102* | 8.5 | 3100 | 75 | 70 | 50 | 132.3 | 0.46 | 17.86
DVH102* | 8.5 | 3100 | 75 | 72 | 50 | 136.9 | 0.39 | 15.54
DVH102* | 8.5 | 3100 | 75 | 57 | 54 | 103.8 | 1 | 30.44
DVH102* | 8.5 | 3100 | 75 | 61 | 54 | 112.4 | 0.82 | 26.89
DVH102* | 8.5 | 3100 | 75 | 64 | 54 | 118.5 | 0.68 | 23.78
DVH102* | 8.5 | 3100 | 75 | 67 | 54 | 124.8 | 0.57 | 20.7
DVH102* | 8.5 | 3100 | 75 | 70 | 54 | 132.2 | 0.46 | 17.83
DVH102* | 8.5 | 3100 | 75 | 72 | 54 | 136.8 | 0.39 | 15.51
DVH102* | 8.5 | 3100 | 75 | 57 | 58 | 103.8 | 1 | 30.44
DVH102* | 8.5 | 3100 | 75 | 61 | 58 | 112.3 | 0.82 | 26.86
DVH102* | 8.5 | 3100 | 75 | 64 | 58 | 118.4 | 0.68 | 23.75
DVH102* | 8.5 | 3100 | 75 | 67 | 58 | 124.7 | 0.57 | 20.67
DVH102* | 8.5 | 3100 | 75 | 70 | 58 | 132.1 | 0.46 | 17.83
DVH102* | 8.5 | 3100 | 75 | 72 | 58 | 136.6 | 0.39 | 15.51
DVH102* | 8.5 | 3100 | 75 | 57 | 62 | 103.2 | 1 | 30.26
DVH102* | 8.5 | 3100 | 75 | 61 | 62 | 111.6 | 0.82 | 26.77
DVH102* | 8.5 | 3100 | 75 | 64 | 62 | 117.7 | 0.69 | 23.67
DVH102* | 8.5 | 3100 | 75 | 67 | 62 | 123.9 | 0.57 | 20.62
DVH102* | 8.5 | 3100 | 75 | 70 | 62 | 131.3 | 0.46 | 17.77
DVH102* | 8.5 | 3100 | 75 | 72 | 62 | 135.8 | 0.39 | 15.45
DVH102* | 8.5 | 3100 | 75 | 57 | 66 | 102 | 1 | 29.91
DVH102* | 8.5 | 3100 | 75 | 61 | 66 | 110 | 0.82 | 26.57
DVH102* | 8.5 | 3100 | 75 | 64 | 66 | 116 | 0.69 | 23.49
DVH102* | 8.5 | 3100 | 75 | 67 | 66 | 122.2 | 0.57 | 20.47
DVH102* | 8.5 | 3100 | 75 | 70 | 66 | 129.4 | 0.46 | 17.62
DVH102* | 8.5 | 3100 | 75 | 72 | 66 | 133.9 | 0.39 | 15.34
DVH102* | 8.5 | 3100 | 75 | 57 | 70 | 100.8 | 1 | 29.56
DVH102* | 8.5 | 3100 | 75 | 61 | 70 | 108.5 | 0.83 | 26.39
DVH102* | 8.5 | 3100 | 75 | 64 | 70 | 114.3 | 0.7 | 23.34
DVH102* | 8.5 | 3100 | 75 | 67 | 70 | 120.4 | 0.58 | 20.32
DVH102* | 8.5 | 3100 | 75 | 70 | 70 | 127.6 | 0.47 | 17.51
DVH102* | 8.5 | 3100 | 75 | 72 | 70 | 132 | 0.39 | 15.22
DVH102* | 8.5 | 3100 | 75 | 57 | 72 | 100.2 | 1 | 29.38
DVH102* | 8.5 | 3100 | 75 | 61 | 72 | 107.7 | 0.83 | 26.28
DVH102* | 8.5 | 3100 | 75 | 64 | 72 | 113.5 | 0.7 | 23.26
DVH102* | 8.5 | 3100 | 75 | 67 | 72 | 119.5 | 0.58 | 20.23
DVH102* | 8.5 | 3100 | 75 | 70 | 72 | 126.6 | 0.47 | 17.45
DVH102* | 8.5 | 3100 | 75 | 72 | 72 | 131 | 0.4 | 15.19
DVH102* | 8.5 | 3100 | 75 | 57 | 75 | 99.3 | 1 | 29.12
DVH102* | 8.5 | 3100 | 75 | 61 | 75 | 106.5 | 0.84 | 26.13
DVH102* | 8.5 | 3100 | 75 | 64 | 75 | 112.3 | 0.7 | 23.11
DVH102* | 8.5 | 3100 | 75 | 67 | 75 | 118.2 | 0.58 | 20.12
DVH102* | 8.5 | 3100 | 75 | 70 | 75 | 125.2 | 0.47 | 17.33
DVH102* | 8.5 | 3100 | 75 | 72 | 75 | 129.6 | 0.4 | 15.1
DVH102* | 8.5 | 3100 | 75 | 57 | 79 | 98.1 | 1 | 28.77
DVH102* | 8.5 | 3100 | 75 | 61 | 79 | 104.9 | 0.84 | 25.92
DVH102* | 8.5 | 3100 | 75 | 64 | 79 | 110.6 | 0.71 | 22.93
DVH102* | 8.5 | 3100 | 75 | 67 | 79 | 116.5 | 0.58 | 19.97
DVH102* | 8.5 | 3100 | 75 | 70 | 79 | 123.4 | 0.48 | 17.21
DVH102* | 8.5 | 3100 | 75 | 72 | 79 | 127.6 | 0.4 | 14.99
DVH102* | 8.5 | 3100 | 75 | 57 | 83 | 96.9 | 1 | 28.42
DVH102* | 8.5 | 3100 | 75 | 61 | 83 | 103.3 | 0.85 | 25.72
DVH102* | 8.5 | 3100 | 75 | 64 | 83 | 108.9 | 0.71 | 22.76
DVH102* | 8.5 | 3100 | 75 | 67 | 83 | 114.7 | 0.59 | 19.79
DVH102* | 8.5 | 3100 | 75 | 70 | 83 | 121.5 | 0.48 | 17.07
DVH102* | 8.5 | 3100 | 75 | 72 | 83 | 125.7 | 0.4 | 14.84
DVH102* | 8.5 | 3100 | 75 | 57 | 87 | 95.7 | 1 | 28.06
DVH102* | 8.5 | 3100 | 75 | 61 | 87 | 101.8 | 0.85 | 25.51
DVH102* | 8.5 | 3100 | 75 | 64 | 87 | 107.3 | 0.72 | 22.55
DVH102* | 8.5 | 3100 | 75 | 67 | 87 | 113 | 0.59 | 19.65
DVH102* | 8.5 | 3100 | 75 | 70 | 87 | 119.7 | 0.48 | 16.92
DVH102* | 8.5 | 3100 | 75 | 72 | 87 | 123.8 | 0.41 | 14.72
DVH102* | 8.5 | 3100 | 75 | 57 | 91 | 94.6 | 1 | 27.74
DVH102* | 8.5 | 3100 | 75 | 61 | 91 | 100.2 | 0.86 | 25.31
DVH102* | 8.5 | 3100 | 75 | 64 | 91 | 105.6 | 0.72 | 22.38
DVH102* | 8.5 | 3100 | 75 | 67 | 91 | 111.3 | 0.6 | 19.47
DVH102* | 8.5 | 3100 | 75 | 70 | 91 | 117.8 | 0.49 | 16.77
DVH102* | 8.5 | 3100 | 75 | 72 | 91 | 121.9 | 0.41 | 14.6
DVH102* | 8.5 | 3100 | 75 | 57 | 93 | 94 | 1 | 27.57
DVH102* | 8.5 | 3100 | 75 | 61 | 93 | 99.4 | 0.86 | 25.19
DVH102* | 8.5 | 3100 | 75 | 64 | 93 | 104.8 | 0.72 | 22.26
DVH102* | 8.5 | 3100 | 75 | 67 | 93 | 110.4 | 0.6 | 19.38
DVH102* | 8.5 | 3100 | 75 | 70 | 93 | 116.9 | 0.49 | 16.72
DVH102* | 8.5 | 3100 | 75 | 72 | 93 | 121 | 0.41 | 14.55
DVH102* | 8.5 | 3100 | 75 | 57 | 95 | 93.4 | 1 | 27.39
DVH102* | 8.5 | 3100 | 75 | 61 | 95 | 98.6 | 0.87 | 25.01
DVH102* | 8.5 | 3100 | 75 | 64 | 95 | 104 | 0.73 | 22.17
DVH102* | 8.5 | 3100 | 75 | 67 | 95 | 109.5 | 0.6 | 19.3
DVH102* | 8.5 | 3100 | 75 | 70 | 95 | 116 | 0.49 | 16.63
DVH102* | 8.5 | 3100 | 75 | 72 | 95 | 120 | 0.41 | 14.49
DVH102* | 8.5 | 3100 | 75 | 57 | 99 | 92.2 | 1 | 27.04
DVH102* | 8.5 | 3100 | 75 | 61 | 99 | 97.1 | 0.87 | 24.69
DVH102* | 8.5 | 3100 | 75 | 64 | 99 | 102.3 | 0.73 | 21.96
DVH102* | 8.5 | 3100 | 75 | 67 | 99 | 107.8 | 0.6 | 19.12
DVH102* | 8.5 | 3100 | 75 | 70 | 99 | 114.1 | 0.49 | 16.48
DVH102* | 8.5 | 3100 | 75 | 72 | 99 | 118.1 | 0.41 | 14.34
DVH102* | 8.5 | 3100 | 75 | 57 | 103 | 91 | 1 | 26.69
DVH102* | 8.5 | 3100 | 75 | 61 | 103 | 95.5 | 0.87 | 24.37
DVH102* | 8.5 | 3100 | 75 | 64 | 103 | 100.7 | 0.74 | 21.76
DVH102* | 8.5 | 3100 | 75 | 67 | 103 | 106 | 0.61 | 18.94
DVH102* | 8.5 | 3100 | 75 | 70 | 103 | 112.3 | 0.5 | 16.33
DVH102* | 8.5 | 3100 | 75 | 72 | 103 | 116.2 | 0.42 | 14.19
DVH102* | 8.5 | 3100 | 75 | 57 | 106 | 90.1 | 1 | 26.42
DVH102* | 8.5 | 3100 | 75 | 61 | 106 | 94.3 | 0.87 | 24.11
DVH102* | 8.5 | 3100 | 75 | 64 | 106 | 99.4 | 0.74 | 21.58
DVH102* | 8.5 | 3100 | 75 | 67 | 106 | 104.7 | 0.61 | 18.8
DVH102* | 8.5 | 3100 | 75 | 70 | 106 | 110.9 | 0.5 | 16.22
DVH102* | 8.5 | 3100 | 75 | 72 | 106 | 114.7 | 0.42 | 14.11
DVH102* | 8.5 | 3100 | 75 | 57 | 110 | 88.9 | 1 | 26.07
DVH102* | 8.5 | 3100 | 75 | 61 | 110 | 92.7 | 0.87 | 23.78
DVH102* | 8.5 | 3100 | 75 | 64 | 110 | 97.7 | 0.75 | 21.38
DVH102* | 8.5 | 3100 | 75 | 67 | 110 | 103 | 0.62 | 18.62
DVH102* | 8.5 | 3100 | 75 | 70 | 110 | 109 | 0.5 | 16.04
DVH102* | 8.5 | 3100 | 75 | 72 | 110 | 112.8 | 0.42 | 13.96
DVH102* | 8.5 | 3100 | 75 | 57 | 115 | 87.5 | 1 | 25.66
DVH102* | 8.5 | 3100 | 75 | 61 | 115 | 90.8 | 0.88 | 23.34
DVH102* | 8.5 | 3100 | 75 | 64 | 115 | 95.7 | 0.75 | 21.09
DVH102* | 8.5 | 3100 | 75 | 67 | 115 | 100.8 | 0.62 | 18.36
DVH102* | 8.5 | 3100 | 75 | 70 | 115 | 106.7 | 0.51 | 15.84
DVH102* | 8.5 | 3100 | 75 | 72 | 115 | 110.4 | 0.43 | 13.78
DVH102* | 8.5 | 3100 | 80 | 57 | 23 | 110.5 | 1 | 32.4
DVH102* | 8.5 | 3100 | 80 | 61 | 23 | 113.2 | 0.94 | 31.29
DVH102* | 8.5 | 3100 | 80 | 64 | 23 | 119.3 | 0.83 | 28.91
DVH102* | 8.5 | 3100 | 80 | 67 | 23 | 125.7 | 0.7 | 25.87
DVH102* | 8.5 | 3100 | 80 | 70 | 23 | 133.1 | 0.59 | 23.14
DVH102* | 8.5 | 3100 | 80 | 72 | 23 | 137.7 | 0.52 | 20.82
DVH102* | 8.5 | 3100 | 80 | 75 | 23 | 145.5 | 0.42 | 18.09
DVH102* | 8.5 | 3100 | 80 | 57 | 30 | 110.4 | 1 | 32.38
DVH102* | 8.5 | 3100 | 80 | 61 | 30 | 113 | 0.94 | 31.26
DVH102* | 8.5 | 3100 | 80 | 64 | 30 | 119.1 | 0.83 | 28.89
DVH102* | 8.5 | 3100 | 80 | 67 | 30 | 125.5 | 0.7 | 25.84
DVH102* | 8.5 | 3100 | 80 | 70 | 30 | 132.9 | 0.59 | 23.11
DVH102* | 8.5 | 3100 | 80 | 72 | 30 | 137.5 | 0.52 | 20.79
DVH102* | 8.5 | 3100 | 80 | 75 | 30 | 145.3 | 0.42 | 18.06
DVH102* | 8.5 | 3100 | 80 | 57 | 40 | 110.2 | 1 | 32.32
DVH102* | 8.5 | 3100 | 80 | 61 | 40 | 112.8 | 0.94 | 31.2
DVH102* | 8.5 | 3100 | 80 | 64 | 40 | 118.9 | 0.83 | 28.8
DVH102* | 8.5 | 3100 | 80 | 67 | 40 | 125.2 | 0.7 | 25.78
DVH102* | 8.5 | 3100 | 80 | 70 | 40 | 132.6 | 0.59 | 23.08
DVH102* | 8.5 | 3100 | 80 | 72 | 40 | 137.2 | 0.52 | 20.73
DVH102* | 8.5 | 3100 | 80 | 75 | 40 | 145.1 | 0.42 | 18.04
DVH102* | 8.5 | 3100 | 80 | 57 | 50 | 110 | 1 | 32.26
DVH102* | 8.5 | 3100 | 80 | 61 | 50 | 112.5 | 0.94 | 31.11
DVH102* | 8.5 | 3100 | 80 | 64 | 50 | 118.6 | 0.83 | 28.74
DVH102* | 8.5 | 3100 | 80 | 67 | 50 | 124.9 | 0.7 | 25.72
DVH102* | 8.5 | 3100 | 80 | 70 | 50 | 132.3 | 0.59 | 23.02
DVH102* | 8.5 | 3100 | 80 | 72 | 50 | 136.9 | 0.51 | 20.67
DVH102* | 8.5 | 3100 | 80 | 75 | 50 | 144.8 | 0.42 | 18.01
DVH102* | 8.5 | 3100 | 80 | 57 | 54 | 109.9 | 1 | 32.23
DVH102* | 8.5 | 3100 | 80 | 61 | 54 | 112.4 | 0.94 | 31.09
DVH102* | 8.5 | 3100 | 80 | 64 | 54 | 118.5 | 0.83 | 28.71
DVH102* | 8.5 | 3100 | 80 | 67 | 54 | 124.8 | 0.7 | 25.69
DVH102* | 8.5 | 3100 | 80 | 70 | 54 | 132.2 | 0.59 | 22.99
DVH102* | 8.5 | 3100 | 80 | 72 | 54 | 136.8 | 0.52 | 20.67
DVH102* | 8.5 | 3100 | 80 | 75 | 54 | 144.7 | 0.42 | 17.98
DVH102* | 8.5 | 3100 | 80 | 57 | 58 | 109.9 | 1 | 32.23
DVH102* | 8.5 | 3100 | 80 | 61 | 58 | 112.3 | 0.94 | 31.06
DVH102* | 8.5 | 3100 | 80 | 64 | 58 | 118.4 | 0.83 | 28.71
DVH102* | 8.5 | 3100 | 80 | 67 | 58 | 124.7 | 0.7 | 25.66
DVH102* | 8.5 | 3100 | 80 | 70 | 58 | 132.1 | 0.59 | 22.96
DVH102* | 8.5 | 3100 | 80 | 72 | 58 | 136.6 | 0.52 | 20.65
DVH102* | 8.5 | 3100 | 80 | 75 | 58 | 144.6 | 0.42 | 17.98
DVH102* | 8.5 | 3100 | 80 | 57 | 62 | 109.2 | 1 | 32.02
DVH102* | 8.5 | 3100 | 80 | 61 | 62 | 111.6 | 0.95 | 30.94
DVH102* | 8.5 | 3100 | 80 | 64 | 62 | 117.7 | 0.83 | 28.59
DVH102* | 8.5 | 3100 | 80 | 67 | 62 | 123.9 | 0.7 | 25.57
DVH102* | 8.5 | 3100 | 80 | 70 | 62 | 131.3 | 0.59 | 22.87
DVH102* | 8.5 | 3100 | 80 | 72 | 62 | 135.8 | 0.52 | 20.56
DVH102* | 8.5 | 3100 | 80 | 75 | 62 | 143 | 0.42 | 17.8
DVH102* | 8.5 | 3100 | 80 | 57 | 66 | 108 | 1 | 31.67
DVH102* | 8.5 | 3100 | 80 | 61 | 66 | 110 | 0.95 | 30.73
DVH102* | 8.5 | 3100 | 80 | 64 | 66 | 116 | 0.83 | 28.39
DVH102* | 8.5 | 3100 | 80 | 67 | 66 | 122.2 | 0.71 | 25.4
DVH102* | 8.5 | 3100 | 80 | 70 | 66 | 129.4 | 0.6 | 22.73
DVH102* | 8.5 | 3100 | 80 | 72 | 66 | 133.9 | 0.52 | 20.44
DVH102* | 8.5 | 3100 | 80 | 75 | 66 | 141 | 0.43 | 17.6
DVH102* | 8.5 | 3100 | 80 | 57 | 70 | 106.7 | 1 | 31.29
DVH102* | 8.5 | 3100 | 80 | 61 | 70 | 108.5 | 0.96 | 30.5
DVH102* | 8.5 | 3100 | 80 | 64 | 70 | 114.3 | 0.84 | 28.18
DVH102* | 8.5 | 3100 | 80 | 67 | 70 | 120.4 | 0.71 | 25.19
DVH102* | 8.5 | 3100 | 80 | 70 | 70 | 127.6 | 0.6 | 22.55
DVH102* | 8.5 | 3100 | 80 | 72 | 70 | 132 | 0.52 | 20.29
DVH102* | 8.5 | 3100 | 80 | 75 | 70 | 139 | 0.43 | 17.39
DVH102* | 8.5 | 3100 | 80 | 57 | 72 | 106.1 | 1 | 31.11
DVH102* | 8.5 | 3100 | 80 | 61 | 72 | 107.7 | 0.96 | 30.41
DVH102* | 8.5 | 3100 | 80 | 64 | 72 | 113.5 | 0.84 | 28.06
DVH102* | 8.5 | 3100 | 80 | 67 | 72 | 119.5 | 0.72 | 25.1
DVH102* | 8.5 | 3100 | 80 | 70 | 72 | 126.6 | 0.61 | 22.49
DVH102* | 8.5 | 3100 | 80 | 72 | 72 | 131 | 0.53 | 20.21
DVH102* | 8.5 | 3100 | 80 | 75 | 72 | 138.1 | 0.43 | 17.3
DVH102* | 8.5 | 3100 | 80 | 57 | 75 | 105.1 | 1 | 30.82
DVH102* | 8.5 | 3100 | 80 | 61 | 75 | 106.5 | 0.97 | 30.23
DVH102* | 8.5 | 3100 | 80 | 64 | 75 | 112.3 | 0.85 | 27.92
DVH102* | 8.5 | 3100 | 80 | 67 | 75 | 118.2 | 0.72 | 24.96
DVH102* | 8.5 | 3100 | 80 | 70 | 75 | 125.2 | 0.61 | 22.35
DVH102* | 8.5 | 3100 | 80 | 72 | 75 | 129.6 | 0.53 | 20.09
DVH102* | 8.5 | 3100 | 80 | 75 | 75 | 136.6 | 0.43 | 17.16
DVH102* | 8.5 | 3100 | 80 | 57 | 79 | 103.9 | 1 | 30.47
DVH102* | 8.5 | 3100 | 80 | 61 | 79 | 104.9 | 0.98 | 30
DVH102* | 8.5 | 3100 | 80 | 64 | 79 | 110.6 | 0.85 | 27.71
DVH102* | 8.5 | 3100 | 80 | 67 | 79 | 116.5 | 0.73 | 24.78
DVH102* | 8.5 | 3100 | 80 | 70 | 79 | 123.4 | 0.61 | 22.17
DVH102* | 8.5 | 3100 | 80 | 72 | 79 | 127.6 | 0.53 | 19.94
DVH102* | 8.5 | 3100 | 80 | 75 | 79 | 134.6 | 0.43 | 16.95
DVH102* | 8.5 | 3100 | 80 | 57 | 83 | 102.6 | 1 | 30.09
DVH102* | 8.5 | 3100 | 80 | 61 | 83 | 103.3 | 0.98 | 29.74
DVH102* | 8.5 | 3100 | 80 | 64 | 83 | 108.9 | 0.86 | 27.48
DVH102* | 8.5 | 3100 | 80 | 67 | 83 | 114.7 | 0.73 | 24.57
DVH102* | 8.5 | 3100 | 80 | 70 | 83 | 121.5 | 0.62 | 21.99
DVH102* | 8.5 | 3100 | 80 | 72 | 83 | 125.7 | 0.54 | 19.77
DVH102* | 8.5 | 3100 | 80 | 75 | 83 | 132.6 | 0.43 | 16.74
DVH102* | 8.5 | 3100 | 80 | 57 | 87 | 101.4 | 1 | 29.74
DVH102* | 8.5 | 3100 | 80 | 61 | 87 | 101.8 | 0.99 | 29.5
DVH102* | 8.5 | 3100 | 80 | 64 | 87 | 107.3 | 0.87 | 27.24
DVH102* | 8.5 | 3100 | 80 | 67 | 87 | 113 | 0.74 | 24.37
DVH102* | 8.5 | 3100 | 80 | 70 | 87 | 119.7 | 0.62 | 21.82
DVH102* | 8.5 | 3100 | 80 | 72 | 87 | 123.8 | 0.54 | 19.62
DVH102* | 8.5 | 3100 | 80 | 75 | 87 | 130.6 | 0.43 | 16.54
DVH102* | 8.5 | 3100 | 80 | 57 | 91 | 100.1 | 1 | 29.35
DVH102* | 8.5 | 3100 | 80 | 61 | 91 | 100.2 | 1 | 29.24
DVH102* | 8.5 | 3100 | 80 | 64 | 91 | 105.6 | 0.87 | 27.01
DVH102* | 8.5 | 3100 | 80 | 67 | 91 | 111.3 | 0.74 | 24.16
DVH102* | 8.5 | 3100 | 80 | 70 | 91 | 117.8 | 0.63 | 21.64
DVH102* | 8.5 | 3100 | 80 | 72 | 91 | 121.9 | 0.54 | 19.44
DVH102* | 8.5 | 3100 | 80 | 75 | 91 | 128.7 | 0.43 | 16.33
DVH102* | 8.5 | 3100 | 80 | 57 | 93 | 99.5 | 1 | 29.18
DVH102* | 8.5 | 3100 | 80 | 61 | 93 | 99.4 | 1 | 29.12
DVH102* | 8.5 | 3100 | 80 | 64 | 93 | 104.8 | 0.88 | 26.89
DVH102* | 8.5 | 3100 | 80 | 67 | 93 | 110.4 | 0.74 | 24.05
DVH102* | 8.5 | 3100 | 80 | 70 | 93 | 116.9 | 0.63 | 21.52
DVH102* | 8.5 | 3100 | 80 | 72 | 93 | 121 | 0.55 | 19.35
DVH102* | 8.5 | 3100 | 80 | 75 | 93 | 127.7 | 0.43 | 16.25
DVH102* | 8.5 | 3100 | 80 | 57 | 95 | 98.9 | 1 | 29
DVH102* | 8.5 | 3100 | 80 | 61 | 95 | 98.6 | 1 | 28.91
DVH102* | 8.5 | 3100 | 80 | 64 | 95 | 104 | 0.88 | 26.77
DVH102* | 8.5 | 3100 | 80 | 67 | 95 | 109.5 | 0.75 | 23.96
DVH102* | 8.5 | 3100 | 80 | 70 | 95 | 116 | 0.63 | 21.44
DVH102* | 8.5 | 3100 | 80 | 72 | 95 | 120 | 0.55 | 19.27
DVH102* | 8.5 | 3100 | 80 | 75 | 95 | 126.7 | 0.43 | 16.13
DVH102* | 8.5 | 3100 | 80 | 57 | 99 | 97.6 | 1 | 28.62
DVH102* | 8.5 | 3100 | 80 | 61 | 99 | 97.1 | 1 | 28.48
DVH102* | 8.5 | 3100 | 80 | 64 | 99 | 102.3 | 0.88 | 26.54
DVH102* | 8.5 | 3100 | 80 | 67 | 99 | 107.8 | 0.75 | 23.72
DVH102* | 8.5 | 3100 | 80 | 70 | 99 | 114.1 | 0.63 | 21.23
DVH102* | 8.5 | 3100 | 80 | 72 | 99 | 118.1 | 0.55 | 19.09
DVH102* | 8.5 | 3100 | 80 | 75 | 99 | 124.7 | 0.44 | 15.92
DVH102* | 8.5 | 3100 | 80 | 57 | 103 | 96.4 | 1 | 28.27
DVH102* | 8.5 | 3100 | 80 | 61 | 103 | 95.5 | 1 | 28.01
DVH102* | 8.5 | 3100 | 80 | 64 | 103 | 100.7 | 0.89 | 26.28
DVH102* | 8.5 | 3100 | 80 | 67 | 103 | 106 | 0.76 | 23.49
DVH102* | 8.5 | 3100 | 80 | 70 | 103 | 112.3 | 0.64 | 21.03
DVH102* | 8.5 | 3100 | 80 | 72 | 103 | 116.2 | 0.56 | 18.91
DVH102* | 8.5 | 3100 | 80 | 75 | 103 | 122.7 | 0.44 | 15.72
DVH102* | 8.5 | 3100 | 80 | 57 | 106 | 95.4 | 1 | 27.98
DVH102* | 8.5 | 3100 | 80 | 61 | 106 | 94.3 | 1 | 27.65
DVH102* | 8.5 | 3100 | 80 | 64 | 106 | 99.4 | 0.9 | 26.1
DVH102* | 8.5 | 3100 | 80 | 67 | 106 | 104.7 | 0.76 | 23.34
DVH102* | 8.5 | 3100 | 80 | 70 | 106 | 110.9 | 0.64 | 20.88
DVH102* | 8.5 | 3100 | 80 | 72 | 106 | 114.7 | 0.56 | 18.77
DVH102* | 8.5 | 3100 | 80 | 75 | 106 | 121.2 | 0.44 | 15.57
DVH102* | 8.5 | 3100 | 80 | 57 | 110 | 94.2 | 1 | 27.62
DVH102* | 8.5 | 3100 | 80 | 61 | 110 | 92.7 | 1 | 27.18
DVH102* | 8.5 | 3100 | 80 | 64 | 110 | 97.7 | 0.9 | 25.84
DVH102* | 8.5 | 3100 | 80 | 67 | 110 | 103 | 0.77 | 23.11
DVH102* | 8.5 | 3100 | 80 | 70 | 110 | 109 | 0.65 | 20.67
DVH102* | 8.5 | 3100 | 80 | 72 | 110 | 112.8 | 0.56 | 18.59
DVH102* | 8.5 | 3100 | 80 | 75 | 110 | 119.3 | 0.44 | 15.37
DVH102* | 8.5 | 3100 | 80 | 57 | 115 | 92.6 | 1 | 27.16
DVH102* | 8.5 | 3100 | 80 | 61 | 115 | 90.8 | 1 | 26.63
DVH102* | 8.5 | 3100 | 80 | 64 | 115 | 95.7 | 0.91 | 25.48
DVH102* | 8.5 | 3100 | 80 | 67 | 115 | 100.8 | 0.77 | 22.79
DVH102* | 8.5 | 3100 | 80 | 70 | 115 | 106.7 | 0.65 | 20.41
DVH102* | 8.5 | 3100 | 80 | 72 | 115 | 110.4 | 0.57 | 18.33
DVH102* | 8.5 | 3100 | 80 | 75 | 115 | 116.8 | 0.44 | 15.1
DVH102* | 8.5 | 3100 | 85 | 57 | 23 | 116.7 | 1 | 34.22
DVH102* | 8.5 | 3100 | 85 | 61 | 23 | 119.6 | 0.94 | 33.08
DVH102* | 8.5 | 3100 | 85 | 64 | 23 | 119.3 | 0.94 | 33.02
DVH102* | 8.5 | 3100 | 85 | 67 | 23 | 125.7 | 0.84 | 30.79
DVH102* | 8.5 | 3100 | 85 | 70 | 23 | 133.1 | 0.72 | 28.21
DVH102* | 8.5 | 3100 | 85 | 72 | 23 | 137.7 | 0.64 | 25.84
DVH102* | 8.5 | 3100 | 85 | 75 | 23 | 145.5 | 0.55 | 23.28
DVH102* | 8.5 | 3100 | 85 | 57 | 30 | 116.6 | 1 | 34.19
DVH102* | 8.5 | 3100 | 85 | 61 | 30 | 119.4 | 0.94 | 33.02
DVH102* | 8.5 | 3100 | 85 | 64 | 30 | 119.1 | 0.94 | 32.99
DVH102* | 8.5 | 3100 | 85 | 67 | 30 | 125.5 | 0.84 | 30.76
DVH102* | 8.5 | 3100 | 85 | 70 | 30 | 132.9 | 0.72 | 28.18
DVH102* | 8.5 | 3100 | 85 | 72 | 30 | 137.5 | 0.64 | 25.81
DVH102* | 8.5 | 3100 | 85 | 75 | 30 | 145.3 | 0.55 | 23.26
DVH102* | 8.5 | 3100 | 85 | 57 | 40 | 116.4 | 1 | 34.13
DVH102* | 8.5 | 3100 | 85 | 61 | 40 | 119.1 | 0.94 | 32.96
DVH102* | 8.5 | 3100 | 85 | 64 | 40 | 118.9 | 0.94 | 32.9
DVH102* | 8.5 | 3100 | 85 | 67 | 40 | 125.2 | 0.84 | 30.67
DVH102* | 8.5 | 3100 | 85 | 70 | 40 | 132.6 | 0.72 | 28.12
DVH102* | 8.5 | 3100 | 85 | 72 | 40 | 137.2 | 0.64 | 25.75
DVH102* | 8.5 | 3100 | 85 | 75 | 40 | 145.1 | 0.55 | 23.2
DVH102* | 8.5 | 3100 | 85 | 57 | 50 | 116.2 | 1 | 34.08
DVH102* | 8.5 | 3100 | 85 | 61 | 50 | 118.9 | 0.94 | 32.87
DVH102* | 8.5 | 3100 | 85 | 64 | 50 | 118.6 | 0.94 | 32.84
DVH102* | 8.5 | 3100 | 85 | 67 | 50 | 124.9 | 0.84 | 30.62
DVH102* | 8.5 | 3100 | 85 | 70 | 50 | 132.3 | 0.72 | 28.04
DVH102* | 8.5 | 3100 | 85 | 72 | 50 | 136.9 | 0.64 | 25.69
DVH102* | 8.5 | 3100 | 85 | 75 | 50 | 144.8 | 0.55 | 23.17
DVH102* | 8.5 | 3100 | 85 | 57 | 54 | 116.1 | 1 | 34.05
DVH102* | 8.5 | 3100 | 85 | 61 | 54 | 118.8 | 0.94 | 32.84
DVH102* | 8.5 | 3100 | 85 | 64 | 54 | 118.5 | 0.94 | 32.82
DVH102* | 8.5 | 3100 | 85 | 67 | 54 | 124.8 | 0.84 | 30.59
DVH102* | 8.5 | 3100 | 85 | 70 | 54 | 132.2 | 0.72 | 28.04
DVH102* | 8.5 | 3100 | 85 | 72 | 54 | 136.8 | 0.64 | 25.66
DVH102* | 8.5 | 3100 | 85 | 75 | 54 | 144.7 | 0.55 | 23.17
DVH102* | 8.5 | 3100 | 85 | 57 | 58 | 116.1 | 1 | 34.05
DVH102* | 8.5 | 3100 | 85 | 61 | 58 | 118.7 | 0.94 | 32.82
DVH102* | 8.5 | 3100 | 85 | 64 | 58 | 118.4 | 0.94 | 32.79
DVH102* | 8.5 | 3100 | 85 | 67 | 58 | 124.7 | 0.84 | 30.56
DVH102* | 8.5 | 3100 | 85 | 70 | 58 | 132.1 | 0.72 | 28.01
DVH102* | 8.5 | 3100 | 85 | 72 | 58 | 136.6 | 0.64 | 25.63
DVH102* | 8.5 | 3100 | 85 | 75 | 58 | 144.6 | 0.55 | 23.14
DVH102* | 8.5 | 3100 | 85 | 57 | 62 | 115.4 | 1 | 33.84
DVH102* | 8.5 | 3100 | 85 | 61 | 62 | 117.9 | 0.95 | 32.7
DVH102* | 8.5 | 3100 | 85 | 64 | 62 | 117.7 | 0.95 | 32.64
DVH102* | 8.5 | 3100 | 85 | 67 | 62 | 123.9 | 0.84 | 30.44
DVH102* | 8.5 | 3100 | 85 | 70 | 62 | 131.3 | 0.72 | 27.89
DVH102* | 8.5 | 3100 | 85 | 72 | 62 | 135.8 | 0.64 | 25.54
DVH102* | 8.5 | 3100 | 85 | 75 | 62 | 143 | 0.55 | 22.9
DVH102* | 8.5 | 3100 | 85 | 57 | 66 | 114.1 | 1 | 33.46
DVH102* | 8.5 | 3100 | 85 | 61 | 66 | 116.2 | 0.95 | 32.46
DVH102* | 8.5 | 3100 | 85 | 64 | 66 | 116 | 0.95 | 32.43
DVH102* | 8.5 | 3100 | 85 | 67 | 66 | 122.2 | 0.84 | 30.23
DVH102* | 8.5 | 3100 | 85 | 70 | 66 | 129.4 | 0.73 | 27.68
DVH102* | 8.5 | 3100 | 85 | 72 | 66 | 133.9 | 0.65 | 25.37
DVH102* | 8.5 | 3100 | 85 | 75 | 66 | 141 | 0.55 | 22.64
DVH102* | 8.5 | 3100 | 85 | 57 | 70 | 112.7 | 1 | 33.05
DVH102* | 8.5 | 3100 | 85 | 61 | 70 | 114.6 | 0.96 | 32.23
DVH102* | 8.5 | 3100 | 85 | 64 | 70 | 114.3 | 0.96 | 32.2
DVH102* | 8.5 | 3100 | 85 | 67 | 70 | 120.4 | 0.85 | 30.03
DVH102* | 8.5 | 3100 | 85 | 70 | 70 | 127.6 | 0.74 | 27.51
DVH102* | 8.5 | 3100 | 85 | 72 | 70 | 132 | 0.65 | 25.19
DVH102* | 8.5 | 3100 | 85 | 75 | 70 | 139 | 0.55 | 22.4
DVH102* | 8.5 | 3100 | 85 | 57 | 72 | 112.1 | 1 | 32.87
DVH102* | 8.5 | 3100 | 85 | 61 | 72 | 113.8 | 0.96 | 32.11
DVH102* | 8.5 | 3100 | 85 | 64 | 72 | 113.5 | 0.96 | 32.08
DVH102* | 8.5 | 3100 | 85 | 67 | 72 | 119.5 | 0.85 | 29.91
DVH102* | 8.5 | 3100 | 85 | 70 | 72 | 126.6 | 0.74 | 27.39
DVH102* | 8.5 | 3100 | 85 | 72 | 72 | 131 | 0.65 | 25.1
DVH102* | 8.5 | 3100 | 85 | 75 | 72 | 138.1 | 0.55 | 22.26
DVH102* | 8.5 | 3100 | 85 | 57 | 75 | 111.1 | 1 | 32.58
DVH102* | 8.5 | 3100 | 85 | 61 | 75 | 112.5 | 0.97 | 31.94
DVH102* | 8.5 | 3100 | 85 | 64 | 75 | 112.3 | 0.97 | 31.91
DVH102* | 8.5 | 3100 | 85 | 67 | 75 | 118.2 | 0.86 | 29.74
DVH102* | 8.5 | 3100 | 85 | 70 | 75 | 125.2 | 0.74 | 27.24
DVH102* | 8.5 | 3100 | 85 | 72 | 75 | 129.6 | 0.66 | 24.96
DVH102* | 8.5 | 3100 | 85 | 75 | 75 | 136.6 | 0.55 | 22.08
DVH102* | 8.5 | 3100 | 85 | 57 | 79 | 109.8 | 1 | 32.2
DVH102* | 8.5 | 3100 | 85 | 61 | 79 | 110.8 | 0.97 | 31.67
DVH102* | 8.5 | 3100 | 85 | 64 | 79 | 110.6 | 0.98 | 31.64
DVH102* | 8.5 | 3100 | 85 | 67 | 79 | 116.5 | 0.86 | 29.5
DVH102* | 8.5 | 3100 | 85 | 70 | 79 | 123.4 | 0.75 | 27.04
DVH102* | 8.5 | 3100 | 85 | 72 | 79 | 127.6 | 0.66 | 24.75
DVH102* | 8.5 | 3100 | 85 | 75 | 79 | 134.6 | 0.55 | 21.82
DVH102* | 8.5 | 3100 | 85 | 57 | 83 | 108.4 | 1 | 31.79
DVH102* | 8.5 | 3100 | 85 | 61 | 83 | 109.2 | 0.98 | 31.44
DVH102* | 8.5 | 3100 | 85 | 64 | 83 | 108.9 | 0.98 | 31.38
DVH102* | 8.5 | 3100 | 85 | 67 | 83 | 114.7 | 0.87 | 29.27
DVH102* | 8.5 | 3100 | 85 | 70 | 83 | 121.5 | 0.75 | 26.8
DVH102* | 8.5 | 3100 | 85 | 72 | 83 | 125.7 | 0.67 | 24.55
DVH102* | 8.5 | 3100 | 85 | 75 | 83 | 132.6 | 0.55 | 21.55
DVH102* | 8.5 | 3100 | 85 | 57 | 87 | 107.1 | 1 | 31.41
DVH102* | 8.5 | 3100 | 85 | 61 | 87 | 107.5 | 0.99 | 31.17
DVH102* | 8.5 | 3100 | 85 | 64 | 87 | 107.3 | 0.99 | 31.14
DVH102* | 8.5 | 3100 | 85 | 67 | 87 | 113 | 0.88 | 29.03
DVH102* | 8.5 | 3100 | 85 | 70 | 87 | 119.7 | 0.76 | 26.6
DVH102* | 8.5 | 3100 | 85 | 72 | 87 | 123.8 | 0.67 | 24.34
DVH102* | 8.5 | 3100 | 85 | 75 | 87 | 130.6 | 0.56 | 21.29
DVH102* | 8.5 | 3100 | 85 | 57 | 91 | 105.8 | 1 | 31.03
DVH102* | 8.5 | 3100 | 85 | 61 | 91 | 105.9 | 1 | 30.91
DVH102* | 8.5 | 3100 | 85 | 64 | 91 | 105.6 | 1 | 30.85
DVH102* | 8.5 | 3100 | 85 | 67 | 91 | 111.3 | 0.88 | 28.77
DVH102* | 8.5 | 3100 | 85 | 70 | 91 | 117.8 | 0.76 | 26.36
DVH102* | 8.5 | 3100 | 85 | 72 | 91 | 121.9 | 0.68 | 24.13
DVH102* | 8.5 | 3100 | 85 | 75 | 91 | 128.7 | 0.56 | 21.03
DVH102* | 8.5 | 3100 | 85 | 57 | 93 | 105.1 | 1 | 30.82
DVH102* | 8.5 | 3100 | 85 | 61 | 93 | 105 | 1 | 30.76
DVH102* | 8.5 | 3100 | 85 | 64 | 93 | 104.8 | 1 | 30.73
DVH102* | 8.5 | 3100 | 85 | 67 | 93 | 110.4 | 0.88 | 28.65
DVH102* | 8.5 | 3100 | 85 | 70 | 93 | 116.9 | 0.77 | 26.25
DVH102* | 8.5 | 3100 | 85 | 72 | 93 | 121 | 0.68 | 24.05
DVH102* | 8.5 | 3100 | 85 | 75 | 93 | 127.7 | 0.56 | 20.91
DVH102* | 8.5 | 3100 | 85 | 57 | 95 | 104.5 | 1 | 30.65
DVH102* | 8.5 | 3100 | 85 | 61 | 95 | 104.2 | 1 | 30.56
DVH102* | 8.5 | 3100 | 85 | 64 | 95 | 104 | 1 | 30.5
DVH102* | 8.5 | 3100 | 85 | 67 | 95 | 109.5 | 0.89 | 28.53
DVH102* | 8.5 | 3100 | 85 | 70 | 95 | 116 | 0.77 | 26.13
DVH102* | 8.5 | 3100 | 85 | 72 | 95 | 120 | 0.68 | 23.93
DVH102* | 8.5 | 3100 | 85 | 75 | 95 | 126.7 | 0.56 | 20.76
DVH102* | 8.5 | 3100 | 85 | 57 | 99 | 103.1 | 1 | 30.23
DVH102* | 8.5 | 3100 | 85 | 61 | 99 | 102.5 | 1 | 30.06
DVH102* | 8.5 | 3100 | 85 | 64 | 99 | 102.3 | 1 | 30
DVH102* | 8.5 | 3100 | 85 | 67 | 99 | 107.8 | 0.89 | 28.27
DVH102* | 8.5 | 3100 | 85 | 70 | 99 | 114.1 | 0.77 | 25.89
DVH102* | 8.5 | 3100 | 85 | 72 | 99 | 118.1 | 0.68 | 23.7
DVH102* | 8.5 | 3100 | 85 | 75 | 99 | 124.7 | 0.56 | 20.5
DVH102* | 8.5 | 3100 | 85 | 57 | 103 | 101.8 | 1 | 29.85
DVH102* | 8.5 | 3100 | 85 | 61 | 103 | 100.9 | 1 | 29.59
DVH102* | 8.5 | 3100 | 85 | 64 | 103 | 100.7 | 1 | 29.53
DVH102* | 8.5 | 3100 | 85 | 67 | 103 | 106 | 0.9 | 28.01
DVH102* | 8.5 | 3100 | 85 | 70 | 103 | 112.3 | 0.78 | 25.63
DVH102* | 8.5 | 3100 | 85 | 72 | 103 | 116.2 | 0.69 | 23.49
DVH102* | 8.5 | 3100 | 85 | 75 | 103 | 122.7 | 0.56 | 20.23
DVH102* | 8.5 | 3100 | 85 | 57 | 106 | 100.8 | 1 | 29.56
DVH102* | 8.5 | 3100 | 85 | 61 | 106 | 99.6 | 1 | 29.21
DVH102* | 8.5 | 3100 | 85 | 64 | 106 | 99.4 | 1 | 29.15
DVH102* | 8.5 | 3100 | 85 | 67 | 106 | 104.7 | 0.9 | 27.77
DVH102* | 8.5 | 3100 | 85 | 70 | 106 | 110.9 | 0.78 | 25.45
DVH102* | 8.5 | 3100 | 85 | 72 | 106 | 114.7 | 0.69 | 23.31
DVH102* | 8.5 | 3100 | 85 | 75 | 106 | 121.2 | 0.56 | 20.03
DVH102* | 8.5 | 3100 | 85 | 57 | 110 | 99.5 | 1 | 29.18
DVH102* | 8.5 | 3100 | 85 | 61 | 110 | 98 | 1 | 28.74
DVH102* | 8.5 | 3100 | 85 | 64 | 110 | 97.7 | 1 | 28.65
DVH102* | 8.5 | 3100 | 85 | 67 | 110 | 103 | 0.91 | 27.51
DVH102* | 8.5 | 3100 | 85 | 70 | 110 | 109 | 0.79 | 25.19
DVH102* | 8.5 | 3100 | 85 | 72 | 110 | 112.8 | 0.7 | 23.08
DVH102* | 8.5 | 3100 | 85 | 75 | 110 | 119.3 | 0.56 | 19.77
DVH102* | 8.5 | 3100 | 85 | 57 | 115 | 97.8 | 1 | 28.68
DVH102* | 8.5 | 3100 | 85 | 61 | 115 | 95.9 | 1 | 28.12
DVH102* | 8.5 | 3100 | 85 | 64 | 115 | 95.7 | 1 | 28.06
DVH102* | 8.5 | 3100 | 85 | 67 | 115 | 100.8 | 0.92 | 27.16
DVH102* | 8.5 | 3100 | 85 | 70 | 115 | 106.7 | 0.79 | 24.87
DVH102* | 8.5 | 3100 | 85 | 72 | 115 | 110.4 | 0.7 | 22.79
DVH102* | 8.5 | 3100 | 85 | 75 | 115 | 116.8 | 0.57 | 19.41
DVH102* | 8.5 | 3500 | 70 | 57 | 23 | 103.8 | 0.9 | 24.16
DVH102* | 8.5 | 3500 | 70 | 61 | 23 | 115.3 | 0.68 | 20.29
DVH102* | 8.5 | 3500 | 70 | 64 | 23 | 121.6 | 0.55 | 17.35
DVH102* | 8.5 | 3500 | 70 | 67 | 23 | 128 | 0.43 | 14.42
DVH102* | 8.5 | 3500 | 70 | 57 | 30 | 103.7 | 0.9 | 24.13
DVH102* | 8.5 | 3500 | 70 | 61 | 30 | 115.1 | 0.68 | 20.26
DVH102* | 8.5 | 3500 | 70 | 64 | 30 | 121.4 | 0.55 | 17.32
DVH102* | 8.5 | 3500 | 70 | 67 | 30 | 127.8 | 0.43 | 14.39
DVH102* | 8.5 | 3500 | 70 | 57 | 40 | 103.5 | 0.9 | 24.08
DVH102* | 8.5 | 3500 | 70 | 61 | 40 | 114.9 | 0.68 | 20.21
DVH102* | 8.5 | 3500 | 70 | 64 | 40 | 121.1 | 0.55 | 17.27
DVH102* | 8.5 | 3500 | 70 | 67 | 40 | 127.6 | 0.43 | 14.36
DVH102* | 8.5 | 3500 | 70 | 57 | 50 | 103.3 | 0.9 | 24.05
DVH102* | 8.5 | 3500 | 70 | 61 | 50 | 114.6 | 0.68 | 20.16
DVH102* | 8.5 | 3500 | 70 | 64 | 50 | 120.8 | 0.55 | 17.25
DVH102* | 8.5 | 3500 | 70 | 67 | 50 | 127.3 | 0.43 | 14.34
DVH102* | 8.5 | 3500 | 70 | 57 | 54 | 103.3 | 0.9 | 24.03
DVH102* | 8.5 | 3500 | 70 | 61 | 54 | 114.5 | 0.68 | 20.16
DVH102* | 8.5 | 3500 | 70 | 64 | 54 | 120.7 | 0.55 | 17.22
DVH102* | 8.5 | 3500 | 70 | 67 | 54 | 127.2 | 0.43 | 14.31
DVH102* | 8.5 | 3500 | 70 | 57 | 58 | 103.2 | 0.9 | 24.03
DVH102* | 8.5 | 3500 | 70 | 61 | 58 | 114.4 | 0.68 | 20.13
DVH102* | 8.5 | 3500 | 70 | 64 | 58 | 120.6 | 0.55 | 17.22
DVH102* | 8.5 | 3500 | 70 | 67 | 58 | 127.1 | 0.43 | 14.31
DVH102* | 8.5 | 3500 | 70 | 57 | 62 | 102.6 | 0.9 | 23.9
DVH102* | 8.5 | 3500 | 70 | 61 | 62 | 113.7 | 0.68 | 20.05
DVH102* | 8.5 | 3500 | 70 | 64 | 62 | 119.9 | 0.55 | 17.14
DVH102* | 8.5 | 3500 | 70 | 67 | 62 | 126.3 | 0.43 | 14.26
DVH102* | 8.5 | 3500 | 70 | 57 | 66 | 101.4 | 0.9 | 23.69
DVH102* | 8.5 | 3500 | 70 | 61 | 66 | 112.1 | 0.68 | 19.9
DVH102* | 8.5 | 3500 | 70 | 64 | 66 | 118.2 | 0.55 | 17.04
DVH102* | 8.5 | 3500 | 70 | 67 | 66 | 124.5 | 0.44 | 14.16
DVH102* | 8.5 | 3500 | 70 | 57 | 70 | 100.3 | 0.9 | 23.48
DVH102* | 8.5 | 3500 | 70 | 61 | 70 | 110.5 | 0.69 | 19.77
DVH102* | 8.5 | 3500 | 70 | 64 | 70 | 116.5 | 0.56 | 16.91
DVH102* | 8.5 | 3500 | 70 | 67 | 70 | 122.7 | 0.44 | 14.05
DVH102* | 8.5 | 3500 | 70 | 57 | 72 | 99.7 | 0.9 | 23.38
DVH102* | 8.5 | 3500 | 70 | 61 | 72 | 109.7 | 0.69 | 19.69
DVH102* | 8.5 | 3500 | 70 | 64 | 72 | 115.7 | 0.56 | 16.83
DVH102* | 8.5 | 3500 | 70 | 67 | 72 | 121.8 | 0.44 | 14
DVH102* | 8.5 | 3500 | 70 | 57 | 75 | 98.8 | 0.9 | 23.22
DVH102* | 8.5 | 3500 | 70 | 61 | 75 | 108.5 | 0.69 | 19.58
DVH102* | 8.5 | 3500 | 70 | 64 | 75 | 114.4 | 0.56 | 16.75
DVH102* | 8.5 | 3500 | 70 | 67 | 75 | 120.5 | 0.44 | 13.92
DVH102* | 8.5 | 3500 | 70 | 57 | 79 | 97.6 | 0.91 | 23.01
DVH102* | 8.5 | 3500 | 70 | 61 | 79 | 106.9 | 0.7 | 19.43
DVH102* | 8.5 | 3500 | 70 | 64 | 79 | 112.7 | 0.57 | 16.62
DVH102* | 8.5 | 3500 | 70 | 67 | 79 | 118.7 | 0.45 | 13.82
DVH102* | 8.5 | 3500 | 70 | 57 | 83 | 96.4 | 0.91 | 22.81
DVH102* | 8.5 | 3500 | 70 | 61 | 83 | 105.3 | 0.7 | 19.27
DVH102* | 8.5 | 3500 | 70 | 64 | 83 | 111 | 0.57 | 16.49
DVH102* | 8.5 | 3500 | 70 | 67 | 83 | 116.9 | 0.45 | 13.69
DVH102* | 8.5 | 3500 | 70 | 57 | 87 | 95.2 | 0.91 | 22.6
DVH102* | 8.5 | 3500 | 70 | 61 | 87 | 103.7 | 0.71 | 19.12
DVH102* | 8.5 | 3500 | 70 | 64 | 87 | 109.3 | 0.58 | 16.34
DVH102* | 8.5 | 3500 | 70 | 67 | 87 | 115.1 | 0.45 | 13.58
DVH102* | 8.5 | 3500 | 70 | 57 | 91 | 94.1 | 0.91 | 22.36
DVH102* | 8.5 | 3500 | 70 | 61 | 91 | 102.1 | 0.71 | 18.96
DVH102* | 8.5 | 3500 | 70 | 64 | 91 | 107.6 | 0.58 | 16.21
DVH102* | 8.5 | 3500 | 70 | 67 | 91 | 113.4 | 0.46 | 13.48
DVH102* | 8.5 | 3500 | 70 | 57 | 93 | 93.5 | 0.92 | 22.26
DVH102* | 8.5 | 3500 | 70 | 61 | 93 | 101.3 | 0.72 | 18.86
DVH102* | 8.5 | 3500 | 70 | 64 | 93 | 106.8 | 0.58 | 16.13
DVH102* | 8.5 | 3500 | 70 | 67 | 93 | 112.5 | 0.46 | 13.4
DVH102* | 8.5 | 3500 | 70 | 57 | 95 | 92.9 | 0.92 | 22.16
DVH102* | 8.5 | 3500 | 70 | 61 | 95 | 100.5 | 0.72 | 18.73
DVH102* | 8.5 | 3500 | 70 | 64 | 95 | 105.9 | 0.58 | 16.05
DVH102* | 8.5 | 3500 | 70 | 67 | 95 | 111.6 | 0.46 | 13.35
DVH102* | 8.5 | 3500 | 70 | 57 | 99 | 91.7 | 0.92 | 21.95
DVH102* | 8.5 | 3500 | 70 | 61 | 99 | 98.9 | 0.72 | 18.49
DVH102* | 8.5 | 3500 | 70 | 64 | 99 | 104.2 | 0.59 | 15.92
DVH102* | 8.5 | 3500 | 70 | 67 | 99 | 109.8 | 0.46 | 13.22
DVH102* | 8.5 | 3500 | 70 | 57 | 103 | 90.5 | 0.92 | 21.71
DVH102* | 8.5 | 3500 | 70 | 61 | 103 | 97.3 | 0.72 | 18.23
DVH102* | 8.5 | 3500 | 70 | 64 | 103 | 102.6 | 0.59 | 15.77
DVH102* | 8.5 | 3500 | 70 | 67 | 103 | 108 | 0.47 | 13.09
DVH102* | 8.5 | 3500 | 70 | 57 | 106 | 89.6 | 0.93 | 21.56
DVH102* | 8.5 | 3500 | 70 | 61 | 106 | 96.1 | 0.72 | 18.05
DVH102* | 8.5 | 3500 | 70 | 64 | 106 | 101.3 | 0.59 | 15.64
DVH102* | 8.5 | 3500 | 70 | 67 | 106 | 106.7 | 0.47 | 13.01
DVH102* | 8.5 | 3500 | 70 | 57 | 110 | 88.5 | 0.93 | 21.32
DVH102* | 8.5 | 3500 | 70 | 61 | 110 | 94.5 | 0.73 | 17.82
DVH102* | 8.5 | 3500 | 70 | 64 | 110 | 99.6 | 0.6 | 15.48
DVH102* | 8.5 | 3500 | 70 | 67 | 110 | 104.9 | 0.47 | 12.88
DVH102* | 8.5 | 3500 | 70 | 57 | 115 | 87 | 0.93 | 21.04
DVH102* | 8.5 | 3500 | 70 | 61 | 115 | 92.5 | 0.73 | 17.48
DVH102* | 8.5 | 3500 | 70 | 64 | 115 | 97.5 | 0.6 | 15.3
DVH102* | 8.5 | 3500 | 70 | 67 | 115 | 102.7 | 0.48 | 12.7
DVH102* | 8.5 | 3500 | 75 | 57 | 23 | 106.3 | 1 | 27.61
DVH102* | 8.5 | 3500 | 75 | 61 | 23 | 115.3 | 0.83 | 24.94
DVH102* | 8.5 | 3500 | 75 | 64 | 23 | 121.6 | 0.7 | 22.03
DVH102* | 8.5 | 3500 | 75 | 67 | 23 | 128 | 0.58 | 19.19
DVH102* | 8.5 | 3500 | 75 | 70 | 23 | 135.6 | 0.47 | 16.55
DVH102* | 8.5 | 3500 | 75 | 72 | 23 | 140.3 | 0.39 | 14.39
DVH102* | 8.5 | 3500 | 75 | 57 | 30 | 106.2 | 1 | 27.58
DVH102* | 8.5 | 3500 | 75 | 61 | 30 | 115.1 | 0.83 | 24.88
DVH102* | 8.5 | 3500 | 75 | 64 | 30 | 121.4 | 0.7 | 22
DVH102* | 8.5 | 3500 | 75 | 67 | 30 | 127.8 | 0.58 | 19.17
DVH102* | 8.5 | 3500 | 75 | 70 | 30 | 135.4 | 0.47 | 16.52
DVH102* | 8.5 | 3500 | 75 | 72 | 30 | 140.1 | 0.39 | 14.36
DVH102* | 8.5 | 3500 | 75 | 57 | 40 | 106 | 1 | 27.53
DVH102* | 8.5 | 3500 | 75 | 61 | 40 | 114.9 | 0.83 | 24.83
DVH102* | 8.5 | 3500 | 75 | 64 | 40 | 121.1 | 0.7 | 21.95
DVH102* | 8.5 | 3500 | 75 | 67 | 40 | 127.6 | 0.58 | 19.12
DVH102* | 8.5 | 3500 | 75 | 70 | 40 | 135.1 | 0.47 | 16.47
DVH102* | 8.5 | 3500 | 75 | 72 | 40 | 139.8 | 0.39 | 14.34
DVH102* | 8.5 | 3500 | 75 | 57 | 50 | 105.8 | 1 | 27.48
DVH102* | 8.5 | 3500 | 75 | 61 | 50 | 114.6 | 0.83 | 24.78
DVH102* | 8.5 | 3500 | 75 | 64 | 50 | 120.8 | 0.7 | 21.9
DVH102* | 8.5 | 3500 | 75 | 67 | 50 | 127.3 | 0.58 | 19.06
DVH102* | 8.5 | 3500 | 75 | 70 | 50 | 134.8 | 0.47 | 16.44
DVH102* | 8.5 | 3500 | 75 | 72 | 50 | 139.5 | 0.39 | 14.31
DVH102* | 8.5 | 3500 | 75 | 57 | 54 | 105.8 | 1 | 27.48
DVH102* | 8.5 | 3500 | 75 | 61 | 54 | 114.5 | 0.83 | 24.75
DVH102* | 8.5 | 3500 | 75 | 64 | 54 | 120.7 | 0.7 | 21.9
DVH102* | 8.5 | 3500 | 75 | 67 | 54 | 127.2 | 0.58 | 19.06
DVH102* | 8.5 | 3500 | 75 | 70 | 54 | 134.7 | 0.47 | 16.42
DVH102* | 8.5 | 3500 | 75 | 72 | 54 | 139.4 | 0.39 | 14.29
DVH102* | 8.5 | 3500 | 75 | 57 | 58 | 105.7 | 1 | 27.45
DVH102* | 8.5 | 3500 | 75 | 61 | 58 | 114.4 | 0.83 | 24.73
DVH102* | 8.5 | 3500 | 75 | 64 | 58 | 120.6 | 0.7 | 21.87
DVH102* | 8.5 | 3500 | 75 | 67 | 58 | 127.1 | 0.58 | 19.04
DVH102* | 8.5 | 3500 | 75 | 70 | 58 | 134.6 | 0.47 | 16.42
DVH102* | 8.5 | 3500 | 75 | 72 | 58 | 139.2 | 0.4 | 14.29
DVH102* | 8.5 | 3500 | 75 | 57 | 62 | 105.1 | 1 | 27.3
DVH102* | 8.5 | 3500 | 75 | 61 | 62 | 113.7 | 0.83 | 24.65
DVH102* | 8.5 | 3500 | 75 | 64 | 62 | 119.9 | 0.7 | 21.79
DVH102* | 8.5 | 3500 | 75 | 67 | 62 | 126.3 | 0.58 | 18.96
DVH102* | 8.5 | 3500 | 75 | 70 | 62 | 133.7 | 0.47 | 16.34
DVH102* | 8.5 | 3500 | 75 | 72 | 62 | 138.4 | 0.4 | 14.23
DVH102* | 8.5 | 3500 | 75 | 57 | 66 | 103.9 | 1 | 26.99
DVH102* | 8.5 | 3500 | 75 | 61 | 66 | 112.1 | 0.84 | 24.47
DVH102* | 8.5 | 3500 | 75 | 64 | 66 | 118.2 | 0.7 | 21.64
DVH102* | 8.5 | 3500 | 75 | 67 | 66 | 124.5 | 0.58 | 18.83
DVH102* | 8.5 | 3500 | 75 | 70 | 66 | 131.8 | 0.47 | 16.23
DVH102* | 8.5 | 3500 | 75 | 72 | 66 | 136.4 | 0.4 | 14.13
DVH102* | 8.5 | 3500 | 75 | 57 | 70 | 102.7 | 1 | 26.68
DVH102* | 8.5 | 3500 | 75 | 61 | 70 | 110.5 | 0.85 | 24.29
DVH102* | 8.5 | 3500 | 75 | 64 | 70 | 116.5 | 0.71 | 21.48
DVH102* | 8.5 | 3500 | 75 | 67 | 70 | 122.7 | 0.59 | 18.7
DVH102* | 8.5 | 3500 | 75 | 70 | 70 | 130 | 0.48 | 16.13
DVH102* | 8.5 | 3500 | 75 | 72 | 70 | 134.5 | 0.4 | 14.03
DVH102* | 8.5 | 3500 | 75 | 57 | 72 | 102.1 | 1 | 26.52
DVH102* | 8.5 | 3500 | 75 | 61 | 72 | 109.7 | 0.85 | 24.21
DVH102* | 8.5 | 3500 | 75 | 64 | 72 | 115.7 | 0.71 | 21.4
DVH102* | 8.5 | 3500 | 75 | 67 | 72 | 121.8 | 0.59 | 18.62
DVH102* | 8.5 | 3500 | 75 | 70 | 72 | 129 | 0.48 | 16.05
DVH102* | 8.5 | 3500 | 75 | 72 | 72 | 133.5 | 0.4 | 13.97
DVH102* | 8.5 | 3500 | 75 | 57 | 75 | 101.2 | 1 | 26.29
DVH102* | 8.5 | 3500 | 75 | 61 | 75 | 108.5 | 0.85 | 24.05
DVH102* | 8.5 | 3500 | 75 | 64 | 75 | 114.4 | 0.72 | 21.27
DVH102* | 8.5 | 3500 | 75 | 67 | 75 | 120.5 | 0.59 | 18.52
DVH102* | 8.5 | 3500 | 75 | 70 | 75 | 127.6 | 0.48 | 15.97
DVH102* | 8.5 | 3500 | 75 | 72 | 75 | 132 | 0.41 | 13.9
DVH102* | 8.5 | 3500 | 75 | 57 | 79 | 100 | 1 | 25.97
DVH102* | 8.5 | 3500 | 75 | 61 | 79 | 106.9 | 0.86 | 23.87
DVH102* | 8.5 | 3500 | 75 | 64 | 79 | 112.7 | 0.72 | 21.12
DVH102* | 8.5 | 3500 | 75 | 67 | 79 | 118.7 | 0.6 | 18.39
DVH102* | 8.5 | 3500 | 75 | 70 | 79 | 125.7 | 0.49 | 15.84
DVH102* | 8.5 | 3500 | 75 | 72 | 79 | 130.1 | 0.41 | 13.79
DVH102* | 8.5 | 3500 | 75 | 57 | 83 | 98.8 | 1 | 25.66
DVH102* | 8.5 | 3500 | 75 | 61 | 83 | 105.3 | 0.87 | 23.69
DVH102* | 8.5 | 3500 | 75 | 64 | 83 | 111 | 0.73 | 20.94
DVH102* | 8.5 | 3500 | 75 | 67 | 83 | 116.9 | 0.6 | 18.23
DVH102* | 8.5 | 3500 | 75 | 70 | 83 | 123.8 | 0.49 | 15.71
DVH102* | 8.5 | 3500 | 75 | 72 | 83 | 128.1 | 0.41 | 13.66
DVH102* | 8.5 | 3500 | 75 | 57 | 87 | 97.6 | 1 | 25.35
DVH102* | 8.5 | 3500 | 75 | 61 | 87 | 103.7 | 0.87 | 23.48
DVH102* | 8.5 | 3500 | 75 | 64 | 87 | 109.3 | 0.73 | 20.75
DVH102* | 8.5 | 3500 | 75 | 67 | 87 | 115.1 | 0.6 | 18.08
DVH102* | 8.5 | 3500 | 75 | 70 | 87 | 122 | 0.49 | 15.58
DVH102* | 8.5 | 3500 | 75 | 72 | 87 | 126.2 | 0.41 | 13.56
DVH102* | 8.5 | 3500 | 75 | 57 | 91 | 96.4 | 1 | 25.04
DVH102* | 8.5 | 3500 | 75 | 61 | 91 | 102.1 | 0.88 | 23.3
DVH102* | 8.5 | 3500 | 75 | 64 | 91 | 107.6 | 0.74 | 20.6
DVH102* | 8.5 | 3500 | 75 | 67 | 91 | 113.4 | 0.61 | 17.92
DVH102* | 8.5 | 3500 | 75 | 70 | 91 | 120.1 | 0.5 | 15.45
DVH102* | 8.5 | 3500 | 75 | 72 | 91 | 124.2 | 0.42 | 13.45
DVH102* | 8.5 | 3500 | 75 | 57 | 93 | 95.7 | 1 | 24.86
DVH102* | 8.5 | 3500 | 75 | 61 | 93 | 101.3 | 0.88 | 23.19
DVH102* | 8.5 | 3500 | 75 | 64 | 93 | 106.8 | 0.74 | 20.49
DVH102* | 8.5 | 3500 | 75 | 67 | 93 | 112.5 | 0.61 | 17.84
DVH102* | 8.5 | 3500 | 75 | 70 | 93 | 119.1 | 0.5 | 15.38
DVH102* | 8.5 | 3500 | 75 | 72 | 93 | 123.2 | 0.42 | 13.38
DVH102* | 8.5 | 3500 | 75 | 57 | 95 | 95.1 | 1 | 24.7
DVH102* | 8.5 | 3500 | 75 | 61 | 95 | 100.5 | 0.88 | 23.04
DVH102* | 8.5 | 3500 | 75 | 64 | 95 | 105.9 | 0.74 | 20.42
DVH102* | 8.5 | 3500 | 75 | 67 | 95 | 111.6 | 0.61 | 17.77
DVH102* | 8.5 | 3500 | 75 | 70 | 95 | 118.2 | 0.5 | 15.32
DVH102* | 8.5 | 3500 | 75 | 72 | 95 | 122.3 | 0.42 | 13.32
DVH102* | 8.5 | 3500 | 75 | 57 | 99 | 93.9 | 1 | 24.39
DVH102* | 8.5 | 3500 | 75 | 61 | 99 | 98.9 | 0.88 | 22.73
DVH102* | 8.5 | 3500 | 75 | 64 | 99 | 104.2 | 0.75 | 20.21
DVH102* | 8.5 | 3500 | 75 | 67 | 99 | 109.8 | 0.62 | 17.61
DVH102* | 8.5 | 3500 | 75 | 70 | 99 | 116.3 | 0.5 | 15.17
DVH102* | 8.5 | 3500 | 75 | 72 | 99 | 120.3 | 0.42 | 13.19
DVH102* | 8.5 | 3500 | 75 | 57 | 103 | 92.7 | 1 | 24.08
DVH102* | 8.5 | 3500 | 75 | 61 | 103 | 97.3 | 0.89 | 22.42
DVH102* | 8.5 | 3500 | 75 | 64 | 103 | 102.6 | 0.75 | 20.03
DVH102* | 8.5 | 3500 | 75 | 67 | 103 | 108 | 0.62 | 17.43
DVH102* | 8.5 | 3500 | 75 | 70 | 103 | 114.4 | 0.51 | 15.04
DVH102* | 8.5 | 3500 | 75 | 72 | 103 | 118.4 | 0.42 | 13.06
DVH102* | 8.5 | 3500 | 75 | 57 | 106 | 91.8 | 1 | 23.84
DVH102* | 8.5 | 3500 | 75 | 61 | 106 | 96.1 | 0.89 | 22.18
DVH102* | 8.5 | 3500 | 75 | 64 | 106 | 101.3 | 0.76 | 19.87
DVH102* | 8.5 | 3500 | 75 | 67 | 106 | 106.7 | 0.62 | 17.3
DVH102* | 8.5 | 3500 | 75 | 70 | 106 | 113 | 0.51 | 14.91
DVH102* | 8.5 | 3500 | 75 | 72 | 106 | 116.9 | 0.43 | 12.99
DVH102* | 8.5 | 3500 | 75 | 57 | 110 | 90.6 | 1 | 23.53
DVH102* | 8.5 | 3500 | 75 | 61 | 110 | 94.5 | 0.89 | 21.87
DVH102* | 8.5 | 3500 | 75 | 64 | 110 | 99.6 | 0.76 | 19.69
DVH102* | 8.5 | 3500 | 75 | 67 | 110 | 104.9 | 0.63 | 17.14
DVH102* | 8.5 | 3500 | 75 | 70 | 110 | 111.1 | 0.51 | 14.78
DVH102* | 8.5 | 3500 | 75 | 72 | 110 | 114.9 | 0.43 | 12.86
DVH102* | 8.5 | 3500 | 75 | 57 | 115 | 89.1 | 1 | 23.14
DVH102* | 8.5 | 3500 | 75 | 61 | 115 | 92.5 | 0.9 | 21.51
DVH102* | 8.5 | 3500 | 75 | 64 | 115 | 97.5 | 0.77 | 19.43
DVH102* | 8.5 | 3500 | 75 | 67 | 115 | 102.7 | 0.63 | 16.91
DVH102* | 8.5 | 3500 | 75 | 70 | 115 | 108.8 | 0.52 | 14.57
DVH102* | 8.5 | 3500 | 75 | 72 | 115 | 112.5 | 0.43 | 12.68
DVH102* | 8.5 | 3500 | 80 | 57 | 23 | 112.6 | 1 | 29.25
DVH102* | 8.5 | 3500 | 80 | 61 | 23 | 115.3 | 0.96 | 28.81
DVH102* | 8.5 | 3500 | 80 | 64 | 23 | 121.6 | 0.84 | 26.62
DVH102* | 8.5 | 3500 | 80 | 67 | 23 | 128 | 0.72 | 23.82
DVH102* | 8.5 | 3500 | 80 | 70 | 23 | 135.6 | 0.61 | 21.32
DVH102* | 8.5 | 3500 | 80 | 72 | 23 | 140.3 | 0.53 | 19.17
DVH102* | 8.5 | 3500 | 80 | 75 | 23 | 148.2 | 0.43 | 16.65
DVH102* | 8.5 | 3500 | 80 | 57 | 30 | 112.4 | 1 | 29.19
DVH102* | 8.5 | 3500 | 80 | 61 | 30 | 115.1 | 0.96 | 28.78
DVH102* | 8.5 | 3500 | 80 | 64 | 30 | 121.4 | 0.84 | 26.57
DVH102* | 8.5 | 3500 | 80 | 67 | 30 | 127.8 | 0.72 | 23.77
DVH102* | 8.5 | 3500 | 80 | 70 | 30 | 135.4 | 0.6 | 21.27
DVH102* | 8.5 | 3500 | 80 | 72 | 30 | 140.1 | 0.53 | 19.12
DVH102* | 8.5 | 3500 | 80 | 75 | 30 | 148.1 | 0.43 | 16.62
DVH102* | 8.5 | 3500 | 80 | 57 | 40 | 112.3 | 1 | 29.17
DVH102* | 8.5 | 3500 | 80 | 61 | 40 | 114.9 | 0.96 | 28.7
DVH102* | 8.5 | 3500 | 80 | 64 | 40 | 121.1 | 0.84 | 26.52
DVH102* | 8.5 | 3500 | 80 | 67 | 40 | 127.6 | 0.72 | 23.71
DVH102* | 8.5 | 3500 | 80 | 70 | 40 | 135.1 | 0.61 | 21.25
DVH102* | 8.5 | 3500 | 80 | 72 | 40 | 139.8 | 0.53 | 19.09
DVH102* | 8.5 | 3500 | 80 | 75 | 40 | 147.8 | 0.43 | 16.6
DVH102* | 8.5 | 3500 | 80 | 57 | 50 | 112.1 | 1 | 29.12
DVH102* | 8.5 | 3500 | 80 | 61 | 50 | 114.6 | 0.96 | 28.65
DVH102* | 8.5 | 3500 | 80 | 64 | 50 | 120.8 | 0.84 | 26.47
DVH102* | 8.5 | 3500 | 80 | 67 | 50 | 127.3 | 0.72 | 23.66
DVH102* | 8.5 | 3500 | 80 | 70 | 50 | 134.8 | 0.61 | 21.19
DVH102* | 8.5 | 3500 | 80 | 72 | 50 | 139.5 | 0.53 | 19.04
DVH102* | 8.5 | 3500 | 80 | 75 | 50 | 147.5 | 0.43 | 16.57
DVH102* | 8.5 | 3500 | 80 | 57 | 54 | 112 | 1 | 29.09
DVH102* | 8.5 | 3500 | 80 | 61 | 54 | 114.5 | 0.96 | 28.62
DVH102* | 8.5 | 3500 | 80 | 64 | 54 | 120.7 | 0.84 | 26.44
DVH102* | 8.5 | 3500 | 80 | 67 | 54 | 127.2 | 0.72 | 23.64
DVH102* | 8.5 | 3500 | 80 | 70 | 54 | 134.7 | 0.61 | 21.17
DVH102* | 8.5 | 3500 | 80 | 72 | 54 | 139.4 | 0.53 | 19.04
DVH102* | 8.5 | 3500 | 80 | 75 | 54 | 147.4 | 0.43 | 16.57
DVH102* | 8.5 | 3500 | 80 | 57 | 58 | 111.9 | 1 | 29.06
DVH102* | 8.5 | 3500 | 80 | 61 | 58 | 114.4 | 0.96 | 28.6
DVH102* | 8.5 | 3500 | 80 | 64 | 58 | 120.6 | 0.84 | 26.42
DVH102* | 8.5 | 3500 | 80 | 67 | 58 | 127.1 | 0.72 | 23.64
DVH102* | 8.5 | 3500 | 80 | 70 | 58 | 134.6 | 0.6 | 21.14
DVH102* | 8.5 | 3500 | 80 | 72 | 58 | 139.2 | 0.53 | 19.01
DVH102* | 8.5 | 3500 | 80 | 75 | 58 | 147.3 | 0.43 | 16.55
DVH102* | 8.5 | 3500 | 80 | 57 | 62 | 111.3 | 1 | 28.91
DVH102* | 8.5 | 3500 | 80 | 61 | 62 | 113.7 | 0.96 | 28.49
DVH102* | 8.5 | 3500 | 80 | 64 | 62 | 119.9 | 0.84 | 26.31
DVH102* | 8.5 | 3500 | 80 | 67 | 62 | 126.3 | 0.72 | 23.53
DVH102* | 8.5 | 3500 | 80 | 70 | 62 | 133.7 | 0.61 | 21.06
DVH102* | 8.5 | 3500 | 80 | 72 | 62 | 138.4 | 0.53 | 18.94
DVH102* | 8.5 | 3500 | 80 | 75 | 62 | 145.7 | 0.43 | 16.36
DVH102* | 8.5 | 3500 | 80 | 57 | 66 | 110 | 1 | 28.57
DVH102* | 8.5 | 3500 | 80 | 61 | 66 | 112.1 | 0.97 | 28.29
DVH102* | 8.5 | 3500 | 80 | 64 | 66 | 118.2 | 0.85 | 26.13
DVH102* | 8.5 | 3500 | 80 | 67 | 66 | 124.5 | 0.72 | 23.38
DVH102* | 8.5 | 3500 | 80 | 70 | 66 | 131.8 | 0.61 | 20.91
DVH102* | 8.5 | 3500 | 80 | 72 | 66 | 136.4 | 0.53 | 18.81
DVH102* | 8.5 | 3500 | 80 | 75 | 66 | 143.7 | 0.43 | 16.21
DVH102* | 8.5 | 3500 | 80 | 57 | 70 | 108.7 | 1 | 28.23
DVH102* | 8.5 | 3500 | 80 | 61 | 70 | 110.5 | 0.98 | 28.08
DVH102* | 8.5 | 3500 | 80 | 64 | 70 | 116.5 | 0.86 | 25.95
DVH102* | 8.5 | 3500 | 80 | 67 | 70 | 122.7 | 0.73 | 23.19
DVH102* | 8.5 | 3500 | 80 | 70 | 70 | 130 | 0.62 | 20.78
DVH102* | 8.5 | 3500 | 80 | 72 | 70 | 134.5 | 0.53 | 18.68
DVH102* | 8.5 | 3500 | 80 | 75 | 70 | 141.7 | 0.44 | 16.03
DVH102* | 8.5 | 3500 | 80 | 57 | 72 | 108.1 | 1 | 28.08
DVH102* | 8.5 | 3500 | 80 | 61 | 72 | 109.7 | 0.98 | 27.97
DVH102* | 8.5 | 3500 | 80 | 64 | 72 | 115.7 | 0.86 | 25.84
DVH102* | 8.5 | 3500 | 80 | 67 | 72 | 121.8 | 0.73 | 23.12
DVH102* | 8.5 | 3500 | 80 | 70 | 72 | 129 | 0.62 | 20.7
DVH102* | 8.5 | 3500 | 80 | 72 | 72 | 133.5 | 0.54 | 18.6
DVH102* | 8.5 | 3500 | 80 | 75 | 72 | 140.7 | 0.44 | 15.92
DVH102* | 8.5 | 3500 | 80 | 57 | 75 | 107.1 | 1 | 27.82
DVH102* | 8.5 | 3500 | 80 | 61 | 75 | 108.5 | 0.99 | 27.82
DVH102* | 8.5 | 3500 | 80 | 64 | 75 | 114.4 | 0.87 | 25.71
DVH102* | 8.5 | 3500 | 80 | 67 | 75 | 120.5 | 0.73 | 22.99
DVH102* | 8.5 | 3500 | 80 | 70 | 75 | 127.6 | 0.62 | 20.57
DVH102* | 8.5 | 3500 | 80 | 72 | 75 | 132 | 0.54 | 18.49
DVH102* | 8.5 | 3500 | 80 | 75 | 75 | 139.2 | 0.44 | 15.79
DVH102* | 8.5 | 3500 | 80 | 57 | 79 | 105.9 | 1 | 27.51
DVH102* | 8.5 | 3500 | 80 | 61 | 79 | 106.9 | 0.99 | 27.61
DVH102* | 8.5 | 3500 | 80 | 64 | 79 | 112.7 | 0.87 | 25.51
DVH102* | 8.5 | 3500 | 80 | 67 | 79 | 118.7 | 0.74 | 22.81
DVH102* | 8.5 | 3500 | 80 | 70 | 79 | 125.7 | 0.63 | 20.42
DVH102* | 8.5 | 3500 | 80 | 72 | 79 | 130.1 | 0.54 | 18.36
DVH102* | 8.5 | 3500 | 80 | 75 | 79 | 137.1 | 0.44 | 15.61
DVH102* | 8.5 | 3500 | 80 | 57 | 83 | 104.6 | 1 | 27.17
DVH102* | 8.5 | 3500 | 80 | 61 | 83 | 105.3 | 1 | 27.38
DVH102* | 8.5 | 3500 | 80 | 64 | 83 | 111 | 0.88 | 25.3
DVH102* | 8.5 | 3500 | 80 | 67 | 83 | 116.9 | 0.75 | 22.62
DVH102* | 8.5 | 3500 | 80 | 70 | 83 | 123.8 | 0.63 | 20.26
DVH102* | 8.5 | 3500 | 80 | 72 | 83 | 128.1 | 0.55 | 18.21
DVH102* | 8.5 | 3500 | 80 | 75 | 83 | 135.1 | 0.44 | 15.43
DVH102* | 8.5 | 3500 | 80 | 57 | 87 | 103.3 | 1 | 26.83
DVH102* | 8.5 | 3500 | 80 | 61 | 87 | 103.7 | 1.01 | 27.17
DVH102* | 8.5 | 3500 | 80 | 64 | 87 | 109.3 | 0.88 | 25.09
DVH102* | 8.5 | 3500 | 80 | 67 | 87 | 115.1 | 0.75 | 22.44
DVH102* | 8.5 | 3500 | 80 | 70 | 87 | 122 | 0.63 | 20.08
DVH102* | 8.5 | 3500 | 80 | 72 | 87 | 126.2 | 0.55 | 18.05
DVH102* | 8.5 | 3500 | 80 | 75 | 87 | 133.1 | 0.44 | 15.22
DVH102* | 8.5 | 3500 | 80 | 57 | 91 | 102 | 1 | 26.49
DVH102* | 8.5 | 3500 | 80 | 61 | 91 | 102.1 | 1.02 | 26.94
DVH102* | 8.5 | 3500 | 80 | 64 | 91 | 107.6 | 0.89 | 24.88
DVH102* | 8.5 | 3500 | 80 | 67 | 91 | 113.4 | 0.75 | 22.23
DVH102* | 8.5 | 3500 | 80 | 70 | 91 | 120.1 | 0.64 | 19.92
DVH102* | 8.5 | 3500 | 80 | 72 | 91 | 124.2 | 0.55 | 17.9
DVH102* | 8.5 | 3500 | 80 | 75 | 91 | 131.1 | 0.44 | 15.04
DVH102* | 8.5 | 3500 | 80 | 57 | 93 | 101.4 | 1 | 26.34
DVH102* | 8.5 | 3500 | 80 | 61 | 93 | 101.3 | 1.02 | 26.81
DVH102* | 8.5 | 3500 | 80 | 64 | 93 | 106.8 | 0.89 | 24.75
DVH102* | 8.5 | 3500 | 80 | 67 | 93 | 112.5 | 0.76 | 22.16
DVH102* | 8.5 | 3500 | 80 | 70 | 93 | 119.1 | 0.64 | 19.82
DVH102* | 8.5 | 3500 | 80 | 72 | 93 | 123.2 | 0.56 | 17.82
DVH102* | 8.5 | 3500 | 80 | 75 | 93 | 130.1 | 0.44 | 14.96
DVH102* | 8.5 | 3500 | 80 | 57 | 95 | 100.7 | 1 | 26.16
DVH102* | 8.5 | 3500 | 80 | 61 | 95 | 100.5 | 1 | 26.1
DVH102* | 8.5 | 3500 | 80 | 64 | 95 | 105.9 | 0.9 | 24.65
DVH102* | 8.5 | 3500 | 80 | 67 | 95 | 111.6 | 0.76 | 22.05
DVH102* | 8.5 | 3500 | 80 | 70 | 95 | 118.2 | 0.64 | 19.74
DVH102* | 8.5 | 3500 | 80 | 72 | 95 | 122.3 | 0.56 | 17.74
DVH102* | 8.5 | 3500 | 80 | 75 | 95 | 129.1 | 0.44 | 14.86
DVH102* | 8.5 | 3500 | 80 | 57 | 99 | 99.5 | 1 | 25.84
DVH102* | 8.5 | 3500 | 80 | 61 | 99 | 98.9 | 1 | 25.69
DVH102* | 8.5 | 3500 | 80 | 64 | 99 | 104.2 | 0.9 | 24.42
DVH102* | 8.5 | 3500 | 80 | 67 | 99 | 109.8 | 0.77 | 21.84
DVH102* | 8.5 | 3500 | 80 | 70 | 99 | 116.3 | 0.65 | 19.56
DVH102* | 8.5 | 3500 | 80 | 72 | 99 | 120.3 | 0.56 | 17.58
DVH102* | 8.5 | 3500 | 80 | 75 | 99 | 127.1 | 0.44 | 14.68
DVH102* | 8.5 | 3500 | 80 | 57 | 103 | 98.2 | 1 | 25.51
DVH102* | 8.5 | 3500 | 80 | 61 | 103 | 97.3 | 1 | 25.27
DVH102* | 8.5 | 3500 | 80 | 64 | 103 | 102.6 | 0.91 | 24.18
DVH102* | 8.5 | 3500 | 80 | 67 | 103 | 108 | 0.77 | 21.64
DVH102* | 8.5 | 3500 | 80 | 70 | 103 | 114.4 | 0.65 | 19.38
DVH102* | 8.5 | 3500 | 80 | 72 | 103 | 118.4 | 0.57 | 17.4
DVH102* | 8.5 | 3500 | 80 | 75 | 103 | 125 | 0.45 | 14.47
DVH102* | 8.5 | 3500 | 80 | 57 | 106 | 97.2 | 1 | 25.25
DVH102* | 8.5 | 3500 | 80 | 61 | 106 | 96.1 | 1 | 24.96
DVH102* | 8.5 | 3500 | 80 | 64 | 106 | 101.3 | 0.91 | 24.03
DVH102* | 8.5 | 3500 | 80 | 67 | 106 | 106.7 | 0.78 | 21.48
DVH102* | 8.5 | 3500 | 80 | 70 | 106 | 113 | 0.65 | 19.22
DVH102* | 8.5 | 3500 | 80 | 72 | 106 | 116.9 | 0.57 | 17.27
DVH102* | 8.5 | 3500 | 80 | 75 | 106 | 123.5 | 0.45 | 14.34
DVH102* | 8.5 | 3500 | 80 | 57 | 110 | 96 | 1 | 24.94
DVH102* | 8.5 | 3500 | 80 | 61 | 110 | 94.5 | 1 | 24.55
DVH102* | 8.5 | 3500 | 80 | 64 | 110 | 99.6 | 0.92 | 23.77
DVH102* | 8.5 | 3500 | 80 | 67 | 110 | 104.9 | 0.78 | 21.27
DVH102* | 8.5 | 3500 | 80 | 70 | 110 | 111.1 | 0.66 | 19.04
DVH102* | 8.5 | 3500 | 80 | 72 | 110 | 114.9 | 0.57 | 17.12
DVH102* | 8.5 | 3500 | 80 | 75 | 110 | 121.5 | 0.45 | 14.13
DVH102* | 8.5 | 3500 | 80 | 57 | 115 | 94.4 | 1 | 24.52
DVH102* | 8.5 | 3500 | 80 | 61 | 115 | 92.5 | 1 | 24.03
DVH102* | 8.5 | 3500 | 80 | 64 | 115 | 97.5 | 0.93 | 23.45
DVH102* | 8.5 | 3500 | 80 | 67 | 115 | 102.7 | 0.79 | 20.99
DVH102* | 8.5 | 3500 | 80 | 70 | 115 | 108.8 | 0.66 | 18.78
DVH102* | 8.5 | 3500 | 80 | 72 | 115 | 112.5 | 0.58 | 16.88
DVH102* | 8.5 | 3500 | 80 | 75 | 115 | 119 | 0.45 | 13.9
DVH102* | 8.5 | 3500 | 85 | 57 | 23 | 118.9 | 1 | 30.88
DVH102* | 8.5 | 3500 | 85 | 61 | 23 | 121.8 | 0.96 | 30.44
DVH102* | 8.5 | 3500 | 85 | 64 | 23 | 121.6 | 0.96 | 30.42
DVH102* | 8.5 | 3500 | 85 | 67 | 23 | 128 | 0.85 | 28.36
DVH102* | 8.5 | 3500 | 85 | 70 | 23 | 135.6 | 0.74 | 25.97
DVH102* | 8.5 | 3500 | 85 | 72 | 23 | 140.3 | 0.65 | 23.79
DVH102* | 8.5 | 3500 | 85 | 75 | 23 | 148.2 | 0.56 | 21.43
DVH102* | 8.5 | 3500 | 85 | 57 | 30 | 118.8 | 1 | 30.86
DVH102* | 8.5 | 3500 | 85 | 61 | 30 | 121.6 | 0.96 | 30.39
DVH102* | 8.5 | 3500 | 85 | 64 | 30 | 121.4 | 0.96 | 30.36
DVH102* | 8.5 | 3500 | 85 | 67 | 30 | 127.8 | 0.85 | 28.31
DVH102* | 8.5 | 3500 | 85 | 70 | 30 | 135.4 | 0.74 | 25.92
DVH102* | 8.5 | 3500 | 85 | 72 | 30 | 140.1 | 0.65 | 23.74
DVH102* | 8.5 | 3500 | 85 | 75 | 30 | 148.1 | 0.56 | 21.4
DVH102* | 8.5 | 3500 | 85 | 57 | 40 | 118.6 | 1 | 30.81
DVH102* | 8.5 | 3500 | 85 | 61 | 40 | 121.4 | 0.96 | 30.34
DVH102* | 8.5 | 3500 | 85 | 64 | 40 | 121.1 | 0.96 | 30.29
DVH102* | 8.5 | 3500 | 85 | 67 | 40 | 127.6 | 0.85 | 28.26
DVH102* | 8.5 | 3500 | 85 | 70 | 40 | 135.1 | 0.74 | 25.87
DVH102* | 8.5 | 3500 | 85 | 72 | 40 | 139.8 | 0.65 | 23.69
DVH102* | 8.5 | 3500 | 85 | 75 | 40 | 147.8 | 0.56 | 21.38
DVH102* | 8.5 | 3500 | 85 | 57 | 50 | 118.4 | 1 | 30.75
DVH102* | 8.5 | 3500 | 85 | 61 | 50 | 121.1 | 0.96 | 30.26
DVH102* | 8.5 | 3500 | 85 | 64 | 50 | 120.8 | 0.96 | 30.23
DVH102* | 8.5 | 3500 | 85 | 67 | 50 | 127.3 | 0.85 | 28.18
DVH102* | 8.5 | 3500 | 85 | 70 | 50 | 134.8 | 0.74 | 25.82
DVH102* | 8.5 | 3500 | 85 | 72 | 50 | 139.5 | 0.65 | 23.64
DVH102* | 8.5 | 3500 | 85 | 75 | 50 | 147.5 | 0.56 | 21.32
DVH102* | 8.5 | 3500 | 85 | 57 | 54 | 118.3 | 1 | 30.73
DVH102* | 8.5 | 3500 | 85 | 61 | 54 | 121 | 0.96 | 30.23
DVH102* | 8.5 | 3500 | 85 | 64 | 54 | 120.7 | 0.96 | 30.21
DVH102* | 8.5 | 3500 | 85 | 67 | 54 | 127.2 | 0.85 | 28.16
DVH102* | 8.5 | 3500 | 85 | 70 | 54 | 134.7 | 0.74 | 25.79
DVH102* | 8.5 | 3500 | 85 | 72 | 54 | 139.4 | 0.65 | 23.64
DVH102* | 8.5 | 3500 | 85 | 75 | 54 | 147.4 | 0.56 | 21.32
DVH102* | 8.5 | 3500 | 85 | 57 | 58 | 118.3 | 1 | 30.73
DVH102* | 8.5 | 3500 | 85 | 61 | 58 | 120.9 | 0.96 | 30.21
DVH102* | 8.5 | 3500 | 85 | 64 | 58 | 120.6 | 0.96 | 30.18
DVH102* | 8.5 | 3500 | 85 | 67 | 58 | 127.1 | 0.85 | 28.13
DVH102* | 8.5 | 3500 | 85 | 70 | 58 | 134.6 | 0.74 | 25.77
DVH102* | 8.5 | 3500 | 85 | 72 | 58 | 139.2 | 0.65 | 23.61
DVH102* | 8.5 | 3500 | 85 | 75 | 58 | 147.3 | 0.56 | 21.3
DVH102* | 8.5 | 3500 | 85 | 57 | 62 | 117.6 | 1 | 30.55
DVH102* | 8.5 | 3500 | 85 | 61 | 62 | 120.1 | 0.97 | 30.1
DVH102* | 8.5 | 3500 | 85 | 64 | 62 | 119.9 | 0.96 | 30.05
DVH102* | 8.5 | 3500 | 85 | 67 | 62 | 126.3 | 0.85 | 28.03
DVH102* | 8.5 | 3500 | 85 | 70 | 62 | 133.7 | 0.74 | 25.66
DVH102* | 8.5 | 3500 | 85 | 72 | 62 | 138.4 | 0.65 | 23.51
DVH102* | 8.5 | 3500 | 85 | 75 | 62 | 145.7 | 0.56 | 21.06
DVH102* | 8.5 | 3500 | 85 | 57 | 66 | 116.2 | 1 | 30.18
DVH102* | 8.5 | 3500 | 85 | 61 | 66 | 118.4 | 0.97 | 29.9
DVH102* | 8.5 | 3500 | 85 | 64 | 66 | 118.2 | 0.97 | 29.84
DVH102* | 8.5 | 3500 | 85 | 67 | 66 | 124.5 | 0.86 | 27.84
DVH102* | 8.5 | 3500 | 85 | 70 | 66 | 131.8 | 0.75 | 25.51
DVH102* | 8.5 | 3500 | 85 | 72 | 66 | 136.4 | 0.66 | 23.35
DVH102* | 8.5 | 3500 | 85 | 75 | 66 | 143.7 | 0.56 | 20.86
DVH102* | 8.5 | 3500 | 85 | 57 | 70 | 114.9 | 1 | 29.84
DVH102* | 8.5 | 3500 | 85 | 61 | 70 | 116.8 | 0.98 | 29.66
DVH102* | 8.5 | 3500 | 85 | 64 | 70 | 116.5 | 0.98 | 29.64
DVH102* | 8.5 | 3500 | 85 | 67 | 70 | 122.7 | 0.87 | 27.64
DVH102* | 8.5 | 3500 | 85 | 70 | 70 | 130 | 0.75 | 25.32
DVH102* | 8.5 | 3500 | 85 | 72 | 70 | 134.5 | 0.66 | 23.17
DVH102* | 8.5 | 3500 | 85 | 75 | 70 | 141.7 | 0.56 | 20.62
DVH102* | 8.5 | 3500 | 85 | 57 | 72 | 114.2 | 1 | 29.66
DVH102* | 8.5 | 3500 | 85 | 61 | 72 | 115.9 | 0.98 | 29.56
DVH102* | 8.5 | 3500 | 85 | 64 | 72 | 115.7 | 0.98 | 29.53
DVH102* | 8.5 | 3500 | 85 | 67 | 72 | 121.8 | 0.87 | 27.53
DVH102* | 8.5 | 3500 | 85 | 70 | 72 | 129 | 0.75 | 25.22
DVH102* | 8.5 | 3500 | 85 | 72 | 72 | 133.5 | 0.67 | 23.09
DVH102* | 8.5 | 3500 | 85 | 75 | 72 | 140.7 | 0.56 | 20.49
DVH102* | 8.5 | 3500 | 85 | 57 | 75 | 113.2 | 1 | 29.4
DVH102* | 8.5 | 3500 | 85 | 61 | 75 | 114.6 | 0.99 | 29.4
DVH102* | 8.5 | 3500 | 85 | 64 | 75 | 114.4 | 0.99 | 29.35
DVH102* | 8.5 | 3500 | 85 | 67 | 75 | 120.5 | 0.87 | 27.38
DVH102* | 8.5 | 3500 | 85 | 70 | 75 | 127.6 | 0.76 | 25.06
DVH102* | 8.5 | 3500 | 85 | 72 | 75 | 132 | 0.67 | 22.96
DVH102* | 8.5 | 3500 | 85 | 75 | 75 | 139.2 | 0.56 | 20.31
DVH102* | 8.5 | 3500 | 85 | 57 | 79 | 111.8 | 1 | 29.04
DVH102* | 8.5 | 3500 | 85 | 61 | 79 | 112.9 | 0.99 | 29.17
DVH102* | 8.5 | 3500 | 85 | 64 | 79 | 112.7 | 1 | 29.14
DVH102* | 8.5 | 3500 | 85 | 67 | 79 | 118.7 | 0.88 | 27.17
DVH102* | 8.5 | 3500 | 85 | 70 | 79 | 125.7 | 0.76 | 24.88
DVH102* | 8.5 | 3500 | 85 | 72 | 79 | 130.1 | 0.67 | 22.78
DVH102* | 8.5 | 3500 | 85 | 75 | 79 | 137.1 | 0.56 | 20.08
DVH102* | 8.5 | 3500 | 85 | 57 | 83 | 110.5 | 1 | 28.7
DVH102* | 8.5 | 3500 | 85 | 61 | 83 | 111.2 | 1 | 28.94
DVH102* | 8.5 | 3500 | 85 | 64 | 83 | 111 | 1 | 28.91
DVH102* | 8.5 | 3500 | 85 | 67 | 83 | 116.9 | 0.89 | 26.94
DVH102* | 8.5 | 3500 | 85 | 70 | 83 | 123.8 | 0.77 | 24.68
DVH102* | 8.5 | 3500 | 85 | 72 | 83 | 128.1 | 0.68 | 22.6
DVH102* | 8.5 | 3500 | 85 | 75 | 83 | 135.1 | 0.57 | 19.84
DVH102* | 8.5 | 3500 | 85 | 57 | 87 | 109.1 | 1 | 28.34
DVH102* | 8.5 | 3500 | 85 | 61 | 87 | 109.6 | 1.01 | 28.7
DVH102* | 8.5 | 3500 | 85 | 64 | 87 | 109.3 | 1.01 | 28.65
DVH102* | 8.5 | 3500 | 85 | 67 | 87 | 115.1 | 0.89 | 26.73
DVH102* | 8.5 | 3500 | 85 | 70 | 87 | 122 | 0.77 | 24.47
DVH102* | 8.5 | 3500 | 85 | 72 | 87 | 126.2 | 0.68 | 22.42
DVH102* | 8.5 | 3500 | 85 | 75 | 87 | 133.1 | 0.57 | 19.61
DVH102* | 8.5 | 3500 | 85 | 57 | 91 | 107.8 | 1 | 28
DVH102* | 8.5 | 3500 | 85 | 61 | 91 | 107.9 | 1.01 | 28.44
DVH102* | 8.5 | 3500 | 85 | 64 | 91 | 107.6 | 1.02 | 28.42
DVH102* | 8.5 | 3500 | 85 | 67 | 91 | 113.4 | 0.9 | 26.49
DVH102* | 8.5 | 3500 | 85 | 70 | 91 | 120.1 | 0.78 | 24.26
DVH102* | 8.5 | 3500 | 85 | 72 | 91 | 124.2 | 0.69 | 22.23
DVH102* | 8.5 | 3500 | 85 | 75 | 91 | 131.1 | 0.57 | 19.38
DVH102* | 8.5 | 3500 | 85 | 57 | 93 | 107.1 | 1 | 27.82
DVH102* | 8.5 | 3500 | 85 | 61 | 93 | 107 | 1.02 | 28.31
DVH102* | 8.5 | 3500 | 85 | 64 | 93 | 106.8 | 1.02 | 28.29
DVH102* | 8.5 | 3500 | 85 | 67 | 93 | 112.5 | 0.9 | 26.36
DVH102* | 8.5 | 3500 | 85 | 70 | 93 | 119.1 | 0.78 | 24.16
DVH102* | 8.5 | 3500 | 85 | 72 | 93 | 123.2 | 0.69 | 22.13
DVH102* | 8.5 | 3500 | 85 | 75 | 93 | 130.1 | 0.57 | 19.25
DVH102* | 8.5 | 3500 | 85 | 57 | 95 | 106.4 | 1 | 27.64
DVH102* | 8.5 | 3500 | 85 | 61 | 95 | 106.2 | 1 | 27.58
DVH102* | 8.5 | 3500 | 85 | 64 | 95 | 105.9 | 1 | 27.51
DVH102* | 8.5 | 3500 | 85 | 67 | 95 | 111.6 | 0.91 | 26.26
DVH102* | 8.5 | 3500 | 85 | 70 | 95 | 118.2 | 0.78 | 24.05
DVH102* | 8.5 | 3500 | 85 | 72 | 95 | 122.3 | 0.69 | 22.03
DVH102* | 8.5 | 3500 | 85 | 75 | 95 | 129.1 | 0.57 | 19.12
DVH102* | 8.5 | 3500 | 85 | 57 | 99 | 105.1 | 1 | 27.3
DVH102* | 8.5 | 3500 | 85 | 61 | 99 | 104.5 | 1 | 27.14
DVH102* | 8.5 | 3500 | 85 | 64 | 99 | 104.2 | 1 | 27.06
DVH102* | 8.5 | 3500 | 85 | 67 | 99 | 109.8 | 0.91 | 26.03
DVH102* | 8.5 | 3500 | 85 | 70 | 99 | 116.3 | 0.79 | 23.82
DVH102* | 8.5 | 3500 | 85 | 72 | 99 | 120.3 | 0.7 | 21.82
DVH102* | 8.5 | 3500 | 85 | 75 | 99 | 127.1 | 0.57 | 18.88
DVH102* | 8.5 | 3500 | 85 | 57 | 103 | 103.7 | 1 | 26.94
DVH102* | 8.5 | 3500 | 85 | 61 | 103 | 102.8 | 1 | 26.7
DVH102* | 8.5 | 3500 | 85 | 64 | 103 | 102.6 | 1 | 26.65
DVH102* | 8.5 | 3500 | 85 | 67 | 103 | 108 | 0.92 | 25.77
DVH102* | 8.5 | 3500 | 85 | 70 | 103 | 114.4 | 0.79 | 23.61
DVH102* | 8.5 | 3500 | 85 | 72 | 103 | 118.4 | 0.7 | 21.61
DVH102* | 8.5 | 3500 | 85 | 75 | 103 | 125 | 0.57 | 18.62
DVH102* | 8.5 | 3500 | 85 | 57 | 106 | 102.7 | 1 | 26.68
DVH102* | 8.5 | 3500 | 85 | 61 | 106 | 101.5 | 1 | 26.36
DVH102* | 8.5 | 3500 | 85 | 64 | 106 | 101.3 | 1 | 26.31
DVH102* | 8.5 | 3500 | 85 | 67 | 106 | 106.7 | 0.92 | 25.58
DVH102* | 8.5 | 3500 | 85 | 70 | 106 | 113 | 0.8 | 23.43
DVH102* | 8.5 | 3500 | 85 | 72 | 106 | 116.9 | 0.71 | 21.45
DVH102* | 8.5 | 3500 | 85 | 75 | 106 | 123.5 | 0.57 | 18.44
DVH102* | 8.5 | 3500 | 85 | 57 | 110 | 101.4 | 1 | 26.34
DVH102* | 8.5 | 3500 | 85 | 61 | 110 | 99.8 | 1 | 25.92
DVH102* | 8.5 | 3500 | 85 | 64 | 110 | 99.6 | 1 | 25.87
DVH102* | 8.5 | 3500 | 85 | 67 | 110 | 104.9 | 0.93 | 25.32
DVH102* | 8.5 | 3500 | 85 | 70 | 110 | 111.1 | 0.8 | 23.19
DVH102* | 8.5 | 3500 | 85 | 72 | 110 | 114.9 | 0.71 | 21.25
DVH102* | 8.5 | 3500 | 85 | 75 | 110 | 121.5 | 0.58 | 18.21
DVH102* | 8.5 | 3500 | 85 | 57 | 115 | 99.7 | 1 | 25.9
DVH102* | 8.5 | 3500 | 85 | 61 | 115 | 97.7 | 1 | 25.38
DVH102* | 8.5 | 3500 | 85 | 64 | 115 | 97.5 | 1 | 25.32
DVH102* | 8.5 | 3500 | 85 | 67 | 115 | 102.7 | 0.94 | 24.99
DVH102* | 8.5 | 3500 | 85 | 70 | 115 | 108.8 | 0.81 | 22.88
DVH102* | 8.5 | 3500 | 85 | 72 | 115 | 112.5 | 0.72 | 20.96
DVH102* | 8.5 | 3500 | 85 | 75 | 115 | 119 | 0.58 | 17.87
DVH120* | 10 | 3200 | 70 | 57 | 23 | 116.2 | 0.84 | 27.76
DVH120* | 10 | 3200 | 70 | 61 | 23 | 128.3 | 0.63 | 23.12
DVH120* | 10 | 3200 | 70 | 64 | 23 | 136.1 | 0.53 | 20.37
DVH120* | 10 | 3200 | 70 | 67 | 23 | 143.5 | 0.42 | 16.96
DVH120* | 10 | 3200 | 70 | 57 | 30 | 116 | 0.84 | 27.7
DVH120* | 10 | 3200 | 70 | 61 | 30 | 128.1 | 0.63 | 23.1
DVH120* | 10 | 3200 | 70 | 64 | 30 | 135.9 | 0.53 | 20.34
DVH120* | 10 | 3200 | 70 | 67 | 30 | 143.3 | 0.42 | 16.93
DVH120* | 10 | 3200 | 70 | 57 | 40 | 115.7 | 0.84 | 27.64
DVH120* | 10 | 3200 | 70 | 61 | 40 | 127.8 | 0.63 | 23.04
DVH120* | 10 | 3200 | 70 | 64 | 40 | 135.6 | 0.53 | 20.31
DVH120* | 10 | 3200 | 70 | 67 | 40 | 143 | 0.42 | 16.9
DVH120* | 10 | 3200 | 70 | 57 | 50 | 115.3 | 0.84 | 27.56
DVH120* | 10 | 3200 | 70 | 61 | 50 | 127.5 | 0.63 | 22.98
DVH120* | 10 | 3200 | 70 | 64 | 50 | 135.3 | 0.53 | 20.26
DVH120* | 10 | 3200 | 70 | 67 | 50 | 142.7 | 0.42 | 16.87
DVH120* | 10 | 3200 | 70 | 57 | 54 | 115.2 | 0.84 | 27.53
DVH120* | 10 | 3200 | 70 | 61 | 54 | 127.4 | 0.64 | 22.98
DVH120* | 10 | 3200 | 70 | 64 | 54 | 135.2 | 0.53 | 20.23
DVH120* | 10 | 3200 | 70 | 67 | 54 | 142.6 | 0.42 | 16.85
DVH120* | 10 | 3200 | 70 | 57 | 58 | 115.1 | 0.84 | 27.5
DVH120* | 10 | 3200 | 70 | 61 | 58 | 127.2 | 0.64 | 22.95
DVH120* | 10 | 3200 | 70 | 64 | 58 | 134.9 | 0.53 | 20.2
DVH120* | 10 | 3200 | 70 | 67 | 58 | 142.3 | 0.42 | 16.82
DVH120* | 10 | 3200 | 70 | 57 | 62 | 113.9 | 0.84 | 27.3
DVH120* | 10 | 3200 | 70 | 61 | 62 | 125.4 | 0.64 | 22.76
DVH120* | 10 | 3200 | 70 | 64 | 62 | 133 | 0.53 | 20.06
DVH120* | 10 | 3200 | 70 | 67 | 62 | 140.3 | 0.42 | 16.7
DVH120* | 10 | 3200 | 70 | 57 | 66 | 112.6 | 0.85 | 27.05
DVH120* | 10 | 3200 | 70 | 61 | 66 | 123.6 | 0.64 | 22.59
DVH120* | 10 | 3200 | 70 | 64 | 66 | 131.1 | 0.53 | 19.89
DVH120* | 10 | 3200 | 70 | 67 | 66 | 138.3 | 0.42 | 16.56
DVH120* | 10 | 3200 | 70 | 57 | 70 | 111.2 | 0.85 | 26.76
DVH120* | 10 | 3200 | 70 | 61 | 70 | 121.8 | 0.65 | 22.39
DVH120* | 10 | 3200 | 70 | 64 | 70 | 129.2 | 0.54 | 19.72
DVH120* | 10 | 3200 | 70 | 67 | 70 | 136.2 | 0.42 | 16.42
DVH120* | 10 | 3200 | 70 | 57 | 72 | 110.5 | 0.85 | 26.65
DVH120* | 10 | 3200 | 70 | 61 | 72 | 120.9 | 0.65 | 22.3
DVH120* | 10 | 3200 | 70 | 64 | 72 | 128.2 | 0.54 | 19.63
DVH120* | 10 | 3200 | 70 | 67 | 72 | 135.2 | 0.43 | 16.36
DVH120* | 10 | 3200 | 70 | 57 | 75 | 109.5 | 0.85 | 26.45
DVH120* | 10 | 3200 | 70 | 61 | 75 | 119.5 | 0.65 | 22.16
DVH120* | 10 | 3200 | 70 | 64 | 75 | 126.8 | 0.54 | 19.52
DVH120* | 10 | 3200 | 70 | 67 | 75 | 133.7 | 0.43 | 16.25
DVH120* | 10 | 3200 | 70 | 57 | 79 | 108.1 | 0.85 | 26.19
DVH120* | 10 | 3200 | 70 | 61 | 79 | 117.7 | 0.66 | 21.96
DVH120* | 10 | 3200 | 70 | 64 | 79 | 124.9 | 0.55 | 19.35
DVH120* | 10 | 3200 | 70 | 67 | 79 | 131.7 | 0.43 | 16.11
DVH120* | 10 | 3200 | 70 | 57 | 83 | 106.8 | 0.85 | 25.91
DVH120* | 10 | 3200 | 70 | 61 | 83 | 115.9 | 0.66 | 21.73
DVH120* | 10 | 3200 | 70 | 64 | 83 | 122.9 | 0.55 | 19.15
DVH120* | 10 | 3200 | 70 | 67 | 83 | 129.6 | 0.43 | 15.94
DVH120* | 10 | 3200 | 70 | 57 | 87 | 105.4 | 0.86 | 25.65
DVH120* | 10 | 3200 | 70 | 61 | 87 | 114.1 | 0.66 | 21.53
DVH120* | 10 | 3200 | 70 | 64 | 87 | 121 | 0.55 | 18.98
DVH120* | 10 | 3200 | 70 | 67 | 87 | 127.6 | 0.44 | 15.8
DVH120* | 10 | 3200 | 70 | 57 | 91 | 104.1 | 0.86 | 25.37
DVH120* | 10 | 3200 | 70 | 61 | 91 | 112.2 | 0.67 | 21.34
DVH120* | 10 | 3200 | 70 | 64 | 91 | 119.1 | 0.55 | 18.78
DVH120* | 10 | 3200 | 70 | 67 | 91 | 125.6 | 0.44 | 15.65
DVH120* | 10 | 3200 | 70 | 57 | 93 | 103.4 | 0.86 | 25.26
DVH120* | 10 | 3200 | 70 | 61 | 93 | 111.3 | 0.67 | 21.22
DVH120* | 10 | 3200 | 70 | 64 | 93 | 118.1 | 0.56 | 18.69
DVH120* | 10 | 3200 | 70 | 67 | 93 | 124.6 | 0.44 | 15.57
DVH120* | 10 | 3200 | 70 | 57 | 95 | 102.7 | 0.86 | 25.11
DVH120* | 10 | 3200 | 70 | 61 | 95 | 110.4 | 0.67 | 21.11
DVH120* | 10 | 3200 | 70 | 64 | 95 | 117.2 | 0.56 | 18.61
DVH120* | 10 | 3200 | 70 | 67 | 95 | 123.6 | 0.44 | 15.48
DVH120* | 10 | 3200 | 70 | 57 | 99 | 101.4 | 0.86 | 24.83
DVH120* | 10 | 3200 | 70 | 61 | 99 | 108.6 | 0.68 | 20.88
DVH120* | 10 | 3200 | 70 | 64 | 99 | 115.2 | 0.56 | 18.41
DVH120* | 10 | 3200 | 70 | 67 | 99 | 121.5 | 0.44 | 15.31
DVH120* | 10 | 3200 | 70 | 57 | 103 | 100 | 0.86 | 24.57
DVH120* | 10 | 3200 | 70 | 61 | 103 | 106.8 | 0.68 | 20.65
DVH120* | 10 | 3200 | 70 | 64 | 103 | 113.3 | 0.57 | 18.21
DVH120* | 10 | 3200 | 70 | 67 | 103 | 119.5 | 0.45 | 15.17
DVH120* | 10 | 3200 | 70 | 57 | 106 | 99 | 0.87 | 24.35
DVH120* | 10 | 3200 | 70 | 61 | 106 | 105.5 | 0.68 | 20.48
DVH120* | 10 | 3200 | 70 | 64 | 106 | 111.9 | 0.57 | 18.07
DVH120* | 10 | 3200 | 70 | 67 | 106 | 118 | 0.45 | 15.03
DVH120* | 10 | 3200 | 70 | 57 | 110 | 97.6 | 0.87 | 24.09
DVH120* | 10 | 3200 | 70 | 61 | 110 | 103.6 | 0.69 | 20.26
DVH120* | 10 | 3200 | 70 | 64 | 110 | 110 | 0.57 | 17.84
DVH120* | 10 | 3200 | 70 | 67 | 110 | 116 | 0.45 | 14.86
DVH120* | 10 | 3200 | 75 | 57 | 23 | 117.4 | 1 | 33.35
DVH120* | 10 | 3200 | 75 | 61 | 23 | 128.3 | 0.77 | 28.12
DVH120* | 10 | 3200 | 75 | 64 | 23 | 136.1 | 0.66 | 25.68
DVH120* | 10 | 3200 | 75 | 67 | 23 | 143.5 | 0.55 | 22.24
DVH120* | 10 | 3200 | 75 | 70 | 23 | 151.8 | 0.45 | 19.32
DVH120* | 10 | 3200 | 75 | 72 | 23 | 157 | 0.38 | 16.87
DVH120* | 10 | 3200 | 75 | 57 | 30 | 117.2 | 1 | 33.3
DVH120* | 10 | 3200 | 75 | 61 | 30 | 128.1 | 0.77 | 28.1
DVH120* | 10 | 3200 | 75 | 64 | 30 | 135.9 | 0.66 | 25.62
DVH120* | 10 | 3200 | 75 | 67 | 30 | 143.3 | 0.55 | 22.22
DVH120* | 10 | 3200 | 75 | 70 | 30 | 151.5 | 0.45 | 19.29
DVH120* | 10 | 3200 | 75 | 72 | 30 | 156.7 | 0.38 | 16.85
DVH120* | 10 | 3200 | 75 | 57 | 40 | 116.9 | 1 | 33.21
DVH120* | 10 | 3200 | 75 | 61 | 40 | 127.8 | 0.77 | 28.04
DVH120* | 10 | 3200 | 75 | 64 | 40 | 135.6 | 0.66 | 25.57
DVH120* | 10 | 3200 | 75 | 67 | 40 | 143 | 0.55 | 22.16
DVH120* | 10 | 3200 | 75 | 70 | 40 | 151.2 | 0.45 | 19.23
DVH120* | 10 | 3200 | 75 | 72 | 40 | 156.4 | 0.38 | 16.82
DVH120* | 10 | 3200 | 75 | 57 | 50 | 116.6 | 1 | 33.12
DVH120* | 10 | 3200 | 75 | 61 | 50 | 127.5 | 0.77 | 27.98
DVH120* | 10 | 3200 | 75 | 64 | 50 | 135.3 | 0.66 | 25.51
DVH120* | 10 | 3200 | 75 | 67 | 50 | 142.7 | 0.55 | 22.13
DVH120* | 10 | 3200 | 75 | 70 | 50 | 150.9 | 0.45 | 19.2
DVH120* | 10 | 3200 | 75 | 72 | 50 | 156.1 | 0.38 | 16.79
DVH120* | 10 | 3200 | 75 | 57 | 54 | 116.5 | 1 | 33.1
DVH120* | 10 | 3200 | 75 | 61 | 54 | 127.4 | 0.77 | 27.95
DVH120* | 10 | 3200 | 75 | 64 | 54 | 135.2 | 0.66 | 25.51
DVH120* | 10 | 3200 | 75 | 67 | 54 | 142.6 | 0.55 | 22.1
DVH120* | 10 | 3200 | 75 | 70 | 54 | 150.7 | 0.45 | 19.18
DVH120* | 10 | 3200 | 75 | 72 | 54 | 155.9 | 0.38 | 16.76
DVH120* | 10 | 3200 | 75 | 57 | 58 | 116.3 | 1 | 33.04
DVH120* | 10 | 3200 | 75 | 61 | 58 | 127.2 | 0.77 | 27.9
DVH120* | 10 | 3200 | 75 | 64 | 58 | 134.9 | 0.66 | 25.45
DVH120* | 10 | 3200 | 75 | 67 | 58 | 142.3 | 0.55 | 22.07
DVH120* | 10 | 3200 | 75 | 70 | 58 | 150.5 | 0.45 | 19.15
DVH120* | 10 | 3200 | 75 | 72 | 58 | 155.6 | 0.38 | 16.73
DVH120* | 10 | 3200 | 75 | 57 | 62 | 115.1 | 1 | 32.7
DVH120* | 10 | 3200 | 75 | 61 | 62 | 125.4 | 0.78 | 27.7
DVH120* | 10 | 3200 | 75 | 64 | 62 | 133 | 0.67 | 25.26
DVH120* | 10 | 3200 | 75 | 67 | 62 | 140.3 | 0.55 | 21.9
DVH120* | 10 | 3200 | 75 | 70 | 62 | 148.3 | 0.45 | 19.01
DVH120* | 10 | 3200 | 75 | 72 | 62 | 153.4 | 0.38 | 16.62
DVH120* | 10 | 3200 | 75 | 57 | 66 | 113.8 | 1 | 32.33
DVH120* | 10 | 3200 | 75 | 61 | 66 | 123.6 | 0.78 | 27.47
DVH120* | 10 | 3200 | 75 | 64 | 66 | 131.1 | 0.67 | 25.06
DVH120* | 10 | 3200 | 75 | 67 | 66 | 138.3 | 0.55 | 21.73
DVH120* | 10 | 3200 | 75 | 70 | 66 | 146.2 | 0.45 | 18.84
DVH120* | 10 | 3200 | 75 | 72 | 66 | 151.2 | 0.38 | 16.48
DVH120* | 10 | 3200 | 75 | 57 | 70 | 112.4 | 1 | 31.93
DVH120* | 10 | 3200 | 75 | 61 | 70 | 121.8 | 0.79 | 27.24
DVH120* | 10 | 3200 | 75 | 64 | 70 | 129.2 | 0.68 | 24.86
DVH120* | 10 | 3200 | 75 | 67 | 70 | 136.2 | 0.56 | 21.53
DVH120* | 10 | 3200 | 75 | 70 | 70 | 144 | 0.46 | 18.69
DVH120* | 10 | 3200 | 75 | 72 | 70 | 149 | 0.39 | 16.34
DVH120* | 10 | 3200 | 75 | 57 | 72 | 111.7 | 1 | 31.73
DVH120* | 10 | 3200 | 75 | 61 | 72 | 120.9 | 0.79 | 27.1
DVH120* | 10 | 3200 | 75 | 64 | 72 | 128.2 | 0.68 | 24.74
DVH120* | 10 | 3200 | 75 | 67 | 72 | 135.2 | 0.56 | 21.45
DVH120* | 10 | 3200 | 75 | 70 | 72 | 143 | 0.46 | 18.61
DVH120* | 10 | 3200 | 75 | 72 | 72 | 147.9 | 0.39 | 16.28
DVH120* | 10 | 3200 | 75 | 57 | 75 | 110.7 | 1 | 31.45
DVH120* | 10 | 3200 | 75 | 61 | 75 | 119.5 | 0.79 | 26.93
DVH120* | 10 | 3200 | 75 | 64 | 75 | 126.8 | 0.68 | 24.57
DVH120* | 10 | 3200 | 75 | 67 | 75 | 133.7 | 0.56 | 21.31
DVH120* | 10 | 3200 | 75 | 70 | 75 | 141.3 | 0.46 | 18.49
DVH120* | 10 | 3200 | 75 | 72 | 75 | 146.2 | 0.39 | 16.16
DVH120* | 10 | 3200 | 75 | 57 | 79 | 109.3 | 1 | 31.05
DVH120* | 10 | 3200 | 75 | 61 | 79 | 117.7 | 0.8 | 26.7
DVH120* | 10 | 3200 | 75 | 64 | 79 | 124.9 | 0.69 | 24.35
DVH120* | 10 | 3200 | 75 | 67 | 79 | 131.7 | 0.56 | 21.11
DVH120* | 10 | 3200 | 75 | 70 | 79 | 139.2 | 0.46 | 18.32
DVH120* | 10 | 3200 | 75 | 72 | 79 | 144 | 0.39 | 16.02
DVH120* | 10 | 3200 | 75 | 57 | 83 | 107.9 | 1 | 30.65
DVH120* | 10 | 3200 | 75 | 61 | 83 | 115.9 | 0.8 | 26.45
DVH120* | 10 | 3200 | 75 | 64 | 83 | 122.9 | 0.69 | 24.12
DVH120* | 10 | 3200 | 75 | 67 | 83 | 129.6 | 0.57 | 20.91
DVH120* | 10 | 3200 | 75 | 70 | 83 | 137.1 | 0.47 | 18.15
DVH120* | 10 | 3200 | 75 | 72 | 83 | 141.8 | 0.39 | 15.85
DVH120* | 10 | 3200 | 75 | 57 | 87 | 106.6 | 1 | 30.28
DVH120* | 10 | 3200 | 75 | 61 | 87 | 114.1 | 0.81 | 26.19
DVH120* | 10 | 3200 | 75 | 64 | 87 | 121 | 0.7 | 23.89
DVH120* | 10 | 3200 | 75 | 67 | 87 | 127.6 | 0.57 | 20.71
DVH120* | 10 | 3200 | 75 | 70 | 87 | 134.9 | 0.47 | 17.98
DVH120* | 10 | 3200 | 75 | 72 | 87 | 139.6 | 0.4 | 15.71
DVH120* | 10 | 3200 | 75 | 57 | 91 | 105.2 | 1 | 29.89
DVH120* | 10 | 3200 | 75 | 61 | 91 | 112.2 | 0.81 | 25.94
DVH120* | 10 | 3200 | 75 | 64 | 91 | 119.1 | 0.7 | 23.66
DVH120* | 10 | 3200 | 75 | 67 | 91 | 125.6 | 0.57 | 20.51
DVH120* | 10 | 3200 | 75 | 70 | 91 | 132.8 | 0.47 | 17.78
DVH120* | 10 | 3200 | 75 | 72 | 91 | 137.3 | 0.4 | 15.57
DVH120* | 10 | 3200 | 75 | 57 | 93 | 104.5 | 1 | 29.69
DVH120* | 10 | 3200 | 75 | 61 | 93 | 111.3 | 0.82 | 25.82
DVH120* | 10 | 3200 | 75 | 64 | 93 | 118.1 | 0.7 | 23.55
DVH120* | 10 | 3200 | 75 | 67 | 93 | 124.6 | 0.58 | 20.43
DVH120* | 10 | 3200 | 75 | 70 | 93 | 131.7 | 0.47 | 17.7
DVH120* | 10 | 3200 | 75 | 72 | 93 | 136.2 | 0.4 | 15.48
DVH120* | 10 | 3200 | 75 | 57 | 95 | 103.8 | 1 | 29.49
DVH120* | 10 | 3200 | 75 | 61 | 95 | 110.4 | 0.82 | 25.68
DVH120* | 10 | 3200 | 75 | 64 | 95 | 117.2 | 0.7 | 23.44
DVH120* | 10 | 3200 | 75 | 67 | 95 | 123.6 | 0.58 | 20.31
DVH120* | 10 | 3200 | 75 | 70 | 95 | 130.6 | 0.47 | 17.61
DVH120* | 10 | 3200 | 75 | 72 | 95 | 135.1 | 0.4 | 15.4
DVH120* | 10 | 3200 | 75 | 57 | 99 | 102.4 | 1 | 29.09
DVH120* | 10 | 3200 | 75 | 61 | 99 | 108.6 | 0.82 | 25.4
DVH120* | 10 | 3200 | 75 | 64 | 99 | 115.2 | 0.71 | 23.18
DVH120* | 10 | 3200 | 75 | 67 | 99 | 121.5 | 0.58 | 20.09
DVH120* | 10 | 3200 | 75 | 70 | 99 | 128.5 | 0.48 | 17.44
DVH120* | 10 | 3200 | 75 | 72 | 99 | 132.9 | 0.4 | 15.26
DVH120* | 10 | 3200 | 75 | 57 | 103 | 101.1 | 1 | 28.72
DVH120* | 10 | 3200 | 75 | 61 | 103 | 106.8 | 0.83 | 25.14
DVH120* | 10 | 3200 | 75 | 64 | 103 | 113.3 | 0.71 | 22.93
DVH120* | 10 | 3200 | 75 | 67 | 103 | 119.5 | 0.59 | 19.89
DVH120* | 10 | 3200 | 75 | 70 | 103 | 126.3 | 0.48 | 17.24
DVH120* | 10 | 3200 | 75 | 72 | 103 | 130.7 | 0.41 | 15.09
DVH120* | 10 | 3200 | 75 | 57 | 106 | 100 | 1 | 28.41
DVH120* | 10 | 3200 | 75 | 61 | 106 | 105.5 | 0.83 | 24.94
DVH120* | 10 | 3200 | 75 | 64 | 106 | 111.9 | 0.72 | 22.76
DVH120* | 10 | 3200 | 75 | 67 | 106 | 118 | 0.59 | 19.72
DVH120* | 10 | 3200 | 75 | 70 | 106 | 124.7 | 0.48 | 17.1
DVH120* | 10 | 3200 | 75 | 72 | 106 | 129 | 0.41 | 14.94
DVH120* | 10 | 3200 | 75 | 57 | 110 | 98.7 | 1 | 28.04
DVH120* | 10 | 3200 | 75 | 61 | 110 | 103.6 | 0.84 | 24.66
DVH120* | 10 | 3200 | 75 | 64 | 110 | 110 | 0.72 | 22.5
DVH120* | 10 | 3200 | 75 | 67 | 110 | 116 | 0.59 | 19.49
DVH120* | 10 | 3200 | 75 | 70 | 110 | 122.6 | 0.49 | 16.9
DVH120* | 10 | 3200 | 75 | 72 | 110 | 126.8 | 0.41 | 14.77
DVH120* | 10 | 3200 | 80 | 57 | 23 | 124.3 | 1 | 35.31
DVH120* | 10 | 3200 | 80 | 61 | 23 | 128.3 | 0.91 | 33.01
DVH120* | 10 | 3200 | 80 | 64 | 23 | 136.1 | 0.79 | 30.71
DVH120* | 10 | 3200 | 80 | 67 | 23 | 143.5 | 0.67 | 27.41
DVH120* | 10 | 3200 | 80 | 70 | 23 | 151.8 | 0.57 | 24.63
DVH120* | 10 | 3200 | 80 | 72 | 23 | 157 | 0.5 | 22.16
DVH120* | 10 | 3200 | 80 | 75 | 23 | 166 | 0.41 | 19.43
DVH120* | 10 | 3200 | 80 | 57 | 30 | 124.1 | 1 | 35.26
DVH120* | 10 | 3200 | 80 | 61 | 30 | 128.1 | 0.91 | 32.98
DVH120* | 10 | 3200 | 80 | 64 | 30 | 135.9 | 0.79 | 30.68
DVH120* | 10 | 3200 | 80 | 67 | 30 | 143.3 | 0.67 | 27.39
DVH120* | 10 | 3200 | 80 | 70 | 30 | 151.5 | 0.57 | 24.57
DVH120* | 10 | 3200 | 80 | 72 | 30 | 156.7 | 0.5 | 22.13
DVH120* | 10 | 3200 | 80 | 75 | 30 | 165.9 | 0.41 | 19.43
DVH120* | 10 | 3200 | 80 | 57 | 40 | 123.7 | 1 | 35.14
DVH120* | 10 | 3200 | 80 | 61 | 40 | 127.8 | 0.91 | 32.9
DVH120* | 10 | 3200 | 80 | 64 | 40 | 135.6 | 0.79 | 30.6
DVH120* | 10 | 3200 | 80 | 67 | 40 | 143 | 0.67 | 27.33
DVH120* | 10 | 3200 | 80 | 70 | 40 | 151.2 | 0.57 | 24.55
DVH120* | 10 | 3200 | 80 | 72 | 40 | 156.4 | 0.5 | 22.07
DVH120* | 10 | 3200 | 80 | 75 | 40 | 165.7 | 0.41 | 19.4
DVH120* | 10 | 3200 | 80 | 57 | 50 | 123.4 | 1 | 35.06
DVH120* | 10 | 3200 | 80 | 61 | 50 | 127.5 | 0.91 | 32.84
DVH120* | 10 | 3200 | 80 | 64 | 50 | 135.3 | 0.79 | 30.54
DVH120* | 10 | 3200 | 80 | 67 | 50 | 142.7 | 0.67 | 27.27
DVH120* | 10 | 3200 | 80 | 70 | 50 | 150.9 | 0.57 | 24.49
DVH120* | 10 | 3200 | 80 | 72 | 50 | 156.1 | 0.5 | 22.02
DVH120* | 10 | 3200 | 80 | 75 | 50 | 165.5 | 0.41 | 19.37
DVH120* | 10 | 3200 | 80 | 57 | 54 | 123.3 | 1 | 35.03
DVH120* | 10 | 3200 | 80 | 61 | 54 | 127.4 | 0.91 | 32.78
DVH120* | 10 | 3200 | 80 | 64 | 54 | 135.2 | 0.79 | 30.51
DVH120* | 10 | 3200 | 80 | 67 | 54 | 142.6 | 0.67 | 27.24
DVH120* | 10 | 3200 | 80 | 70 | 54 | 150.7 | 0.57 | 24.46
DVH120* | 10 | 3200 | 80 | 72 | 54 | 155.9 | 0.5 | 22.02
DVH120* | 10 | 3200 | 80 | 75 | 54 | 165.5 | 0.41 | 19.37
DVH120* | 10 | 3200 | 80 | 57 | 58 | 123.1 | 1 | 34.97
DVH120* | 10 | 3200 | 80 | 61 | 58 | 127.2 | 0.91 | 32.76
DVH120* | 10 | 3200 | 80 | 64 | 58 | 134.9 | 0.79 | 30.45
DVH120* | 10 | 3200 | 80 | 67 | 58 | 142.3 | 0.67 | 27.22
DVH120* | 10 | 3200 | 80 | 70 | 58 | 150.5 | 0.57 | 24.43
DVH120* | 10 | 3200 | 80 | 72 | 58 | 155.6 | 0.5 | 21.96
DVH120* | 10 | 3200 | 80 | 75 | 58 | 163.5 | 0.41 | 19.15
DVH120* | 10 | 3200 | 80 | 57 | 62 | 121.9 | 1 | 34.63
DVH120* | 10 | 3200 | 80 | 61 | 62 | 125.4 | 0.91 | 32.5
DVH120* | 10 | 3200 | 80 | 64 | 62 | 133 | 0.8 | 30.23
DVH120* | 10 | 3200 | 80 | 67 | 62 | 140.3 | 0.68 | 26.99
DVH120* | 10 | 3200 | 80 | 70 | 62 | 148.3 | 0.58 | 24.23
DVH120* | 10 | 3200 | 80 | 72 | 62 | 153.4 | 0.5 | 21.79
DVH120* | 10 | 3200 | 80 | 75 | 62 | 161.2 | 0.41 | 18.92
DVH120* | 10 | 3200 | 80 | 57 | 66 | 120.4 | 1 | 34.2
DVH120* | 10 | 3200 | 80 | 61 | 66 | 123.6 | 0.92 | 32.22
DVH120* | 10 | 3200 | 80 | 64 | 66 | 131.1 | 0.8 | 29.97
DVH120* | 10 | 3200 | 80 | 67 | 66 | 138.3 | 0.68 | 26.76
DVH120* | 10 | 3200 | 80 | 70 | 66 | 146.2 | 0.58 | 24.03
DVH120* | 10 | 3200 | 80 | 72 | 66 | 151.2 | 0.5 | 21.62
DVH120* | 10 | 3200 | 80 | 75 | 66 | 158.9 | 0.41 | 18.69
DVH120* | 10 | 3200 | 80 | 57 | 70 | 119 | 1 | 33.81
DVH120* | 10 | 3200 | 80 | 61 | 70 | 121.8 | 0.92 | 31.96
DVH120* | 10 | 3200 | 80 | 64 | 70 | 129.2 | 0.81 | 29.72
DVH120* | 10 | 3200 | 80 | 67 | 70 | 136.2 | 0.69 | 26.53
DVH120* | 10 | 3200 | 80 | 70 | 70 | 144 | 0.58 | 23.84
DVH120* | 10 | 3200 | 80 | 72 | 70 | 149 | 0.51 | 21.45
DVH120* | 10 | 3200 | 80 | 75 | 70 | 156.7 | 0.41 | 18.47
DVH120* | 10 | 3200 | 80 | 57 | 72 | 118.3 | 1 | 33.61
DVH120* | 10 | 3200 | 80 | 61 | 72 | 120.9 | 0.93 | 31.82
DVH120* | 10 | 3200 | 80 | 64 | 72 | 128.2 | 0.81 | 29.6
DVH120* | 10 | 3200 | 80 | 67 | 72 | 135.2 | 0.69 | 26.42
DVH120* | 10 | 3200 | 80 | 70 | 72 | 143 | 0.58 | 23.72
DVH120* | 10 | 3200 | 80 | 72 | 72 | 147.9 | 0.51 | 21.34
DVH120* | 10 | 3200 | 80 | 75 | 72 | 155.5 | 0.42 | 18.35
DVH120* | 10 | 3200 | 80 | 57 | 75 | 117.2 | 1 | 33.3
DVH120* | 10 | 3200 | 80 | 61 | 75 | 119.5 | 0.93 | 31.62
DVH120* | 10 | 3200 | 80 | 64 | 75 | 126.8 | 0.82 | 29.4
DVH120* | 10 | 3200 | 80 | 67 | 75 | 133.7 | 0.69 | 26.25
DVH120* | 10 | 3200 | 80 | 70 | 75 | 141.3 | 0.59 | 23.58
DVH120* | 10 | 3200 | 80 | 72 | 75 | 146.2 | 0.51 | 21.22
DVH120* | 10 | 3200 | 80 | 75 | 75 | 153.8 | 0.42 | 18.21
DVH120* | 10 | 3200 | 80 | 57 | 79 | 115.7 | 1 | 32.87
DVH120* | 10 | 3200 | 80 | 61 | 79 | 117.7 | 0.94 | 31.34
DVH120* | 10 | 3200 | 80 | 64 | 79 | 124.9 | 0.82 | 29.15
DVH120* | 10 | 3200 | 80 | 67 | 79 | 131.7 | 0.7 | 26.02
DVH120* | 10 | 3200 | 80 | 70 | 79 | 139.2 | 0.59 | 23.35
DVH120* | 10 | 3200 | 80 | 72 | 79 | 144 | 0.51 | 21.02
DVH120* | 10 | 3200 | 80 | 75 | 79 | 151.5 | 0.42 | 17.98
DVH120* | 10 | 3200 | 80 | 57 | 83 | 114.3 | 1 | 32.47
DVH120* | 10 | 3200 | 80 | 61 | 83 | 115.9 | 0.94 | 31.05
DVH120* | 10 | 3200 | 80 | 64 | 83 | 122.9 | 0.83 | 28.86
DVH120* | 10 | 3200 | 80 | 67 | 83 | 129.6 | 0.7 | 25.8
DVH120* | 10 | 3200 | 80 | 70 | 83 | 137.1 | 0.59 | 23.15
DVH120* | 10 | 3200 | 80 | 72 | 83 | 141.8 | 0.52 | 20.82
DVH120* | 10 | 3200 | 80 | 75 | 83 | 149.3 | 0.42 | 17.76
DVH120* | 10 | 3200 | 80 | 57 | 87 | 112.8 | 1 | 32.05
DVH120* | 10 | 3200 | 80 | 61 | 87 | 114.1 | 0.95 | 30.74
DVH120* | 10 | 3200 | 80 | 64 | 87 | 121 | 0.83 | 28.61
DVH120* | 10 | 3200 | 80 | 67 | 87 | 127.6 | 0.7 | 25.54
DVH120* | 10 | 3200 | 80 | 70 | 87 | 134.9 | 0.6 | 22.93
DVH120* | 10 | 3200 | 80 | 72 | 87 | 139.6 | 0.52 | 20.62
DVH120* | 10 | 3200 | 80 | 75 | 87 | 147 | 0.42 | 17.53
DVH120* | 10 | 3200 | 80 | 57 | 91 | 111.4 | 1 | 31.65
DVH120* | 10 | 3200 | 80 | 61 | 91 | 112.2 | 0.96 | 30.45
DVH120* | 10 | 3200 | 80 | 64 | 91 | 119.1 | 0.84 | 28.32
DVH120* | 10 | 3200 | 80 | 67 | 91 | 125.6 | 0.71 | 25.28
DVH120* | 10 | 3200 | 80 | 70 | 91 | 132.8 | 0.6 | 22.7
DVH120* | 10 | 3200 | 80 | 72 | 91 | 137.3 | 0.52 | 20.43
DVH120* | 10 | 3200 | 80 | 75 | 91 | 144.7 | 0.42 | 17.3
DVH120* | 10 | 3200 | 80 | 57 | 93 | 110.6 | 1 | 31.42
DVH120* | 10 | 3200 | 80 | 61 | 93 | 111.3 | 0.96 | 30.28
DVH120* | 10 | 3200 | 80 | 64 | 93 | 118.1 | 0.84 | 28.18
DVH120* | 10 | 3200 | 80 | 67 | 93 | 124.6 | 0.71 | 25.17
DVH120* | 10 | 3200 | 80 | 70 | 93 | 131.7 | 0.6 | 22.59
DVH120* | 10 | 3200 | 80 | 72 | 93 | 136.2 | 0.52 | 20.31
DVH120* | 10 | 3200 | 80 | 75 | 93 | 143.6 | 0.42 | 17.19
DVH120* | 10 | 3200 | 80 | 57 | 95 | 109.9 | 1 | 31.22
DVH120* | 10 | 3200 | 80 | 61 | 95 | 110.4 | 0.96 | 30.14
DVH120* | 10 | 3200 | 80 | 64 | 95 | 117.2 | 0.84 | 28.04
DVH120* | 10 | 3200 | 80 | 67 | 95 | 123.6 | 0.71 | 25.03
DVH120* | 10 | 3200 | 80 | 70 | 95 | 130.6 | 0.61 | 22.47
DVH120* | 10 | 3200 | 80 | 72 | 95 | 135.1 | 0.53 | 20.23
DVH120* | 10 | 3200 | 80 | 75 | 95 | 142.4 | 0.42 | 17.05
DVH120* | 10 | 3200 | 80 | 57 | 99 | 108.4 | 1 | 30.8
DVH120* | 10 | 3200 | 80 | 61 | 99 | 108.6 | 0.97 | 29.83
DVH120* | 10 | 3200 | 80 | 64 | 99 | 115.2 | 0.85 | 27.73
DVH120* | 10 | 3200 | 80 | 67 | 99 | 121.5 | 0.72 | 24.77
DVH120* | 10 | 3200 | 80 | 70 | 99 | 128.5 | 0.61 | 22.24
DVH120* | 10 | 3200 | 80 | 72 | 99 | 132.9 | 0.53 | 20
DVH120* | 10 | 3200 | 80 | 75 | 99 | 140.2 | 0.42 | 16.82
DVH120* | 10 | 3200 | 80 | 57 | 103 | 107 | 1 | 30.4
DVH120* | 10 | 3200 | 80 | 61 | 103 | 106.8 | 0.97 | 29.49
DVH120* | 10 | 3200 | 80 | 64 | 103 | 113.3 | 0.85 | 27.44
DVH120* | 10 | 3200 | 80 | 67 | 103 | 119.5 | 0.72 | 24.52
DVH120* | 10 | 3200 | 80 | 70 | 103 | 126.3 | 0.61 | 21.99
DVH120* | 10 | 3200 | 80 | 72 | 103 | 130.7 | 0.53 | 19.8
DVH120* | 10 | 3200 | 80 | 75 | 103 | 137.9 | 0.42 | 16.59
DVH120* | 10 | 3200 | 80 | 57 | 106 | 105.9 | 1 | 30.09
DVH120* | 10 | 3200 | 80 | 61 | 106 | 105.5 | 0.98 | 29.26
DVH120* | 10 | 3200 | 80 | 64 | 106 | 111.9 | 0.86 | 27.22
DVH120* | 10 | 3200 | 80 | 67 | 106 | 118 | 0.72 | 24.29
DVH120* | 10 | 3200 | 80 | 70 | 106 | 124.7 | 0.62 | 21.82
DVH120* | 10 | 3200 | 80 | 72 | 106 | 129 | 0.54 | 19.63
DVH120* | 10 | 3200 | 80 | 75 | 106 | 136.2 | 0.42 | 16.42
DVH120* | 10 | 3200 | 80 | 57 | 110 | 104.4 | 1 | 29.66
DVH120* | 10 | 3200 | 80 | 61 | 110 | 103.6 | 0.98 | 28.92
DVH120* | 10 | 3200 | 80 | 64 | 110 | 110 | 0.86 | 26.9
DVH120* | 10 | 3200 | 80 | 67 | 110 | 116 | 0.73 | 24.03
DVH120* | 10 | 3200 | 80 | 70 | 110 | 122.6 | 0.62 | 21.56
DVH120* | 10 | 3200 | 80 | 72 | 110 | 126.8 | 0.54 | 19.4
DVH120* | 10 | 3200 | 80 | 75 | 110 | 133.9 | 0.43 | 16.19
DVH120* | 10 | 3200 | 85 | 57 | 23 | 131.1 | 1 | 37.24
DVH120* | 10 | 3200 | 85 | 61 | 23 | 134.4 | 0.92 | 35.17
DVH120* | 10 | 3200 | 85 | 64 | 23 | 136.1 | 0.92 | 35.68
DVH120* | 10 | 3200 | 85 | 67 | 23 | 143.5 | 0.8 | 32.41
DVH120* | 10 | 3200 | 85 | 70 | 23 | 151.8 | 0.69 | 29.8
DVH120* | 10 | 3200 | 85 | 72 | 23 | 157 | 0.61 | 27.36
DVH120* | 10 | 3200 | 85 | 75 | 23 | 166 | 0.53 | 24.8
DVH120* | 10 | 3200 | 85 | 57 | 30 | 130.9 | 1 | 37.19
DVH120* | 10 | 3200 | 85 | 61 | 30 | 134.2 | 0.92 | 35.14
DVH120* | 10 | 3200 | 85 | 64 | 30 | 135.9 | 0.92 | 35.62
DVH120* | 10 | 3200 | 85 | 67 | 30 | 143.3 | 0.79 | 32.36
DVH120* | 10 | 3200 | 85 | 70 | 30 | 151.5 | 0.69 | 29.74
DVH120* | 10 | 3200 | 85 | 72 | 30 | 156.7 | 0.61 | 27.33
DVH120* | 10 | 3200 | 85 | 75 | 30 | 165.9 | 0.53 | 24.8
DVH120* | 10 | 3200 | 85 | 57 | 40 | 130.5 | 1 | 37.07
DVH120* | 10 | 3200 | 85 | 61 | 40 | 133.9 | 0.92 | 35.06
DVH120* | 10 | 3200 | 85 | 64 | 40 | 135.6 | 0.92 | 35.54
DVH120* | 10 | 3200 | 85 | 67 | 40 | 143 | 0.79 | 32.27
DVH120* | 10 | 3200 | 85 | 70 | 40 | 151.2 | 0.69 | 29.69
DVH120* | 10 | 3200 | 85 | 72 | 40 | 156.4 | 0.61 | 27.24
DVH120* | 10 | 3200 | 85 | 75 | 40 | 165.7 | 0.53 | 24.77
DVH120* | 10 | 3200 | 85 | 57 | 50 | 130.2 | 1 | 36.99
DVH120* | 10 | 3200 | 85 | 61 | 50 | 133.6 | 0.92 | 34.97
DVH120* | 10 | 3200 | 85 | 64 | 50 | 135.3 | 0.92 | 35.45
DVH120* | 10 | 3200 | 85 | 67 | 50 | 142.7 | 0.79 | 32.22
DVH120* | 10 | 3200 | 85 | 70 | 50 | 150.9 | 0.69 | 29.63
DVH120* | 10 | 3200 | 85 | 72 | 50 | 156.1 | 0.61 | 27.19
DVH120* | 10 | 3200 | 85 | 75 | 50 | 165.5 | 0.53 | 24.74
DVH120* | 10 | 3200 | 85 | 57 | 54 | 130 | 1 | 36.93
DVH120* | 10 | 3200 | 85 | 61 | 54 | 133.5 | 0.92 | 34.94
DVH120* | 10 | 3200 | 85 | 64 | 54 | 135.2 | 0.92 | 35.43
DVH120* | 10 | 3200 | 85 | 67 | 54 | 142.6 | 0.79 | 32.19
DVH120* | 10 | 3200 | 85 | 70 | 54 | 150.7 | 0.69 | 29.6
DVH120* | 10 | 3200 | 85 | 72 | 54 | 155.9 | 0.61 | 27.19
DVH120* | 10 | 3200 | 85 | 75 | 54 | 165.5 | 0.53 | 24.72
DVH120* | 10 | 3200 | 85 | 57 | 58 | 129.9 | 1 | 36.9
DVH120* | 10 | 3200 | 85 | 61 | 58 | 133.2 | 0.92 | 34.89
DVH120* | 10 | 3200 | 85 | 64 | 58 | 134.9 | 0.92 | 35.37
DVH120* | 10 | 3200 | 85 | 67 | 58 | 142.3 | 0.79 | 32.13
DVH120* | 10 | 3200 | 85 | 70 | 58 | 150.5 | 0.69 | 29.57
DVH120* | 10 | 3200 | 85 | 72 | 58 | 155.6 | 0.61 | 27.13
DVH120* | 10 | 3200 | 85 | 75 | 58 | 163.5 | 0.53 | 24.43
DVH120* | 10 | 3200 | 85 | 57 | 62 | 128.6 | 1 | 36.53
DVH120* | 10 | 3200 | 85 | 61 | 62 | 131.3 | 0.93 | 34.63
DVH120* | 10 | 3200 | 85 | 64 | 62 | 133 | 0.93 | 35.09
DVH120* | 10 | 3200 | 85 | 67 | 62 | 140.3 | 0.8 | 31.87
DVH120* | 10 | 3200 | 85 | 70 | 62 | 148.3 | 0.7 | 29.32
DVH120* | 10 | 3200 | 85 | 72 | 62 | 153.4 | 0.62 | 26.93
DVH120* | 10 | 3200 | 85 | 75 | 62 | 161.2 | 0.53 | 24.15
DVH120* | 10 | 3200 | 85 | 57 | 66 | 127 | 1 | 36.08
DVH120* | 10 | 3200 | 85 | 61 | 66 | 129.4 | 0.93 | 34.35
DVH120* | 10 | 3200 | 85 | 64 | 66 | 131.1 | 0.93 | 34.8
DVH120* | 10 | 3200 | 85 | 67 | 66 | 138.3 | 0.8 | 31.62
DVH120* | 10 | 3200 | 85 | 70 | 66 | 146.2 | 0.7 | 29.09
DVH120* | 10 | 3200 | 85 | 72 | 66 | 151.2 | 0.62 | 26.7
DVH120* | 10 | 3200 | 85 | 75 | 66 | 158.9 | 0.53 | 23.86
DVH120* | 10 | 3200 | 85 | 57 | 70 | 125.5 | 1 | 35.65
DVH120* | 10 | 3200 | 85 | 61 | 70 | 127.5 | 0.94 | 34.06
DVH120* | 10 | 3200 | 85 | 64 | 70 | 129.2 | 0.94 | 34.52
DVH120* | 10 | 3200 | 85 | 67 | 70 | 136.2 | 0.81 | 31.36
DVH120* | 10 | 3200 | 85 | 70 | 70 | 144 | 0.7 | 28.84
DVH120* | 10 | 3200 | 85 | 72 | 70 | 149 | 0.63 | 26.48
DVH120* | 10 | 3200 | 85 | 75 | 70 | 156.7 | 0.53 | 23.58
DVH120* | 10 | 3200 | 85 | 57 | 72 | 124.7 | 1 | 35.43
DVH120* | 10 | 3200 | 85 | 61 | 72 | 126.6 | 0.94 | 33.89
DVH120* | 10 | 3200 | 85 | 64 | 72 | 128.2 | 0.94 | 34.37
DVH120* | 10 | 3200 | 85 | 67 | 72 | 135.2 | 0.81 | 31.22
DVH120* | 10 | 3200 | 85 | 70 | 72 | 143 | 0.71 | 28.72
DVH120* | 10 | 3200 | 85 | 72 | 72 | 147.9 | 0.63 | 26.36
DVH120* | 10 | 3200 | 85 | 75 | 72 | 155.5 | 0.53 | 23.44
DVH120* | 10 | 3200 | 85 | 57 | 75 | 123.6 | 1 | 35.11
DVH120* | 10 | 3200 | 85 | 61 | 75 | 125.2 | 0.95 | 33.69
DVH120* | 10 | 3200 | 85 | 64 | 75 | 126.8 | 0.95 | 34.15
DVH120* | 10 | 3200 | 85 | 67 | 75 | 133.7 | 0.82 | 31.02
DVH120* | 10 | 3200 | 85 | 70 | 75 | 141.3 | 0.71 | 28.52
DVH120* | 10 | 3200 | 85 | 72 | 75 | 146.2 | 0.63 | 26.19
DVH120* | 10 | 3200 | 85 | 75 | 75 | 153.8 | 0.53 | 23.24
DVH120* | 10 | 3200 | 85 | 57 | 79 | 122.1 | 1 | 34.69
DVH120* | 10 | 3200 | 85 | 61 | 79 | 123.3 | 0.95 | 33.38
DVH120* | 10 | 3200 | 85 | 64 | 79 | 124.9 | 0.95 | 33.84
DVH120* | 10 | 3200 | 85 | 67 | 79 | 131.7 | 0.82 | 30.74
DVH120* | 10 | 3200 | 85 | 70 | 79 | 139.2 | 0.71 | 28.27
DVH120* | 10 | 3200 | 85 | 72 | 79 | 144 | 0.63 | 25.97
DVH120* | 10 | 3200 | 85 | 75 | 79 | 151.5 | 0.53 | 22.95
DVH120* | 10 | 3200 | 85 | 57 | 83 | 120.5 | 1 | 34.23
DVH120* | 10 | 3200 | 85 | 61 | 83 | 121.4 | 0.96 | 33.07
DVH120* | 10 | 3200 | 85 | 64 | 83 | 122.9 | 0.96 | 33.52
DVH120* | 10 | 3200 | 85 | 67 | 83 | 129.6 | 0.83 | 30.45
DVH120* | 10 | 3200 | 85 | 70 | 83 | 137.1 | 0.72 | 28.01
DVH120* | 10 | 3200 | 85 | 72 | 83 | 141.8 | 0.64 | 25.71
DVH120* | 10 | 3200 | 85 | 75 | 83 | 149.3 | 0.53 | 22.64
DVH120* | 10 | 3200 | 85 | 57 | 87 | 119 | 1 | 33.81
DVH120* | 10 | 3200 | 85 | 61 | 87 | 119.5 | 0.96 | 32.76
DVH120* | 10 | 3200 | 85 | 64 | 87 | 121 | 0.97 | 33.21
DVH120* | 10 | 3200 | 85 | 67 | 87 | 127.6 | 0.83 | 30.17
DVH120* | 10 | 3200 | 85 | 70 | 87 | 134.9 | 0.72 | 27.76
DVH120* | 10 | 3200 | 85 | 72 | 87 | 139.6 | 0.64 | 25.48
DVH120* | 10 | 3200 | 85 | 75 | 87 | 147 | 0.54 | 22.36
DVH120* | 10 | 3200 | 85 | 57 | 91 | 117.5 | 1 | 33.38
DVH120* | 10 | 3200 | 85 | 61 | 91 | 117.6 | 0.97 | 32.44
DVH120* | 10 | 3200 | 85 | 64 | 91 | 119.1 | 0.97 | 32.9
DVH120* | 10 | 3200 | 85 | 67 | 91 | 125.6 | 0.84 | 29.89
DVH120* | 10 | 3200 | 85 | 70 | 91 | 132.8 | 0.73 | 27.47
DVH120* | 10 | 3200 | 85 | 72 | 91 | 137.3 | 0.65 | 25.23
DVH120* | 10 | 3200 | 85 | 75 | 91 | 144.7 | 0.54 | 22.07
DVH120* | 10 | 3200 | 85 | 57 | 93 | 116.7 | 1 | 33.15
DVH120* | 10 | 3200 | 85 | 61 | 93 | 116.6 | 0.97 | 32.27
DVH120* | 10 | 3200 | 85 | 64 | 93 | 118.1 | 0.98 | 32.73
DVH120* | 10 | 3200 | 85 | 67 | 93 | 124.6 | 0.84 | 29.72
DVH120* | 10 | 3200 | 85 | 70 | 93 | 131.7 | 0.73 | 27.33
DVH120* | 10 | 3200 | 85 | 72 | 93 | 136.2 | 0.65 | 25.09
DVH120* | 10 | 3200 | 85 | 75 | 93 | 143.6 | 0.54 | 21.93
DVH120* | 10 | 3200 | 85 | 57 | 95 | 115.9 | 1 | 32.93
DVH120* | 10 | 3200 | 85 | 61 | 95 | 115.7 | 0.98 | 32.1
DVH120* | 10 | 3200 | 85 | 64 | 95 | 117.2 | 0.98 | 32.56
DVH120* | 10 | 3200 | 85 | 67 | 95 | 123.6 | 0.84 | 29.57
DVH120* | 10 | 3200 | 85 | 70 | 95 | 130.6 | 0.73 | 27.19
DVH120* | 10 | 3200 | 85 | 72 | 95 | 135.1 | 0.65 | 24.97
DVH120* | 10 | 3200 | 85 | 75 | 95 | 142.4 | 0.54 | 21.79
DVH120* | 10 | 3200 | 85 | 57 | 99 | 114.4 | 1 | 32.5
DVH120* | 10 | 3200 | 85 | 61 | 99 | 113.8 | 0.98 | 31.76
DVH120* | 10 | 3200 | 85 | 64 | 99 | 115.2 | 0.98 | 32.22
DVH120* | 10 | 3200 | 85 | 67 | 99 | 121.5 | 0.85 | 29.26
DVH120* | 10 | 3200 | 85 | 70 | 99 | 128.5 | 0.74 | 26.9
DVH120* | 10 | 3200 | 85 | 72 | 99 | 132.9 | 0.65 | 24.72
DVH120* | 10 | 3200 | 85 | 75 | 99 | 140.2 | 0.54 | 21.48
DVH120* | 10 | 3200 | 85 | 57 | 103 | 112.9 | 1 | 32.07
DVH120* | 10 | 3200 | 85 | 61 | 103 | 111.9 | 1 | 31.79
DVH120* | 10 | 3200 | 85 | 64 | 103 | 113.3 | 1 | 32.19
DVH120* | 10 | 3200 | 85 | 67 | 103 | 119.5 | 0.85 | 28.95
DVH120* | 10 | 3200 | 85 | 70 | 103 | 126.3 | 0.74 | 26.62
DVH120* | 10 | 3200 | 85 | 72 | 103 | 130.7 | 0.66 | 24.43
DVH120* | 10 | 3200 | 85 | 75 | 103 | 137.9 | 0.54 | 21.19
DVH120* | 10 | 3200 | 85 | 57 | 106 | 111.7 | 1 | 31.73
DVH120* | 10 | 3200 | 85 | 61 | 106 | 110.5 | 1 | 31.39
DVH120* | 10 | 3200 | 85 | 64 | 106 | 111.9 | 1 | 31.79
DVH120* | 10 | 3200 | 85 | 67 | 106 | 118 | 0.86 | 28.72
DVH120* | 10 | 3200 | 85 | 70 | 106 | 124.7 | 0.75 | 26.42
DVH120* | 10 | 3200 | 85 | 72 | 106 | 129 | 0.66 | 24.23
DVH120* | 10 | 3200 | 85 | 75 | 106 | 136.2 | 0.54 | 20.97
DVH120* | 10 | 3200 | 85 | 57 | 110 | 110.2 | 1 | 31.31
DVH120* | 10 | 3200 | 85 | 61 | 110 | 108.6 | 1 | 30.85
DVH120* | 10 | 3200 | 85 | 64 | 110 | 110 | 1 | 31.25
DVH120* | 10 | 3200 | 85 | 67 | 110 | 116 | 0.86 | 28.38
DVH120* | 10 | 3200 | 85 | 70 | 110 | 122.6 | 0.75 | 26.11
DVH120* | 10 | 3200 | 85 | 72 | 110 | 126.8 | 0.67 | 23.98
DVH120* | 10 | 3200 | 85 | 75 | 110 | 133.9 | 0.54 | 20.65
DVH120* | 10 | 3600 | 70 | 57 | 23 | 118.9 | 0.85 | 25.61
DVH120* | 10 | 3600 | 70 | 61 | 23 | 131.2 | 0.64 | 21.34
DVH120* | 10 | 3600 | 70 | 64 | 23 | 139.2 | 0.54 | 18.81
DVH120* | 10 | 3600 | 70 | 67 | 23 | 146.8 | 0.42 | 15.66
DVH120* | 10 | 3600 | 70 | 57 | 30 | 118.6 | 0.85 | 25.58
DVH120* | 10 | 3600 | 70 | 61 | 30 | 131 | 0.64 | 21.31
DVH120* | 10 | 3600 | 70 | 64 | 30 | 139 | 0.53 | 18.76
DVH120* | 10 | 3600 | 70 | 67 | 30 | 146.6 | 0.42 | 15.63
DVH120* | 10 | 3600 | 70 | 57 | 40 | 118.3 | 0.85 | 25.51
DVH120* | 10 | 3600 | 70 | 61 | 40 | 130.8 | 0.64 | 21.26
DVH120* | 10 | 3600 | 70 | 64 | 40 | 138.7 | 0.53 | 18.74
DVH120* | 10 | 3600 | 70 | 67 | 40 | 146.3 | 0.42 | 15.61
DVH120* | 10 | 3600 | 70 | 57 | 50 | 118 | 0.85 | 25.43
DVH120* | 10 | 3600 | 70 | 61 | 50 | 130.5 | 0.64 | 21.21
DVH120* | 10 | 3600 | 70 | 64 | 50 | 138.4 | 0.53 | 18.69
DVH120* | 10 | 3600 | 70 | 67 | 50 | 146 | 0.42 | 15.56
DVH120* | 10 | 3600 | 70 | 57 | 54 | 117.9 | 0.85 | 25.4
DVH120* | 10 | 3600 | 70 | 61 | 54 | 130.4 | 0.64 | 21.21
DVH120* | 10 | 3600 | 70 | 64 | 54 | 138.3 | 0.54 | 18.69
DVH120* | 10 | 3600 | 70 | 67 | 54 | 145.8 | 0.42 | 15.56
DVH120* | 10 | 3600 | 70 | 57 | 58 | 117.7 | 0.85 | 25.38
DVH120* | 10 | 3600 | 70 | 61 | 58 | 130.1 | 0.64 | 21.16
DVH120* | 10 | 3600 | 70 | 64 | 58 | 138 | 0.53 | 18.64
DVH120* | 10 | 3600 | 70 | 67 | 58 | 145.6 | 0.42 | 15.53
DVH120* | 10 | 3600 | 70 | 57 | 62 | 116.5 | 0.86 | 25.18
DVH120* | 10 | 3600 | 70 | 61 | 62 | 128.3 | 0.65 | 21.01
DVH120* | 10 | 3600 | 70 | 64 | 62 | 136.1 | 0.54 | 18.51
DVH120* | 10 | 3600 | 70 | 67 | 62 | 143.5 | 0.43 | 15.4
DVH120* | 10 | 3600 | 70 | 57 | 66 | 115.1 | 0.86 | 24.95
DVH120* | 10 | 3600 | 70 | 61 | 66 | 126.4 | 0.65 | 20.83
DVH120* | 10 | 3600 | 70 | 64 | 66 | 134.1 | 0.54 | 18.36
DVH120* | 10 | 3600 | 70 | 67 | 66 | 141.4 | 0.43 | 15.28
DVH120* | 10 | 3600 | 70 | 57 | 70 | 113.8 | 0.86 | 24.7
DVH120* | 10 | 3600 | 70 | 61 | 70 | 124.6 | 0.66 | 20.66
DVH120* | 10 | 3600 | 70 | 64 | 70 | 132.1 | 0.55 | 18.21
DVH120* | 10 | 3600 | 70 | 67 | 70 | 139.4 | 0.43 | 15.15
DVH120* | 10 | 3600 | 70 | 57 | 72 | 113.1 | 0.86 | 24.57
DVH120* | 10 | 3600 | 70 | 61 | 72 | 123.6 | 0.66 | 20.58
DVH120* | 10 | 3600 | 70 | 64 | 72 | 131.2 | 0.55 | 18.13
DVH120* | 10 | 3600 | 70 | 67 | 72 | 138.3 | 0.43 | 15.08
DVH120* | 10 | 3600 | 70 | 57 | 75 | 112 | 0.86 | 24.39
DVH120* | 10 | 3600 | 70 | 61 | 75 | 122.2 | 0.66 | 20.43
DVH120* | 10 | 3600 | 70 | 64 | 75 | 129.7 | 0.55 | 18.01
DVH120* | 10 | 3600 | 70 | 67 | 75 | 136.8 | 0.43 | 15
DVH120* | 10 | 3600 | 70 | 57 | 79 | 110.6 | 0.87 | 24.17
DVH120* | 10 | 3600 | 70 | 61 | 79 | 120.4 | 0.67 | 20.25
DVH120* | 10 | 3600 | 70 | 64 | 79 | 127.7 | 0.55 | 17.83
DVH120* | 10 | 3600 | 70 | 67 | 79 | 134.7 | 0.44 | 14.85
DVH120* | 10 | 3600 | 70 | 57 | 83 | 109.2 | 0.87 | 23.91
DVH120* | 10 | 3600 | 70 | 61 | 83 | 118.5 | 0.67 | 20.05
DVH120* | 10 | 3600 | 70 | 64 | 83 | 125.8 | 0.56 | 17.68
DVH120* | 10 | 3600 | 70 | 67 | 83 | 132.6 | 0.44 | 14.72
DVH120* | 10 | 3600 | 70 | 57 | 87 | 107.8 | 0.87 | 23.66
DVH120* | 10 | 3600 | 70 | 61 | 87 | 116.7 | 0.67 | 19.87
DVH120* | 10 | 3600 | 70 | 64 | 87 | 123.8 | 0.56 | 17.5
DVH120* | 10 | 3600 | 70 | 67 | 87 | 130.5 | 0.44 | 14.57
DVH120* | 10 | 3600 | 70 | 57 | 91 | 106.5 | 0.87 | 23.41
DVH120* | 10 | 3600 | 70 | 61 | 91 | 114.8 | 0.68 | 19.67
DVH120* | 10 | 3600 | 70 | 64 | 91 | 121.8 | 0.56 | 17.32
DVH120* | 10 | 3600 | 70 | 67 | 91 | 128.5 | 0.45 | 14.44
DVH120* | 10 | 3600 | 70 | 57 | 93 | 105.8 | 0.87 | 23.28
DVH120* | 10 | 3600 | 70 | 61 | 93 | 113.9 | 0.68 | 19.57
DVH120* | 10 | 3600 | 70 | 64 | 93 | 120.8 | 0.57 | 17.25
DVH120* | 10 | 3600 | 70 | 67 | 93 | 127.4 | 0.45 | 14.37
DVH120* | 10 | 3600 | 70 | 57 | 95 | 105.1 | 0.87 | 23.18
DVH120* | 10 | 3600 | 70 | 61 | 95 | 113 | 0.68 | 19.47
DVH120* | 10 | 3600 | 70 | 64 | 95 | 119.9 | 0.57 | 17.15
DVH120* | 10 | 3600 | 70 | 67 | 95 | 126.4 | 0.45 | 14.29
DVH120* | 10 | 3600 | 70 | 57 | 99 | 103.7 | 0.88 | 22.93
DVH120* | 10 | 3600 | 70 | 61 | 99 | 111.1 | 0.69 | 19.27
DVH120* | 10 | 3600 | 70 | 64 | 99 | 117.9 | 0.57 | 16.97
DVH120* | 10 | 3600 | 70 | 67 | 99 | 124.3 | 0.45 | 14.14
DVH120* | 10 | 3600 | 70 | 57 | 103 | 102.3 | 0.88 | 22.68
DVH120* | 10 | 3600 | 70 | 61 | 103 | 109.3 | 0.69 | 19.07
DVH120* | 10 | 3600 | 70 | 64 | 103 | 115.9 | 0.57 | 16.79
DVH120* | 10 | 3600 | 70 | 67 | 103 | 122.2 | 0.45 | 13.99
DVH120* | 10 | 3600 | 70 | 57 | 106 | 101.2 | 0.88 | 22.47
DVH120* | 10 | 3600 | 70 | 61 | 106 | 107.9 | 0.69 | 18.91
DVH120* | 10 | 3600 | 70 | 64 | 106 | 114.5 | 0.58 | 16.67
DVH120* | 10 | 3600 | 70 | 67 | 106 | 120.7 | 0.45 | 13.86
DVH120* | 10 | 3600 | 70 | 57 | 110 | 99.9 | 0.88 | 22.22
DVH120* | 10 | 3600 | 70 | 61 | 110 | 106 | 0.7 | 18.69
DVH120* | 10 | 3600 | 70 | 64 | 110 | 112.5 | 0.58 | 16.46
DVH120* | 10 | 3600 | 70 | 67 | 110 | 118.6 | 0.46 | 13.71
DVH120* | 10 | 3600 | 75 | 57 | 23 | 120.1 | 1 | 30.33
DVH120* | 10 | 3600 | 75 | 61 | 23 | 131.2 | 0.78 | 25.96
DVH120* | 10 | 3600 | 75 | 64 | 23 | 139.2 | 0.67 | 23.69
DVH120* | 10 | 3600 | 75 | 67 | 23 | 146.8 | 0.55 | 20.53
DVH120* | 10 | 3600 | 75 | 70 | 23 | 155.2 | 0.45 | 17.8
DVH120* | 10 | 3600 | 75 | 72 | 23 | 160.6 | 0.38 | 15.58
DVH120* | 10 | 3600 | 75 | 57 | 30 | 119.9 | 1 | 30.28
DVH120* | 10 | 3600 | 75 | 61 | 30 | 131 | 0.78 | 25.93
DVH120* | 10 | 3600 | 75 | 64 | 30 | 139 | 0.67 | 23.66
DVH120* | 10 | 3600 | 75 | 67 | 30 | 146.6 | 0.55 | 20.51
DVH120* | 10 | 3600 | 75 | 70 | 30 | 155 | 0.45 | 17.78
DVH120* | 10 | 3600 | 75 | 72 | 30 | 160.3 | 0.38 | 15.56
DVH120* | 10 | 3600 | 75 | 57 | 40 | 119.6 | 1 | 30.2
DVH120* | 10 | 3600 | 75 | 61 | 40 | 130.8 | 0.78 | 25.86
DVH120* | 10 | 3600 | 75 | 64 | 40 | 138.7 | 0.67 | 23.61
DVH120* | 10 | 3600 | 75 | 67 | 40 | 146.3 | 0.55 | 20.45
DVH120* | 10 | 3600 | 75 | 70 | 40 | 154.7 | 0.45 | 17.75
DVH120* | 10 | 3600 | 75 | 72 | 40 | 160 | 0.38 | 15.51
DVH120* | 10 | 3600 | 75 | 57 | 50 | 119.3 | 1 | 30.13
DVH120* | 10 | 3600 | 75 | 61 | 50 | 130.5 | 0.78 | 25.81
DVH120* | 10 | 3600 | 75 | 64 | 50 | 138.4 | 0.67 | 23.56
DVH120* | 10 | 3600 | 75 | 67 | 50 | 146 | 0.55 | 20.4
DVH120* | 10 | 3600 | 75 | 70 | 50 | 154.3 | 0.45 | 17.7
DVH120* | 10 | 3600 | 75 | 72 | 50 | 159.6 | 0.38 | 15.48
DVH120* | 10 | 3600 | 75 | 57 | 54 | 119.1 | 1 | 30.08
DVH120* | 10 | 3600 | 75 | 61 | 54 | 130.4 | 0.78 | 25.78
DVH120* | 10 | 3600 | 75 | 64 | 54 | 138.3 | 0.67 | 23.54
DVH120* | 10 | 3600 | 75 | 67 | 54 | 145.8 | 0.55 | 20.4
DVH120* | 10 | 3600 | 75 | 70 | 54 | 154.2 | 0.45 | 17.7
DVH120* | 10 | 3600 | 75 | 72 | 54 | 159.5 | 0.38 | 15.48
DVH120* | 10 | 3600 | 75 | 57 | 58 | 119 | 1 | 30.05
DVH120* | 10 | 3600 | 75 | 61 | 58 | 130.1 | 0.78 | 25.76
DVH120* | 10 | 3600 | 75 | 64 | 58 | 138 | 0.67 | 23.48
DVH120* | 10 | 3600 | 75 | 67 | 58 | 145.6 | 0.55 | 20.38
DVH120* | 10 | 3600 | 75 | 70 | 58 | 153.9 | 0.45 | 17.68
DVH120* | 10 | 3600 | 75 | 72 | 58 | 159.2 | 0.38 | 15.45
DVH120* | 10 | 3600 | 75 | 57 | 62 | 117.8 | 1 | 29.75
DVH120* | 10 | 3600 | 75 | 61 | 62 | 128.3 | 0.79 | 25.56
DVH120* | 10 | 3600 | 75 | 64 | 62 | 136.1 | 0.68 | 23.31
DVH120* | 10 | 3600 | 75 | 67 | 62 | 143.5 | 0.56 | 20.2
DVH120* | 10 | 3600 | 75 | 70 | 62 | 151.7 | 0.46 | 17.53
DVH120* | 10 | 3600 | 75 | 72 | 62 | 156.9 | 0.39 | 15.33
DVH120* | 10 | 3600 | 75 | 57 | 66 | 116.4 | 1 | 29.39
DVH120* | 10 | 3600 | 75 | 61 | 66 | 126.4 | 0.79 | 25.33
DVH120* | 10 | 3600 | 75 | 64 | 66 | 134.1 | 0.68 | 23.13
DVH120* | 10 | 3600 | 75 | 67 | 66 | 141.4 | 0.56 | 20.05
DVH120* | 10 | 3600 | 75 | 70 | 66 | 149.5 | 0.46 | 17.37
DVH120* | 10 | 3600 | 75 | 72 | 66 | 154.7 | 0.39 | 15.2
DVH120* | 10 | 3600 | 75 | 57 | 70 | 115 | 1 | 29.04
DVH120* | 10 | 3600 | 75 | 61 | 70 | 124.6 | 0.8 | 25.13
DVH120* | 10 | 3600 | 75 | 64 | 70 | 132.1 | 0.69 | 22.93
DVH120* | 10 | 3600 | 75 | 67 | 70 | 139.4 | 0.56 | 19.87
DVH120* | 10 | 3600 | 75 | 70 | 70 | 147.3 | 0.46 | 17.25
DVH120* | 10 | 3600 | 75 | 72 | 70 | 152.4 | 0.39 | 15.08
DVH120* | 10 | 3600 | 75 | 57 | 72 | 114.3 | 1 | 28.86
DVH120* | 10 | 3600 | 75 | 61 | 72 | 123.6 | 0.8 | 25.03
DVH120* | 10 | 3600 | 75 | 64 | 72 | 131.2 | 0.69 | 22.83
DVH120* | 10 | 3600 | 75 | 67 | 72 | 138.3 | 0.57 | 19.8
DVH120* | 10 | 3600 | 75 | 70 | 72 | 146.2 | 0.47 | 17.17
DVH120* | 10 | 3600 | 75 | 72 | 72 | 151.3 | 0.39 | 15
DVH120* | 10 | 3600 | 75 | 57 | 75 | 113.2 | 1 | 28.59
DVH120* | 10 | 3600 | 75 | 61 | 75 | 122.2 | 0.81 | 24.85
DVH120* | 10 | 3600 | 75 | 64 | 75 | 129.7 | 0.69 | 22.68
DVH120* | 10 | 3600 | 75 | 67 | 75 | 136.8 | 0.57 | 19.65
DVH120* | 10 | 3600 | 75 | 70 | 75 | 144.6 | 0.47 | 17.05
DVH120* | 10 | 3600 | 75 | 72 | 75 | 149.6 | 0.39 | 14.9
DVH120* | 10 | 3600 | 75 | 57 | 79 | 111.8 | 1 | 28.23
DVH120* | 10 | 3600 | 75 | 61 | 79 | 120.4 | 0.81 | 24.62
DVH120* | 10 | 3600 | 75 | 64 | 79 | 127.7 | 0.7 | 22.47
DVH120* | 10 | 3600 | 75 | 67 | 79 | 134.7 | 0.57 | 19.49
DVH120* | 10 | 3600 | 75 | 70 | 79 | 142.4 | 0.47 | 16.89
DVH120* | 10 | 3600 | 75 | 72 | 79 | 147.3 | 0.4 | 14.77
DVH120* | 10 | 3600 | 75 | 57 | 83 | 110.4 | 1 | 27.88
DVH120* | 10 | 3600 | 75 | 61 | 83 | 118.5 | 0.82 | 24.39
DVH120* | 10 | 3600 | 75 | 64 | 83 | 125.8 | 0.7 | 22.27
DVH120* | 10 | 3600 | 75 | 67 | 83 | 132.6 | 0.58 | 19.29
DVH120* | 10 | 3600 | 75 | 70 | 83 | 140.2 | 0.47 | 16.74
DVH120* | 10 | 3600 | 75 | 72 | 83 | 145 | 0.4 | 14.65
DVH120* | 10 | 3600 | 75 | 57 | 87 | 109 | 1 | 27.53
DVH120* | 10 | 3600 | 75 | 61 | 87 | 116.7 | 0.82 | 24.17
DVH120* | 10 | 3600 | 75 | 64 | 87 | 123.8 | 0.71 | 22.05
DVH120* | 10 | 3600 | 75 | 67 | 87 | 130.5 | 0.58 | 19.12
DVH120* | 10 | 3600 | 75 | 70 | 87 | 138 | 0.48 | 16.59
DVH120* | 10 | 3600 | 75 | 72 | 87 | 142.8 | 0.4 | 14.49
DVH120* | 10 | 3600 | 75 | 57 | 91 | 107.6 | 1 | 27.17
DVH120* | 10 | 3600 | 75 | 61 | 91 | 114.8 | 0.83 | 23.94
DVH120* | 10 | 3600 | 75 | 64 | 91 | 121.8 | 0.71 | 21.84
DVH120* | 10 | 3600 | 75 | 67 | 91 | 128.5 | 0.58 | 18.94
DVH120* | 10 | 3600 | 75 | 70 | 91 | 135.8 | 0.48 | 16.41
DVH120* | 10 | 3600 | 75 | 72 | 91 | 140.5 | 0.4 | 14.37
DVH120* | 10 | 3600 | 75 | 57 | 93 | 106.9 | 1 | 26.99
DVH120* | 10 | 3600 | 75 | 61 | 93 | 113.9 | 0.83 | 23.81
DVH120* | 10 | 3600 | 75 | 64 | 93 | 120.8 | 0.71 | 21.72
DVH120* | 10 | 3600 | 75 | 67 | 93 | 127.4 | 0.59 | 18.84
DVH120* | 10 | 3600 | 75 | 70 | 93 | 134.7 | 0.48 | 16.34
DVH120* | 10 | 3600 | 75 | 72 | 93 | 139.4 | 0.41 | 14.29
DVH120* | 10 | 3600 | 75 | 57 | 95 | 106.2 | 1 | 26.82
DVH120* | 10 | 3600 | 75 | 61 | 95 | 113 | 0.83 | 23.69
DVH120* | 10 | 3600 | 75 | 64 | 95 | 119.9 | 0.71 | 21.62
DVH120* | 10 | 3600 | 75 | 67 | 95 | 126.4 | 0.59 | 18.74
DVH120* | 10 | 3600 | 75 | 70 | 95 | 133.6 | 0.48 | 16.26
DVH120* | 10 | 3600 | 75 | 72 | 95 | 138.2 | 0.41 | 14.22
DVH120* | 10 | 3600 | 75 | 57 | 99 | 104.8 | 1 | 26.46
DVH120* | 10 | 3600 | 75 | 61 | 99 | 111.1 | 0.84 | 23.43
DVH120* | 10 | 3600 | 75 | 64 | 99 | 117.9 | 0.72 | 21.39
DVH120* | 10 | 3600 | 75 | 67 | 99 | 124.3 | 0.59 | 18.54
DVH120* | 10 | 3600 | 75 | 70 | 99 | 131.4 | 0.48 | 16.09
DVH120* | 10 | 3600 | 75 | 72 | 99 | 136 | 0.41 | 14.07
DVH120* | 10 | 3600 | 75 | 57 | 103 | 103.4 | 1 | 26.11
DVH120* | 10 | 3600 | 75 | 61 | 103 | 109.3 | 0.84 | 23.21
DVH120* | 10 | 3600 | 75 | 64 | 103 | 115.9 | 0.72 | 21.16
DVH120* | 10 | 3600 | 75 | 67 | 103 | 122.2 | 0.59 | 18.33
DVH120* | 10 | 3600 | 75 | 70 | 103 | 129.2 | 0.49 | 15.91
DVH120* | 10 | 3600 | 75 | 72 | 103 | 133.7 | 0.41 | 13.91
DVH120* | 10 | 3600 | 75 | 57 | 106 | 102.3 | 1 | 25.83
DVH120* | 10 | 3600 | 75 | 61 | 106 | 107.9 | 0.84 | 23.01
DVH120* | 10 | 3600 | 75 | 64 | 106 | 114.5 | 0.73 | 20.98
DVH120* | 10 | 3600 | 75 | 67 | 106 | 120.7 | 0.6 | 18.18
DVH120* | 10 | 3600 | 75 | 70 | 106 | 127.6 | 0.49 | 15.78
DVH120* | 10 | 3600 | 75 | 72 | 106 | 132 | 0.41 | 13.79
DVH120* | 10 | 3600 | 75 | 57 | 110 | 100.9 | 1 | 25.48
DVH120* | 10 | 3600 | 75 | 61 | 110 | 106 | 0.85 | 22.75
DVH120* | 10 | 3600 | 75 | 64 | 110 | 112.5 | 0.73 | 20.76
DVH120* | 10 | 3600 | 75 | 67 | 110 | 118.6 | 0.6 | 17.98
DVH120* | 10 | 3600 | 75 | 70 | 110 | 125.4 | 0.49 | 15.61
DVH120* | 10 | 3600 | 75 | 72 | 110 | 129.7 | 0.42 | 13.64
DVH120* | 10 | 3600 | 80 | 57 | 23 | 127.2 | 1 | 32.12
DVH120* | 10 | 3600 | 80 | 61 | 23 | 131.2 | 0.92 | 30.45
DVH120* | 10 | 3600 | 80 | 64 | 23 | 139.2 | 0.81 | 28.33
DVH120* | 10 | 3600 | 80 | 67 | 23 | 146.8 | 0.68 | 25.3
DVH120* | 10 | 3600 | 80 | 70 | 23 | 155.2 | 0.58 | 22.73
DVH120* | 10 | 3600 | 80 | 72 | 23 | 160.6 | 0.5 | 20.43
DVH120* | 10 | 3600 | 80 | 75 | 23 | 169.8 | 0.42 | 17.93
DVH120* | 10 | 3600 | 80 | 57 | 30 | 126.9 | 1 | 32.05
DVH120* | 10 | 3600 | 80 | 61 | 30 | 131 | 0.92 | 30.43
DVH120* | 10 | 3600 | 80 | 64 | 30 | 139 | 0.81 | 28.31
DVH120* | 10 | 3600 | 80 | 67 | 30 | 146.6 | 0.68 | 25.28
DVH120* | 10 | 3600 | 80 | 70 | 30 | 155 | 0.58 | 22.68
DVH120* | 10 | 3600 | 80 | 72 | 30 | 160.3 | 0.5 | 20.4
DVH120* | 10 | 3600 | 80 | 75 | 30 | 169.7 | 0.42 | 17.93
DVH120* | 10 | 3600 | 80 | 57 | 40 | 126.6 | 1 | 31.97
DVH120* | 10 | 3600 | 80 | 61 | 40 | 130.8 | 0.92 | 30.35
DVH120* | 10 | 3600 | 80 | 64 | 40 | 138.7 | 0.81 | 28.23
DVH120* | 10 | 3600 | 80 | 67 | 40 | 146.3 | 0.68 | 25.23
DVH120* | 10 | 3600 | 80 | 70 | 40 | 154.7 | 0.58 | 22.63
DVH120* | 10 | 3600 | 80 | 72 | 40 | 160 | 0.5 | 20.35
DVH120* | 10 | 3600 | 80 | 75 | 40 | 169.5 | 0.42 | 17.9
DVH120* | 10 | 3600 | 80 | 57 | 50 | 126.2 | 1 | 31.87
DVH120* | 10 | 3600 | 80 | 61 | 50 | 130.5 | 0.92 | 30.28
DVH120* | 10 | 3600 | 80 | 64 | 50 | 138.4 | 0.81 | 28.18
DVH120* | 10 | 3600 | 80 | 67 | 50 | 146 | 0.68 | 25.15
DVH120* | 10 | 3600 | 80 | 70 | 50 | 154.3 | 0.58 | 22.58
DVH120* | 10 | 3600 | 80 | 72 | 50 | 159.6 | 0.5 | 20.33
DVH120* | 10 | 3600 | 80 | 75 | 50 | 169.3 | 0.42 | 17.88
DVH120* | 10 | 3600 | 80 | 57 | 54 | 126.1 | 1 | 31.84
DVH120* | 10 | 3600 | 80 | 61 | 54 | 130.4 | 0.92 | 30.25
DVH120* | 10 | 3600 | 80 | 64 | 54 | 138.3 | 0.81 | 28.16
DVH120* | 10 | 3600 | 80 | 67 | 54 | 145.8 | 0.68 | 25.13
DVH120* | 10 | 3600 | 80 | 70 | 54 | 154.2 | 0.58 | 22.58
DVH120* | 10 | 3600 | 80 | 72 | 54 | 159.5 | 0.5 | 20.3
DVH120* | 10 | 3600 | 80 | 75 | 54 | 169.3 | 0.42 | 17.88
DVH120* | 10 | 3600 | 80 | 57 | 58 | 126 | 1 | 31.82
DVH120* | 10 | 3600 | 80 | 61 | 58 | 130.1 | 0.92 | 30.23
DVH120* | 10 | 3600 | 80 | 64 | 58 | 138 | 0.81 | 28.11
DVH120* | 10 | 3600 | 80 | 67 | 58 | 145.6 | 0.68 | 25.1
DVH120* | 10 | 3600 | 80 | 70 | 58 | 153.9 | 0.58 | 22.53
DVH120* | 10 | 3600 | 80 | 72 | 58 | 159.2 | 0.5 | 20.28
DVH120* | 10 | 3600 | 80 | 75 | 58 | 167.2 | 0.42 | 17.65
DVH120* | 10 | 3600 | 80 | 57 | 62 | 124.7 | 1 | 31.49
DVH120* | 10 | 3600 | 80 | 61 | 62 | 128.3 | 0.93 | 29.97
DVH120* | 10 | 3600 | 80 | 64 | 62 | 136.1 | 0.81 | 27.88
DVH120* | 10 | 3600 | 80 | 67 | 62 | 143.5 | 0.69 | 24.9
DVH120* | 10 | 3600 | 80 | 70 | 62 | 151.7 | 0.58 | 22.35
DVH120* | 10 | 3600 | 80 | 72 | 62 | 156.9 | 0.51 | 20.1
DVH120* | 10 | 3600 | 80 | 75 | 62 | 164.9 | 0.42 | 17.45
DVH120* | 10 | 3600 | 80 | 57 | 66 | 123.2 | 1 | 31.11
DVH120* | 10 | 3600 | 80 | 61 | 66 | 126.4 | 0.93 | 29.75
DVH120* | 10 | 3600 | 80 | 64 | 66 | 134.1 | 0.82 | 27.65
DVH120* | 10 | 3600 | 80 | 67 | 66 | 141.4 | 0.69 | 24.7
DVH120* | 10 | 3600 | 80 | 70 | 66 | 149.5 | 0.59 | 22.17
DVH120* | 10 | 3600 | 80 | 72 | 66 | 154.7 | 0.51 | 19.95
DVH120* | 10 | 3600 | 80 | 75 | 66 | 162.6 | 0.42 | 17.25
DVH120* | 10 | 3600 | 80 | 57 | 70 | 121.7 | 1 | 30.73
DVH120* | 10 | 3600 | 80 | 61 | 70 | 124.6 | 0.94 | 29.49
DVH120* | 10 | 3600 | 80 | 64 | 70 | 132.1 | 0.82 | 27.42
DVH120* | 10 | 3600 | 80 | 67 | 70 | 139.4 | 0.7 | 24.49
DVH120* | 10 | 3600 | 80 | 70 | 70 | 147.3 | 0.59 | 21.99
DVH120* | 10 | 3600 | 80 | 72 | 70 | 152.4 | 0.51 | 19.77
DVH120* | 10 | 3600 | 80 | 75 | 70 | 160.3 | 0.42 | 17.05
DVH120* | 10 | 3600 | 80 | 57 | 72 | 121 | 1 | 30.56
DVH120* | 10 | 3600 | 80 | 61 | 72 | 123.6 | 0.94 | 29.37
DVH120* | 10 | 3600 | 80 | 64 | 72 | 131.2 | 0.82 | 27.32
DVH120* | 10 | 3600 | 80 | 67 | 72 | 138.3 | 0.7 | 24.39
DVH120* | 10 | 3600 | 80 | 70 | 72 | 146.2 | 0.59 | 21.89
DVH120* | 10 | 3600 | 80 | 72 | 72 | 151.3 | 0.52 | 19.7
DVH120* | 10 | 3600 | 80 | 75 | 72 | 159.1 | 0.42 | 16.94
DVH120* | 10 | 3600 | 80 | 57 | 75 | 119.9 | 1 | 30.28
DVH120* | 10 | 3600 | 80 | 61 | 75 | 122.2 | 0.95 | 29.17
DVH120* | 10 | 3600 | 80 | 64 | 75 | 129.7 | 0.83 | 27.15
DVH120* | 10 | 3600 | 80 | 67 | 75 | 136.8 | 0.7 | 24.22
DVH120* | 10 | 3600 | 80 | 70 | 75 | 144.6 | 0.6 | 21.74
DVH120* | 10 | 3600 | 80 | 72 | 75 | 149.6 | 0.52 | 19.57
DVH120* | 10 | 3600 | 80 | 75 | 75 | 157.3 | 0.42 | 16.79
DVH120* | 10 | 3600 | 80 | 57 | 79 | 118.4 | 1 | 29.9
DVH120* | 10 | 3600 | 80 | 61 | 79 | 120.4 | 0.95 | 28.91
DVH120* | 10 | 3600 | 80 | 64 | 79 | 127.7 | 0.83 | 26.89
DVH120* | 10 | 3600 | 80 | 67 | 79 | 134.7 | 0.71 | 24.02
DVH120* | 10 | 3600 | 80 | 70 | 79 | 142.4 | 0.6 | 21.57
DVH120* | 10 | 3600 | 80 | 72 | 79 | 147.3 | 0.52 | 19.39
DVH120* | 10 | 3600 | 80 | 75 | 79 | 155 | 0.42 | 16.59
DVH120* | 10 | 3600 | 80 | 57 | 83 | 116.9 | 1 | 29.52
DVH120* | 10 | 3600 | 80 | 61 | 83 | 118.5 | 0.96 | 28.64
DVH120* | 10 | 3600 | 80 | 64 | 83 | 125.8 | 0.84 | 26.64
DVH120* | 10 | 3600 | 80 | 67 | 83 | 132.6 | 0.71 | 23.79
DVH120* | 10 | 3600 | 80 | 70 | 83 | 140.2 | 0.6 | 21.36
DVH120* | 10 | 3600 | 80 | 72 | 83 | 145 | 0.52 | 19.22
DVH120* | 10 | 3600 | 80 | 75 | 83 | 152.7 | 0.42 | 16.36
DVH120* | 10 | 3600 | 80 | 57 | 87 | 115.4 | 1 | 29.14
DVH120* | 10 | 3600 | 80 | 61 | 87 | 116.7 | 0.96 | 28.36
DVH120* | 10 | 3600 | 80 | 64 | 87 | 123.8 | 0.84 | 26.39
DVH120* | 10 | 3600 | 80 | 67 | 87 | 130.5 | 0.71 | 23.56
DVH120* | 10 | 3600 | 80 | 70 | 87 | 138 | 0.61 | 21.16
DVH120* | 10 | 3600 | 80 | 72 | 87 | 142.8 | 0.53 | 19.04
DVH120* | 10 | 3600 | 80 | 75 | 87 | 150.4 | 0.43 | 16.16
DVH120* | 10 | 3600 | 80 | 57 | 91 | 113.9 | 1 | 28.76
DVH120* | 10 | 3600 | 80 | 61 | 91 | 114.8 | 0.97 | 28.08
DVH120* | 10 | 3600 | 80 | 64 | 91 | 121.8 | 0.85 | 26.14
DVH120* | 10 | 3600 | 80 | 67 | 91 | 128.5 | 0.72 | 23.33
DVH120* | 10 | 3600 | 80 | 70 | 91 | 135.8 | 0.61 | 20.93
DVH120* | 10 | 3600 | 80 | 72 | 91 | 140.5 | 0.53 | 18.84
DVH120* | 10 | 3600 | 80 | 75 | 91 | 148 | 0.43 | 15.96
DVH120* | 10 | 3600 | 80 | 57 | 93 | 113.2 | 1 | 28.59
DVH120* | 10 | 3600 | 80 | 61 | 93 | 113.9 | 0.97 | 27.95
DVH120* | 10 | 3600 | 80 | 64 | 93 | 120.8 | 0.85 | 26.01
DVH120* | 10 | 3600 | 80 | 67 | 93 | 127.4 | 0.72 | 23.21
DVH120* | 10 | 3600 | 80 | 70 | 93 | 134.7 | 0.61 | 20.83
DVH120* | 10 | 3600 | 80 | 72 | 93 | 139.4 | 0.53 | 18.74
DVH120* | 10 | 3600 | 80 | 75 | 93 | 146.9 | 0.43 | 15.86
DVH120* | 10 | 3600 | 80 | 57 | 95 | 112.4 | 1 | 28.38
DVH120* | 10 | 3600 | 80 | 61 | 95 | 113 | 0.97 | 27.8
DVH120* | 10 | 3600 | 80 | 64 | 95 | 119.9 | 0.85 | 25.86
DVH120* | 10 | 3600 | 80 | 67 | 95 | 126.4 | 0.72 | 23.11
DVH120* | 10 | 3600 | 80 | 70 | 95 | 133.6 | 0.61 | 20.73
DVH120* | 10 | 3600 | 80 | 72 | 95 | 138.2 | 0.53 | 18.66
DVH120* | 10 | 3600 | 80 | 75 | 95 | 145.7 | 0.43 | 15.73
DVH120* | 10 | 3600 | 80 | 57 | 99 | 110.9 | 1 | 28.01
DVH120* | 10 | 3600 | 80 | 61 | 99 | 111.1 | 0.98 | 27.53
DVH120* | 10 | 3600 | 80 | 64 | 99 | 117.9 | 0.86 | 25.61
DVH120* | 10 | 3600 | 80 | 67 | 99 | 124.3 | 0.73 | 22.85
DVH120* | 10 | 3600 | 80 | 70 | 99 | 131.4 | 0.62 | 20.53
DVH120* | 10 | 3600 | 80 | 72 | 99 | 136 | 0.54 | 18.46
DVH120* | 10 | 3600 | 80 | 75 | 99 | 143.4 | 0.43 | 15.53
DVH120* | 10 | 3600 | 80 | 57 | 103 | 109.4 | 1 | 27.63
DVH120* | 10 | 3600 | 80 | 61 | 103 | 109.3 | 0.99 | 27.22
DVH120* | 10 | 3600 | 80 | 64 | 103 | 115.9 | 0.87 | 25.33
DVH120* | 10 | 3600 | 80 | 67 | 103 | 122.2 | 0.73 | 22.6
DVH120* | 10 | 3600 | 80 | 70 | 103 | 129.2 | 0.62 | 20.3
DVH120* | 10 | 3600 | 80 | 72 | 103 | 133.7 | 0.54 | 18.26
DVH120* | 10 | 3600 | 80 | 75 | 103 | 141.1 | 0.43 | 15.3
DVH120* | 10 | 3600 | 80 | 57 | 106 | 108.3 | 1 | 27.35
DVH120* | 10 | 3600 | 80 | 61 | 106 | 107.9 | 0.99 | 26.99
DVH120* | 10 | 3600 | 80 | 64 | 106 | 114.5 | 0.87 | 25.1
DVH120* | 10 | 3600 | 80 | 67 | 106 | 120.7 | 0.74 | 22.42
DVH120* | 10 | 3600 | 80 | 70 | 106 | 127.6 | 0.62 | 20.13
DVH120* | 10 | 3600 | 80 | 72 | 106 | 132 | 0.54 | 18.11
DVH120* | 10 | 3600 | 80 | 75 | 106 | 139.3 | 0.43 | 15.15
DVH120* | 10 | 3600 | 80 | 57 | 110 | 106.8 | 1 | 26.97
DVH120* | 10 | 3600 | 80 | 61 | 110 | 106 | 1 | 26.69
DVH120* | 10 | 3600 | 80 | 64 | 110 | 112.5 | 0.87 | 24.82
DVH120* | 10 | 3600 | 80 | 67 | 110 | 118.6 | 0.74 | 22.17
DVH120* | 10 | 3600 | 80 | 70 | 110 | 125.4 | 0.63 | 19.9
DVH120* | 10 | 3600 | 80 | 72 | 110 | 129.7 | 0.55 | 17.9
DVH120* | 10 | 3600 | 80 | 75 | 110 | 137 | 0.43 | 14.92
DVH120* | 10 | 3600 | 85 | 57 | 23 | 134.1 | 1 | 33.86
DVH120* | 10 | 3600 | 85 | 61 | 23 | 137.5 | 0.94 | 32.47
DVH120* | 10 | 3600 | 85 | 64 | 23 | 139.2 | 0.94 | 32.9
DVH120* | 10 | 3600 | 85 | 67 | 23 | 146.8 | 0.81 | 29.9
DVH120* | 10 | 3600 | 85 | 70 | 23 | 155.2 | 0.7 | 27.5
DVH120* | 10 | 3600 | 85 | 72 | 23 | 160.6 | 0.62 | 25.25
DVH120* | 10 | 3600 | 85 | 75 | 23 | 169.8 | 0.53 | 22.9
DVH120* | 10 | 3600 | 85 | 57 | 30 | 133.9 | 1 | 33.81
DVH120* | 10 | 3600 | 85 | 61 | 30 | 137.3 | 0.94 | 32.42
DVH120* | 10 | 3600 | 85 | 64 | 30 | 139 | 0.94 | 32.85
DVH120* | 10 | 3600 | 85 | 67 | 30 | 146.6 | 0.81 | 29.85
DVH120* | 10 | 3600 | 85 | 70 | 30 | 155 | 0.7 | 27.45
DVH120* | 10 | 3600 | 85 | 72 | 30 | 160.3 | 0.62 | 25.2
DVH120* | 10 | 3600 | 85 | 75 | 30 | 169.7 | 0.53 | 22.88
DVH120* | 10 | 3600 | 85 | 57 | 40 | 133.5 | 1 | 33.71
DVH120* | 10 | 3600 | 85 | 61 | 40 | 137 | 0.94 | 32.35
DVH120* | 10 | 3600 | 85 | 64 | 40 | 138.7 | 0.94 | 32.78
DVH120* | 10 | 3600 | 85 | 67 | 40 | 146.3 | 0.81 | 29.8
DVH120* | 10 | 3600 | 85 | 70 | 40 | 154.7 | 0.7 | 27.4
DVH120* | 10 | 3600 | 85 | 72 | 40 | 160 | 0.62 | 25.15
DVH120* | 10 | 3600 | 85 | 75 | 40 | 169.5 | 0.53 | 22.85
DVH120* | 10 | 3600 | 85 | 57 | 50 | 133.2 | 1 | 33.64
DVH120* | 10 | 3600 | 85 | 61 | 50 | 136.7 | 0.93 | 32.27
DVH120* | 10 | 3600 | 85 | 64 | 50 | 138.4 | 0.94 | 32.73
DVH120* | 10 | 3600 | 85 | 67 | 50 | 146 | 0.81 | 29.72
DVH120* | 10 | 3600 | 85 | 70 | 50 | 154.3 | 0.7 | 27.35
DVH120* | 10 | 3600 | 85 | 72 | 50 | 159.6 | 0.62 | 25.1
DVH120* | 10 | 3600 | 85 | 75 | 50 | 169.3 | 0.53 | 22.83
DVH120* | 10 | 3600 | 85 | 57 | 54 | 133 | 1 | 33.59
DVH120* | 10 | 3600 | 85 | 61 | 54 | 136.6 | 0.93 | 32.25
DVH120* | 10 | 3600 | 85 | 64 | 54 | 138.3 | 0.94 | 32.7
DVH120* | 10 | 3600 | 85 | 67 | 54 | 145.8 | 0.81 | 29.7
DVH120* | 10 | 3600 | 85 | 70 | 54 | 154.2 | 0.7 | 27.32
DVH120* | 10 | 3600 | 85 | 72 | 54 | 159.5 | 0.62 | 25.08
DVH120* | 10 | 3600 | 85 | 75 | 54 | 169.3 | 0.53 | 22.83
DVH120* | 10 | 3600 | 85 | 57 | 58 | 132.9 | 1 | 33.56
DVH120* | 10 | 3600 | 85 | 61 | 58 | 136.3 | 0.94 | 32.2
DVH120* | 10 | 3600 | 85 | 64 | 58 | 138 | 0.94 | 32.65
DVH120* | 10 | 3600 | 85 | 67 | 58 | 145.6 | 0.81 | 29.65
DVH120* | 10 | 3600 | 85 | 70 | 58 | 153.9 | 0.7 | 27.27
DVH120* | 10 | 3600 | 85 | 72 | 58 | 159.2 | 0.62 | 25.03
DVH120* | 10 | 3600 | 85 | 75 | 58 | 167.2 | 0.53 | 22.55
DVH120* | 10 | 3600 | 85 | 57 | 62 | 131.5 | 1 | 33.21
DVH120* | 10 | 3600 | 85 | 61 | 62 | 134.4 | 0.94 | 31.94
DVH120* | 10 | 3600 | 85 | 64 | 62 | 136.1 | 0.94 | 32.37
DVH120* | 10 | 3600 | 85 | 67 | 62 | 143.5 | 0.81 | 29.42
DVH120* | 10 | 3600 | 85 | 70 | 62 | 151.7 | 0.71 | 27.07
DVH120* | 10 | 3600 | 85 | 72 | 62 | 156.9 | 0.63 | 24.85
DVH120* | 10 | 3600 | 85 | 75 | 62 | 164.9 | 0.54 | 22.3
DVH120* | 10 | 3600 | 85 | 57 | 66 | 130 | 1 | 32.83
DVH120* | 10 | 3600 | 85 | 61 | 66 | 132.4 | 0.95 | 31.69
DVH120* | 10 | 3600 | 85 | 64 | 66 | 134.1 | 0.95 | 32.12
DVH120* | 10 | 3600 | 85 | 67 | 66 | 141.4 | 0.82 | 29.19
DVH120* | 10 | 3600 | 85 | 70 | 66 | 149.5 | 0.71 | 26.84
DVH120* | 10 | 3600 | 85 | 72 | 66 | 154.7 | 0.63 | 24.65
DVH120* | 10 | 3600 | 85 | 75 | 66 | 162.6 | 0.54 | 22.02
DVH120* | 10 | 3600 | 85 | 57 | 70 | 128.4 | 1 | 32.42
DVH120* | 10 | 3600 | 85 | 61 | 70 | 130.5 | 0.95 | 31.41
DVH120* | 10 | 3600 | 85 | 64 | 70 | 132.1 | 0.95 | 31.84
DVH120* | 10 | 3600 | 85 | 67 | 70 | 139.4 | 0.82 | 28.94
DVH120* | 10 | 3600 | 85 | 70 | 70 | 147.3 | 0.72 | 26.62
DVH120* | 10 | 3600 | 85 | 72 | 70 | 152.4 | 0.63 | 24.42
DVH120* | 10 | 3600 | 85 | 75 | 70 | 160.3 | 0.54 | 21.77
DVH120* | 10 | 3600 | 85 | 57 | 72 | 127.6 | 1 | 32.22
DVH120* | 10 | 3600 | 85 | 61 | 72 | 129.5 | 0.96 | 31.29
DVH120* | 10 | 3600 | 85 | 64 | 72 | 131.2 | 0.96 | 31.72
DVH120* | 10 | 3600 | 85 | 67 | 72 | 138.3 | 0.83 | 28.81
DVH120* | 10 | 3600 | 85 | 70 | 72 | 146.2 | 0.72 | 26.49
DVH120* | 10 | 3600 | 85 | 72 | 72 | 151.3 | 0.64 | 24.32
DVH120* | 10 | 3600 | 85 | 75 | 72 | 159.1 | 0.54 | 21.64
DVH120* | 10 | 3600 | 85 | 57 | 75 | 126.4 | 1 | 31.92
DVH120* | 10 | 3600 | 85 | 61 | 75 | 128.1 | 0.96 | 31.09
DVH120* | 10 | 3600 | 85 | 64 | 75 | 129.7 | 0.96 | 31.52
DVH120* | 10 | 3600 | 85 | 67 | 75 | 136.8 | 0.83 | 28.64
DVH120* | 10 | 3600 | 85 | 70 | 75 | 144.6 | 0.72 | 26.34
DVH120* | 10 | 3600 | 85 | 72 | 75 | 149.6 | 0.64 | 24.17
DVH120* | 10 | 3600 | 85 | 75 | 75 | 157.3 | 0.54 | 21.44
DVH120* | 10 | 3600 | 85 | 57 | 79 | 124.9 | 1 | 31.54
DVH120* | 10 | 3600 | 85 | 61 | 79 | 126.1 | 0.97 | 30.81
DVH120* | 10 | 3600 | 85 | 64 | 79 | 127.7 | 0.97 | 31.24
DVH120* | 10 | 3600 | 85 | 67 | 79 | 134.7 | 0.83 | 28.36
DVH120* | 10 | 3600 | 85 | 70 | 79 | 142.4 | 0.73 | 26.09
DVH120* | 10 | 3600 | 85 | 72 | 79 | 147.3 | 0.64 | 23.94
DVH120* | 10 | 3600 | 85 | 75 | 79 | 155 | 0.54 | 21.16
DVH120* | 10 | 3600 | 85 | 57 | 83 | 123.3 | 1 | 31.14
DVH120* | 10 | 3600 | 85 | 61 | 83 | 124.2 | 0.97 | 30.51
DVH120* | 10 | 3600 | 85 | 64 | 83 | 125.8 | 0.97 | 30.93
DVH120* | 10 | 3600 | 85 | 67 | 83 | 132.6 | 0.84 | 28.11
DVH120* | 10 | 3600 | 85 | 70 | 83 | 140.2 | 0.73 | 25.86
DVH120* | 10 | 3600 | 85 | 72 | 83 | 145 | 0.65 | 23.74
DVH120* | 10 | 3600 | 85 | 75 | 83 | 152.7 | 0.54 | 20.91
DVH120* | 10 | 3600 | 85 | 57 | 87 | 121.7 | 1 | 30.73
DVH120* | 10 | 3600 | 85 | 61 | 87 | 122.2 | 0.98 | 30.23
DVH120* | 10 | 3600 | 85 | 64 | 87 | 123.8 | 0.98 | 30.63
DVH120* | 10 | 3600 | 85 | 67 | 87 | 130.5 | 0.84 | 27.83
DVH120* | 10 | 3600 | 85 | 70 | 87 | 138 | 0.73 | 25.61
DVH120* | 10 | 3600 | 85 | 72 | 87 | 142.8 | 0.65 | 23.51
DVH120* | 10 | 3600 | 85 | 75 | 87 | 150.4 | 0.54 | 20.63
DVH120* | 10 | 3600 | 85 | 57 | 91 | 120.2 | 1 | 30.35
DVH120* | 10 | 3600 | 85 | 61 | 91 | 120.3 | 0.99 | 29.92
DVH120* | 10 | 3600 | 85 | 64 | 91 | 121.8 | 0.99 | 30.35
DVH120* | 10 | 3600 | 85 | 67 | 91 | 128.5 | 0.85 | 27.58
DVH120* | 10 | 3600 | 85 | 70 | 91 | 135.8 | 0.74 | 25.35
DVH120* | 10 | 3600 | 85 | 72 | 91 | 140.5 | 0.66 | 23.28
DVH120* | 10 | 3600 | 85 | 75 | 91 | 148 | 0.55 | 20.38
DVH120* | 10 | 3600 | 85 | 57 | 93 | 119.4 | 1 | 30.15
DVH120* | 10 | 3600 | 85 | 61 | 93 | 119.3 | 0.99 | 29.77
DVH120* | 10 | 3600 | 85 | 64 | 93 | 120.8 | 0.99 | 30.2
DVH120* | 10 | 3600 | 85 | 67 | 93 | 127.4 | 0.85 | 27.42
DVH120* | 10 | 3600 | 85 | 70 | 93 | 134.7 | 0.74 | 25.23
DVH120* | 10 | 3600 | 85 | 72 | 93 | 139.4 | 0.66 | 23.16
DVH120* | 10 | 3600 | 85 | 75 | 93 | 146.9 | 0.55 | 20.23
DVH120* | 10 | 3600 | 85 | 57 | 95 | 118.6 | 1 | 29.95
DVH120* | 10 | 3600 | 85 | 61 | 95 | 118.3 | 0.99 | 29.62
DVH120* | 10 | 3600 | 85 | 64 | 95 | 119.9 | 0.99 | 30.03
DVH120* | 10 | 3600 | 85 | 67 | 95 | 126.4 | 0.86 | 27.3
DVH120* | 10 | 3600 | 85 | 70 | 95 | 133.6 | 0.74 | 25.1
DVH120* | 10 | 3600 | 85 | 72 | 95 | 138.2 | 0.66 | 23.03
DVH120* | 10 | 3600 | 85 | 75 | 95 | 145.7 | 0.55 | 20.1
DVH120* | 10 | 3600 | 85 | 57 | 99 | 117 | 1 | 29.55
DVH120* | 10 | 3600 | 85 | 61 | 99 | 116.4 | 1 | 29.32
DVH120* | 10 | 3600 | 85 | 64 | 99 | 117.9 | 1 | 29.72
DVH120* | 10 | 3600 | 85 | 67 | 99 | 124.3 | 0.86 | 26.99
DVH120* | 10 | 3600 | 85 | 70 | 99 | 131.4 | 0.75 | 24.82
DVH120* | 10 | 3600 | 85 | 72 | 99 | 136 | 0.66 | 22.8
DVH120* | 10 | 3600 | 85 | 75 | 99 | 143.4 | 0.55 | 19.82
DVH120* | 10 | 3600 | 85 | 57 | 103 | 115.5 | 1 | 29.17
DVH120* | 10 | 3600 | 85 | 61 | 103 | 114.5 | 1 | 28.91
DVH120* | 10 | 3600 | 85 | 64 | 103 | 115.9 | 1 | 29.27
DVH120* | 10 | 3600 | 85 | 67 | 103 | 122.2 | 0.87 | 26.72
DVH120* | 10 | 3600 | 85 | 70 | 103 | 129.2 | 0.75 | 24.57
DVH120* | 10 | 3600 | 85 | 72 | 103 | 133.7 | 0.67 | 22.55
DVH120* | 10 | 3600 | 85 | 75 | 103 | 141.1 | 0.55 | 19.55
DVH120* | 10 | 3600 | 85 | 57 | 106 | 114.3 | 1 | 28.86
DVH120* | 10 | 3600 | 85 | 61 | 106 | 113 | 1 | 28.54
DVH120* | 10 | 3600 | 85 | 64 | 106 | 114.5 | 1 | 28.91
DVH120* | 10 | 3600 | 85 | 67 | 106 | 120.7 | 0.87 | 26.49
DVH120* | 10 | 3600 | 85 | 70 | 106 | 127.6 | 0.76 | 24.37
DVH120* | 10 | 3600 | 85 | 72 | 106 | 132 | 0.67 | 22.37
DVH120* | 10 | 3600 | 85 | 75 | 106 | 139.3 | 0.55 | 19.34
DVH120* | 10 | 3600 | 85 | 57 | 110 | 112.7 | 1 | 28.46
DVH120* | 10 | 3600 | 85 | 61 | 110 | 111.1 | 1 | 28.06
DVH120* | 10 | 3600 | 85 | 64 | 110 | 112.5 | 1 | 28.41
DVH120* | 10 | 3600 | 85 | 67 | 110 | 118.6 | 0.87 | 26.19
DVH120* | 10 | 3600 | 85 | 70 | 110 | 125.4 | 0.76 | 24.09
DVH120* | 10 | 3600 | 85 | 72 | 110 | 129.7 | 0.68 | 22.12
DVH120* | 10 | 3600 | 85 | 75 | 110 | 137 | 0.55 | 19.07
DVH120* | 10 | 4000 | 70 | 57 | 23 | 121.1 | 0.87 | 23.89
DVH120* | 10 | 4000 | 70 | 61 | 23 | 133.7 | 0.66 | 19.91
DVH120* | 10 | 4000 | 70 | 64 | 23 | 141.9 | 0.54 | 17.52
DVH120* | 10 | 4000 | 70 | 67 | 23 | 149.6 | 0.43 | 14.59
DVH120* | 10 | 4000 | 70 | 57 | 30 | 120.9 | 0.87 | 23.84
DVH120* | 10 | 4000 | 70 | 61 | 30 | 133.5 | 0.65 | 19.86
DVH120* | 10 | 4000 | 70 | 64 | 30 | 141.7 | 0.54 | 17.5
DVH120* | 10 | 4000 | 70 | 67 | 30 | 149.4 | 0.43 | 14.57
DVH120* | 10 | 4000 | 70 | 57 | 40 | 120.6 | 0.87 | 23.77
DVH120* | 10 | 4000 | 70 | 61 | 40 | 133.2 | 0.65 | 19.82
DVH120* | 10 | 4000 | 70 | 64 | 40 | 141.4 | 0.54 | 17.48
DVH120* | 10 | 4000 | 70 | 67 | 40 | 149.1 | 0.43 | 14.55
DVH120* | 10 | 4000 | 70 | 57 | 50 | 120.2 | 0.87 | 23.7
DVH120* | 10 | 4000 | 70 | 61 | 50 | 133 | 0.65 | 19.8
DVH120* | 10 | 4000 | 70 | 64 | 50 | 141.1 | 0.54 | 17.43
DVH120* | 10 | 4000 | 70 | 67 | 50 | 148.8 | 0.43 | 14.52
DVH120* | 10 | 4000 | 70 | 57 | 54 | 120.1 | 0.87 | 23.68
DVH120* | 10 | 4000 | 70 | 61 | 54 | 132.8 | 0.66 | 19.77
DVH120* | 10 | 4000 | 70 | 64 | 54 | 140.9 | 0.54 | 17.41
DVH120* | 10 | 4000 | 70 | 67 | 54 | 148.6 | 0.43 | 14.5
DVH120* | 10 | 4000 | 70 | 57 | 58 | 120 | 0.87 | 23.66
DVH120* | 10 | 4000 | 70 | 61 | 58 | 132.6 | 0.65 | 19.73
DVH120* | 10 | 4000 | 70 | 64 | 58 | 140.7 | 0.54 | 17.39
DVH120* | 10 | 4000 | 70 | 67 | 58 | 148.3 | 0.43 | 14.48
DVH120* | 10 | 4000 | 70 | 57 | 62 | 118.7 | 0.87 | 23.48
DVH120* | 10 | 4000 | 70 | 61 | 62 | 130.7 | 0.66 | 19.59
DVH120* | 10 | 4000 | 70 | 64 | 62 | 138.7 | 0.55 | 17.25
DVH120* | 10 | 4000 | 70 | 67 | 62 | 146.2 | 0.43 | 14.36
DVH120* | 10 | 4000 | 70 | 57 | 66 | 117.3 | 0.87 | 23.25
DVH120* | 10 | 4000 | 70 | 61 | 66 | 128.8 | 0.66 | 19.43
DVH120* | 10 | 4000 | 70 | 64 | 66 | 136.7 | 0.55 | 17.11
DVH120* | 10 | 4000 | 70 | 67 | 66 | 144.1 | 0.44 | 14.25
DVH120* | 10 | 4000 | 70 | 57 | 70 | 115.9 | 0.87 | 23.02
DVH120* | 10 | 4000 | 70 | 61 | 70 | 126.9 | 0.67 | 19.25
DVH120* | 10 | 4000 | 70 | 64 | 70 | 134.7 | 0.55 | 16.98
DVH120* | 10 | 4000 | 70 | 67 | 70 | 142 | 0.44 | 14.14
DVH120* | 10 | 4000 | 70 | 57 | 72 | 115.2 | 0.88 | 22.93
DVH120* | 10 | 4000 | 70 | 61 | 72 | 126 | 0.67 | 19.18
DVH120* | 10 | 4000 | 70 | 64 | 72 | 133.7 | 0.56 | 16.89
DVH120* | 10 | 4000 | 70 | 67 | 72 | 141 | 0.44 | 14.07
DVH120* | 10 | 4000 | 70 | 57 | 75 | 114.1 | 0.88 | 22.75
DVH120* | 10 | 4000 | 70 | 61 | 75 | 124.6 | 0.67 | 19.05
DVH120* | 10 | 4000 | 70 | 64 | 75 | 132.2 | 0.56 | 16.8
DVH120* | 10 | 4000 | 70 | 67 | 75 | 139.4 | 0.44 | 13.98
DVH120* | 10 | 4000 | 70 | 57 | 79 | 112.7 | 0.88 | 22.52
DVH120* | 10 | 4000 | 70 | 61 | 79 | 122.7 | 0.68 | 18.89
DVH120* | 10 | 4000 | 70 | 64 | 79 | 130.2 | 0.56 | 16.64
DVH120* | 10 | 4000 | 70 | 67 | 79 | 137.3 | 0.44 | 13.84
DVH120* | 10 | 4000 | 70 | 57 | 83 | 111.3 | 0.88 | 22.3
DVH120* | 10 | 4000 | 70 | 61 | 83 | 120.8 | 0.68 | 18.7
DVH120* | 10 | 4000 | 70 | 64 | 83 | 128.2 | 0.57 | 16.48
DVH120* | 10 | 4000 | 70 | 67 | 83 | 135.1 | 0.45 | 13.73
DVH120* | 10 | 4000 | 70 | 57 | 87 | 109.9 | 0.88 | 22.07
DVH120* | 10 | 4000 | 70 | 61 | 87 | 118.9 | 0.69 | 18.52
DVH120* | 10 | 4000 | 70 | 64 | 87 | 126.1 | 0.57 | 16.32
DVH120* | 10 | 4000 | 70 | 67 | 87 | 133 | 0.45 | 13.59
DVH120* | 10 | 4000 | 70 | 57 | 91 | 108.5 | 0.89 | 21.84
DVH120* | 10 | 4000 | 70 | 61 | 91 | 117 | 0.69 | 18.34
DVH120* | 10 | 4000 | 70 | 64 | 91 | 124.1 | 0.57 | 16.16
DVH120* | 10 | 4000 | 70 | 67 | 91 | 130.9 | 0.45 | 13.45
DVH120* | 10 | 4000 | 70 | 57 | 93 | 107.8 | 0.89 | 21.73
DVH120* | 10 | 4000 | 70 | 61 | 93 | 116.1 | 0.69 | 18.25
DVH120* | 10 | 4000 | 70 | 64 | 93 | 123.1 | 0.58 | 16.09
DVH120* | 10 | 4000 | 70 | 67 | 93 | 129.9 | 0.45 | 13.39
DVH120* | 10 | 4000 | 70 | 57 | 95 | 107.1 | 0.89 | 21.61
DVH120* | 10 | 4000 | 70 | 61 | 95 | 115.1 | 0.69 | 18.16
DVH120* | 10 | 4000 | 70 | 64 | 95 | 122.1 | 0.58 | 16
DVH120* | 10 | 4000 | 70 | 67 | 95 | 128.8 | 0.45 | 13.32
DVH120* | 10 | 4000 | 70 | 57 | 99 | 105.7 | 0.89 | 21.36
DVH120* | 10 | 4000 | 70 | 61 | 99 | 113.2 | 0.7 | 17.98
DVH120* | 10 | 4000 | 70 | 64 | 99 | 120.1 | 0.58 | 15.84
DVH120* | 10 | 4000 | 70 | 67 | 99 | 126.7 | 0.46 | 13.18
DVH120* | 10 | 4000 | 70 | 57 | 103 | 104.2 | 0.89 | 21.14
DVH120* | 10 | 4000 | 70 | 61 | 103 | 111.3 | 0.7 | 17.77
DVH120* | 10 | 4000 | 70 | 64 | 103 | 118.1 | 0.58 | 15.66
DVH120* | 10 | 4000 | 70 | 67 | 103 | 124.6 | 0.46 | 13.05
DVH120* | 10 | 4000 | 70 | 57 | 106 | 103.2 | 0.89 | 20.95
DVH120* | 10 | 4000 | 70 | 61 | 106 | 109.9 | 0.71 | 17.64
DVH120* | 10 | 4000 | 70 | 64 | 106 | 116.6 | 0.59 | 15.52
DVH120* | 10 | 4000 | 70 | 67 | 106 | 123 | 0.46 | 12.93
DVH120* | 10 | 4000 | 70 | 57 | 110 | 101.8 | 0.9 | 20.73
DVH120* | 10 | 4000 | 70 | 61 | 110 | 108 | 0.71 | 17.43
DVH120* | 10 | 4000 | 70 | 64 | 110 | 114.6 | 0.59 | 15.36
DVH120* | 10 | 4000 | 70 | 67 | 110 | 120.9 | 0.47 | 12.8
DVH120* | 10 | 4000 | 75 | 57 | 23 | 122.4 | 1 | 27.82
DVH120* | 10 | 4000 | 75 | 61 | 23 | 133.7 | 0.8 | 24.2
DVH120* | 10 | 4000 | 75 | 64 | 23 | 141.9 | 0.68 | 22.09
DVH120* | 10 | 4000 | 75 | 67 | 23 | 149.6 | 0.56 | 19.14
DVH120* | 10 | 4000 | 75 | 70 | 23 | 158.2 | 0.46 | 16.61
DVH120* | 10 | 4000 | 75 | 72 | 23 | 163.6 | 0.39 | 14.52
DVH120* | 10 | 4000 | 75 | 57 | 30 | 122.2 | 1 | 27.77
DVH120* | 10 | 4000 | 75 | 61 | 30 | 133.5 | 0.8 | 24.18
DVH120* | 10 | 4000 | 75 | 64 | 30 | 141.7 | 0.68 | 22.05
DVH120* | 10 | 4000 | 75 | 67 | 30 | 149.4 | 0.56 | 19.11
DVH120* | 10 | 4000 | 75 | 70 | 30 | 158 | 0.46 | 16.59
DVH120* | 10 | 4000 | 75 | 72 | 30 | 163.4 | 0.39 | 14.5
DVH120* | 10 | 4000 | 75 | 57 | 40 | 121.9 | 1 | 27.7
DVH120* | 10 | 4000 | 75 | 61 | 40 | 133.2 | 0.8 | 24.11
DVH120* | 10 | 4000 | 75 | 64 | 40 | 141.4 | 0.68 | 22
DVH120* | 10 | 4000 | 75 | 67 | 40 | 149.1 | 0.56 | 19.07
DVH120* | 10 | 4000 | 75 | 70 | 40 | 157.6 | 0.46 | 16.55
DVH120* | 10 | 4000 | 75 | 72 | 40 | 163 | 0.39 | 14.48
DVH120* | 10 | 4000 | 75 | 57 | 50 | 121.5 | 1 | 27.61
DVH120* | 10 | 4000 | 75 | 61 | 50 | 133 | 0.8 | 24.07
DVH120* | 10 | 4000 | 75 | 64 | 50 | 141.1 | 0.68 | 21.95
DVH120* | 10 | 4000 | 75 | 67 | 50 | 148.8 | 0.56 | 19.05
DVH120* | 10 | 4000 | 75 | 70 | 50 | 157.3 | 0.46 | 16.52
DVH120* | 10 | 4000 | 75 | 72 | 50 | 162.7 | 0.39 | 14.43
DVH120* | 10 | 4000 | 75 | 57 | 54 | 121.4 | 1 | 27.59
DVH120* | 10 | 4000 | 75 | 61 | 54 | 132.8 | 0.8 | 24.05
DVH120* | 10 | 4000 | 75 | 64 | 54 | 140.9 | 0.68 | 21.93
DVH120* | 10 | 4000 | 75 | 67 | 54 | 148.6 | 0.56 | 19.02
DVH120* | 10 | 4000 | 75 | 70 | 54 | 157.1 | 0.46 | 16.5
DVH120* | 10 | 4000 | 75 | 72 | 54 | 162.5 | 0.39 | 14.43
DVH120* | 10 | 4000 | 75 | 57 | 58 | 121.3 | 1 | 27.57
DVH120* | 10 | 4000 | 75 | 61 | 58 | 132.6 | 0.8 | 24
DVH120* | 10 | 4000 | 75 | 64 | 58 | 140.7 | 0.69 | 21.91
DVH120* | 10 | 4000 | 75 | 67 | 58 | 148.3 | 0.56 | 19
DVH120* | 10 | 4000 | 75 | 70 | 58 | 156.8 | 0.46 | 16.48
DVH120* | 10 | 4000 | 75 | 72 | 58 | 162.2 | 0.39 | 14.41
DVH120* | 10 | 4000 | 75 | 57 | 62 | 120 | 1 | 27.27
DVH120* | 10 | 4000 | 75 | 61 | 62 | 130.7 | 0.8 | 23.82
DVH120* | 10 | 4000 | 75 | 64 | 62 | 138.7 | 0.69 | 21.73
DVH120* | 10 | 4000 | 75 | 67 | 62 | 146.2 | 0.57 | 18.84
DVH120* | 10 | 4000 | 75 | 70 | 62 | 154.6 | 0.47 | 16.34
DVH120* | 10 | 4000 | 75 | 72 | 62 | 159.9 | 0.39 | 14.3
DVH120* | 10 | 4000 | 75 | 57 | 66 | 118.6 | 1 | 26.95
DVH120* | 10 | 4000 | 75 | 61 | 66 | 128.8 | 0.81 | 23.64
DVH120* | 10 | 4000 | 75 | 64 | 66 | 136.7 | 0.69 | 21.57
DVH120* | 10 | 4000 | 75 | 67 | 66 | 144.1 | 0.57 | 18.68
DVH120* | 10 | 4000 | 75 | 70 | 66 | 152.4 | 0.47 | 16.2
DVH120* | 10 | 4000 | 75 | 72 | 66 | 157.6 | 0.4 | 14.18
DVH120* | 10 | 4000 | 75 | 57 | 70 | 117.2 | 1 | 26.64
DVH120* | 10 | 4000 | 75 | 61 | 70 | 126.9 | 0.81 | 23.43
DVH120* | 10 | 4000 | 75 | 64 | 70 | 134.7 | 0.7 | 21.39
DVH120* | 10 | 4000 | 75 | 67 | 70 | 142 | 0.57 | 18.52
DVH120* | 10 | 4000 | 75 | 70 | 70 | 150.1 | 0.47 | 16.07
DVH120* | 10 | 4000 | 75 | 72 | 70 | 155.3 | 0.4 | 14.05
DVH120* | 10 | 4000 | 75 | 57 | 72 | 116.4 | 1 | 26.45
DVH120* | 10 | 4000 | 75 | 61 | 72 | 126 | 0.81 | 23.32
DVH120* | 10 | 4000 | 75 | 64 | 72 | 133.7 | 0.7 | 21.3
DVH120* | 10 | 4000 | 75 | 67 | 72 | 141 | 0.58 | 18.45
DVH120* | 10 | 4000 | 75 | 70 | 72 | 149 | 0.47 | 16
DVH120* | 10 | 4000 | 75 | 72 | 72 | 154.1 | 0.4 | 14
DVH120* | 10 | 4000 | 75 | 57 | 75 | 115.4 | 1 | 26.23
DVH120* | 10 | 4000 | 75 | 61 | 75 | 124.6 | 0.82 | 23.18
DVH120* | 10 | 4000 | 75 | 64 | 75 | 132.2 | 0.7 | 21.14
DVH120* | 10 | 4000 | 75 | 67 | 75 | 139.4 | 0.58 | 18.34
DVH120* | 10 | 4000 | 75 | 70 | 75 | 147.3 | 0.48 | 15.91
DVH120* | 10 | 4000 | 75 | 72 | 75 | 152.4 | 0.4 | 13.91
DVH120* | 10 | 4000 | 75 | 57 | 79 | 113.9 | 1 | 25.89
DVH120* | 10 | 4000 | 75 | 61 | 79 | 122.7 | 0.82 | 22.98
DVH120* | 10 | 4000 | 75 | 64 | 79 | 130.2 | 0.71 | 20.95
DVH120* | 10 | 4000 | 75 | 67 | 79 | 137.3 | 0.58 | 18.16
DVH120* | 10 | 4000 | 75 | 70 | 79 | 145.1 | 0.48 | 15.75
DVH120* | 10 | 4000 | 75 | 72 | 79 | 150.1 | 0.4 | 13.77
DVH120* | 10 | 4000 | 75 | 57 | 83 | 112.5 | 1 | 25.57
DVH120* | 10 | 4000 | 75 | 61 | 83 | 120.8 | 0.83 | 22.75
DVH120* | 10 | 4000 | 75 | 64 | 83 | 128.2 | 0.71 | 20.77
DVH120* | 10 | 4000 | 75 | 67 | 83 | 135.1 | 0.59 | 18
DVH120* | 10 | 4000 | 75 | 70 | 83 | 142.9 | 0.48 | 15.61
DVH120* | 10 | 4000 | 75 | 72 | 83 | 147.8 | 0.41 | 13.66
DVH120* | 10 | 4000 | 75 | 57 | 87 | 111.1 | 1 | 25.25
DVH120* | 10 | 4000 | 75 | 61 | 87 | 118.9 | 0.83 | 22.55
DVH120* | 10 | 4000 | 75 | 64 | 87 | 126.1 | 0.72 | 20.57
DVH120* | 10 | 4000 | 75 | 67 | 87 | 133 | 0.59 | 17.82
DVH120* | 10 | 4000 | 75 | 70 | 87 | 140.6 | 0.48 | 15.45
DVH120* | 10 | 4000 | 75 | 72 | 87 | 145.5 | 0.41 | 13.52
DVH120* | 10 | 4000 | 75 | 57 | 91 | 109.6 | 1 | 24.91
DVH120* | 10 | 4000 | 75 | 61 | 91 | 117 | 0.84 | 22.32
DVH120* | 10 | 4000 | 75 | 64 | 91 | 124.1 | 0.72 | 20.36
DVH120* | 10 | 4000 | 75 | 67 | 91 | 130.9 | 0.59 | 17.66
DVH120* | 10 | 4000 | 75 | 70 | 91 | 138.4 | 0.49 | 15.32
DVH120* | 10 | 4000 | 75 | 72 | 91 | 143.2 | 0.41 | 13.39
DVH120* | 10 | 4000 | 75 | 57 | 93 | 108.9 | 1 | 24.75
DVH120* | 10 | 4000 | 75 | 61 | 93 | 116.1 | 0.84 | 22.2
DVH120* | 10 | 4000 | 75 | 64 | 93 | 123.1 | 0.72 | 20.25
DVH120* | 10 | 4000 | 75 | 67 | 93 | 129.9 | 0.6 | 17.57
DVH120* | 10 | 4000 | 75 | 70 | 93 | 137.3 | 0.49 | 15.23
DVH120* | 10 | 4000 | 75 | 72 | 93 | 142 | 0.41 | 13.32
DVH120* | 10 | 4000 | 75 | 57 | 95 | 108.2 | 1 | 24.59
DVH120* | 10 | 4000 | 75 | 61 | 95 | 115.1 | 0.84 | 22.09
DVH120* | 10 | 4000 | 75 | 64 | 95 | 122.1 | 0.73 | 20.16
DVH120* | 10 | 4000 | 75 | 67 | 95 | 128.8 | 0.6 | 17.48
DVH120* | 10 | 4000 | 75 | 70 | 95 | 136.2 | 0.49 | 15.16
DVH120* | 10 | 4000 | 75 | 72 | 95 | 140.9 | 0.41 | 13.25
DVH120* | 10 | 4000 | 75 | 57 | 99 | 106.8 | 1 | 24.27
DVH120* | 10 | 4000 | 75 | 61 | 99 | 113.2 | 0.85 | 21.86
DVH120* | 10 | 4000 | 75 | 64 | 99 | 120.1 | 0.73 | 19.95
DVH120* | 10 | 4000 | 75 | 67 | 99 | 126.7 | 0.6 | 17.3
DVH120* | 10 | 4000 | 75 | 70 | 99 | 133.9 | 0.49 | 15
DVH120* | 10 | 4000 | 75 | 72 | 99 | 138.5 | 0.42 | 13.11
DVH120* | 10 | 4000 | 75 | 57 | 103 | 105.4 | 1 | 23.95
DVH120* | 10 | 4000 | 75 | 61 | 103 | 111.3 | 0.86 | 21.64
DVH120* | 10 | 4000 | 75 | 64 | 103 | 118.1 | 0.73 | 19.73
DVH120* | 10 | 4000 | 75 | 67 | 103 | 124.6 | 0.6 | 17.11
DVH120* | 10 | 4000 | 75 | 70 | 103 | 131.7 | 0.5 | 14.84
DVH120* | 10 | 4000 | 75 | 72 | 103 | 136.2 | 0.42 | 12.98
DVH120* | 10 | 4000 | 75 | 57 | 106 | 104.3 | 1 | 23.7
DVH120* | 10 | 4000 | 75 | 61 | 106 | 109.9 | 0.86 | 21.45
DVH120* | 10 | 4000 | 75 | 64 | 106 | 116.6 | 0.74 | 19.57
DVH120* | 10 | 4000 | 75 | 67 | 106 | 123 | 0.61 | 16.95
DVH120* | 10 | 4000 | 75 | 70 | 106 | 130 | 0.5 | 14.73
DVH120* | 10 | 4000 | 75 | 72 | 106 | 134.5 | 0.42 | 12.86
DVH120* | 10 | 4000 | 75 | 57 | 110 | 102.9 | 1 | 23.39
DVH120* | 10 | 4000 | 75 | 61 | 110 | 108 | 0.86 | 21.2
DVH120* | 10 | 4000 | 75 | 64 | 110 | 114.6 | 0.74 | 19.34
DVH120* | 10 | 4000 | 75 | 67 | 110 | 120.9 | 0.61 | 16.77
DVH120* | 10 | 4000 | 75 | 70 | 110 | 127.8 | 0.5 | 14.55
DVH120* | 10 | 4000 | 75 | 72 | 110 | 132.2 | 0.42 | 12.73
DVH120* | 10 | 4000 | 80 | 57 | 23 | 129.6 | 1 | 29.45
DVH120* | 10 | 4000 | 80 | 61 | 23 | 133.7 | 0.93 | 28.41
DVH120* | 10 | 4000 | 80 | 64 | 23 | 141.9 | 0.82 | 26.43
DVH120* | 10 | 4000 | 80 | 67 | 23 | 149.6 | 0.69 | 23.59
DVH120* | 10 | 4000 | 80 | 70 | 23 | 158.2 | 0.59 | 21.18
DVH120* | 10 | 4000 | 80 | 72 | 23 | 163.6 | 0.51 | 19.07
DVH120* | 10 | 4000 | 80 | 75 | 23 | 173.1 | 0.43 | 16.73
DVH120* | 10 | 4000 | 80 | 57 | 30 | 129.3 | 1 | 29.39
DVH120* | 10 | 4000 | 80 | 61 | 30 | 133.5 | 0.93 | 28.36
DVH120* | 10 | 4000 | 80 | 64 | 30 | 141.7 | 0.82 | 26.39
DVH120* | 10 | 4000 | 80 | 67 | 30 | 149.4 | 0.69 | 23.57
DVH120* | 10 | 4000 | 80 | 70 | 30 | 158 | 0.59 | 21.16
DVH120* | 10 | 4000 | 80 | 72 | 30 | 163.4 | 0.51 | 19.02
DVH120* | 10 | 4000 | 80 | 75 | 30 | 172.9 | 0.43 | 16.7
DVH120* | 10 | 4000 | 80 | 57 | 40 | 129 | 1 | 29.32
DVH120* | 10 | 4000 | 80 | 61 | 40 | 133.2 | 0.93 | 28.3
DVH120* | 10 | 4000 | 80 | 64 | 40 | 141.4 | 0.82 | 26.34
DVH120* | 10 | 4000 | 80 | 67 | 40 | 149.1 | 0.69 | 23.5
DVH120* | 10 | 4000 | 80 | 70 | 40 | 157.6 | 0.59 | 21.11
DVH120* | 10 | 4000 | 80 | 72 | 40 | 163 | 0.51 | 18.98
DVH120* | 10 | 4000 | 80 | 75 | 40 | 172.7 | 0.43 | 16.68
DVH120* | 10 | 4000 | 80 | 57 | 50 | 128.7 | 1 | 29.25
DVH120* | 10 | 4000 | 80 | 61 | 50 | 133 | 0.93 | 28.25
DVH120* | 10 | 4000 | 80 | 64 | 50 | 141.1 | 0.82 | 26.27
DVH120* | 10 | 4000 | 80 | 67 | 50 | 148.8 | 0.69 | 23.45
DVH120* | 10 | 4000 | 80 | 70 | 50 | 157.3 | 0.59 | 21.07
DVH120* | 10 | 4000 | 80 | 72 | 50 | 162.7 | 0.51 | 18.95
DVH120* | 10 | 4000 | 80 | 75 | 50 | 172.6 | 0.43 | 16.68
DVH120* | 10 | 4000 | 80 | 57 | 54 | 128.5 | 1 | 29.2
DVH120* | 10 | 4000 | 80 | 61 | 54 | 132.8 | 0.94 | 28.23
DVH120* | 10 | 4000 | 80 | 64 | 54 | 140.9 | 0.82 | 26.25
DVH120* | 10 | 4000 | 80 | 67 | 54 | 148.6 | 0.69 | 23.43
DVH120* | 10 | 4000 | 80 | 70 | 54 | 157.1 | 0.59 | 21.05
DVH120* | 10 | 4000 | 80 | 72 | 54 | 162.5 | 0.51 | 18.93
DVH120* | 10 | 4000 | 80 | 75 | 54 | 172.5 | 0.42 | 16.66
DVH120* | 10 | 4000 | 80 | 57 | 58 | 128.4 | 1 | 29.18
DVH120* | 10 | 4000 | 80 | 61 | 58 | 132.6 | 0.94 | 28.18
DVH120* | 10 | 4000 | 80 | 64 | 58 | 140.7 | 0.82 | 26.2
DVH120* | 10 | 4000 | 80 | 67 | 58 | 148.3 | 0.69 | 23.41
DVH120* | 10 | 4000 | 80 | 70 | 58 | 156.8 | 0.59 | 21.02
DVH120* | 10 | 4000 | 80 | 72 | 58 | 162.2 | 0.51 | 18.91
DVH120* | 10 | 4000 | 80 | 75 | 58 | 170.4 | 0.42 | 16.45
DVH120* | 10 | 4000 | 80 | 57 | 62 | 127.1 | 1 | 28.89
DVH120* | 10 | 4000 | 80 | 61 | 62 | 130.7 | 0.94 | 27.95
DVH120* | 10 | 4000 | 80 | 64 | 62 | 138.7 | 0.82 | 26
DVH120* | 10 | 4000 | 80 | 67 | 62 | 146.2 | 0.7 | 23.23
DVH120* | 10 | 4000 | 80 | 70 | 62 | 154.6 | 0.59 | 20.84
DVH120* | 10 | 4000 | 80 | 72 | 62 | 159.9 | 0.52 | 18.75
DVH120* | 10 | 4000 | 80 | 75 | 62 | 168 | 0.43 | 16.27
DVH120* | 10 | 4000 | 80 | 57 | 66 | 125.5 | 1 | 28.52
DVH120* | 10 | 4000 | 80 | 61 | 66 | 128.8 | 0.95 | 27.73
DVH120* | 10 | 4000 | 80 | 64 | 66 | 136.7 | 0.83 | 25.8
DVH120* | 10 | 4000 | 80 | 67 | 66 | 144.1 | 0.7 | 23.02
DVH120* | 10 | 4000 | 80 | 70 | 66 | 152.4 | 0.6 | 20.68
DVH120* | 10 | 4000 | 80 | 72 | 66 | 157.6 | 0.52 | 18.59
DVH120* | 10 | 4000 | 80 | 75 | 66 | 165.7 | 0.43 | 16.09
DVH120* | 10 | 4000 | 80 | 57 | 70 | 124 | 1 | 28.18
DVH120* | 10 | 4000 | 80 | 61 | 70 | 126.9 | 0.95 | 27.5
DVH120* | 10 | 4000 | 80 | 64 | 70 | 134.7 | 0.84 | 25.57
DVH120* | 10 | 4000 | 80 | 67 | 70 | 142 | 0.71 | 22.84
DVH120* | 10 | 4000 | 80 | 70 | 70 | 150.1 | 0.6 | 20.5
DVH120* | 10 | 4000 | 80 | 72 | 70 | 155.3 | 0.52 | 18.45
DVH120* | 10 | 4000 | 80 | 75 | 70 | 163.3 | 0.43 | 15.89
DVH120* | 10 | 4000 | 80 | 57 | 72 | 123.3 | 1 | 28.02
DVH120* | 10 | 4000 | 80 | 61 | 72 | 126 | 0.96 | 27.39
DVH120* | 10 | 4000 | 80 | 64 | 72 | 133.7 | 0.84 | 25.48
DVH120* | 10 | 4000 | 80 | 67 | 72 | 141 | 0.71 | 22.75
DVH120* | 10 | 4000 | 80 | 70 | 72 | 149 | 0.6 | 20.41
DVH120* | 10 | 4000 | 80 | 72 | 72 | 154.1 | 0.52 | 18.36
DVH120* | 10 | 4000 | 80 | 75 | 72 | 162.1 | 0.43 | 15.8
DVH120* | 10 | 4000 | 80 | 57 | 75 | 122.1 | 1 | 27.75
DVH120* | 10 | 4000 | 80 | 61 | 75 | 124.6 | 0.96 | 27.2
DVH120* | 10 | 4000 | 80 | 64 | 75 | 132.2 | 0.84 | 25.3
DVH120* | 10 | 4000 | 80 | 67 | 75 | 139.4 | 0.71 | 22.59
DVH120* | 10 | 4000 | 80 | 70 | 75 | 147.3 | 0.61 | 20.27
DVH120* | 10 | 4000 | 80 | 72 | 75 | 152.4 | 0.53 | 18.25
DVH120* | 10 | 4000 | 80 | 75 | 75 | 160.3 | 0.43 | 15.66
DVH120* | 10 | 4000 | 80 | 57 | 79 | 120.6 | 1 | 27.41
DVH120* | 10 | 4000 | 80 | 61 | 79 | 122.7 | 0.97 | 26.95
DVH120* | 10 | 4000 | 80 | 64 | 79 | 130.2 | 0.85 | 25.07
DVH120* | 10 | 4000 | 80 | 67 | 79 | 137.3 | 0.72 | 22.39
DVH120* | 10 | 4000 | 80 | 70 | 79 | 145.1 | 0.61 | 20.09
DVH120* | 10 | 4000 | 80 | 72 | 79 | 150.1 | 0.53 | 18.09
DVH120* | 10 | 4000 | 80 | 75 | 79 | 158 | 0.43 | 15.45
DVH120* | 10 | 4000 | 80 | 57 | 83 | 119.1 | 1 | 27.07
DVH120* | 10 | 4000 | 80 | 61 | 83 | 120.8 | 0.97 | 26.7
DVH120* | 10 | 4000 | 80 | 64 | 83 | 128.2 | 0.85 | 24.84
DVH120* | 10 | 4000 | 80 | 67 | 83 | 135.1 | 0.72 | 22.18
DVH120* | 10 | 4000 | 80 | 70 | 83 | 142.9 | 0.61 | 19.91
DVH120* | 10 | 4000 | 80 | 72 | 83 | 147.8 | 0.53 | 17.91
DVH120* | 10 | 4000 | 80 | 75 | 83 | 155.6 | 0.43 | 15.27
DVH120* | 10 | 4000 | 80 | 57 | 87 | 117.6 | 1 | 26.73
DVH120* | 10 | 4000 | 80 | 61 | 87 | 118.9 | 0.98 | 26.45
DVH120* | 10 | 4000 | 80 | 64 | 87 | 126.1 | 0.86 | 24.61
DVH120* | 10 | 4000 | 80 | 67 | 87 | 133 | 0.73 | 21.98
DVH120* | 10 | 4000 | 80 | 70 | 87 | 140.6 | 0.62 | 19.73
DVH120* | 10 | 4000 | 80 | 72 | 87 | 145.5 | 0.54 | 17.75
DVH120* | 10 | 4000 | 80 | 75 | 87 | 153.2 | 0.43 | 15.07
DVH120* | 10 | 4000 | 80 | 57 | 91 | 116.1 | 1 | 26.39
DVH120* | 10 | 4000 | 80 | 61 | 91 | 117 | 0.98 | 26.18
DVH120* | 10 | 4000 | 80 | 64 | 91 | 124.1 | 0.86 | 24.36
DVH120* | 10 | 4000 | 80 | 67 | 91 | 130.9 | 0.73 | 21.75
DVH120* | 10 | 4000 | 80 | 70 | 91 | 138.4 | 0.62 | 19.52
DVH120* | 10 | 4000 | 80 | 72 | 91 | 143.2 | 0.54 | 17.57
DVH120* | 10 | 4000 | 80 | 75 | 91 | 150.9 | 0.43 | 14.86
DVH120* | 10 | 4000 | 80 | 57 | 93 | 115.3 | 1 | 26.2
DVH120* | 10 | 4000 | 80 | 61 | 93 | 116.1 | 0.99 | 26.07
DVH120* | 10 | 4000 | 80 | 64 | 93 | 123.1 | 0.87 | 24.25
DVH120* | 10 | 4000 | 80 | 67 | 93 | 129.9 | 0.73 | 21.64
DVH120* | 10 | 4000 | 80 | 70 | 93 | 137.3 | 0.62 | 19.43
DVH120* | 10 | 4000 | 80 | 72 | 93 | 142 | 0.54 | 17.48
DVH120* | 10 | 4000 | 80 | 75 | 93 | 149.7 | 0.43 | 14.77
DVH120* | 10 | 4000 | 80 | 57 | 95 | 114.6 | 1 | 26.05
DVH120* | 10 | 4000 | 80 | 61 | 95 | 115.1 | 0.99 | 25.93
DVH120* | 10 | 4000 | 80 | 64 | 95 | 122.1 | 0.87 | 24.11
DVH120* | 10 | 4000 | 80 | 67 | 95 | 128.8 | 0.74 | 21.55
DVH120* | 10 | 4000 | 80 | 70 | 95 | 136.2 | 0.62 | 19.34
DVH120* | 10 | 4000 | 80 | 72 | 95 | 140.9 | 0.54 | 17.39
DVH120* | 10 | 4000 | 80 | 75 | 95 | 148.5 | 0.44 | 14.68
DVH120* | 10 | 4000 | 80 | 57 | 99 | 113 | 1 | 25.68
DVH120* | 10 | 4000 | 80 | 61 | 99 | 113.2 | 1 | 25.66
DVH120* | 10 | 4000 | 80 | 64 | 99 | 120.1 | 0.87 | 23.86
DVH120* | 10 | 4000 | 80 | 67 | 99 | 126.7 | 0.74 | 21.32
DVH120* | 10 | 4000 | 80 | 70 | 99 | 133.9 | 0.63 | 19.14
DVH120* | 10 | 4000 | 80 | 72 | 99 | 138.5 | 0.55 | 17.2
DVH120* | 10 | 4000 | 80 | 75 | 99 | 146.1 | 0.44 | 14.48
DVH120* | 10 | 4000 | 80 | 57 | 103 | 111.5 | 1 | 25.34
DVH120* | 10 | 4000 | 80 | 61 | 103 | 111.3 | 1 | 25.39
DVH120* | 10 | 4000 | 80 | 64 | 103 | 118.1 | 0.88 | 23.61
DVH120* | 10 | 4000 | 80 | 67 | 103 | 124.6 | 0.74 | 21.09
DVH120* | 10 | 4000 | 80 | 70 | 103 | 131.7 | 0.63 | 18.93
DVH120* | 10 | 4000 | 80 | 72 | 103 | 136.2 | 0.55 | 17.02
DVH120* | 10 | 4000 | 80 | 75 | 103 | 143.7 | 0.44 | 14.27
DVH120* | 10 | 4000 | 80 | 57 | 106 | 110.4 | 1 | 25.09
DVH120* | 10 | 4000 | 80 | 61 | 106 | 109.9 | 1.01 | 25.18
DVH120* | 10 | 4000 | 80 | 64 | 106 | 116.6 | 0.88 | 23.41
DVH120* | 10 | 4000 | 80 | 67 | 106 | 123 | 0.75 | 20.91
DVH120* | 10 | 4000 | 80 | 70 | 106 | 130 | 0.64 | 18.77
DVH120* | 10 | 4000 | 80 | 72 | 106 | 134.5 | 0.55 | 16.89
DVH120* | 10 | 4000 | 80 | 75 | 106 | 142 | 0.44 | 14.14
DVH120* | 10 | 4000 | 80 | 57 | 110 | 108.9 | 1 | 24.75
DVH120* | 10 | 4000 | 80 | 61 | 110 | 108 | 1.01 | 24.89
DVH120* | 10 | 4000 | 80 | 64 | 110 | 114.6 | 0.89 | 23.16
DVH120* | 10 | 4000 | 80 | 67 | 110 | 120.9 | 0.75 | 20.68
DVH120* | 10 | 4000 | 80 | 70 | 110 | 127.8 | 0.64 | 18.57
DVH120* | 10 | 4000 | 80 | 72 | 110 | 132.2 | 0.56 | 16.7
DVH120* | 10 | 4000 | 80 | 75 | 110 | 139.6 | 0.44 | 13.93
DVH120* | 10 | 4000 | 85 | 57 | 23 | 136.7 | 1 | 31.07
DVH120* | 10 | 4000 | 85 | 61 | 23 | 140.1 | 0.95 | 30.27
DVH120* | 10 | 4000 | 85 | 64 | 23 | 141.9 | 0.95 | 30.68
DVH120* | 10 | 4000 | 85 | 67 | 23 | 149.6 | 0.82 | 27.89
DVH120* | 10 | 4000 | 85 | 70 | 23 | 158.2 | 0.71 | 25.64
DVH120* | 10 | 4000 | 85 | 72 | 23 | 163.6 | 0.63 | 23.55
DVH120* | 10 | 4000 | 85 | 75 | 23 | 173.1 | 0.54 | 21.34
DVH120* | 10 | 4000 | 85 | 57 | 30 | 136.4 | 1 | 31
DVH120* | 10 | 4000 | 85 | 61 | 30 | 139.9 | 0.95 | 30.23
DVH120* | 10 | 4000 | 85 | 64 | 30 | 141.7 | 0.95 | 30.64
DVH120* | 10 | 4000 | 85 | 67 | 30 | 149.4 | 0.82 | 27.84
DVH120* | 10 | 4000 | 85 | 70 | 30 | 158 | 0.71 | 25.59
DVH120* | 10 | 4000 | 85 | 72 | 30 | 163.4 | 0.63 | 23.5
DVH120* | 10 | 4000 | 85 | 75 | 30 | 172.9 | 0.54 | 21.34
DVH120* | 10 | 4000 | 85 | 57 | 40 | 136.1 | 1 | 30.93
DVH120* | 10 | 4000 | 85 | 61 | 40 | 139.6 | 0.95 | 30.16
DVH120* | 10 | 4000 | 85 | 64 | 40 | 141.4 | 0.95 | 30.57
DVH120* | 10 | 4000 | 85 | 67 | 40 | 149.1 | 0.82 | 27.77
DVH120* | 10 | 4000 | 85 | 70 | 40 | 157.6 | 0.71 | 25.55
DVH120* | 10 | 4000 | 85 | 72 | 40 | 163 | 0.63 | 23.45
DVH120* | 10 | 4000 | 85 | 75 | 40 | 172.7 | 0.54 | 21.32
DVH120* | 10 | 4000 | 85 | 57 | 50 | 135.7 | 1 | 30.84
DVH120* | 10 | 4000 | 85 | 61 | 50 | 139.3 | 0.95 | 30.09
DVH120* | 10 | 4000 | 85 | 64 | 50 | 141.1 | 0.95 | 30.5
DVH120* | 10 | 4000 | 85 | 67 | 50 | 148.8 | 0.82 | 27.7
DVH120* | 10 | 4000 | 85 | 70 | 50 | 157.3 | 0.71 | 25.5
DVH120* | 10 | 4000 | 85 | 72 | 50 | 162.7 | 0.63 | 23.41
DVH120* | 10 | 4000 | 85 | 75 | 50 | 172.6 | 0.54 | 21.27
DVH120* | 10 | 4000 | 85 | 57 | 54 | 135.6 | 1 | 30.82
DVH120* | 10 | 4000 | 85 | 61 | 54 | 139.2 | 0.95 | 30.07
DVH120* | 10 | 4000 | 85 | 64 | 54 | 140.9 | 0.95 | 30.48
DVH120* | 10 | 4000 | 85 | 67 | 54 | 148.6 | 0.82 | 27.68
DVH120* | 10 | 4000 | 85 | 70 | 54 | 157.1 | 0.71 | 25.48
DVH120* | 10 | 4000 | 85 | 72 | 54 | 162.5 | 0.63 | 23.39
DVH120* | 10 | 4000 | 85 | 75 | 54 | 172.5 | 0.54 | 21.27
DVH120* | 10 | 4000 | 85 | 57 | 58 | 135.4 | 1 | 30.77
DVH120* | 10 | 4000 | 85 | 61 | 58 | 138.9 | 0.95 | 30.02
DVH120* | 10 | 4000 | 85 | 64 | 58 | 140.7 | 0.95 | 30.43
DVH120* | 10 | 4000 | 85 | 67 | 58 | 148.3 | 0.82 | 27.66
DVH120* | 10 | 4000 | 85 | 70 | 58 | 156.8 | 0.71 | 25.43
DVH120* | 10 | 4000 | 85 | 72 | 58 | 162.2 | 0.63 | 23.34
DVH120* | 10 | 4000 | 85 | 75 | 58 | 170.4 | 0.54 | 21.02
DVH120* | 10 | 4000 | 85 | 57 | 62 | 134 | 1 | 30.45
DVH120* | 10 | 4000 | 85 | 61 | 62 | 136.9 | 0.96 | 29.8
DVH120* | 10 | 4000 | 85 | 64 | 62 | 138.7 | 0.96 | 30.2
DVH120* | 10 | 4000 | 85 | 67 | 62 | 146.2 | 0.83 | 27.43
DVH120* | 10 | 4000 | 85 | 70 | 62 | 154.6 | 0.72 | 25.23
DVH120* | 10 | 4000 | 85 | 72 | 62 | 159.9 | 0.64 | 23.16
DVH120* | 10 | 4000 | 85 | 75 | 62 | 168 | 0.54 | 20.77
DVH120* | 10 | 4000 | 85 | 57 | 66 | 132.4 | 1 | 30.09
DVH120* | 10 | 4000 | 85 | 61 | 66 | 134.9 | 0.96 | 29.55
DVH120* | 10 | 4000 | 85 | 64 | 66 | 136.7 | 0.96 | 29.95
DVH120* | 10 | 4000 | 85 | 67 | 66 | 144.1 | 0.83 | 27.2
DVH120* | 10 | 4000 | 85 | 70 | 66 | 152.4 | 0.72 | 25.02
DVH120* | 10 | 4000 | 85 | 72 | 66 | 157.6 | 0.64 | 22.98
DVH120* | 10 | 4000 | 85 | 75 | 66 | 165.7 | 0.55 | 20.55
DVH120* | 10 | 4000 | 85 | 57 | 70 | 130.8 | 1 | 29.73
DVH120* | 10 | 4000 | 85 | 61 | 70 | 133 | 0.97 | 29.3
DVH120* | 10 | 4000 | 85 | 64 | 70 | 134.7 | 0.97 | 29.7
DVH120* | 10 | 4000 | 85 | 67 | 70 | 142 | 0.84 | 26.98
DVH120* | 10 | 4000 | 85 | 70 | 70 | 150.1 | 0.73 | 24.82
DVH120* | 10 | 4000 | 85 | 72 | 70 | 155.3 | 0.65 | 22.77
DVH120* | 10 | 4000 | 85 | 75 | 70 | 163.3 | 0.55 | 20.3
DVH120* | 10 | 4000 | 85 | 57 | 72 | 130 | 1 | 29.55
DVH120* | 10 | 4000 | 85 | 61 | 72 | 132 | 0.97 | 29.16
DVH120* | 10 | 4000 | 85 | 64 | 72 | 133.7 | 0.97 | 29.57
DVH120* | 10 | 4000 | 85 | 67 | 72 | 141 | 0.84 | 26.86
DVH120* | 10 | 4000 | 85 | 70 | 72 | 149 | 0.73 | 24.7
DVH120* | 10 | 4000 | 85 | 72 | 72 | 154.1 | 0.65 | 22.68
DVH120* | 10 | 4000 | 85 | 75 | 72 | 162.1 | 0.55 | 20.18
DVH120* | 10 | 4000 | 85 | 57 | 75 | 128.8 | 1 | 29.27
DVH120* | 10 | 4000 | 85 | 61 | 75 | 130.5 | 0.98 | 28.98
DVH120* | 10 | 4000 | 85 | 64 | 75 | 132.2 | 0.98 | 29.39
DVH120* | 10 | 4000 | 85 | 67 | 75 | 139.4 | 0.84 | 26.68
DVH120* | 10 | 4000 | 85 | 70 | 75 | 147.3 | 0.73 | 24.55
DVH120* | 10 | 4000 | 85 | 72 | 75 | 152.4 | 0.65 | 22.52
DVH120* | 10 | 4000 | 85 | 75 | 75 | 160.3 | 0.55 | 19.98
DVH120* | 10 | 4000 | 85 | 57 | 79 | 127.2 | 1 | 28.91
DVH120* | 10 | 4000 | 85 | 61 | 79 | 128.5 | 0.98 | 28.73
DVH120* | 10 | 4000 | 85 | 64 | 79 | 130.2 | 0.98 | 29.11
DVH120* | 10 | 4000 | 85 | 67 | 79 | 137.3 | 0.85 | 26.45
DVH120* | 10 | 4000 | 85 | 70 | 79 | 145.1 | 0.74 | 24.32
DVH120* | 10 | 4000 | 85 | 72 | 79 | 150.1 | 0.65 | 22.34
DVH120* | 10 | 4000 | 85 | 75 | 79 | 158 | 0.55 | 19.75
DVH120* | 10 | 4000 | 85 | 57 | 83 | 125.6 | 1 | 28.55
DVH120* | 10 | 4000 | 85 | 61 | 83 | 126.5 | 0.99 | 28.45
DVH120* | 10 | 4000 | 85 | 64 | 83 | 128.2 | 0.99 | 28.84
DVH120* | 10 | 4000 | 85 | 67 | 83 | 135.1 | 0.85 | 26.2
DVH120* | 10 | 4000 | 85 | 70 | 83 | 142.9 | 0.74 | 24.11
DVH120* | 10 | 4000 | 85 | 72 | 83 | 147.8 | 0.66 | 22.11
DVH120* | 10 | 4000 | 85 | 75 | 83 | 155.6 | 0.55 | 19.5
DVH120* | 10 | 4000 | 85 | 57 | 87 | 124 | 1 | 28.18
DVH120* | 10 | 4000 | 85 | 61 | 87 | 124.6 | 1 | 28.18
DVH120* | 10 | 4000 | 85 | 64 | 87 | 126.1 | 1 | 28.57
DVH120* | 10 | 4000 | 85 | 67 | 87 | 133 | 0.86 | 25.95
DVH120* | 10 | 4000 | 85 | 70 | 87 | 140.6 | 0.75 | 23.86
DVH120* | 10 | 4000 | 85 | 72 | 87 | 145.5 | 0.66 | 21.91
DVH120* | 10 | 4000 | 85 | 75 | 87 | 153.2 | 0.55 | 19.25
DVH120* | 10 | 4000 | 85 | 57 | 91 | 122.4 | 1 | 27.82
DVH120* | 10 | 4000 | 85 | 61 | 91 | 122.6 | 1 | 27.91
DVH120* | 10 | 4000 | 85 | 64 | 91 | 124.1 | 1 | 28.3
DVH120* | 10 | 4000 | 85 | 67 | 91 | 130.9 | 0.86 | 25.7
DVH120* | 10 | 4000 | 85 | 70 | 91 | 138.4 | 0.75 | 23.64
DVH120* | 10 | 4000 | 85 | 72 | 91 | 143.2 | 0.67 | 21.7
DVH120* | 10 | 4000 | 85 | 75 | 91 | 150.9 | 0.55 | 19
DVH120* | 10 | 4000 | 85 | 57 | 93 | 121.6 | 1 | 27.64
DVH120* | 10 | 4000 | 85 | 61 | 93 | 121.6 | 1 | 27.77
DVH120* | 10 | 4000 | 85 | 64 | 93 | 123.1 | 1.01 | 28.16
DVH120* | 10 | 4000 | 85 | 67 | 93 | 129.9 | 0.87 | 25.57
DVH120* | 10 | 4000 | 85 | 70 | 93 | 137.3 | 0.75 | 23.52
DVH120* | 10 | 4000 | 85 | 72 | 93 | 142 | 0.67 | 21.59
DVH120* | 10 | 4000 | 85 | 75 | 93 | 149.7 | 0.55 | 18.86
DVH120* | 10 | 4000 | 85 | 57 | 95 | 120.8 | 1 | 27.45
DVH120* | 10 | 4000 | 85 | 61 | 95 | 120.6 | 1.01 | 27.61
DVH120* | 10 | 4000 | 85 | 64 | 95 | 122.1 | 1.01 | 28
DVH120* | 10 | 4000 | 85 | 67 | 95 | 128.8 | 0.87 | 25.43
DVH120* | 10 | 4000 | 85 | 70 | 95 | 136.2 | 0.76 | 23.41
DVH120* | 10 | 4000 | 85 | 72 | 95 | 140.9 | 0.67 | 21.48
DVH120* | 10 | 4000 | 85 | 75 | 95 | 148.5 | 0.55 | 18.73
DVH120* | 10 | 4000 | 85 | 57 | 99 | 119.2 | 1 | 27.09
DVH120* | 10 | 4000 | 85 | 61 | 99 | 118.6 | 1.01 | 27.34
DVH120* | 10 | 4000 | 85 | 64 | 99 | 120.1 | 1.01 | 27.7
DVH120* | 10 | 4000 | 85 | 67 | 99 | 126.7 | 0.87 | 25.18
DVH120* | 10 | 4000 | 85 | 70 | 99 | 133.9 | 0.76 | 23.16
DVH120* | 10 | 4000 | 85 | 72 | 99 | 138.5 | 0.68 | 21.25
DVH120* | 10 | 4000 | 85 | 75 | 99 | 146.1 | 0.56 | 18.48
DVH120* | 10 | 4000 | 85 | 57 | 103 | 117.6 | 1 | 26.73
DVH120* | 10 | 4000 | 85 | 61 | 103 | 116.6 | 1 | 26.5
DVH120* | 10 | 4000 | 85 | 64 | 103 | 118.1 | 1 | 26.84
DVH120* | 10 | 4000 | 85 | 67 | 103 | 124.6 | 0.88 | 24.91
DVH120* | 10 | 4000 | 85 | 70 | 103 | 131.7 | 0.77 | 22.91
DVH120* | 10 | 4000 | 85 | 72 | 103 | 136.2 | 0.68 | 21.02
DVH120* | 10 | 4000 | 85 | 75 | 103 | 143.7 | 0.56 | 18.23
DVH120* | 10 | 4000 | 85 | 57 | 106 | 116.4 | 1 | 26.45
DVH120* | 10 | 4000 | 85 | 61 | 106 | 115.2 | 1 | 26.18
DVH120* | 10 | 4000 | 85 | 64 | 106 | 116.6 | 1 | 26.5
DVH120* | 10 | 4000 | 85 | 67 | 106 | 123 | 0.88 | 24.7
DVH120* | 10 | 4000 | 85 | 70 | 106 | 130 | 0.77 | 22.73
DVH120* | 10 | 4000 | 85 | 72 | 106 | 134.5 | 0.68 | 20.86
DVH120* | 10 | 4000 | 85 | 75 | 106 | 142 | 0.56 | 18.05
DVH120* | 10 | 4000 | 85 | 57 | 110 | 114.9 | 1 | 26.11
DVH120* | 10 | 4000 | 85 | 61 | 110 | 113.2 | 1 | 25.73
DVH120* | 10 | 4000 | 85 | 64 | 110 | 114.6 | 1 | 26.05
DVH120* | 10 | 4000 | 85 | 67 | 110 | 120.9 | 0.89 | 24.43
DVH120* | 10 | 4000 | 85 | 70 | 110 | 127.8 | 0.77 | 22.45
DVH120* | 10 | 4000 | 85 | 72 | 110 | 132.2 | 0.69 | 20.61
DVH120* | 10 | 4000 | 85 | 75 | 110 | 139.6 | 0.56 | 17.77

## Gas Heating
Model | Tons | Phase | Gas Heat | Input - High Stage (MBH) | Output - High Stage (MBH) | Input - Low Stage (MBH) | Output - Low Stage (MBH) | Temp Rise - High Stage (°F) | Temp Rise - Low Stage (°F) | Thermal Efficiency (%)
DSG036 | 3 | 3-Phase | Low | 45 | 36 | 33.8 | 27 | 15-45 | 10-40 | 80
DSG036 | 3 | 3-Phase | Medium | 70 | 56 | 52.5 | 42 | 25-55 | 20-50 | 80
DSG036 | 3 | 3-Phase | High | 90 | 72 | 67.5 | 54 | 25-55 | 20-50 | 80
DSG048 | 4 | 3-Phase | Low | 70 | 56 | 52.5 | 42 | 25-55 | 20-50 | 80
DSG048 | 4 | 3-Phase | Medium | 90 | 72 | 67.5 | 54 | 25-55 | 20-50 | 80
DSG048 | 4 | 3-Phase | High | 115 | 92 | 86.3 | 69 | 30-60 | 25-55 | 80
DSG060 | 5 | 3-Phase | Low | 90 | 72 | 67.5 | 54 | 30-60 | 25-55 | 80
DSG060 | 5 | 3-Phase | Medium | 115 | 92 | 86.3 | 69 | 45-75 | 40-70 | 80
DSG060 | 5 | 3-Phase | High | 140 | 112 | 105 | 84 | 35-65 | 35-65 | 80
DSG072 | 6 | 3-Phase | Low | 90 | 72 | 67.5 | 54 | 25-55 | 20-50 | 80
DSG072 | 6 | 3-Phase | Medium | 115 | 92 | 86.3 | 69 | 25-55 | 20-50 | 80
DSG072 | 6 | 3-Phase | High | 140 | 112 | 105 | 84 | 35-65 | 30-60 | 80
DSG090 | 7.5 | 3-Phase | Low | 130 | 105.3 | 97.5 | 79 | 25-55 | 25-55 | 81
DSG090 | 7.5 | 3-Phase | Medium | 180 | 145.8 | 135 | 109.35 | 25-55 | 25-55 | 81
DSG090 | 7.5 | 3-Phase | High | 225 | 182.25 | 168.75 | 136.69 | 30-60 | 30-60 | 81
DSG102 | 8.5 | 3-Phase | Low | 130 | 105.3 | 97.5 | 79 | 25-55 | 25-55 | 81
DSG102 | 8.5 | 3-Phase | Medium | 180 | 145.8 | 135 | 109.35 | 25-55 | 25-55 | 81
DSG102 | 8.5 | 3-Phase | High | 225 | 182.25 | 168.75 | 136.69 | 30-60 | 30-60 | 81
DSG120 | 10 | 3-Phase | Low | 130 | 105.3 | 97.5 | 79 | 25-55 | 25-55 | 81
DSG120 | 10 | 3-Phase | Medium | 180 | 145.8 | 135 | 109.35 | 25-55 | 25-55 | 81
DSG120 | 10 | 3-Phase | High | 240 | 194.4 | 180 | 145.8 | 30-60 | 30-60 | 81
DSG150 | 12.5 | 3-Phase | Low | 130 | 105.3 | 97.5 | 79 | 25-55 | 25-55 | 81
DSG150 | 12.5 | 3-Phase | Medium | 180 | 145.8 | 135 | 109.35 | 25-55 | 25-55 | 81
DSG150 | 12.5 | 3-Phase | High | 240 | 194.4 | 180 | 145.8 | 30-60 | 30-60 | 81
DSG180 | 15 | 3-Phase | Low | 260 | 210.6 | 195 | 157.95 | 25-55 | 15-45 | 81
DSG180 | 15 | 3-Phase | Medium | 360 | 291.6 | 270 | 218.7 | 25-55 | 15-45 | 81
DSG180 | 15 | 3-Phase | High | 400 | 324 | 300 | 243 | 25-55 | 15-45 | 81
DSG240 | 20 | 3-Phase | Low | 260 | 210.6 | 195 | 157.95 | 25-55 | 15-45 | 81
DSG240 | 20 | 3-Phase | Medium | 360 | 291.6 | 270 | 218.7 | 25-55 | 15-45 | 81
DSG240 | 20 | 3-Phase | High | 400 | 324 | 300 | 243 | 25-55 | 15-45 | 81
DSG300 | 25 | 3-Phase | Low | 260 | 210.6 | 195 | 157.95 | 25-55 | 15-45 | 81
DSG300 | 25 | 3-Phase | Medium | 360 | 291.6 | 270 | 218.7 | 25-55 | 15-45 | 81
DSG300 | 25 | 3-Phase | High | 400 | 324 | 300 | 243 | 25-55 | 15-45 | 81
DHG036 | 3 | 3-Phase | Low | 45 | 36.45 | 33.75 | 27.38 | 15-45 | 5-35 | 80
DHG036 | 3 | 3-Phase | Medium | 70 | 56.7 | 52.5 | 42.53 | 25-55 | 15-45 | 80
DHG036 | 3 | 3-Phase | High | 115 | 93.15 | 86.25 | 69.86 | 45-75 | 35-65 | 80
DHG048 | 4 | 3-Phase | Low | 70 | 56.7 | 52.5 | 42.53 | 25-55 | 20-50 | 80
DHG048 | 4 | 3-Phase | Medium | 115 | 93.15 | 86.25 | 69.86 | 30-60 | 20-50 | 80
DHG048 | 4 | 3-Phase | High | 140 | 113.4 | 105 | 85.05 | 35-65 | 25-55 | 80
DHG060 | 5 | 3-Phase | Low | 70 | 56.7 | 52.5 | 42.53 | 25-55 | 15-45 | 80
DHG060 | 5 | 3-Phase | Medium | 115 | 93.15 | 86.25 | 69.86 | 35-65 | 35-65 | 80
DHG060 | 5 | 3-Phase | High | 140 | 113.4 | 105 | 85.05 | 35-65 | 25-55 | 80
DHG072 | 6 | 3-Phase | Low | 70 | 56.7 | 52.5 | 42.53 | 25-55 | 15-45 | 80
DHG072 | 6 | 3-Phase | Medium | 125 | 101.25 | 93.75 | 75.94 | 35-65 | 25-55 | 80
DHG072 | 6 | 3-Phase | High | 150 | 121.5 | 112.5 | 91.13 | 35-65 | 25-55 | 80
DHG090 | 7.5 | 3-Phase | Low | 130 | 105.3 | 97.5 | 79 | 25-55 | 25-55 | 81
DHG090 | 7.5 | 3-Phase | Medium | 180 | 145.8 | 135 | 109.35 | 25-55 | 25-55 | 81
DHG090 | 7.5 | 3-Phase | High | 225 | 182.25 | 168.75 | 136.69 | 40-70 | 40-70 | 81
DHG102 | 8.5 | 3-Phase | Low | 130 | 105.3 | 97.5 | 79 | 25-55 | 25-55 | 81
DHG102 | 8.5 | 3-Phase | Medium | 180 | 145.8 | 135 | 109.35 | 25-55 | 25-55 | 81
DHG102 | 8.5 | 3-Phase | High | 225 | 182.25 | 168.75 | 136.69 | 40-70 | 40-70 | 81
DHG120 | 10 | 3-Phase | Low | 130 | 105.3 | 97.5 | 79 | 25-55 | 25-55 | 81
DHG120 | 10 | 3-Phase | Medium | 180 | 145.8 | 135 | 109.35 | 25-55 | 25-55 | 81
DHG120 | 10 | 3-Phase | High | 240 | 194.4 | 180 | 145.8 | 30-60 | 30-60 | 81
DHG150 | 12.5 | 3-Phase | Low | 130 | 105.3 | 97.5 | 79 | 25-55 | 25-55 | 81
DHG150 | 12.5 | 3-Phase | Medium | 180 | 145.8 | 135 | 109.35 | 25-55 | 25-55 | 81
DHG150 | 12.5 | 3-Phase | High | 240 | 194.4 | 180 | 145.8 | 35-65 | 35-65 | 81

## Heat Pump
Model | Tons | CFM | EAT DB (°F) | OA DB (°F) | OA WB (°F) | MBh | ∆T (°F) | kW | COP
DSH036*D | 3 | 1220 | 70 | 65 |  | 43.43 | 31.7 | 2.91 | 4.37
DSH036*D | 3 | 1220 | 70 | 60 |  | 40.68 | 29.98 | 2.86 | 4.16
DSH036*D | 3 | 1220 | 70 | 55 |  | 37.97 | 28.26 | 2.81 | 3.96
DSH036*D | 3 | 1220 | 70 | 50 |  | 35.31 | 26.53 | 2.76 | 3.74
DSH036*D | 3 | 1220 | 70 | 47 |  | 33.6 | 25.5 | 2.74 | 3.6
DSH036*D | 3 | 1220 | 70 | 45 |  | 32.35 | 24.56 | 2.72 | 3.49
DSH036*D | 3 | 1220 | 70 | 40 |  | 29.17 | 22.14 | 2.67 | 3.21
DSH036*D | 3 | 1220 | 70 | 35 |  | 26.22 | 19.9 | 2.62 | 2.93
DSH036*D | 3 | 1220 | 70 | 30 |  | 23.8 | 18.06 | 2.57 | 2.71
DSH036*D | 3 | 1220 | 70 | 25 |  | 22.02 | 16.71 | 2.52 | 2.56
DSH036*D | 3 | 1220 | 70 | 20 |  | 20.7 | 15.71 | 2.47 | 2.46
DSH036*D | 3 | 1220 | 70 | 17 |  | 20 | 15.18 | 2.44 | 2.4
DSH036*D | 3 | 1220 | 70 | 15 |  | 19.09 | 14.49 | 2.42 | 2.31
DSH036*D | 3 | 1220 | 70 | 10 |  | 16.83 | 12.77 | 2.37 | 2.08
DSH036*D | 3 | 1220 | 70 | 5 |  | 14.56 | 11.05 | 2.33 | 1.84
DSH036*D | 3 | 1220 | 70 | 0 |  | 12.29 | 9.33 | 2.28 | 1.58
DSH036*D | 3 | 1220 | 70 | -5 |  | 10.03 | 7.61 | 2.23 | 1.32
DSH048*D | 4 | 1580 | 70 | 65 |  | 58.66 | 33.05 | 3.96 | 4.34
DSH048*D | 4 | 1580 | 70 | 60 |  | 54.83 | 31.2 | 3.88 | 4.15
DSH048*D | 4 | 1580 | 70 | 55 |  | 51.07 | 29.34 | 3.79 | 3.95
DSH048*D | 4 | 1580 | 70 | 50 |  | 47.37 | 27.49 | 3.71 | 3.74
DSH048*D | 4 | 1580 | 70 | 47 |  | 45 | 26.37 | 3.66 | 3.6
DSH048*D | 4 | 1580 | 70 | 45 |  | 43.24 | 25.34 | 3.63 | 3.49
DSH048*D | 4 | 1580 | 70 | 40 |  | 38.78 | 22.73 | 3.55 | 3.2
DSH048*D | 4 | 1580 | 70 | 35 |  | 34.68 | 20.32 | 3.47 | 2.93
DSH048*D | 4 | 1580 | 70 | 30 |  | 31.33 | 18.36 | 3.39 | 2.71
DSH048*D | 4 | 1580 | 70 | 25 |  | 28.84 | 16.9 | 3.31 | 2.56
DSH048*D | 4 | 1580 | 70 | 20 |  | 26.99 | 15.82 | 3.22 | 2.45
DSH048*D | 4 | 1580 | 70 | 17 |  | 26 | 15.24 | 3.18 | 2.4
DSH048*D | 4 | 1580 | 70 | 15 |  | 24.73 | 14.49 | 3.14 | 2.31
DSH048*D | 4 | 1580 | 70 | 10 |  | 21.57 | 12.64 | 3.06 | 2.06
DSH048*D | 4 | 1580 | 70 | 5 |  | 18.4 | 10.78 | 2.98 | 1.81
DSH048*D | 4 | 1580 | 70 | 0 |  | 15.23 | 8.93 | 2.9 | 1.54
DSH048*D | 4 | 1580 | 70 | -5 |  | 12.07 | 7.07 | 2.82 | 1.26
DSH060*D | 5 | 1870 | 70 | 65 |  | 69.68 | 33.18 | 4.6 | 4.44
DSH060*D | 5 | 1870 | 70 | 60 |  | 65.58 | 31.53 | 4.57 | 4.21
DSH060*D | 5 | 1870 | 70 | 55 |  | 61.54 | 29.88 | 4.53 | 3.98
DSH060*D | 5 | 1870 | 70 | 50 |  | 57.57 | 28.23 | 4.5 | 3.75
DSH060*D | 5 | 1870 | 70 | 47 |  | 55 | 27.23 | 4.48 | 3.6
DSH060*D | 5 | 1870 | 70 | 45 |  | 53.13 | 26.35 | 4.46 | 3.49
DSH060*D | 5 | 1870 | 70 | 40 |  | 48.57 | 24.05 | 4.43 | 3.21
DSH060*D | 5 | 1870 | 70 | 35 |  | 44.16 | 21.87 | 4.4 | 2.94
DSH060*D | 5 | 1870 | 70 | 30 |  | 40.54 | 20.07 | 4.36 | 2.72
DSH060*D | 5 | 1870 | 70 | 25 |  | 37.91 | 18.77 | 4.33 | 2.57
DSH060*D | 5 | 1870 | 70 | 20 |  | 36.02 | 17.83 | 4.29 | 2.46
DSH060*D | 5 | 1870 | 70 | 17 |  | 35 | 17.33 | 4.27 | 2.4
DSH060*D | 5 | 1870 | 70 | 15 |  | 33.67 | 16.67 | 4.26 | 2.32
DSH060*D | 5 | 1870 | 70 | 10 |  | 30.33 | 15.02 | 4.23 | 2.1
DSH060*D | 5 | 1870 | 70 | 5 |  | 27 | 13.37 | 4.19 | 1.89
DSH060*D | 5 | 1870 | 70 | 0 |  | 23.67 | 11.72 | 4.16 | 1.67
DSH060*D | 5 | 1870 | 70 | -5 |  | 20.33 | 10.07 | 4.12 | 1.44
DSH072*D | 6 | 2380 | 70 | 65 |  | 87.78 | 32.84 | 6.27 | 4.1
DSH072*D | 6 | 2380 | 70 | 60 |  | 81.95 | 30.96 | 6.13 | 3.92
DSH072*D | 6 | 2380 | 70 | 55 |  | 76.23 | 29.08 | 6 | 3.73
DSH072*D | 6 | 2380 | 70 | 50 |  | 70.6 | 27.2 | 5.86 | 3.53
DSH072*D | 6 | 2380 | 70 | 47 |  | 67 | 26.07 | 5.78 | 3.4
DSH072*D | 6 | 2380 | 70 | 45 |  | 64.3 | 25.01 | 5.72 | 3.29
DSH072*D | 6 | 2380 | 70 | 40 |  | 57.48 | 22.36 | 5.58 | 3.02
DSH072*D | 6 | 2380 | 70 | 35 |  | 51.24 | 19.93 | 5.45 | 2.76
DSH072*D | 6 | 2380 | 70 | 30 |  | 46.14 | 17.95 | 5.31 | 2.55
DSH072*D | 6 | 2380 | 70 | 25 |  | 42.35 | 16.48 | 5.17 | 2.4
DSH072*D | 6 | 2380 | 70 | 20 |  | 39.52 | 15.37 | 5.03 | 2.3
DSH072*D | 6 | 2380 | 70 | 17 |  | 38 | 14.78 | 4.95 | 2.25
DSH072*D | 6 | 2380 | 70 | 15 |  | 36.07 | 14.03 | 4.89 | 2.16
DSH072*D | 6 | 2380 | 70 | 10 |  | 31.23 | 12.15 | 4.76 | 1.92
DSH072*D | 6 | 2380 | 70 | 5 |  | 26.4 | 10.27 | 4.62 | 1.67
DSH072*D | 6 | 2380 | 70 | 0 |  | 21.57 | 8.39 | 4.48 | 1.41
DSH072*D | 6 | 2380 | 70 | -5 |  | 16.73 | 6.51 | 4.34 | 1.13
DSH090* | 7.5 | 3000 | 70 | 65 |  | 109.62 | 32.53 | 7.74 | 4.15
DSH090* | 7.5 | 3000 | 70 | 60 |  | 102.73 | 30.78 | 7.62 | 3.95
DSH090* | 7.5 | 3000 | 70 | 55 |  | 95.95 | 29.03 | 7.51 | 3.74
DSH090* | 7.5 | 3000 | 70 | 50 |  | 89.28 | 27.29 | 7.4 | 3.54
DSH090* | 7.5 | 3000 | 70 | 47 |  | 85 | 26.5 | 7.33 | 3.4
DSH090* | 7.5 | 3000 | 70 | 45 |  | 81.9 | 25.28 | 7.28 | 3.3
DSH090* | 7.5 | 3000 | 70 | 40 |  | 73.94 | 22.82 | 7.17 | 3.02
DSH090* | 7.5 | 3000 | 70 | 35 |  | 66.54 | 20.54 | 7.05 | 2.76
DSH090* | 7.5 | 3000 | 70 | 30 |  | 60.49 | 18.67 | 6.94 | 2.55
DSH090* | 7.5 | 3000 | 70 | 25 |  | 56.03 | 17.29 | 6.83 | 2.41
DSH090* | 7.5 | 3000 | 70 | 20 |  | 52.76 | 16.28 | 6.71 | 2.3
DSH090* | 7.5 | 3000 | 70 | 17 |  | 51 | 15.74 | 6.64 | 2.25
DSH090* | 7.5 | 3000 | 70 | 15 |  | 48.73 | 15.04 | 6.6 | 2.16
DSH090* | 7.5 | 3000 | 70 | 10 |  | 43.07 | 13.29 | 6.48 | 1.95
DSH090* | 7.5 | 3000 | 70 | 5 |  | 37.4 | 11.54 | 6.37 | 1.72
DSH090* | 7.5 | 3000 | 70 | 0 |  | 31.73 | 9.79 | 6.26 | 1.49
DSH090* | 7.5 | 3000 | 70 | -5 |  | 26.07 | 8.04 | 6.14 | 1.24
DSH102* | 8.5 | 3000 | 70 | 65 |  | 128.34 | 38.09 | 9.02 | 4.17
DSH102* | 8.5 | 3000 | 70 | 60 |  | 120.41 | 36.08 | 8.91 | 3.96
DSH102* | 8.5 | 3000 | 70 | 55 |  | 112.61 | 34.08 | 8.8 | 3.75
DSH102* | 8.5 | 3000 | 70 | 50 |  | 104.94 | 32.07 | 8.69 | 3.54
DSH102* | 8.5 | 3000 | 70 | 47 |  | 100 | 30.87 | 8.62 | 3.4
DSH102* | 8.5 | 3000 | 70 | 45 |  | 96.43 | 29.77 | 8.58 | 3.3
DSH102* | 8.5 | 3000 | 70 | 40 |  | 87.35 | 26.96 | 8.46 | 3.03
DSH102* | 8.5 | 3000 | 70 | 35 |  | 78.84 | 24.33 | 8.35 | 2.77
DSH102* | 8.5 | 3000 | 70 | 30 |  | 71.87 | 22.18 | 8.24 | 2.56
DSH102* | 8.5 | 3000 | 70 | 25 |  | 66.75 | 20.6 | 8.13 | 2.41
DSH102* | 8.5 | 3000 | 70 | 20 |  | 63.01 | 19.45 | 8.01 | 2.3
DSH102* | 8.5 | 3000 | 70 | 17 |  | 61 | 18.83 | 7.95 | 2.25
DSH102* | 8.5 | 3000 | 70 | 15 |  | 58.4 | 18.02 | 7.9 | 2.17
DSH102* | 8.5 | 3000 | 70 | 10 |  | 51.9 | 16.02 | 7.79 | 1.95
DSH102* | 8.5 | 3000 | 70 | 5 |  | 45.4 | 14.01 | 7.68 | 1.73
DSH102* | 8.5 | 3000 | 70 | 0 |  | 38.9 | 12.01 | 7.56 | 1.51
DSH102* | 8.5 | 3000 | 70 | -5 |  | 32.4 | 10 | 7.45 | 1.27
DSH120* | 10 | 3850 | 70 | 65 |  | 152.46 | 35.26 | 10.92 | 4.09
DSH120* | 10 | 3850 | 70 | 60 |  | 142.24 | 33.22 | 10.66 | 3.91
DSH120* | 10 | 3850 | 70 | 55 |  | 132.19 | 31.17 | 10.41 | 3.72
DSH120* | 10 | 3850 | 70 | 50 |  | 122.31 | 29.13 | 10.15 | 3.53
DSH120* | 10 | 3850 | 70 | 47 |  | 116 | 27.9 | 10 | 3.4
DSH120* | 10 | 3850 | 70 | 45 |  | 111.23 | 26.75 | 9.9 | 3.29
DSH120* | 10 | 3850 | 70 | 40 |  | 99.23 | 23.87 | 9.64 | 3.02
DSH120* | 10 | 3850 | 70 | 35 |  | 88.27 | 21.23 | 9.39 | 2.76
DSH120* | 10 | 3850 | 70 | 30 |  | 79.34 | 19.08 | 9.13 | 2.55
DSH120* | 10 | 3850 | 70 | 25 |  | 72.67 | 17.48 | 8.88 | 2.4
DSH120* | 10 | 3850 | 70 | 20 |  | 67.68 | 16.28 | 8.62 | 2.3
DSH120* | 10 | 3850 | 70 | 17 |  | 65 | 15.63 | 8.47 | 2.25
DSH120* | 10 | 3850 | 70 | 15 |  | 61.6 | 14.81 | 8.36 | 2.16
DSH120* | 10 | 3850 | 70 | 10 |  | 53.1 | 12.77 | 8.11 | 1.92
DSH120* | 10 | 3850 | 70 | 5 |  | 44.6 | 10.73 | 7.85 | 1.66
DSH120* | 10 | 3850 | 70 | 0 |  | 36.1 | 8.68 | 7.6 | 1.39
DSH120* | 10 | 3850 | 70 | -5 |  | 27.6 | 6.64 | 7.34 | 1.1
DSH150* | 12.5 | 4300 | 70 | 65 |  | 184.6 | 38.22 | 12.39 | 4.37
DSH150* | 12.5 | 4300 | 70 | 60 |  | 172.95 | 36.16 | 12.37 | 4.1
DSH150* | 12.5 | 4300 | 70 | 55 |  | 161.5 | 34.1 | 12.35 | 3.83
DSH150* | 12.5 | 4300 | 70 | 50 |  | 150.24 | 32.03 | 12.34 | 3.57
DSH150* | 12.5 | 4300 | 70 | 47 |  | 143 | 30.79 | 12.33 | 3.4
DSH150* | 12.5 | 4300 | 70 | 45 |  | 137.75 | 29.66 | 12.32 | 3.28
DSH150* | 12.5 | 4300 | 70 | 40 |  | 124.28 | 26.76 | 12.3 | 2.96
DSH150* | 12.5 | 4300 | 70 | 35 |  | 111.78 | 24.07 | 12.29 | 2.67
DSH150* | 12.5 | 4300 | 70 | 30 |  | 101.56 | 21.87 | 12.27 | 2.43
DSH150* | 12.5 | 4300 | 70 | 25 |  | 94.02 | 20.25 | 12.25 | 2.25
DSH150* | 12.5 | 4300 | 70 | 20 |  | 88.48 | 19.05 | 12.23 | 2.12
DSH150* | 12.5 | 4300 | 70 | 17 |  | 85.5 | 18.41 | 12.22 | 2.05
DSH150* | 12.5 | 4300 | 70 | 15 |  | 81.67 | 17.59 | 12.22 | 1.96
DSH150* | 12.5 | 4300 | 70 | 10 |  | 72.08 | 15.52 | 12.2 | 1.73
DSH150* | 12.5 | 4300 | 70 | 5 |  | 62.5 | 13.46 | 12.18 | 1.5
DSH150* | 12.5 | 4300 | 70 | 0 |  | 52.92 | 11.39 | 12.17 | 1.27
DSH150* | 12.5 | 4300 | 70 | -5 |  | 43.33 | 9.33 | 12.15 | 1.05
DSH180* | 15 | 7700 | 70 | 65 |  | 223.8 | 28 | 15.87 | 4.13
DSH180* | 15 | 7700 | 70 | 60 |  | 209.3 | 26.2 | 15.71 | 3.91
DSH180* | 15 | 7700 | 70 | 55 |  | 195 | 24.4 | 15.55 | 3.68
DSH180* | 15 | 7700 | 70 | 50 |  | 181 | 22.6 | 15.38 | 3.45
DSH180* | 15 | 7700 | 70 | 47 |  | 172 | 21.5 | 15.28 | 3.3
DSH180* | 15 | 7700 | 70 | 45 |  | 165.3 | 20.7 | 15.22 | 3.19
DSH180* | 15 | 7700 | 70 | 40 |  | 148.5 | 18.6 | 15.06 | 2.89
DSH180* | 15 | 7700 | 70 | 35 |  | 132.9 | 16.6 | 14.89 | 2.62
DSH180* | 15 | 7700 | 70 | 30 |  | 120.2 | 15 | 14.73 | 2.39
DSH180* | 15 | 7700 | 70 | 25 |  | 110.7 | 13.9 | 14.57 | 2.23
DSH180* | 15 | 7700 | 70 | 20 |  | 103.8 | 13 | 14.4 | 2.11
DSH180* | 15 | 7700 | 70 | 17 |  | 100 | 12.5 | 14.31 | 2.05
DSH180* | 15 | 7700 | 70 | 15 |  | 95.2 | 11.9 | 14.24 | 1.96
DSH180* | 15 | 7700 | 70 | 10 |  | 83.2 | 10.4 | 14.08 | 1.73
DSH180* | 15 | 7700 | 70 | 5 |  | 71.2 | 8.9 | 13.91 | 1.5
DSH180* | 15 | 7700 | 70 | 0 |  | 59.2 | 7.4 | 13.75 | 1.26
DSH240* | 20 | 7000 | 70 | 65 |  | 290 | 33.6 | 20.8 | 4.1
DSH240* | 20 | 7000 | 70 | 60 |  | 270.3 | 31.3 | 20.5 | 3.9
DSH240* | 20 | 7000 | 70 | 55 |  | 251.1 | 29.1 | 20.1 | 3.7
DSH240* | 20 | 7000 | 70 | 50 |  | 232.1 | 26.9 | 19.8 | 3.4
DSH240* | 20 | 7000 | 70 | 47 |  | 220 | 25.5 | 19.6 | 3.3
DSH240* | 20 | 7000 | 70 | 45 |  | 210.8 | 24.4 | 19.4 | 3.2
DSH240* | 20 | 7000 | 70 | 40 |  | 187.7 | 21.7 | 19.1 | 2.9
DSH240* | 20 | 7000 | 70 | 35 |  | 166.7 | 19.3 | 18.7 | 2.6
DSH240* | 20 | 7000 | 70 | 30 |  | 149.6 | 17.3 | 18.4 | 2.4
DSH240* | 20 | 7000 | 70 | 25 |  | 136.8 | 15.8 | 18 | 2.2
DSH240* | 20 | 7000 | 70 | 20 |  | 127.2 | 14.7 | 17.7 | 2.1
DSH240* | 20 | 7000 | 70 | 17 |  | 122 | 14.1 | 17.5 | 2.1
DSH240* | 20 | 7000 | 70 | 15 |  | 115.5 | 13.4 | 17.3 | 2
DSH240* | 20 | 7000 | 70 | 10 |  | 99.1 | 11.5 | 17 | 1.7
DSH240* | 20 | 7000 | 70 | 5 |  | 82.8 | 9.6 | 16.6 | 1.5
DSH240* | 20 | 7000 | 70 | 0 |  | 66.5 | 7.7 | 16.3 | 1.2
DHH036* | 3 | 1150 | 70 | 65 |  | 44.01 | 34.08 | 2.72 | 4.74
DHH036* | 3 | 1150 | 70 | 60 |  | 40.98 | 32.04 | 2.68 | 4.49
DHH036* | 3 | 1150 | 70 | 55 |  | 38 | 30 | 2.63 | 4.23
DHH036* | 3 | 1150 | 70 | 50 |  | 35.07 | 27.96 | 2.59 | 3.97
DHH036* | 3 | 1150 | 70 | 47 |  | 33.2 | 26.73 | 2.56 | 3.8
DHH036* | 3 | 1150 | 70 | 45 |  | 31.76 | 25.57 | 2.54 | 3.66
DHH036* | 3 | 1150 | 70 | 40 |  | 28.18 | 22.69 | 2.5 | 3.31
DHH036* | 3 | 1150 | 70 | 35 |  | 24.93 | 20.07 | 2.45 | 2.98
DHH036* | 3 | 1150 | 70 | 30 |  | 22.28 | 17.94 | 2.41 | 2.71
DHH036* | 3 | 1150 | 70 | 25 |  | 20.3 | 16.34 | 2.36 | 2.52
DHH036* | 3 | 1150 | 70 | 20 |  | 18.8 | 15.14 | 2.32 | 2.37
DHH036* | 3 | 1150 | 70 | 17 |  | 18 | 14.49 | 2.29 | 2.3
DHH036* | 3 | 1150 | 70 | 15 |  | 16.99 | 13.68 | 2.28 | 2.19
DHH036* | 3 | 1150 | 70 | 10 |  | 14.46 | 11.64 | 2.23 | 1.9
DHH036* | 3 | 1150 | 70 | 5 |  |  | 9.6 | 2.19
DHH036* | 3 | 1150 | 70 | 0 |  | 9.39 | 7.56 | 2.14 | 1.28
DHH036* | 3 | 1150 | 70 | -5 |  | 6.85 | 5.52 | 2.1 | 0.96
DHH048* | 4 | 1550 | 70 | 65 |  | 59.7 | 34.29 | 3.78 | 4.63
DHH048* | 4 | 1550 | 70 | 60 |  | 55.86 | 32.4 | 3.71 | 4.41
DHH048* | 4 | 1550 | 70 | 55 |  | 52.09 | 30.51 | 3.65 | 4.18
DHH048* | 4 | 1550 | 70 | 50 |  | 48.38 | 28.62 | 3.59 | 3.95
DHH048* | 4 | 1550 | 70 | 47 |  | 46 | 27.48 | 3.55 | 3.8
DHH048* | 4 | 1550 | 70 | 45 |  | 44.25 | 26.43 | 3.52 | 3.68
DHH048* | 4 | 1550 | 70 | 40 |  | 39.8 | 23.77 | 3.46 | 3.37
DHH048* | 4 | 1550 | 70 | 35 |  | 35.68 | 21.31 | 3.39 | 3.08
DHH048* | 4 | 1550 | 70 | 30 |  | 32.32 | 19.31 | 3.33 | 2.84
DHH048* | 4 | 1550 | 70 | 25 |  | 29.83 | 17.82 | 3.27 | 2.68
DHH048* | 4 | 1550 | 70 | 20 |  | 27.99 | 16.72 | 3.2 | 2.56
DHH048* | 4 | 1550 | 70 | 17 |  | 27 | 16.13 | 3.17 | 2.5
DHH048* | 4 | 1550 | 70 | 15 |  | 25.73 | 15.37 | 3.14 | 2.4
DHH048* | 4 | 1550 | 70 | 10 |  | 22.57 | 13.48 | 3.08 | 2.15
DHH048* | 4 | 1550 | 70 | 5 |  | 19.4 | 11.59 | 3.01 | 1.89
DHH048* | 4 | 1550 | 70 | 0 |  | 16.23 | 9.7 | 2.95 | 1.61
DHH048* | 4 | 1550 | 70 | -5 |  | 13.07 | 7.8 | 2.88 | 1.33
DHH060* | 5 | 1950 | 70 | 65 |  | 76.34 | 34.86 | 4.82 | 4.64
DHH060* | 5 | 1950 | 70 | 60 |  | 71.48 | 32.96 | 4.74 | 4.42
DHH060* | 5 | 1950 | 70 | 55 |  | 66.71 | 31.06 | 4.67 | 4.19
DHH060* | 5 | 1950 | 70 | 50 |  | 62.01 | 29.16 | 4.6 | 3.96
DHH060* | 5 | 1950 | 70 | 47 |  | 59 | 28.02 | 4.55 | 3.8
DHH060* | 5 | 1950 | 70 | 45 |  | 56.8 | 26.97 | 4.52 | 3.68
DHH060* | 5 | 1950 | 70 | 40 |  | 51.18 | 24.3 | 4.45 | 3.37
DHH060* | 5 | 1950 | 70 | 35 |  | 45.97 | 21.83 | 4.37 | 3.08
DHH060* | 5 | 1950 | 70 | 30 |  | 41.71 | 19.81 | 4.3 | 2.84
DHH060* | 5 | 1950 | 70 | 25 |  | 38.56 | 18.31 | 4.22 | 2.68
DHH060* | 5 | 1950 | 70 | 20 |  | 36.24 | 17.21 | 4.15 | 2.56
DHH060* | 5 | 1950 | 70 | 17 |  | 35 | 16.62 | 4.1 | 2.5
DHH060* | 5 | 1950 | 70 | 15 |  | 33.4 | 15.86 | 4.07 | 2.4
DHH060* | 5 | 1950 | 70 | 10 |  | 29.4 | 13.96 | 4 | 2.15
DHH060* | 5 | 1950 | 70 | 5 |  | 25.4 | 12.06 | 3.92 | 1.9
DHH060* | 5 | 1950 | 70 | 0 |  | 21.4 | 10.16 | 3.85 | 1.63
DHH060* | 5 | 1950 | 70 | -5 |  | 17.4 | 8.26 | 3.78 | 1.35
DHH072* | 6 | 2200 | 70 | 65 |  | 80.7 | 32.66 | 5.67 | 4.17
DHH072* | 6 | 2200 | 70 | 60 |  | 75.46 | 30.84 | 5.54 | 3.99
DHH072* | 6 | 2200 | 70 | 55 |  | 70.31 | 29.01 | 5.4 | 3.81
DHH072* | 6 | 2200 | 70 | 50 |  | 65.25 | 27.19 | 5.27 | 3.63
DHH072* | 6 | 2200 | 70 | 47 |  | 62 | 26.1 | 5.19 | 3.5
DHH072* | 6 | 2200 | 70 | 45 |  | 59.6 | 25.08 | 5.14 | 3.4
DHH072* | 6 | 2200 | 70 | 40 |  | 53.5 | 22.52 | 5.01 | 3.13
DHH072* | 6 | 2200 | 70 | 35 |  | 47.87 | 20.15 | 4.87 | 2.88
DHH072* | 6 | 2200 | 70 | 30 |  | 43.29 | 18.22 | 4.74 | 2.68
DHH072* | 6 | 2200 | 70 | 25 |  | 39.88 | 16.78 | 4.61 | 2.54
DHH072* | 6 | 2200 | 70 | 20 |  | 37.36 | 15.72 | 4.48 | 2.45
DHH072* | 6 | 2200 | 70 | 17 |  | 36 | 15.15 | 4.4 | 2.4
DHH072* | 6 | 2200 | 70 | 15 |  | 34.27 | 14.42 | 4.34 | 2.31
DHH072* | 6 | 2200 | 70 | 10 |  | 29.93 | 12.6 | 4.21 | 2.08
DHH072* | 6 | 2200 | 70 | 5 |  | 25.6 | 10.77 | 4.08 | 1.84
DHH072* | 6 | 2200 | 70 | 0 |  | 21.27 | 8.95 | 3.95 | 1.58
DHH072* | 6 | 2200 | 70 | -5 |  | 16.93 | 7.13 | 3.81 | 1.3
DVH090* | 7.5 | 2550 | 61 |  | 65 | 126 | 45.75 | 6.24
DVH090* | 7.5 | 2550 | 61 |  | 60 | 116.83 | 42.42 | 6.14
DVH090* | 7.5 | 2550 | 61 |  | 55 | 108.05 | 39.23 | 6.03
DVH090* | 7.5 | 2550 | 61 |  | 50 | 99.66 | 36.19 | 5.92
DVH090* | 7.5 | 2550 | 61 |  | 45 | 91.66 | 33.28 | 5.8
DVH090* | 7.5 | 2550 | 61 |  | 40 | 84.05 | 30.52 | 5.68
DVH090* | 7.5 | 2550 | 61 |  | 35 | 76.83 | 27.9 | 5.56
DVH090* | 7.5 | 2550 | 61 |  | 30 | 70 | 25.42 | 5.43
DVH090* | 7.5 | 2550 | 61 |  | 25 | 63.56 | 23.08 | 5.3
DVH090* | 7.5 | 2550 | 61 |  | 20 | 57.51 | 20.88 | 5.16
DVH090* | 7.5 | 2550 | 61 |  | 15 | 51.85 | 18.83 | 5.02
DVH090* | 7.5 | 2550 | 61 |  | 10 | 46.58 | 16.91 | 5.96
DVH090* | 7.5 | 2550 | 61 |  | 5 | 41.71 | 15.15 | 5.83
DVH090* | 7.5 | 2550 | 61 |  | 0 | 37.22 | 13.51 | 5.71
DVH090* | 7.5 | 2550 | 61 |  | -5 | 33.12 | 12.03 | 5.59
DVH090* | 7.5 | 2550 | 61 |  | -10 | 29.41 | 10.68 | 5.48
DVH090* | 7.5 | 2550 | 61 |  | -13 | 27.37 | 9.94 | 5.42
DVH090* | 7.5 | 2550 | 65 |  | 65 | 124.92 | 45.36 | 6.61
DVH090* | 7.5 | 2550 | 65 |  | 60 | 115.81 | 42.05 | 6.49
DVH090* | 7.5 | 2550 | 65 |  | 55 | 107.09 | 38.89 | 6.37
DVH090* | 7.5 | 2550 | 65 |  | 50 | 98.75 | 35.86 | 6.24
DVH090* | 7.5 | 2550 | 65 |  | 45 | 90.8 | 32.97 | 6.11
DVH090* | 7.5 | 2550 | 65 |  | 40 | 83.23 | 30.22 | 5.98
DVH090* | 7.5 | 2550 | 65 |  | 35 | 76.05 | 27.61 | 5.84
DVH090* | 7.5 | 2550 | 65 |  | 30 | 69.25 | 25.15 | 5.7
DVH090* | 7.5 | 2550 | 65 |  | 25 | 62.84 | 22.82 | 5.55
DVH090* | 7.5 | 2550 | 65 |  | 20 | 56.82 | 20.63 | 5.4
DVH090* | 7.5 | 2550 | 65 |  | 15 | 51.17 | 18.58 | 5.25
DVH090* | 7.5 | 2550 | 65 |  | 10 | 45.92 | 16.67 | 6.18
DVH090* | 7.5 | 2550 | 65 |  | 5 | 41.04 | 14.9 | 6.04
DVH090* | 7.5 | 2550 | 65 |  | 0 | 36.56 | 13.28 | 5.91
DVH090* | 7.5 | 2550 | 65 |  | -5 | 32.45 | 11.78 | 5.79
DVH090* | 7.5 | 2550 | 65 |  | -10 | 28.73 | 10.43 | 5.67
DVH090* | 7.5 | 2550 | 65 |  | -13 | 26.69 | 9.69 | 5.6
DVH090* | 7.5 | 2550 | 68 |  | 65 | 124.1 | 45.06 | 6.89
DVH090* | 7.5 | 2550 | 68 |  | 60 | 115.05 | 41.78 | 6.76
DVH090* | 7.5 | 2550 | 68 |  | 55 | 106.37 | 38.62 | 6.62
DVH090* | 7.5 | 2550 | 68 |  | 50 | 98.07 | 35.61 | 6.49
DVH090* | 7.5 | 2550 | 68 |  | 45 | 90.16 | 32.74 | 6.35
DVH090* | 7.5 | 2550 | 68 |  | 40 | 82.62 | 30 | 6.2
DVH090* | 7.5 | 2550 | 68 |  | 35 | 75.47 | 27.4 | 6.05
DVH090* | 7.5 | 2550 | 68 |  | 30 | 68.7 | 24.95 | 5.9
DVH090* | 7.5 | 2550 | 68 |  | 25 | 62.3 | 22.62 | 5.75
DVH090* | 7.5 | 2550 | 68 |  | 20 | 56.29 | 20.44 | 5.59
DVH090* | 7.5 | 2550 | 68 |  | 15 | 50.66 | 18.4 | 5.43
DVH090* | 7.5 | 2550 | 68 |  | 10 | 45.41 | 16.49 | 6.35
DVH090* | 7.5 | 2550 | 68 |  | 5 | 40.55 | 14.72 | 6.21
DVH090* | 7.5 | 2550 | 68 |  | 0 | 36.06 | 13.09 | 6.07
DVH090* | 7.5 | 2550 | 68 |  | -5 | 31.95 | 11.6 | 5.93
DVH090* | 7.5 | 2550 | 68 |  | -10 | 28.23 | 10.25 | 5.81
DVH090* | 7.5 | 2550 | 68 |  | -13 | 26.17 | 9.5 | 5.74
DVH090* | 7.5 | 2550 | 70 |  | 65 | 123.56 | 44.87 | 7.07
DVH090* | 7.5 | 2550 | 70 |  | 60 | 114.54 | 41.59 | 6.93
DVH090* | 7.5 | 2550 | 70 |  | 55 | 105.89 | 38.45 | 6.79
DVH090* | 7.5 | 2550 | 70 |  | 50 | 97.62 | 35.45 | 6.65
DVH090* | 7.5 | 2550 | 70 |  | 45 | 89.73 | 32.58 | 6.5
DVH090* | 7.5 | 2550 | 70 |  | 40 | 82.22 | 29.85 | 6.35
DVH090* | 7.5 | 2550 | 70 |  | 35 | 75.08 | 27.26 | 6.2
DVH090* | 7.5 | 2550 | 70 |  | 30 | 68.32 | 24.81 | 6.04
DVH090* | 7.5 | 2550 | 70 |  | 25 | 61.95 | 22.49 | 5.88
DVH090* | 7.5 | 2550 | 70 |  | 20 | 55.95 | 20.32 | 5.71
DVH090* | 7.5 | 2550 | 70 |  | 15 | 50.32 | 18.27 | 5.54
DVH090* | 7.5 | 2550 | 70 |  | 10 | 45.08 | 16.37 | 6.47
DVH090* | 7.5 | 2550 | 70 |  | 5 | 40.21 | 14.6 | 6.31
DVH090* | 7.5 | 2550 | 70 |  | 0 | 35.73 | 12.97 | 6.17
DVH090* | 7.5 | 2550 | 70 |  | -5 | 31.62 | 11.48 | 6.03
DVH090* | 7.5 | 2550 | 70 |  | -10 | 27.89 | 10.13 | 5.9
DVH090* | 7.5 | 2550 | 70 |  | -13 | 25.83 | 9.38 | 5.83
DVH090* | 7.5 | 2550 | 72 |  | 65 | 123 | 44.66 | 7.26
DVH090* | 7.5 | 2550 | 72 |  | 60 | 114.01 | 41.4 | 7.11
DVH090* | 7.5 | 2550 | 72 |  | 55 | 105.39 | 38.27 | 6.96
DVH090* | 7.5 | 2550 | 72 |  | 50 | 97.14 | 35.27 | 6.81
DVH090* | 7.5 | 2550 | 72 |  | 45 | 89.28 | 32.42 | 6.66
DVH090* | 7.5 | 2550 | 72 |  | 40 | 81.78 | 29.69 | 6.5
DVH090* | 7.5 | 2550 | 72 |  | 35 | 74.67 | 27.11 | 6.34
DVH090* | 7.5 | 2550 | 72 |  | 30 | 67.93 | 24.67 | 6.17
DVH090* | 7.5 | 2550 | 72 |  | 25 | 61.56 | 22.35 | 6.01
DVH090* | 7.5 | 2550 | 72 |  | 20 | 55.57 | 20.18 | 5.83
DVH090* | 7.5 | 2550 | 72 |  | 15 | 49.96 | 18.14 | 5.66
DVH090* | 7.5 | 2550 | 72 |  | 10 | 44.72 | 16.24 | 6.58
DVH090* | 7.5 | 2550 | 72 |  | 5 | 39.86 | 14.47 | 6.42
DVH090* | 7.5 | 2550 | 72 |  | 0 | 35.38 | 12.85 | 6.27
DVH090* | 7.5 | 2550 | 72 |  | -5 | 31.27 | 11.35 | 6.13
DVH090* | 7.5 | 2550 | 72 |  | -10 | 27.53 | 10 | 6
DVH090* | 7.5 | 2550 | 72 |  | -13 | 25.47 | 9.25 | 5.92
DVH090* | 7.5 | 2550 | 75 |  | 60 | 113.21 | 41.11 | 7.38
DVH090* | 7.5 | 2550 | 75 |  | 55 | 104.63 | 37.99 | 7.22
DVH090* | 7.5 | 2550 | 75 |  | 50 | 96.43 | 35.01 | 7.06
DVH090* | 7.5 | 2550 | 75 |  | 45 | 88.6 | 32.17 | 6.89
DVH090* | 7.5 | 2550 | 75 |  | 40 | 81.13 | 29.46 | 6.72
DVH090* | 7.5 | 2550 | 75 |  | 35 | 74.05 | 26.89 | 6.55
DVH090* | 7.5 | 2550 | 75 |  | 30 | 67.33 | 24.45 | 6.38
DVH090* | 7.5 | 2550 | 75 |  | 25 | 60.99 | 22.15 | 6.2
DVH090* | 7.5 | 2550 | 75 |  | 20 | 55.01 | 19.97 | 6.02
DVH090* | 7.5 | 2550 | 75 |  | 15 | 49.42 | 17.94 | 5.84
DVH090* | 7.5 | 2550 | 75 |  | 10 | 44.19 | 16.05 | 6.76
DVH090* | 7.5 | 2550 | 75 |  | 5 | 39.33 | 14.28 | 6.59
DVH090* | 7.5 | 2550 | 75 |  | 0 | 34.85 | 12.65 | 6.43
DVH090* | 7.5 | 2550 | 75 |  | -5 | 30.74 | 11.16 | 6.28
DVH090* | 7.5 | 2550 | 75 |  | -10 | 27 | 9.8 | 6.14
DVH090* | 7.5 | 2550 | 75 |  | -13 | 24.94 | 9.06 | 6.06
DVH090* | 7.5 | 2950 | 61 |  | 65 | 127.25 | 39.94 | 6
DVH090* | 7.5 | 2950 | 61 |  | 60 | 117.99 | 37.03 | 5.9
DVH090* | 7.5 | 2950 | 61 |  | 55 | 109.12 | 34.25 | 5.8
DVH090* | 7.5 | 2950 | 61 |  | 50 | 100.65 | 31.59 | 5.69
DVH090* | 7.5 | 2950 | 61 |  | 45 | 92.57 | 29.06 | 5.58
DVH090* | 7.5 | 2950 | 61 |  | 40 | 84.88 | 26.64 | 5.47
DVH090* | 7.5 | 2950 | 61 |  | 35 | 77.59 | 24.35 | 5.35
DVH090* | 7.5 | 2950 | 61 |  | 30 | 70.69 | 22.19 | 5.22
DVH090* | 7.5 | 2950 | 61 |  | 25 | 64.19 | 20.15 | 5.1
DVH090* | 7.5 | 2950 | 61 |  | 20 | 58.08 | 18.23 | 4.96
DVH090* | 7.5 | 2950 | 61 |  | 15 | 52.37 | 16.44 | 4.83
DVH090* | 7.5 | 2950 | 61 |  | 10 | 47.05 | 14.77 | 5.73
DVH090* | 7.5 | 2950 | 61 |  | 5 | 42.12 | 13.22 | 5.61
DVH090* | 7.5 | 2950 | 61 |  | 0 | 37.59 | 11.8 | 5.49
DVH090* | 7.5 | 2950 | 61 |  | -5 | 33.45 | 10.5 | 5.38
DVH090* | 7.5 | 2950 | 61 |  | -10 | 29.7 | 9.32 | 5.28
DVH090* | 7.5 | 2950 | 61 |  | -13 | 27.65 | 8.68 | 5.21
DVH090* | 7.5 | 2950 | 65 |  | 65 | 126.16 | 39.6 | 6.36
DVH090* | 7.5 | 2950 | 65 |  | 60 | 116.96 | 36.71 | 6.24
DVH090* | 7.5 | 2950 | 65 |  | 55 | 108.15 | 33.95 | 6.13
DVH090* | 7.5 | 2950 | 65 |  | 50 | 99.73 | 31.3 | 6.01
DVH090* | 7.5 | 2950 | 65 |  | 45 | 91.7 | 28.78 | 5.88
DVH090* | 7.5 | 2950 | 65 |  | 40 | 84.06 | 26.38 | 5.75
DVH090* | 7.5 | 2950 | 65 |  | 35 | 76.81 | 24.11 | 5.62
DVH090* | 7.5 | 2950 | 65 |  | 30 | 69.94 | 21.95 | 5.48
DVH090* | 7.5 | 2950 | 65 |  | 25 | 63.47 | 19.92 | 5.34
DVH090* | 7.5 | 2950 | 65 |  | 20 | 57.38 | 18.01 | 5.2
DVH090* | 7.5 | 2950 | 65 |  | 15 | 51.68 | 16.22 | 5.05
DVH090* | 7.5 | 2950 | 65 |  | 10 | 46.37 | 14.55 | 5.95
DVH090* | 7.5 | 2950 | 65 |  | 5 | 41.45 | 13.01 | 5.82
DVH090* | 7.5 | 2950 | 65 |  | 0 | 36.92 | 11.59 | 5.69
DVH090* | 7.5 | 2950 | 65 |  | -5 | 32.77 | 10.29 | 5.57
DVH090* | 7.5 | 2950 | 65 |  | -10 | 29.02 | 9.11 | 5.45
DVH090* | 7.5 | 2950 | 65 |  | -13 | 26.95 | 8.46 | 5.39
DVH090* | 7.5 | 2950 | 68 |  | 65 | 125.34 | 39.34 | 6.63
DVH090* | 7.5 | 2950 | 68 |  | 60 | 116.19 | 36.47 | 6.5
DVH090* | 7.5 | 2950 | 68 |  | 55 | 107.42 | 33.72 | 6.37
DVH090* | 7.5 | 2950 | 68 |  | 50 | 99.05 | 31.09 | 6.24
DVH090* | 7.5 | 2950 | 68 |  | 45 | 91.05 | 28.58 | 6.11
DVH090* | 7.5 | 2950 | 68 |  | 40 | 83.44 | 26.19 | 5.97
DVH090* | 7.5 | 2950 | 68 |  | 35 | 76.22 | 23.92 | 5.82
DVH090* | 7.5 | 2950 | 68 |  | 30 | 69.38 | 21.78 | 5.68
DVH090* | 7.5 | 2950 | 68 |  | 25 | 62.92 | 19.75 | 5.53
DVH090* | 7.5 | 2950 | 68 |  | 20 | 56.85 | 17.84 | 5.38
DVH090* | 7.5 | 2950 | 68 |  | 15 | 51.17 | 16.06 | 5.22
DVH090* | 7.5 | 2950 | 68 |  | 10 | 45.86 | 14.39 | 6.11
DVH090* | 7.5 | 2950 | 68 |  | 5 | 40.95 | 12.85 | 5.97
DVH090* | 7.5 | 2950 | 68 |  | 0 | 36.42 | 11.43 | 5.84
DVH090* | 7.5 | 2950 | 68 |  | -5 | 32.27 | 10.13 | 5.71
DVH090* | 7.5 | 2950 | 68 |  | -10 | 28.51 | 8.95 | 5.59
DVH090* | 7.5 | 2950 | 68 |  | -13 | 26.43 | 8.3 | 5.52
DVH090* | 7.5 | 2950 | 70 |  | 65 | 124.79 | 39.17 | 6.8
DVH090* | 7.5 | 2950 | 70 |  | 60 | 115.67 | 36.31 | 6.67
DVH090* | 7.5 | 2950 | 70 |  | 55 | 106.94 | 33.57 | 6.54
DVH090* | 7.5 | 2950 | 70 |  | 50 | 98.59 | 30.94 | 6.4
DVH090* | 7.5 | 2950 | 70 |  | 45 | 90.62 | 28.44 | 6.26
DVH090* | 7.5 | 2950 | 70 |  | 40 | 83.03 | 26.06 | 6.11
DVH090* | 7.5 | 2950 | 70 |  | 35 | 75.83 | 23.8 | 5.96
DVH090* | 7.5 | 2950 | 70 |  | 30 | 69 | 21.66 | 5.81
DVH090* | 7.5 | 2950 | 70 |  | 25 | 62.56 | 19.64 | 5.65
DVH090* | 7.5 | 2950 | 70 |  | 20 | 56.5 | 17.73 | 5.49
DVH090* | 7.5 | 2950 | 70 |  | 15 | 50.82 | 15.95 | 5.33
DVH090* | 7.5 | 2950 | 70 |  | 10 | 45.53 | 14.29 | 6.22
DVH090* | 7.5 | 2950 | 70 |  | 5 | 40.61 | 12.75 | 6.07
DVH090* | 7.5 | 2950 | 70 |  | 0 | 36.08 | 11.32 | 5.94
DVH090* | 7.5 | 2950 | 70 |  | -5 | 31.93 | 10.02 | 5.8
DVH090* | 7.5 | 2950 | 70 |  | -10 | 28.16 | 8.84 | 5.68
DVH090* | 7.5 | 2950 | 70 |  | -13 | 26.09 | 8.19 | 5.6
DVH090* | 7.5 | 2950 | 72 |  | 65 | 124.22 | 38.99 | 6.98
DVH090* | 7.5 | 2950 | 72 |  | 60 | 115.14 | 36.14 | 6.84
DVH090* | 7.5 | 2950 | 72 |  | 55 | 106.43 | 33.41 | 6.7
DVH090* | 7.5 | 2950 | 72 |  | 50 | 98.11 | 30.79 | 6.55
DVH090* | 7.5 | 2950 | 72 |  | 45 | 90.16 | 28.3 | 6.41
DVH090* | 7.5 | 2950 | 72 |  | 40 | 82.59 | 25.92 | 6.25
DVH090* | 7.5 | 2950 | 72 |  | 35 | 75.41 | 23.67 | 6.1
DVH090* | 7.5 | 2950 | 72 |  | 30 | 68.6 | 21.53 | 5.94
DVH090* | 7.5 | 2950 | 72 |  | 25 | 62.17 | 19.51 | 5.78
DVH090* | 7.5 | 2950 | 72 |  | 20 | 56.12 | 17.61 | 5.61
DVH090* | 7.5 | 2950 | 72 |  | 15 | 50.46 | 15.84 | 5.45
DVH090* | 7.5 | 2950 | 72 |  | 10 | 45.17 | 14.18 | 6.33
DVH090* | 7.5 | 2950 | 72 |  | 5 | 40.26 | 12.64 | 6.18
DVH090* | 7.5 | 2950 | 72 |  | 0 | 35.73 | 11.21 | 6.04
DVH090* | 7.5 | 2950 | 72 |  | -5 | 31.58 | 9.91 | 5.9
DVH090* | 7.5 | 2950 | 72 |  | -10 | 27.81 | 8.73 | 5.77
DVH090* | 7.5 | 2950 | 72 |  | -13 | 25.73 | 8.08 | 5.69
DVH090* | 7.5 | 2950 | 75 |  | 65 | 123.37 | 38.72 | 7.25
DVH090* | 7.5 | 2950 | 75 |  | 60 | 114.34 | 35.89 | 7.1
DVH090* | 7.5 | 2950 | 75 |  | 55 | 105.67 | 33.17 | 6.95
DVH090* | 7.5 | 2950 | 75 |  | 50 | 97.39 | 30.57 | 6.79
DVH090* | 7.5 | 2950 | 75 |  | 45 | 89.47 | 28.08 | 6.63
DVH090* | 7.5 | 2950 | 75 |  | 40 | 81.94 | 25.72 | 6.47
DVH090* | 7.5 | 2950 | 75 |  | 35 | 74.78 | 23.47 | 6.3
DVH090* | 7.5 | 2950 | 75 |  | 30 | 68 | 21.34 | 6.14
DVH090* | 7.5 | 2950 | 75 |  | 25 | 61.59 | 19.33 | 5.97
DVH090* | 7.5 | 2950 | 75 |  | 20 | 55.56 | 17.44 | 5.79
DVH090* | 7.5 | 2950 | 75 |  | 15 | 49.91 | 15.67 | 5.62
DVH090* | 7.5 | 2950 | 75 |  | 10 | 44.63 | 14.01 | 6.5
DVH090* | 7.5 | 2950 | 75 |  | 5 | 39.72 | 12.47 | 6.34
DVH090* | 7.5 | 2950 | 75 |  | 0 | 35.2 | 11.05 | 6.19
DVH090* | 7.5 | 2950 | 75 |  | -5 | 31.05 | 9.75 | 6.04
DVH090* | 7.5 | 2950 | 75 |  | -10 | 27.27 | 8.56 | 5.91
DVH090* | 7.5 | 2950 | 75 |  | -13 | 25.19 | 7.91 | 5.83
DVH090* | 7.5 | 3350 | 61 |  | 65 | 127.4 | 35.21 | 5.77
DVH090* | 7.5 | 3350 | 61 |  | 60 | 118.13 | 32.65 | 5.67
DVH090* | 7.5 | 3350 | 61 |  | 55 | 109.25 | 30.2 | 5.57
DVH090* | 7.5 | 3350 | 61 |  | 50 | 100.77 | 27.85 | 5.47
DVH090* | 7.5 | 3350 | 61 |  | 45 | 92.68 | 25.62 | 5.36
DVH090* | 7.5 | 3350 | 61 |  | 40 | 84.98 | 23.49 | 5.25
DVH090* | 7.5 | 3350 | 61 |  | 35 | 77.68 | 21.47 | 5.14
DVH090* | 7.5 | 3350 | 61 |  | 30 | 70.78 | 19.56 | 5.02
DVH090* | 7.5 | 3350 | 61 |  | 25 | 64.27 | 17.76 | 4.9
DVH090* | 7.5 | 3350 | 61 |  | 20 | 58.15 | 16.07 | 4.77
DVH090* | 7.5 | 3350 | 61 |  | 15 | 52.43 | 14.49 | 4.64
DVH090* | 7.5 | 3350 | 61 |  | 10 | 47.1 | 13.02 | 5.51
DVH090* | 7.5 | 3350 | 61 |  | 5 | 42.17 | 11.66 | 5.39
DVH090* | 7.5 | 3350 | 61 |  | 0 | 37.63 | 10.4 | 5.28
DVH090* | 7.5 | 3350 | 61 |  | -5 | 33.49 | 9.26 | 5.17
DVH090* | 7.5 | 3350 | 61 |  | -10 | 29.74 | 8.22 | 5.07
DVH090* | 7.5 | 3350 | 61 |  | -13 | 27.68 | 7.65 | 5.01
DVH090* | 7.5 | 3350 | 65 |  | 65 | 126.31 | 34.91 | 6.11
DVH090* | 7.5 | 3350 | 65 |  | 60 | 117.1 | 32.37 | 6
DVH090* | 7.5 | 3350 | 65 |  | 55 | 108.28 | 29.93 | 5.89
DVH090* | 7.5 | 3350 | 65 |  | 50 | 99.85 | 27.6 | 5.77
DVH090* | 7.5 | 3350 | 65 |  | 45 | 91.81 | 25.38 | 5.65
DVH090* | 7.5 | 3350 | 65 |  | 40 | 84.16 | 23.26 | 5.53
DVH090* | 7.5 | 3350 | 65 |  | 35 | 76.9 | 21.25 | 5.4
DVH090* | 7.5 | 3350 | 65 |  | 30 | 70.03 | 19.36 | 5.27
DVH090* | 7.5 | 3350 | 65 |  | 25 | 63.54 | 17.56 | 5.13
DVH090* | 7.5 | 3350 | 65 |  | 20 | 57.45 | 15.88 | 5
DVH090* | 7.5 | 3350 | 65 |  | 15 | 51.74 | 14.3 | 4.85
DVH090* | 7.5 | 3350 | 65 |  | 10 | 46.43 | 12.83 | 5.72
DVH090* | 7.5 | 3350 | 65 |  | 5 | 41.5 | 11.47 | 5.59
DVH090* | 7.5 | 3350 | 65 |  | 0 | 36.96 | 10.22 | 5.47
DVH090* | 7.5 | 3350 | 65 |  | -5 | 32.81 | 9.07 | 5.35
DVH090* | 7.5 | 3350 | 65 |  | -10 | 29.05 | 8.03 | 5.24
DVH090* | 7.5 | 3350 | 65 |  | -13 | 26.99 | 7.46 | 5.18
DVH090* | 7.5 | 3350 | 68 |  | 65 | 125.49 | 34.68 | 6.37
DVH090* | 7.5 | 3350 | 68 |  | 60 | 116.33 | 32.15 | 6.25
DVH090* | 7.5 | 3350 | 68 |  | 55 | 107.55 | 29.73 | 6.12
DVH090* | 7.5 | 3350 | 68 |  | 50 | 99.17 | 27.41 | 6
DVH090* | 7.5 | 3350 | 68 |  | 45 | 91.16 | 25.2 | 5.87
DVH090* | 7.5 | 3350 | 68 |  | 40 | 83.54 | 23.09 | 5.73
DVH090* | 7.5 | 3350 | 68 |  | 35 | 76.31 | 21.09 | 5.6
DVH090* | 7.5 | 3350 | 68 |  | 30 | 69.46 | 19.2 | 5.46
DVH090* | 7.5 | 3350 | 68 |  | 25 | 63 | 17.41 | 5.31
DVH090* | 7.5 | 3350 | 68 |  | 20 | 56.92 | 15.73 | 5.17
DVH090* | 7.5 | 3350 | 68 |  | 15 | 51.23 | 14.16 | 5.01
DVH090* | 7.5 | 3350 | 68 |  | 10 | 45.92 | 12.69 | 5.87
DVH090* | 7.5 | 3350 | 68 |  | 5 | 41 | 11.33 | 5.74
DVH090* | 7.5 | 3350 | 68 |  | 0 | 36.46 | 10.08 | 5.61
DVH090* | 7.5 | 3350 | 68 |  | -5 | 32.31 | 8.93 | 5.48
DVH090* | 7.5 | 3350 | 68 |  | -10 | 28.54 | 7.89 | 5.37
DVH090* | 7.5 | 3350 | 68 |  | -13 | 26.47 | 7.32 | 5.3
DVH090* | 7.5 | 3350 | 70 |  | 65 | 124.94 | 34.53 | 6.54
DVH090* | 7.5 | 3350 | 70 |  | 60 | 115.81 | 32.01 | 6.41
DVH090* | 7.5 | 3350 | 70 |  | 55 | 107.07 | 29.59 | 6.28
DVH090* | 7.5 | 3350 | 70 |  | 50 | 98.71 | 27.28 | 6.15
DVH090* | 7.5 | 3350 | 70 |  | 45 | 90.73 | 25.08 | 6.01
DVH090* | 7.5 | 3350 | 70 |  | 40 | 83.13 | 22.98 | 5.87
DVH090* | 7.5 | 3350 | 70 |  | 35 | 75.92 | 20.98 | 5.73
DVH090* | 7.5 | 3350 | 70 |  | 30 | 69.09 | 19.1 | 5.58
DVH090* | 7.5 | 3350 | 70 |  | 25 | 62.64 | 17.31 | 5.43
DVH090* | 7.5 | 3350 | 70 |  | 20 | 56.57 | 15.64 | 5.28
DVH090* | 7.5 | 3350 | 70 |  | 15 | 50.88 | 14.06 | 5.12
DVH090* | 7.5 | 3350 | 70 |  | 10 | 45.58 | 12.6 | 5.98
DVH090* | 7.5 | 3350 | 70 |  | 5 | 40.66 | 11.24 | 5.84
DVH090* | 7.5 | 3350 | 70 |  | 0 | 36.13 | 9.99 | 5.7
DVH090* | 7.5 | 3350 | 70 |  | -5 | 31.97 | 8.84 | 5.57
DVH090* | 7.5 | 3350 | 70 |  | -10 | 28.2 | 7.79 | 5.45
DVH090* | 7.5 | 3350 | 70 |  | -13 | 26.12 | 7.22 | 5.38
DVH090* | 7.5 | 3350 | 72 |  | 65 | 124.37 | 34.38 | 6.71
DVH090* | 7.5 | 3350 | 72 |  | 60 | 115.28 | 31.86 | 6.57
DVH090* | 7.5 | 3350 | 72 |  | 55 | 106.56 | 29.45 | 6.44
DVH090* | 7.5 | 3350 | 72 |  | 50 | 98.23 | 27.15 | 6.3
DVH090* | 7.5 | 3350 | 72 |  | 45 | 90.27 | 24.95 | 6.15
DVH090* | 7.5 | 3350 | 72 |  | 40 | 82.69 | 22.86 | 6.01
DVH090* | 7.5 | 3350 | 72 |  | 35 | 75.5 | 20.87 | 5.86
DVH090* | 7.5 | 3350 | 72 |  | 30 | 68.68 | 18.98 | 5.71
DVH090* | 7.5 | 3350 | 72 |  | 25 | 62.25 | 17.21 | 5.55
DVH090* | 7.5 | 3350 | 72 |  | 20 | 56.19 | 15.53 | 5.39
DVH090* | 7.5 | 3350 | 72 |  | 15 | 50.52 | 13.96 | 5.23
DVH090* | 7.5 | 3350 | 72 |  | 10 | 45.22 | 12.5 | 6.08
DVH090* | 7.5 | 3350 | 72 |  | 5 | 40.31 | 11.14 | 5.94
DVH090* | 7.5 | 3350 | 72 |  | 0 | 35.77 | 9.89 | 5.8
DVH090* | 7.5 | 3350 | 72 |  | -5 | 31.62 | 8.74 | 5.67
DVH090* | 7.5 | 3350 | 72 |  | -10 | 27.84 | 7.69 | 5.54
DVH090* | 7.5 | 3350 | 72 |  | -13 | 25.76 | 7.12 | 5.47
DVH090* | 7.5 | 3350 | 75 |  | 65 | 123.52 | 34.14 | 6.97
DVH090* | 7.5 | 3350 | 75 |  | 60 | 114.47 | 31.64 | 6.82
DVH090* | 7.5 | 3350 | 75 |  | 55 | 105.8 | 29.24 | 6.67
DVH090* | 7.5 | 3350 | 75 |  | 50 | 97.5 | 26.95 | 6.52
DVH090* | 7.5 | 3350 | 75 |  | 45 | 89.58 | 24.76 | 6.37
DVH090* | 7.5 | 3350 | 75 |  | 40 | 82.04 | 22.68 | 6.21
DVH090* | 7.5 | 3350 | 75 |  | 35 | 74.87 | 20.69 | 6.06
DVH090* | 7.5 | 3350 | 75 |  | 30 | 68.08 | 18.82 | 5.89
DVH090* | 7.5 | 3350 | 75 |  | 25 | 61.67 | 17.05 | 5.73
DVH090* | 7.5 | 3350 | 75 |  | 20 | 55.63 | 15.38 | 5.57
DVH090* | 7.5 | 3350 | 75 |  | 15 | 49.97 | 13.81 | 5.4
DVH090* | 7.5 | 3350 | 75 |  | 10 | 44.68 | 12.35 | 6.25
DVH090* | 7.5 | 3350 | 75 |  | 5 | 39.77 | 10.99 | 6.09
DVH090* | 7.5 | 3350 | 75 |  | 0 | 35.24 | 9.74 | 5.95
DVH090* | 7.5 | 3350 | 75 |  | -5 | 31.08 | 8.59 | 5.81
DVH090* | 7.5 | 3350 | 75 |  | -10 | 27.31 | 7.55 | 5.68
DVH090* | 7.5 | 3350 | 75 |  | -13 | 25.22 | 6.97 | 5.6
DVH102* | 8.5 | 2700 | 61 |  | 65 | 142.44 | 48.85 | 7.17
DVH102* | 8.5 | 2700 | 61 |  | 60 | 132.12 | 45.31 | 7.04
DVH102* | 8.5 | 2700 | 61 |  | 55 | 122.23 | 41.92 | 6.9
DVH102* | 8.5 | 2700 | 61 |  | 50 | 112.76 | 38.67 | 6.76
DVH102* | 8.5 | 2700 | 61 |  | 45 | 103.73 | 35.57 | 6.61
DVH102* | 8.5 | 2700 | 61 |  | 40 | 95.13 | 32.62 | 6.46
DVH102* | 8.5 | 2700 | 61 |  | 35 | 86.96 | 29.82 | 6.31
DVH102* | 8.5 | 2700 | 61 |  | 30 | 79.22 | 27.17 | 6.16
DVH102* | 8.5 | 2700 | 61 |  | 25 | 71.91 | 24.66 | 6
DVH102* | 8.5 | 2700 | 61 |  | 20 | 65.03 | 22.3 | 5.84
DVH102* | 8.5 | 2700 | 61 |  | 15 | 58.58 | 20.09 | 5.68
DVH102* | 8.5 | 2700 | 61 |  | 10 | 52.56 | 18.02 | 6.29
DVH102* | 8.5 | 2700 | 61 |  | 5 | 46.97 | 16.11 | 6.15
DVH102* | 8.5 | 2700 | 61 |  | 0 | 41.81 | 14.34 | 6.02
DVH102* | 8.5 | 2700 | 61 |  | -5 | 37.08 | 12.72 | 5.89
DVH102* | 8.5 | 2700 | 61 |  | -10 | 32.78 | 11.24 | 5.77
DVH102* | 8.5 | 2700 | 61 |  | -13 | 30.41 | 10.43 | 5.7
DVH102* | 8.5 | 2700 | 65 |  | 65 | 141.24 | 48.44 | 7.56
DVH102* | 8.5 | 2700 | 65 |  | 60 | 130.99 | 44.92 | 7.4
DVH102* | 8.5 | 2700 | 65 |  | 55 | 121.16 | 41.55 | 7.25
DVH102* | 8.5 | 2700 | 65 |  | 50 | 111.76 | 38.33 | 7.09
DVH102* | 8.5 | 2700 | 65 |  | 45 | 102.78 | 35.25 | 6.94
DVH102* | 8.5 | 2700 | 65 |  | 40 | 94.22 | 32.31 | 6.77
DVH102* | 8.5 | 2700 | 65 |  | 35 | 86.09 | 29.52 | 6.61
DVH102* | 8.5 | 2700 | 65 |  | 30 | 78.39 | 26.88 | 6.44
DVH102* | 8.5 | 2700 | 65 |  | 25 | 71.11 | 24.39 | 6.27
DVH102* | 8.5 | 2700 | 65 |  | 20 | 64.25 | 22.03 | 6.1
DVH102* | 8.5 | 2700 | 65 |  | 15 | 57.82 | 19.83 | 5.92
DVH102* | 8.5 | 2700 | 65 |  | 10 | 51.81 | 17.77 | 6.52
DVH102* | 8.5 | 2700 | 65 |  | 5 | 46.23 | 15.85 | 6.37
DVH102* | 8.5 | 2700 | 65 |  | 0 | 41.07 | 14.08 | 6.22
DVH102* | 8.5 | 2700 | 65 |  | -5 | 36.34 | 12.46 | 6.09
DVH102* | 8.5 | 2700 | 65 |  | -10 | 32.03 | 10.98 | 5.96
DVH102* | 8.5 | 2700 | 65 |  | -13 | 29.64 | 10.16 | 5.89
DVH102* | 8.5 | 2700 | 68 |  | 65 | 140.33 | 48.12 | 7.84
DVH102* | 8.5 | 2700 | 68 |  | 60 | 130.13 | 44.63 | 7.68
DVH102* | 8.5 | 2700 | 68 |  | 55 | 120.36 | 41.28 | 7.52
DVH102* | 8.5 | 2700 | 68 |  | 50 | 111 | 38.07 | 7.35
DVH102* | 8.5 | 2700 | 68 |  | 45 | 102.06 | 35 | 7.18
DVH102* | 8.5 | 2700 | 68 |  | 40 | 93.54 | 32.08 | 7.01
DVH102* | 8.5 | 2700 | 68 |  | 35 | 85.45 | 29.3 | 6.83
DVH102* | 8.5 | 2700 | 68 |  | 30 | 77.77 | 26.67 | 6.65
DVH102* | 8.5 | 2700 | 68 |  | 25 | 70.51 | 24.18 | 6.47
DVH102* | 8.5 | 2700 | 68 |  | 20 | 63.67 | 21.83 | 6.29
DVH102* | 8.5 | 2700 | 68 |  | 15 | 57.25 | 19.63 | 6.1
DVH102* | 8.5 | 2700 | 68 |  | 10 | 51.25 | 17.58 | 6.7
DVH102* | 8.5 | 2700 | 68 |  | 5 | 45.68 | 15.67 | 6.53
DVH102* | 8.5 | 2700 | 68 |  | 0 | 40.52 | 13.9 | 6.38
DVH102* | 8.5 | 2700 | 68 |  | -5 | 35.78 | 12.27 | 6.24
DVH102* | 8.5 | 2700 | 68 |  | -10 | 31.46 | 10.79 | 6.1
DVH102* | 8.5 | 2700 | 68 |  | -13 | 29.07 | 9.97 | 6.02
DVH102* | 8.5 | 2700 | 70 |  | 65 | 139.73 | 47.92 | 8.03
DVH102* | 8.5 | 2700 | 70 |  | 60 | 129.57 | 44.43 | 7.86
DVH102* | 8.5 | 2700 | 70 |  | 55 | 119.82 | 41.09 | 7.69
DVH102* | 8.5 | 2700 | 70 |  | 50 | 110.5 | 37.89 | 7.52
DVH102* | 8.5 | 2700 | 70 |  | 45 | 101.59 | 34.84 | 7.34
DVH102* | 8.5 | 2700 | 70 |  | 40 | 93.09 | 31.92 | 7.16
DVH102* | 8.5 | 2700 | 70 |  | 35 | 85.02 | 29.16 | 6.98
DVH102* | 8.5 | 2700 | 70 |  | 30 | 77.36 | 26.53 | 6.79
DVH102* | 8.5 | 2700 | 70 |  | 25 | 70.11 | 24.04 | 6.6
DVH102* | 8.5 | 2700 | 70 |  | 20 | 63.29 | 21.7 | 6.41
DVH102* | 8.5 | 2700 | 70 |  | 15 | 56.88 | 19.51 | 6.22
DVH102* | 8.5 | 2700 | 70 |  | 10 | 50.88 | 17.45 | 6.81
DVH102* | 8.5 | 2700 | 70 |  | 5 | 45.31 | 15.54 | 6.64
DVH102* | 8.5 | 2700 | 70 |  | 0 | 40.15 | 13.77 | 6.48
DVH102* | 8.5 | 2700 | 70 |  | -5 | 35.4 | 12.14 | 6.33
DVH102* | 8.5 | 2700 | 70 |  | -10 | 31.08 | 10.66 | 6.19
DVH102* | 8.5 | 2700 | 70 |  | -13 | 28.68 | 9.84 | 6.11
DVH102* | 8.5 | 2700 | 72 |  | 60 | 128.97 | 44.23 | 8.05
DVH102* | 8.5 | 2700 | 72 |  | 55 | 119.26 | 40.9 | 7.87
DVH102* | 8.5 | 2700 | 72 |  | 50 | 109.96 | 37.71 | 7.69
DVH102* | 8.5 | 2700 | 72 |  | 45 | 101.08 | 34.66 | 7.5
DVH102* | 8.5 | 2700 | 72 |  | 40 | 92.61 | 31.76 | 7.31
DVH102* | 8.5 | 2700 | 72 |  | 35 | 84.55 | 29 | 7.12
DVH102* | 8.5 | 2700 | 72 |  | 30 | 76.91 | 26.38 | 6.93
DVH102* | 8.5 | 2700 | 72 |  | 25 | 69.68 | 23.9 | 6.74
DVH102* | 8.5 | 2700 | 72 |  | 20 | 62.87 | 21.56 | 6.54
DVH102* | 8.5 | 2700 | 72 |  | 15 | 56.47 | 19.37 | 6.34
DVH102* | 8.5 | 2700 | 72 |  | 10 | 50.49 | 17.31 | 6.93
DVH102* | 8.5 | 2700 | 72 |  | 5 | 44.92 | 15.4 | 6.76
DVH102* | 8.5 | 2700 | 72 |  | 0 | 39.76 | 13.64 | 6.59
DVH102* | 8.5 | 2700 | 72 |  | -5 | 35.01 | 12.01 | 6.44
DVH102* | 8.5 | 2700 | 72 |  | -10 | 30.68 | 10.52 | 6.29
DVH102* | 8.5 | 2700 | 72 |  | -13 | 28.29 | 9.7 | 6.21
DVH102* | 8.5 | 2700 | 75 |  | 55 | 118.4 | 40.6 | 8.13
DVH102* | 8.5 | 2700 | 75 |  | 50 | 109.15 | 37.43 | 7.94
DVH102* | 8.5 | 2700 | 75 |  | 45 | 100.31 | 34.4 | 7.74
DVH102* | 8.5 | 2700 | 75 |  | 40 | 91.88 | 31.51 | 7.54
DVH102* | 8.5 | 2700 | 75 |  | 35 | 83.86 | 28.76 | 7.34
DVH102* | 8.5 | 2700 | 75 |  | 30 | 76.25 | 26.15 | 7.14
DVH102* | 8.5 | 2700 | 75 |  | 25 | 69.04 | 23.68 | 6.94
DVH102* | 8.5 | 2700 | 75 |  | 20 | 62.25 | 21.35 | 6.73
DVH102* | 8.5 | 2700 | 75 |  | 15 | 55.87 | 19.16 | 6.52
DVH102* | 8.5 | 2700 | 75 |  | 10 | 49.89 | 17.11 | 7.11
DVH102* | 8.5 | 2700 | 75 |  | 5 | 44.33 | 15.2 | 6.93
DVH102* | 8.5 | 2700 | 75 |  | 0 | 39.17 | 13.43 | 6.75
DVH102* | 8.5 | 2700 | 75 |  | -5 | 34.43 | 11.81 | 6.59
DVH102* | 8.5 | 2700 | 75 |  | -10 | 30.09 | 10.32 | 6.43
DVH102* | 8.5 | 2700 | 75 |  | -13 | 27.69 | 9.5 | 6.35
DVH102* | 8.5 | 3100 | 61 |  | 65 | 143.85 | 42.97 | 6.93
DVH102* | 8.5 | 3100 | 61 |  | 60 | 133.42 | 39.85 | 6.8
DVH102* | 8.5 | 3100 | 61 |  | 55 | 123.43 | 36.87 | 6.66
DVH102* | 8.5 | 3100 | 61 |  | 50 | 113.87 | 34.01 | 6.53
DVH102* | 8.5 | 3100 | 61 |  | 45 | 104.75 | 31.29 | 6.39
DVH102* | 8.5 | 3100 | 61 |  | 40 | 96.07 | 28.69 | 6.24
DVH102* | 8.5 | 3100 | 61 |  | 35 | 87.81 | 26.23 | 6.1
DVH102* | 8.5 | 3100 | 61 |  | 30 | 80 | 23.89 | 5.95
DVH102* | 8.5 | 3100 | 61 |  | 25 | 72.61 | 21.69 | 5.8
DVH102* | 8.5 | 3100 | 61 |  | 20 | 65.67 | 19.61 | 5.65
DVH102* | 8.5 | 3100 | 61 |  | 15 | 59.15 | 17.67 | 5.49
DVH102* | 8.5 | 3100 | 61 |  | 10 | 53.07 | 15.85 | 6.08
DVH102* | 8.5 | 3100 | 61 |  | 5 | 47.43 | 14.17 | 5.94
DVH102* | 8.5 | 3100 | 61 |  | 0 | 42.22 | 12.61 | 5.81
DVH102* | 8.5 | 3100 | 61 |  | -5 | 37.45 | 11.19 | 5.69
DVH102* | 8.5 | 3100 | 61 |  | -10 | 33.11 | 9.89 | 5.58
DVH102* | 8.5 | 3100 | 61 |  | -13 | 30.71 | 9.17 | 5.51
DVH102* | 8.5 | 3100 | 65 |  | 65 | 142.63 | 42.6 | 7.3
DVH102* | 8.5 | 3100 | 65 |  | 60 | 132.27 | 39.51 | 7.15
DVH102* | 8.5 | 3100 | 65 |  | 55 | 122.35 | 36.54 | 7
DVH102* | 8.5 | 3100 | 65 |  | 50 | 112.86 | 33.71 | 6.85
DVH102* | 8.5 | 3100 | 65 |  | 45 | 103.79 | 31 | 6.7
DVH102* | 8.5 | 3100 | 65 |  | 40 | 95.15 | 28.42 | 6.54
DVH102* | 8.5 | 3100 | 65 |  | 35 | 86.94 | 25.97 | 6.38
DVH102* | 8.5 | 3100 | 65 |  | 30 | 79.16 | 23.64 | 6.22
DVH102* | 8.5 | 3100 | 65 |  | 25 | 71.81 | 21.45 | 6.06
DVH102* | 8.5 | 3100 | 65 |  | 20 | 64.88 | 19.38 | 5.89
DVH102* | 8.5 | 3100 | 65 |  | 15 | 58.39 | 17.44 | 5.72
DVH102* | 8.5 | 3100 | 65 |  | 10 | 52.32 | 15.63 | 6.3
DVH102* | 8.5 | 3100 | 65 |  | 5 | 46.68 | 13.94 | 6.15
DVH102* | 8.5 | 3100 | 65 |  | 0 | 41.47 | 12.39 | 6.01
DVH102* | 8.5 | 3100 | 65 |  | -5 | 36.69 | 10.96 | 5.88
DVH102* | 8.5 | 3100 | 65 |  | -10 | 32.34 | 9.66 | 5.76
DVH102* | 8.5 | 3100 | 65 |  | -13 | 29.94 | 8.94 | 5.69
DVH102* | 8.5 | 3100 | 68 |  | 65 | 141.71 | 42.33 | 7.58
DVH102* | 8.5 | 3100 | 68 |  | 60 | 131.41 | 39.25 | 7.42
DVH102* | 8.5 | 3100 | 68 |  | 55 | 121.54 | 36.3 | 7.26
DVH102* | 8.5 | 3100 | 68 |  | 50 | 112.09 | 33.48 | 7.1
DVH102* | 8.5 | 3100 | 68 |  | 45 | 103.07 | 30.79 | 6.93
DVH102* | 8.5 | 3100 | 68 |  | 40 | 94.47 | 28.22 | 6.77
DVH102* | 8.5 | 3100 | 68 |  | 35 | 86.29 | 25.77 | 6.6
DVH102* | 8.5 | 3100 | 68 |  | 30 | 78.53 | 23.46 | 6.43
DVH102* | 8.5 | 3100 | 68 |  | 25 | 71.2 | 21.27 | 6.25
DVH102* | 8.5 | 3100 | 68 |  | 20 | 64.3 | 19.21 | 6.07
DVH102* | 8.5 | 3100 | 68 |  | 15 | 57.82 | 17.27 | 5.89
DVH102* | 8.5 | 3100 | 68 |  | 10 | 51.76 | 15.46 | 6.47
DVH102* | 8.5 | 3100 | 68 |  | 5 | 46.13 | 13.78 | 6.31
DVH102* | 8.5 | 3100 | 68 |  | 0 | 40.92 | 12.22 | 6.16
DVH102* | 8.5 | 3100 | 68 |  | -5 | 36.13 | 10.79 | 6.02
DVH102* | 8.5 | 3100 | 68 |  | -10 | 31.77 | 9.49 | 5.89
DVH102* | 8.5 | 3100 | 68 |  | -13 | 29.35 | 8.77 | 5.82
DVH102* | 8.5 | 3100 | 70 |  | 65 | 141.1 | 42.14 | 7.76
DVH102* | 8.5 | 3100 | 70 |  | 60 | 130.84 | 39.08 | 7.6
DVH102* | 8.5 | 3100 | 70 |  | 55 | 121 | 36.14 | 7.43
DVH102* | 8.5 | 3100 | 70 |  | 50 | 111.58 | 33.33 | 7.26
DVH102* | 8.5 | 3100 | 70 |  | 45 | 102.58 | 30.64 | 7.09
DVH102* | 8.5 | 3100 | 70 |  | 40 | 94.01 | 28.08 | 6.92
DVH102* | 8.5 | 3100 | 70 |  | 35 | 85.85 | 25.64 | 6.74
DVH102* | 8.5 | 3100 | 70 |  | 30 | 78.12 | 23.33 | 6.56
DVH102* | 8.5 | 3100 | 70 |  | 25 | 70.8 | 21.15 | 6.38
DVH102* | 8.5 | 3100 | 70 |  | 20 | 63.91 | 19.09 | 6.2
DVH102* | 8.5 | 3100 | 70 |  | 15 | 57.44 | 17.16 | 6.01
DVH102* | 8.5 | 3100 | 70 |  | 10 | 51.38 | 15.35 | 6.58
DVH102* | 8.5 | 3100 | 70 |  | 5 | 45.75 | 13.66 | 6.42
DVH102* | 8.5 | 3100 | 70 |  | 0 | 40.54 | 12.11 | 6.26
DVH102* | 8.5 | 3100 | 70 |  | -5 | 35.75 | 10.68 | 6.12
DVH102* | 8.5 | 3100 | 70 |  | -10 | 31.38 | 9.37 | 5.98
DVH102* | 8.5 | 3100 | 70 |  | -13 | 28.97 | 8.65 | 5.91
DVH102* | 8.5 | 3100 | 72 |  | 65 | 140.46 | 41.95 | 7.95
DVH102* | 8.5 | 3100 | 72 |  | 60 | 130.23 | 38.9 | 7.78
DVH102* | 8.5 | 3100 | 72 |  | 55 | 120.43 | 35.97 | 7.6
DVH102* | 8.5 | 3100 | 72 |  | 50 | 111.04 | 33.17 | 7.43
DVH102* | 8.5 | 3100 | 72 |  | 45 | 102.07 | 30.49 | 7.25
DVH102* | 8.5 | 3100 | 72 |  | 40 | 93.52 | 27.93 | 7.07
DVH102* | 8.5 | 3100 | 72 |  | 35 | 85.38 | 25.5 | 6.88
DVH102* | 8.5 | 3100 | 72 |  | 30 | 77.67 | 23.2 | 6.7
DVH102* | 8.5 | 3100 | 72 |  | 25 | 70.37 | 21.02 | 6.51
DVH102* | 8.5 | 3100 | 72 |  | 20 | 63.49 | 18.96 | 6.32
DVH102* | 8.5 | 3100 | 72 |  | 15 | 57.03 | 17.03 | 6.13
DVH102* | 8.5 | 3100 | 72 |  | 10 | 50.98 | 15.23 | 6.7
DVH102* | 8.5 | 3100 | 72 |  | 5 | 45.36 | 13.55 | 6.53
DVH102* | 8.5 | 3100 | 72 |  | 0 | 40.15 | 11.99 | 6.37
DVH102* | 8.5 | 3100 | 72 |  | -5 | 35.36 | 10.56 | 6.22
DVH102* | 8.5 | 3100 | 72 |  | -10 | 30.99 | 9.26 | 6.08
DVH102* | 8.5 | 3100 | 72 |  | -13 | 28.56 | 8.53 | 6
DVH102* | 8.5 | 3100 | 75 |  | 60 | 129.32 | 38.63 | 8.04
DVH102* | 8.5 | 3100 | 75 |  | 55 | 119.57 | 35.71 | 7.86
DVH102* | 8.5 | 3100 | 75 |  | 50 | 110.23 | 32.92 | 7.67
DVH102* | 8.5 | 3100 | 75 |  | 45 | 101.3 | 30.26 | 7.48
DVH102* | 8.5 | 3100 | 75 |  | 40 | 92.78 | 27.71 | 7.29
DVH102* | 8.5 | 3100 | 75 |  | 35 | 84.68 | 25.29 | 7.1
DVH102* | 8.5 | 3100 | 75 |  | 30 | 77 | 23 | 6.9
DVH102* | 8.5 | 3100 | 75 |  | 25 | 69.72 | 20.82 | 6.7
DVH102* | 8.5 | 3100 | 75 |  | 20 | 62.86 | 18.78 | 6.5
DVH102* | 8.5 | 3100 | 75 |  | 15 | 56.42 | 16.85 | 6.3
DVH102* | 8.5 | 3100 | 75 |  | 10 | 50.38 | 15.05 | 6.87
DVH102* | 8.5 | 3100 | 75 |  | 5 | 44.76 | 13.37 | 6.69
DVH102* | 8.5 | 3100 | 75 |  | 0 | 39.56 | 11.82 | 6.52
DVH102* | 8.5 | 3100 | 75 |  | -5 | 34.77 | 10.39 | 6.36
DVH102* | 8.5 | 3100 | 75 |  | -10 | 30.39 | 9.08 | 6.22
DVH102* | 8.5 | 3100 | 75 |  | -13 | 27.96 | 8.35 | 6.13
DVH102* | 8.5 | 3500 | 61 |  | 65 | 144.01 | 38.1 | 6.68
DVH102* | 8.5 | 3500 | 61 |  | 60 | 133.57 | 35.34 | 6.55
DVH102* | 8.5 | 3500 | 61 |  | 55 | 123.57 | 32.69 | 6.42
DVH102* | 8.5 | 3500 | 61 |  | 50 | 114.01 | 30.16 | 6.29
DVH102* | 8.5 | 3500 | 61 |  | 45 | 104.87 | 27.74 | 6.15
DVH102* | 8.5 | 3500 | 61 |  | 40 | 96.18 | 25.44 | 6.02
DVH102* | 8.5 | 3500 | 61 |  | 35 | 87.92 | 23.26 | 5.88
DVH102* | 8.5 | 3500 | 61 |  | 30 | 80.09 | 21.19 | 5.73
DVH102* | 8.5 | 3500 | 61 |  | 25 | 72.7 | 19.23 | 5.59
DVH102* | 8.5 | 3500 | 61 |  | 20 | 65.74 | 17.39 | 5.44
DVH102* | 8.5 | 3500 | 61 |  | 15 | 59.22 | 15.67 | 5.29
DVH102* | 8.5 | 3500 | 61 |  | 10 | 53.14 | 14.06 | 5.85
DVH102* | 8.5 | 3500 | 61 |  | 5 | 47.48 | 12.56 | 5.72
DVH102* | 8.5 | 3500 | 61 |  | 0 | 42.27 | 11.18 | 5.6
DVH102* | 8.5 | 3500 | 61 |  | -5 | 37.49 | 9.92 | 5.48
DVH102* | 8.5 | 3500 | 61 |  | -10 | 33.15 | 8.77 | 5.37
DVH102* | 8.5 | 3500 | 61 |  | -13 | 30.75 | 8.13 | 5.31
DVH102* | 8.5 | 3500 | 65 |  | 65 | 142.79 | 37.78 | 7.03
DVH102* | 8.5 | 3500 | 65 |  | 60 | 132.43 | 35.03 | 6.89
DVH102* | 8.5 | 3500 | 65 |  | 55 | 122.49 | 32.4 | 6.75
DVH102* | 8.5 | 3500 | 65 |  | 50 | 112.99 | 29.89 | 6.6
DVH102* | 8.5 | 3500 | 65 |  | 45 | 103.91 | 27.49 | 6.45
DVH102* | 8.5 | 3500 | 65 |  | 40 | 95.26 | 25.2 | 6.3
DVH102* | 8.5 | 3500 | 65 |  | 35 | 87.04 | 23.03 | 6.15
DVH102* | 8.5 | 3500 | 65 |  | 30 | 79.25 | 20.97 | 5.99
DVH102* | 8.5 | 3500 | 65 |  | 25 | 71.89 | 19.02 | 5.84
DVH102* | 8.5 | 3500 | 65 |  | 20 | 64.96 | 17.19 | 5.67
DVH102* | 8.5 | 3500 | 65 |  | 15 | 58.46 | 15.47 | 5.51
DVH102* | 8.5 | 3500 | 65 |  | 10 | 52.38 | 13.86 | 6.07
DVH102* | 8.5 | 3500 | 65 |  | 5 | 46.74 | 12.37 | 5.93
DVH102* | 8.5 | 3500 | 65 |  | 0 | 41.52 | 10.98 | 5.79
DVH102* | 8.5 | 3500 | 65 |  | -5 | 36.74 | 9.72 | 5.67
DVH102* | 8.5 | 3500 | 65 |  | -10 | 32.38 | 8.57 | 5.55
DVH102* | 8.5 | 3500 | 65 |  | -13 | 29.97 | 7.93 | 5.48
DVH102* | 8.5 | 3500 | 68 |  | 65 | 141.88 | 37.53 | 7.3
DVH102* | 8.5 | 3500 | 68 |  | 60 | 131.57 | 34.81 | 7.15
DVH102* | 8.5 | 3500 | 68 |  | 55 | 121.68 | 32.19 | 6.99
DVH102* | 8.5 | 3500 | 68 |  | 50 | 112.22 | 29.69 | 6.84
DVH102* | 8.5 | 3500 | 68 |  | 45 | 103.19 | 27.3 | 6.68
DVH102* | 8.5 | 3500 | 68 |  | 40 | 94.57 | 25.02 | 6.52
DVH102* | 8.5 | 3500 | 68 |  | 35 | 86.39 | 22.85 | 6.36
DVH102* | 8.5 | 3500 | 68 |  | 30 | 78.62 | 20.8 | 6.19
DVH102* | 8.5 | 3500 | 68 |  | 25 | 71.29 | 18.86 | 6.02
DVH102* | 8.5 | 3500 | 68 |  | 20 | 64.37 | 17.03 | 5.85
DVH102* | 8.5 | 3500 | 68 |  | 15 | 57.88 | 15.31 | 5.68
DVH102* | 8.5 | 3500 | 68 |  | 10 | 51.82 | 13.71 | 6.23
DVH102* | 8.5 | 3500 | 68 |  | 5 | 46.18 | 12.22 | 6.08
DVH102* | 8.5 | 3500 | 68 |  | 0 | 40.96 | 10.84 | 5.94
DVH102* | 8.5 | 3500 | 68 |  | -5 | 36.17 | 9.57 | 5.8
DVH102* | 8.5 | 3500 | 68 |  | -10 | 31.8 | 8.41 | 5.68
DVH102* | 8.5 | 3500 | 68 |  | -13 | 29.39 | 7.78 | 5.6
DVH102* | 8.5 | 3500 | 70 |  | 65 | 141.27 | 37.37 | 7.48
DVH102* | 8.5 | 3500 | 70 |  | 60 | 130.99 | 34.65 | 7.32
DVH102* | 8.5 | 3500 | 70 |  | 55 | 121.14 | 32.05 | 7.16
DVH102* | 8.5 | 3500 | 70 |  | 50 | 111.71 | 29.55 | 7
DVH102* | 8.5 | 3500 | 70 |  | 45 | 102.7 | 27.17 | 6.83
DVH102* | 8.5 | 3500 | 70 |  | 40 | 94.12 | 24.9 | 6.66
DVH102* | 8.5 | 3500 | 70 |  | 35 | 85.95 | 22.74 | 6.49
DVH102* | 8.5 | 3500 | 70 |  | 30 | 78.21 | 20.69 | 6.32
DVH102* | 8.5 | 3500 | 70 |  | 25 | 70.88 | 18.75 | 6.15
DVH102* | 8.5 | 3500 | 70 |  | 20 | 63.98 | 16.93 | 5.97
DVH102* | 8.5 | 3500 | 70 |  | 15 | 57.5 | 15.21 | 5.79
DVH102* | 8.5 | 3500 | 70 |  | 10 | 51.44 | 13.61 | 6.34
DVH102* | 8.5 | 3500 | 70 |  | 5 | 45.81 | 12.12 | 6.18
DVH102* | 8.5 | 3500 | 70 |  | 0 | 40.59 | 10.74 | 6.04
DVH102* | 8.5 | 3500 | 70 |  | -5 | 35.79 | 9.47 | 5.9
DVH102* | 8.5 | 3500 | 70 |  | -10 | 31.42 | 8.31 | 5.76
DVH102* | 8.5 | 3500 | 70 |  | -13 | 29 | 7.67 | 5.69
DVH102* | 8.5 | 3500 | 72 |  | 65 | 140.62 | 37.2 | 7.66
DVH102* | 8.5 | 3500 | 72 |  | 60 | 130.39 | 34.49 | 7.49
DVH102* | 8.5 | 3500 | 72 |  | 55 | 120.57 | 31.9 | 7.32
DVH102* | 8.5 | 3500 | 72 |  | 50 | 111.17 | 29.41 | 7.15
DVH102* | 8.5 | 3500 | 72 |  | 45 | 102.19 | 27.03 | 6.98
DVH102* | 8.5 | 3500 | 72 |  | 40 | 93.63 | 24.77 | 6.81
DVH102* | 8.5 | 3500 | 72 |  | 35 | 85.48 | 22.61 | 6.63
DVH102* | 8.5 | 3500 | 72 |  | 30 | 77.76 | 20.57 | 6.45
DVH102* | 8.5 | 3500 | 72 |  | 25 | 70.45 | 18.64 | 6.27
DVH102* | 8.5 | 3500 | 72 |  | 20 | 63.56 | 16.81 | 6.09
DVH102* | 8.5 | 3500 | 72 |  | 15 | 57.09 | 15.1 | 5.9
DVH102* | 8.5 | 3500 | 72 |  | 10 | 51.04 | 13.5 | 6.45
DVH102* | 8.5 | 3500 | 72 |  | 5 | 45.41 | 12.01 | 6.29
DVH102* | 8.5 | 3500 | 72 |  | 0 | 40.2 | 10.63 | 6.13
DVH102* | 8.5 | 3500 | 72 |  | -5 | 35.4 | 9.37 | 5.99
DVH102* | 8.5 | 3500 | 72 |  | -10 | 31.02 | 8.21 | 5.85
DVH102* | 8.5 | 3500 | 72 |  | -13 | 28.6 | 7.57 | 5.78
DVH102* | 8.5 | 3500 | 75 |  | 65 | 139.65 | 36.94 | 7.92
DVH102* | 8.5 | 3500 | 75 |  | 60 | 129.47 | 34.25 | 7.75
DVH102* | 8.5 | 3500 | 75 |  | 55 | 119.71 | 31.67 | 7.57
DVH102* | 8.5 | 3500 | 75 |  | 50 | 110.35 | 29.19 | 7.39
DVH102* | 8.5 | 3500 | 75 |  | 45 | 101.42 | 26.83 | 7.21
DVH102* | 8.5 | 3500 | 75 |  | 40 | 92.89 | 24.57 | 7.02
DVH102* | 8.5 | 3500 | 75 |  | 35 | 84.78 | 22.43 | 6.84
DVH102* | 8.5 | 3500 | 75 |  | 30 | 77.08 | 20.39 | 6.65
DVH102* | 8.5 | 3500 | 75 |  | 25 | 69.8 | 18.47 | 6.46
DVH102* | 8.5 | 3500 | 75 |  | 20 | 62.94 | 16.65 | 6.27
DVH102* | 8.5 | 3500 | 75 |  | 15 | 56.48 | 14.94 | 6.07
DVH102* | 8.5 | 3500 | 75 |  | 10 | 50.44 | 13.34 | 6.62
DVH102* | 8.5 | 3500 | 75 |  | 5 | 44.82 | 11.86 | 6.45
DVH102* | 8.5 | 3500 | 75 |  | 0 | 39.61 | 10.48 | 6.28
DVH102* | 8.5 | 3500 | 75 |  | -5 | 34.81 | 9.21 | 6.13
DVH102* | 8.5 | 3500 | 75 |  | -10 | 30.43 | 8.05 | 5.99
DVH102* | 8.5 | 3500 | 75 |  | -13 | 27.99 | 7.4 | 5.91
DVH120* | 10 | 3200 | 61 |  | 65 | 156.93 | 45.41 | 8.08
DVH120* | 10 | 3200 | 61 |  | 60 | 145.69 | 42.16 | 7.93
DVH120* | 10 | 3200 | 61 |  | 55 | 134.95 | 39.05 | 7.78
DVH120* | 10 | 3200 | 61 |  | 50 | 124.69 | 36.08 | 7.62
DVH120* | 10 | 3200 | 61 |  | 45 | 114.92 | 33.25 | 7.46
DVH120* | 10 | 3200 | 61 |  | 40 | 105.65 | 30.57 | 7.3
DVH120* | 10 | 3200 | 61 |  | 35 | 96.86 | 28.03 | 7.14
DVH120* | 10 | 3200 | 61 |  | 30 | 88.56 | 25.62 | 6.98
DVH120* | 10 | 3200 | 61 |  | 25 | 80.75 | 23.37 | 6.81
DVH120* | 10 | 3200 | 61 |  | 20 | 73.43 | 21.25 | 6.64
DVH120* | 10 | 3200 | 61 |  | 15 | 66.6 | 19.27 | 6.48
DVH120* | 10 | 3200 | 61 |  | 10 | 60.26 | 17.44 | 6.85
DVH120* | 10 | 3200 | 61 |  | 5 | 54.41 | 15.74 | 6.71
DVH120* | 10 | 3200 | 61 |  | 0 | 49.05 | 14.19 | 6.58
DVH120* | 10 | 3200 | 61 |  | -5 | 44.18 | 12.78 | 6.46
DVH120* | 10 | 3200 | 61 |  | -10 | 39.79 | 11.51 | 6.34
DVH120* | 10 | 3200 | 61 |  | -13 | 37.4 | 10.82 | 6.27
DVH120* | 10 | 3200 | 65 |  | 65 | 155.63 | 45.03 | 8.48
DVH120* | 10 | 3200 | 65 |  | 60 | 144.47 | 41.8 | 8.3
DVH120* | 10 | 3200 | 65 |  | 55 | 133.8 | 38.72 | 8.13
DVH120* | 10 | 3200 | 65 |  | 50 | 123.61 | 35.77 | 7.96
DVH120* | 10 | 3200 | 65 |  | 45 | 113.9 | 32.96 | 7.78
DVH120* | 10 | 3200 | 65 |  | 40 | 104.68 | 30.29 | 7.61
DVH120* | 10 | 3200 | 65 |  | 35 | 95.94 | 27.76 | 7.43
DVH120* | 10 | 3200 | 65 |  | 30 | 87.69 | 25.37 | 7.25
DVH120* | 10 | 3200 | 65 |  | 25 | 79.92 | 23.12 | 7.07
DVH120* | 10 | 3200 | 65 |  | 20 | 72.64 | 21.02 | 6.89
DVH120* | 10 | 3200 | 65 |  | 15 | 65.84 | 19.05 | 6.71
DVH120* | 10 | 3200 | 65 |  | 10 | 59.52 | 17.22 | 7.07
DVH120* | 10 | 3200 | 65 |  | 5 | 53.69 | 15.54 | 6.92
DVH120* | 10 | 3200 | 65 |  | 0 | 48.35 | 13.99 | 6.78
DVH120* | 10 | 3200 | 65 |  | -5 | 43.48 | 12.58 | 6.65
DVH120* | 10 | 3200 | 65 |  | -10 | 39.11 | 11.32 | 6.52
DVH120* | 10 | 3200 | 65 |  | -13 | 36.71 | 10.62 | 6.44
DVH120* | 10 | 3200 | 68 |  | 65 | 154.67 | 44.75 | 8.77
DVH120* | 10 | 3200 | 68 |  | 60 | 143.56 | 41.54 | 8.58
DVH120* | 10 | 3200 | 68 |  | 55 | 132.94 | 38.47 | 8.4
DVH120* | 10 | 3200 | 68 |  | 50 | 122.8 | 35.53 | 8.21
DVH120* | 10 | 3200 | 68 |  | 45 | 113.14 | 32.74 | 8.02
DVH120* | 10 | 3200 | 68 |  | 40 | 103.96 | 30.08 | 7.83
DVH120* | 10 | 3200 | 68 |  | 35 | 95.26 | 27.56 | 7.65
DVH120* | 10 | 3200 | 68 |  | 30 | 87.04 | 25.19 | 7.46
DVH120* | 10 | 3200 | 68 |  | 25 | 79.3 | 22.95 | 7.27
DVH120* | 10 | 3200 | 68 |  | 20 | 72.04 | 20.84 | 7.07
DVH120* | 10 | 3200 | 68 |  | 15 | 65.27 | 18.89 | 6.88
DVH120* | 10 | 3200 | 68 |  | 10 | 58.97 | 17.06 | 7.24
DVH120* | 10 | 3200 | 68 |  | 5 | 53.15 | 15.38 | 7.08
DVH120* | 10 | 3200 | 68 |  | 0 | 47.82 | 13.84 | 6.93
DVH120* | 10 | 3200 | 68 |  | -5 | 42.96 | 12.43 | 6.79
DVH120* | 10 | 3200 | 68 |  | -10 | 38.59 | 11.17 | 6.65
DVH120* | 10 | 3200 | 68 |  | -13 | 36.2 | 10.47 | 6.57
DVH120* | 10 | 3200 | 70 |  | 65 | 154.02 | 44.57 | 8.96
DVH120* | 10 | 3200 | 70 |  | 60 | 142.95 | 41.36 | 8.77
DVH120* | 10 | 3200 | 70 |  | 55 | 132.37 | 38.3 | 8.57
DVH120* | 10 | 3200 | 70 |  | 50 | 122.26 | 35.38 | 8.38
DVH120* | 10 | 3200 | 70 |  | 45 | 112.63 | 32.59 | 8.18
DVH120* | 10 | 3200 | 70 |  | 40 | 103.47 | 29.94 | 7.99
DVH120* | 10 | 3200 | 70 |  | 35 | 94.8 | 27.43 | 7.79
DVH120* | 10 | 3200 | 70 |  | 30 | 86.6 | 25.06 | 7.59
DVH120* | 10 | 3200 | 70 |  | 25 | 78.88 | 22.82 | 7.4
DVH120* | 10 | 3200 | 70 |  | 20 | 71.64 | 20.73 | 7.2
DVH120* | 10 | 3200 | 70 |  | 15 | 64.88 | 18.77 | 7
DVH120* | 10 | 3200 | 70 |  | 10 | 58.6 | 16.96 | 7.35
DVH120* | 10 | 3200 | 70 |  | 5 | 52.79 | 15.27 | 7.19
DVH120* | 10 | 3200 | 70 |  | 0 | 47.47 | 13.74 | 7.03
DVH120* | 10 | 3200 | 70 |  | -5 | 42.62 | 12.33 | 6.88
DVH120* | 10 | 3200 | 70 |  | -10 | 38.25 | 11.07 | 6.74
DVH120* | 10 | 3200 | 70 |  | -13 | 35.85 | 10.37 | 6.66
DVH120* | 10 | 3200 | 72 |  | 65 | 153.36 | 44.38 | 9.16
DVH120* | 10 | 3200 | 72 |  | 60 | 142.33 | 41.18 | 8.96
DVH120* | 10 | 3200 | 72 |  | 55 | 131.78 | 38.13 | 8.76
DVH120* | 10 | 3200 | 72 |  | 50 | 121.7 | 35.21 | 8.55
DVH120* | 10 | 3200 | 72 |  | 45 | 112.1 | 32.44 | 8.35
DVH120* | 10 | 3200 | 72 |  | 40 | 102.97 | 29.79 | 8.14
DVH120* | 10 | 3200 | 72 |  | 35 | 94.33 | 27.29 | 7.94
DVH120* | 10 | 3200 | 72 |  | 30 | 86.15 | 24.93 | 7.73
DVH120* | 10 | 3200 | 72 |  | 25 | 78.46 | 22.7 | 7.53
DVH120* | 10 | 3200 | 72 |  | 20 | 71.23 | 20.61 | 7.32
DVH120* | 10 | 3200 | 72 |  | 15 | 64.49 | 18.66 | 7.12
DVH120* | 10 | 3200 | 72 |  | 10 | 58.22 | 16.85 | 7.47
DVH120* | 10 | 3200 | 72 |  | 5 | 52.43 | 15.17 | 7.3
DVH120* | 10 | 3200 | 72 |  | 0 | 47.11 | 13.63 | 7.13
DVH120* | 10 | 3200 | 72 |  | -5 | 42.27 | 12.23 | 6.98
DVH120* | 10 | 3200 | 72 |  | -10 | 37.9 | 10.97 | 6.83
DVH120* | 10 | 3200 | 72 |  | -13 | 35.51 | 10.27 | 6.75
DVH120* | 10 | 3200 | 75 |  | 60 | 141.39 | 40.91 | 9.24
DVH120* | 10 | 3200 | 75 |  | 55 | 130.89 | 37.87 | 9.03
DVH120* | 10 | 3200 | 75 |  | 50 | 120.86 | 34.97 | 8.81
DVH120* | 10 | 3200 | 75 |  | 45 | 111.31 | 32.21 | 8.59
DVH120* | 10 | 3200 | 75 |  | 40 | 102.23 | 29.58 | 8.38
DVH120* | 10 | 3200 | 75 |  | 35 | 93.62 | 27.09 | 8.16
DVH120* | 10 | 3200 | 75 |  | 30 | 85.48 | 24.73 | 7.94
DVH120* | 10 | 3200 | 75 |  | 25 | 77.81 | 22.51 | 7.73
DVH120* | 10 | 3200 | 75 |  | 20 | 70.62 | 20.43 | 7.51
DVH120* | 10 | 3200 | 75 |  | 15 | 63.9 | 18.49 | 7.3
DVH120* | 10 | 3200 | 75 |  | 10 | 57.65 | 16.68 | 7.64
DVH120* | 10 | 3200 | 75 |  | 5 | 51.88 | 15.01 | 7.46
DVH120* | 10 | 3200 | 75 |  | 0 | 46.57 | 13.48 | 7.29
DVH120* | 10 | 3200 | 75 |  | -5 | 41.74 | 12.08 | 7.13
DVH120* | 10 | 3200 | 75 |  | -10 | 37.39 | 10.82 | 6.98
DVH120* | 10 | 3200 | 75 |  | -13 | 35 | 10.13 | 6.89
DVH120* | 10 | 3600 | 61 |  | 65 | 158.21 | 40.69 | 7.87
DVH120* | 10 | 3600 | 61 |  | 60 | 146.89 | 37.78 | 7.72
DVH120* | 10 | 3600 | 61 |  | 55 | 136.05 | 34.99 | 7.57
DVH120* | 10 | 3600 | 61 |  | 50 | 125.71 | 32.33 | 7.42
DVH120* | 10 | 3600 | 61 |  | 45 | 115.87 | 29.8 | 7.26
DVH120* | 10 | 3600 | 61 |  | 40 | 106.51 | 27.39 | 7.11
DVH120* | 10 | 3600 | 61 |  | 35 | 97.65 | 25.12 | 6.95
DVH120* | 10 | 3600 | 61 |  | 30 | 89.29 | 22.97 | 6.79
DVH120* | 10 | 3600 | 61 |  | 25 | 81.41 | 20.94 | 6.63
DVH120* | 10 | 3600 | 61 |  | 20 | 74.03 | 19.04 | 6.47
DVH120* | 10 | 3600 | 61 |  | 15 | 67.15 | 17.27 | 6.3
DVH120* | 10 | 3600 | 61 |  | 10 | 60.76 | 15.63 | 6.67
DVH120* | 10 | 3600 | 61 |  | 5 | 54.86 | 14.11 | 6.54
DVH120* | 10 | 3600 | 61 |  | 0 | 49.45 | 12.72 | 6.41
DVH120* | 10 | 3600 | 61 |  | -5 | 44.54 | 11.46 | 6.29
DVH120* | 10 | 3600 | 61 |  | -10 | 40.12 | 10.32 | 6.17
DVH120* | 10 | 3600 | 61 |  | -13 | 37.71 | 9.7 | 6.1
DVH120* | 10 | 3600 | 65 |  | 65 | 156.91 | 40.36 | 8.25
DVH120* | 10 | 3600 | 65 |  | 60 | 145.66 | 37.46 | 8.08
DVH120* | 10 | 3600 | 65 |  | 55 | 134.9 | 34.7 | 7.91
DVH120* | 10 | 3600 | 65 |  | 50 | 124.62 | 32.05 | 7.74
DVH120* | 10 | 3600 | 65 |  | 45 | 114.84 | 29.54 | 7.57
DVH120* | 10 | 3600 | 65 |  | 40 | 105.54 | 27.15 | 7.4
DVH120* | 10 | 3600 | 65 |  | 35 | 96.73 | 24.88 | 7.23
DVH120* | 10 | 3600 | 65 |  | 30 | 88.41 | 22.74 | 7.06
DVH120* | 10 | 3600 | 65 |  | 25 | 80.58 | 20.73 | 6.88
DVH120* | 10 | 3600 | 65 |  | 20 | 73.23 | 18.83 | 6.71
DVH120* | 10 | 3600 | 65 |  | 15 | 66.38 | 17.07 | 6.53
DVH120* | 10 | 3600 | 65 |  | 10 | 60.01 | 15.43 | 6.89
DVH120* | 10 | 3600 | 65 |  | 5 | 54.13 | 13.92 | 6.74
DVH120* | 10 | 3600 | 65 |  | 0 | 48.74 | 12.54 | 6.6
DVH120* | 10 | 3600 | 65 |  | -5 | 43.84 | 11.28 | 6.47
DVH120* | 10 | 3600 | 65 |  | -10 | 39.43 | 10.14 | 6.34
DVH120* | 10 | 3600 | 65 |  | -13 | 37.01 | 9.52 | 6.27
DVH120* | 10 | 3600 | 68 |  | 65 | 155.93 | 40.11 | 8.54
DVH120* | 10 | 3600 | 68 |  | 60 | 144.74 | 37.23 | 8.35
DVH120* | 10 | 3600 | 68 |  | 55 | 134.03 | 34.47 | 8.17
DVH120* | 10 | 3600 | 68 |  | 50 | 123.81 | 31.84 | 7.99
DVH120* | 10 | 3600 | 68 |  | 45 | 114.07 | 29.34 | 7.81
DVH120* | 10 | 3600 | 68 |  | 40 | 104.81 | 26.96 | 7.63
DVH120* | 10 | 3600 | 68 |  | 35 | 96.04 | 24.7 | 7.44
DVH120* | 10 | 3600 | 68 |  | 30 | 87.75 | 22.57 | 7.26
DVH120* | 10 | 3600 | 68 |  | 25 | 79.95 | 20.56 | 7.07
DVH120* | 10 | 3600 | 68 |  | 20 | 72.63 | 18.68 | 6.89
DVH120* | 10 | 3600 | 68 |  | 15 | 65.8 | 16.92 | 6.7
DVH120* | 10 | 3600 | 68 |  | 10 | 59.45 | 15.29 | 7.05
DVH120* | 10 | 3600 | 68 |  | 5 | 53.59 | 13.78 | 6.89
DVH120* | 10 | 3600 | 68 |  | 0 | 48.21 | 12.4 | 6.75
DVH120* | 10 | 3600 | 68 |  | -5 | 43.32 | 11.14 | 6.61
DVH120* | 10 | 3600 | 68 |  | -10 | 38.91 | 10.01 | 6.47
DVH120* | 10 | 3600 | 68 |  | -13 | 36.49 | 9.39 | 6.39
DVH120* | 10 | 3600 | 70 |  | 65 | 155.28 | 39.94 | 8.73
DVH120* | 10 | 3600 | 70 |  | 60 | 144.13 | 37.07 | 8.54
DVH120* | 10 | 3600 | 70 |  | 55 | 133.45 | 34.32 | 8.35
DVH120* | 10 | 3600 | 70 |  | 50 | 123.26 | 31.7 | 8.16
DVH120* | 10 | 3600 | 70 |  | 45 | 113.55 | 29.21 | 7.96
DVH120* | 10 | 3600 | 70 |  | 40 | 104.32 | 26.83 | 7.77
DVH120* | 10 | 3600 | 70 |  | 35 | 95.58 | 24.58 | 7.58
DVH120* | 10 | 3600 | 70 |  | 30 | 87.31 | 22.46 | 7.39
DVH120* | 10 | 3600 | 70 |  | 25 | 79.53 | 20.46 | 7.2
DVH120* | 10 | 3600 | 70 |  | 20 | 72.23 | 18.58 | 7.01
DVH120* | 10 | 3600 | 70 |  | 15 | 65.42 | 16.83 | 6.81
DVH120* | 10 | 3600 | 70 |  | 10 | 59.08 | 15.2 | 7.16
DVH120* | 10 | 3600 | 70 |  | 5 | 53.23 | 13.69 | 7
DVH120* | 10 | 3600 | 70 |  | 0 | 47.86 | 12.31 | 6.84
DVH120* | 10 | 3600 | 70 |  | -5 | 42.97 | 11.05 | 6.7
DVH120* | 10 | 3600 | 70 |  | -10 | 38.56 | 9.92 | 6.56
DVH120* | 10 | 3600 | 70 |  | -13 | 36.15 | 9.3 | 6.48
DVH120* | 10 | 3600 | 72 |  | 65 | 154.61 | 39.77 | 8.92
DVH120* | 10 | 3600 | 72 |  | 60 | 143.5 | 36.91 | 8.72
DVH120* | 10 | 3600 | 72 |  | 55 | 132.86 | 34.17 | 8.52
DVH120* | 10 | 3600 | 72 |  | 50 | 122.7 | 31.56 | 8.32
DVH120* | 10 | 3600 | 72 |  | 45 | 113.02 | 29.07 | 8.12
DVH120* | 10 | 3600 | 72 |  | 40 | 103.82 | 26.7 | 7.93
DVH120* | 10 | 3600 | 72 |  | 35 | 95.1 | 24.46 | 7.73
DVH120* | 10 | 3600 | 72 |  | 30 | 86.86 | 22.34 | 7.53
DVH120* | 10 | 3600 | 72 |  | 25 | 79.1 | 20.34 | 7.33
DVH120* | 10 | 3600 | 72 |  | 20 | 71.82 | 18.47 | 7.13
DVH120* | 10 | 3600 | 72 |  | 15 | 65.02 | 16.72 | 6.93
DVH120* | 10 | 3600 | 72 |  | 10 | 58.7 | 15.1 | 7.27
DVH120* | 10 | 3600 | 72 |  | 5 | 52.86 | 13.6 | 7.1
DVH120* | 10 | 3600 | 72 |  | 0 | 47.5 | 12.22 | 6.94
DVH120* | 10 | 3600 | 72 |  | -5 | 42.61 | 10.96 | 6.79
DVH120* | 10 | 3600 | 72 |  | -10 | 38.21 | 9.83 | 6.65
DVH120* | 10 | 3600 | 72 |  | -13 | 35.8 | 9.21 | 6.57
DVH120* | 10 | 3600 | 75 |  | 65 | 153.61 | 39.51 | 9.21
DVH120* | 10 | 3600 | 75 |  | 60 | 142.55 | 36.66 | 9
DVH120* | 10 | 3600 | 75 |  | 55 | 131.96 | 33.94 | 8.78
DVH120* | 10 | 3600 | 75 |  | 50 | 121.85 | 31.34 | 8.57
DVH120* | 10 | 3600 | 75 |  | 45 | 112.22 | 28.86 | 8.36
DVH120* | 10 | 3600 | 75 |  | 40 | 103.06 | 26.51 | 8.15
DVH120* | 10 | 3600 | 75 |  | 35 | 94.38 | 24.27 | 7.94
DVH120* | 10 | 3600 | 75 |  | 30 | 86.18 | 22.17 | 7.73
DVH120* | 10 | 3600 | 75 |  | 25 | 78.45 | 20.18 | 7.52
DVH120* | 10 | 3600 | 75 |  | 20 | 71.2 | 18.31 | 7.31
DVH120* | 10 | 3600 | 75 |  | 15 | 64.42 | 16.57 | 7.1
DVH120* | 10 | 3600 | 75 |  | 10 | 58.12 | 14.95 | 7.44
DVH120* | 10 | 3600 | 75 |  | 5 | 52.3 | 13.45 | 7.26
DVH120* | 10 | 3600 | 75 |  | 0 | 46.96 | 12.08 | 7.1
DVH120* | 10 | 3600 | 75 |  | -5 | 42.09 | 10.83 | 6.94
DVH120* | 10 | 3600 | 75 |  | -10 | 37.69 | 9.69 | 6.79
DVH120* | 10 | 3600 | 75 |  | -13 | 35.29 | 9.08 | 6.7
DVH120* | 10 | 4000 | 61 |  | 65 | 158.4 | 36.67 | 7.65
DVH120* | 10 | 4000 | 61 |  | 60 | 147.06 | 34.04 | 7.5
DVH120* | 10 | 4000 | 61 |  | 55 | 136.21 | 31.53 | 7.36
DVH120* | 10 | 4000 | 61 |  | 50 | 125.86 | 29.13 | 7.21
DVH120* | 10 | 4000 | 61 |  | 45 | 116 | 26.85 | 7.06
DVH120* | 10 | 4000 | 61 |  | 40 | 106.64 | 24.69 | 6.91
DVH120* | 10 | 4000 | 61 |  | 35 | 97.77 | 22.63 | 6.75
DVH120* | 10 | 4000 | 61 |  | 30 | 89.39 | 20.69 | 6.6
DVH120* | 10 | 4000 | 61 |  | 25 | 81.51 | 18.87 | 6.44
DVH120* | 10 | 4000 | 61 |  | 20 | 74.12 | 17.16 | 6.29
DVH120* | 10 | 4000 | 61 |  | 15 | 67.23 | 15.56 | 6.13
DVH120* | 10 | 4000 | 61 |  | 10 | 60.83 | 14.08 | 6.48
DVH120* | 10 | 4000 | 61 |  | 5 | 54.92 | 12.71 | 6.35
DVH120* | 10 | 4000 | 61 |  | 0 | 49.51 | 11.46 | 6.23
DVH120* | 10 | 4000 | 61 |  | -5 | 44.59 | 10.32 | 6.11
DVH120* | 10 | 4000 | 61 |  | -10 | 40.17 | 9.3 | 6
DVH120* | 10 | 4000 | 61 |  | -13 | 37.75 | 8.74 | 5.93
DVH120* | 10 | 4000 | 65 |  | 65 | 157.1 | 36.37 | 8.02
DVH120* | 10 | 4000 | 65 |  | 60 | 145.83 | 33.76 | 7.86
DVH120* | 10 | 4000 | 65 |  | 55 | 135.06 | 31.26 | 7.69
DVH120* | 10 | 4000 | 65 |  | 50 | 124.77 | 28.88 | 7.53
DVH120* | 10 | 4000 | 65 |  | 45 | 114.97 | 26.61 | 7.36
DVH120* | 10 | 4000 | 65 |  | 40 | 105.67 | 24.46 | 7.2
DVH120* | 10 | 4000 | 65 |  | 35 | 96.85 | 22.42 | 7.03
DVH120* | 10 | 4000 | 65 |  | 30 | 88.51 | 20.49 | 6.86
DVH120* | 10 | 4000 | 65 |  | 25 | 80.67 | 18.67 | 6.69
DVH120* | 10 | 4000 | 65 |  | 20 | 73.32 | 16.97 | 6.52
DVH120* | 10 | 4000 | 65 |  | 15 | 66.46 | 15.38 | 6.35
DVH120* | 10 | 4000 | 65 |  | 10 | 60.08 | 13.91 | 6.69
DVH120* | 10 | 4000 | 65 |  | 5 | 54.2 | 12.55 | 6.55
DVH120* | 10 | 4000 | 65 |  | 0 | 48.8 | 11.3 | 6.42
DVH120* | 10 | 4000 | 65 |  | -5 | 43.89 | 10.16 | 6.29
DVH120* | 10 | 4000 | 65 |  | -10 | 39.47 | 9.14 | 6.16
DVH120* | 10 | 4000 | 65 |  | -13 | 37.06 | 8.58 | 6.09
DVH120* | 10 | 4000 | 68 |  | 65 | 156.12 | 36.14 | 8.3
DVH120* | 10 | 4000 | 68 |  | 60 | 144.91 | 33.54 | 8.12
DVH120* | 10 | 4000 | 68 |  | 55 | 134.19 | 31.06 | 7.94
DVH120* | 10 | 4000 | 68 |  | 50 | 123.95 | 28.69 | 7.77
DVH120* | 10 | 4000 | 68 |  | 45 | 114.2 | 26.44 | 7.59
DVH120* | 10 | 4000 | 68 |  | 40 | 104.93 | 24.29 | 7.41
DVH120* | 10 | 4000 | 68 |  | 35 | 96.15 | 22.26 | 7.23
DVH120* | 10 | 4000 | 68 |  | 30 | 87.86 | 20.34 | 7.05
DVH120* | 10 | 4000 | 68 |  | 25 | 80.05 | 18.53 | 6.87
DVH120* | 10 | 4000 | 68 |  | 20 | 72.72 | 16.83 | 6.69
DVH120* | 10 | 4000 | 68 |  | 15 | 65.88 | 15.25 | 6.51
DVH120* | 10 | 4000 | 68 |  | 10 | 59.52 | 13.78 | 6.85
DVH120* | 10 | 4000 | 68 |  | 5 | 53.65 | 12.42 | 6.7
DVH120* | 10 | 4000 | 68 |  | 0 | 48.27 | 11.17 | 6.56
DVH120* | 10 | 4000 | 68 |  | -5 | 43.37 | 10.04 | 6.42
DVH120* | 10 | 4000 | 68 |  | -10 | 38.95 | 9.02 | 6.29
DVH120* | 10 | 4000 | 68 |  | -13 | 36.54 | 8.46 | 6.22
DVH120* | 10 | 4000 | 70 |  | 65 | 155.47 | 35.99 | 8.48
DVH120* | 10 | 4000 | 70 |  | 60 | 144.3 | 33.4 | 8.3
DVH120* | 10 | 4000 | 70 |  | 55 | 133.61 | 30.93 | 8.11
DVH120* | 10 | 4000 | 70 |  | 50 | 123.41 | 28.57 | 7.93
DVH120* | 10 | 4000 | 70 |  | 45 | 113.69 | 26.32 | 7.74
DVH120* | 10 | 4000 | 70 |  | 40 | 104.45 | 24.18 | 7.56
DVH120* | 10 | 4000 | 70 |  | 35 | 95.69 | 22.15 | 7.37
DVH120* | 10 | 4000 | 70 |  | 30 | 87.42 | 20.24 | 7.18
DVH120* | 10 | 4000 | 70 |  | 25 | 79.63 | 18.43 | 7
DVH120* | 10 | 4000 | 70 |  | 20 | 72.32 | 16.74 | 6.81
DVH120* | 10 | 4000 | 70 |  | 15 | 65.49 | 15.16 | 6.62
DVH120* | 10 | 4000 | 70 |  | 10 | 59.15 | 13.69 | 6.96
DVH120* | 10 | 4000 | 70 |  | 5 | 53.29 | 12.34 | 6.8
DVH120* | 10 | 4000 | 70 |  | 0 | 47.91 | 11.09 | 6.65
DVH120* | 10 | 4000 | 70 |  | -5 | 43.02 | 9.96 | 6.51
DVH120* | 10 | 4000 | 70 |  | -10 | 38.61 | 8.94 | 6.37
DVH120* | 10 | 4000 | 70 |  | -13 | 36.19 | 8.38 | 6.3
DVH120* | 10 | 4000 | 72 |  | 65 | 154.8 | 35.83 | 8.67
DVH120* | 10 | 4000 | 72 |  | 60 | 143.67 | 33.26 | 8.48
DVH120* | 10 | 4000 | 72 |  | 55 | 133.02 | 30.79 | 8.28
DVH120* | 10 | 4000 | 72 |  | 50 | 122.84 | 28.44 | 8.09
DVH120* | 10 | 4000 | 72 |  | 45 | 113.15 | 26.19 | 7.9
DVH120* | 10 | 4000 | 72 |  | 40 | 103.94 | 24.06 | 7.7
DVH120* | 10 | 4000 | 72 |  | 35 | 95.21 | 22.04 | 7.51
DVH120* | 10 | 4000 | 72 |  | 30 | 86.96 | 20.13 | 7.32
DVH120* | 10 | 4000 | 72 |  | 25 | 79.19 | 18.33 | 7.12
DVH120* | 10 | 4000 | 72 |  | 20 | 71.9 | 16.64 | 6.93
DVH120* | 10 | 4000 | 72 |  | 15 | 65.1 | 15.07 | 6.73
DVH120* | 10 | 4000 | 72 |  | 10 | 58.77 | 13.6 | 7.07
DVH120* | 10 | 4000 | 72 |  | 5 | 52.92 | 12.25 | 6.9
DVH120* | 10 | 4000 | 72 |  | 0 | 47.55 | 11.01 | 6.75
DVH120* | 10 | 4000 | 72 |  | -5 | 42.67 | 9.88 | 6.6
DVH120* | 10 | 4000 | 72 |  | -10 | 38.26 | 8.86 | 6.46
DVH120* | 10 | 4000 | 72 |  | -13 | 35.85 | 8.3 | 6.38
DVH120* | 10 | 4000 | 75 |  | 65 | 153.8 | 35.6 | 8.95
DVH120* | 10 | 4000 | 75 |  | 60 | 142.72 | 33.04 | 8.74
DVH120* | 10 | 4000 | 75 |  | 55 | 132.12 | 30.58 | 8.54
DVH120* | 10 | 4000 | 75 |  | 50 | 122 | 28.24 | 8.33
DVH120* | 10 | 4000 | 75 |  | 45 | 112.35 | 26.01 | 8.13
DVH120* | 10 | 4000 | 75 |  | 40 | 103.19 | 23.89 | 7.92
DVH120* | 10 | 4000 | 75 |  | 35 | 94.49 | 21.87 | 7.72
DVH120* | 10 | 4000 | 75 |  | 30 | 86.28 | 19.97 | 7.52
DVH120* | 10 | 4000 | 75 |  | 25 | 78.54 | 18.18 | 7.31
DVH120* | 10 | 4000 | 75 |  | 20 | 71.28 | 16.5 | 7.11
DVH120* | 10 | 4000 | 75 |  | 15 | 64.5 | 14.93 | 6.91
DVH120* | 10 | 4000 | 75 |  | 10 | 58.19 | 13.47 | 7.23
DVH120* | 10 | 4000 | 75 |  | 5 | 52.36 | 12.12 | 7.06
DVH120* | 10 | 4000 | 75 |  | 0 | 47.01 | 10.88 | 6.9
DVH120* | 10 | 4000 | 75 |  | -5 | 42.14 | 9.75 | 6.75
DVH120* | 10 | 4000 | 75 |  | -10 | 37.74 | 8.74 | 6.6
DVH120* | 10 | 4000 | 75 |  | -13 | 35.33 | 8.18 | 6.51

## Electrical Data
Model | Tons | Motor | Power Supply | Electric Heat kW | Electric Heat Kit | Electric Heat FLA | MCA - Base Unit | MOP - Base Unit | Conv. Outlet FLA | MCA - w/ Conv. Outlet | MOP - w/ Conv. Outlet | Power Exhaust FLA | MCA - w/ Power Exhaust | MOP - w/ Power Exhaust | MCA - w/ Conv. Outlet + Pwr Exhaust | MOP - w/ Conv. Outlet + Pwr Exhaust | Indoor Motor HP
DSG0363D | 3 | D - Standard Static | 208/230/3/60 |  |  |  | 19.9/19.9 | 30/30 | 9.6/8.7 | 29.5/28.6 | 40/35 | 2.2/1.9 (1.7/1.5) | 22.1/21.8 | 30/30 | 31.7/30.5 | 40/40 | 0.75
DSG0363W | 3 | W - High Static | 208/230/3/60 |  |  |  | 19.2/19.2 | 25/25 | 9.6/8.7 | 28.8/27.9 | 35/35 | 2.2/1.9 (1.7/1.5) | 21.4/21.1 | 30/30 | 31.0/29.8 | 40/35
DSG0364D | 3 | D - Standard Static | 460/3/60 |  |  |  | 9.1 | 15 | 4.3 | 13.4 | 15 | 0.9 (0.5) | 10 | 15 | 14.3 | 15 | 1.2
DSG0364W | 3 | W - High Static | 460/3/60 |  |  |  | 9.1 | 15 | 4.3 | 13.4 | 15 | 0.9 (0.5) | 10 | 15 | 14.3 | 15
DSG0483D | 4 | D - Standard Static | 208/230/3/60 |  |  |  | 24.1/24.1 | 35/35 | 9.6/8.7 | 33.7/32.8 | 45/40 | 2.2/1.9 (1.7/1.5) | 26.3/26.0 | 35/35 | 35.9/34.7 | 45/45 | 1
DSG0483W | 4 | W - High Static | 208/230/3/60 |  |  |  | 22.2/22.2 | 30/30 | 9.6/8.7 | 31.8/30.9 | 40/40 | 2.2/1.9 (1.7/1.5) | 24.4/24.1 | 35/35 | 34.0/32.8 | 45/40
DSG0484D | 4 | D - Standard Static | 460/3/60 |  |  |  | 10.6 | 15 | 4.3 | 14.9 | 20 | 0.9 (0.5) | 11.5 | 15 | 15.8 | 20 | 1.2
DSG0484W | 4 | W - High Static | 460/3/60 |  |  |  | 10.6 | 15 | 4.3 | 14.9 | 20 | 0.9 (0.5) | 11.5 | 15 | 15.8 | 20
DSG0603D | 5 | D - Standard Static | 208/230/3/60 |  |  |  | 28.1/28.1 | 40/40 | 9.6/8.7 | 37.7/36.8 | 50/50 | 2.2/1.9 (1.7/1.5) | 30.3/30.0 | 45/40 | 39.9/38.7 | 50/50 | 1
DSG0603W | 5 | W - High Static | 208/230/3/60 |  |  |  | 28.9/28.9 | 40/40 | 9.6/8.7 | 38.5/37.6 | 50/50 | 2.2/1.9 (1.7/1.5) | 31.1/30.8 | 45/45 | 40.7/39.5 | 50/50
DSG0604D | 5 | D - Standard Static | 460/3/60 |  |  |  | 13 | 20 | 4.3 | 17.3 | 20 | 0.9 (0.5) | 13.9 | 20 | 18.2 | 25 | 1.2
DSG0604W | 5 | W - High Static | 460/3/60 |  |  |  | 15 | 20 | 4.3 | 19.3 | 25 | 0.9 (0.5) | 15.9 | 20 | 20.2 | 25
DSG0723D | 6 | D - Standard Static | 208/230/3/60 |  |  |  | 27.2/27.2 | 40/40 | 9.6/8.7 | 36.8/35.9 | 50/50 | 2.2/1.9 (1.7/1.5) | 29.4/29.1 | 40/40 | 39.0/37.8 | 50/50 | 1.2
DSG0723W | 6 | W - High Static | 208/230/3/60 |  |  |  | 29.9/29.9 | 45/45 | 9.6/8.7 | 39.5/38.6 | 50/50 | 2.2/1.9 (1.7/1.5) | 32.1/31.8 | 45/45 | 41.7/40.5 | 50/50
DSG0724D | 6 | D - Standard Static | 460/3/60 |  |  |  | 12.2 | 15 | 4.3 | 16.5 | 20 | 0.9 (0.5) | 13.1 | 15 | 17.4 | 20 | 1.2
DSG0724W | 6 | W - High Static | 460/3/60 |  |  |  | 14.2 | 20 | 4.3 | 18.5 | 25 | 0.9 (0.5) | 15.1 | 20 | 19.4 | 25
DSG0903D | 7.5 | D - Standard Static | 208/230/3/60 |  |  |  | 39.4/39.4 | 50/50 | 9.6/8.7 | 49.0/48.1 | 60/60 | 3.3/3.0 (2.4) | 42.7/42.4 | 50/50 | 52.3/51.1 | 60/60 | 2.4
DSG0903L | 7.5 | L - Medium Static | 208/230/3/60 |  |  |  | 39.4/39.4 | 50/50 | 9.6/8.7 | 49.0/48.1 | 60/60 | 3.3/3.0 (2.4) | 42.7/42.4 | 50/50 | 52.3/51.1 | 60/60 | 2.4
DSG0903W | 7.5 | W - High Static | 208/230/3/60 |  |  |  | 42.3/42.3 | 50/50 | 9.6/8.7 | 51.9/51.0 | 60/60 | 3.3/3.0 (2.4) | 45.6/45.3 | 50/50 | 55.2/54.0 | 60/60 | 3.5
DSG0904D | 7.5 | D - Standard Static | 460/3/60 |  |  |  | 20.1 | 25 | 4.3 | 24.4 | 30 | 1.2 (1.0) | 21.3 | 25 | 25.6 | 30 | 2.4
DSG0904L | 7.5 | L - Medium Static | 460/3/60 |  |  |  | 20.1 | 25 | 4.3 | 24.4 | 30 | 1.2 (1.0) | 21.3 | 25 | 25.6 | 30 | 2.4
DSG0904W | 7.5 | W - High Static | 460/3/60 |  |  |  | 21.9 | 25 | 4.3 | 26.2 | 30 | 1.2 (1.0) | 23.1 | 30 | 27.4 | 30 | 3.5
DSG1023D | 8.5 | D - Standard Static | 208/230/3/60 |  |  |  | 43.7/43.7 | 50/50 | 9.6/8.7 | 53.3/52.4 | 60/60 | 3.3/3.0 (2.4) | 47.0/46.7 | 60/60 | 56.6/55.4 | 60/60 | 2.4
DSG1023L | 8.5 | L - Medium Static | 208/230/3/60 |  |  |  | 46.6/46.6 | 60/60 | 9.6/8.7 | 56.2/55.3 | 70/60 | 3.3/3.0 (2.4) | 49.9/49.6 | 60/60 | 59.5/58.3 | 70/70 | 3.5
DSG1023W | 8.5 | W - High Static | 208/230/3/60 |  |  |  | 46.6/46.6 | 60/60 | 9.6/8.7 | 56.2/55.3 | 70/60 | 3.3/3.0 (2.4) | 49.9/49.6 | 60/60 | 59.5/58.3 | 70/70 | 3.5
DSG1024D | 8.5 | D - Standard Static | 460/3/60 |  |  |  | 21.5 | 25 | 4.3 | 25.8 | 30 | 1.2 (1.0) | 22.7 | 25 | 27 | 30 | 2.4
DSG1024L | 8.5 | L - Medium Static | 460/3/60 |  |  |  | 23.3 | 30 | 4.3 | 27.6 | 35 | 1.2 (1.0) | 24.5 | 30 | 28.8 | 35 | 3.5
DSG1024W | 8.5 | W - High Static | 460/3/60 |  |  |  | 23.3 | 30 | 4.3 | 27.6 | 35 | 1.2 (1.0) | 24.5 | 30 | 28.8 | 35 | 3.5
DSG1203D | 10 | D - Standard Static | 208/230/3/60 |  |  |  | 53.8/53.8 | 70/70 | 9.6/8.7 | 63.4/62.5 | 80/70 | 3.3/3.0 (2.4) | 57.1/56.8 | 70/70 | 66.7/65.5 | 80/80 | 3.5
DSG1203L | 10 | L - Medium Static | 208/230/3/60 |  |  |  | 57.4/57.4 | 70/70 | 9.6/8.7 | 67.0/66.1 | 80/80 | 3.3/3.0 (2.4) | 60.7/60.4 | 70/70 | 70.3/69.1 | 80/80 | 5
DSG1203W | 10 | W - High Static | 208/230/3/60 |  |  |  | 57.4/57.4 | 70/70 | 9.6/8.7 | 67.0/66.1 | 80/80 | 3.3/3.0 (2.4) | 60.7/60.4 | 70/70 | 70.3/69.1 | 80/80 | 5
DSG1204D | 10 | D - Standard Static | 460/3/60 |  |  |  | 26.2 | 30 | 4.3 | 30.5 | 35 | 1.2 (1.0) | 27.4 | 30 | 31.7 | 35 | 3.5
DSG1204L | 10 | L - Medium Static | 460/3/60 |  |  |  | 29.6 | 40 | 4.3 | 33.9 | 45 | 1.2 (1.0) | 30.8 | 40 | 35.1 | 45 | 5
DSG1204W | 10 | W - High Static | 460/3/60 |  |  |  | 29.6 | 40 | 4.3 | 33.9 | 45 | 1.2 (1.0) | 30.8 | 40 | 35.1 | 45 | 5
DSG1503D | 12.5 | D - Standard Static | 208/230/3/60 |  |  |  | 59.5/59.5 | 70/70 | 9.6/8.7 | 69.1/68.2 | 80/80 | 3.3/3.0 (2.4) | 62.8/62.5 | 80/80 | 72.4/71.2 | 90/80 | 3.5
DSG1503L | 12.5 | L - Medium Static | 208/230/3/60 |  |  |  | 63.1/63.1 | 80/80 | 9.6/8.7 | 72.7/71.8 | 90/90 | 3.3/3.0 (2.4) | 66.4/66.1 | 80/80 | 76.0/74.8 | 90/90 | 5
DSG1503W | 12.5 | W - High Static | 208/230/3/60 |  |  |  | 63.1/63.1 | 80/80 | 9.6/8.7 | 72.7/71.8 | 90/90 | 3.3/3.0 (2.4) | 66.4/66.1 | 80/80 | 76.0/74.8 | 90/90 | 5
DSG1504D | 12.5 | D - Standard Static | 460/3/60 |  |  |  | 30.2 | 35 | 4.3 | 34.5 | 40 | 1.2 (1.0) | 31.4 | 40 | 35.7 | 40 | 3.5
DSG1504L | 12.5 | L - Medium Static | 460/3/60 |  |  |  | 33.6 | 40 | 4.3 | 37.9 | 45 | 1.2 (1.0) | 34.8 | 45 | 39.1 | 45 | 5
DSG1504W | 12.5 | W - High Static | 460/3/60 |  |  |  | 33.6 | 40 | 4.3 | 37.9 | 45 | 1.2 (1.0) | 34.8 | 45 | 39.1 | 45 | 5
DSG1803D | 15 | D - Standard Static | 208/230/3/60 |  |  |  | 84.1/84.1 | 100/100 | 9.6/8.7 | 93.7/92.8 | 110/110 | 4.8 | 88.9/88.9 | 110/110 | 98.5/97.6 | 110/110 | 3.5
DSG1803W | 15 | W - High Static | 208/230/3/60 |  |  |  | 91.3/91.3 | 110/110 | 9.6/8.7 | 101/100 | 125/125 | 4.8 | 96.1/96.1 | 110/110 | 106/105 | 125/125 | 5
DSG1804D | 15 | D - Standard Static | 460/3/60 |  |  |  | 41.4 | 50 | 4.3 | 45.7 | 50 | 2.4 | 43.8 | 50 | 48.1 | 50 | 3.5
DSG1804W | 15 | W - High Static | 460/3/60 |  |  |  | 48.2 | 50 | 4.3 | 52.5 | 60 | 2.4 | 50.6 | 60 | 54.9 | 60 | 5
DSG2403D | 20 | D - Standard Static | 208/230/3/60 |  |  |  | 98.7/98.7 | 125/125 | 9.6/8.7 | 108/107 | 125/125 | 4.8 | 103/103 | 125/125 | 113/112 | 125/125 | 3.5
DSG2403W | 20 | W - High Static | 208/230/3/60 |  |  |  | 106/106 | 125/125 | 9.6/8.7 | 115/115 | 125/125 | 4.8 | 111/111 | 125/125 | 120/119 | 125/125 | 5
DSG2404D | 20 | D - Standard Static | 460/3/60 |  |  |  | 50.8 | 60 | 4.3 | 55.1 | 60 | 2.4 | 53.2 | 60 | 57.5 | 70 | 3.5
DSG2404W | 20 | W - High Static | 460/3/60 |  |  |  | 57.6 | 70 | 4.3 | 61.9 | 70 | 2.4 | 60 | 70 | 64.3 | 70 | 5
DSG3003D | 25 | D - Standard Static | 208/230/3/60 |  |  |  | 122/122 | 150/150 | 9.6/8.7 | 131/131 | 150/150 | 4.8 | 127/127 | 150/150 | 136/135 | 150/150 | 5
DSG3003W | 25 | W - High Static | 208/230/3/60 |  |  |  | 122/122 | 150/150 | 9.6/8.7 | 131/131 | 150/150 | 4.8 | 127/127 | 150/150 | 136/135 | 150/150 | 5
DSG3004D | 25 | D - Standard Static | 460/3/60 |  |  |  | 74.3 | 90 | 4.3 | 78.6 | 90 | 2.4 | 76.7 | 90 | 81 | 100 | 5
DSG3004W | 25 | W - High Static | 460/3/60 |  |  |  | 74.3 | 90 | 4.3 | 78.6 | 90 | 2.4 | 76.7 | 90 | 81 | 100 | 5
DHG0363D | 3 | D - Standard Static | 208/230/3/60 |  |  |  | 18.1/18.1 | 25/25 | 9.6/8.7 | 27.7/26.8 | 35/35 | 2.2/1.9 (1.7/1.5) | 20.3/20.0 | 25/25 | 29.9/28.7 | 35/35 | 0.75
DHG0363W | 3 | W - High Static | 208/230/3/60 |  |  |  | 17.4/17.4 | 25/25 | 9.6/8.7 | 27.0/26.1 | 35/35 | 2.2/1.9 (1.7/1.5) | 19.6/19.3 | 25/25 | 29.2/28.0 | 35/35 | 1.2
DHG0364D | 3 | D - Standard Static | 460/3/60 |  |  |  | 8.2 | 15 | 4.3 | 12.5 | 15 | 0.9 (0.5) | 9.1 | 15 | 13.4 | 15 | 1.2
DHG0364W | 3 | W - High Static | 460/3/60 |  |  |  | 8.2 | 15 | 4.3 | 12.5 | 15 | 0.9 (0.5) | 9.1 | 15 | 13.4 | 15 | 1.2
DHG0483D | 4 | D - Standard Static | 208/230/3/60 |  |  |  | 22.8/22.8 | 30/30 | 9.6/8.7 | 32.4/31.5 | 40/40 | 2.2/1.9 (1.7/1.5) | 25.0/24.7 | 35/35 | 34.6/33.4 | 45/40 | 1
DHG0483W | 4 | W - High Static | 208/230/3/60 |  |  |  | 20.9/20.9 | 30/30 | 9.6/8.7 | 30.5/29.6 | 40/40 | 2.2/1.9 (1.7/1.5) | 23.1/22.8 | 30/30 | 32.7/31.5 | 40/40 | 1.2
DHG0484D | 4 | D - Standard Static | 460/3/60 |  |  |  | 10.7 | 15 | 4.3 | 15 | 20 | 0.9 (0.5) | 11.6 | 15 | 15.9 | 20 | 1.2
DHG0484W | 4 | W - High Static | 460/3/60 |  |  |  | 10.7 | 15 | 4.3 | 15 | 20 | 0.9 (0.5) | 11.6 | 15 | 15.9 | 20 | 1.2
DHG0603D | 5 | D - Standard Static | 208/230/3/60 |  |  |  | 28.5/28.5 | 40/40 | 9.6/8.7 | 38.1/37.2 | 50/50 | 2.2/1.9 (1.7/1.5) | 30.7/30.4 | 45/45 | 40.3/39.1 | 50/50 | 1
DHG0603W | 5 | W - High Static | 208/230/3/60 |  |  |  | 29.3/29.3 | 40/40 | 9.6/8.7 | 38.9/38.0 | 50/50 | 2.2/1.9 (1.7/1.5) | 31.5/31.2 | 45/45 | 41.1/39.9 | 50/50 | 2.3
DHG0604D | 5 | D - Standard Static | 460/3/60 |  |  |  | 13.3 | 20 | 4.3 | 17.6 | 20 | 0.9 (0.5) | 14.2 | 20 | 18.5 | 25 | 1.2
DHG0604W | 5 | W - High Static | 460/3/60 |  |  |  | 15.3 | 20 | 4.3 | 19.6 | 25 | 0.9 (0.5) | 16.2 | 20 | 20.5 | 25 | 2.3
DHG0723D | 6 | D - Standard Static | 208/230/3/60 |  |  |  | 27.2/27.2 | 40/40 | 9.6/8.7 | 36.8/35.9 | 50/50 | 2.2/1.9 (1.7/1.5) | 29.4/29.1 | 40/40 | 39.0/37.8 | 50/50 | 1.2
DHG0723W | 6 | W - High Static | 208/230/3/60 |  |  |  | 29.9/29.9 | 45/45 | 9.6/8.7 | 39.5/38.6 | 50/50 | 2.2/1.9 (1.7/1.5) | 32.1/31.8 | 45/45 | 41.7/40.5 | 50/50 | 2.3
DHG0724D | 6 | D - Standard Static | 460/3/60 |  |  |  | 12.2 | 15 | 4.3 | 16.5 | 20 | 0.9 (0.5) | 13.1 | 15 | 17.4 | 20 | 1.2
DHG0724W | 6 | W - High Static | 460/3/60 |  |  |  | 14.2 | 20 | 4.3 | 18.5 | 25 | 0.9 (0.5) | 15.1 | 20 | 19.4 | 25 | 2.3
DHG0903D | 7.5 | D - Standard Static | 208/230/3/60 |  |  |  | 39.4/39.4 | 50/50 | 9.6/8.7 | 49.0/48.1 | 60/60 | 3.3/3.0 (2.4) | 42.7/42.4 | 50/50 | 52.3/51.1 | 60/60 | 2.4
DHG0903L | 7.5 | L - Medium Static | 208/230/3/60 |  |  |  | 39.4/39.4 | 50/50 | 9.6/8.7 | 49.0/48.1 | 60/60 | 3.3/3.0 (2.4) | 42.7/42.4 | 50/50 | 52.3/51.1 | 60/60 | 2.4
DHG0903W | 7.5 | W - High Static | 208/230/3/60 |  |  |  | 42.3/42.3 | 50/50 | 9.6/8.7 | 51.9/51.0 | 60/60 | 3.3/3.0 (2.4) | 45.6/45.3 | 50/50 | 55.2/54.0 | 60/60 | 3.5
DHG0904D | 7.5 | D - Standard Static | 460/3/60 |  |  |  | 20.1 | 25 | 4.3 | 24.4 | 30 | 1.2 (1.0) | 21.3 | 25 | 25.6 | 30 | 2.4
DHG0904L | 7.5 | L - Medium Static | 460/3/60 |  |  |  | 20.1 | 25 | 4.3 | 24.4 | 30 | 1.2 (1.0) | 21.3 | 25 | 25.6 | 30 | 2.4
DHG0904W | 7.5 | W - High Static | 460/3/60 |  |  |  | 21.9 | 25 | 4.3 | 26.2 | 30 | 1.2 (1.0) | 23.1 | 30 | 27.4 | 30 | 3.5
DHG1023D | 8.5 | D - Standard Static | 208/230/3/60 |  |  |  | 43.7/43.7 | 50/50 | 9.6/8.7 | 53.3/52.4 | 60/60 | 3.3/3.0 (2.4) | 47.0/46.7 | 60/60 | 56.6/55.4 | 60/60 | 2.4
DHG1023L | 8.5 | L - Medium Static | 208/230/3/60 |  |  |  | 46.6/46.6 | 60/60 | 9.6/8.7 | 56.2/55.3 | 70/60 | 3.3/3.0 (2.4) | 49.9/49.6 | 60/60 | 59.5/58.3 | 70/70 | 3.5
DHG1023W | 8.5 | W - High Static | 208/230/3/60 |  |  |  | 46.6/46.6 | 60/60 | 9.6/8.7 | 56.2/55.3 | 70/60 | 3.3/3.0 (2.4) | 49.9/49.6 | 60/60 | 59.5/58.3 | 70/70 | 3.5
DHG1024D | 8.5 | D - Standard Static | 460/3/60 |  |  |  | 21.5 | 25 | 4.3 | 25.8 | 30 | 1.2 (1.0) | 22.7 | 25 | 27 | 30 | 2.4
DHG1024L | 8.5 | L - Medium Static | 460/3/60 |  |  |  | 23.3 | 30 | 4.3 | 27.6 | 35 | 1.2 (1.0) | 24.5 | 30 | 28.8 | 35 | 3.5
DHG1024W | 8.5 | W - High Static | 460/3/60 |  |  |  | 23.3 | 30 | 4.3 | 27.6 | 35 | 1.2 (1.0) | 24.5 | 30 | 28.8 | 35 | 3.5
DHG1203D | 10 | D - Standard Static | 208/230/3/60 |  |  |  | 46.6/46.6 | 60/60 | 9.6/8.7 | 56.2/55.3 | 70/70 | 3.3/3.0 (2.4) | 49.9/49.6 | 60/60 | 59.5/58.3 | 70/70 | 2.4
DHG1203L | 10 | L - Medium Static | 208/230/3/60 |  |  |  | 49.5/49.5 | 60/60 | 9.6/8.7 | 59.1/58.2 | 70/70 | 3.3/3.0 (2.4) | 52.8/52.5 | 60/60 | 62.4/61.2 | 70/70 | 3.5
DHG1203W | 10 | W - High Static | 208/230/3/60 |  |  |  | 53.1/53.1 | 60/60 | 9.6/8.7 | 62.7/61.8 | 70/70 | 3.3/3.0 (2.4) | 56.4/56.1 | 70/70 | 66.0/64.8 | 80/80 | 5
DHG1204D | 10 | D - Standard Static | 460/3/60 |  |  |  | 24.4 | 30 | 4.3 | 28.7 | 35 | 1.2 (1.0) | 25.6 | 30 | 29.9 | 35 | 2.4
DHG1204L | 10 | L - Medium Static | 460/3/60 |  |  |  | 26.2 | 30 | 4.3 | 30.5 | 35 | 1.2 (1.0) | 27.4 | 35 | 31.7 | 35 | 3.5
DHG1204W | 10 | W - High Static | 460/3/60 |  |  |  | 29.6 | 40 | 4.3 | 33.9 | 45 | 1.2 (1.0) | 30.8 | 40 | 35.1 | 45 | 5
DHG1503D | 12.5 | D - Standard Static | 208/230/3/60 |  |  |  | 61.1/61.1 | 80/80 | 9.6/8.7 | 70.7/69.8 | 80/80 | 3.3/3.0 (2.4) | 64.4/64.1 | 80/80 | 74.0/72.8 | 90/90 | 3.5
DHG1503L | 12.5 | L - Medium Static | 208/230/3/60 |  |  |  | 61.1/61.1 | 80/80 | 9.6/8.7 | 70.7/69.8 | 80/80 | 3.3/3.0 (2.4) | 64.4/64.1 | 80/80 | 74.0/72.8 | 90/90 | 3.5
DHG1503W | 12.5 | W - High Static | 208/230/3/60 |  |  |  | 64.7/64.7 | 80/80 | 9.6/8.7 | 74.3/73.4 | 90/90 | 3.3/3.0 (2.4) | 68.0/67.7 | 80/80 | 77.6/76.4 | 90/90 | 5
DHG1504D | 12.5 | D - Standard Static | 460/3/60 |  |  |  | 30.6 | 35 | 4.3 | 34.9 | 40 | 1.2 (1.0) | 31.8 | 40 | 36.1 | 40 | 3.5
DHG1504L | 12.5 | L - Medium Static | 460/3/60 |  |  |  | 30.6 | 35 | 4.3 | 34.9 | 40 | 1.2 (1.0) | 31.8 | 40 | 36.1 | 40 | 3.5
DHG1504W | 12.5 | W - High Static | 460/3/60 |  |  |  | 34 | 40 | 4.3 | 38.3 | 45 | 1.2 (1.0) | 35.2 | 45 | 39.5 | 50 | 5
DSH0363D | 3 | D - Standard Static | 208/230/3/60 | 0 |  |  | 19.9/19.9 | 30/30 | 9.6/8.7 | 29.5/28.6 | 40/35 | 2.2/1.9 (1.7/1.5) | 22.1/21.8 | 30/30 | 31.7/30.5 | 40/40 | 0.75
DSH0363D | 3 | D - Standard Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 32.9/34.9 | 40/40 | 9.6/8.7 | 42.5/43.6 | 50/50 | 2.2/1.9 (1.7/1.5) | 35.1/36.8 | 40/40 | 44.7/45.5 | 50/50 | 0.75
DSH0363D | 3 | D - Standard Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 45.8/49.8 | 50/50 | 9.6/8.7 | 55.4/58.5 | 60/60 | 2.2/1.9 (1.7/1.5) | 48.0/51.7 | 50/60 | 57.6/60.4 | 60/70 | 0.75
DSH0363D | 3 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 58.9/65.0 | 60/70 | 9.6/8.7 | 68.5/73.7 | 70/80 | 2.2/1.9 (1.7/1.5) | 61.1/66.9 | 70/70 | 70.7/75.6 | 80/80 | 0.75
DSH0363W | 3 | W - High Static | 208/230/3/60 | 0 |  |  | 19.2/19.2 | 25/25 | 9.6/8.7 | 28.8/27.9 | 35/35 | 2.2/1.9 (1.7/1.5) | 21.4/21.1 | 30/30 | 31.0/29.8 | 40/35 | 1.2
DSH0363W | 3 | W - High Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 32.2/34.2 | 40/40 | 9.6/8.7 | 41.8/42.9 | 45/50 | 2.2/1.9 (1.7/1.5) | 34.4/36.1 | 40/40 | 44.0/44.8 | 50/50 | 1.2
DSH0363W | 3 | W - High Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 45.1/49.1 | 50/50 | 9.6/8.7 | 54.7/57.8 | 60/60 | 2.2/1.9 (1.7/1.5) | 47.3/51.0 | 50/60 | 56.9/59.7 | 60/60 | 1.2
DSH0363W | 3 | W - High Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 58.2/64.3 | 60/70 | 9.6/8.7 | 67.8/73.0 | 70/80 | 2.2/1.9 (1.7/1.5) | 60.4/66.2 | 70/70 | 70.0/74.9 | 80/80 | 1.2
DSH0364D | 3 | D - Standard Static | 460/3/60 | 0 |  |  | 9.1 | 15 | 4.3 | 13.4 | 15 | 0.9 (0.5) | 10 | 15 | 14.3 | 15 | 1.2
DSH0364D | 3 | D - Standard Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 16.6 | 20 | 4.3 | 20.9 | 25 | 0.9 (0.5) | 17.5 | 20 | 21.8 | 25 | 1.2
DSH0364D | 3 | D - Standard Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 24.1 | 25 | 4.3 | 28.4 | 30 | 0.9 (0.5) | 25 | 25 | 29.3 | 30 | 1.2
DSH0364D | 3 | D - Standard Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 31.6 | 35 | 4.3 | 35.9 | 40 | 0.9 (0.5) | 32.5 | 35 | 36.8 | 40 | 1.2
DSH0364W | 3 | W - High Static | 460/3/60 | 0 |  |  | 9.1 | 15 | 4.3 | 13.4 | 15 | 0.9 (0.5) | 10 | 15 | 14.3 | 15 | 1.2
DSH0364W | 3 | W - High Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 16.6 | 20 | 4.3 | 20.9 | 25 | 0.9 (0.5) | 17.5 | 20 | 21.8 | 25 | 1.2
DSH0364W | 3 | W - High Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 24.1 | 25 | 4.3 | 28.4 | 30 | 0.9 (0.5) | 25 | 25 | 29.3 | 30 | 1.2
DSH0364W | 3 | W - High Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 31.6 | 35 | 4.3 | 35.9 | 40 | 0.9 (0.5) | 32.5 | 35 | 36.8 | 40 | 1.2
DSH0483D | 4 | D - Standard Static | 208/230/3/60 | 0 |  |  | 23.5/23.5 | 35/35 | 9.6/8.7 | 33.1/32.2 | 45/40 | 2.2/1.9 (1.7/1.5) | 25.7/25.4 | 35/35 | 35.3/34.1 | 45/45 | 1
DSH0483D | 4 | D - Standard Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 36.5/38.5 | 45/45 | 9.6/8.7 | 46.1/47.2 | 50/50 | 2.2/1.9 (1.7/1.5) | 38.7/40.4 | 45/45 | 48.3/49.1 | 50/50 | 1
DSH0483D | 4 | D - Standard Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 49.5/53.5 | 50/60 | 9.6/8.7 | 59.1/62.2 | 60/70 | 2.2/1.9 (1.7/1.5) | 51.7/55.4 | 60/60 | 61.3/64.1 | 70/70 | 1
DSH0483D | 4 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 62.6/68.6 | 70/70 | 9.6/8.7 | 72.2/77.3 | 80/80 | 2.2/1.9 (1.7/1.5) | 64.8/70.5 | 70/80 | 74.4/79.2 | 80/80 | 1
DSH0483D | 4 | D - Standard Static | 208/230/3/60 | 20 | EH*D-3S20A | 41.5/47.9 | 75.4/83.3 | 80/90 | 9.6/8.7 | 85.0/92.0 | 90/100 | 2.2/1.9 (1.7/1.5) | 77.6/85.2 | 80/90 | 87.2/93.9 | 90/100 | 1
DSH0483W | 4 | W - High Static | 208/230/3/60 | 0 |  |  | 21.6/21.6 | 30/30 | 9.6/8.7 | 31.2/30.3 | 40/40 | 2.2/1.9 (1.7/1.5) | 23.8/23.5 | 35/35 | 33.4/32.2 | 45/40 | 1.2
DSH0483W | 4 | W - High Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 34.6/36.6 | 40/45 | 9.6/8.7 | 44.2/45.3 | 50/50 | 2.2/1.9 (1.7/1.5) | 36.8/38.5 | 45/45 | 46.4/47.2 | 50/50 | 1.2
DSH0483W | 4 | W - High Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 47.6/51.6 | 50/60 | 9.6/8.7 | 57.2/60.3 | 60/70 | 2.2/1.9 (1.7/1.5) | 49.8/53.5 | 50/60 | 59.4/62.2 | 60/70 | 1.2
DSH0483W | 4 | W - High Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 60.7/66.7 | 70/70 | 9.6/8.7 | 70.3/75.4 | 80/80 | 2.2/1.9 (1.7/1.5) | 62.9/68.6 | 70/70 | 72.5/77.3 | 80/80 | 1.2
DSH0483W | 4 | W - High Static | 208/230/3/60 | 20 | EH*D-3S20A | 41.5/47.9 | 73.5/81.4 | 80/90 | 9.6/8.7 | 83.1/90.1 | 90/100 | 2.2/1.9 (1.7/1.5) | 75.7/83.3 | 80/90 | 85.3/92.0 | 90/100 | 1.2
DSH0484D | 4 | D - Standard Static | 460/3/60 | 0 |  |  | 10.4 | 15 | 4.3 | 14.7 | 20 | 0.9 (0.5) | 11.3 | 15 | 15.6 | 20 | 1.2
DSH0484D | 4 | D - Standard Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 17.9 | 20 | 4.3 | 22.2 | 25 | 0.9 (0.5) | 18.8 | 20 | 23.1 | 25 | 1.2
DSH0484D | 4 | D - Standard Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 25.4 | 30 | 4.3 | 29.7 | 30 | 0.9 (0.5) | 26.3 | 30 | 30.6 | 35 | 1.2
DSH0484D | 4 | D - Standard Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 33 | 35 | 4.3 | 37.3 | 40 | 0.9 (0.5) | 33.9 | 35 | 38.2 | 40 | 1.2
DSH0484D | 4 | D - Standard Static | 460/3/60 | 20 | EH*D-4S20A | 24.1 | 40.5 | 45 | 4.3 | 44.8 | 45 | 0.9 (0.5) | 41.4 | 45 | 45.7 | 50 | 1.2
DSH0484W | 4 | W - High Static | 460/3/60 | 0 |  |  | 10.4 | 15 | 4.3 | 14.7 | 20 | 0.9 (0.5) | 11.3 | 15 | 15.6 | 20 | 1.2
DSH0484W | 4 | W - High Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 17.9 | 20 | 4.3 | 22.2 | 25 | 0.9 (0.5) | 18.8 | 20 | 23.1 | 25 | 1.2
DSH0484W | 4 | W - High Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 25.4 | 30 | 4.3 | 29.7 | 30 | 0.9 (0.5) | 26.3 | 30 | 30.6 | 35 | 1.2
DSH0484W | 4 | W - High Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 33 | 35 | 4.3 | 37.3 | 40 | 0.9 (0.5) | 33.9 | 35 | 38.2 | 40 | 1.2
DSH0484W | 4 | W - High Static | 460/3/60 | 20 | EH*D-4S20A | 24.1 | 40.5 | 45 | 4.3 | 44.8 | 45 | 0.9 (0.5) | 41.4 | 45 | 45.7 | 50 | 1.2
DSH0603D | 5 | D - Standard Static | 208/230/3/60 | 0 |  |  | 30.5/30.5 | 45/45 | 9.6/8.7 | 40.1/39.2 | 50/50 | 2.2/1.9 (1.7/1.5) | 32.7/32.4 | 45/45 | 42.3/41.1 | 50/50 | 1
DSH0603D | 5 | D - Standard Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 43.5/45.5 | 50/50 | 9.6/8.7 | 53.1/54.2 | 60/60 | 2.2/1.9 (1.7/1.5) | 45.7/47.4 | 50/60 | 55.3/56.1 | 60/70 | 1
DSH0603D | 5 | D - Standard Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 56.5/60.5 | 60/70 | 9.6/8.7 | 66.1/69.2 | 70/80 | 2.2/1.9 (1.7/1.5) | 58.7/62.4 | 70/70 | 68.3/71.1 | 70/80 | 1
DSH0603D | 5 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 69.6/75.6 | 70/80 | 9.6/8.7 | 79.2/84.3 | 80/90 | 2.2/1.9 (1.7/1.5) | 71.8/77.5 | 80/80 | 81.4/86.2 | 90/90 | 1
DSH0603D | 5 | D - Standard Static | 208/230/3/60 | 20 | EH*D-3S20A | 41.5/47.9 | 82.4/90.3 | 90/100 | 9.6/8.7 | 92.0/99.0 | 100/100 | 2.2/1.9 (1.7/1.5) | 84.6/92.2 | 90/100 | 94.2/101 | 100/110 | 1
DSH0603W | 5 | W - High Static | 208/230/3/60 | 0 |  |  | 31.3/31.3 | 45/45 | 9.6/8.7 | 40.9/40.0 | 50/50 | 2.2/1.9 (1.7/1.5) | 33.5/33.2 | 50/50 | 43.1/41.9 | 50/50 | 2.3
DSH0603W | 5 | W - High Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 44.3/46.3 | 50/60 | 9.6/8.7 | 53.9/55.0 | 60/60 | 2.2/1.9 (1.7/1.5) | 46.5/48.2 | 60/60 | 56.1/56.9 | 70/70 | 2.3
DSH0603W | 5 | W - High Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 57.3/61.3 | 60/70 | 9.6/8.7 | 66.9/70.0 | 70/80 | 2.2/1.9 (1.7/1.5) | 59.5/63.2 | 70/70 | 69.1/71.9 | 80/80 | 2.3
DSH0603W | 5 | W - High Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 70.4/76.4 | 80/80 | 9.6/8.7 | 80.0/85.1 | 80/90 | 2.2/1.9 (1.7/1.5) | 72.6/78.3 | 80/80 | 82.2/87.0 | 90/90 | 2.3
DSH0603W | 5 | W - High Static | 208/230/3/60 | 20 | EH*D-3S20A | 41.5/47.9 | 83.2/91.1 | 90/100 | 9.6/8.7 | 92.8/99.8 | 100/100 | 2.2/1.9 (1.7/1.5) | 85.4/93.0 | 90/100 | 95.0/102 | 100/110 | 2.3
DSH0604D | 5 | D - Standard Static | 460/3/60 | 0 |  |  | 13 | 20 | 4.3 | 17.3 | 20 | 0.9 (0.5) | 13.9 | 20 | 18.2 | 25 | 1.2
DSH0604D | 5 | D - Standard Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 20.5 | 25 | 4.3 | 24.8 | 30 | 0.9 (0.5) | 21.4 | 25 | 25.7 | 30 | 1.2
DSH0604D | 5 | D - Standard Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 28 | 30 | 4.3 | 32.3 | 35 | 0.9 (0.5) | 28.9 | 30 | 33.2 | 35 | 1.2
DSH0604D | 5 | D - Standard Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 35.5 | 40 | 4.3 | 39.8 | 40 | 0.9 (0.5) | 36.4 | 40 | 40.7 | 45 | 1.2
DSH0604D | 5 | D - Standard Static | 460/3/60 | 20 | EH*D-4S20A | 24.1 | 43 | 45 | 4.3 | 47.3 | 50 | 0.9 (0.5) | 43.9 | 45 | 48.2 | 50 | 1.2
DSH0604W | 5 | W - High Static | 460/3/60 | 0 |  |  | 15 | 20 | 4.3 | 19.3 | 25 | 0.9 (0.5) | 15.9 | 20 | 20.2 | 25 | 2.3
DSH0604W | 5 | W - High Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 22.5 | 25 | 4.3 | 26.8 | 30 | 0.9 (0.5) | 23.4 | 25 | 27.7 | 30 | 2.3
DSH0604W | 5 | W - High Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 30 | 30 | 4.3 | 34.3 | 35 | 0.9 (0.5) | 30.9 | 35 | 35.2 | 40 | 2.3
DSH0604W | 5 | W - High Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 37.5 | 40 | 4.3 | 41.8 | 45 | 0.9 (0.5) | 38.4 | 40 | 42.7 | 45 | 2.3
DSH0604W | 5 | W - High Static | 460/3/60 | 20 | EH*D-4S20A | 24.1 | 45 | 50 | 4.3 | 49.3 | 50 | 0.9 (0.5) | 45.9 | 50 | 50.2 | 60 | 2.3
DSH0723D | 6 | D - Standard Static | 208/230/3/60 | 0 |  |  | 27.9/27.9 | 40/40 | 9.6/8.7 | 37.5/36.6 | 50/50 | 2.2/1.9 (1.7/1.5) | 30.1/29.8 | 45/45 | 39.7/38.5 | 50/50 | 1.2
DSH0723D | 6 | D - Standard Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 40.9/42.9 | 50/50 | 9.6/8.7 | 50.5/51.6 | 60/60 | 2.2/1.9 (1.7/1.5) | 43.1/44.8 | 50/50 | 52.7/53.5 | 60/60 | 1.2
DSH0723D | 6 | D - Standard Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 53.8/57.8 | 60/60 | 9.6/8.7 | 63.4/66.5 | 70/70 | 2.2/1.9 (1.7/1.5) | 56.0/59.7 | 60/60 | 65.6/68.4 | 70/70 | 1.2
DSH0723D | 6 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 67.0/73.0 | 70/80 | 9.6/8.7 | 76.6/81.7 | 80/90 | 2.2/1.9 (1.7/1.5) | 69.2/74.9 | 70/80 | 78.8/83.6 | 80/90 | 1.2
DSH0723D | 6 | D - Standard Static | 208/230/3/60 | 20 | EH*D-3S20A | 41.5/47.9 | 79.7/87.7 | 80/90 | 9.6/8.7 | 89.3/96.4 | 90/100 | 2.2/1.9 (1.7/1.5) | 81.9/89.6 | 90/90 | 91.5/98.3 | 100/100 | 1.2
DSH0723D | 6 | D - Standard Static | 208/230/3/60 | 30 | EH*D-3S30A | 62.5/72.2 | 106/118 | 110/125 | 9.6/8.7 | 116/127 | 125/150 | 2.2/1.9 (1.7/1.5) | 108/120 | 110/125 | 118/129 | 125/150 | 1.2
DSH0723W | 6 | W - High Static | 208/230/3/60 | 0 |  |  | 30.6/30.6 | 45/45 | 9.6/8.7 | 40.2/39.3 | 50/50 | 2.2/1.9 (1.7/1.5) | 32.8/32.5 | 45/45 | 42.4/41.2 | 50/50 | 2.3
DSH0723W | 6 | W - High Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 43.6/45.6 | 50/50 | 9.6/8.7 | 53.2/54.3 | 60/60 | 2.2/1.9 (1.7/1.5) | 45.8/47.5 | 50/60 | 55.4/56.2 | 60/60 | 2.3
DSH0723W | 6 | W - High Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 56.5/60.5 | 60/70 | 9.6/8.7 | 66.1/69.2 | 70/70 | 2.2/1.9 (1.7/1.5) | 58.7/62.4 | 60/70 | 68.3/71.1 | 70/80 | 2.3
DSH0723W | 6 | W - High Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 69.7/75.7 | 70/80 | 9.6/8.7 | 79.3/84.4 | 80/90 | 2.2/1.9 (1.7/1.5) | 71.9/77.6 | 80/80 | 81.5/86.3 | 90/90 | 2.3
DSH0723W | 6 | W - High Static | 208/230/3/60 | 20 | EH*D-3S20A | 41.5/47.9 | 82.4/90.4 | 90/100 | 9.6/8.7 | 92.0/99.1 | 100/100 | 2.2/1.9 (1.7/1.5) | 84.6/92.3 | 90/100 | 94.2/101 | 100/110 | 2.3
DSH0723W | 6 | W - High Static | 208/230/3/60 | 30 | EH*D-3S30B | 62.5/72.2 | 109/121 | 110/125 | 9.6/8.7 | 118/129 | 125/150 | 2.2/1.9 (1.7/1.5) | 111/123 | 125/125 | 121/131 | 125/150 | 2.3
DSH0724D | 6 | D - Standard Static | 460/3/60 | 0 |  |  | 12.7 | 15 | 4.3 | 17 | 20 | 0.9 (0.5) | 13.6 | 20 | 17.9 | 20 | 1.2
DSH0724D | 6 | D - Standard Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 20.2 | 25 | 4.3 | 24.5 | 30 | 0.9 (0.5) | 21.1 | 25 | 25.4 | 30 | 1.2
DSH0724D | 6 | D - Standard Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 27.7 | 30 | 4.3 | 32 | 35 | 0.9 (0.5) | 28.6 | 30 | 32.9 | 35 | 1.2
DSH0724D | 6 | D - Standard Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 35.3 | 40 | 4.3 | 39.6 | 40 | 0.9 (0.5) | 36.2 | 40 | 40.5 | 45 | 1.2
DSH0724D | 6 | D - Standard Static | 460/3/60 | 20 | EH*D-4S20A | 24.1 | 42.8 | 45 | 4.3 | 47.1 | 50 | 0.9 (0.5) | 43.7 | 45 | 48 | 50 | 1.2
DSH0724D | 6 | D - Standard Static | 460/3/60 | 30 | EH*D-4S30A | 36.1 | 57.8 | 60 | 4.3 | 62.1 | 70 | 0.9 (0.5) | 58.7 | 60 | 63 | 70 | 1.2
DSH0724W | 6 | W - High Static | 460/3/60 | 0 |  |  | 14.7 | 20 | 4.3 | 19 | 25 | 0.9 (0.5) | 15.6 | 20 | 19.9 | 25 | 2.3
DSH0724W | 6 | W - High Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 22.2 | 25 | 4.3 | 26.5 | 30 | 0.9 (0.5) | 23.1 | 25 | 27.4 | 30 | 2.3
DSH0724W | 6 | W - High Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 29.7 | 30 | 4.3 | 34 | 35 | 0.9 (0.5) | 30.6 | 35 | 34.9 | 35 | 2.3
DSH0724W | 6 | W - High Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 37.3 | 40 | 4.3 | 41.6 | 45 | 0.9 (0.5) | 38.2 | 40 | 42.5 | 45 | 2.3
DSH0724W | 6 | W - High Static | 460/3/60 | 20 | EH*D-4S20A | 24.1 | 44.8 | 45 | 4.3 | 49.1 | 50 | 0.9 (0.5) | 45.7 | 50 | 50 | 50 | 2.3
DSH0724W | 6 | W - High Static | 460/3/60 | 30 | EH*D-4S30B | 36.1 | 59.8 | 60 | 4.3 | 64.1 | 70 | 0.9 (0.5) | 60.7 | 70 | 65 | 70 | 2.3
DSH0903D | 7.5 | D - Standard Static | 208/230/3/60 | 0 |  |  | 39.4/39.4 | 50/50 | 9.6/8.7 | 49.0/48.1 | 60/60 | 3.3/3.0 (2.4) | 42.7/42.4 | 50/50 | 52.3/51.1 | 60/60 | 2.4
DSH0903D | 7.5 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 78.5/84.5 | 80/90 | 9.6/8.7 | 88.1/93.2 | 90/100 | 3.3/3.0 (2.4) | 81.8/87.5 | 90/90 | 91.4/96.2 | 100/100 | 2.4
DSH0903D | 7.5 | D - Standard Static | 208/230/3/60 | 30 | EH*D-3M30 | 62.5/72.2 | 118/130 | 125/150 | 9.6/8.7 | 127/138 | 150/150 | 3.3/3.0 (2.4) | 121/133 | 125/150 | 130/141 | 150/150 | 2.4
DSH0903D | 7.5 | D - Standard Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 157/175 | 175/175 | 9.6/8.7 | 166/183 | 175/200 | 3.3/3.0 (2.4) | 160/178 | 175/200 | 170/186 | 175/200 | 2.4
DSH0903W | 7.5 | W - High Static | 208/230/3/60 | 0 |  |  | 42.3/42.3 | 50/50 | 9.6/8.7 | 51.9/51.0 | 60/60 | 3.3/3.0 (2.4) | 45.6/45.3 | 50/50 | 55.2/54.0 | 60/60 | 3.5
DSH0903W | 7.5 | W - High Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 81.4/87.4 | 90/90 | 9.6/8.7 | 91.0/96.1 | 100/100 | 3.3/3.0 (2.4) | 84.7/90.4 | 90/100 | 94.3/99.1 | 100/100 | 3.5
DSH0903W | 7.5 | W - High Static | 208/230/3/60 | 30 | EH*D-3M30 | 62.5/72.2 | 120/132 | 125/150 | 9.6/8.7 | 130/141 | 150/150 | 3.3/3.0 (2.4) | 124/135 | 125/150 | 133/144 | 150/150 | 3.5
DSH0903W | 7.5 | W - High Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 160/178 | 175/200 | 9.6/8.7 | 169/186 | 175/200 | 3.3/3.0 (2.4) | 163/181 | 175/200 | 172/189 | 175/200 | 3.5
DSH0904D | 7.5 | D - Standard Static | 460/3/60 | 0 |  |  | 20.1 | 25 | 4.3 | 24.4 | 30 | 1.2 (1.0) | 21.3 | 25 | 25.6 | 30 | 2.4
DSH0904D | 7.5 | D - Standard Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 42.6 | 45 | 4.3 | 46.9 | 50 | 1.2 (1.0) | 43.8 | 45 | 48.1 | 50 | 2.4
DSH0904D | 7.5 | D - Standard Static | 460/3/60 | 30 | EH*D-4M30 | 36.1 | 65.2 | 70 | 4.3 | 69.5 | 70 | 1.2 (1.0) | 66.4 | 70 | 70.7 | 80 | 2.4
DSH0904D | 7.5 | D - Standard Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 87.7 | 90 | 4.3 | 92 | 100 | 1.2 (1.0) | 88.9 | 90 | 93.2 | 100 | 2.4
DSH0904W | 7.5 | W - High Static | 460/3/60 | 0 |  |  | 21.9 | 25 | 4.3 | 26.2 | 30 | 1.2 (1.0) | 23.1 | 30 | 27.4 | 30 | 3.5
DSH0904W | 7.5 | W - High Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 44.4 | 45 | 4.3 | 48.7 | 50 | 1.2 (1.0) | 45.6 | 50 | 49.9 | 50 | 3.5
DSH0904W | 7.5 | W - High Static | 460/3/60 | 30 | EH*D-4M30 | 36.1 | 67 | 70 | 4.3 | 71.3 | 80 | 1.2 (1.0) | 68.2 | 70 | 72.5 | 80 | 3.5
DSH0904W | 7.5 | W - High Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 89.5 | 90 | 4.3 | 93.8 | 100 | 1.2 (1.0) | 90.7 | 100 | 95 | 100 | 3.5
DSH1023D | 8.5 | D - Standard Static | 208/230/3/60 | 0 |  |  | 43.7/43.7 | 50/50 | 9.6/8.7 | 53.3/52.4 | 60/60 | 3.3/3.0 (2.4) | 47.0/46.7 | 60/60 | 56.6/55.4 | 60/60 | 2.4
DSH1023D | 8.5 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 82.8/88.8 | 90/90 | 9.6/8.7 | 92.4/97.5 | 100/100 | 3.3/3.0 (2.4) | 86.1/91.8 | 90/100 | 95.7/100 | 100/110 | 2.4
DSH1023D | 8.5 | D - Standard Static | 208/230/3/60 | 30 | EH*D-3M30 | 62.5/72.2 | 122/134 | 125/150 | 9.6/8.7 | 131/143 | 150/150 | 3.3/3.0 (2.4) | 125/137 | 150/150 | 135/146 | 150/150 | 2.4
DSH1023D | 8.5 | D - Standard Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 161/179 | 175/200 | 9.6/8.7 | 171/188 | 175/200 | 3.3/3.0 (2.4) | 164/182 | 175/200 | 174/191 | 175/200 | 2.4
DSH1023W | 8.5 | W - High Static | 208/230/3/60 | 0 |  |  | 46.6/46.6 | 60/60 | 9.6/8.7 | 56.2/55.3 | 70/60 | 3.3/3.0 (2.4) | 49.9/49.6 | 60/60 | 59.5/58.3 | 70/70 | 3.5
DSH1023W | 8.5 | W - High Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 85.7/91.7 | 90/100 | 9.6/8.7 | 95.3/100 | 100/110 | 3.3/3.0 (2.4) | 89.0/94.7 | 90/100 | 98.6/103 | 100/110 | 3.5
DSH1023W | 8.5 | W - High Static | 208/230/3/60 | 30 | EH*D-3M30 | 62.5/72.2 | 125/137 | 125/150 | 9.6/8.7 | 134/145 | 150/150 | 3.3/3.0 (2.4) | 128/140 | 150/150 | 138/148 | 150/150 | 3.5
DSH1023W | 8.5 | W - High Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 164/182 | 175/200 | 9.6/8.7 | 173/191 | 175/200 | 3.3/3.0 (2.4) | 167/185 | 175/200 | 177/194 | 200/200 | 3.5
DSH1024D | 8.5 | D - Standard Static | 460/3/60 | 0 |  |  | 21.5 | 25 | 4.3 | 25.8 | 30 | 1.2 (1.0) | 22.7 | 25 | 27 | 30 | 2.4
DSH1024D | 8.5 | D - Standard Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 44.1 | 45 | 4.3 | 48.4 | 50 | 1.2 (1.0) | 45.3 | 50 | 49.6 | 50 | 2.4
DSH1024D | 8.5 | D - Standard Static | 460/3/60 | 30 | EH*D-4M30 | 36.1 | 66.6 | 70 | 4.3 | 70.9 | 80 | 1.2 (1.0) | 67.8 | 70 | 72.1 | 80 | 2.4
DSH1024D | 8.5 | D - Standard Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 89.2 | 90 | 4.3 | 93.5 | 100 | 1.2 (1.0) | 90.4 | 100 | 94.7 | 100 | 2.4
DSH1024W | 8.5 | W - High Static | 460/3/60 | 0 |  |  | 23.3 | 30 | 4.3 | 27.6 | 35 | 1.2 (1.0) | 24.5 | 30 | 28.8 | 35 | 3.5
DSH1024W | 8.5 | W - High Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 45.9 | 50 | 4.3 | 50.2 | 60 | 1.2 (1.0) | 47.1 | 50 | 51.4 | 60 | 3.5
DSH1024W | 8.5 | W - High Static | 460/3/60 | 30 | EH*D-4M30 | 36.1 | 68.4 | 70 | 4.3 | 72.7 | 80 | 1.2 (1.0) | 69.6 | 70 | 73.9 | 80 | 3.5
DSH1024W | 8.5 | W - High Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 91 | 100 | 4.3 | 95.3 | 100 | 1.2 (1.0) | 92.2 | 100 | 96.5 | 100 | 3.5
DSH1203D | 10 | D - Standard Static | 208/230/3/60 | 0 |  |  | 55.2/55.2 | 70/70 | 9.6/8.7 | 64.8/63.9 | 80/80 | 3.3/3.0 (2.4) | 58.5/58.2 | 70/70 | 68.1/66.9 | 80/80 | 3.5
DSH1203D | 10 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 94.3/100 | 100/110 | 9.6/8.7 | 104/109 | 110/110 | 3.3/3.0 (2.4) | 97.6/103 | 100/110 | 107/112 | 110/125 | 3.5
DSH1203D | 10 | D - Standard Static | 208/230/3/60 | 30 | EH*D-3M30 | 62.5/72.2 | 133/145 | 150/150 | 9.6/8.7 | 143/154 | 150/175 | 3.3/3.0 (2.4) | 137/148 | 150/150 | 146/157 | 150/175 | 3.5
DSH1203D | 10 | D - Standard Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 172/190 | 175/200 | 9.6/8.7 | 182/199 | 200/200 | 3.3/3.0 (2.4) | 176/193 | 200/200 | 185/202 | 200/225 | 3.5
DSH1203W | 10 | W - High Static | 208/230/3/60 | 0 |  |  | 58.8/58.8 | 70/70 | 9.6/8.7 | 68.4/67.5 | 80/80 | 3.3/3.0 (2.4) | 62.1/61.8 | 70/70 | 71.7/70.5 | 80/80 | 5
DSH1203W | 10 | W - High Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 97.9/104 | 100/110 | 9.6/8.7 | 107/113 | 110/125 | 3.3/3.0 (2.4) | 101/107 | 110/110 | 111/116 | 125/125 | 5
DSH1203W | 10 | W - High Static | 208/230/3/60 | 30 | EH*D-3M30 | 62.5/72.2 | 137/149 | 150/150 | 9.6/8.7 | 147/158 | 150/175 | 3.3/3.0 (2.4) | 140/152 | 150/175 | 150/161 | 150/175 | 5
DSH1203W | 10 | W - High Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 176/194 | 200/200 | 9.6/8.7 | 186/203 | 200/225 | 3.3/3.0 (2.4) | 179/197 | 200/200 | 189/206 | 200/225 | 5
DSH1204D | 10 | D - Standard Static | 460/3/60 | 0 |  |  | 27.3 | 30 | 4.3 | 31.6 | 35 | 1.2 (1.0) | 28.5 | 35 | 32.8 | 40 | 3.5
DSH1204D | 10 | D - Standard Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 49.8 | 50 | 4.3 | 54.1 | 60 | 1.2 (1.0) | 51 | 60 | 55.3 | 60 | 3.5
DSH1204D | 10 | D - Standard Static | 460/3/60 | 30 | EH*D-4M30 | 36.1 | 72.4 | 80 | 4.3 | 76.7 | 80 | 1.2 (1.0) | 73.6 | 80 | 77.9 | 80 | 3.5
DSH1204D | 10 | D - Standard Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 94.9 | 100 | 4.3 | 99.2 | 100 | 1.2 (1.0) | 96.1 | 100 | 100 | 110 | 3.5
DSH1204W | 10 | W - High Static | 460/3/60 | 0 |  |  | 30.7 | 40 | 4.3 | 35 | 45 | 1.2 (1.0) | 31.9 | 40 | 36.2 | 45 | 5
DSH1204W | 10 | W - High Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 53.2 | 60 | 4.3 | 57.5 | 60 | 1.2 (1.0) | 54.4 | 60 | 58.7 | 60 | 5
DSH1204W | 10 | W - High Static | 460/3/60 | 30 | EH*D-4M30 | 36.1 | 75.8 | 80 | 4.3 | 80.1 | 90 | 1.2 (1.0) | 77 | 80 | 81.3 | 90 | 5
DSH1204W | 10 | W - High Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 98.3 | 100 | 4.3 | 103 | 110 | 1.2 (1.0) | 99.5 | 100 | 104 | 110 | 5
DSH1503D | 12.5 | D - Standard Static | 208/230/3/60 | 0 |  |  | 65.1/65.1 | 80/80 | 9.6/8.7 | 74.7/73.8 | 90/90 | 3.3/3.0 (2.4) | 68.4/68.1 | 80/80 | 78.0/76.8 | 90/90 | 3.5
DSH1503D | 12.5 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 104/110 | 110/125 | 9.6/8.7 | 114/119 | 125/125 | 3.3/3.0 (2.4) | 108/113 | 110/125 | 117/122 | 125/125 | 3.5
DSH1503D | 12.5 | D - Standard Static | 208/230/3/60 | 30 | EH*D-3M30 | 60.0/69.3 | 140/152 | 150/175 | 9.6/8.7 | 150/160 | 150/175 | 3.3/3.0 (2.4) | 143/155 | 150/175 | 153/163 | 175/175 | 3.5
DSH1503D | 12.5 | D - Standard Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 182/200 | 200/225 | 9.6/8.7 | 192/209 | 200/225 | 3.3/3.0 (2.4) | 186/203 | 200/225 | 195/212 | 200/225 | 3.5
DSH1503D | 12.5 | D - Standard Static | 208/230/3/60 | 60 | EH*D-3M60 | 120/139 | 215/204 | 225/225 | 9.6/8.7 | 225/212 | 225/225 | 3.3/3.0 (2.4) | 219/207 | 225/225 | 228/215 | 250/225 | 3.5
DSH1503W | 12.5 | W - High Static | 208/230/3/60 | 0 |  |  | 68.7/68.7 | 90/90 | 9.6/8.7 | 78.3/77.4 | 100/90 | 3.3/3.0 (2.4) | 72.0/71.7 | 90/90 | 81.6/80.4 | 100/100 | 5
DSH1503W | 12.5 | W - High Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 108/114 | 110/125 | 9.6/8.7 | 117/123 | 125/125 | 3.3/3.0 (2.4) | 111/117 | 125/125 | 121/126 | 125/150 | 5
DSH1503W | 12.5 | W - High Static | 208/230/3/60 | 30 | EH*D-3M30 | 60.0/69.3 | 144/155 | 150/175 | 9.6/8.7 | 153/164 | 175/175 | 3.3/3.0 (2.4) | 147/158 | 150/175 | 157/167 | 175/175 | 5
DSH1503W | 12.5 | W - High Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 186/204 | 200/225 | 9.6/8.7 | 196/213 | 200/225 | 3.3/3.0 (2.4) | 189/207 | 200/225 | 199/216 | 200/225 | 5
DSH1503W | 12.5 | W - High Static | 208/230/3/60 | 60 | EH*D-3M60 | 120/139 | 219/207 | 225/225 | 9.6/8.7 | 228/216 | 250/225 | 3.3/3.0 (2.4) | 222/210 | 225/225 | 232/219 | 250/225 | 5
DSH1504D | 12.5 | D - Standard Static | 460/3/60 | 0 |  |  | 31.6 | 40 | 4.3 | 35.9 | 45 | 1.2 (1.0) | 32.8 | 40 | 37.1 | 45 | 3.5
DSH1504D | 12.5 | D - Standard Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 54.2 | 60 | 4.3 | 58.5 | 60 | 1.2 (1.0) | 55.4 | 60 | 59.7 | 60 | 3.5
DSH1504D | 12.5 | D - Standard Static | 460/3/60 | 30 | EH*D-4M30 | 34.6 | 74.9 | 80 | 4.3 | 79.2 | 80 | 1.2 (1.0) | 76.1 | 80 | 80.4 | 90 | 3.5
DSH1504D | 12.5 | D - Standard Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 99.3 | 100 | 4.3 | 104 | 110 | 1.2 (1.0) | 100 | 110 | 105 | 110 | 3.5
DSH1504D | 12.5 | D - Standard Static | 460/3/60 | 60 | EH*D-4M60 | 69.3 | 101 | 110 | 4.3 | 105 | 110 | 1.2 (1.0) | 102 | 110 | 106 | 110 | 3.5
DSH1504W | 12.5 | W - High Static | 460/3/60 | 0 |  |  | 35 | 45 | 4.3 | 39.3 | 50 | 1.2 (1.0) | 36.2 | 45 | 40.5 | 50 | 5
DSH1504W | 12.5 | W - High Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 57.6 | 60 | 4.3 | 61.9 | 70 | 1.2 (1.0) | 58.8 | 60 | 63.1 | 70 | 5
DSH1504W | 12.5 | W - High Static | 460/3/60 | 30 | EH*D-4M30 | 34.6 | 78.3 | 80 | 4.3 | 82.6 | 90 | 1.2 (1.0) | 79.5 | 80 | 83.8 | 90 | 5
DSH1504W | 12.5 | W - High Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 103 | 110 | 4.3 | 107 | 110 | 1.2 (1.0) | 104 | 110 | 108 | 110 | 5
DSH1504W | 12.5 | W - High Static | 460/3/60 | 60 | EH*D-4M60 | 69.3 | 104 | 110 | 4.3 | 109 | 110 | 1.2 (1.0) | 105 | 110 | 110 | 110 | 5
DSH1803D | 15 | D - Standard Static | 208/230/3/60 | 0 |  |  | 88.9/88.9 | 110/110 | 9.6/8.7 | 98.5/97.6 | 110/110 | 4.8 | 93.7/93.7 | 110/110 | 103/102 | 125/125 | 3.5
DSH1803D | 15 | D - Standard Static | 208/230/3/60 | 30 | EH**-3L30A | 60.0/69.3 | 164/176 | 175/200 | 9.6/8.7 | 174/184 | 175/200 | 4.8 | 169/180 | 175/200 | 178/189 | 200/200 | 3.5
DSH1803D | 15 | D - Standard Static | 208/230/3/60 | 45 | EH**-3L45A | 90.1/104 | 201/219 | 225/225 | 9.6/8.7 | 211/228 | 225/250 | 4.8 | 206/224 | 225/225 | 216/232 | 225/250 | 3.5
DSH1803D | 15 | D - Standard Static | 208/230/3/60 | 60 | EH**-3L60A | 120/139 | 239/227 | 250/250 | 9.6/8.7 | 249/236 | 250/250 | 4.8 | 244/232 | 250/250 | 253/241 | 300/250 | 3.5
DSH1803W | 15 | W - High Static | 208/230/3/60 | 0 |  |  | 96.1/96.1 | 110/110 | 9.6/8.7 | 106/105 | 125/125 | 4.8 | 101/101 | 125/125 | 111/110 | 125/125 | 5
DSH1803W | 15 | W - High Static | 208/230/3/60 | 30 | EH**-3L30A | 60.0/69.3 | 171/183 | 175/200 | 9.6/8.7 | 181/191 | 200/200 | 4.8 | 176/188 | 200/200 | 186/196 | 200/200 | 5
DSH1803W | 15 | W - High Static | 208/230/3/60 | 45 | EH**-3L45A | 90.1/104 | 209/226 | 225/250 | 9.6/8.7 | 218/235 | 225/250 | 4.8 | 213/231 | 225/250 | 223/240 | 225/250 | 5
DSH1803W | 15 | W - High Static | 208/230/3/60 | 60 | EH**-3L60A | 120/139 | 246/235 | 250/250 | 9.6/8.7 | 256/243 | 300/250 | 4.8 | 251/239 | 300/250 | 261/248 | 300/250 | 5
DSH1804D | 15 | D - Standard Static | 460/3/60 | 0 |  |  | 44.5 | 50 | 4.3 | 48.8 | 50 | 2.4 | 46.9 | 50 | 51.2 | 60 | 3.5
DSH1804D | 15 | D - Standard Static | 460/3/60 | 30 | EH**-4L30A | 34.6 | 87.8 | 90 | 4.3 | 92.1 | 100 | 2.4 | 90.2 | 100 | 94.5 | 100 | 3.5
DSH1804D | 15 | D - Standard Static | 460/3/60 | 45 | EH**-4L45A | 52 | 109 | 110 | 4.3 | 114 | 125 | 2.4 | 112 | 125 | 116 | 125 | 3.5
DSH1804D | 15 | D - Standard Static | 460/3/60 | 60 | EH**-4L60A | 69.3 | 114 | 125 | 4.3 | 118 | 125 | 2.4 | 116 | 125 | 120 | 125 | 3.5
DSH1804W | 15 | W - High Static | 460/3/60 | 0 |  |  | 51.3 | 60 | 4.3 | 55.6 | 60 | 2.4 | 53.7 | 60 | 58 | 60 | 5
DSH1804W | 15 | W - High Static | 460/3/60 | 30 | EH**-4L30A | 34.6 | 94.6 | 100 | 4.3 | 98.9 | 100 | 2.4 | 97 | 100 | 101 | 110 | 5
DSH1804W | 15 | W - High Static | 460/3/60 | 45 | EH**-4L45A | 52 | 116 | 125 | 4.3 | 121 | 125 | 2.4 | 119 | 125 | 123 | 125 | 5
DSH1804W | 15 | W - High Static | 460/3/60 | 60 | EH**-4L60A | 69.3 | 121 | 125 | 4.3 | 125 | 125 | 2.4 | 123 | 125 | 127 | 150 | 5
DSH2403D | 20 | D - Standard Static | 208/230/3/60 | 0 |  |  | 98.7/98.7 | 125/125 | 9.6/8.7 | 108/107 | 125/125 | 4.8 | 103/103 | 125/125 | 113/112 | 125/125 | 3.5
DSH2403D | 20 | D - Standard Static | 208/230/3/60 | 30 | EH**-3L30A | 60.0/69.3 | 174/185 | 175/200 | 9.6/8.7 | 183/194 | 200/200 | 4.8 | 179/190 | 200/200 | 188/199 | 200/200 | 3.5
DSH2403D | 20 | D - Standard Static | 208/230/3/60 | 45 | EH**-3L45A | 90.1/104 | 211/229 | 225/250 | 9.6/8.7 | 221/237 | 225/250 | 4.8 | 216/233 | 225/250 | 226/242 | 250/250 | 3.5
DSH2403D | 20 | D - Standard Static | 208/230/3/60 | 60 | EH**-3L60A | 120/139 | 249/237 | 250/250 | 9.6/8.7 | 258/246 | 300/250 | 4.8 | 254/242 | 300/250 | 263/251 | 300/300 | 3.5
DSH2403D | 20 | D - Standard Static | 208/230/3/60 | 75 | EH**-3L75A | 150/173 | 249/272 | 250/300 | 9.6/8.7 | 258/281 | 300/300 | 4.8 | 254/277 | 300/300 | 263/285 | 300/300 | 3.5
DSH2403W | 20 | W - High Static | 208/230/3/60 | 0 |  |  | 106/106 | 125/125 | 9.6/8.7 | 115/115 | 125/125 | 4.8 | 111/111 | 125/125 | 120/119 | 125/125 | 5
DSH2403W | 20 | W - High Static | 208/230/3/60 | 30 | EH**-3L30A | 60.0/69.3 | 181/192 | 200/200 | 9.6/8.7 | 191/201 | 200/225 | 4.8 | 186/197 | 200/200 | 195/206 | 200/225 | 5
DSH2403W | 20 | W - High Static | 208/230/3/60 | 45 | EH**-3L45A | 90.1/104 | 218/236 | 225/250 | 9.6/8.7 | 228/244 | 250/250 | 4.8 | 223/241 | 225/250 | 233/249 | 250/250 | 5
DSH2403W | 20 | W - High Static | 208/230/3/60 | 60 | EH**-3L60A | 120/139 | 256/244 | 300/250 | 9.6/8.7 | 266/253 | 300/300 | 4.8 | 261/249 | 300/250 | 270/258 | 300/300 | 5
DSH2403W | 20 | W - High Static | 208/230/3/60 | 75 | EH**-3L75A | 150/173 | 256/279 | 300/300 | 9.6/8.7 | 266/288 | 300/300 | 4.8 | 261/284 | 300/300 | 270/293 | 300/300 | 5
DSH2404D | 20 | D - Standard Static | 460/3/60 | 0 |  |  | 50.8 | 60 | 4.3 | 55.1 | 60 | 2.4 | 53.2 | 60 | 57.5 | 70 | 3.5
DSH2404D | 20 | D - Standard Static | 460/3/60 | 30 | EH**-4L30A | 34.6 | 94.1 | 100 | 4.3 | 98.4 | 100 | 2.4 | 96.5 | 100 | 101 | 110 | 3.5
DSH2404D | 20 | D - Standard Static | 460/3/60 | 45 | EH**-4L45A | 52 | 116 | 125 | 4.3 | 120 | 125 | 2.4 | 118 | 125 | 122 | 125 | 3.5
DSH2404D | 20 | D - Standard Static | 460/3/60 | 60 | EH**-4L60A | 69.3 | 120 | 125 | 4.3 | 124 | 125 | 2.4 | 122 | 125 | 127 | 150 | 3.5
DSH2404D | 20 | D - Standard Static | 460/3/60 | 75 | EH**-4L75A | 86.6 | 137 | 150 | 4.3 | 142 | 150 | 2.4 | 140 | 150 | 144 | 150 | 3.5
DSH2404W | 20 | W - High Static | 460/3/60 | 0 |  |  | 57.6 | 70 | 4.3 | 61.9 | 70 | 2.4 | 60 | 70 | 64.3 | 70 | 5
DSH2404W | 20 | W - High Static | 460/3/60 | 30 | EH**-4L30A | 34.6 | 101 | 110 | 4.3 | 105 | 110 | 2.4 | 103 | 110 | 108 | 110 | 5
DSH2404W | 20 | W - High Static | 460/3/60 | 45 | EH**-4L45A | 52 | 123 | 125 | 4.3 | 127 | 150 | 2.4 | 125 | 125 | 129 | 150 | 5
DSH2404W | 20 | W - High Static | 460/3/60 | 60 | EH**-4L60A | 69.3 | 127 | 150 | 4.3 | 131 | 150 | 2.4 | 129 | 150 | 134 | 150 | 5
DSH2404W | 20 | W - High Static | 460/3/60 | 75 | EH**-4L75A | 86.6 | 144 | 150 | 4.3 | 149 | 150 | 2.4 | 147 | 150 | 151 | 175 | 5
DHH0363D | 3 | D - Standard Static | 208/230/3/60 | 0 |  |  | 18.1/18.1 | 25/25 | 9.6/8.7 | 27.7/26.8 | 35/35 | 2.2/1.9 (1.7/1.5) | 20.3/20.0 | 25/25 | 29.9/28.7 | 35/35 | 0.75
DHH0363D | 3 | D - Standard Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 31.1/33.1 | 35/35 | 9.6/8.7 | 40.7/41.8 | 45/45 | 2.2/1.9 (1.7/1.5) | 33.3/35.0 | 35/40 | 42.9/43.7 | 45/45 | 0.75
DHH0363D | 3 | D - Standard Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 44.0/48.0 | 45/50 | 9.6/8.7 | 53.6/56.7 | 60/60 | 2.2/1.9 (1.7/1.5) | 46.2/49.9 | 50/50 | 55.8/58.6 | 60/60 | 0.75
DHH0363D | 3 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 57.2/63.2 | 60/70 | 9.6/8.7 | 66.8/71.9 | 70/80 | 2.2/1.9 (1.7/1.5) | 59.4/65.1 | 60/70 | 69.0/73.8 | 70/80 | 0.75
DHH0363W | 3 | W - High Static | 208/230/3/60 | 0 |  |  | 17.4/17.4 | 25/25 | 9.6/8.7 | 27.0/26.1 | 35/35 | 2.2/1.9 (1.7/1.5) | 19.6/19.3 | 25/25 | 29.2/28.0 | 35/35 | 1.2
DHH0363W | 3 | W - High Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 30.4/32.4 | 35/35 | 9.6/8.7 | 40.0/41.1 | 45/45 | 2.2/1.9 (1.7/1.5) | 32.6/34.3 | 35/40 | 42.2/43.0 | 45/45 | 1.2
DHH0363W | 3 | W - High Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 43.3/47.3 | 45/50 | 9.6/8.7 | 52.9/56.0 | 60/60 | 2.2/1.9 (1.7/1.5) | 45.5/49.2 | 50/50 | 55.1/57.9 | 60/60 | 1.2
DHH0363W | 3 | W - High Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 56.5/62.5 | 60/70 | 9.6/8.7 | 66.1/71.2 | 70/80 | 2.2/1.9 (1.7/1.5) | 58.7/64.4 | 60/70 | 68.3/73.1 | 70/80 | 1.2
DHH0364D | 3 | D - Standard Static | 460/3/60 | 0 |  |  | 8.2 | 15 | 4.3 | 12.5 | 15 | 0.9 (0.5) | 9.1 | 15 | 13.4 | 15 | 1.2
DHH0364D | 3 | D - Standard Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 15.7 | 20 | 4.3 | 20 | 20 | 0.9 (0.5) | 16.6 | 20 | 20.9 | 25 | 1.2
DHH0364D | 3 | D - Standard Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 23.2 | 25 | 4.3 | 27.5 | 30 | 0.9 (0.5) | 24.1 | 25 | 28.4 | 30 | 1.2
DHH0364D | 3 | D - Standard Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 30.7 | 35 | 4.3 | 35 | 40 | 0.9 (0.5) | 31.6 | 35 | 35.9 | 40 | 1.2
DHH0364W | 3 | W - High Static | 460/3/60 | 0 |  |  | 8.2 | 15 | 4.3 | 12.5 | 15 | 0.9 (0.5) | 9.1 | 15 | 13.4 | 15 | 1.2
DHH0364W | 3 | W - High Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 15.7 | 20 | 4.3 | 20 | 20 | 0.9 (0.5) | 16.6 | 20 | 20.9 | 25 | 1.2
DHH0364W | 3 | W - High Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 23.2 | 25 | 4.3 | 27.5 | 30 | 0.9 (0.5) | 24.1 | 25 | 28.4 | 30 | 1.2
DHH0364W | 3 | W - High Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 30.7 | 35 | 4.3 | 35 | 40 | 0.9 (0.5) | 31.6 | 35 | 35.9 | 40 | 1.2
DHH0483D | 4 | D - Standard Static | 208/230/3/60 | 0 |  |  | 25.4/25.4 | 35/35 | 9.6/8.7 | 35.0/34.1 | 45/45 | 2.2/1.9 (1.7/1.5) | 27.6/27.3 | 35/35 | 37.2/36.0 | 45/45 | 1
DHH0483D | 4 | D - Standard Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 38.4/40.4 | 45/45 | 9.6/8.7 | 48.0/49.1 | 50/50 | 2.2/1.9 (1.7/1.5) | 40.6/42.3 | 45/50 | 50.2/51.0 | 60/60 | 1
DHH0483D | 4 | D - Standard Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 51.3/55.3 | 60/60 | 9.6/8.7 | 60.9/64.0 | 70/70 | 2.2/1.9 (1.7/1.5) | 53.5/57.2 | 60/60 | 63.1/65.9 | 70/70 | 1
DHH0483D | 4 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 64.5/70.5 | 70/80 | 9.6/8.7 | 74.1/79.2 | 80/80 | 2.2/1.9 (1.7/1.5) | 66.7/72.4 | 70/80 | 76.3/81.1 | 80/90 | 1
DHH0483D | 4 | D - Standard Static | 208/230/3/60 | 20 | EH*D-3S20A | 41.5/47.9 | 77.2/85.2 | 80/90 | 9.6/8.7 | 86.8/93.9 | 90/100 | 2.2/1.9 (1.7/1.5) | 79.4/87.1 | 80/90 | 89.0/95.8 | 90/100 | 1
DHH0483W | 4 | W - High Static | 208/230/3/60 | 0 |  |  | 23.5/23.5 | 35/35 | 9.6/8.7 | 33.1/32.2 | 45/40 | 2.2/1.9 (1.7/1.5) | 25.7/25.4 | 35/35 | 35.3/34.1 | 45/45 | 1.2
DHH0483W | 4 | W - High Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 36.5/38.5 | 45/45 | 9.6/8.7 | 46.1/47.2 | 50/50 | 2.2/1.9 (1.7/1.5) | 38.7/40.4 | 45/45 | 48.3/49.1 | 50/50 | 1.2
DHH0483W | 4 | W - High Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 49.4/53.4 | 50/60 | 9.6/8.7 | 59.0/62.1 | 60/70 | 2.2/1.9 (1.7/1.5) | 51.6/55.3 | 60/60 | 61.2/64.0 | 70/70 | 1.2
DHH0483W | 4 | W - High Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 62.6/68.6 | 70/70 | 9.6/8.7 | 72.2/77.3 | 80/80 | 2.2/1.9 (1.7/1.5) | 64.8/70.5 | 70/80 | 74.4/79.2 | 80/80 | 1.2
DHH0483W | 4 | W - High Static | 208/230/3/60 | 20 | EH*D-3S20A | 41.5/47.9 | 75.3/83.3 | 80/90 | 9.6/8.7 | 84.9/92.0 | 90/100 | 2.2/1.9 (1.7/1.5) | 77.5/85.2 | 80/90 | 87.1/93.9 | 90/100 | 1.2
DHH0484D | 4 | D - Standard Static | 460/3/60 | 0 |  |  | 11.9 | 15 | 4.3 | 16.2 | 20 | 0.9 (0.5) | 12.8 | 15 | 17.1 | 20 | 1.2
DHH0484D | 4 | D - Standard Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 19.4 | 20 | 4.3 | 23.7 | 25 | 0.9 (0.5) | 20.3 | 25 | 24.6 | 25 | 1.2
DHH0484D | 4 | D - Standard Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 26.9 | 30 | 4.3 | 31.2 | 35 | 0.9 (0.5) | 27.8 | 30 | 32.1 | 35 | 1.2
DHH0484D | 4 | D - Standard Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 34.4 | 35 | 4.3 | 38.7 | 40 | 0.9 (0.5) | 35.3 | 40 | 39.6 | 40 | 1.2
DHH0484D | 4 | D - Standard Static | 460/3/60 | 20 | EH*D-4S20A | 24.1 | 41.9 | 45 | 4.3 | 46.2 | 50 | 0.9 (0.5) | 42.8 | 45 | 47.1 | 50 | 1.2
DHH0484W | 4 | W - High Static | 460/3/60 | 0 |  |  | 11.9 | 15 | 4.3 | 16.2 | 20 | 0.9 (0.5) | 12.8 | 15 | 17.1 | 20 | 1.2
DHH0484W | 4 | W - High Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 19.4 | 20 | 4.3 | 23.7 | 25 | 0.9 (0.5) | 20.3 | 25 | 24.6 | 25 | 1.2
DHH0484W | 4 | W - High Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 26.9 | 30 | 4.3 | 31.2 | 35 | 0.9 (0.5) | 27.8 | 30 | 32.1 | 35 | 1.2
DHH0484W | 4 | W - High Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 34.4 | 35 | 4.3 | 38.7 | 40 | 0.9 (0.5) | 35.3 | 40 | 39.6 | 40 | 1.2
DHH0484W | 4 | W - High Static | 460/3/60 | 20 | EH*D-4S20A | 24.1 | 41.9 | 45 | 4.3 | 46.2 | 50 | 0.9 (0.5) | 42.8 | 45 | 47.1 | 50 | 1.2
DHH0603D | 5 | D - Standard Static | 208/230/3/60 | 0 |  |  | 29.4/29.4 | 40/40 | 9.6/8.7 | 39.0/38.1 | 50/50 | 2.2/1.9 (1.7/1.5) | 31.6/31.3 | 45/45 | 41.2/40.0 | 50/50 | 1
DHH0603D | 5 | D - Standard Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 42.4/44.4 | 50/50 | 9.6/8.7 | 52.0/53.1 | 60/60 | 2.2/1.9 (1.7/1.5) | 44.6/46.3 | 50/50 | 54.2/55.0 | 60/60 | 1
DHH0603D | 5 | D - Standard Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 55.3/59.3 | 60/60 | 9.6/8.7 | 64.9/68.0 | 70/70 | 2.2/1.9 (1.7/1.5) | 57.5/61.2 | 60/70 | 67.1/69.9 | 70/70 | 1
DHH0603D | 5 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 68.5/74.5 | 70/80 | 9.6/8.7 | 78.1/83.2 | 80/90 | 2.2/1.9 (1.7/1.5) | 70.7/76.4 | 80/80 | 80.3/85.1 | 90/90 | 1
DHH0603D | 5 | D - Standard Static | 208/230/3/60 | 20 | EH*D-3S20A | 41.5/47.9 | 81.2/89.2 | 90/90 | 9.6/8.7 | 90.8/97.9 | 100/100 | 2.2/1.9 (1.7/1.5) | 83.4/91.1 | 90/100 | 93.0/99.8 | 100/100 | 1
DHH0603W | 5 | W - High Static | 208/230/3/60 | 0 |  |  | 30.2/30.2 | 45/45 | 9.6/8.7 | 39.8/38.9 | 50/50 | 2.2/1.9 (1.7/1.5) | 32.4/32.1 | 45/45 | 42.0/40.8 | 50/50 | 2.3
DHH0603W | 5 | W - High Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 43.2/45.2 | 50/50 | 9.6/8.7 | 52.8/53.9 | 60/60 | 2.2/1.9 (1.7/1.5) | 45.4/47.1 | 50/50 | 55.0/55.8 | 60/60 | 2.3
DHH0603W | 5 | W - High Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 56.1/60.1 | 60/70 | 9.6/8.7 | 65.7/68.8 | 70/70 | 2.2/1.9 (1.7/1.5) | 58.3/62.0 | 60/70 | 67.9/70.7 | 70/80 | 2.3
DHH0603W | 5 | W - High Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 69.3/75.3 | 70/80 | 9.6/8.7 | 78.9/84.0 | 80/90 | 2.2/1.9 (1.7/1.5) | 71.5/77.2 | 80/80 | 81.1/85.9 | 90/90 | 2.3
DHH0603W | 5 | W - High Static | 208/230/3/60 | 20 | EH*D-3S20A | 41.5/47.9 | 82.0/90.0 | 90/90 | 9.6/8.7 | 91.6/98.7 | 100/100 | 2.2/1.9 (1.7/1.5) | 84.2/91.9 | 90/100 | 93.8/101 | 100/110 | 2.3
DHH0604D | 5 | D - Standard Static | 460/3/60 | 0 |  |  | 13.3 | 20 | 4.3 | 17.6 | 20 | 0.9 (0.5) | 14.2 | 20 | 18.5 | 25 | 1.2
DHH0604D | 5 | D - Standard Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 20.8 | 25 | 4.3 | 25.1 | 30 | 0.9 (0.5) | 21.7 | 25 | 26 | 30 | 1.2
DHH0604D | 5 | D - Standard Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 28.3 | 30 | 4.3 | 32.6 | 35 | 0.9 (0.5) | 29.2 | 30 | 33.5 | 35 | 1.2
DHH0604D | 5 | D - Standard Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 35.9 | 40 | 4.3 | 40.2 | 45 | 0.9 (0.5) | 36.8 | 40 | 41.1 | 45 | 1.2
DHH0604D | 5 | D - Standard Static | 460/3/60 | 20 | EH*D-4S20A | 24.1 | 43.4 | 45 | 4.3 | 47.7 | 50 | 0.9 (0.5) | 44.3 | 45 | 48.6 | 50 | 1.2
DHH0604W | 5 | W - High Static | 460/3/60 | 0 |  |  | 15.3 | 20 | 4.3 | 19.6 | 25 | 0.9 (0.5) | 16.2 | 20 | 20.5 | 25 | 2.3
DHH0604W | 5 | W - High Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 22.8 | 25 | 4.3 | 27.1 | 30 | 0.9 (0.5) | 23.7 | 25 | 28 | 30 | 2.3
DHH0604W | 5 | W - High Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 30.3 | 35 | 4.3 | 34.6 | 35 | 0.9 (0.5) | 31.2 | 35 | 35.5 | 40 | 2.3
DHH0604W | 5 | W - High Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 37.9 | 40 | 4.3 | 42.2 | 45 | 0.9 (0.5) | 38.8 | 40 | 43.1 | 45 | 2.3
DHH0604W | 5 | W - High Static | 460/3/60 | 20 | EH*D-4S20A | 24.1 | 45.4 | 50 | 4.3 | 49.7 | 50 | 0.9 (0.5) | 46.3 | 50 | 50.6 | 60 | 2.3
DHH0723D | 6 | D - Standard Static | 208/230/3/60 | 0 |  |  | 27.2/27.2 | 40/40 | 9.6/8.7 | 36.8/35.9 | 50/50 | 2.2/1.9 (1.7/1.5) | 29.4/29.1 | 40/40 | 39.0/37.8 | 50/50 | 1.2
DHH0723D | 6 | D - Standard Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 40.2/42.2 | 50/50 | 9.6/8.7 | 49.8/50.9 | 60/60 | 2.2/1.9 (1.7/1.5) | 42.4/44.1 | 50/50 | 52.0/52.8 | 60/60 | 1.2
DHH0723D | 6 | D - Standard Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 53.1/57.1 | 60/60 | 9.6/8.7 | 62.7/65.8 | 70/70 | 2.2/1.9 (1.7/1.5) | 55.3/59.0 | 60/60 | 64.9/67.7 | 70/70 | 1.2
DHH0723D | 6 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 66.3/72.3 | 70/80 | 9.6/8.7 | 75.9/81.0 | 80/90 | 2.2/1.9 (1.7/1.5) | 68.5/74.2 | 70/80 | 78.1/82.9 | 80/90 | 1.2
DHH0723D | 6 | D - Standard Static | 208/230/3/60 | 20 | EH*D-3S20A | 41.5/47.9 | 79.0/87.0 | 80/90 | 9.6/8.7 | 88.6/95.7 | 90/100 | 2.2/1.9 (1.7/1.5) | 81.2/88.9 | 90/90 | 90.8/97.6 | 100/100 | 1.2
DHH0723D | 6 | D - Standard Static | 208/230/3/60 | 30 | EH*D-3S30A | 62.5/72.2 | 105/117 | 110/125 | 9.6/8.7 | 115/126 | 125/150 | 2.2/1.9 (1.7/1.5) | 108/119 | 110/125 | 117/128 | 125/150 | 1.2
DHH0723W | 6 | W - High Static | 208/230/3/60 | 0 |  |  | 29.9/29.9 | 45/45 | 9.6/8.7 | 39.5/38.6 | 50/50 | 2.2/1.9 (1.7/1.5) | 32.1/31.8 | 45/45 | 41.7/40.5 | 50/50 | 2.3
DHH0723W | 6 | W - High Static | 208/230/3/60 | 5 | EH*D-3S05A | 10.4/12.0 | 42.9/44.9 | 50/50 | 9.6/8.7 | 52.5/53.6 | 60/60 | 2.2/1.9 (1.7/1.5) | 45.1/46.8 | 50/50 | 54.7/55.5 | 60/60 | 2.3
DHH0723W | 6 | W - High Static | 208/230/3/60 | 10 | EH*D-3S10A | 20.8/24.0 | 55.8/59.8 | 60/60 | 9.6/8.7 | 65.4/68.5 | 70/70 | 2.2/1.9 (1.7/1.5) | 58.0/61.7 | 60/70 | 67.6/70.4 | 70/80 | 2.3
DHH0723W | 6 | W - High Static | 208/230/3/60 | 15 | EH*D-3S15A | 31.3/36.1 | 69.0/75.0 | 70/80 | 9.6/8.7 | 78.6/83.7 | 80/90 | 2.2/1.9 (1.7/1.5) | 71.2/76.9 | 80/80 | 80.8/85.6 | 90/90 | 2.3
DHH0723W | 6 | W - High Static | 208/230/3/60 | 20 | EH*D-3S20A | 41.5/47.9 | 81.7/89.7 | 90/90 | 9.6/8.7 | 91.3/98.4 | 100/100 | 2.2/1.9 (1.7/1.5) | 83.9/91.6 | 90/100 | 93.5/100 | 100/110 | 2.3
DHH0723W | 6 | W - High Static | 208/230/3/60 | 30 | EH*D-3S30B | 62.5/72.2 | 108/120 | 110/125 | 9.6/8.7 | 118/129 | 125/150 | 2.2/1.9 (1.7/1.5) | 110/122 | 125/125 | 120/131 | 125/150 | 2.3
DHH0724D | 6 | D - Standard Static | 460/3/60 | 0 |  |  | 12.2 | 15 | 4.3 | 16.5 | 20 | 0.9 (0.5) | 13.1 | 15 | 17.4 | 20 | 1.2
DHH0724D | 6 | D - Standard Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 19.7 | 25 | 4.3 | 24 | 25 | 0.9 (0.5) | 20.6 | 25 | 24.9 | 30 | 1.2
DHH0724D | 6 | D - Standard Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 27.2 | 30 | 4.3 | 31.5 | 35 | 0.9 (0.5) | 28.1 | 30 | 32.4 | 35 | 1.2
DHH0724D | 6 | D - Standard Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 34.7 | 35 | 4.3 | 39 | 40 | 0.9 (0.5) | 35.6 | 40 | 39.9 | 40 | 1.2
DHH0724D | 6 | D - Standard Static | 460/3/60 | 20 | EH*D-4S20A | 24.1 | 42.2 | 45 | 4.3 | 46.5 | 50 | 0.9 (0.5) | 43.1 | 45 | 47.4 | 50 | 1.2
DHH0724D | 6 | D - Standard Static | 460/3/60 | 30 | EH*D-4S30A | 36.1 | 57.3 | 60 | 4.3 | 61.6 | 70 | 0.9 (0.5) | 58.2 | 60 | 62.5 | 70 | 1.2
DHH0724W | 6 | W - High Static | 460/3/60 | 0 |  |  | 14.2 | 20 | 4.3 | 18.5 | 25 | 0.9 (0.5) | 15.1 | 20 | 19.4 | 25 | 2.3
DHH0724W | 6 | W - High Static | 460/3/60 | 5 | EH*D-4S05A | 6 | 21.7 | 25 | 4.3 | 26 | 30 | 0.9 (0.5) | 22.6 | 25 | 26.9 | 30 | 2.3
DHH0724W | 6 | W - High Static | 460/3/60 | 10 | EH*D-4S10A | 12 | 29.2 | 30 | 4.3 | 33.5 | 35 | 0.9 (0.5) | 30.1 | 35 | 34.4 | 35 | 2.3
DHH0724W | 6 | W - High Static | 460/3/60 | 15 | EH*D-4S15A | 18 | 36.7 | 40 | 4.3 | 41 | 45 | 0.9 (0.5) | 37.6 | 40 | 41.9 | 45 | 2.3
DHH0724W | 6 | W - High Static | 460/3/60 | 20 | EH*D-4S20A | 24.1 | 44.2 | 45 | 4.3 | 48.5 | 50 | 0.9 (0.5) | 45.1 | 50 | 49.4 | 50 | 2.3
DHH0724W | 6 | W - High Static | 460/3/60 | 30 | EH*D-4S30B | 36.1 | 59.3 | 60 | 4.3 | 63.6 | 70 | 0.9 (0.5) | 60.2 | 70 | 64.5 | 70 | 2.3
DVH0903D | 7.5 | D - Standard Static | 208/230/3/60 | 0 |  |  | 49.9/49.9 | 60/60 | 9.6/8.7 | 59.5/58.6 | 70/70 | 3.3/3.0 (2.4) | 54.0/53.6 | 60/60 | 63.6/62.3 | 70/70 | 3.5
DVH0903D | 7.5 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 88.9/95.0 | 100/100 | 9.6/8.7 | 98.5/104 | 110/110 | 3.3/3.0 (2.4) | 93.1/98.7 | 100/100 | 103/107 | 110/110 | 3.5
DVH0903D | 7.5 | D - Standard Static | 208/230/3/60 | 30 | EH*D-3M30 | 60.0/69.3 | 125/136 | 125/150 | 9.6/8.7 | 135/145 | 150/150 | 3.3/3.0 (2.4) | 129/140 | 150/150 | 139/149 | 150/150 | 3.5
DVH0903D | 7.5 | D - Standard Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 167/185 | 175/200 | 9.6/8.7 | 177/194 | 200/200 | 3.3/3.0 (2.4) | 171/189 | 175/200 | 181/198 | 200/200 | 3.5
DVH0903W | 7.5 | W - High Static | 208/230/3/60 | 0 |  |  | 49.9/49.9 | 60/60 | 9.6/8.7 | 59.5/58.6 | 70/70 | 3.3/3.0 (2.4) | 54.0/53.6 | 60/60 | 63.6/62.3 | 70/70 | 3.5
DVH0903W | 7.5 | W - High Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 88.9/95.0 | 100/100 | 9.6/8.7 | 98.5/104 | 110/110 | 3.3/3.0 (2.4) | 93.1/98.7 | 100/100 | 103/107 | 110/110 | 3.5
DVH0903W | 7.5 | W - High Static | 208/230/3/60 | 30 | EH*D-3M30 | 60.0/69.3 | 125/136 | 125/150 | 9.6/8.7 | 135/145 | 150/150 | 3.3/3.0 (2.4) | 129/140 | 150/150 | 139/149 | 150/150 | 3.5
DVH0903W | 7.5 | W - High Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 167/185 | 175/200 | 9.6/8.7 | 177/194 | 200/200 | 3.3/3.0 (2.4) | 171/189 | 175/200 | 181/198 | 200/200 | 3.5
DVH0904D | 7.5 | D - Standard Static | 460/3/60 | 0 |  |  | 24.8 | 30 | 4.3 | 29.1 | 35 | 1.2 (1.0) | 26.3 | 30 | 30.6 | 35 | 3.5
DVH0904D | 7.5 | D - Standard Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 47.3 | 50 | 4.3 | 51.6 | 60 | 1.2 (1.0) | 48.8 | 50 | 53.1 | 60 | 3.5
DVH0904D | 7.5 | D - Standard Static | 460/3/60 | 30 | EH*D-4M30 | 34.6 | 68.1 | 70 | 4.3 | 72.4 | 80 | 1.2 (1.0) | 69.6 | 70 | 73.9 | 80 | 3.5
DVH0904D | 7.5 | D - Standard Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 92.4 | 100 | 4.3 | 96.7 | 100 | 1.2 (1.0) | 93.9 | 100 | 98.2 | 100 | 3.5
DVH0904W | 7.5 | W - High Static | 460/3/60 | 0 |  |  | 24.8 | 30 | 4.3 | 29.1 | 35 | 1.2 (1.0) | 26.3 | 30 | 30.6 | 35 | 3.5
DVH0904W | 7.5 | W - High Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 47.3 | 50 | 4.3 | 51.6 | 60 | 1.2 (1.0) | 48.8 | 50 | 53.1 | 60 | 3.5
DVH0904W | 7.5 | W - High Static | 460/3/60 | 30 | EH*D-4M30 | 34.6 | 68.1 | 70 | 4.3 | 72.4 | 80 | 1.2 (1.0) | 69.6 | 70 | 73.9 | 80 | 3.5
DVH0904W | 7.5 | W - High Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 92.4 | 100 | 4.3 | 96.7 | 100 | 1.2 (1.0) | 93.9 | 100 | 98.2 | 100 | 3.5
DVH1023D | 8.5 | D - Standard Static | 208/230/3/60 | 0 |  |  | 52.7/52.7 | 60/60 | 9.6/8.7 | 62.3/61.4 | 70/70 | 3.3/3.0 (2.4) | 56.9/56.5 | 70/70 | 66.5/65.2 | 80/80 | 3.5
DVH1023D | 8.5 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 91.8/97.8 | 100/110 | 9.6/8.7 | 101/107 | 110/110 | 3.3/3.0 (2.4) | 96.0/102 | 100/110 | 106/110 | 110/125 | 3.5
DVH1023D | 8.5 | D - Standard Static | 208/230/3/60 | 30 | EH*D-3M30 | 60.0/69.3 | 128/139 | 150/150 | 9.6/8.7 | 137/148 | 150/150 | 3.3/3.0 (2.4) | 132/143 | 150/150 | 142/152 | 150/175 | 3.5
DVH1023D | 8.5 | D - Standard Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 170/188 | 175/200 | 9.6/8.7 | 180/197 | 200/200 | 3.3/3.0 (2.4) | 174/192 | 175/200 | 184/200 | 200/225 | 3.5
DVH1023W | 8.5 | W - High Static | 208/230/3/60 | 0 |  |  | 56.5/56.5 | 70/70 | 9.6/8.7 | 66.1/65.2 | 80/80 | 3.3/3.0 (2.4) | 60.6/60.2 | 70/70 | 70.2/68.9 | 80/80 | 5
DVH1023W | 8.5 | W - High Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 95.5/102 | 100/110 | 9.6/8.7 | 105/110 | 125/125 | 3.3/3.0 (2.4) | 99.7/105 | 110/110 | 109/114 | 125/125 | 5
DVH1023W | 8.5 | W - High Static | 208/230/3/60 | 30 | EH*D-3M30 | 60.0/69.3 | 132/143 | 150/150 | 9.6/8.7 | 141/152 | 150/175 | 3.3/3.0 (2.4) | 136/147 | 150/150 | 145/156 | 150/175 | 5
DVH1023W | 8.5 | W - High Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 174/192 | 175/200 | 9.6/8.7 | 183/200 | 200/225 | 3.3/3.0 (2.4) | 178/196 | 200/200 | 187/204 | 200/225 | 5
DVH1024D | 8.5 | D - Standard Static | 460/3/60 | 0 |  |  | 26 | 30 | 4.3 | 30.3 | 35 | 1.2 (1.0) | 27.5 | 35 | 31.8 | 35 | 3.5
DVH1024D | 8.5 | D - Standard Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 48.5 | 50 | 4.3 | 52.8 | 60 | 1.2 (1.0) | 50 | 60 | 54.3 | 60 | 3.5
DVH1024D | 8.5 | D - Standard Static | 460/3/60 | 30 | EH*D-4M30 | 34.6 | 69.3 | 70 | 4.3 | 73.6 | 80 | 1.2 (1.0) | 70.8 | 80 | 75.1 | 80 | 3.5
DVH1024D | 8.5 | D - Standard Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 93.6 | 100 | 4.3 | 97.9 | 100 | 1.2 (1.0) | 95.1 | 100 | 99.4 | 100 | 3.5
DVH1024W | 8.5 | W - High Static | 460/3/60 | 0 |  |  | 29.7 | 35 | 4.3 | 34 | 40 | 1.2 (1.0) | 31.2 | 35 | 35.5 | 40 | 5
DVH1024W | 8.5 | W - High Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 52.3 | 60 | 4.3 | 56.6 | 60 | 1.2 (1.0) | 53.8 | 60 | 58.1 | 60 | 5
DVH1024W | 8.5 | W - High Static | 460/3/60 | 30 | EH*D-4M30 | 34.6 | 73 | 80 | 4.3 | 77.3 | 80 | 1.2 (1.0) | 74.5 | 80 | 78.8 | 80 | 5
DVH1024W | 8.5 | W - High Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 97.4 | 100 | 4.3 | 102 | 110 | 1.2 (1.0) | 98.9 | 100 | 103 | 110 | 5
DVH1203D | 10 | D - Standard Static | 208/230/3/60 | 0 |  |  | 54.0/54.0 | 70/70 | 9.6/8.7 | 63.6/62.7 | 80/70 | 3.3/3.0 (2.4) | 58.2/57.8 | 70/70 | 67.8/66.5 | 80/80 | 3.5
DVH1203D | 10 | D - Standard Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 93.1/99.1 | 100/110 | 9.6/8.7 | 103/108 | 110/110 | 3.3/3.0 (2.4) | 97.3/103 | 110/110 | 107/112 | 110/125 | 3.5
DVH1203D | 10 | D - Standard Static | 208/230/3/60 | 30 | EH*D-3M30 | 60.0/69.3 | 129/141 | 150/150 | 9.6/8.7 | 139/149 | 150/150 | 3.3/3.0 (2.4) | 133/144 | 150/150 | 143/153 | 150/175 | 3.5
DVH1203D | 10 | D - Standard Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 171/189 | 175/200 | 9.6/8.7 | 181/198 | 200/200 | 3.3/3.0 (2.4) | 175/193 | 200/200 | 185/202 | 200/225 | 3.5
DVH1203W | 10 | W - High Static | 208/230/3/60 | 0 |  |  | 57.8/57.8 |  | 9.6/8.7 | 67.4/66.5 |  | 3.3/3.0 (2.4) | 61.9/61.5 |  | 71.5/70.2 |  | 5
DVH1203W | 10 | W - High Static | 208/230/3/60 | 15 | EH*D-3M15 | 31.3/36.1 | 96.9/103 |  | 9.6/8.7 | 106/112 |  | 3.3/3.0 (2.4) | 101/107 |  | 111/115 |  | 5
DVH1203W | 10 | W - High Static | 208/230/3/60 | 30 | EH*D-3M30 | 60.0/69.3 | 133/144 |  | 9.6/8.7 | 142/153 |  | 3.3/3.0 (2.4) | 137/148 |  | 147/157 |  | 5
DVH1203W | 10 | W - High Static | 208/230/3/60 | 45 | EH*D-3M45 | 93.8/108 | 175/193 |  | 9.6/8.7 | 185/202 |  | 3.3/3.0 (2.4) | 179/197 |  | 189/206 |  | 5
DVH1204D | 10 | D - Standard Static | 460/3/60 | 0 |  |  | 26.5 | 35 | 4.3 | 30.8 | 35 | 1.2 (1.0) | 28 | 35 | 32.3 | 40 | 3.5
DVH1204D | 10 | D - Standard Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 49.1 | 50 | 4.3 | 53.4 | 60 | 1.2 (1.0) | 50.6 | 60 | 54.9 | 60 | 3.5
DVH1204D | 10 | D - Standard Static | 460/3/60 | 30 | EH*D-4M30 | 34.6 | 69.8 | 70 | 4.3 | 74.1 | 80 | 1.2 (1.0) | 71.3 | 80 | 75.6 | 80 | 3.5
DVH1204D | 10 | D - Standard Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 94.2 | 100 | 4.3 | 98.5 | 100 | 1.2 (1.0) | 95.7 | 100 | 100 | 100 | 3.5
DVH1204W | 10 | W - High Static | 460/3/60 | 0 |  |  | 30.3 | 35 | 4.3 | 34.6 | 40 | 1.2 (1.0) | 31.8 | 40 | 36.1 | 40 | 5
DVH1204W | 10 | W - High Static | 460/3/60 | 15 | EH*D-4M15 | 18 | 52.8 | 60 | 4.3 | 57.1 | 60 | 1.2 (1.0) | 54.3 | 60 | 58.6 | 60 | 5
DVH1204W | 10 | W - High Static | 460/3/60 | 30 | EH*D-4M30 | 34.6 | 73.6 | 80 | 4.3 | 77.9 | 80 | 1.2 (1.0) | 75.1 | 80 | 79.4 | 80 | 5
DVH1204W | 10 | W - High Static | 460/3/60 | 45 | EH*D-4M45 | 54.1 | 97.9 | 100 | 4.3 | 102 | 110 | 1.2 (1.0) | 99.4 | 100 | 104 | 110 | 5

## Airflow
Model | Tons | Motor | Gas Heat | Burner Input (MBH) | ESP Min (in. w.c.) | ESP Max (in. w.c.) | CFM Min | CFM Max | Max CFM at ESP Max | Gas Heat Min CFM | Gas Heat Max CFM | Manual | Pages
DSG036 | 3 | D - Standard Static | Low | 45 | 0.1 | 0.8 | 1000 | 1490 | 1205 | 750 |  | SS-DSG3-R32 | 39, 42
DSG036 | 3 | D - Standard Static | Medium | 70 | 0.1 | 0.8 | 995 | 1490 | 1205 | 1050 |  | SS-DSG3-R32 | 40, 43
DSG036 | 3 | D - Standard Static | High | 90 | 0.1 | 0.8 | 1000 | 1490 | 1205 | 1200 |  | SS-DSG3-R32 | 41, 44
DSG036 | 3 | W - High Static | Low | 45 | 0.8 | 1.8 | 900 | 1485 | 1005 | 750 |  | SS-DSG3-R32 | 64
DSG036 | 3 | W - High Static | Medium | 70 | 0.8 | 1.8 | 915 | 1485 | 1005 | 1050 |  | SS-DSG3-R32 | 66
DSG036 | 3 | W - High Static | High | 90 | 0.8 | 1.8 | 915 | 1500 | 1195 | 1200 |  | SS-DSG3-R32 | 68
DSG048 | 4 | D - Standard Static | Low | 70 | 0.1 | 0.8 | 1435 | 1880 | 1600 | 950 |  | SS-DSG3-R32 | 47, 50
DSG048 | 4 | D - Standard Static | Medium | 90 | 0.1 | 0.8 | 1435 | 1880 | 1600 | 1200 |  | SS-DSG3-R32 | 48, 51
DSG048 | 4 | D - Standard Static | High | 115 | 0.1 | 0.8 | 1430 | 1880 | 1600 | 1400 |  | SS-DSG3-R32 | 49, 52
DSG048 | 4 | W - High Static | Low | 70 | 0.8 | 1.8 | 1200 | 1895 | 1480 | 950 |  | SS-DSG3-R32 | 70
DSG048 | 4 | W - High Static | Medium | 90 | 0.8 | 1.8 | 1205 | 1895 | 1480 | 1200 |  | SS-DSG3-R32 | 72
DSG048 | 4 | W - High Static | High | 115 | 0.8 | 1.8 | 1200 | 1895 | 1480 | 1400 |  | SS-DSG3-R32 | 74
DSG060 | 5 | D - Standard Static | Low | 90 | 0.1 | 0.8 | 1705 | 2245 | 1970 | 1100 |  | SS-DSG3-R32 | 55, 58
DSG060 | 5 | D - Standard Static | Medium | 115 | 0.1 | 0.8 | 1705 | 2245 | 1970 | 1150 |  | SS-DSG3-R32 | 56, 59
DSG060 | 5 | D - Standard Static | High | 140 | 0.1 | 0.8 | 1705 | 2245 | 1970 | 1600 |  | SS-DSG3-R32 | 57, 60
DSG060 | 5 | W - High Static | Low | 90 | 0.8 | 1.8 | 1500 | 2035 | 1660 | 1100 |  | SS-DSG3-R32 | 76
DSG060 | 5 | W - High Static | Medium | 115 | 0.8 | 1.8 | 1500 | 2035 | 1660 | 1150 |  | SS-DSG3-R32 | 78
DSG060 | 5 | W - High Static | High | 140 | 0.8 | 1.8 | 1505 | 2065 | 1695 | 1600 |  | SS-DSG3-R32 | 80
DSG072 | 6 | D - Standard Static | Low | 90 | 0.1 | 0.8 | 1850 | 2390 | 2115 | 1200 |  | SS-DSG3-R32 | 61
DSG072 | 6 | D - Standard Static | Medium | 115 | 0.1 | 0.8 | 1850 | 2390 | 2115 | 1550 |  | SS-DSG3-R32 | 62
DSG072 | 6 | D - Standard Static | High | 140 | 0.1 | 0.8 | 1850 | 2390 | 2115 | 1600 |  | SS-DSG3-R32 | 63
DSG072 | 6 | W - High Static | Low | 90 | 0.6 | 1.8 | 1800 | 2690 | 2280 | 1200 |  | SS-DSG3-R32 | 82
DSG072 | 6 | W - High Static | Medium | 115 | 0.6 | 1.8 | 1800 | 2690 | 2280 | 1550 |  | SS-DSG3-R32 | 84
DSG072 | 6 | W - High Static | High | 140 | 0.6 | 1.8 | 1800 | 2690 | 2280 | 1600 |  | SS-DSG3-R32 | 86
DSG090 | 7.5 | D - Standard Static | Low | 130 | 0.2 | 0.8 | 2627 | 3374 | 3008 | 1765 | 3882 | SS-DSG7-R32 | 30
DSG090 | 7.5 | D - Standard Static | Medium | 180 | 0.2 | 0.8 | 2625 | 3404 | 3050 | 2443 | 5375 | SS-DSG7-R32 | 34
DSG090 | 7.5 | D - Standard Static | High | 225 | 0.2 | 0.8 | 2650 | 3330 | 3004 | 2800 | 5599 | SS-DSG7-R32 | 38
DSG090 | 7.5 | W - High Static | Low | 130 | 0.2 | 1.8 | 2562 | 3957 | 3008 | 1765 | 3882 | SS-DSG7-R32 | 32-33
DSG090 | 7.5 | W - High Static | Medium | 180 | 0.2 | 1.8 | 2443 | 3981 | 3000 | 2443 | 5375 | SS-DSG7-R32 | 36-37
DSG090 | 7.5 | W - High Static | High | 225 | 0.2 | 1.8 | 2637 | 3856 | 3004 | 2800 | 5599 | SS-DSG7-R32 | 40-41
DSG102 | 8.5 | D - Standard Static | Low | 130 | 0.2 | 0.8 | 2934 | 3740 | 3402 | 1765 | 3882 | SS-DSG7-R32 | 42
DSG102 | 8.5 | D - Standard Static | Medium | 180 | 0.2 | 0.8 | 2883 | 3721 | 3398 | 2443 | 5375 | SS-DSG7-R32 | 46
DSG102 | 8.5 | D - Standard Static | High | 225 | 0.2 | 0.8 | 3028 | 3708 | 3417 | 2800 | 5599 | SS-DSG7-R32 | 50
DSG102 | 8.5 | W - High Static | Low | 130 | 0.2 | 1.8 | 2788 | 4271 | 3403 | 1765 | 3882 | SS-DSG7-R32 | 44-45
DSG102 | 8.5 | W - High Static | Medium | 180 | 0.2 | 1.8 | 2721 | 4267 | 3400 | 2443 | 5375 | SS-DSG7-R32 | 48-49
DSG102 | 8.5 | W - High Static | High | 225 | 0.2 | 1.8 | 2894 | 4136 | 3400 | 2800 | 5599 | SS-DSG7-R32 | 52-53
DSG120 | 10 | D - Standard Static | Low | 130 | 0.2 | 0.8 | 3000 | 4353 | 4000 | 1765 | 3882 | SS-DSG7-R32 | 54
DSG120 | 10 | D - Standard Static | Medium | 180 | 0.2 | 0.8 | 3000 | 4305 | 4004 | 2443 | 5375 | SS-DSG7-R32 | 58
DSG120 | 10 | D - Standard Static | High | 240 | 0.2 | 0.8 | 3004 | 4287 | 4012 | 2986 | 5972 | SS-DSG7-R32 | 62
DSG120 | 10 | W - High Static | Low | 130 | 0.2 | 1.8 | 3000 | 4973 | 4001 | 1765 | 3882 | SS-DSG7-R32 | 56-57
DSG120 | 10 | W - High Static | Medium | 180 | 0.2 | 1.8 | 3000 | 5125 | 4004 | 2443 | 5375 | SS-DSG7-R32 | 60-61
DSG120 | 10 | W - High Static | High | 240 | 0.2 | 1.8 | 3000 | 4912 | 3996 | 2986 | 5972 | SS-DSG7-R32 | 64-65
DSG150 | 12.5 | D - Standard Static | Low | 130 | 0.2 | 0.8 | 3951 | 4718 | 4425 | 1765 | 3882 | SS-DSG7-R32 | 66
DSG150 | 12.5 | D - Standard Static | Medium | 180 | 0.2 | 0.8 | 3950 | 4486 | 4234 | 2443 | 5375 | SS-DSG7-R32 | 70
DSG150 | 12.5 | D - Standard Static | High | 240 | 0.2 | 0.8 | 3784 | 4371 | 4054 | 2986 | 5972 | SS-DSG7-R32 | 74
DSG150 | 12.5 | W - High Static | Low | 130 | 0.2 | 1.8 | 3750 | 5804 | 5009 | 1765 | 3882 | SS-DSG7-R32 | 68-69
DSG150 | 12.5 | W - High Static | Medium | 180 | 0.2 | 1.8 | 3750 | 5813 | 4884 | 2443 | 5375 | SS-DSG7-R32 | 72-73
DSG150 | 12.5 | W - High Static | High | 240 | 0.2 | 1.8 | 3750 | 5600 | 4731 | 2986 | 5972 | SS-DSG7-R32 | 76-77
DSG180 | 15 | D - Standard Static | Low | 260 | 0.2 | 1.2 | 4500 | 6824 | 6034 |  |  | SS-DSG15-R32 | 50-51
DSG180 | 15 | D - Standard Static | Medium | 360 | 0.2 | 1.2 | 4500 | 6786 | 6020 |  |  | SS-DSG15-R32 | 52-53
DSG180 | 15 | D - Standard Static | High | 400 | 0.2 | 1.2 | 4500 | 6803 | 6035 |  |  | SS-DSG15-R32 | 54-55
DSG180 | 15 | W - High Static | Low | 260 | 0.2 | 2.2 | 4500 | 8561 | 6023 |  |  | SS-DSG15-R32 | 23-25
DSG180 | 15 | W - High Static | Medium | 360 | 0.2 | 2.2 | 4500 | 8561 | 6023 |  |  | SS-DSG15-R32 | 26-28
DSG180 | 15 | W - High Static | High | 400 | 0.2 | 2.2 | 4500 | 8561 | 6023 |  |  | SS-DSG15-R32 | 29-31
DSG240 | 20 | D - Standard Static | Low | 260 | 0.2 | 1.2 | 6000 | 8870 | 8015 |  |  | SS-DSG15-R32 | 56-57
DSG240 | 20 | D - Standard Static | Medium | 360 | 0.2 | 1.2 | 6000 | 9175 | 8024 |  |  | SS-DSG15-R32 | 58-59
DSG240 | 20 | D - Standard Static | High | 400 | 0.2 | 1.2 | 6000 | 9175 | 8024 |  |  | SS-DSG15-R32 | 60-61
DSG240 | 20 | W - High Static | Low | 260 | 0.2 | 2.2 | 6660 | 10340 | 8015 |  |  | SS-DSG15-R32 | 32-34
DSG240 | 20 | W - High Static | Medium | 360 | 0.2 | 2.2 | 6965 | 9883 | 8015 |  |  | SS-DSG15-R32 | 35-37
DSG240 | 20 | W - High Static | High | 400 | 0.2 | 2.2 | 6965 | 9883 | 8015 |  |  | SS-DSG15-R32 | 38-40
DSG300 | 25 | D - Standard Static | Low | 260 | 0.2 | 1.2 | 7500 | 10848 | 10005 |  |  | SS-DSG15-R32 | 62-63
DSG300 | 25 | D - Standard Static | Medium | 360 | 0.2 | 1.2 | 7500 | 10848 | 10005 |  |  | SS-DSG15-R32 | 64-65
DSG300 | 25 | D - Standard Static | High | 400 | 0.2 | 1.2 | 7500 | 10848 | 10005 |  |  | SS-DSG15-R32 | 66-67
DSG300 | 25 | W - High Static | Low | 260 | 0.2 | 2.2 | 9257 | 11801 | 10003 |  |  | SS-DSG15-R32 | 41-43
DSG300 | 25 | W - High Static | Medium | 360 | 0.2 | 2.2 | 9257 | 11801 | 10003 |  |  | SS-DSG15-R32 | 44-46
DSG300 | 25 | W - High Static | High | 400 | 0.2 | 2.2 | 9257 | 11801 | 10003 |  |  | SS-DSG15-R32 | 47-49
DHG036 | 3 | D - Standard Static | Low | 45 | 0.2 | 0.8 | 900 | 1425 | 1115 | 750 |  | SS-DHG3-R32 | 42-43
DHG036 | 3 | D - Standard Static | Medium | 70 | 0.2 | 0.8 | 900 | 1425 | 1115 | 950 |  | SS-DHG3-R32 | 42, 44
DHG036 | 3 | D - Standard Static | High | 115 | 0.2 | 0.8 | 900 | 1500 | 1250 | 1150 |  | SS-DHG3-R32 | 43-44
DHG036 | 3 | W - High Static | Low | 45 | 0.8 | 2 | 900 | 1500 | 1139 | 750 |  | SS-DHG3-R32 | 52
DHG036 | 3 | W - High Static | Medium | 70 | 0.8 | 2 | 900 | 1500 | 1139 | 950 |  | SS-DHG3-R32 | 53
DHG036 | 3 | W - High Static | High | 115 | 0.8 | 2 | 900 | 1500 | 1139 | 1150 |  | SS-DHG3-R32 | 54
DHG048 | 4 | D - Standard Static | Low | 70 | 0.2 | 0.8 | 1200 | 1805 | 1550 | 950 |  | SS-DHG3-R32 | 45-46
DHG048 | 4 | D - Standard Static | Medium | 115 | 0.2 | 0.8 | 1205 | 1820 | 1560 | 1325 |  | SS-DHG3-R32 | 45, 47
DHG048 | 4 | D - Standard Static | High | 140 | 0.2 | 0.8 | 1205 | 1930 | 1680 | 1500 |  | SS-DHG3-R32 | 46-47
DHG048 | 4 | W - High Static | Low | 70 | 0.8 | 2 | 1282 | 2000 | 1550 | 950 |  | SS-DHG3-R32 | 55
DHG048 | 4 | W - High Static | Medium | 115 | 0.8 | 2 | 1282 | 2000 | 1550 | 1325 |  | SS-DHG3-R32 | 56
DHG048 | 4 | W - High Static | High | 140 | 0.8 | 2 | 1282 | 2000 | 1550 | 1500 |  | SS-DHG3-R32 | 57
DHG060 | 5 | D - Standard Static | Low | 70 | 0.2 | 0.8 | 1500 | 2145 | 1900 | 950 |  | SS-DHG3-R32 | 48-49
DHG060 | 5 | D - Standard Static | Medium | 115 | 0.2 | 0.8 | 1500 | 2145 | 1900 | 1150 |  | SS-DHG3-R32 | 48, 50
DHG060 | 5 | D - Standard Static | High | 140 | 0.2 | 0.8 | 1685 | 2145 | 1900 | 1615 |  | SS-DHG3-R32 | 49-50
DHG060 | 5 | W - High Static | Low | 70 | 0.8 | 2 | 1500 | 2446 | 2037 | 950 |  | SS-DHG3-R32 | 58
DHG060 | 5 | W - High Static | Medium | 115 | 0.8 | 2 | 1500 | 2446 | 2037 | 1150 |  | SS-DHG3-R32 | 59
DHG060 | 5 | W - High Static | High | 140 | 0.8 | 2 | 1660 | 2446 | 2037 | 1615 |  | SS-DHG3-R32 | 60
DHG072 | 6 | D - Standard Static | Low | 70 | 0.2 | 0.8 | 1800 | 2370 | 2119 | 950 |  | SS-DHG3-R32 | 51
DHG072 | 6 | D - Standard Static | Medium | 125 | 0.2 | 0.8 | 1944 | 2370 | 2119 | 1565 |  | SS-DHG3-R32 | 51
DHG072 | 6 | D - Standard Static | High | 150 | 0.2 | 0.8 | 1944 | 2370 | 2119 | 1730 |  | SS-DHG3-R32 | 51
DHG072 | 6 | W - High Static | Low | 70 | 0.8 | 2 | 2224 | 2764 | 2483 | 950 |  | SS-DHG3-R32 | 61
DHG072 | 6 | W - High Static | Medium | 125 | 0.8 | 2 | 2305 | 2764 | 2483 | 1565 |  | SS-DHG3-R32 | 62
DHG072 | 6 | W - High Static | High | 150 | 0.8 | 2 | 2224 | 2764 | 2483 | 1730 |  | SS-DHG3-R32 | 63
DHG090 | 7.5 | D - Standard Static | Low | 130 | 0.2 | 0.8 | 2651 | 3622 | 3160 | 1765 | 3882 | SS-DHG7-R32 | 29
DHG090 | 7.5 | D - Standard Static | Medium | 180 | 0.2 | 0.8 | 2633 | 3417 | 2988 | 2443 | 5375 | SS-DHG7-R32 | 33
DHG090 | 7.5 | D - Standard Static | High | 225 | 0.2 | 0.8 | 2705 | 3622 | 3160 | 2400 | 4199 | SS-DHG7-R32 | 37
DHG090 | 7.5 | W - High Static | Low | 130 | 0.2 | 2 | 2307 | 3728 | 3161 | 1765 | 3882 | SS-DHG7-R32 | 31-32
DHG090 | 7.5 | W - High Static | Medium | 180 | 0.2 | 2 | 2280 | 3767 | 3317 | 2443 | 5375 | SS-DHG7-R32 | 35-36
DHG090 | 7.5 | W - High Static | High | 225 | 0.2 | 2 | 2360 | 3769 | 3161 | 2400 | 4199 | SS-DHG7-R32 | 39-40
DHG102 | 8.5 | D - Standard Static | Low | 130 | 0.2 | 0.8 | 2687 | 3830 | 3399 | 1765 | 3882 | SS-DHG7-R32 | 41
DHG102 | 8.5 | D - Standard Static | Medium | 180 | 0.2 | 0.8 | 2593 | 3830 | 3399 | 2443 | 5375 | SS-DHG7-R32 | 45
DHG102 | 8.5 | D - Standard Static | High | 225 | 0.2 | 0.8 | 2593 | 3830 | 3399 | 2400 | 4199 | SS-DHG7-R32 | 49
DHG102 | 8.5 | W - High Static | Low | 130 | 0.2 | 2 | 2687 | 4221 | 3041 | 1765 | 3882 | SS-DHG7-R32 | 43-44
DHG102 | 8.5 | W - High Static | Medium | 180 | 0.2 | 2 | 2593 | 4221 | 3041 | 2443 | 5375 | SS-DHG7-R32 | 47-48
DHG102 | 8.5 | W - High Static | High | 225 | 0.2 | 2 | 2593 | 4221 | 3041 | 2400 | 4199 | SS-DHG7-R32 | 51-52
DHG120 | 10 | D - Standard Static | Low | 130 | 0.2 | 0.8 | 3010 | 4126 | 3808 | 1765 | 3882 | SS-DHG7-R32 | 53
DHG120 | 10 | D - Standard Static | Medium | 180 | 0.2 | 0.8 | 3274 | 4126 | 3808 | 2443 | 5375 | SS-DHG7-R32 | 57
DHG120 | 10 | D - Standard Static | High | 240 | 0.2 | 0.8 | 3274 | 4126 | 3808 | 2986 | 5972 | SS-DHG7-R32 | 61
DHG120 | 10 | W - High Static | Low | 130 | 0.2 | 2 | 3012 | 4976 | 3976 | 1765 | 3882 | SS-DHG7-R32 | 55-56
DHG120 | 10 | W - High Static | Medium | 180 | 0.2 | 2 | 3012 | 4976 | 3976 | 2443 | 5375 | SS-DHG7-R32 | 59-60
DHG120 | 10 | W - High Static | High | 240 | 0.2 | 2 | 3012 | 4976 | 3976 | 2986 | 5972 | SS-DHG7-R32 | 63-64
DHG150 | 12.5 | D - Standard Static | Low | 130 | 0.2 | 0.8 | 3783 | 4719 | 4329 | 1765 | 3882 | SS-DHG7-R32 | 65
DHG150 | 12.5 | D - Standard Static | Medium | 180 | 0.2 | 0.8 | 3783 | 4719 | 4329 | 2443 | 5375 | SS-DHG7-R32 | 69
DHG150 | 12.5 | D - Standard Static | High | 240 | 0.2 | 0.8 | 3783 | 4719 | 4329 | 2756 | 5119 | SS-DHG7-R32 | 73
DHG150 | 12.5 | W - High Static | Low | 130 | 0.2 | 2 | 3835 | 5128 | 4015 | 1765 | 3882 | SS-DHG7-R32 | 67-68
DHG150 | 12.5 | W - High Static | Medium | 180 | 0.2 | 2 | 3835 | 5128 | 4015 | 2443 | 5375 | SS-DHG7-R32 | 71-72
DHG150 | 12.5 | W - High Static | High | 240 | 0.2 | 2 | 3835 | 5128 | 4015 | 2756 | 5119 | SS-DHG7-R32 | 75-76
DSH036 | 3 | D - Standard Static |  |  | 0.1 | 0.8 | 1135 | 1500 | 1325 |  |  | SS-DSH3-R32 | 27-28
DSH036 | 3 | W - High Static |  |  | 0.8 | 1.8 | 913 | 1500 | 1088 |  |  | SS-DSH3-R32 | 34
DSH048 | 4 | D - Standard Static |  |  | 0.1 | 0.8 | 1360 | 1886 | 1600 |  |  | SS-DSH3-R32 | 29-30
DSH048 | 4 | W - High Static |  |  | 0.8 | 1.8 | 1329 | 1856 | 1425 |  |  | SS-DSH3-R32 | 36
DSH060 | 5 | D - Standard Static |  |  | 0.1 | 0.8 | 1610 | 2243 | 2000 |  |  | SS-DSH3-R32 | 31-32
DSH060 | 5 | W - High Static |  |  | 0.8 | 1.8 | 1659 | 2220 | 1829 |  |  | SS-DSH3-R32 | 38
DSH072 | 6 | D - Standard Static |  |  | 0.1 | 0.8 | 1985 | 2380 | 2140 |  |  | SS-DSH3-R32 | 33
DSH072 | 6 | W - High Static |  |  | 0.6 | 1.6 | 2070 | 2654 | 2300 |  |  | SS-DSH3-R32 | 40
DSH090 | 7.5 | D - Standard Static |  |  | 0.2 | 0.8 | 2695 | 3370 | 3070 |  |  | SS-DSH7-R32 | 26
DSH090 | 7.5 | W - High Static |  |  | 0.2 | 1.8 | 2785 | 3850 | 3001 |  |  | SS-DSH7-R32 | 28-29
DSH102 | 8.5 | D - Standard Static |  |  | 0.2 | 0.8 | 2695 | 3737 | 3410 |  |  | SS-DSH7-R32 | 30
DSH102 | 8.5 | W - High Static |  |  | 0.2 | 1.8 | 2843 | 4262 | 3463 |  |  | SS-DSH7-R32 | 32-33
DSH120 | 10 | D - Standard Static |  |  | 0.2 | 0.8 | 3664 | 4430 | 4054 |  |  | SS-DSH7-R32 | 34
DSH120 | 10 | W - High Static |  |  | 0.2 | 1.8 | 3558 | 5194 | 4050 |  |  | SS-DSH7-R32 | 36-37
DSH150 | 12.5 | D - Standard Static |  |  | 0.2 | 0.8 | 4095 | 4970 | 4655 |  |  | SS-DSH7-R32 | 38
DSH150 | 12.5 | W - High Static |  |  | 0.2 | 1.8 | 4010 | 5875 | 5000 |  |  | SS-DSH7-R32 | 40-41
DSH180 | 15 | D - Standard Static |  |  | 0.2 | 1.2 | 5156 | 8322 | 6052 |  |  | SS-DSH15-R32 | 20
DSH180 | 15 | W - High Static |  |  | 0.2 | 2.2 | 5431 | 10997 | 7827 |  |  | SS-DSH15-R32 | 24-26
DSH240 | 20 | D - Standard Static |  |  | 0.2 | 1.2 | 6000 | 10371 | 8044 |  |  | SS-DSH15-R32 | 21
DSH240 | 20 | W - High Static |  |  | 0.2 | 2.2 | 6825 | 11430 | 8308 |  |  | SS-DSH15-R32 | 27-29
DHH036 | 3 | D - Standard Static |  |  | 0.2 | 0.8 | 1030 | 1565 | 1390 |  |  | SS-DHH3-R32 | 34
DHH036 | 3 | W - High Static |  |  | 0.8 | 2 | 900 | 1600 | 1174 |  |  | SS-DHH3-R32 | 38
DHH048 | 4 | D - Standard Static |  |  | 0.2 | 0.8 | 1455 | 1900 | 1655 |  |  | SS-DHH3-R32 | 35
DHH048 | 4 | W - High Static |  |  | 0.8 | 2 | 1200 | 2132 | 1602 |  |  | SS-DHH3-R32 | 40
DHH060 | 5 | D - Standard Static |  |  | 0.2 | 0.8 | 1810 | 2175 | 1940 |  |  | SS-DHH3-R32 | 36
DHH060 | 5 | W - High Static |  |  | 0.8 | 2 | 1664 | 2385 | 1901 |  |  | SS-DHH3-R32 | 42
DHH072 | 6 | D - Standard Static |  |  | 0.2 | 0.8 | 1950 | 2435 | 2209 |  |  | SS-DHH3-R32 | 37
DHH072 | 6 | W - High Static |  |  | 0.8 | 2 | 2085 | 2759 | 2346 |  |  | SS-DHH3-R32 | 44
DVH090 | 7.5 | D - Standard Static |  |  | 0.2 | 1.4 | 2250 | 3600 | 3600 |  |  | SS-DVH7-R32 | 43
DVH090 | 7.5 | W - High Static |  |  | 0.2 | 2 | 2250 | 3800 | 3600 |  |  | SS-DVH7-R32 | 45
DVH102 | 8.5 | D - Standard Static |  |  | 0.2 | 1.4 | 2550 | 3800 | 3800 |  |  | SS-DVH7-R32 | 43-44
DVH102 | 8.5 | W - High Static |  |  | 0.2 | 2 | 2550 | 4200 | 4200 |  |  | SS-DVH7-R32 | 45-46
DVH120 | 10 | D - Standard Static |  |  | 0.2 | 1.4 | 3000 | 4800 | 4000 |  |  | SS-DVH7-R32 | 44
DVH120 | 10 | W - High Static |  |  | 0.2 | 2 | 3000 | 5000 | 5000 |  |  | SS-DVH7-R32 | 46

## Airflow - Electric Heat
Model | Tons | Motor | Electric Heat kW | Min CFM | Max CFM | Manual | Pages
DSH036 | 3 | D - Standard Static | 5 | 1325 |  | SS-DSH3-R32 | 26
DSH036 | 3 | D - Standard Static | 10 | 1325 |  | SS-DSH3-R32 | 26
DSH036 | 3 | D - Standard Static | 15 | 1325 |  | SS-DSH3-R32 | 26
DSH036 | 3 | W - High Static | 5 | 1325 |  | SS-DSH3-R32 | 26
DSH036 | 3 | W - High Static | 10 | 1325 |  | SS-DSH3-R32 | 26
DSH036 | 3 | W - High Static | 15 | 1325 |  | SS-DSH3-R32 | 26
DSH048 | 4 | D - Standard Static | 5 | 1600 |  | SS-DSH3-R32 | 26
DSH048 | 4 | D - Standard Static | 10 | 1600 |  | SS-DSH3-R32 | 26
DSH048 | 4 | D - Standard Static | 15 | 1600 |  | SS-DSH3-R32 | 26
DSH048 | 4 | D - Standard Static | 20 | 1600 |  | SS-DSH3-R32 | 26
DSH048 | 4 | W - High Static | 5 | 1600 |  | SS-DSH3-R32 | 26
DSH048 | 4 | W - High Static | 10 | 1600 |  | SS-DSH3-R32 | 26
DSH048 | 4 | W - High Static | 15 | 1600 |  | SS-DSH3-R32 | 26
DSH048 | 4 | W - High Static | 20 | 1600 |  | SS-DSH3-R32 | 26
DSH060 | 5 | D - Standard Static | 5 | 1900 |  | SS-DSH3-R32 | 26
DSH060 | 5 | D - Standard Static | 10 | 1900 |  | SS-DSH3-R32 | 26
DSH060 | 5 | D - Standard Static | 15 | 1900 |  | SS-DSH3-R32 | 26
DSH060 | 5 | D - Standard Static | 20 | 1900 |  | SS-DSH3-R32 | 26
DSH060 | 5 | W - High Static | 5 | 1900 |  | SS-DSH3-R32 | 26
DSH060 | 5 | W - High Static | 10 | 1900 |  | SS-DSH3-R32 | 26
DSH060 | 5 | W - High Static | 15 | 1900 |  | SS-DSH3-R32 | 26
DSH060 | 5 | W - High Static | 20 | 1900 |  | SS-DSH3-R32 | 26
DSH072 | 6 | D - Standard Static | 5 | 2100 |  | SS-DSH3-R32 | 26
DSH072 | 6 | D - Standard Static | 10 | 2100 |  | SS-DSH3-R32 | 26
DSH072 | 6 | D - Standard Static | 15 | 2100 |  | SS-DSH3-R32 | 26
DSH072 | 6 | D - Standard Static | 20 | 2100 |  | SS-DSH3-R32 | 26
DSH072 | 6 | D - Standard Static | 30 | 2100 |  | SS-DSH3-R32 | 26
DSH072 | 6 | W - High Static | 5 | 2175 |  | SS-DSH3-R32 | 26
DSH072 | 6 | W - High Static | 10 | 2175 |  | SS-DSH3-R32 | 26
DSH072 | 6 | W - High Static | 15 | 2175 |  | SS-DSH3-R32 | 26
DSH072 | 6 | W - High Static | 20 | 2175 |  | SS-DSH3-R32 | 26
DSH072 | 6 | W - High Static | 30 | 2175 |  | SS-DSH3-R32 | 26
DSH090 | 7.5 | D - Standard Static | 15 | 2400 |  | SS-DSH7-R32 | 25
DSH090 | 7.5 | D - Standard Static | 30 | 2400 |  | SS-DSH7-R32 | 25
DSH090 | 7.5 | D - Standard Static | 45 | 2400 |  | SS-DSH7-R32 | 25
DSH090 | 7.5 | W - High Static | 15 | 2400 |  | SS-DSH7-R32 | 25
DSH090 | 7.5 | W - High Static | 30 | 2400 |  | SS-DSH7-R32 | 25
DSH090 | 7.5 | W - High Static | 45 | 2400 |  | SS-DSH7-R32 | 25
DSH102 | 8.5 | D - Standard Static | 15 | 2750 |  | SS-DSH7-R32 | 25
DSH102 | 8.5 | D - Standard Static | 30 | 2750 |  | SS-DSH7-R32 | 25
DSH102 | 8.5 | D - Standard Static | 45 | 2750 |  | SS-DSH7-R32 | 25
DSH102 | 8.5 | W - High Static | 15 | 2750 |  | SS-DSH7-R32 | 25
DSH102 | 8.5 | W - High Static | 30 | 2750 |  | SS-DSH7-R32 | 25
DSH102 | 8.5 | W - High Static | 45 | 2750 |  | SS-DSH7-R32 | 25
DSH120 | 10 | D - Standard Static | 15 | 3200 |  | SS-DSH7-R32 | 25
DSH120 | 10 | D - Standard Static | 30 | 3200 |  | SS-DSH7-R32 | 25
DSH120 | 10 | D - Standard Static | 45 | 3200 |  | SS-DSH7-R32 | 25
DSH120 | 10 | W - High Static | 15 | 3200 |  | SS-DSH7-R32 | 25
DSH120 | 10 | W - High Static | 30 | 3200 |  | SS-DSH7-R32 | 25
DSH120 | 10 | W - High Static | 45 | 3200 |  | SS-DSH7-R32 | 25
DSH150 | 12.5 | D - Standard Static | 15 | 4400 |  | SS-DSH7-R32 | 25
DSH150 | 12.5 | D - Standard Static | 30 | 4400 |  | SS-DSH7-R32 | 25
DSH150 | 12.5 | D - Standard Static | 45 | 4400 |  | SS-DSH7-R32 | 25
DSH150 | 12.5 | D - Standard Static | 60 | 4400 |  | SS-DSH7-R32 | 25
DSH150 | 12.5 | W - High Static | 15 | 3750 |  | SS-DSH7-R32 | 25
DSH150 | 12.5 | W - High Static | 30 | 3750 |  | SS-DSH7-R32 | 25
DSH150 | 12.5 | W - High Static | 45 | 3750 |  | SS-DSH7-R32 | 25
DSH150 | 12.5 | W - High Static | 60 | 3750 |  | SS-DSH7-R32 | 25
DSH180 | 15 | D - Standard Static | 30 | 5400 | 8300 | SS-DSH15-R32 | 40
DSH180 | 15 | D - Standard Static | 45 | 5400 | 8300 | SS-DSH15-R32 | 40
DSH180 | 15 | D - Standard Static | 60 | 5400 | 8300 | SS-DSH15-R32 | 40
DSH180 | 15 | W - High Static | 30 | 5500 | 9500 | SS-DSH15-R32 | 40
DSH180 | 15 | W - High Static | 45 | 5500 | 9500 | SS-DSH15-R32 | 40
DSH180 | 15 | W - High Static | 60 | 5500 | 9500 | SS-DSH15-R32 | 40
DSH240 | 20 | D - Standard Static | 30 | 6500 | 10300 | SS-DSH15-R32 | 40
DSH240 | 20 | D - Standard Static | 45 | 6500 | 10300 | SS-DSH15-R32 | 40
DSH240 | 20 | D - Standard Static | 60 | 6500 | 10300 | SS-DSH15-R32 | 40
DSH240 | 20 | D - Standard Static | 75 | 6500 | 10300 | SS-DSH15-R32 | 40
DSH240 | 20 | W - High Static | 30 | 6100 | 11100 | SS-DSH15-R32 | 40
DSH240 | 20 | W - High Static | 45 | 6100 | 11100 | SS-DSH15-R32 | 40
DSH240 | 20 | W - High Static | 60 | 6100 | 11100 | SS-DSH15-R32 | 40
DSH240 | 20 | W - High Static | 75 | 6100 | 11100 | SS-DSH15-R32 | 40
DHH036 | 3 | D - Standard Static | 5 | 1325 | 1500 | SS-DHH3-R32 | 33
DHH036 | 3 | D - Standard Static | 10 | 1325 | 1500 | SS-DHH3-R32 | 33
DHH036 | 3 | D - Standard Static | 15 | 1325 | 1500 | SS-DHH3-R32 | 33
DHH036 | 3 | W - High Static | 5 | 1325 | 1500 | SS-DHH3-R32 | 33
DHH036 | 3 | W - High Static | 10 | 1325 | 1500 | SS-DHH3-R32 | 33
DHH036 | 3 | W - High Static | 15 | 1325 | 1500 | SS-DHH3-R32 | 33
DHH048 | 4 | D - Standard Static | 5 | 1600 | 2000 | SS-DHH3-R32 | 33
DHH048 | 4 | D - Standard Static | 10 | 1600 | 2000 | SS-DHH3-R32 | 33
DHH048 | 4 | D - Standard Static | 15 | 1600 | 2000 | SS-DHH3-R32 | 33
DHH048 | 4 | D - Standard Static | 20 | 1600 | 2000 | SS-DHH3-R32 | 33
DHH048 | 4 | W - High Static | 5 | 1600 | 2000 | SS-DHH3-R32 | 33
DHH048 | 4 | W - High Static | 10 | 1600 | 2000 | SS-DHH3-R32 | 33
DHH048 | 4 | W - High Static | 15 | 1600 | 2000 | SS-DHH3-R32 | 33
DHH048 | 4 | W - High Static | 20 | 1600 | 2000 | SS-DHH3-R32 | 33
DHH060 | 5 | D - Standard Static | 5 | 1900 | 2500 | SS-DHH3-R32 | 33
DHH060 | 5 | D - Standard Static | 10 | 1900 | 2500 | SS-DHH3-R32 | 33
DHH060 | 5 | D - Standard Static | 15 | 1900 | 2500 | SS-DHH3-R32 | 33
DHH060 | 5 | D - Standard Static | 20 | 1900 | 2500 | SS-DHH3-R32 | 33
DHH060 | 5 | W - High Static | 5 | 1900 | 2500 | SS-DHH3-R32 | 33
DHH060 | 5 | W - High Static | 10 | 1900 | 2500 | SS-DHH3-R32 | 33
DHH060 | 5 | W - High Static | 15 | 1900 | 2500 | SS-DHH3-R32 | 33
DHH060 | 5 | W - High Static | 20 | 1900 | 2500 | SS-DHH3-R32 | 33
DHH072 | 6 | D - Standard Static | 5 | 2100 | 3000 | SS-DHH3-R32 | 33
DHH072 | 6 | D - Standard Static | 10 | 2100 | 3000 | SS-DHH3-R32 | 33
DHH072 | 6 | D - Standard Static | 15 | 2100 | 3000 | SS-DHH3-R32 | 33
DHH072 | 6 | D - Standard Static | 20 | 2100 | 3000 | SS-DHH3-R32 | 33
DHH072 | 6 | D - Standard Static | 30 | 2100 | 3000 | SS-DHH3-R32 | 33
DHH072 | 6 | W - High Static | 5 | 2175 | 3000 | SS-DHH3-R32 | 33
DHH072 | 6 | W - High Static | 10 | 2175 | 3000 | SS-DHH3-R32 | 33
DHH072 | 6 | W - High Static | 15 | 2175 | 3000 | SS-DHH3-R32 | 33
DHH072 | 6 | W - High Static | 20 | 2175 | 3000 | SS-DHH3-R32 | 33
DHH072 | 6 | W - High Static | 30 | 2175 | 3000 | SS-DHH3-R32 | 33
DVH090 | 7.5 | D - Standard Static | 15 | 2500 |  | SS-DVH7-R32 | 42
DVH090 | 7.5 | D - Standard Static | 30 | 2500 |  | SS-DVH7-R32 | 42
DVH090 | 7.5 | D - Standard Static | 45 | 2500 |  | SS-DVH7-R32 | 42
DVH090 | 7.5 | W - High Static | 15 | 2500 |  | SS-DVH7-R32 | 42
DVH090 | 7.5 | W - High Static | 30 | 2500 |  | SS-DVH7-R32 | 42
DVH090 | 7.5 | W - High Static | 45 | 2500 |  | SS-DVH7-R32 | 42
DVH102 | 8.5 | D - Standard Static | 15 | 2750 |  | SS-DVH7-R32 | 42
DVH102 | 8.5 | D - Standard Static | 30 | 2750 |  | SS-DVH7-R32 | 42
DVH102 | 8.5 | D - Standard Static | 45 | 2750 |  | SS-DVH7-R32 | 42
DVH102 | 8.5 | W - High Static | 15 | 2750 |  | SS-DVH7-R32 | 42
DVH102 | 8.5 | W - High Static | 30 | 2750 |  | SS-DVH7-R32 | 42
DVH102 | 8.5 | W - High Static | 45 | 2750 |  | SS-DVH7-R32 | 42
DVH120 | 10 | D - Standard Static | 15 | 3200 |  | SS-DVH7-R32 | 42
DVH120 | 10 | D - Standard Static | 30 | 3200 |  | SS-DVH7-R32 | 42
DVH120 | 10 | D - Standard Static | 45 | 3200 |  | SS-DVH7-R32 | 42
DVH120 | 10 | W - High Static | 15 | 3200 |  | SS-DVH7-R32 | 42
DVH120 | 10 | W - High Static | 30 | 3200 |  | SS-DVH7-R32 | 42
DVH120 | 10 | W - High Static | 45 | 3200 |  | SS-DVH7-R32 | 42

## Notes
Daikin Light Commercial RTU Capacity Tables — DSG 3-6 Ton, Standard Efficiency, R-32 Gas/Electric
Source: Daikin Spec Sheet SS-DSG3-R32 (ss-dsg3-r32.pdf). Extracted 8/13/2026.
COOLING sheet (source: Expanded Cooling Data, pages 26-35)
• Cooling tables are published per cabinet size with "*" as the voltage digit (e.g. DSG036*D covers 0361/0363/0364/0367).
• EAT DB = entering (indoor) dry bulb, EAT WB = entering (indoor) wet bulb, OA DB = outdoor ambient dry bulb.
• MBh = total cooling capacity; S/T = sensible-to-total ratio; ∆T = dry bulb temperature drop across the coil.
• "DSG072*D (70% - Low Stage)" is the 6-ton unit operating on the low stage of its two-stage compressor (~70% capacity/airflow).
• Combinations printed as "-" in the spec sheet (physically impossible DB/WB pairs, e.g. 71°F WB with 70°F DB) are omitted.
GAS HEATING sheet (source: Heating Rating Table - Natural Gas and Propane, page 36)
• Single-phase models are single-stage furnaces (no low stage) and are rated by AFUE (81%) — see column note below.
• 3-phase models are two-stage furnaces rated by Thermal Efficiency (80%) instead of AFUE.
• Temp rise ranges are the allowable rise ranges (°F) at high and low fire.
• ULN heating tables (page 37) intentionally excluded.
ELECTRICAL DATA sheet (source: Electrical Data, pages 125-128)
• Models ending in ULN excluded per request. Motor codes in this spec sheet: D = standard static, W = high static.
• No "L" (medium static) motor models exist in SS-DSG3-R32 — only D and W are published.
• Dual values "x/y" on 208/230V models = 208V/230V ratings. MCA/MOP shown for all 4 option combinations.
• Power Exhaust FLA values like "2.2/1.9 (1.7/1.5)" are printed verbatim from the spec sheet.
DSG 7.5-12.5 Ton, Standard Efficiency, R-32 Gas/Electric — added 8/15/2026
Source: Daikin Spec Sheet SS-DSG7-R32 (ss-dsg7-r32.pdf), 06/26 revision.
• Models: DSG090 (7.5 ton), DSG102 (8.5 ton), DSG120 (10 ton), DSG150 (12.5 ton).
• Only 208/230/3/60 and 460/3/60 are included; 575/3/60 (voltage digit 7) excluded per request.
• No ULN (ultra low NOx) models are published in SS-DSG7-R32.
COOLING (source: Expanded Cooling Data, pages 22-29)
• These tables are published per cabinet only (title is just "DSG090"), so they apply to every voltage
AND every motor code (D/L/W). Model is written "DSG090*" — unlike the 3-6 ton rows, there is no motor suffix.
• Three airflows per cabinet: DSG090 = 2625/3000/3375, DSG102 = 2975/3200/3825, DSG120 = 3150/3400/4050 CFM.
• The 71°F wet bulb column is published to fewer decimals than the others (S/T 0.4 vs 0.71, ∆T 14.3 vs 22.60);
values are recorded exactly as printed.
• 71°F WB at 70°F DB is printed "-" (impossible pair) and is omitted, same as the 3-6 ton data.
• DSG150 (12.5 ton) COOLING IS INTENTIONALLY ABSENT: pages 28-29 of SS-DSG7-R32 reprint the DSG120 tables
verbatim (identical MBh/S/T/∆T and identical 3150/3400/4050 airflows). DSG150 is rated 140,000 BTU/h vs
116,000 for DSG120 (AHRI table, page 19), so the printed data is a publishing error, not real 12.5 ton capacity.
Request corrected DSG150 tables from Daikin before adding them.
GAS HEATING (source: Heating Rating Table - Natural Gas and Propane, page 30)
• All 7.5-12.5 ton units are two-stage furnaces rated by Thermal Efficiency (81%), not AFUE.
• Heat sizes: DSG090/DSG102 = 130/180/225 MBH, DSG120/DSG150 = 130/180/240 MBH,
mapped to the Low/Medium/High convention used by the 3-6 ton rows.
• Low stage is 75% of high stage input. LP high-fire rate is reduced 10% vs natural gas (spec sheet footnote).
• Recommended min/max heating airflow (SCFM) is published on page 30 but is not carried in this schema.
ELECTRICAL DATA (source: Electrical Data, pages 81-83)
• Motor codes D (standard static), L (medium static) and W (high static) all exist in this size range,
unlike the 3-6 ton units where only D and W are published.
• Dual values "x/y" on 208/230V models = 208V/230V ratings.
• Power Exhaust FLA values like "3.3/3.0 (2.4)" are printed verbatim from the spec sheet.
KNOWN SPEC-SHEET TYPOS (SS-DSG7-R32 cooling tables)
• Three cells print MBh as "240.0" with an S/T computed from that bogus total (S/T 0.26 / 0.29 / 0.33).
Affected points, all at 80°F EAT DB / 67°F EAT WB / 95°F OA on the lowest airflow:
DSG090* @ 2625 CFM (pg 23), DSG102* @ 2975 CFM (pg 25), DSG120* @ 3150 CFM (pg 27).
• MBh and S/T are left BLANK in those three rows rather than carry an obviously wrong 240 MBh.
∆T is printed correctly (21.40 / 20.92 / 22.98) and is retained.
• Interpolating the neighbors gives roughly MBh 88.8 / 96.4 / 115.3 with S/T ~0.68, but these are estimates —
confirm against Daikin selection software before filling them in.
DSG 15-25 Ton, Standard Efficiency, R-32 Gas/Electric — added 8/15/2026
Source: Daikin Spec Sheet SS-DSG15-R32 (ss-dsg15-r32.pdf), 06/26 revision.
• Models: DSG180 (15 ton), DSG240 (20 ton), DSG300 (25 ton). Motor codes D and W only (no L).
• Only 208/230/3/60 and 460/3/60 are included; 575/3/60 excluded per request.
• ULN is a heat-exchanger option (nomenclature position 15) in this size range, but no separate ULN
ratings are published, so nothing needed to be excluded.
COOLING (source: Expanded Cooling Data, pages 17-22)
• Tables are titled "DSG180*D" etc., i.e. the 3-6 ton convention: * = voltage digit, D = standard-static motor.
• Airflows: DSG180 = 4500/5012/6000, DSG240 = 6000/6400/8000, DSG300 = 7500/7650/10000 CFM.
The middle value is the nominal indoor CFM from Product Specifications (5000 / 6400 / 7650).
• This spec sheet omits the "Amps" row that SS-DSG7-R32 prints; MBh / S/T / ∆T are unaffected.
• 71°F WB at 70°F DB is printed "-" and is omitted, same as every other size range.
• No 240.0-style misprints and no duplicated cabinets were found in these six pages.
GAS HEATING (source: Product Specifications "HEATING CAPACITY" blocks, pages 9-14)
• SS-DSG15-R32 has no standalone heating rating table, so values come from the per-model spec columns.
• Heating is IDENTICAL for all three cabinets, both voltages and both motors — only the heat range varies:
Low = 260/210.6 MBH high stage (6 burners), Medium = 360/291.6 (8), High = 400/324 (8).
• Low stage is 75% of high stage input, as in the smaller sizes.
• Temp rise differs from the 7.5-12.5 ton units: high stage 25-55°F, low stage 15-45°F.
• Thermal Efficiency 81% (these units have no AFUE rating).
ELECTRICAL DATA (source: Electrical Data, pages 80-81)
• These units also offer a MODULATING power exhaust (six MCA/MOP combinations in the spec sheet instead
of four). Those two extra combinations are DELIBERATELY NOT CARRIED here — modulating power exhaust is
rarely specified on this class of RTU. Only the base / +conv. outlet / +power exhaust / +both columns are kept.
• If it is ever needed: SS-DSG15-R32 pages 80-81, modulating FLA 13.9 (208/230V), 8.1 (460V).
• Dual values "x/y" on 208/230V models = 208V/230V ratings.
SCHEMA CHANGES MADE BY HAND 8/15/2026
• Gas Heating: the AFUE (%) column was removed. Every 3-phase model in this workbook is rated by Thermal
Efficiency, so AFUE was "N/A" on every row. Single-phase gas packs are AFUE-rated but are not in this file.
• Electrical Data: the five modulating-power-exhaust columns (O-S) were removed — see the 15-25 ton section.
The sheet is back to its original 14-column layout for all sizes.
DHG 3-6 Ton, HIGH Efficiency, R-32 Gas/Electric — added 8/15/2026
Source: Daikin Spec Sheet SS-DHG3-R32 (ss-dhg3-r32.pdf).
• First high-efficiency (DHG) family in this workbook — everything above it is standard-efficiency DSG.
Match on the DSG/DHG prefix, not on tonnage alone: DSG036 and DHG036 are both 3 ton but different units.
• Only 208/230/3/60 and 460/3/60 are included; single phase (voltage 1) and 575/3/60 excluded.
COOLING (source: Expanded Cooling Data, pages 25-40)
• EVERY DHG cabinet is two-stage, so all four have a 70% low-stage table — 8 tables in total, 270 rows each.
Rows are named "DHG036*" and "DHG036* (70% - Low Stage)", following the DSG072*D low-stage convention.
• Full-load airflows: 036 = 900/1160/1500, 048 = 1200/1460/2000, 060 = 1500/1880/2500, 072 = 1800/2150/3000.
Low-stage airflows: 036 = 630/970/1050, 048 = 840/1060/1400, 060 = 1050/1240/1750, 072 = 1260/1520/2100.
• The cooling table headings print the cabinet only ("DHG036"); the AHRI Ratings table on page 21 of the same
spec sheet writes the same units as "DHG036*D", so the tables are not motor-specific in this document.
• 71°F WB at 70°F DB is printed "-" and is omitted, same as every other family.
• No duplicated cabinets and no misprinted cells were found across these 16 pages.
GAS HEATING (source: Heating Rating Table - Natural Gas and Propane, page 41)
• 3-phase rows only. The ULN Heating Rating Table on page 42 is excluded per request.
• This sheet labels the columns "Stage 1" and "Stage 2" rather than High/Low. Stage 1 is HIGH fire
(it pairs with the Temp Rise High column) and Stage 2 is low fire at 75% of stage 1, matching the DSG layout.
• Daikin's own inconsistency, recorded verbatim: the outputs are computed at 81% (45 → 36.45) but the
Thermal Efficiency column still reads 80% for 3-phase. Standard-efficiency DSG prints 80% outputs (45 → 36).
• DHG072 has no single-phase offering, so its heat sizes differ (70/125/150 MBH vs 70/115/140 on DHG048/060).
ELECTRICAL DATA (source: Electrical Data, pages 91-92)
• Same four MCA/MOP combinations as the DSG 3-6 ton units, so no schema change was needed.
• The spec sheet adds Optional Electric Heat columns (Part # / kW / FLA); they are blank on every gas/electric
row and are not carried here.
• ULN is a heat-exchanger option only — no separate ULN electrical ratings are published.
• NOT a copy/paste bug: all four DHG072 rows match their DSG072 counterparts exactly. The 6-ton high- and
standard-efficiency units share an electrical package; their COOLING tables do differ (verified point by point).
DHG 7.5-12.5 Ton, HIGH Efficiency, R-32 Gas/Electric — added 8/15/2026
Source: Daikin Spec Sheet SS-DHG7-R32 (ss-dhg7-r32.pdf).
• Models: DHG090 (7.5), DHG102 (8.5), DHG120 (10), DHG150 (12.5 ton). Motor codes D / L / W.
• Only 208/230/3/60 and 460/3/60 are included; 575/3/60 excluded per request.
COOLING (source: Expanded Cooling Data, pages 21-28)
• DHG150 COOLING IS PRESENT AND CORRECT HERE — unlike standard-efficiency DSG150, whose tables are
misprinted in SS-DSG7-R32. Verified distinct from DHG120 (140.4 vs 118.6 MBh at 70/59/65) with its own
airflows. This does NOT fill the DSG150 gap; the two are different units.
• Airflows: 090 = 2625/3000/3375, 102 = 2800/3025/3600, 120 = 3250/3500/4150, 150 = 3500/3800/4500.
• Tables are titled by cabinet only ("DHG090"), so rows are named "DHG090*" with no motor suffix.
• Single-stage tables only — unlike DHG 3-6 ton, no 70% low-stage tables are published in this size range.
• 71°F WB at 70°F DB is printed "-" and is omitted. No misprints or duplicated cabinets found.
GAS HEATING (source: Heating Rating Table - Natural Gas and Propane, page 29)
• Heat sizes: DHG090/DHG102 = 130/180/225 MBH, DHG120/DHG150 = 130/180/240 MBH. Thermal Efficiency 81%.
• Input/output values match standard-efficiency DSG 7.5-12.5, but the TEMP RISE RANGES DO NOT —
DHG090/102 High is 40-70°F (DSG is 30-60) and DHG150 High is 35-65°F (DSG is 30-60). Do not copy across.
• Low stage is 75% of high stage input. LP high-fire rate is reduced 10% vs natural gas.
ELECTRICAL DATA (source: Electrical Data, pages 94-96)
• Same four MCA/MOP combinations as the DSG units; no schema change needed.
• Dual values "x/y" on 208/230V models = 208V/230V ratings.
• Verified, not a paste bug: all DHG090 and DHG102 rows equal their DSG twins (shared electrical package at
those sizes); DHG120/DHG150 mostly differ, with DHG1204W the one incidental match. Cooling tables differ throughout.
INDOOR MOTOR HP column added 8/15/2026 (Electrical Data column O)
• Taken from the Indoor Fan Motor group of each spec sheet’s electrical table (QTY / HP / FLA).
• Cross-checked against GAS PACKS DATA.xlsx column V on all 30 overlapping D-motor models — exact match.
• The eight DSG 3-6 ton W-motor rows are BLANK: SS-DSG3-R32 was not available when this column was built.
Their D-motor values came from GAS PACKS DATA.xlsx instead. Fill the W rows from SS-DSG3-R32 when it is at hand.
HEAT PUMP RTUs — DSH (standard eff.), DHH (high eff.), DVH (variable speed), R-32 — added 9/23/2026
Sources: Daikin spec sheets in ASSETS\DAIKIN LIGHT COMMERCIAL RTU\ENGINEERING MANUALS —
SS-DSH3-R32 (06/26), SS-DSH7-R32 (06/26), SS-DSH15-R32 (08/26), SS-DHH3-R32 (06/26), SS-DVH7-R32 (undated).
• 100% capacity data only: the DSH072 and DHH036-072 70% low-stage tables are NOT carried (unlike the DSG/DHG rows).
• DVH COOLING: the 'Maximum' compressor-speed tables are carried as 100%. Minimum and Rated tables are not.
Checked: LC RTU DATA's DVH cooling (e.g. DVH090 102,928 / 79,341 BTU/h) equals the Maximum table exactly.
• DVH HEATING: the 'Rated' tables (changed from Maximum 9/28/2026 - see HEAT PUMP sheet below).
• Only 208/230/3/60 and 460/3/60 and only D (standard static) / W (high static) motors. 575V, single phase and
the L (medium static) motors on DSH 7.5-12.5 are excluded.
COOLING sheet
• Rows added: DSH 3490, DHH 1080, DVH 4752. Names follow the table titles: DSH036*D (3-6 ton,
motor-specific title), DSH090* / DSH180* / DHH036* / DVH090* (cabinet-only titles). '-' cells are omitted.
• DSH 15-20 tables have 5 airflows, EAT DB 70-90 and OA DB 65-125 (one more ambient than the smaller sizes).
• DVH publishes gross evaporator TC / SC (blower heat NOT subtracted), 7 WB values (57-75) and OA DB 23-118°F.
MBh = TC, S/T = SC/TC and ∆T = SC / (1.10 × CFM) - CALCULATED, using the 1.10 factor that every
DSH/DHH table's own S/T and ∆T agree on. The whole DVH grid is shaded 'reference data' in the spec sheet.
• DHH048 (SS-DHH3 p21): the 70°F EAT block is printed in a different layout (Capacity in BTU/h, 'Evap dT',
no 71°F WB column) and its S/T disagrees with its own ∆T (e.g. S/T 1.00 where ∆T implies ~0.63).
MBh and ∆T are kept as printed; S/T was RECALCULATED from ∆T (1.10 factor) on all 54 points of that block.
• SS-DVH7 p23 (DVH090 Maximum, 85°F EAT) prints a stray extra 'PI' column at the right edge - ignored.
HEAT PUMP sheet (new) - heat pump heating capacity
• DSH / DHH: Daikin 'Heating Data' tables, 100% capacity, 70°F EAT DB at the NOMINAL CFM from Product
Specifications (the tables say 'Calculations are based on nominal CFM'). OA DB 65 to -5°F (DSH 15-20: 65 to 0).
∆T = the table's T/R (temperature rise); kW = total system power; COP as printed.
• DVH: 'Expanded Heating Data' RATED tables. These are indexed by OUTDOOR WET BULB (-13 to 65°F), 6 indoor
temps (61-75°F) and 3 airflows, so the OA WB column is used and OA DB is blank. MBh = condenser TC (blower
heat NOT added); kW = PI = compressor + outdoor fan only (excludes the indoor blower, unlike DSH/DHH);
∆T = TC / (1.08 × CFM) - CALCULATED (1.08 is the factor the DSH/DHH T/R values use); COP not published.
Changed 9/28/2026 from the Maximum tables (Eric). Maximum is the compressor's top speed and ran far above the
AHRI ratings (DVH090 140.04 MBh at 45°F WB vs 90,000 AHRI at 47°F); Rated at 45°F WB is 89.73 / 90.62 /
90.73 MBh at 2550 / 2950 / 3350 CFM. Neither grid reproduces the AHRI 17°F rating (DVH090 63,000 vs Rated
50.82 / Maximum 93.23 MBh at 15°F WB, 2950 CFM, 70°F EAT).
6 Rated cells are blank in the spec sheet ('operation at this compressor speed is not possible') and are
omitted: 65°F WB at 75°F EAT (DVH090 2550, DVH102 2700 and 3100, DVH120 3200 CFM), DVH102 2700 CFM at
65°F WB / 72°F EAT and at 60°F WB / 75°F EAT.
• Misprints fixed from the table's own columns:
DHH036 10°F: printed 15.45 MBh; COP × kW and T/R both give 14.46 - 14.46 used.
DHH036 5°F: printed 15.00 MBh / COP 1.85 disagree with each other and with T/R - MBh and COP left BLANK.
(T/R and the straight-line trend 16.99 / 14.46 / ? / 9.39 point to ~11.92 MBh, COP ~1.60.)
DSH090 47°F: printed kW 7.08 is out of line (7.40 at 50°F, 7.28 at 45°F); MBh / COP give 7.33 - used.
DSH240 (SS-DSH15 p33): row labels are printed as numbers; rows taken in the DSH180 order MBh / T/R / kW / COP
(checked: COP = MBh / (kW × 3.412) on every column).
• These tables do not exactly equal the AHRI ratings in LC RTU DATA for DSH090/102/120 (e.g. DSH102 at 47°F is
100.0 MBh in the table vs 97,000 AHRI). LC RTU DATA's values are the AHRI ones and are correct as AHRI data.
ELECTRICAL DATA sheet - heat pump rows
• Columns E-G (Electric Heat kW / Kit / FLA) were inserted after Power Supply on 9/23/2026. They are blank on the
gas pack rows. Heat pumps have one row per model + heat kit; kW 0 = no electric heat.
• Electric Heat kW is the NOMINAL kit size from the part number (EH*D-3S05A = 5 kW), which is what LC RTU DATA
column W uses. The spec sheets print the actual output: 208/230V kits as 208V/240V (e.g. 3.8/5.0) and 460V
30/45/60/75 kW kits as 28.8/43.2/57.6/72.0.
• Same four MCA/MOP combinations as the gas packs. DSH 15-20 also publishes a MODULATING power exhaust; as with
DSG 15-25 it is not carried.
• DVH1203W (SS-DVH7 p63) is misprinted: the MCA values sit under the Power Exhaust FLA heading and two MOP
columns follow that disagree on the power-exhaust rows. MCA is carried (read by row position: base / outlet /
exhaust / both); ALL MOP cells are left BLANK until Daikin confirms. Its Power Exhaust FLA (3.3/3.0 (2.4)) is
taken from DVH1203D - the same accessory, identical on every other DVH D/W pair.
• Daikin oddities kept as printed: DSH2403 60 kW and 75 kW both show 249 MCA at 208V, and several 60 kW 208/230V
rows show a lower 230V MCA than 208V (e.g. DSH1803D 239/227). LC RTU DATA matches these.
• Cross-check 9/23/2026: all 137 heat pump rows in LC RTU DATA (MCA / MOCP / indoor HP) equal the D-motor,
no-outlet, no-exhaust row here for the same kW.
convert_to_json.py
• convert_gas_pack_capacity() reads every family here, heat pumps included (Heat Pump sheet -> hpHeat, 9/23/2026).
Eric runs it to regenerate DATA/JSON/gas_pack_capacity.json after any change to this workbook.
AIRFLOW and AIRFLOW - ELECTRIC HEAT sheets (added 10/1/2026)
Source: the downflow fan tables ("Airflow" / "Airflow Data" / "Fan Data") in each family's engineering manual - SS-DSG3, SS-DSG7, SS-DSG15, SS-DHG3, SS-DHG7, SS-DSH3, SS-DSH7, SS-DSH15, SS-DHH3 and SS-DVH7 (-R32) - plus the airflow limits Daikin prints in them. Manual + Pages on each row point at the fan table used.
These sheets feed the "?" beside ESP on the LC RTU product page and beside Motor in Design Search. They are not shown on the project schedule or in any export.
• One row per cabinet + drive (D - Standard Static, W - High Static) + gas heat size. Medium Static (L), horizontal, DDC% and ULN tables are not used. Tables printed for both downflow and horizontal (DSG 15-25, DSH 15-20) are used as printed.
• Only the standard cooling speed taps are used. Taps a footnote or legend restricts are left out: fan mode only, part load only, heat mode / gas heating / supplemental heat (shaded) taps, and the primed taps (T1'-T5', T1'H...) that the wiring diagrams assign to TB1-DH = 24 VAC.
• ESP Min / Max = the lowest and highest external static the drive's fan table prints for those taps.
• CFM Min = Daikin's published cooling minimum, or the lowest airflow the fan table reaches if that is higher. Published minimums: the Min-Max Airflow Range tables (DSG/DHG 3-6), the electric heater tables (DSH/DHH 3-6) and the "air flow below 300 SCFM/ton is not recommended for High Stage cooling or heating" notes (DHG/DHH). Where a manual prints no minimum (DSG 7.5-25, DSH 7.5-20, DVH), the same 300 SCFM/ton is applied.
• CFM Max = Daikin's published maximum (3-6 ton: 500 SCFM/ton) or the most the fan table moves, whichever is lower. Larger units publish no cooling maximum, so it is the fan table's highest cooling-tap airflow.
• Max CFM at ESP Max = the most the cooling taps move at the top ESP. The site shows it only when it is lower than CFM Max.
• Where the manual prints separate standard-static tables per voltage (208/230 V vs 460/575 V on the 3-5 ton DSG / DHG / DSH), each value is the one that holds for both.
• Gas Heat Min / Max CFM = Daikin's heating airflow limits for that burner at high fire: Min-Max Airflow Range (3-6 ton, minimum only) and Recommended Minimum / Maximum Airflow (7.5-12.5 ton). DSG 15-25 publishes none.
• Airflow - Electric Heat: minimum (and, where printed, maximum) airflow per heat pump drive + heater kit, from the Electrical Heater Data / Min Airflow tables (DSH/DHH 3-6, DSH 7.5-20, DVH).
• Misprints noticed in the fan tables (left as printed; none of them moves a range): DHG3 p52 T5C 198 CFM at 1.6 in.; DHG3 p58-59 T3C 1098 at 0.8 in.; DHG3 p51 title DHG0607D for DHG0727D; DSG3 p50 header DSG0483D for DSG0484D; DSG3 p74 header DFG048W; DSG7 p58 caption DFG1207D; DSH3 p38 caption DSH06083W; DVH p42 lists DVH1023 twice (the 3200 CFM row is DVH1203/1204); DSH15 p40 20-ton High Static electric heat minimum (6100) is lower than Standard Static (6500).