## NOTES
MINI SPLIT & SKY AIR CAPACITY TABLES - NOTES
Source: Daikin capacity table PDFs (Fahrenheit tables only). One tab per outdoor unit - indoor unit matchup, named "ODU - IDU".
Layout follows Multi Position Split Capacity Tables.xlsx. This NOTES tab has no " - " in its name so convert_to_json.py skips it.
COOLING TABLE (columns A-F, long form)
IDB / IWB Entering air dry bulb / wet bulb, deg F. The PDF pairs (68/57.2, 71.6/60.8, 77/64.4, 80/67, 86/71.6, 89.6/75.2) are
recorded as the nominal pairs 68/57, 72/61, 77/64, 80/67, 86/72, 90/75. Sky Air tables list wet bulb only; the same
nominal dry bulbs are assumed, and the extra 70 WB column is paired with 84 DB (interpolated).
OA Ambient Outdoor dry bulb, deg F.
Airflow CFM. Mini splits: PDF cooling AFR (m3/min) x 35.3147, rounded. Sky Air PDFs list no airflow; CFM taken from the
MINI SPLIT DATA / MULTI POSITION SPLIT DATA schedule files.
VALUE rows MBh = total capacity (kBtu/h) from the PDF.
S/T = sensible / total, from the PDF sensible capacity (capped at 1.0 where the PDF sensible exceeds total).
∆T = dry bulb drop, deg F = sensible Btu/h / (1.08 x CFM).
LDB = leaving dry bulb = IDB - ∆T.
LWB = leaving wet bulb, from leaving enthalpy = entering enthalpy - total Btu/h / (4.5 x CFM), at sea level.
Where the calculation lands beyond saturation the leaving air is reported saturated (LWB = LDB).
kW = compressor + fan power input from the PDF.
HEATING TABLE (columns H-L)
Ambient DB / WB Outdoor dry bulb / wet bulb, deg F, rounded to whole degrees (PDF lists e.g. 43 WB / 47 DB, 14 WB / 15.8 DB).
Aurora and Oterra heat pump PDFs list outdoor wet bulb only; dry bulbs are the same Daikin rating points
the other series print (-13/-13, -4/-4, 5/5, 14/15.8, 23/24.8, 32/34.7, 43/47, 50/59, 60 or 64/75.2).
IDB Entering (indoor) dry bulb, deg F, rounded (59, 70, 71.6->72, 75.2->75, 77, 80.6->81).
MBH / kW Total heating capacity (kBtu/h) and power input from the PDF.
Cooling-only matchups (Oterra FTKF + RKF, Polara FTXV + RKV) have no heating table.
Heating capacities do not include the frost / defrost correction (see the RZA capacity correction notes, and equivalent
notes in each mini split engineering manual).

## RXM09WVJU9 - FTXM09WVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 516 | 57 | MBh | 13.97 | 75 | 60 | 59 | 24.36 | 1.88
68 | 50 | 516 | 57 | S/T | 0.795 | 75 | 60 | 70 | 23.68 | 1.92
68 | 50 | 516 | 57 | ∆T | 19.9 | 75 | 60 | 72 | 23.41 | 1.94
68 | 50 | 516 | 57 | LDB | 48.1 | 75 | 60 | 75 | 23.15 | 1.95
68 | 50 | 516 | 57 | LWB | 46.4 | 75 | 60 | 77 | 23.01 | 1.96
68 | 50 | 516 | 57 | kW | 0.53 | 75 | 60 | 81 | 22.74 | 1.98
72 | 50 | 516 | 61 | MBh | 14.54 | 47 | 43 | 59 | 20.17 | 1.74
72 | 50 | 516 | 61 | S/T | 0.749 | 47 | 43 | 70 | 19.5 | 1.78
72 | 50 | 516 | 61 | ∆T | 19.5 | 47 | 43 | 72 | 19.23 | 1.8
72 | 50 | 516 | 61 | LDB | 52.5 | 47 | 43 | 75 | 18.96 | 1.81
72 | 50 | 516 | 61 | LWB | 50.9 | 47 | 43 | 77 | 18.83 | 1.82
72 | 50 | 516 | 61 | kW | 0.54 | 47 | 43 | 81 | 18.56 | 1.84
77 | 50 | 516 | 64 | MBh | 15.12 | 35 | 32 | 59 | 17.75 | 1.69
77 | 50 | 516 | 64 | S/T | 0.76 | 35 | 32 | 70 | 17.07 | 1.73
77 | 50 | 516 | 64 | ∆T | 20.6 | 35 | 32 | 72 | 16.8 | 1.75
77 | 50 | 516 | 64 | LDB | 56.4 | 35 | 32 | 75 | 16.53 | 1.76
77 | 50 | 516 | 64 | LWB | 54.1 | 35 | 32 | 77 | 16.39 | 1.77
77 | 50 | 516 | 64 | kW | 0.54 | 35 | 32 | 81 | 16.12 | 1.79
80 | 50 | 516 | 67 | MBh | 15.41 | 25 | 23 | 59 | 15.74 | 1.65
80 | 50 | 516 | 67 | S/T | 0.792 | 25 | 23 | 70 | 15.05 | 1.69
80 | 50 | 516 | 67 | ∆T | 21.9 | 25 | 23 | 72 | 14.77 | 1.71
80 | 50 | 516 | 67 | LDB | 58.1 | 25 | 23 | 75 | 14.49 | 1.73
80 | 50 | 516 | 67 | LWB | 57.6 | 25 | 23 | 77 | 14.36 | 1.73
80 | 50 | 516 | 67 | kW | 0.54 | 25 | 23 | 81 | 14.08 | 1.75
86 | 50 | 516 | 72 | MBh | 16.27 | 16 | 14 | 59 | 13.73 | 1.61
86 | 50 | 516 | 72 | S/T | 0.725 | 16 | 14 | 70 | 13.02 | 1.65
86 | 50 | 516 | 72 | ∆T | 21.2 | 16 | 14 | 72 | 12.74 | 1.67
86 | 50 | 516 | 72 | LDB | 64.8 | 16 | 14 | 75 | 12.46 | 1.69
86 | 50 | 516 | 72 | LWB | 63.2 | 16 | 14 | 77 | 12.32 | 1.69
86 | 50 | 516 | 72 | kW | 0.55 | 16 | 14 | 81 | 12.04 | 1.71
90 | 50 | 516 | 75 | MBh | 16.85 | 5 | 5 | 59 | 11.72 | 1.57
90 | 50 | 516 | 75 | S/T | 0.682 | 5 | 5 | 70 | 11 | 1.61
90 | 50 | 516 | 75 | ∆T | 20.6 | 5 | 5 | 72 | 10.71 | 1.63
90 | 50 | 516 | 75 | LDB | 69.4 | 5 | 5 | 75 | 10.42 | 1.65
90 | 50 | 516 | 75 | LWB | 66.5 | 5 | 5 | 77 | 10.28 | 1.66
90 | 50 | 516 | 75 | kW | 0.68 | 5 | 5 | 81 | 9.99 | 1.67
68 | 68 | 516 | 57 | MBh | 12.81 | -4 | -4 | 59 | 11.38 | 1.56
68 | 68 | 516 | 57 | S/T | 0.823 | -4 | -4 | 70 | 10.5 | 1.61
68 | 68 | 516 | 57 | ∆T | 18.9 | -4 | -4 | 72 | 10.15 | 1.62
68 | 68 | 516 | 57 | LDB | 49.1 | -4 | -4 | 75 | 9.8 | 1.64
68 | 68 | 516 | 57 | LWB | 47.4 | -4 | -4 | 77 | 9.62 | 1.65
68 | 68 | 516 | 57 | kW | 0.66 | -4 | -4 | 81 | 9.27 | 1.67
72 | 68 | 516 | 61 | MBh | 13.38 | -13 | -13 | 59 | 11.15 | 1.55
72 | 68 | 516 | 61 | S/T | 0.775 | -13 | -13 | 70 | 10 | 1.6
72 | 68 | 516 | 61 | ∆T | 18.6 | -13 | -13 | 72 | 9.54 | 1.62
72 | 68 | 516 | 61 | LDB | 53.4 | -13 | -13 | 75 | 9.08 | 1.64
72 | 68 | 516 | 61 | LWB | 51.8 | -13 | -13 | 77 | 8.85 | 1.65
72 | 68 | 516 | 61 | kW | 0.66 | -13 | -13 | 81 | 8.39 | 1.67
77 | 68 | 516 | 64 | MBh | 13.96
77 | 68 | 516 | 64 | S/T | 0.789
77 | 68 | 516 | 64 | ∆T | 19.8
77 | 68 | 516 | 64 | LDB | 57.2
77 | 68 | 516 | 64 | LWB | 55
77 | 68 | 516 | 64 | kW | 0.67
80 | 68 | 516 | 67 | MBh | 14.24
80 | 68 | 516 | 67 | S/T | 0.825
80 | 68 | 516 | 67 | ∆T | 21.1
80 | 68 | 516 | 67 | LDB | 58.9
80 | 68 | 516 | 67 | LWB | 58.4
80 | 68 | 516 | 67 | kW | 0.67
86 | 68 | 516 | 72 | MBh | 15.11
86 | 68 | 516 | 72 | S/T | 0.753
86 | 68 | 516 | 72 | ∆T | 20.4
86 | 68 | 516 | 72 | LDB | 65.6
86 | 68 | 516 | 72 | LWB | 63.8
86 | 68 | 516 | 72 | kW | 0.67
90 | 68 | 516 | 75 | MBh | 15.68
90 | 68 | 516 | 75 | S/T | 0.71
90 | 68 | 516 | 75 | ∆T | 20
90 | 68 | 516 | 75 | LDB | 70
90 | 68 | 516 | 75 | LWB | 67.1
90 | 68 | 516 | 75 | kW | 0.68
68 | 86 | 516 | 57 | MBh | 11.64
68 | 86 | 516 | 57 | S/T | 0.859
68 | 86 | 516 | 57 | ∆T | 17.9
68 | 86 | 516 | 57 | LDB | 50.1
68 | 86 | 516 | 57 | LWB | 48.3
68 | 86 | 516 | 57 | kW | 0.79
72 | 86 | 516 | 61 | MBh | 12.22
72 | 86 | 516 | 61 | S/T | 0.807
72 | 86 | 516 | 61 | ∆T | 17.7
72 | 86 | 516 | 61 | LDB | 54.3
72 | 86 | 516 | 61 | LWB | 52.6
72 | 86 | 516 | 61 | kW | 0.79
77 | 86 | 516 | 64 | MBh | 12.79
77 | 86 | 516 | 64 | S/T | 0.824
77 | 86 | 516 | 64 | ∆T | 18.9
77 | 86 | 516 | 64 | LDB | 58.1
77 | 86 | 516 | 64 | LWB | 55.8
77 | 86 | 516 | 64 | kW | 0.79
80 | 86 | 516 | 67 | MBh | 13.08
80 | 86 | 516 | 67 | S/T | 0.864
80 | 86 | 516 | 67 | ∆T | 20.3
80 | 86 | 516 | 67 | LDB | 59.7
80 | 86 | 516 | 67 | LWB | 59.1
80 | 86 | 516 | 67 | kW | 0.8
86 | 86 | 516 | 72 | MBh | 13.94
86 | 86 | 516 | 72 | S/T | 0.788
86 | 86 | 516 | 72 | ∆T | 19.7
86 | 86 | 516 | 72 | LDB | 66.3
86 | 86 | 516 | 72 | LWB | 64.5
86 | 86 | 516 | 72 | kW | 0.8
90 | 86 | 516 | 75 | MBh | 14.52
90 | 86 | 516 | 75 | S/T | 0.742
90 | 86 | 516 | 75 | ∆T | 19.3
90 | 86 | 516 | 75 | LDB | 70.7
90 | 86 | 516 | 75 | LWB | 67.7
90 | 86 | 516 | 75 | kW | 0.81
68 | 95 | 516 | 57 | MBh | 11.06
68 | 95 | 516 | 57 | S/T | 0.88
68 | 95 | 516 | 57 | ∆T | 17.5
68 | 95 | 516 | 57 | LDB | 50.5
68 | 95 | 516 | 57 | LWB | 48.8
68 | 95 | 516 | 57 | kW | 0.85
72 | 95 | 516 | 61 | MBh | 11.64
72 | 95 | 516 | 61 | S/T | 0.826
72 | 95 | 516 | 61 | ∆T | 17.2
72 | 95 | 516 | 61 | LDB | 54.8
72 | 95 | 516 | 61 | LWB | 53.1
72 | 95 | 516 | 61 | kW | 0.85
77 | 95 | 516 | 64 | MBh | 12.21
77 | 95 | 516 | 64 | S/T | 0.844
77 | 95 | 516 | 64 | ∆T | 18.5
77 | 95 | 516 | 64 | LDB | 58.5
77 | 95 | 516 | 64 | LWB | 56.2
77 | 95 | 516 | 64 | kW | 0.86
80 | 95 | 516 | 67 | MBh | 12.5
80 | 95 | 516 | 67 | S/T | 0.886
80 | 95 | 516 | 67 | ∆T | 19.9
80 | 95 | 516 | 67 | LDB | 60.1
80 | 95 | 516 | 67 | LWB | 59.5
80 | 95 | 516 | 67 | kW | 0.86
86 | 95 | 516 | 72 | MBh | 13.36
86 | 95 | 516 | 72 | S/T | 0.808
86 | 95 | 516 | 72 | ∆T | 19.4
86 | 95 | 516 | 72 | LDB | 66.6
86 | 95 | 516 | 72 | LWB | 64.8
86 | 95 | 516 | 72 | kW | 0.87
90 | 95 | 516 | 75 | MBh | 13.94
90 | 95 | 516 | 75 | S/T | 0.76
90 | 95 | 516 | 75 | ∆T | 19
90 | 95 | 516 | 75 | LDB | 71
90 | 95 | 516 | 75 | LWB | 68
90 | 95 | 516 | 75 | kW | 0.87
68 | 104 | 516 | 57 | MBh | 10.48
68 | 104 | 516 | 57 | S/T | 0.904
68 | 104 | 516 | 57 | ∆T | 17
68 | 104 | 516 | 57 | LDB | 51
68 | 104 | 516 | 57 | LWB | 49.3
68 | 104 | 516 | 57 | kW | 0.91
72 | 104 | 516 | 61 | MBh | 11.05
72 | 104 | 516 | 61 | S/T | 0.847
72 | 104 | 516 | 61 | ∆T | 16.8
72 | 104 | 516 | 61 | LDB | 55.2
72 | 104 | 516 | 61 | LWB | 53.5
72 | 104 | 516 | 61 | kW | 0.92
77 | 104 | 516 | 64 | MBh | 11.63
77 | 104 | 516 | 64 | S/T | 0.867
77 | 104 | 516 | 64 | ∆T | 18.1
77 | 104 | 516 | 64 | LDB | 58.9
77 | 104 | 516 | 64 | LWB | 56.6
77 | 104 | 516 | 64 | kW | 0.92
80 | 104 | 516 | 67 | MBh | 11.92
80 | 104 | 516 | 67 | S/T | 0.91
80 | 104 | 516 | 67 | ∆T | 19.5
80 | 104 | 516 | 67 | LDB | 60.5
80 | 104 | 516 | 67 | LWB | 59.9
80 | 104 | 516 | 67 | kW | 0.92
86 | 104 | 516 | 72 | MBh | 12.78
86 | 104 | 516 | 72 | S/T | 0.829
86 | 104 | 516 | 72 | ∆T | 19
86 | 104 | 516 | 72 | LDB | 67
86 | 104 | 516 | 72 | LWB | 65.2
86 | 104 | 516 | 72 | kW | 0.93
90 | 104 | 516 | 75 | MBh | 13.36
90 | 104 | 516 | 75 | S/T | 0.779
90 | 104 | 516 | 75 | ∆T | 18.7
90 | 104 | 516 | 75 | LDB | 71.3
90 | 104 | 516 | 75 | LWB | 68.3
90 | 104 | 516 | 75 | kW | 0.93
68 | 115 | 516 | 57 | MBh | 9.78
68 | 115 | 516 | 57 | S/T | 0.936
68 | 115 | 516 | 57 | ∆T | 16.4
68 | 115 | 516 | 57 | LDB | 51.6
68 | 115 | 516 | 57 | LWB | 49.8
68 | 115 | 516 | 57 | kW | 0.99
72 | 115 | 516 | 61 | MBh | 10.35
72 | 115 | 516 | 61 | S/T | 0.876
72 | 115 | 516 | 61 | ∆T | 16.3
72 | 115 | 516 | 61 | LDB | 55.7
72 | 115 | 516 | 61 | LWB | 54
72 | 115 | 516 | 61 | kW | 0.99
77 | 115 | 516 | 64 | MBh | 10.93
77 | 115 | 516 | 64 | S/T | 0.897
77 | 115 | 516 | 64 | ∆T | 17.6
77 | 115 | 516 | 64 | LDB | 59.4
77 | 115 | 516 | 64 | LWB | 57
77 | 115 | 516 | 64 | kW | 1
80 | 115 | 516 | 67 | MBh | 11.22
80 | 115 | 516 | 67 | S/T | 0.944
80 | 115 | 516 | 67 | ∆T | 19
80 | 115 | 516 | 67 | LDB | 61
80 | 115 | 516 | 67 | LWB | 60.3
80 | 115 | 516 | 67 | kW | 1
86 | 115 | 516 | 72 | MBh | 12.08
86 | 115 | 516 | 72 | S/T | 0.858
86 | 115 | 516 | 72 | ∆T | 18.6
86 | 115 | 516 | 72 | LDB | 67.4
86 | 115 | 516 | 72 | LWB | 65.6
86 | 115 | 516 | 72 | kW | 1.01
90 | 115 | 516 | 75 | MBh | 12.66
90 | 115 | 516 | 75 | S/T | 0.806
90 | 115 | 516 | 75 | ∆T | 18.3
90 | 115 | 516 | 75 | LDB | 71.7
90 | 115 | 516 | 75 | LWB | 68.7
90 | 115 | 516 | 75 | kW | 1.01

## RXM12WVJU9 - FTXM12WVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 558 | 57 | MBh | 17.85 | 75 | 60 | 59 | 28.2 | 2.42
68 | 50 | 558 | 57 | S/T | 0.748 | 75 | 60 | 70 | 27.34 | 2.42
68 | 50 | 558 | 57 | ∆T | 22.2 | 75 | 60 | 72 | 27.01 | 2.42
68 | 50 | 558 | 57 | LDB | 45.8 | 75 | 60 | 75 | 26.69 | 2.42
68 | 50 | 558 | 57 | LWB | 44.3 | 75 | 60 | 77 | 26.54 | 2.42
68 | 50 | 558 | 57 | kW | 0.87 | 75 | 60 | 81 | 26.23 | 2.42
72 | 50 | 558 | 61 | MBh | 18.58 | 47 | 43 | 59 | 23.38 | 2.25
72 | 50 | 558 | 61 | S/T | 0.705 | 47 | 43 | 70 | 22.6 | 2.3
72 | 50 | 558 | 61 | ∆T | 21.7 | 47 | 43 | 72 | 22.29 | 2.32
72 | 50 | 558 | 61 | LDB | 50.3 | 47 | 43 | 75 | 21.98 | 2.34
72 | 50 | 558 | 61 | LWB | 48.8 | 47 | 43 | 77 | 21.82 | 2.35
72 | 50 | 558 | 61 | kW | 0.87 | 47 | 43 | 81 | 21.51 | 2.37
77 | 50 | 558 | 64 | MBh | 19.32 | 35 | 32 | 59 | 20.83 | 2.16
77 | 50 | 558 | 64 | S/T | 0.709 | 35 | 32 | 70 | 20.03 | 2.21
77 | 50 | 558 | 64 | ∆T | 22.7 | 35 | 32 | 72 | 19.71 | 2.23
77 | 50 | 558 | 64 | LDB | 54.3 | 35 | 32 | 75 | 19.39 | 2.25
77 | 50 | 558 | 64 | LWB | 52.1 | 35 | 32 | 77 | 19.23 | 2.26
77 | 50 | 558 | 64 | kW | 0.88 | 35 | 32 | 81 | 18.91 | 2.29
80 | 50 | 558 | 67 | MBh | 19.69 | 25 | 23 | 59 | 18.71 | 2.09
80 | 50 | 558 | 67 | S/T | 0.734 | 25 | 23 | 70 | 17.89 | 2.14
80 | 50 | 558 | 67 | ∆T | 24 | 25 | 23 | 72 | 17.56 | 2.16
80 | 50 | 558 | 67 | LDB | 56 | 25 | 23 | 75 | 17.23 | 2.18
80 | 50 | 558 | 67 | LWB | 55.7 | 25 | 23 | 77 | 17.06 | 2.19
80 | 50 | 558 | 67 | kW | 0.88 | 25 | 23 | 81 | 16.74 | 2.21
86 | 50 | 558 | 72 | MBh | 20.79 | 16 | 14 | 59 | 16.59 | 2.01
86 | 50 | 558 | 72 | S/T | 0.669 | 16 | 14 | 70 | 15.74 | 2.07
86 | 50 | 558 | 72 | ∆T | 23.1 | 16 | 14 | 72 | 15.4 | 2.09
86 | 50 | 558 | 72 | LDB | 62.9 | 16 | 14 | 75 | 15.06 | 2.11
86 | 50 | 558 | 72 | LWB | 61.4 | 16 | 14 | 77 | 14.89 | 2.12
86 | 50 | 558 | 72 | kW | 0.89 | 16 | 14 | 81 | 14.55 | 2.14
90 | 50 | 558 | 75 | MBh | 21.52 | 5 | 5 | 59 | 14.49 | 1.94
90 | 50 | 558 | 75 | S/T | 0.629 | 5 | 5 | 70 | 13.6 | 1.99
90 | 50 | 558 | 75 | ∆T | 22.5 | 5 | 5 | 72 | 13.24 | 2.01
90 | 50 | 558 | 75 | LDB | 67.5 | 5 | 5 | 75 | 12.89 | 2.04
90 | 50 | 558 | 75 | LWB | 64.8 | 5 | 5 | 77 | 12.71 | 2.05
90 | 50 | 558 | 75 | kW | 1.1 | 5 | 5 | 81 | 12.35 | 2.07
68 | 68 | 558 | 57 | MBh | 16.36 | -4 | -4 | 59 | 13.17 | 1.84
68 | 68 | 558 | 57 | S/T | 0.771 | -4 | -4 | 70 | 12.15 | 1.9
68 | 68 | 558 | 57 | ∆T | 20.9 | -4 | -4 | 72 | 11.74 | 1.92
68 | 68 | 558 | 57 | LDB | 47.1 | -4 | -4 | 75 | 11.34 | 1.94
68 | 68 | 558 | 57 | LWB | 45.5 | -4 | -4 | 77 | 11.13 | 1.95
68 | 68 | 558 | 57 | kW | 1.07 | -4 | -4 | 81 | 10.73 | 1.97
72 | 68 | 558 | 61 | MBh | 17.1 | -13 | -13 | 59 | 11.93 | 1.75
72 | 68 | 558 | 61 | S/T | 0.725 | -13 | -13 | 70 | 10.7 | 1.8
72 | 68 | 558 | 61 | ∆T | 20.6 | -13 | -13 | 72 | 10.21 | 1.82
72 | 68 | 558 | 61 | LDB | 51.4 | -13 | -13 | 75 | 9.71 | 1.84
72 | 68 | 558 | 61 | LWB | 49.9 | -13 | -13 | 77 | 9.47 | 1.85
72 | 68 | 558 | 61 | kW | 1.08 | -13 | -13 | 81 | 8.98 | 1.88
77 | 68 | 558 | 64 | MBh | 17.83
77 | 68 | 558 | 64 | S/T | 0.732
77 | 68 | 558 | 64 | ∆T | 21.7
77 | 68 | 558 | 64 | LDB | 55.3
77 | 68 | 558 | 64 | LWB | 53.1
77 | 68 | 558 | 64 | kW | 1.09
80 | 68 | 558 | 67 | MBh | 18.2
80 | 68 | 558 | 67 | S/T | 0.76
80 | 68 | 558 | 67 | ∆T | 23
80 | 68 | 558 | 67 | LDB | 57
80 | 68 | 558 | 67 | LWB | 56.6
80 | 68 | 558 | 67 | kW | 1.09
86 | 68 | 558 | 72 | MBh | 19.3
86 | 68 | 558 | 72 | S/T | 0.693
86 | 68 | 558 | 72 | ∆T | 22.2
86 | 68 | 558 | 72 | LDB | 63.8
86 | 68 | 558 | 72 | LWB | 62.2
86 | 68 | 558 | 72 | kW | 1.1
90 | 68 | 558 | 75 | MBh | 20.04
90 | 68 | 558 | 75 | S/T | 0.651
90 | 68 | 558 | 75 | ∆T | 21.6
90 | 68 | 558 | 75 | LDB | 68.4
90 | 68 | 558 | 75 | LWB | 65.5
90 | 68 | 558 | 75 | kW | 1.1
68 | 86 | 558 | 57 | MBh | 14.87
68 | 86 | 558 | 57 | S/T | 0.8
68 | 86 | 558 | 57 | ∆T | 19.7
68 | 86 | 558 | 57 | LDB | 48.3
68 | 86 | 558 | 57 | LWB | 46.6
68 | 86 | 558 | 57 | kW | 1.28
72 | 86 | 558 | 61 | MBh | 15.61
72 | 86 | 558 | 61 | S/T | 0.751
72 | 86 | 558 | 61 | ∆T | 19.4
72 | 86 | 558 | 61 | LDB | 52.6
72 | 86 | 558 | 61 | LWB | 51
72 | 86 | 558 | 61 | kW | 1.29
77 | 86 | 558 | 64 | MBh | 16.34
77 | 86 | 558 | 64 | S/T | 0.761
77 | 86 | 558 | 64 | ∆T | 20.6
77 | 86 | 558 | 64 | LDB | 56.4
77 | 86 | 558 | 64 | LWB | 54.1
77 | 86 | 558 | 64 | kW | 1.29
80 | 86 | 558 | 67 | MBh | 16.71
80 | 86 | 558 | 67 | S/T | 0.792
80 | 86 | 558 | 67 | ∆T | 22
80 | 86 | 558 | 67 | LDB | 58
80 | 86 | 558 | 67 | LWB | 57.6
80 | 86 | 558 | 67 | kW | 1.3
86 | 86 | 558 | 72 | MBh | 17.82
86 | 86 | 558 | 72 | S/T | 0.72
86 | 86 | 558 | 72 | ∆T | 21.3
86 | 86 | 558 | 72 | LDB | 64.7
86 | 86 | 558 | 72 | LWB | 63
86 | 86 | 558 | 72 | kW | 1.31
90 | 86 | 558 | 75 | MBh | 18.55
90 | 86 | 558 | 75 | S/T | 0.677
90 | 86 | 558 | 75 | ∆T | 20.8
90 | 86 | 558 | 75 | LDB | 69.2
90 | 86 | 558 | 75 | LWB | 66.3
90 | 86 | 558 | 75 | kW | 1.31
68 | 95 | 558 | 57 | MBh | 14.13
68 | 95 | 558 | 57 | S/T | 0.817
68 | 95 | 558 | 57 | ∆T | 19.1
68 | 95 | 558 | 57 | LDB | 48.9
68 | 95 | 558 | 57 | LWB | 47.2
68 | 95 | 558 | 57 | kW | 1.38
72 | 95 | 558 | 61 | MBh | 14.86
72 | 95 | 558 | 61 | S/T | 0.766
72 | 95 | 558 | 61 | ∆T | 18.9
72 | 95 | 558 | 61 | LDB | 53.1
72 | 95 | 558 | 61 | LWB | 51.5
72 | 95 | 558 | 61 | kW | 1.39
77 | 95 | 558 | 64 | MBh | 15.6
77 | 95 | 558 | 64 | S/T | 0.777
77 | 95 | 558 | 64 | ∆T | 20.1
77 | 95 | 558 | 64 | LDB | 56.9
77 | 95 | 558 | 64 | LWB | 54.6
77 | 95 | 558 | 64 | kW | 1.4
80 | 95 | 558 | 67 | MBh | 16
80 | 95 | 558 | 67 | S/T | 0.808
80 | 95 | 558 | 67 | ∆T | 21.5
80 | 95 | 558 | 67 | LDB | 58.5
80 | 95 | 558 | 67 | LWB | 58
80 | 95 | 558 | 67 | kW | 1.4
86 | 95 | 558 | 72 | MBh | 17.07
86 | 95 | 558 | 72 | S/T | 0.736
86 | 95 | 558 | 72 | ∆T | 20.9
86 | 95 | 558 | 72 | LDB | 65.1
86 | 95 | 558 | 72 | LWB | 63.4
86 | 95 | 558 | 72 | kW | 1.41
90 | 95 | 558 | 75 | MBh | 17.81
90 | 95 | 558 | 75 | S/T | 0.691
90 | 95 | 558 | 75 | ∆T | 20.4
90 | 95 | 558 | 75 | LDB | 69.6
90 | 95 | 558 | 75 | LWB | 66.7
90 | 95 | 558 | 75 | kW | 1.42
68 | 104 | 558 | 57 | MBh | 13.39
68 | 104 | 558 | 57 | S/T | 0.836
68 | 104 | 558 | 57 | ∆T | 18.6
68 | 104 | 558 | 57 | LDB | 49.4
68 | 104 | 558 | 57 | LWB | 47.7
68 | 104 | 558 | 57 | kW | 1.49
72 | 104 | 558 | 61 | MBh | 14.12
72 | 104 | 558 | 61 | S/T | 0.783
72 | 104 | 558 | 61 | ∆T | 18.4
72 | 104 | 558 | 61 | LDB | 53.6
72 | 104 | 558 | 61 | LWB | 52
72 | 104 | 558 | 61 | kW | 1.49
77 | 104 | 558 | 64 | MBh | 14.86
77 | 104 | 558 | 64 | S/T | 0.795
77 | 104 | 558 | 64 | ∆T | 19.6
77 | 104 | 558 | 64 | LDB | 57.4
77 | 104 | 558 | 64 | LWB | 55.1
77 | 104 | 558 | 64 | kW | 1.5
80 | 104 | 558 | 67 | MBh | 15.22
80 | 104 | 558 | 67 | S/T | 0.83
80 | 104 | 558 | 67 | ∆T | 21
80 | 104 | 558 | 67 | LDB | 59
80 | 104 | 558 | 67 | LWB | 58.5
80 | 104 | 558 | 67 | kW | 1.5
86 | 104 | 558 | 72 | MBh | 16.33
86 | 104 | 558 | 72 | S/T | 0.754
86 | 104 | 558 | 72 | ∆T | 20.4
86 | 104 | 558 | 72 | LDB | 65.6
86 | 104 | 558 | 72 | LWB | 63.8
86 | 104 | 558 | 72 | kW | 1.51
90 | 104 | 558 | 75 | MBh | 17.06
90 | 104 | 558 | 75 | S/T | 0.708
90 | 104 | 558 | 75 | ∆T | 20
90 | 104 | 558 | 75 | LDB | 70
90 | 104 | 558 | 75 | LWB | 67.1
90 | 104 | 558 | 75 | kW | 1.52
68 | 115 | 558 | 57 | MBh | 12.49
68 | 115 | 558 | 57 | S/T | 0.862
68 | 115 | 558 | 57 | ∆T | 17.9
68 | 115 | 558 | 57 | LDB | 50.1
68 | 115 | 558 | 57 | LWB | 48.4
68 | 115 | 558 | 57 | kW | 1.61
72 | 115 | 558 | 61 | MBh | 13.23
72 | 115 | 558 | 61 | S/T | 0.807
72 | 115 | 558 | 61 | ∆T | 17.7
72 | 115 | 558 | 61 | LDB | 54.3
72 | 115 | 558 | 61 | LWB | 52.6
72 | 115 | 558 | 61 | kW | 1.62
77 | 115 | 558 | 64 | MBh | 13.96
77 | 115 | 558 | 64 | S/T | 0.82
77 | 115 | 558 | 64 | ∆T | 19
77 | 115 | 558 | 64 | LDB | 58
77 | 115 | 558 | 64 | LWB | 55.7
77 | 115 | 558 | 64 | kW | 1.62
80 | 115 | 558 | 67 | MBh | 14.33
80 | 115 | 558 | 67 | S/T | 0.858
80 | 115 | 558 | 67 | ∆T | 20.4
80 | 115 | 558 | 67 | LDB | 59.6
80 | 115 | 558 | 67 | LWB | 59
80 | 115 | 558 | 67 | kW | 1.63
86 | 115 | 558 | 72 | MBh | 15.44
86 | 115 | 558 | 72 | S/T | 0.777
86 | 115 | 558 | 72 | ∆T | 19.9
86 | 115 | 558 | 72 | LDB | 66.1
86 | 115 | 558 | 72 | LWB | 64.3
86 | 115 | 558 | 72 | kW | 1.64
90 | 115 | 558 | 75 | MBh | 16.17
90 | 115 | 558 | 75 | S/T | 0.729
90 | 115 | 558 | 75 | ∆T | 19.6
90 | 115 | 558 | 75 | LDB | 70.4
90 | 115 | 558 | 75 | LWB | 67.5
90 | 115 | 558 | 75 | kW | 1.64

## RXM18WVJU9 - FTXM18WVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 777 | 57 | MBh | 24.56 | 75 | 60 | 59 | 37.72 | 3.48
68 | 50 | 777 | 57 | S/T | 0.719 | 75 | 60 | 70 | 36.68 | 3.56
68 | 50 | 777 | 57 | ∆T | 21.1 | 75 | 60 | 72 | 36.26 | 3.59
68 | 50 | 777 | 57 | LDB | 46.9 | 75 | 60 | 75 | 35.85 | 3.62
68 | 50 | 777 | 57 | LWB | 44.5 | 75 | 60 | 77 | 35.64 | 3.63
68 | 50 | 777 | 57 | kW | 1.25 | 75 | 60 | 81 | 35.22 | 3.66
72 | 50 | 777 | 61 | MBh | 25.57 | 47 | 43 | 59 | 31.24 | 3.23
72 | 50 | 777 | 61 | S/T | 0.677 | 47 | 43 | 70 | 30.2 | 3.3
72 | 50 | 777 | 61 | ∆T | 20.6 | 47 | 43 | 72 | 29.78 | 3.33
72 | 50 | 777 | 61 | LDB | 51.4 | 47 | 43 | 75 | 29.37 | 3.36
72 | 50 | 777 | 61 | LWB | 49 | 47 | 43 | 77 | 29.16 | 3.37
72 | 50 | 777 | 61 | kW | 1.26 | 47 | 43 | 81 | 28.74 | 3.4
77 | 50 | 777 | 64 | MBh | 26.58 | 35 | 32 | 59 | 28.85 | 3.28
77 | 50 | 777 | 64 | S/T | 0.678 | 35 | 32 | 70 | 27.74 | 3.36
77 | 50 | 777 | 64 | ∆T | 21.5 | 35 | 32 | 72 | 27.3 | 3.39
77 | 50 | 777 | 64 | LDB | 55.5 | 35 | 32 | 75 | 26.86 | 3.43
77 | 50 | 777 | 64 | LWB | 52.3 | 35 | 32 | 77 | 26.64 | 3.44
77 | 50 | 777 | 64 | kW | 1.27 | 35 | 32 | 81 | 26.19 | 3.47
80 | 50 | 777 | 67 | MBh | 27.09 | 25 | 23 | 59 | 26.88 | 3.33
80 | 50 | 777 | 67 | S/T | 0.697 | 25 | 23 | 70 | 25.7 | 3.41
80 | 50 | 777 | 67 | ∆T | 22.5 | 25 | 23 | 72 | 25.22 | 3.45
80 | 50 | 777 | 67 | LDB | 57.5 | 25 | 23 | 75 | 24.75 | 3.48
80 | 50 | 777 | 67 | LWB | 55.9 | 25 | 23 | 77 | 24.52 | 3.5
80 | 50 | 777 | 67 | kW | 1.27 | 25 | 23 | 81 | 24.04 | 3.53
86 | 50 | 777 | 72 | MBh | 28.61 | 16 | 14 | 59 | 24.93 | 3.38
86 | 50 | 777 | 72 | S/T | 0.634 | 16 | 14 | 70 | 23.65 | 3.47
86 | 50 | 777 | 72 | ∆T | 21.6 | 16 | 14 | 72 | 23.14 | 3.5
86 | 50 | 777 | 72 | LDB | 64.4 | 16 | 14 | 75 | 22.63 | 3.54
86 | 50 | 777 | 72 | LWB | 61.5 | 16 | 14 | 77 | 22.37 | 3.56
86 | 50 | 777 | 72 | kW | 1.29 | 16 | 14 | 81 | 21.86 | 3.59
90 | 50 | 777 | 75 | MBh | 29.62 | 5 | 5 | 59 | 23.02 | 3.42
90 | 50 | 777 | 75 | S/T | 0.595 | 5 | 5 | 70 | 21.6 | 3.52
90 | 50 | 777 | 75 | ∆T | 21 | 5 | 5 | 72 | 21.03 | 3.56
90 | 50 | 777 | 75 | LDB | 69 | 5 | 5 | 75 | 20.47 | 3.59
90 | 50 | 777 | 75 | LWB | 64.9 | 5 | 5 | 77 | 20.18 | 3.61
90 | 50 | 777 | 75 | kW | 1.3 | 5 | 5 | 81 | 19.61 | 3.65
68 | 68 | 777 | 57 | MBh | 22.51 | -4 | -4 | 59 | 20.48 | 3.21
68 | 68 | 777 | 57 | S/T | 0.738 | -4 | -4 | 70 | 18.9 | 3.31
68 | 68 | 777 | 57 | ∆T | 19.8 | -4 | -4 | 72 | 18.27 | 3.35
68 | 68 | 777 | 57 | LDB | 48.2 | -4 | -4 | 75 | 17.64 | 3.38
68 | 68 | 777 | 57 | LWB | 45.6 | -4 | -4 | 77 | 17.32 | 3.4
68 | 68 | 777 | 57 | kW | 1.55 | -4 | -4 | 81 | 14.87 | 2.74
72 | 68 | 777 | 61 | MBh | 23.52 | -13 | -13 | 59 | 18.06 | 3.01
72 | 68 | 777 | 61 | S/T | 0.694 | -13 | -13 | 70 | 16.2 | 3.1
72 | 68 | 777 | 61 | ∆T | 19.5 | -13 | -13 | 72 | 15.42 | 3.12
72 | 68 | 777 | 61 | LDB | 52.5 | -13 | -13 | 75 | 12.79 | 2.44
72 | 68 | 777 | 61 | LWB | 50.1 | -13 | -13 | 77 | 11.48 | 2.12
72 | 68 | 777 | 61 | kW | 1.56 | -13 | -13 | 81 | 8.86 | 1.55
77 | 68 | 777 | 64 | MBh | 24.54
77 | 68 | 777 | 64 | S/T | 0.696
77 | 68 | 777 | 64 | ∆T | 20.4
77 | 68 | 777 | 64 | LDB | 56.6
77 | 68 | 777 | 64 | LWB | 53.3
77 | 68 | 777 | 64 | kW | 1.57
80 | 68 | 777 | 67 | MBh | 25.04
80 | 68 | 777 | 67 | S/T | 0.719
80 | 68 | 777 | 67 | ∆T | 21.5
80 | 68 | 777 | 67 | LDB | 58.5
80 | 68 | 777 | 67 | LWB | 56.8
80 | 68 | 777 | 67 | kW | 1.57
86 | 68 | 777 | 72 | MBh | 26.56
86 | 68 | 777 | 72 | S/T | 0.654
86 | 68 | 777 | 72 | ∆T | 20.7
86 | 68 | 777 | 72 | LDB | 65.3
86 | 68 | 777 | 72 | LWB | 62.3
86 | 68 | 777 | 72 | kW | 1.59
90 | 68 | 777 | 75 | MBh | 27.57
90 | 68 | 777 | 75 | S/T | 0.613
90 | 68 | 777 | 75 | ∆T | 20.1
90 | 68 | 777 | 75 | LDB | 69.9
90 | 68 | 777 | 75 | LWB | 65.7
90 | 68 | 777 | 75 | kW | 1.6
68 | 86 | 777 | 57 | MBh | 20.47
68 | 86 | 777 | 57 | S/T | 0.762
68 | 86 | 777 | 57 | ∆T | 18.6
68 | 86 | 777 | 57 | LDB | 49.4
68 | 86 | 777 | 57 | LWB | 46.8
68 | 86 | 777 | 57 | kW | 1.85
72 | 86 | 777 | 61 | MBh | 21.48
72 | 86 | 777 | 61 | S/T | 0.715
72 | 86 | 777 | 61 | ∆T | 18.3
72 | 86 | 777 | 61 | LDB | 53.7
72 | 86 | 777 | 61 | LWB | 51.1
72 | 86 | 777 | 61 | kW | 1.86
77 | 86 | 777 | 64 | MBh | 22.49
77 | 86 | 777 | 64 | S/T | 0.72
77 | 86 | 777 | 64 | ∆T | 19.3
77 | 86 | 777 | 64 | LDB | 57.7
77 | 86 | 777 | 64 | LWB | 54.3
77 | 86 | 777 | 64 | kW | 1.87
80 | 86 | 777 | 67 | MBh | 23
80 | 86 | 777 | 67 | S/T | 0.745
80 | 86 | 777 | 67 | ∆T | 20.4
80 | 86 | 777 | 67 | LDB | 59.6
80 | 86 | 777 | 67 | LWB | 57.7
80 | 86 | 777 | 67 | kW | 1.87
86 | 86 | 777 | 72 | MBh | 24.51
86 | 86 | 777 | 72 | S/T | 0.677
86 | 86 | 777 | 72 | ∆T | 19.8
86 | 86 | 777 | 72 | LDB | 66.2
86 | 86 | 777 | 72 | LWB | 63.2
86 | 86 | 777 | 72 | kW | 1.89
90 | 86 | 777 | 75 | MBh | 25.53
90 | 86 | 777 | 75 | S/T | 0.635
90 | 86 | 777 | 75 | ∆T | 19.3
90 | 86 | 777 | 75 | LDB | 70.7
90 | 86 | 777 | 75 | LWB | 66.4
90 | 86 | 777 | 75 | kW | 1.89
68 | 95 | 777 | 57 | MBh | 19.44
68 | 95 | 777 | 57 | S/T | 0.776
68 | 95 | 777 | 57 | ∆T | 18
68 | 95 | 777 | 57 | LDB | 50
68 | 95 | 777 | 57 | LWB | 47.3
68 | 95 | 777 | 57 | kW | 2
72 | 95 | 777 | 61 | MBh | 20.45
72 | 95 | 777 | 61 | S/T | 0.728
72 | 95 | 777 | 61 | ∆T | 17.7
72 | 95 | 777 | 61 | LDB | 54.3
72 | 95 | 777 | 61 | LWB | 51.6
72 | 95 | 777 | 61 | kW | 2.01
77 | 95 | 777 | 64 | MBh | 21.47
77 | 95 | 777 | 64 | S/T | 0.734
77 | 95 | 777 | 64 | ∆T | 18.8
77 | 95 | 777 | 64 | LDB | 58.2
77 | 95 | 777 | 64 | LWB | 54.8
77 | 95 | 777 | 64 | kW | 2.02
80 | 95 | 777 | 67 | MBh | 22
80 | 95 | 777 | 67 | S/T | 0.76
80 | 95 | 777 | 67 | ∆T | 19.9
80 | 95 | 777 | 67 | LDB | 60.1
80 | 95 | 777 | 67 | LWB | 58.1
80 | 95 | 777 | 67 | kW | 2.02
86 | 95 | 777 | 72 | MBh | 23.49
86 | 95 | 777 | 72 | S/T | 0.691
86 | 95 | 777 | 72 | ∆T | 19.3
86 | 95 | 777 | 72 | LDB | 66.7
86 | 95 | 777 | 72 | LWB | 63.6
86 | 95 | 777 | 72 | kW | 2.03
90 | 95 | 777 | 75 | MBh | 24.5
90 | 95 | 777 | 75 | S/T | 0.647
90 | 95 | 777 | 75 | ∆T | 18.9
90 | 95 | 777 | 75 | LDB | 71.1
90 | 95 | 777 | 75 | LWB | 66.8
90 | 95 | 777 | 75 | kW | 2.04
68 | 104 | 777 | 57 | MBh | 18.42
68 | 104 | 777 | 57 | S/T | 0.792
68 | 104 | 777 | 57 | ∆T | 17.4
68 | 104 | 777 | 57 | LDB | 50.6
68 | 104 | 777 | 57 | LWB | 47.9
68 | 104 | 777 | 57 | kW | 2.15
72 | 104 | 777 | 61 | MBh | 19.43
72 | 104 | 777 | 61 | S/T | 0.743
72 | 104 | 777 | 61 | ∆T | 17.2
72 | 104 | 777 | 61 | LDB | 54.8
72 | 104 | 777 | 61 | LWB | 52.1
72 | 104 | 777 | 61 | kW | 2.16
77 | 104 | 777 | 64 | MBh | 20.44
77 | 104 | 777 | 64 | S/T | 0.75
77 | 104 | 777 | 64 | ∆T | 18.3
77 | 104 | 777 | 64 | LDB | 58.7
77 | 104 | 777 | 64 | LWB | 55.2
77 | 104 | 777 | 64 | kW | 2.17
80 | 104 | 777 | 67 | MBh | 20.95
80 | 104 | 777 | 67 | S/T | 0.778
80 | 104 | 777 | 67 | ∆T | 19.4
80 | 104 | 777 | 67 | LDB | 60.6
80 | 104 | 777 | 67 | LWB | 58.6
80 | 104 | 777 | 67 | kW | 2.17
86 | 104 | 777 | 72 | MBh | 22.47
86 | 104 | 777 | 72 | S/T | 0.705
86 | 104 | 777 | 72 | ∆T | 18.9
86 | 104 | 777 | 72 | LDB | 67.1
86 | 104 | 777 | 72 | LWB | 64
86 | 104 | 777 | 72 | kW | 2.18
90 | 104 | 777 | 75 | MBh | 23.48
90 | 104 | 777 | 75 | S/T | 0.661
90 | 104 | 777 | 75 | ∆T | 18.5
90 | 104 | 777 | 75 | LDB | 71.5
90 | 104 | 777 | 75 | LWB | 67.2
90 | 104 | 777 | 75 | kW | 2.19
68 | 115 | 777 | 57 | MBh | 17.19
68 | 115 | 777 | 57 | S/T | 0.815
68 | 115 | 777 | 57 | ∆T | 16.7
68 | 115 | 777 | 57 | LDB | 51.3
68 | 115 | 777 | 57 | LWB | 48.5
68 | 115 | 777 | 57 | kW | 2.33
72 | 115 | 777 | 61 | MBh | 18.2
72 | 115 | 777 | 61 | S/T | 0.763
72 | 115 | 777 | 61 | ∆T | 16.5
72 | 115 | 777 | 61 | LDB | 55.5
72 | 115 | 777 | 61 | LWB | 52.7
72 | 115 | 777 | 61 | kW | 2.34
77 | 115 | 777 | 64 | MBh | 19.22
77 | 115 | 777 | 64 | S/T | 0.771
77 | 115 | 777 | 64 | ∆T | 17.6
77 | 115 | 777 | 64 | LDB | 59.4
77 | 115 | 777 | 64 | LWB | 55.8
77 | 115 | 777 | 64 | kW | 2.35
80 | 115 | 777 | 67 | MBh | 19.72
80 | 115 | 777 | 67 | S/T | 0.802
80 | 115 | 777 | 67 | ∆T | 18.8
80 | 115 | 777 | 67 | LDB | 61.2
80 | 115 | 777 | 67 | LWB | 59.1
80 | 115 | 777 | 67 | kW | 2.35
86 | 115 | 777 | 72 | MBh | 21.24
86 | 115 | 777 | 72 | S/T | 0.726
86 | 115 | 777 | 72 | ∆T | 18.4
86 | 115 | 777 | 72 | LDB | 67.6
86 | 115 | 777 | 72 | LWB | 64.4
86 | 115 | 777 | 72 | kW | 2.36
90 | 115 | 777 | 75 | MBh | 22.25
90 | 115 | 777 | 75 | S/T | 0.68
90 | 115 | 777 | 75 | ∆T | 18
90 | 115 | 777 | 75 | LDB | 72
90 | 115 | 777 | 75 | LWB | 67.6
90 | 115 | 777 | 75 | kW | 2.37

## RXM24WVJU9 - FTXM24WVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 844 | 57 | MBh | 25.41 | 75 | 60 | 59 | 40.22 | 3.76
68 | 50 | 844 | 57 | S/T | 0.704 | 75 | 60 | 70 | 39.11 | 3.84
68 | 50 | 844 | 57 | ∆T | 19.6 | 75 | 60 | 72 | 38.66 | 3.87
68 | 50 | 844 | 57 | LDB | 48.4 | 75 | 60 | 75 | 38.22 | 3.9
68 | 50 | 844 | 57 | LWB | 45.1 | 75 | 60 | 77 | 38 | 3.92
68 | 50 | 844 | 57 | kW | 1.36 | 75 | 60 | 81 | 37.55 | 3.95
72 | 50 | 844 | 61 | MBh | 30.22 | 47 | 43 | 59 | 33.31 | 3.48
72 | 50 | 844 | 61 | S/T | 0.644 | 47 | 43 | 70 | 32.2 | 3.56
72 | 50 | 844 | 61 | ∆T | 21.4 | 47 | 43 | 72 | 31.76 | 3.59
72 | 50 | 844 | 61 | LDB | 50.6 | 47 | 43 | 75 | 31.31 | 3.62
72 | 50 | 844 | 61 | LWB | 47.8 | 47 | 43 | 77 | 31.09 | 3.64
72 | 50 | 844 | 61 | kW | 1.75 | 47 | 43 | 81 | 30.64 | 3.67
77 | 50 | 844 | 64 | MBh | 31.41 | 35 | 32 | 59 | 31.05 | 3.57
77 | 50 | 844 | 64 | S/T | 0.638 | 35 | 32 | 70 | 29.86 | 3.66
77 | 50 | 844 | 64 | ∆T | 22 | 35 | 32 | 72 | 29.38 | 3.69
77 | 50 | 844 | 64 | LDB | 55 | 35 | 32 | 75 | 28.9 | 3.73
77 | 50 | 844 | 64 | LWB | 51.1 | 35 | 32 | 77 | 28.66 | 3.75
77 | 50 | 844 | 64 | kW | 1.76 | 35 | 32 | 81 | 28.19 | 3.78
80 | 50 | 844 | 67 | MBh | 32.01 | 25 | 23 | 59 | 29.19 | 3.65
80 | 50 | 844 | 67 | S/T | 0.651 | 25 | 23 | 70 | 27.9 | 3.74
80 | 50 | 844 | 67 | ∆T | 22.9 | 25 | 23 | 72 | 27.39 | 3.78
80 | 50 | 844 | 67 | LDB | 57.1 | 25 | 23 | 75 | 26.88 | 3.82
80 | 50 | 844 | 67 | LWB | 54.8 | 25 | 23 | 77 | 26.62 | 3.83
80 | 50 | 844 | 67 | kW | 1.77 | 25 | 23 | 81 | 26.11 | 3.87
86 | 50 | 844 | 72 | MBh | 33.8 | 16 | 14 | 59 | 27.36 | 3.73
86 | 50 | 844 | 72 | S/T | 0.59 | 16 | 14 | 70 | 25.95 | 3.82
86 | 50 | 844 | 72 | ∆T | 21.9 | 16 | 14 | 72 | 25.39 | 3.86
86 | 50 | 844 | 72 | LDB | 64.1 | 16 | 14 | 75 | 24.83 | 3.9
86 | 50 | 844 | 72 | LWB | 60.5 | 16 | 14 | 77 | 24.55 | 3.92
86 | 50 | 844 | 72 | kW | 1.78 | 16 | 14 | 81 | 23.99 | 3.96
90 | 50 | 844 | 75 | MBh | 35 | 5 | 5 | 59 | 25.58 | 3.8
90 | 50 | 844 | 75 | S/T | 0.551 | 5 | 5 | 70 | 24 | 3.91
90 | 50 | 844 | 75 | ∆T | 21.2 | 5 | 5 | 72 | 23.37 | 3.95
90 | 50 | 844 | 75 | LDB | 68.8 | 5 | 5 | 75 | 22.8 | 3.96
90 | 50 | 844 | 75 | LWB | 63.9 | 5 | 5 | 77 | 22.54 | 3.96
90 | 50 | 844 | 75 | kW | 1.8 | 5 | 5 | 81 | 22.03 | 3.96
68 | 68 | 844 | 57 | MBh | 25.41 | -4 | -4 | 59 | 22.76 | 3.6
68 | 68 | 844 | 57 | S/T | 0.704 | -4 | -4 | 70 | 21 | 3.7
68 | 68 | 844 | 57 | ∆T | 19.6 | -4 | -4 | 72 | 20.3 | 3.75
68 | 68 | 844 | 57 | LDB | 48.4 | -4 | -4 | 75 | 19.6 | 3.79
68 | 68 | 844 | 57 | LWB | 45.1 | -4 | -4 | 77 | 19.24 | 3.81
68 | 68 | 844 | 57 | kW | 1.95 | -4 | -4 | 81 | 16.71 | 3.14
72 | 68 | 844 | 61 | MBh | 27.8 | -13 | -13 | 59 | 20.07 | 3.39
72 | 68 | 844 | 61 | S/T | 0.655 | -13 | -13 | 70 | 18 | 3.5
72 | 68 | 844 | 61 | ∆T | 20 | -13 | -13 | 72 | 17.17 | 3.54
72 | 68 | 844 | 61 | LDB | 52 | -13 | -13 | 75 | 14.38 | 2.81
72 | 68 | 844 | 61 | LWB | 49 | -13 | -13 | 77 | 12.9 | 2.45
72 | 68 | 844 | 61 | kW | 2.16 | -13 | -13 | 81 | 9.95 | 1.78
77 | 68 | 844 | 64 | MBh | 28.99
77 | 68 | 844 | 64 | S/T | 0.651
77 | 68 | 844 | 64 | ∆T | 20.7
77 | 68 | 844 | 64 | LDB | 56.3
77 | 68 | 844 | 64 | LWB | 52.2
77 | 68 | 844 | 64 | kW | 2.17
80 | 68 | 844 | 67 | MBh | 29.59
80 | 68 | 844 | 67 | S/T | 0.666
80 | 68 | 844 | 67 | ∆T | 21.6
80 | 68 | 844 | 67 | LDB | 58.4
80 | 68 | 844 | 67 | LWB | 55.8
80 | 68 | 844 | 67 | kW | 2.18
86 | 68 | 844 | 72 | MBh | 31.39
86 | 68 | 844 | 72 | S/T | 0.603
86 | 68 | 844 | 72 | ∆T | 20.8
86 | 68 | 844 | 72 | LDB | 65.2
86 | 68 | 844 | 72 | LWB | 61.4
86 | 68 | 844 | 72 | kW | 2.2
90 | 68 | 844 | 75 | MBh | 32.58
90 | 68 | 844 | 75 | S/T | 0.564
90 | 68 | 844 | 75 | ∆T | 20.1
90 | 68 | 844 | 75 | LDB | 69.9
90 | 68 | 844 | 75 | LWB | 64.8
90 | 68 | 844 | 75 | kW | 2.21
68 | 86 | 844 | 57 | MBh | 24.18
68 | 86 | 844 | 57 | S/T | 0.713
68 | 86 | 844 | 57 | ∆T | 18.9
68 | 86 | 844 | 57 | LDB | 49.1
68 | 86 | 844 | 57 | LWB | 45.8
68 | 86 | 844 | 57 | kW | 2.56
72 | 86 | 844 | 61 | MBh | 25.38
72 | 86 | 844 | 61 | S/T | 0.669
72 | 86 | 844 | 61 | ∆T | 18.6
72 | 86 | 844 | 61 | LDB | 53.4
72 | 86 | 844 | 61 | LWB | 50.2
72 | 86 | 844 | 61 | kW | 2.58
77 | 86 | 844 | 64 | MBh | 26.58
77 | 86 | 844 | 64 | S/T | 0.667
77 | 86 | 844 | 64 | ∆T | 19.5
77 | 86 | 844 | 64 | LDB | 57.5
77 | 86 | 844 | 64 | LWB | 53.3
77 | 86 | 844 | 64 | kW | 2.59
80 | 86 | 844 | 67 | MBh | 27.17
80 | 86 | 844 | 67 | S/T | 0.685
80 | 86 | 844 | 67 | ∆T | 20.4
80 | 86 | 844 | 67 | LDB | 59.6
80 | 86 | 844 | 67 | LWB | 56.8
80 | 86 | 844 | 67 | kW | 2.59
86 | 86 | 844 | 72 | MBh | 28.97
86 | 86 | 844 | 72 | S/T | 0.62
86 | 86 | 844 | 72 | ∆T | 19.7
86 | 86 | 844 | 72 | LDB | 66.3
86 | 86 | 844 | 72 | LWB | 62.3
86 | 86 | 844 | 72 | kW | 2.61
90 | 86 | 844 | 75 | MBh | 30.17
90 | 86 | 844 | 75 | S/T | 0.579
90 | 86 | 844 | 75 | ∆T | 19.2
90 | 86 | 844 | 75 | LDB | 70.8
90 | 86 | 844 | 75 | LWB | 65.6
90 | 86 | 844 | 75 | kW | 2.62
68 | 95 | 844 | 57 | MBh | 22.97
68 | 95 | 844 | 57 | S/T | 0.723
68 | 95 | 844 | 57 | ∆T | 18.2
68 | 95 | 844 | 57 | LDB | 49.8
68 | 95 | 844 | 57 | LWB | 46.4
68 | 95 | 844 | 57 | kW | 2.77
72 | 95 | 844 | 61 | MBh | 24.17
72 | 95 | 844 | 61 | S/T | 0.679
72 | 95 | 844 | 61 | ∆T | 18
72 | 95 | 844 | 61 | LDB | 54
72 | 95 | 844 | 61 | LWB | 50.7
72 | 95 | 844 | 61 | kW | 2.78
77 | 95 | 844 | 64 | MBh | 25.37
77 | 95 | 844 | 64 | S/T | 0.677
77 | 95 | 844 | 64 | ∆T | 18.8
77 | 95 | 844 | 64 | LDB | 58.2
77 | 95 | 844 | 64 | LWB | 53.9
77 | 95 | 844 | 64 | kW | 2.79
80 | 95 | 844 | 67 | MBh | 26
80 | 95 | 844 | 67 | S/T | 0.695
80 | 95 | 844 | 67 | ∆T | 19.8
80 | 95 | 844 | 67 | LDB | 60.2
80 | 95 | 844 | 67 | LWB | 57.3
80 | 95 | 844 | 67 | kW | 2.8
86 | 95 | 844 | 72 | MBh | 27.76
86 | 95 | 844 | 72 | S/T | 0.63
86 | 95 | 844 | 72 | ∆T | 19.2
86 | 95 | 844 | 72 | LDB | 66.8
86 | 95 | 844 | 72 | LWB | 62.8
86 | 95 | 844 | 72 | kW | 2.82
90 | 95 | 844 | 75 | MBh | 28.96
90 | 95 | 844 | 75 | S/T | 0.588
90 | 95 | 844 | 75 | ∆T | 18.7
90 | 95 | 844 | 75 | LDB | 71.3
90 | 95 | 844 | 75 | LWB | 66
90 | 95 | 844 | 75 | kW | 2.83
68 | 104 | 844 | 57 | MBh | 21.77
68 | 104 | 844 | 57 | S/T | 0.734
68 | 104 | 844 | 57 | ∆T | 17.5
68 | 104 | 844 | 57 | LDB | 50.5
68 | 104 | 844 | 57 | LWB | 47
68 | 104 | 844 | 57 | kW | 2.98
72 | 104 | 844 | 61 | MBh | 22.96
72 | 104 | 844 | 61 | S/T | 0.689
72 | 104 | 844 | 61 | ∆T | 17.3
72 | 104 | 844 | 61 | LDB | 54.7
72 | 104 | 844 | 61 | LWB | 51.3
72 | 104 | 844 | 61 | kW | 2.99
77 | 104 | 844 | 64 | MBh | 24.16
77 | 104 | 844 | 64 | S/T | 0.688
77 | 104 | 844 | 64 | ∆T | 18.2
77 | 104 | 844 | 64 | LDB | 58.8
77 | 104 | 844 | 64 | LWB | 54.4
77 | 104 | 844 | 64 | kW | 3
80 | 104 | 844 | 67 | MBh | 24.76
80 | 104 | 844 | 67 | S/T | 0.708
80 | 104 | 844 | 67 | ∆T | 19.2
80 | 104 | 844 | 67 | LDB | 60.8
80 | 104 | 844 | 67 | LWB | 57.8
80 | 104 | 844 | 67 | kW | 3.01
86 | 104 | 844 | 72 | MBh | 26.55
86 | 104 | 844 | 72 | S/T | 0.641
86 | 104 | 844 | 72 | ∆T | 18.7
86 | 104 | 844 | 72 | LDB | 67.3
86 | 104 | 844 | 72 | LWB | 63.2
86 | 104 | 844 | 72 | kW | 3.03
90 | 104 | 844 | 75 | MBh | 27.75
90 | 104 | 844 | 75 | S/T | 0.599
90 | 104 | 844 | 75 | ∆T | 18.2
90 | 104 | 844 | 75 | LDB | 71.8
90 | 104 | 844 | 75 | LWB | 66.4
90 | 104 | 844 | 75 | kW | 3.04
68 | 115 | 844 | 57 | MBh | 19.01
68 | 115 | 844 | 57 | S/T | 0.769
68 | 115 | 844 | 57 | ∆T | 16
68 | 115 | 844 | 57 | LDB | 52
68 | 115 | 844 | 57 | LWB | 48.4
68 | 115 | 844 | 57 | kW | 2.95
72 | 115 | 844 | 61 | MBh | 20.15
72 | 115 | 844 | 61 | S/T | 0.719
72 | 115 | 844 | 61 | ∆T | 15.9
72 | 115 | 844 | 61 | LDB | 56.1
72 | 115 | 844 | 61 | LWB | 52.6
72 | 115 | 844 | 61 | kW | 2.95
77 | 115 | 844 | 64 | MBh | 21.28
77 | 115 | 844 | 64 | S/T | 0.722
77 | 115 | 844 | 64 | ∆T | 16.9
77 | 115 | 844 | 64 | LDB | 60.1
77 | 115 | 844 | 64 | LWB | 55.6
77 | 115 | 844 | 64 | kW | 2.95
80 | 115 | 844 | 67 | MBh | 21.85
80 | 115 | 844 | 67 | S/T | 0.746
80 | 115 | 844 | 67 | ∆T | 17.9
80 | 115 | 844 | 67 | LDB | 62.1
80 | 115 | 844 | 67 | LWB | 59
80 | 115 | 844 | 67 | kW | 2.95
86 | 115 | 844 | 72 | MBh | 23.56
86 | 115 | 844 | 72 | S/T | 0.674
86 | 115 | 844 | 72 | ∆T | 17.4
86 | 115 | 844 | 72 | LDB | 68.6
86 | 115 | 844 | 72 | LWB | 64.3
86 | 115 | 844 | 72 | kW | 2.95
90 | 115 | 844 | 75 | MBh | 24.7
90 | 115 | 844 | 75 | S/T | 0.63
90 | 115 | 844 | 75 | ∆T | 17.1
90 | 115 | 844 | 75 | LDB | 72.9
90 | 115 | 844 | 75 | LWB | 67.4
90 | 115 | 844 | 75 | kW | 2.95

## RXT09AVJU9 - FTXV09AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 381 | 57 | MBh | 12.42 | 75 | 60 | 59 | 18.94 | 1.58
68 | 50 | 381 | 57 | S/T | 0.733 | 75 | 60 | 70 | 18.31 | 1.62
68 | 50 | 381 | 57 | ∆T | 22.1 | 75 | 60 | 72 | 18.21 | 1.62
68 | 50 | 381 | 57 | LDB | 45.9 | 75 | 60 | 75 | 18.01 | 1.64
68 | 50 | 381 | 57 | LWB | 44 | 75 | 60 | 77 | 17.9 | 1.64
68 | 50 | 381 | 57 | kW | 0.6 | 75 | 60 | 81 | 17.69 | 1.66
72 | 50 | 381 | 61 | MBh | 12.93 | 47 | 43 | 59 | 16.67 | 1.46
72 | 50 | 381 | 61 | S/T | 0.689 | 47 | 43 | 70 | 16 | 1.5
72 | 50 | 381 | 61 | ∆T | 21.7 | 47 | 43 | 72 | 15.9 | 1.51
72 | 50 | 381 | 61 | LDB | 50.3 | 47 | 43 | 75 | 15.68 | 1.52
72 | 50 | 381 | 61 | LWB | 48.6 | 47 | 43 | 77 | 15.57 | 1.53
72 | 50 | 381 | 61 | kW | 0.61 | 47 | 43 | 81 | 15.35 | 1.54
77 | 50 | 381 | 64 | MBh | 13.45 | 35 | 32 | 59 | 15.25 | 1.53
77 | 50 | 381 | 64 | S/T | 0.691 | 35 | 32 | 70 | 14.54 | 1.58
77 | 50 | 381 | 64 | ∆T | 22.6 | 35 | 32 | 72 | 14.44 | 1.59
77 | 50 | 381 | 64 | LDB | 54.4 | 35 | 32 | 75 | 14.21 | 1.6
77 | 50 | 381 | 64 | LWB | 51.9 | 35 | 32 | 77 | 14.09 | 1.61
77 | 50 | 381 | 64 | kW | 0.61 | 35 | 32 | 81 | 13.86 | 1.62
80 | 50 | 381 | 67 | MBh | 13.81 | 25 | 23 | 59 | 14.08 | 1.59
80 | 50 | 381 | 67 | S/T | 0.675 | 25 | 23 | 70 | 13.33 | 1.64
80 | 50 | 381 | 67 | ∆T | 22.6 | 25 | 23 | 72 | 13.22 | 1.65
80 | 50 | 381 | 67 | LDB | 57.4 | 25 | 23 | 75 | 12.97 | 1.67
80 | 50 | 381 | 67 | LWB | 55.4 | 25 | 23 | 77 | 12.85 | 1.68
80 | 50 | 381 | 67 | kW | 0.61 | 25 | 23 | 81 | 12.61 | 1.69
86 | 50 | 381 | 72 | MBh | 14.48 | 16 | 14 | 59 | 12.91 | 1.66
86 | 50 | 381 | 72 | S/T | 0.65 | 16 | 14 | 70 | 12.11 | 1.71
86 | 50 | 381 | 72 | ∆T | 22.9 | 16 | 14 | 72 | 12 | 1.72
86 | 50 | 381 | 72 | LDB | 63.1 | 16 | 14 | 75 | 11.73 | 1.73
86 | 50 | 381 | 72 | LWB | 61.1 | 16 | 14 | 77 | 11.6 | 1.74
86 | 50 | 381 | 72 | kW | 0.76 | 16 | 14 | 81 | 11.34 | 1.76
90 | 50 | 381 | 75 | MBh | 15 | 5 | 5 | 59 | 11.77 | 1.72
90 | 50 | 381 | 75 | S/T | 0.61 | 5 | 5 | 70 | 10.9 | 1.77
90 | 50 | 381 | 75 | ∆T | 22.2 | 5 | 5 | 72 | 10.77 | 1.78
90 | 50 | 381 | 75 | LDB | 67.8 | 5 | 5 | 75 | 10.48 | 1.8
90 | 50 | 381 | 75 | LWB | 64.5 | 5 | 5 | 77 | 10.34 | 1.81
90 | 50 | 381 | 75 | kW | 0.77 | 5 | 5 | 81 | 10.06 | 1.83
68 | 68 | 381 | 57 | MBh | 11.37 | -4 | -4 | 59 | 9.71 | 1.68
68 | 68 | 381 | 57 | S/T | 0.754 | -4 | -4 | 70 | 8.81 | 1.74
68 | 68 | 381 | 57 | ∆T | 20.8 | -4 | -4 | 72 | 8.68 | 1.74
68 | 68 | 381 | 57 | LDB | 47.2 | -4 | -4 | 75 | 6.38 | 1.76
68 | 68 | 381 | 57 | LWB | 45.2 | -4 | -4 | 77 | 8.24 | 1.77
68 | 68 | 381 | 57 | kW | 0.75 | -4 | -4 | 81 | 7.56 | 1.62
72 | 68 | 381 | 61 | MBh | 11.89 | -13 | -13 | 59 | 7.57 | 1.64
72 | 68 | 381 | 61 | S/T | 0.708 | -13 | -13 | 70 | 6.63 | 1.7
72 | 68 | 381 | 61 | ∆T | 20.5 | -13 | -13 | 72 | 6.5 | 1.71
72 | 68 | 381 | 61 | LDB | 51.5 | -13 | -13 | 75 | 6.19 | 1.73
72 | 68 | 381 | 61 | LWB | 49.7 | -13 | -13 | 77 | 5.5 | 1.45
72 | 68 | 381 | 61 | kW | 0.75 | -13 | -13 | 81 | 4.12 | 0.97
77 | 68 | 381 | 64 | MBh | 12.41
77 | 68 | 381 | 64 | S/T | 0.712
77 | 68 | 381 | 64 | ∆T | 21.5
77 | 68 | 381 | 64 | LDB | 55.5
77 | 68 | 381 | 64 | LWB | 52.9
77 | 68 | 381 | 64 | kW | 0.75
80 | 68 | 381 | 67 | MBh | 12.77
80 | 68 | 381 | 67 | S/T | 0.695
80 | 68 | 381 | 67 | ∆T | 21.6
80 | 68 | 381 | 67 | LDB | 58.4
80 | 68 | 381 | 67 | LWB | 56.3
80 | 68 | 381 | 67 | kW | 0.76
86 | 68 | 381 | 72 | MBh | 13.44
86 | 68 | 381 | 72 | S/T | 0.671
86 | 68 | 381 | 72 | ∆T | 21.9
86 | 68 | 381 | 72 | LDB | 64.1
86 | 68 | 381 | 72 | LWB | 62
86 | 68 | 381 | 72 | kW | 0.76
90 | 68 | 381 | 75 | MBh | 13.95
90 | 68 | 381 | 75 | S/T | 0.63
90 | 68 | 381 | 75 | ∆T | 21.4
90 | 68 | 381 | 75 | LDB | 68.6
90 | 68 | 381 | 75 | LWB | 65.3
90 | 68 | 381 | 75 | kW | 0.77
68 | 86 | 381 | 57 | MBh | 10.33
68 | 86 | 381 | 57 | S/T | 1
68 | 86 | 381 | 57 | ∆T | 25.1
68 | 86 | 381 | 57 | LDB | 42.9
68 | 86 | 381 | 57 | LWB | 42.9
68 | 86 | 381 | 57 | kW | 0.89
72 | 86 | 381 | 61 | MBh | 10.85
72 | 86 | 381 | 61 | S/T | 0.732
72 | 86 | 381 | 61 | ∆T | 19.3
72 | 86 | 381 | 61 | LDB | 52.7
72 | 86 | 381 | 61 | LWB | 50.8
72 | 86 | 381 | 61 | kW | 0.89
77 | 86 | 381 | 64 | MBh | 11.36
77 | 86 | 381 | 64 | S/T | 0.739
77 | 86 | 381 | 64 | ∆T | 20.4
77 | 86 | 381 | 64 | LDB | 56.6
77 | 86 | 381 | 64 | LWB | 53.9
77 | 86 | 381 | 64 | kW | 0.9
80 | 86 | 381 | 67 | MBh | 11.72
80 | 86 | 381 | 67 | S/T | 0.722
80 | 86 | 381 | 67 | ∆T | 20.6
80 | 86 | 381 | 67 | LDB | 59.4
80 | 86 | 381 | 67 | LWB | 57.3
80 | 86 | 381 | 67 | kW | 0.9
86 | 86 | 381 | 72 | MBh | 12.39
86 | 86 | 381 | 72 | S/T | 0.697
86 | 86 | 381 | 72 | ∆T | 21
86 | 86 | 381 | 72 | LDB | 65
86 | 86 | 381 | 72 | LWB | 62.9
86 | 86 | 381 | 72 | kW | 0.91
90 | 86 | 381 | 75 | MBh | 12.91
90 | 86 | 381 | 75 | S/T | 0.654
90 | 86 | 381 | 75 | ∆T | 20.5
90 | 86 | 381 | 75 | LDB | 69.5
90 | 86 | 381 | 75 | LWB | 66.1
90 | 86 | 381 | 75 | kW | 0.91
68 | 95 | 381 | 57 | MBh | 9.81
68 | 95 | 381 | 57 | S/T | 0.795
68 | 95 | 381 | 57 | ∆T | 19
68 | 95 | 381 | 57 | LDB | 49
68 | 95 | 381 | 57 | LWB | 47
68 | 95 | 381 | 57 | kW | 0.96
72 | 95 | 381 | 61 | MBh | 10.32
72 | 95 | 381 | 61 | S/T | 0.746
72 | 95 | 381 | 61 | ∆T | 18.7
72 | 95 | 381 | 61 | LDB | 53.3
72 | 95 | 381 | 61 | LWB | 51.3
72 | 95 | 381 | 61 | kW | 0.97
77 | 95 | 381 | 64 | MBh | 10.84
77 | 95 | 381 | 64 | S/T | 0.755
77 | 95 | 381 | 64 | ∆T | 19.9
77 | 95 | 381 | 64 | LDB | 57.1
77 | 95 | 381 | 64 | LWB | 54.5
77 | 95 | 381 | 64 | kW | 0.97
80 | 95 | 381 | 67 | MBh | 11.2
80 | 95 | 381 | 67 | S/T | 0.737
80 | 95 | 381 | 67 | ∆T | 20
80 | 95 | 381 | 67 | LDB | 60
80 | 95 | 381 | 67 | LWB | 57.8
80 | 95 | 381 | 67 | kW | 0.97
86 | 95 | 381 | 72 | MBh | 11.87
86 | 95 | 381 | 72 | S/T | 0.712
86 | 95 | 381 | 72 | ∆T | 20.5
86 | 95 | 381 | 72 | LDB | 65.5
86 | 95 | 381 | 72 | LWB | 63.3
86 | 95 | 381 | 72 | kW | 0.98
90 | 95 | 381 | 75 | MBh | 12.39
90 | 95 | 381 | 75 | S/T | 0.667
90 | 95 | 381 | 75 | ∆T | 20.1
90 | 95 | 381 | 75 | LDB | 69.9
90 | 95 | 381 | 75 | LWB | 66.5
90 | 95 | 381 | 75 | kW | 0.98
68 | 104 | 381 | 57 | MBh | 9.29
68 | 104 | 381 | 57 | S/T | 0.813
68 | 104 | 381 | 57 | ∆T | 18.3
68 | 104 | 381 | 57 | LDB | 49.7
68 | 104 | 381 | 57 | LWB | 47.6
68 | 104 | 381 | 57 | kW | 1.03
72 | 104 | 381 | 61 | MBh | 9.8
72 | 104 | 381 | 61 | S/T | 0.762
72 | 104 | 381 | 61 | ∆T | 18.2
72 | 104 | 381 | 61 | LDB | 53.8
72 | 104 | 381 | 61 | LWB | 51.9
72 | 104 | 381 | 61 | kW | 1.04
77 | 104 | 381 | 64 | MBh | 10.32
77 | 104 | 381 | 64 | S/T | 0.771
77 | 104 | 381 | 64 | ∆T | 19.3
77 | 104 | 381 | 64 | LDB | 57.7
77 | 104 | 381 | 64 | LWB | 55
77 | 104 | 381 | 64 | kW | 1.04
80 | 104 | 381 | 67 | MBh | 11.2
80 | 104 | 381 | 67 | S/T | 0.718
80 | 104 | 381 | 67 | ∆T | 19.5
80 | 104 | 381 | 67 | LDB | 60.5
80 | 104 | 381 | 67 | LWB | 57.8
80 | 104 | 381 | 67 | kW | 1.05
86 | 104 | 381 | 72 | MBh | 11.35
86 | 104 | 381 | 72 | S/T | 0.729
86 | 104 | 381 | 72 | ∆T | 20.1
86 | 104 | 381 | 72 | LDB | 65.9
86 | 104 | 381 | 72 | LWB | 63.7
86 | 104 | 381 | 72 | kW | 1.05
90 | 104 | 381 | 75 | MBh | 11.87
90 | 104 | 381 | 75 | S/T | 0.682
90 | 104 | 381 | 75 | ∆T | 19.7
90 | 104 | 381 | 75 | LDB | 70.3
90 | 104 | 381 | 75 | LWB | 66.9
90 | 104 | 381 | 75 | kW | 1.06
68 | 115 | 381 | 57 | MBh | 8.66
68 | 115 | 381 | 57 | S/T | 0.838
68 | 115 | 381 | 57 | ∆T | 17.6
68 | 115 | 381 | 57 | LDB | 50.4
68 | 115 | 381 | 57 | LWB | 48.3
68 | 115 | 381 | 57 | kW | 1.08
72 | 115 | 381 | 61 | MBh | 9.18
72 | 115 | 381 | 61 | S/T | 0.783
72 | 115 | 381 | 61 | ∆T | 17.5
72 | 115 | 381 | 61 | LDB | 54.5
72 | 115 | 381 | 61 | LWB | 52.5
72 | 115 | 381 | 61 | kW | 1.08
77 | 115 | 381 | 64 | MBh | 9.69
77 | 115 | 381 | 64 | S/T | 0.795
77 | 115 | 381 | 64 | ∆T | 18.7
77 | 115 | 381 | 64 | LDB | 58.3
77 | 115 | 381 | 64 | LWB | 55.5
77 | 115 | 381 | 64 | kW | 1.08
80 | 115 | 381 | 67 | MBh | 10.05
80 | 115 | 381 | 67 | S/T | 0.776
80 | 115 | 381 | 67 | ∆T | 19
80 | 115 | 381 | 67 | LDB | 61
80 | 115 | 381 | 67 | LWB | 58.8
80 | 115 | 381 | 67 | kW | 1.08
86 | 115 | 381 | 72 | MBh | 10.73
86 | 115 | 381 | 72 | S/T | 0.75
86 | 115 | 381 | 72 | ∆T | 19.6
86 | 115 | 381 | 72 | LDB | 66.4
86 | 115 | 381 | 72 | LWB | 64.2
86 | 115 | 381 | 72 | kW | 1.08
90 | 115 | 381 | 75 | MBh | 11.24
90 | 115 | 381 | 75 | S/T | 0.703
90 | 115 | 381 | 75 | ∆T | 19.2
90 | 115 | 381 | 75 | LDB | 70.8
90 | 115 | 381 | 75 | LWB | 67.4
90 | 115 | 381 | 75 | kW | 1.08

## RXT12AVJU9 - FTXV12AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 392 | 57 | MBh | 14.94 | 75 | 60 | 59 | 23.63 | 1.89
68 | 50 | 392 | 57 | S/T | 0.704 | 75 | 60 | 70 | 22.83 | 1.94
68 | 50 | 392 | 57 | ∆T | 24.8 | 75 | 60 | 72 | 22.72 | 1.95
68 | 50 | 392 | 57 | LDB | 43.2 | 75 | 60 | 75 | 22.46 | 1.96
68 | 50 | 392 | 57 | LWB | 41.5 | 75 | 60 | 77 | 22.33 | 1.97
68 | 50 | 392 | 57 | kW | 0.79 | 75 | 60 | 81 | 21.12 | 1.83
72 | 50 | 392 | 61 | MBh | 16.86 | 47 | 43 | 59 | 19.59 | 1.75
72 | 50 | 392 | 61 | S/T | 0.651 | 47 | 43 | 70 | 18.8 | 1.8
72 | 50 | 392 | 61 | ∆T | 25.9 | 47 | 43 | 72 | 18.68 | 1.81
72 | 50 | 392 | 61 | LDB | 46.1 | 47 | 43 | 75 | 18.42 | 1.82
72 | 50 | 392 | 61 | LWB | 44.7 | 47 | 43 | 77 | 18.29 | 1.83
72 | 50 | 392 | 61 | kW | 0.92 | 47 | 43 | 81 | 18.03 | 1.85
77 | 50 | 392 | 64 | MBh | 17.53 | 35 | 32 | 59 | 18.13 | 1.86
77 | 50 | 392 | 64 | S/T | 0.646 | 35 | 32 | 70 | 17.29 | 1.91
77 | 50 | 392 | 64 | ∆T | 26.7 | 35 | 32 | 72 | 17.16 | 1.92
77 | 50 | 392 | 64 | LDB | 50.3 | 35 | 32 | 75 | 16.89 | 1.94
77 | 50 | 392 | 64 | LWB | 48.1 | 35 | 32 | 77 | 16.75 | 1.95
77 | 50 | 392 | 64 | kW | 0.93 | 35 | 32 | 81 | 16.47 | 1.97
80 | 50 | 392 | 67 | MBh | 18 | 25 | 23 | 59 | 16.93 | 1.95
80 | 50 | 392 | 67 | S/T | 0.628 | 25 | 23 | 70 | 16.03 | 2.01
80 | 50 | 392 | 67 | ∆T | 26.7 | 25 | 23 | 72 | 15.9 | 2.02
80 | 50 | 392 | 67 | LDB | 53.3 | 25 | 23 | 75 | 15.6 | 2.04
80 | 50 | 392 | 67 | LWB | 51.7 | 25 | 23 | 77 | 15.46 | 2.05
80 | 50 | 392 | 67 | kW | 0.93 | 25 | 23 | 81 | 15.16 | 2.07
86 | 50 | 392 | 72 | MBh | 18.87 | 16 | 14 | 59 | 15.74 | 2.04
86 | 50 | 392 | 72 | S/T | 0.599 | 16 | 14 | 70 | 14.77 | 2.1
86 | 50 | 392 | 72 | ∆T | 26.7 | 16 | 14 | 72 | 14.63 | 2.11
86 | 50 | 392 | 72 | LDB | 59.3 | 16 | 14 | 75 | 14.31 | 2.14
86 | 50 | 392 | 72 | LWB | 57.8 | 16 | 14 | 77 | 14.15 | 2.15
86 | 50 | 392 | 72 | kW | 0.94 | 16 | 14 | 81 | 13.83 | 2.17
90 | 50 | 392 | 75 | MBh | 19.55 | 5 | 5 | 59 | 14.59 | 2.13
90 | 50 | 392 | 75 | S/T | 0.56 | 5 | 5 | 70 | 13.5 | 2.2
90 | 50 | 392 | 75 | ∆T | 25.8 | 5 | 5 | 72 | 13.35 | 2.21
90 | 50 | 392 | 75 | LDB | 64.2 | 5 | 5 | 75 | 13 | 2.23
90 | 50 | 392 | 75 | LWB | 61.3 | 5 | 5 | 77 | 12.82 | 2.25
90 | 50 | 392 | 75 | kW | 1.17 | 5 | 5 | 81 | 12.46 | 2.27
68 | 68 | 392 | 57 | MBh | 14.82 | -4 | -4 | 59 | 12.04 | 2.08
68 | 68 | 392 | 57 | S/T | 0.706 | -4 | -4 | 70 | 10.92 | 2.15
68 | 68 | 392 | 57 | ∆T | 24.7 | -4 | -4 | 72 | 10.76 | 2.16
68 | 68 | 392 | 57 | LDB | 43.3 | -4 | -4 | 75 | 10.39 | 2.19
68 | 68 | 392 | 57 | LWB | 41.6 | -4 | -4 | 77 | 10.21 | 2.2
68 | 68 | 392 | 57 | kW | 1.13 | -4 | -4 | 81 | 9.84 | 2.22
72 | 68 | 392 | 61 | MBh | 15.5 | -13 | -13 | 59 | 9.38 | 2.04
72 | 68 | 392 | 61 | S/T | 0.663 | -13 | -13 | 70 | 8.22 | 2.11
72 | 68 | 392 | 61 | ∆T | 24.3 | -13 | -13 | 72 | 8.05 | 2.13
72 | 68 | 392 | 61 | LDB | 47.7 | -13 | -13 | 75 | 7.67 | 2.15
72 | 68 | 392 | 61 | LWB | 46.2 | -13 | -13 | 77 | 7.49 | 2.16
72 | 68 | 392 | 61 | kW | 1.14 | -13 | -13 | 81 | 7.11 | 2.19
77 | 68 | 392 | 64 | MBh | 16.17
77 | 68 | 392 | 64 | S/T | 0.66
77 | 68 | 392 | 64 | ∆T | 25.2
77 | 68 | 392 | 64 | LDB | 51.8
77 | 68 | 392 | 64 | LWB | 49.5
77 | 68 | 392 | 64 | kW | 1.15
80 | 68 | 392 | 67 | MBh | 16.64
80 | 68 | 392 | 67 | S/T | 0.642
80 | 68 | 392 | 67 | ∆T | 25.2
80 | 68 | 392 | 67 | LDB | 54.8
80 | 68 | 392 | 67 | LWB | 53.1
80 | 68 | 392 | 67 | kW | 1.15
86 | 68 | 392 | 72 | MBh | 17.51
86 | 68 | 392 | 72 | S/T | 0.614
86 | 68 | 392 | 72 | ∆T | 25.4
86 | 68 | 392 | 72 | LDB | 60.6
86 | 68 | 392 | 72 | LWB | 59
86 | 68 | 392 | 72 | kW | 1.16
90 | 68 | 392 | 75 | MBh | 18.19
90 | 68 | 392 | 75 | S/T | 0.574
90 | 68 | 392 | 75 | ∆T | 24.7
90 | 68 | 392 | 75 | LDB | 65.3
90 | 68 | 392 | 75 | LWB | 62.4
90 | 68 | 392 | 75 | kW | 1.17
68 | 86 | 392 | 57 | MBh | 13.46
68 | 86 | 392 | 57 | S/T | 0.724
68 | 86 | 392 | 57 | ∆T | 23
68 | 86 | 392 | 57 | LDB | 45
68 | 86 | 392 | 57 | LWB | 43.2
68 | 86 | 392 | 57 | kW | 1.35
72 | 86 | 392 | 61 | MBh | 14.14
72 | 86 | 392 | 61 | S/T | 0.679
72 | 86 | 392 | 61 | ∆T | 22.7
72 | 86 | 392 | 61 | LDB | 49.3
72 | 86 | 392 | 61 | LWB | 47.7
72 | 86 | 392 | 61 | kW | 1.36
77 | 86 | 392 | 64 | MBh | 14.81
77 | 86 | 392 | 64 | S/T | 0.679
77 | 86 | 392 | 64 | ∆T | 23.7
77 | 86 | 392 | 64 | LDB | 53.3
77 | 86 | 392 | 64 | LWB | 50.9
77 | 86 | 392 | 64 | kW | 1.37
80 | 86 | 392 | 67 | MBh | 15.28
80 | 86 | 392 | 67 | S/T | 0.66
80 | 86 | 392 | 67 | ∆T | 23.8
80 | 86 | 392 | 67 | LDB | 56.2
80 | 86 | 392 | 67 | LWB | 54.4
80 | 86 | 392 | 67 | kW | 1.37
86 | 86 | 392 | 72 | MBh | 16.15
86 | 86 | 392 | 72 | S/T | 0.632
86 | 86 | 392 | 72 | ∆T | 24.1
86 | 86 | 392 | 72 | LDB | 61.9
86 | 86 | 392 | 72 | LWB | 60.1
86 | 86 | 392 | 72 | kW | 1.38
90 | 86 | 392 | 75 | MBh | 16.83
90 | 86 | 392 | 75 | S/T | 0.591
90 | 86 | 392 | 75 | ∆T | 23.5
90 | 86 | 392 | 75 | LDB | 66.5
90 | 86 | 392 | 75 | LWB | 63.5
90 | 86 | 392 | 75 | kW | 1.39
68 | 95 | 392 | 57 | MBh | 12.78
68 | 95 | 392 | 57 | S/T | 0.736
68 | 95 | 392 | 57 | ∆T | 22.2
68 | 95 | 392 | 57 | LDB | 45.8
68 | 95 | 392 | 57 | LWB | 44
68 | 95 | 392 | 57 | kW | 1.46
72 | 95 | 392 | 61 | MBh | 13.46
72 | 95 | 392 | 61 | S/T | 0.689
72 | 95 | 392 | 61 | ∆T | 21.9
72 | 95 | 392 | 61 | LDB | 50.1
72 | 95 | 392 | 61 | LWB | 48.4
72 | 95 | 392 | 61 | kW | 1.47
77 | 95 | 392 | 64 | MBh | 14.13
77 | 95 | 392 | 64 | S/T | 0.689
77 | 95 | 392 | 64 | ∆T | 23
77 | 95 | 392 | 64 | LDB | 54
77 | 95 | 392 | 64 | LWB | 51.6
77 | 95 | 392 | 64 | kW | 1.48
80 | 95 | 392 | 67 | MBh | 14.6
80 | 95 | 392 | 67 | S/T | 0.671
80 | 95 | 392 | 67 | ∆T | 23.1
80 | 95 | 392 | 67 | LDB | 56.9
80 | 95 | 392 | 67 | LWB | 55
80 | 95 | 392 | 67 | kW | 1.48
86 | 95 | 392 | 72 | MBh | 15.47
86 | 95 | 392 | 72 | S/T | 0.643
86 | 95 | 392 | 72 | ∆T | 23.5
86 | 95 | 392 | 72 | LDB | 62.5
86 | 95 | 392 | 72 | LWB | 60.7
86 | 95 | 392 | 72 | kW | 1.49
90 | 95 | 392 | 75 | MBh | 16.15
90 | 95 | 392 | 75 | S/T | 0.601
90 | 95 | 392 | 75 | ∆T | 22.9
90 | 95 | 392 | 75 | LDB | 67.1
90 | 95 | 392 | 75 | LWB | 64
90 | 95 | 392 | 75 | kW | 1.5
68 | 104 | 392 | 57 | MBh | 12.1
68 | 104 | 392 | 57 | S/T | 0.748
68 | 104 | 392 | 57 | ∆T | 21.4
68 | 104 | 392 | 57 | LDB | 46.6
68 | 104 | 392 | 57 | LWB | 44.8
68 | 104 | 392 | 57 | kW | 1.51
72 | 104 | 392 | 61 | MBh | 12.78
72 | 104 | 392 | 61 | S/T | 0.7
72 | 104 | 392 | 61 | ∆T | 21.1
72 | 104 | 392 | 61 | LDB | 50.9
72 | 104 | 392 | 61 | LWB | 49.1
72 | 104 | 392 | 61 | kW | 1.51
77 | 104 | 392 | 64 | MBh | 13.45
77 | 104 | 392 | 64 | S/T | 0.702
77 | 104 | 392 | 64 | ∆T | 22.3
77 | 104 | 392 | 64 | LDB | 54.7
77 | 104 | 392 | 64 | LWB | 52.3
77 | 104 | 392 | 64 | kW | 1.51
80 | 104 | 392 | 67 | MBh | 13.92
80 | 104 | 392 | 67 | S/T | 0.683
80 | 104 | 392 | 67 | ∆T | 22.5
80 | 104 | 392 | 67 | LDB | 57.5
80 | 104 | 392 | 67 | LWB | 55.6
80 | 104 | 392 | 67 | kW | 1.51
86 | 104 | 392 | 72 | MBh | 14.78
86 | 104 | 392 | 72 | S/T | 0.656
86 | 104 | 392 | 72 | ∆T | 22.9
86 | 104 | 392 | 72 | LDB | 63.1
86 | 104 | 392 | 72 | LWB | 61.2
86 | 104 | 392 | 72 | kW | 1.51
90 | 104 | 392 | 75 | MBh | 15.42
90 | 104 | 392 | 75 | S/T | 0.613
90 | 104 | 392 | 75 | ∆T | 22.3
90 | 104 | 392 | 75 | LDB | 67.7
90 | 104 | 392 | 75 | LWB | 64.5
90 | 104 | 392 | 75 | kW | 1.51
68 | 115 | 392 | 57 | MBh | 11.29
68 | 115 | 392 | 57 | S/T | 0.766
68 | 115 | 392 | 57 | ∆T | 20.4
68 | 115 | 392 | 57 | LDB | 47.6
68 | 115 | 392 | 57 | LWB | 45.7
68 | 115 | 392 | 57 | kW | 1.19
72 | 115 | 392 | 61 | MBh | 11.96
72 | 115 | 392 | 61 | S/T | 0.717
72 | 115 | 392 | 61 | ∆T | 20.2
72 | 115 | 392 | 61 | LDB | 51.8
72 | 115 | 392 | 61 | LWB | 50
72 | 115 | 392 | 61 | kW | 1.19
77 | 115 | 392 | 64 | MBh | 12.63
77 | 115 | 392 | 64 | S/T | 0.719
77 | 115 | 392 | 64 | ∆T | 21.4
77 | 115 | 392 | 64 | LDB | 55.6
77 | 115 | 392 | 64 | LWB | 53
77 | 115 | 392 | 64 | kW | 1.19
80 | 115 | 392 | 67 | MBh | 13.1
80 | 115 | 392 | 67 | S/T | 0.7
80 | 115 | 392 | 67 | ∆T | 21.7
80 | 115 | 392 | 67 | LDB | 58.3
80 | 115 | 392 | 67 | LWB | 56.4
80 | 115 | 392 | 67 | kW | 1.19
86 | 115 | 392 | 72 | MBh | 13.98
86 | 115 | 392 | 72 | S/T | 0.672
86 | 115 | 392 | 72 | ∆T | 22.2
86 | 115 | 392 | 72 | LDB | 63.8
86 | 115 | 392 | 72 | LWB | 61.9
86 | 115 | 392 | 72 | kW | 1.19
90 | 115 | 392 | 75 | MBh | 14.65
90 | 115 | 392 | 75 | S/T | 0.627
90 | 115 | 392 | 75 | ∆T | 21.7
90 | 115 | 392 | 75 | LDB | 68.3
90 | 115 | 392 | 75 | LWB | 65.1
90 | 115 | 392 | 75 | kW | 1.19

## RXT15AVJU9 - FTXV15AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 540 | 57 | MBh | 19.83 | 75 | 60 | 59 | 30.91 | 2.15
68 | 50 | 540 | 57 | S/T | 0.704 | 75 | 60 | 70 | 29.88 | 2.21
68 | 50 | 540 | 57 | ∆T | 23.9 | 75 | 60 | 72 | 29.72 | 2.22
68 | 50 | 540 | 57 | LDB | 44.1 | 75 | 60 | 75 | 29.39 | 2.24
68 | 50 | 540 | 57 | LWB | 42.1 | 75 | 60 | 77 | 29.22 | 2.25
68 | 50 | 540 | 57 | kW | 0.89 | 75 | 60 | 81 | 28.88 | 2.26
72 | 50 | 540 | 61 | MBh | 21.27 | 47 | 43 | 59 | 25.64 | 1.99
72 | 50 | 540 | 61 | S/T | 0.658 | 47 | 43 | 70 | 24.6 | 2.05
72 | 50 | 540 | 61 | ∆T | 24 | 47 | 43 | 72 | 24.45 | 2.06
72 | 50 | 540 | 61 | LDB | 48 | 47 | 43 | 75 | 24.11 | 2.08
72 | 50 | 540 | 61 | LWB | 46.3 | 47 | 43 | 77 | 23.94 | 2.09
72 | 50 | 540 | 61 | kW | 0.94 | 47 | 43 | 81 | 23.6 | 2.1
77 | 50 | 540 | 64 | MBh | 22.12 | 35 | 32 | 59 | 23.91 | 2.25
77 | 50 | 540 | 64 | S/T | 0.655 | 35 | 32 | 70 | 22.8 | 2.31
77 | 50 | 540 | 64 | ∆T | 24.8 | 35 | 32 | 72 | 22.64 | 2.32
77 | 50 | 540 | 64 | LDB | 52.2 | 35 | 32 | 75 | 22.27 | 2.35
77 | 50 | 540 | 64 | LWB | 49.6 | 35 | 32 | 77 | 22.09 | 2.36
77 | 50 | 540 | 64 | kW | 0.95 | 35 | 32 | 81 | 21.73 | 2.38
80 | 50 | 540 | 67 | MBh | 22.71 | 25 | 23 | 59 | 22.49 | 2.46
80 | 50 | 540 | 67 | S/T | 0.637 | 25 | 23 | 70 | 21.3 | 2.53
80 | 50 | 540 | 67 | ∆T | 24.8 | 25 | 23 | 72 | 21.12 | 2.54
80 | 50 | 540 | 67 | LDB | 55.2 | 25 | 23 | 75 | 20.73 | 2.57
80 | 50 | 540 | 67 | LWB | 53.2 | 25 | 23 | 77 | 20.54 | 2.58
80 | 50 | 540 | 67 | kW | 0.95 | 25 | 23 | 81 | 20.15 | 2.61
86 | 50 | 540 | 72 | MBh | 23.82 | 16 | 14 | 59 | 21.11 | 2.67
86 | 50 | 540 | 72 | S/T | 0.608 | 16 | 14 | 70 | 19.8 | 2.75
86 | 50 | 540 | 72 | ∆T | 24.8 | 16 | 14 | 72 | 19.61 | 2.77
86 | 50 | 540 | 72 | LDB | 61.2 | 16 | 14 | 75 | 19.18 | 2.79
86 | 50 | 540 | 72 | LWB | 59.1 | 16 | 14 | 77 | 18.97 | 2.81
86 | 50 | 540 | 72 | kW | 0.96 | 16 | 14 | 81 | 18.54 | 2.84
90 | 50 | 540 | 75 | MBh | 24.67 | 5 | 5 | 59 | 19.77 | 2.87
90 | 50 | 540 | 75 | S/T | 0.57 | 5 | 5 | 70 | 18.3 | 2.97
90 | 50 | 540 | 75 | ∆T | 24.1 | 5 | 5 | 72 | 18.08 | 2.99
90 | 50 | 540 | 75 | LDB | 65.9 | 5 | 5 | 75 | 17.6 | 3.02
90 | 50 | 540 | 75 | LWB | 62.6 | 5 | 5 | 77 | 17.36 | 3.04
90 | 50 | 540 | 75 | kW | 0.97 | 5 | 5 | 81 | 16.88 | 3.07
68 | 68 | 540 | 57 | MBh | 18.71 | -4 | -4 | 59 | 16.3 | 2.81
68 | 68 | 540 | 57 | S/T | 0.715 | -4 | -4 | 70 | 14.79 | 2.91
68 | 68 | 540 | 57 | ∆T | 22.9 | -4 | -4 | 72 | 14.57 | 2.92
68 | 68 | 540 | 57 | LDB | 45.1 | -4 | -4 | 75 | 14.08 | 2.96
68 | 68 | 540 | 57 | LWB | 43.1 | -4 | -4 | 77 | 13.83 | 2.97
68 | 68 | 540 | 57 | kW | 1.16 | -4 | -4 | 81 | 13.33 | 3.01
72 | 68 | 540 | 61 | MBh | 19.56 | -13 | -13 | 59 | 12.7 | 2.75
72 | 68 | 540 | 61 | S/T | 0.672 | -13 | -13 | 70 | 11.14 | 2.86
72 | 68 | 540 | 61 | ∆T | 22.5 | -13 | -13 | 72 | 10.91 | 2.87
72 | 68 | 540 | 61 | LDB | 49.5 | -13 | -13 | 75 | 10.39 | 2.91
72 | 68 | 540 | 61 | LWB | 47.6 | -13 | -13 | 77 | 10.14 | 2.92
72 | 68 | 540 | 61 | kW | 1.16 | -13 | -13 | 81 | 9.63 | 2.96
77 | 68 | 540 | 64 | MBh | 20.4
77 | 68 | 540 | 64 | S/T | 0.671
77 | 68 | 540 | 64 | ∆T | 23.5
77 | 68 | 540 | 64 | LDB | 53.5
77 | 68 | 540 | 64 | LWB | 50.9
77 | 68 | 540 | 64 | kW | 1.17
80 | 68 | 540 | 67 | MBh | 21
80 | 68 | 540 | 67 | S/T | 0.652
80 | 68 | 540 | 67 | ∆T | 23.5
80 | 68 | 540 | 67 | LDB | 56.5
80 | 68 | 540 | 67 | LWB | 54.4
80 | 68 | 540 | 67 | kW | 1.18
86 | 68 | 540 | 72 | MBh | 22.1
86 | 68 | 540 | 72 | S/T | 0.625
86 | 68 | 540 | 72 | ∆T | 23.7
86 | 68 | 540 | 72 | LDB | 62.3
86 | 68 | 540 | 72 | LWB | 60.2
86 | 68 | 540 | 72 | kW | 1.18
90 | 68 | 540 | 75 | MBh | 22.95
90 | 68 | 540 | 75 | S/T | 0.585
90 | 68 | 540 | 75 | ∆T | 23
90 | 68 | 540 | 75 | LDB | 67
90 | 68 | 540 | 75 | LWB | 63.6
90 | 68 | 540 | 75 | kW | 1.19
68 | 86 | 540 | 57 | MBh | 16.99
68 | 86 | 540 | 57 | S/T | 0.735
68 | 86 | 540 | 57 | ∆T | 21.4
68 | 86 | 540 | 57 | LDB | 46.6
68 | 86 | 540 | 57 | LWB | 44.5
68 | 86 | 540 | 57 | kW | 1.38
72 | 86 | 540 | 61 | MBh | 17.84
72 | 86 | 540 | 61 | S/T | 0.689
72 | 86 | 540 | 61 | ∆T | 21.1
72 | 86 | 540 | 61 | LDB | 50.9
72 | 86 | 540 | 61 | LWB | 49
72 | 86 | 540 | 61 | kW | 1.39
77 | 86 | 540 | 64 | MBh | 18.69
77 | 86 | 540 | 64 | S/T | 0.69
77 | 86 | 540 | 64 | ∆T | 22.1
77 | 86 | 540 | 64 | LDB | 54.9
77 | 86 | 540 | 64 | LWB | 52.1
77 | 86 | 540 | 64 | kW | 1.39
80 | 86 | 540 | 67 | MBh | 19.28
80 | 86 | 540 | 67 | S/T | 0.672
80 | 86 | 540 | 67 | ∆T | 22.2
80 | 86 | 540 | 67 | LDB | 57.8
80 | 86 | 540 | 67 | LWB | 55.6
80 | 86 | 540 | 67 | kW | 1.4
86 | 86 | 540 | 72 | MBh | 20.39
86 | 86 | 540 | 72 | S/T | 0.645
86 | 86 | 540 | 72 | ∆T | 22.5
86 | 86 | 540 | 72 | LDB | 63.5
86 | 86 | 540 | 72 | LWB | 61.2
86 | 86 | 540 | 72 | kW | 1.41
90 | 86 | 540 | 75 | MBh | 21.24
90 | 86 | 540 | 75 | S/T | 0.604
90 | 86 | 540 | 75 | ∆T | 22
90 | 86 | 540 | 75 | LDB | 68
90 | 86 | 540 | 75 | LWB | 64.5
90 | 86 | 540 | 75 | kW | 1.41
68 | 95 | 540 | 57 | MBh | 16.13
68 | 95 | 540 | 57 | S/T | 0.747
68 | 95 | 540 | 57 | ∆T | 20.7
68 | 95 | 540 | 57 | LDB | 47.3
68 | 95 | 540 | 57 | LWB | 45.2
68 | 95 | 540 | 57 | kW | 1.49
72 | 95 | 540 | 61 | MBh | 16.98
72 | 95 | 540 | 61 | S/T | 0.701
72 | 95 | 540 | 61 | ∆T | 20.4
72 | 95 | 540 | 61 | LDB | 51.6
72 | 95 | 540 | 61 | LWB | 49.6
72 | 95 | 540 | 61 | kW | 1.5
77 | 95 | 540 | 64 | MBh | 17.83
77 | 95 | 540 | 64 | S/T | 0.702
77 | 95 | 540 | 64 | ∆T | 21.5
77 | 95 | 540 | 64 | LDB | 55.5
77 | 95 | 540 | 64 | LWB | 52.7
77 | 95 | 540 | 64 | kW | 1.51
80 | 95 | 540 | 67 | MBh | 18.4
80 | 95 | 540 | 67 | S/T | 0.685
80 | 95 | 540 | 67 | ∆T | 21.6
80 | 95 | 540 | 67 | LDB | 58.4
80 | 95 | 540 | 67 | LWB | 56.1
80 | 95 | 540 | 67 | kW | 1.51
86 | 95 | 540 | 72 | MBh | 19.53
86 | 95 | 540 | 72 | S/T | 0.656
86 | 95 | 540 | 72 | ∆T | 22
86 | 95 | 540 | 72 | LDB | 64
86 | 95 | 540 | 72 | LWB | 61.7
86 | 95 | 540 | 72 | kW | 1.52
90 | 95 | 540 | 75 | MBh | 20.38
90 | 95 | 540 | 75 | S/T | 0.614
90 | 95 | 540 | 75 | ∆T | 21.5
90 | 95 | 540 | 75 | LDB | 68.5
90 | 95 | 540 | 75 | LWB | 65
90 | 95 | 540 | 75 | kW | 1.53
68 | 104 | 540 | 57 | MBh | 15.27
68 | 104 | 540 | 57 | S/T | 0.761
68 | 104 | 540 | 57 | ∆T | 19.9
68 | 104 | 540 | 57 | LDB | 48.1
68 | 104 | 540 | 57 | LWB | 45.9
68 | 104 | 540 | 57 | kW | 1.6
72 | 104 | 540 | 61 | MBh | 16.12
72 | 104 | 540 | 61 | S/T | 0.713
72 | 104 | 540 | 61 | ∆T | 19.7
72 | 104 | 540 | 61 | LDB | 52.3
72 | 104 | 540 | 61 | LWB | 50.2
72 | 104 | 540 | 61 | kW | 1.61
77 | 104 | 540 | 64 | MBh | 16.97
77 | 104 | 540 | 64 | S/T | 0.715
77 | 104 | 540 | 64 | ∆T | 20.8
77 | 104 | 540 | 64 | LDB | 56.2
77 | 104 | 540 | 64 | LWB | 53.3
77 | 104 | 540 | 64 | kW | 1.62
80 | 104 | 540 | 67 | MBh | 17.57
80 | 104 | 540 | 67 | S/T | 0.697
80 | 104 | 540 | 67 | ∆T | 21
80 | 104 | 540 | 67 | LDB | 59
80 | 104 | 540 | 67 | LWB | 56.7
80 | 104 | 540 | 67 | kW | 1.62
86 | 104 | 540 | 72 | MBh | 18.67
86 | 104 | 540 | 72 | S/T | 0.67
86 | 104 | 540 | 72 | ∆T | 21.4
86 | 104 | 540 | 72 | LDB | 64.6
86 | 104 | 540 | 72 | LWB | 62.2
86 | 104 | 540 | 72 | kW | 1.63
90 | 104 | 540 | 75 | MBh | 19.52
90 | 104 | 540 | 75 | S/T | 0.627
90 | 104 | 540 | 75 | ∆T | 21
90 | 104 | 540 | 75 | LDB | 69
90 | 104 | 540 | 75 | LWB | 65.5
90 | 104 | 540 | 75 | kW | 1.64
68 | 115 | 540 | 57 | MBh | 14.25
68 | 115 | 540 | 57 | S/T | 0.78
68 | 115 | 540 | 57 | ∆T | 19.1
68 | 115 | 540 | 57 | LDB | 48.9
68 | 115 | 540 | 57 | LWB | 46.7
68 | 115 | 540 | 57 | kW | 1.74
72 | 115 | 540 | 61 | MBh | 15.09
72 | 115 | 540 | 61 | S/T | 0.73
72 | 115 | 540 | 61 | ∆T | 18.9
72 | 115 | 540 | 61 | LDB | 53.1
72 | 115 | 540 | 61 | LWB | 51
72 | 115 | 540 | 61 | kW | 1.74
77 | 115 | 540 | 64 | MBh | 15.94
77 | 115 | 540 | 64 | S/T | 0.734
77 | 115 | 540 | 64 | ∆T | 20.1
77 | 115 | 540 | 64 | LDB | 56.9
77 | 115 | 540 | 64 | LWB | 54.1
77 | 115 | 540 | 64 | kW | 1.75
80 | 115 | 540 | 67 | MBh | 16.54
80 | 115 | 540 | 67 | S/T | 0.715
80 | 115 | 540 | 67 | ∆T | 20.3
80 | 115 | 540 | 67 | LDB | 59.7
80 | 115 | 540 | 67 | LWB | 57.3
80 | 115 | 540 | 67 | kW | 1.76
86 | 115 | 540 | 72 | MBh | 17.64
86 | 115 | 540 | 72 | S/T | 0.687
86 | 115 | 540 | 72 | ∆T | 20.8
86 | 115 | 540 | 72 | LDB | 65.2
86 | 115 | 540 | 72 | LWB | 62.8
86 | 115 | 540 | 72 | kW | 1.76
90 | 115 | 540 | 75 | MBh | 18.49
90 | 115 | 540 | 75 | S/T | 0.643
90 | 115 | 540 | 75 | ∆T | 20.4
90 | 115 | 540 | 75 | LDB | 69.6
90 | 115 | 540 | 75 | LWB | 66
90 | 115 | 540 | 75 | kW | 1.77

## RXT18AVJU9 - FTXV18AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 565 | 57 | MBh | 20.47 | 75 | 60 | 59 | 34.97 | 2.96
68 | 50 | 565 | 57 | S/T | 0.704 | 75 | 60 | 70 | 34.01 | 3.02
68 | 50 | 565 | 57 | ∆T | 23.6 | 75 | 60 | 72 | 33.62 | 3.04
68 | 50 | 565 | 57 | LDB | 44.4 | 75 | 60 | 75 | 33.23 | 3.07
68 | 50 | 565 | 57 | LWB | 42.4 | 75 | 60 | 77 | 33.04 | 3.08
68 | 50 | 565 | 57 | kW | 0.87 | 75 | 60 | 81 | 32.65 | 3.11
72 | 50 | 565 | 61 | MBh | 25.14 | 47 | 43 | 59 | 28.97 | 2.74
72 | 50 | 565 | 61 | S/T | 0.64 | 47 | 43 | 70 | 28 | 2.8
72 | 50 | 565 | 61 | ∆T | 26.4 | 47 | 43 | 72 | 27.61 | 2.83
72 | 50 | 565 | 61 | LDB | 45.6 | 47 | 43 | 75 | 27.23 | 2.85
72 | 50 | 565 | 61 | LWB | 44 | 47 | 43 | 77 | 27.03 | 2.86
72 | 50 | 565 | 61 | kW | 1.16 | 47 | 43 | 81 | 26.65 | 2.89
77 | 50 | 565 | 64 | MBh | 26.41 | 35 | 32 | 59 | 27.22 | 2.93
77 | 50 | 565 | 64 | S/T | 0.632 | 35 | 32 | 70 | 26.17 | 3
77 | 50 | 565 | 64 | ∆T | 27.4 | 35 | 32 | 72 | 25.75 | 3.03
77 | 50 | 565 | 64 | LDB | 49.6 | 35 | 32 | 75 | 25.34 | 3.06
77 | 50 | 565 | 64 | LWB | 47.2 | 35 | 32 | 77 | 25.13 | 3.08
77 | 50 | 565 | 64 | kW | 1.19 | 35 | 32 | 81 | 24.71 | 3.1
80 | 50 | 565 | 67 | MBh | 27.12 | 25 | 23 | 59 | 25.78 | 3.1
80 | 50 | 565 | 67 | S/T | 0.613 | 25 | 23 | 70 | 24.65 | 3.18
80 | 50 | 565 | 67 | ∆T | 27.3 | 25 | 23 | 72 | 24.19 | 3.21
80 | 50 | 565 | 67 | LDB | 52.7 | 25 | 23 | 75 | 23.74 | 3.24
80 | 50 | 565 | 67 | LWB | 50.9 | 25 | 23 | 77 | 23.52 | 3.25
80 | 50 | 565 | 67 | kW | 1.19 | 25 | 23 | 81 | 23.06 | 3.29
86 | 50 | 565 | 72 | MBh | 28.44 | 16 | 14 | 59 | 24.37 | 3.26
86 | 50 | 565 | 72 | S/T | 0.583 | 16 | 14 | 70 | 23.12 | 3.35
86 | 50 | 565 | 72 | ∆T | 27.2 | 16 | 14 | 72 | 22.62 | 3.38
86 | 50 | 565 | 72 | LDB | 58.8 | 16 | 14 | 75 | 22.12 | 3.42
86 | 50 | 565 | 72 | LWB | 57 | 16 | 14 | 77 | 21.87 | 3.43
86 | 50 | 565 | 72 | kW | 1.2 | 16 | 14 | 81 | 21.37 | 3.47
90 | 50 | 565 | 75 | MBh | 29.45 | 5 | 5 | 59 | 23.02 | 3.42
90 | 50 | 565 | 75 | S/T | 0.544 | 5 | 5 | 70 | 21.6 | 3.52
90 | 50 | 565 | 75 | ∆T | 26.3 | 5 | 5 | 72 | 21.03 | 3.56
90 | 50 | 565 | 75 | LDB | 63.7 | 5 | 5 | 75 | 20.47 | 3.59
90 | 50 | 565 | 75 | LWB | 60.6 | 5 | 5 | 77 | 20.18 | 3.61
90 | 50 | 565 | 75 | kW | 1.21 | 5 | 5 | 81 | 19.61 | 3.65
68 | 68 | 565 | 57 | MBh | 20.47 | -4 | -4 | 59 | 19.9 | 3.07
68 | 68 | 565 | 57 | S/T | 0.704 | -4 | -4 | 70 | 18.36 | 3.17
68 | 68 | 565 | 57 | ∆T | 23.6 | -4 | -4 | 72 | 17.75 | 3.2
68 | 68 | 565 | 57 | LDB | 44.4 | -4 | -4 | 75 | 17.13 | 3.24
68 | 68 | 565 | 57 | LWB | 42.4 | -4 | -4 | 77 | 16.82 | 3.26
68 | 68 | 565 | 57 | kW | 1.23 | -4 | -4 | 81 | 16.21 | 3.29
72 | 68 | 565 | 61 | MBh | 23.35 | -13 | -13 | 59 | 16.86 | 2.73
72 | 68 | 565 | 61 | S/T | 0.649 | -13 | -13 | 70 | 15.12 | 2.81
72 | 68 | 565 | 61 | ∆T | 24.8 | -13 | -13 | 72 | 14.42 | 2.85
72 | 68 | 565 | 61 | LDB | 47.2 | -13 | -13 | 75 | 13.73 | 2.88
72 | 68 | 565 | 61 | LWB | 45.4 | -13 | -13 | 77 | 13.38 | 2.9
72 | 68 | 565 | 61 | kW | 1.46 | -13 | -13 | 81 | 12.53 | 2.86
77 | 68 | 565 | 64 | MBh | 24.36
77 | 68 | 565 | 64 | S/T | 0.644
77 | 68 | 565 | 64 | ∆T | 25.7
77 | 68 | 565 | 64 | LDB | 51.3
77 | 68 | 565 | 64 | LWB | 48.8
77 | 68 | 565 | 64 | kW | 1.47
80 | 68 | 565 | 67 | MBh | 25.07
80 | 68 | 565 | 67 | S/T | 0.625
80 | 68 | 565 | 67 | ∆T | 25.7
80 | 68 | 565 | 67 | LDB | 54.3
80 | 68 | 565 | 67 | LWB | 52.3
80 | 68 | 565 | 67 | kW | 1.47
86 | 68 | 565 | 72 | MBh | 26.39
86 | 68 | 565 | 72 | S/T | 0.595
86 | 68 | 565 | 72 | ∆T | 25.7
86 | 68 | 565 | 72 | LDB | 60.3
86 | 68 | 565 | 72 | LWB | 58.3
86 | 68 | 565 | 72 | kW | 1.48
90 | 68 | 565 | 75 | MBh | 27.4
90 | 68 | 565 | 75 | S/T | 0.556
90 | 68 | 565 | 75 | ∆T | 25
90 | 68 | 565 | 75 | LDB | 65
90 | 68 | 565 | 75 | LWB | 61.7
90 | 68 | 565 | 75 | kW | 1.49
68 | 86 | 565 | 57 | MBh | 20.29
68 | 86 | 565 | 57 | S/T | 0.706
68 | 86 | 565 | 57 | ∆T | 23.5
68 | 86 | 565 | 57 | LDB | 44.5
68 | 86 | 565 | 57 | LWB | 42.5
68 | 86 | 565 | 57 | kW | 1.73
72 | 86 | 565 | 61 | MBh | 21.3
72 | 86 | 565 | 61 | S/T | 0.662
72 | 86 | 565 | 61 | ∆T | 23.1
72 | 86 | 565 | 61 | LDB | 48.9
72 | 86 | 565 | 61 | LWB | 47
72 | 86 | 565 | 61 | kW | 1.74
77 | 86 | 565 | 64 | MBh | 22.31
77 | 86 | 565 | 64 | S/T | 0.659
77 | 86 | 565 | 64 | ∆T | 24.1
77 | 86 | 565 | 64 | LDB | 52.9
77 | 86 | 565 | 64 | LWB | 50.2
77 | 86 | 565 | 64 | kW | 1.74
80 | 86 | 565 | 67 | MBh | 23.02
80 | 86 | 565 | 67 | S/T | 0.64
80 | 86 | 565 | 67 | ∆T | 24.2
80 | 86 | 565 | 67 | LDB | 55.8
80 | 86 | 565 | 67 | LWB | 53.7
80 | 86 | 565 | 67 | kW | 1.75
86 | 86 | 565 | 72 | MBh | 24.34
86 | 86 | 565 | 72 | S/T | 0.611
86 | 86 | 565 | 72 | ∆T | 24.4
86 | 86 | 565 | 72 | LDB | 61.6
86 | 86 | 565 | 72 | LWB | 59.5
86 | 86 | 565 | 72 | kW | 1.76
90 | 86 | 565 | 75 | MBh | 25.36
90 | 86 | 565 | 75 | S/T | 0.57
90 | 86 | 565 | 75 | ∆T | 23.7
90 | 86 | 565 | 75 | LDB | 66.3
90 | 86 | 565 | 75 | LWB | 62.9
90 | 86 | 565 | 75 | kW | 1.77
68 | 95 | 565 | 57 | MBh | 19.26
68 | 95 | 565 | 57 | S/T | 0.715
68 | 95 | 565 | 57 | ∆T | 22.6
68 | 95 | 565 | 57 | LDB | 45.4
68 | 95 | 565 | 57 | LWB | 43.4
68 | 95 | 565 | 57 | kW | 1.87
72 | 95 | 565 | 61 | MBh | 20.28
72 | 95 | 565 | 61 | S/T | 0.671
72 | 95 | 565 | 61 | ∆T | 22.3
72 | 95 | 565 | 61 | LDB | 49.7
72 | 95 | 565 | 61 | LWB | 47.8
72 | 95 | 565 | 61 | kW | 1.88
77 | 95 | 565 | 64 | MBh | 21.29
77 | 95 | 565 | 64 | S/T | 0.668
77 | 95 | 565 | 64 | ∆T | 23.3
77 | 95 | 565 | 64 | LDB | 53.7
77 | 95 | 565 | 64 | LWB | 50.9
77 | 95 | 565 | 64 | kW | 1.88
80 | 95 | 565 | 67 | MBh | 22
80 | 95 | 565 | 67 | S/T | 0.649
80 | 95 | 565 | 67 | ∆T | 23.4
80 | 95 | 565 | 67 | LDB | 56.6
80 | 95 | 565 | 67 | LWB | 54.4
80 | 95 | 565 | 67 | kW | 1.89
86 | 95 | 565 | 72 | MBh | 23.32
86 | 95 | 565 | 72 | S/T | 0.62
86 | 95 | 565 | 72 | ∆T | 23.7
86 | 95 | 565 | 72 | LDB | 62.3
86 | 95 | 565 | 72 | LWB | 60.1
86 | 95 | 565 | 72 | kW | 1.9
90 | 95 | 565 | 75 | MBh | 24.33
90 | 95 | 565 | 75 | S/T | 0.579
90 | 95 | 565 | 75 | ∆T | 23.1
90 | 95 | 565 | 75 | LDB | 66.9
90 | 95 | 565 | 75 | LWB | 63.4
90 | 95 | 565 | 75 | kW | 1.91
68 | 104 | 565 | 57 | MBh | 18.24
68 | 104 | 565 | 57 | S/T | 0.726
68 | 104 | 565 | 57 | ∆T | 21.7
68 | 104 | 565 | 57 | LDB | 46.3
68 | 104 | 565 | 57 | LWB | 44.2
68 | 104 | 565 | 57 | kW | 2.01
72 | 104 | 565 | 61 | MBh | 19.25
72 | 104 | 565 | 61 | S/T | 0.681
72 | 104 | 565 | 61 | ∆T | 21.5
72 | 104 | 565 | 61 | LDB | 50.5
72 | 104 | 565 | 61 | LWB | 48.5
72 | 104 | 565 | 61 | kW | 2.02
77 | 104 | 565 | 64 | MBh | 20.27
77 | 104 | 565 | 64 | S/T | 0.679
77 | 104 | 565 | 64 | ∆T | 22.5
77 | 104 | 565 | 64 | LDB | 54.5
77 | 104 | 565 | 64 | LWB | 51.6
77 | 104 | 565 | 64 | kW | 2.02
80 | 104 | 565 | 67 | MBh | 20.98
80 | 104 | 565 | 67 | S/T | 0.66
80 | 104 | 565 | 67 | ∆T | 22.7
80 | 104 | 565 | 67 | LDB | 57.3
80 | 104 | 565 | 67 | LWB | 55
80 | 104 | 565 | 67 | kW | 2.03
86 | 104 | 565 | 72 | MBh | 22.29
86 | 104 | 565 | 72 | S/T | 0.63
86 | 104 | 565 | 72 | ∆T | 23
86 | 104 | 565 | 72 | LDB | 63
86 | 104 | 565 | 72 | LWB | 60.7
86 | 104 | 565 | 72 | kW | 2.04
90 | 104 | 565 | 75 | MBh | 23.31
90 | 104 | 565 | 75 | S/T | 0.589
90 | 104 | 565 | 75 | ∆T | 22.5
90 | 104 | 565 | 75 | LDB | 67.5
90 | 104 | 565 | 75 | LWB | 64
90 | 104 | 565 | 75 | kW | 2.05
68 | 115 | 565 | 57 | MBh | 17.01
68 | 115 | 565 | 57 | S/T | 0.742
68 | 115 | 565 | 57 | ∆T | 20.7
68 | 115 | 565 | 57 | LDB | 47.3
68 | 115 | 565 | 57 | LWB | 45.1
68 | 115 | 565 | 57 | kW | 2.17
72 | 115 | 565 | 61 | MBh | 18.02
72 | 115 | 565 | 61 | S/T | 0.694
72 | 115 | 565 | 61 | ∆T | 20.5
72 | 115 | 565 | 61 | LDB | 51.5
72 | 115 | 565 | 61 | LWB | 49.4
72 | 115 | 565 | 61 | kW | 2.18
77 | 115 | 565 | 64 | MBh | 19.04
77 | 115 | 565 | 64 | S/T | 0.693
77 | 115 | 565 | 64 | ∆T | 21.6
77 | 115 | 565 | 64 | LDB | 55.4
77 | 115 | 565 | 64 | LWB | 52.5
77 | 115 | 565 | 64 | kW | 2.19
80 | 115 | 565 | 67 | MBh | 19.75
80 | 115 | 565 | 67 | S/T | 0.674
80 | 115 | 565 | 67 | ∆T | 21.8
80 | 115 | 565 | 67 | LDB | 58.2
80 | 115 | 565 | 67 | LWB | 55.8
80 | 115 | 565 | 67 | kW | 2.2
86 | 115 | 565 | 72 | MBh | 21.06
86 | 115 | 565 | 72 | S/T | 0.645
86 | 115 | 565 | 72 | ∆T | 22.3
86 | 115 | 565 | 72 | LDB | 63.7
86 | 115 | 565 | 72 | LWB | 61.4
86 | 115 | 565 | 72 | kW | 2.21
90 | 115 | 565 | 75 | MBh | 22.08
90 | 115 | 565 | 75 | S/T | 0.601
90 | 115 | 565 | 75 | ∆T | 21.8
90 | 115 | 565 | 75 | LDB | 68.2
90 | 115 | 565 | 75 | LWB | 64.6
90 | 115 | 565 | 75 | kW | 2.22

## RXT24AVJU9 - FTXV24AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 629 | 57 | MBh | 22.18 | 75 | 60 | 59 | 39.97 | 3.8
68 | 50 | 629 | 57 | S/T | 0.704 | 75 | 60 | 70 | 38.87 | 3.88
68 | 50 | 629 | 57 | ∆T | 23 | 75 | 60 | 72 | 38.42 | 3.91
68 | 50 | 629 | 57 | LDB | 45 | 75 | 60 | 75 | 37.58 | 3.86
68 | 50 | 629 | 57 | LWB | 42.8 | 75 | 60 | 77 | 36.32 | 3.67
68 | 50 | 629 | 57 | kW | 0.99 | 75 | 60 | 81 | 33.82 | 3.3
72 | 50 | 629 | 61 | MBh | 27.24 | 47 | 43 | 59 | 33.1 | 3.52
72 | 50 | 629 | 61 | S/T | 0.641 | 47 | 43 | 70 | 32 | 3.6
72 | 50 | 629 | 61 | ∆T | 25.7 | 47 | 43 | 72 | 31.56 | 3.63
72 | 50 | 629 | 61 | LDB | 46.3 | 47 | 43 | 75 | 31.12 | 3.66
72 | 50 | 629 | 61 | LWB | 44.6 | 47 | 43 | 77 | 30.9 | 3.68
72 | 50 | 629 | 61 | kW | 1.29 | 47 | 43 | 81 | 30.45 | 3.71
77 | 50 | 629 | 64 | MBh | 31.69 | 35 | 32 | 59 | 30.9 | 3.6
77 | 50 | 629 | 64 | S/T | 0.621 | 35 | 32 | 70 | 29.71 | 3.69
77 | 50 | 629 | 64 | ∆T | 29 | 35 | 32 | 72 | 29.24 | 3.72
77 | 50 | 629 | 64 | LDB | 48 | 35 | 32 | 75 | 28.77 | 3.76
77 | 50 | 629 | 64 | LWB | 45.7 | 35 | 32 | 77 | 28.53 | 3.78
77 | 50 | 629 | 64 | kW | 1.56 | 35 | 32 | 81 | 28.05 | 3.81
80 | 50 | 629 | 67 | MBh | 32.55 | 25 | 23 | 59 | 29.09 | 3.67
80 | 50 | 629 | 67 | S/T | 0.601 | 25 | 23 | 70 | 27.81 | 3.76
80 | 50 | 629 | 67 | ∆T | 28.8 | 25 | 23 | 72 | 27.3 | 3.8
80 | 50 | 629 | 67 | LDB | 51.2 | 25 | 23 | 75 | 26.79 | 3.84
80 | 50 | 629 | 67 | LWB | 49.4 | 25 | 23 | 77 | 26.53 | 3.85
80 | 50 | 629 | 67 | kW | 1.57 | 25 | 23 | 81 | 26.02 | 3.89
86 | 50 | 629 | 72 | MBh | 34.13 | 16 | 14 | 59 | 27.3 | 3.74
86 | 50 | 629 | 72 | S/T | 0.569 | 16 | 14 | 70 | 25.9 | 3.83
86 | 50 | 629 | 72 | ∆T | 28.6 | 16 | 14 | 72 | 25.34 | 3.87
86 | 50 | 629 | 72 | LDB | 57.4 | 16 | 14 | 75 | 24.78 | 3.91
86 | 50 | 629 | 72 | LWB | 55.6 | 16 | 14 | 77 | 24.5 | 3.93
86 | 50 | 629 | 72 | kW | 1.58 | 16 | 14 | 81 | 23.95 | 3.96
90 | 50 | 629 | 75 | MBh | 35.34 | 5 | 5 | 59 | 25.58 | 3.8
90 | 50 | 629 | 75 | S/T | 0.531 | 5 | 5 | 70 | 24 | 3.91
90 | 50 | 629 | 75 | ∆T | 27.6 | 5 | 5 | 72 | 23.37 | 3.95
90 | 50 | 629 | 75 | LDB | 62.4 | 5 | 5 | 75 | 22.77 | 3.96
90 | 50 | 629 | 75 | LWB | 59.2 | 5 | 5 | 77 | 22.48 | 3.96
90 | 50 | 629 | 75 | kW | 1.59 | 5 | 5 | 81 | 21.92 | 3.96
68 | 68 | 629 | 57 | MBh | 22.18 | -4 | -4 | 59 | 22.11 | 3.42
68 | 68 | 629 | 57 | S/T | 0.704 | -4 | -4 | 70 | 20.4 | 3.52
68 | 68 | 629 | 57 | ∆T | 23 | -4 | -4 | 72 | 19.72 | 3.56
68 | 68 | 629 | 57 | LDB | 45 | -4 | -4 | 75 | 19.04 | 3.6
68 | 68 | 629 | 57 | LWB | 42.8 | -4 | -4 | 77 | 18.69 | 3.62
68 | 68 | 629 | 57 | kW | 1.37 | -4 | -4 | 81 | 16.7 | 3.17
72 | 68 | 629 | 61 | MBh | 27.24 | -13 | -13 | 59 | 18.73 | 3.03
72 | 68 | 629 | 61 | S/T | 0.641 | -13 | -13 | 70 | 16.8 | 3.13
72 | 68 | 629 | 61 | ∆T | 25.7 | -13 | -13 | 72 | 16.03 | 3.16
72 | 68 | 629 | 61 | LDB | 46.3 | -13 | -13 | 75 | 15.25 | 3.2
72 | 68 | 629 | 61 | LWB | 44.6 | -13 | -13 | 77 | 14.87 | 3.22
72 | 68 | 629 | 61 | kW | 1.82 | -13 | -13 | 81 | 12.53 | 2.65
77 | 68 | 629 | 64 | MBh | 29.24
77 | 68 | 629 | 64 | S/T | 0.629
77 | 68 | 629 | 64 | ∆T | 27.1
77 | 68 | 629 | 64 | LDB | 49.9
77 | 68 | 629 | 64 | LWB | 47.4
77 | 68 | 629 | 64 | kW | 1.93
80 | 68 | 629 | 67 | MBh | 30.09
80 | 68 | 629 | 67 | S/T | 0.61
80 | 68 | 629 | 67 | ∆T | 27
80 | 68 | 629 | 67 | LDB | 53
80 | 68 | 629 | 67 | LWB | 51
80 | 68 | 629 | 67 | kW | 1.94
86 | 68 | 629 | 72 | MBh | 31.67
86 | 68 | 629 | 72 | S/T | 0.579
86 | 68 | 629 | 72 | ∆T | 27
86 | 68 | 629 | 72 | LDB | 59
86 | 68 | 629 | 72 | LWB | 57
86 | 68 | 629 | 72 | kW | 1.95
90 | 68 | 629 | 75 | MBh | 32.89
90 | 68 | 629 | 75 | S/T | 0.54
90 | 68 | 629 | 75 | ∆T | 26.1
90 | 68 | 629 | 75 | LDB | 63.9
90 | 68 | 629 | 75 | LWB | 60.5
90 | 68 | 629 | 75 | kW | 1.96
68 | 86 | 629 | 57 | MBh | 22.18
68 | 86 | 629 | 57 | S/T | 0.704
68 | 86 | 629 | 57 | ∆T | 23
68 | 86 | 629 | 57 | LDB | 45
68 | 86 | 629 | 57 | LWB | 42.8
68 | 86 | 629 | 57 | kW | 1.9
72 | 86 | 629 | 61 | MBh | 25.56
72 | 86 | 629 | 61 | S/T | 0.648
72 | 86 | 629 | 61 | ∆T | 24.4
72 | 86 | 629 | 61 | LDB | 47.6
72 | 86 | 629 | 61 | LWB | 45.7
72 | 86 | 629 | 61 | kW | 2.29
77 | 86 | 629 | 64 | MBh | 26.78
77 | 86 | 629 | 64 | S/T | 0.642
77 | 86 | 629 | 64 | ∆T | 25.3
77 | 86 | 629 | 64 | LDB | 51.7
77 | 86 | 629 | 64 | LWB | 49
77 | 86 | 629 | 64 | kW | 2.3
80 | 86 | 629 | 67 | MBh | 27.63
80 | 86 | 629 | 67 | S/T | 0.622
80 | 86 | 629 | 67 | ∆T | 25.3
80 | 86 | 629 | 67 | LDB | 54.7
80 | 86 | 629 | 67 | LWB | 52.5
80 | 86 | 629 | 67 | kW | 2.31
86 | 86 | 629 | 72 | MBh | 29.21
86 | 86 | 629 | 72 | S/T | 0.591
86 | 86 | 629 | 72 | ∆T | 25.4
86 | 86 | 629 | 72 | LDB | 60.6
86 | 86 | 629 | 72 | LWB | 58.4
86 | 86 | 629 | 72 | kW | 2.32
90 | 86 | 629 | 75 | MBh | 30.43
90 | 86 | 629 | 75 | S/T | 0.551
90 | 86 | 629 | 75 | ∆T | 24.7
90 | 86 | 629 | 75 | LDB | 65.3
90 | 86 | 629 | 75 | LWB | 61.8
90 | 86 | 629 | 75 | kW | 2.33
68 | 95 | 629 | 57 | MBh | 22.18
68 | 95 | 629 | 57 | S/T | 0.704
68 | 95 | 629 | 57 | ∆T | 23
68 | 95 | 629 | 57 | LDB | 45
68 | 95 | 629 | 57 | LWB | 42.8
68 | 95 | 629 | 57 | kW | 2.26
72 | 95 | 629 | 61 | MBh | 24.33
72 | 95 | 629 | 61 | S/T | 0.655
72 | 95 | 629 | 61 | ∆T | 23.4
72 | 95 | 629 | 61 | LDB | 48.6
72 | 95 | 629 | 61 | LWB | 46.6
72 | 95 | 629 | 61 | kW | 2.47
77 | 95 | 629 | 64 | MBh | 25.55
77 | 95 | 629 | 64 | S/T | 0.649
77 | 95 | 629 | 64 | ∆T | 24.4
77 | 95 | 629 | 64 | LDB | 52.6
77 | 95 | 629 | 64 | LWB | 49.8
77 | 95 | 629 | 64 | kW | 2.48
80 | 95 | 629 | 67 | MBh | 26.4
80 | 95 | 629 | 67 | S/T | 0.63
80 | 95 | 629 | 67 | ∆T | 24.5
80 | 95 | 629 | 67 | LDB | 55.5
80 | 95 | 629 | 67 | LWB | 53.3
80 | 95 | 629 | 67 | kW | 2.49
86 | 95 | 629 | 72 | MBh | 27.98
86 | 95 | 629 | 72 | S/T | 0.599
86 | 95 | 629 | 72 | ∆T | 24.7
86 | 95 | 629 | 72 | LDB | 61.3
86 | 95 | 629 | 72 | LWB | 59
86 | 95 | 629 | 72 | kW | 2.5
90 | 95 | 629 | 75 | MBh | 29.2
90 | 95 | 629 | 75 | S/T | 0.559
90 | 95 | 629 | 75 | ∆T | 24
90 | 95 | 629 | 75 | LDB | 66
90 | 95 | 629 | 75 | LWB | 62.4
90 | 95 | 629 | 75 | kW | 2.52
68 | 104 | 629 | 57 | MBh | 21.89
68 | 104 | 629 | 57 | S/T | 0.706
68 | 104 | 629 | 57 | ∆T | 22.8
68 | 104 | 629 | 57 | LDB | 45.2
68 | 104 | 629 | 57 | LWB | 43
68 | 104 | 629 | 57 | kW | 2.64
72 | 104 | 629 | 61 | MBh | 23.1
72 | 104 | 629 | 61 | S/T | 0.663
72 | 104 | 629 | 61 | ∆T | 22.5
72 | 104 | 629 | 61 | LDB | 49.5
72 | 104 | 629 | 61 | LWB | 47.4
72 | 104 | 629 | 61 | kW | 2.66
77 | 104 | 629 | 64 | MBh | 24.32
77 | 104 | 629 | 64 | S/T | 0.658
77 | 104 | 629 | 64 | ∆T | 23.6
77 | 104 | 629 | 64 | LDB | 53.4
77 | 104 | 629 | 64 | LWB | 50.6
77 | 104 | 629 | 64 | kW | 2.67
80 | 104 | 629 | 67 | MBh | 25.17
80 | 104 | 629 | 67 | S/T | 0.638
80 | 104 | 629 | 67 | ∆T | 23.7
80 | 104 | 629 | 67 | LDB | 56.3
80 | 104 | 629 | 67 | LWB | 54
80 | 104 | 629 | 67 | kW | 2.67
86 | 104 | 629 | 72 | MBh | 26.75
86 | 104 | 629 | 72 | S/T | 0.608
86 | 104 | 629 | 72 | ∆T | 23.9
86 | 104 | 629 | 72 | LDB | 62.1
86 | 104 | 629 | 72 | LWB | 59.7
86 | 104 | 629 | 72 | kW | 2.69
90 | 104 | 629 | 75 | MBh | 27.97
90 | 104 | 629 | 75 | S/T | 0.567
90 | 104 | 629 | 75 | ∆T | 23.3
90 | 104 | 629 | 75 | LDB | 66.7
90 | 104 | 629 | 75 | LWB | 63
90 | 104 | 629 | 75 | kW | 2.7
68 | 115 | 629 | 57 | MBh | 20.41
68 | 115 | 629 | 57 | S/T | 0.72
68 | 115 | 629 | 57 | ∆T | 21.6
68 | 115 | 629 | 57 | LDB | 46.4
68 | 115 | 629 | 57 | LWB | 44.1
68 | 115 | 629 | 57 | kW | 2.59
72 | 115 | 629 | 61 | MBh | 21.63
72 | 115 | 629 | 61 | S/T | 0.674
72 | 115 | 629 | 61 | ∆T | 21.4
72 | 115 | 629 | 61 | LDB | 50.6
72 | 115 | 629 | 61 | LWB | 48.4
72 | 115 | 629 | 61 | kW | 2.59
77 | 115 | 629 | 64 | MBh | 22.84
77 | 115 | 629 | 64 | S/T | 0.67
77 | 115 | 629 | 64 | ∆T | 22.5
77 | 115 | 629 | 64 | LDB | 54.5
77 | 115 | 629 | 64 | LWB | 51.5
77 | 115 | 629 | 64 | kW | 2.59
80 | 115 | 629 | 67 | MBh | 23.7
80 | 115 | 629 | 67 | S/T | 0.65
80 | 115 | 629 | 67 | ∆T | 22.7
80 | 115 | 629 | 67 | LDB | 57.3
80 | 115 | 629 | 67 | LWB | 54.8
80 | 115 | 629 | 67 | kW | 2.59
86 | 115 | 629 | 72 | MBh | 25.28
86 | 115 | 629 | 72 | S/T | 0.62
86 | 115 | 629 | 72 | ∆T | 23.1
86 | 115 | 629 | 72 | LDB | 62.9
86 | 115 | 629 | 72 | LWB | 60.4
86 | 115 | 629 | 72 | kW | 2.59
90 | 115 | 629 | 75 | MBh | 26.49
90 | 115 | 629 | 75 | S/T | 0.578
90 | 115 | 629 | 75 | ∆T | 22.5
90 | 115 | 629 | 75 | LDB | 67.5
90 | 115 | 629 | 75 | LWB | 63.7
90 | 115 | 629 | 75 | kW | 2.59

## RXC09BVJU9 - FTXC09BVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 406 | 57 | MBh | 11.64 | 75 | 64 | 59 | 14.71 | 1.14
68 | 50 | 406 | 57 | S/T | 0.798 | 75 | 64 | 70 | 14.24 | 1.16
68 | 50 | 406 | 57 | ∆T | 21.2 | 75 | 64 | 72 | 14.17 | 1.17
68 | 50 | 406 | 57 | LDB | 46.8 | 75 | 64 | 75 | 14.01 | 1.18
68 | 50 | 406 | 57 | LWB | 45.8 | 75 | 64 | 77 | 13.93 | 1.18
68 | 50 | 406 | 57 | kW | 0.69 | 75 | 64 | 81 | 13.78 | 1.19
72 | 50 | 406 | 61 | MBh | 12.12 | 59 | 50 | 59 | 12.68 | 1.07
72 | 50 | 406 | 61 | S/T | 0.752 | 59 | 50 | 70 | 12.21 | 1.09
72 | 50 | 406 | 61 | ∆T | 20.8 | 59 | 50 | 72 | 12.14 | 1.1
72 | 50 | 406 | 61 | LDB | 51.2 | 59 | 50 | 75 | 11.99 | 1.11
72 | 50 | 406 | 61 | LWB | 50.2 | 59 | 50 | 77 | 11.91 | 1.11
72 | 50 | 406 | 61 | kW | 0.69 | 59 | 50 | 81 | 11.76 | 1.12
77 | 50 | 406 | 64 | MBh | 12.61 | 47 | 43 | 59 | 11.67 | 1.03
77 | 50 | 406 | 64 | S/T | 0.764 | 47 | 43 | 70 | 11.2 | 1.06
77 | 50 | 406 | 64 | ∆T | 22 | 47 | 43 | 72 | 11.13 | 1.06
77 | 50 | 406 | 64 | LDB | 55 | 47 | 43 | 75 | 10.98 | 1.07
77 | 50 | 406 | 64 | LWB | 53.5 | 47 | 43 | 77 | 10.9 | 1.08
77 | 50 | 406 | 64 | kW | 0.7 | 47 | 43 | 81 | 10.74 | 1.09
80 | 50 | 406 | 67 | MBh | 12.94 | 35 | 32 | 59 | 9.14 | 0.91
80 | 50 | 406 | 67 | S/T | 0.75 | 35 | 32 | 70 | 8.71 | 0.94
80 | 50 | 406 | 67 | ∆T | 22.1 | 35 | 32 | 72 | 8.65 | 0.94
80 | 50 | 406 | 67 | LDB | 57.9 | 35 | 32 | 75 | 8.51 | 0.95
80 | 50 | 406 | 67 | LWB | 56.9 | 35 | 32 | 77 | 8.44 | 0.95
80 | 50 | 406 | 67 | kW | 0.7 | 35 | 32 | 81 | 8.3 | 0.96
86 | 50 | 406 | 72 | MBh | 13.57 | 25 | 23 | 59 | 8 | 0.87
86 | 50 | 406 | 72 | S/T | 0.73 | 25 | 23 | 70 | 7.58 | 0.9
86 | 50 | 406 | 72 | ∆T | 22.6 | 25 | 23 | 72 | 7.51 | 0.9
86 | 50 | 406 | 72 | LDB | 63.4 | 25 | 23 | 75 | 7.37 | 0.91
86 | 50 | 406 | 72 | LWB | 62.6 | 25 | 23 | 77 | 7.3 | 0.91
86 | 50 | 406 | 72 | kW | 0.79 | 25 | 23 | 81 | 7.17 | 0.92
90 | 50 | 406 | 75 | MBh | 14.06 | 16 | 14 | 59 | 6.86 | 0.83
90 | 50 | 406 | 75 | S/T | 0.687 | 16 | 14 | 70 | 6.44 | 0.86
90 | 50 | 406 | 75 | ∆T | 22 | 16 | 14 | 72 | 6.38 | 0.86
90 | 50 | 406 | 75 | LDB | 68 | 16 | 14 | 75 | 6.24 | 0.87
90 | 50 | 406 | 75 | LWB | 65.9 | 16 | 14 | 77 | 6.17 | 0.87
90 | 50 | 406 | 75 | kW | 0.79 | 16 | 14 | 81 | 6.03 | 0.88
68 | 68 | 406 | 57 | MBh | 10.66 | 5 | 5 | 59 | 6.27 | 0.76
68 | 68 | 406 | 57 | S/T | 0.828 | 5 | 5 | 70 | 5.8 | 0.79
68 | 68 | 406 | 57 | ∆T | 20.1 | 5 | 5 | 72 | 5.73 | 0.79
68 | 68 | 406 | 57 | LDB | 47.9 | 5 | 5 | 75 | 5.58 | 0.8
68 | 68 | 406 | 57 | LWB | 46.8 | 5 | 5 | 77 | 5.5 | 0.81
68 | 68 | 406 | 57 | kW | 0.85 | 5 | 5 | 81 | 5.35 | 0.81
72 | 68 | 406 | 61 | MBh | 11.14
72 | 68 | 406 | 61 | S/T | 0.779
72 | 68 | 406 | 61 | ∆T | 19.8
72 | 68 | 406 | 61 | LDB | 52.2
72 | 68 | 406 | 61 | LWB | 51.2
72 | 68 | 406 | 61 | kW | 0.86
77 | 68 | 406 | 64 | MBh | 11.63
77 | 68 | 406 | 64 | S/T | 0.794
77 | 68 | 406 | 64 | ∆T | 21
77 | 68 | 406 | 64 | LDB | 56
77 | 68 | 406 | 64 | LWB | 54.4
77 | 68 | 406 | 64 | kW | 0.86
80 | 68 | 406 | 67 | MBh | 11.97
80 | 68 | 406 | 67 | S/T | 0.778
80 | 68 | 406 | 67 | ∆T | 21.2
80 | 68 | 406 | 67 | LDB | 58.8
80 | 68 | 406 | 67 | LWB | 57.7
80 | 68 | 406 | 67 | kW | 0.86
86 | 68 | 406 | 72 | MBh | 12.6
86 | 68 | 406 | 72 | S/T | 0.758
86 | 68 | 406 | 72 | ∆T | 21.8
86 | 68 | 406 | 72 | LDB | 64.2
86 | 68 | 406 | 72 | LWB | 63.3
86 | 68 | 406 | 72 | kW | 0.87
90 | 68 | 406 | 75 | MBh | 13.08
90 | 68 | 406 | 75 | S/T | 0.715
90 | 68 | 406 | 75 | ∆T | 21.3
90 | 68 | 406 | 75 | LDB | 68.7
90 | 68 | 406 | 75 | LWB | 66.6
90 | 68 | 406 | 75 | kW | 0.88
68 | 86 | 406 | 57 | MBh | 9.68
68 | 86 | 406 | 57 | S/T | 0.865
68 | 86 | 406 | 57 | ∆T | 19.1
68 | 86 | 406 | 57 | LDB | 48.9
68 | 86 | 406 | 57 | LWB | 47.8
68 | 86 | 406 | 57 | kW | 1.01
72 | 86 | 406 | 61 | MBh | 10.17
72 | 86 | 406 | 61 | S/T | 0.812
72 | 86 | 406 | 61 | ∆T | 18.8
72 | 86 | 406 | 61 | LDB | 53.2
72 | 86 | 406 | 61 | LWB | 52.1
72 | 86 | 406 | 61 | kW | 1.02
77 | 86 | 406 | 64 | MBh | 10.65
77 | 86 | 406 | 64 | S/T | 0.83
77 | 86 | 406 | 64 | ∆T | 20.2
77 | 86 | 406 | 64 | LDB | 56.8
77 | 86 | 406 | 64 | LWB | 55.3
77 | 86 | 406 | 64 | kW | 1.02
80 | 86 | 406 | 67 | MBh | 10.99
80 | 86 | 406 | 67 | S/T | 0.813
80 | 86 | 406 | 67 | ∆T | 20.4
80 | 86 | 406 | 67 | LDB | 59.6
80 | 86 | 406 | 67 | LWB | 58.6
80 | 86 | 406 | 67 | kW | 1.03
86 | 86 | 406 | 72 | MBh | 11.62
86 | 86 | 406 | 72 | S/T | 0.793
86 | 86 | 406 | 72 | ∆T | 21
86 | 86 | 406 | 72 | LDB | 65
86 | 86 | 406 | 72 | LWB | 64
86 | 86 | 406 | 72 | kW | 1.03
90 | 86 | 406 | 75 | MBh | 12.1
90 | 86 | 406 | 75 | S/T | 0.747
90 | 86 | 406 | 75 | ∆T | 20.6
90 | 86 | 406 | 75 | LDB | 69.4
90 | 86 | 406 | 75 | LWB | 67.3
90 | 86 | 406 | 75 | kW | 1.04
68 | 95 | 406 | 57 | MBh | 9.19
68 | 95 | 406 | 57 | S/T | 0.887
68 | 95 | 406 | 57 | ∆T | 18.6
68 | 95 | 406 | 57 | LDB | 49.4
68 | 95 | 406 | 57 | LWB | 48.3
68 | 95 | 406 | 57 | kW | 1.1
72 | 95 | 406 | 61 | MBh | 9.68
72 | 95 | 406 | 61 | S/T | 0.832
72 | 95 | 406 | 61 | ∆T | 18.4
72 | 95 | 406 | 61 | LDB | 53.6
72 | 95 | 406 | 61 | LWB | 52.6
72 | 95 | 406 | 61 | kW | 1.1
77 | 95 | 406 | 64 | MBh | 10.16
77 | 95 | 406 | 64 | S/T | 0.85
77 | 95 | 406 | 64 | ∆T | 19.7
77 | 95 | 406 | 64 | LDB | 57.3
77 | 95 | 406 | 64 | LWB | 55.7
77 | 95 | 406 | 64 | kW | 1.11
80 | 95 | 406 | 67 | MBh | 10.5
80 | 95 | 406 | 67 | S/T | 0.834
80 | 95 | 406 | 67 | ∆T | 20
80 | 95 | 406 | 67 | LDB | 60
80 | 95 | 406 | 67 | LWB | 59
80 | 95 | 406 | 67 | kW | 1.11
86 | 95 | 406 | 72 | MBh | 11.13
86 | 95 | 406 | 72 | S/T | 0.813
86 | 95 | 406 | 72 | ∆T | 20.6
86 | 95 | 406 | 72 | LDB | 65.4
86 | 95 | 406 | 72 | LWB | 64.4
86 | 95 | 406 | 72 | kW | 1.12
90 | 95 | 406 | 75 | MBh | 11.61
90 | 95 | 406 | 75 | S/T | 0.766
90 | 95 | 406 | 75 | ∆T | 20.3
90 | 95 | 406 | 75 | LDB | 69.7
90 | 95 | 406 | 75 | LWB | 67.6
90 | 95 | 406 | 75 | kW | 1.12
68 | 104 | 406 | 57 | MBh | 8.7
68 | 104 | 406 | 57 | S/T | 0.911
68 | 104 | 406 | 57 | ∆T | 18.1
68 | 104 | 406 | 57 | LDB | 49.9
68 | 104 | 406 | 57 | LWB | 48.8
68 | 104 | 406 | 57 | kW | 1.18
72 | 104 | 406 | 61 | MBh | 9.19
72 | 104 | 406 | 61 | S/T | 0.853
72 | 104 | 406 | 61 | ∆T | 17.9
72 | 104 | 406 | 61 | LDB | 54.1
72 | 104 | 406 | 61 | LWB | 53
72 | 104 | 406 | 61 | kW | 1.18
77 | 104 | 406 | 64 | MBh | 9.67
77 | 104 | 406 | 64 | S/T | 0.874
77 | 104 | 406 | 64 | ∆T | 19.3
77 | 104 | 406 | 64 | LDB | 57.7
77 | 104 | 406 | 64 | LWB | 56.1
77 | 104 | 406 | 64 | kW | 1.19
80 | 104 | 406 | 67 | MBh | 10.01
80 | 104 | 406 | 67 | S/T | 0.856
80 | 104 | 406 | 67 | ∆T | 19.5
80 | 104 | 406 | 67 | LDB | 60.5
80 | 104 | 406 | 67 | LWB | 59.4
80 | 104 | 406 | 67 | kW | 1.19
86 | 104 | 406 | 72 | MBh | 10.64
86 | 104 | 406 | 72 | S/T | 0.836
86 | 104 | 406 | 72 | ∆T | 20.3
86 | 104 | 406 | 72 | LDB | 65.7
86 | 104 | 406 | 72 | LWB | 64.7
86 | 104 | 406 | 72 | kW | 1.2
90 | 104 | 406 | 75 | MBh | 11.12
90 | 104 | 406 | 75 | S/T | 0.786
90 | 104 | 406 | 75 | ∆T | 19.9
90 | 104 | 406 | 75 | LDB | 70.1
90 | 104 | 406 | 75 | LWB | 67.9
90 | 104 | 406 | 75 | kW | 1.2
68 | 115 | 406 | 57 | MBh | 7.52
68 | 115 | 406 | 57 | S/T | 0.984
68 | 115 | 406 | 57 | ∆T | 16.9
68 | 115 | 406 | 57 | LDB | 51.1
68 | 115 | 406 | 57 | LWB | 50
68 | 115 | 406 | 57 | kW | 1.07
72 | 115 | 406 | 61 | MBh | 7.99
72 | 115 | 406 | 61 | S/T | 0.919
72 | 115 | 406 | 61 | ∆T | 16.7
72 | 115 | 406 | 61 | LDB | 55.3
72 | 115 | 406 | 61 | LWB | 54.1
72 | 115 | 406 | 61 | kW | 1.07
77 | 115 | 406 | 64 | MBh | 8.46
77 | 115 | 406 | 64 | S/T | 0.943
77 | 115 | 406 | 64 | ∆T | 18.2
77 | 115 | 406 | 64 | LDB | 58.8
77 | 115 | 406 | 64 | LWB | 57.2
77 | 115 | 406 | 64 | kW | 1.07
80 | 115 | 406 | 67 | MBh | 8.79
80 | 115 | 406 | 67 | S/T | 0.924
80 | 115 | 406 | 67 | ∆T | 18.5
80 | 115 | 406 | 67 | LDB | 61.5
80 | 115 | 406 | 67 | LWB | 60.3
80 | 115 | 406 | 67 | kW | 1.07
86 | 115 | 406 | 72 | MBh | 9.4
86 | 115 | 406 | 72 | S/T | 0.902
86 | 115 | 406 | 72 | ∆T | 19.3
86 | 115 | 406 | 72 | LDB | 66.7
86 | 115 | 406 | 72 | LWB | 65.6
86 | 115 | 406 | 72 | kW | 1.07
90 | 115 | 406 | 75 | MBh | 9.87
90 | 115 | 406 | 75 | S/T | 0.847
90 | 115 | 406 | 75 | ∆T | 19.1
90 | 115 | 406 | 75 | LDB | 70.9
90 | 115 | 406 | 75 | LWB | 68.8
90 | 115 | 406 | 75 | kW | 1.07

## RXC12BVJU9 - FTXC12BVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 434 | 57 | MBh | 13.19 | 75 | 64 | 59 | 16.81 | 1.19
68 | 50 | 434 | 57 | S/T | 0.776 | 75 | 64 | 70 | 16.27 | 1.22
68 | 50 | 434 | 57 | ∆T | 21.8 | 75 | 64 | 72 | 16.19 | 1.22
68 | 50 | 434 | 57 | LDB | 46.2 | 75 | 64 | 75 | 16.01 | 1.23
68 | 50 | 434 | 57 | LWB | 45 | 75 | 64 | 77 | 15.92 | 1.24
68 | 50 | 434 | 57 | kW | 0.85 | 75 | 64 | 81 | 15.75 | 1.25
72 | 50 | 434 | 61 | MBh | 13.74 | 59 | 50 | 59 | 14.5 | 1.12
72 | 50 | 434 | 61 | S/T | 0.73 | 59 | 50 | 70 | 13.96 | 1.15
72 | 50 | 434 | 61 | ∆T | 21.4 | 59 | 50 | 72 | 13.88 | 1.15
72 | 50 | 434 | 61 | LDB | 50.6 | 59 | 50 | 75 | 13.7 | 1.16
72 | 50 | 434 | 61 | LWB | 49.5 | 59 | 50 | 77 | 13.61 | 1.17
72 | 50 | 434 | 61 | kW | 0.85 | 59 | 50 | 81 | 13.43 | 1.18
77 | 50 | 434 | 64 | MBh | 14.29 | 47 | 43 | 59 | 13.34 | 1.08
77 | 50 | 434 | 64 | S/T | 0.739 | 47 | 43 | 70 | 12.8 | 1.11
77 | 50 | 434 | 64 | ∆T | 22.5 | 47 | 43 | 72 | 12.72 | 1.11
77 | 50 | 434 | 64 | LDB | 54.5 | 47 | 43 | 75 | 12.54 | 1.12
77 | 50 | 434 | 64 | LWB | 52.8 | 47 | 43 | 77 | 12.46 | 1.13
77 | 50 | 434 | 64 | kW | 0.86 | 47 | 43 | 81 | 12.28 | 1.14
80 | 50 | 434 | 67 | MBh | 14.67 | 35 | 32 | 59 | 10.44 | 0.99
80 | 50 | 434 | 67 | S/T | 0.723 | 35 | 32 | 70 | 9.96 | 1.02
80 | 50 | 434 | 67 | ∆T | 22.6 | 35 | 32 | 72 | 9.89 | 1.03
80 | 50 | 434 | 67 | LDB | 57.4 | 35 | 32 | 75 | 9.73 | 1.04
80 | 50 | 434 | 67 | LWB | 56.2 | 35 | 32 | 77 | 9.65 | 1.04
80 | 50 | 434 | 67 | kW | 0.86 | 35 | 32 | 81 | 9.49 | 1.05
86 | 50 | 434 | 72 | MBh | 15.38 | 25 | 23 | 59 | 9.14 | 0.95
86 | 50 | 434 | 72 | S/T | 0.702 | 25 | 23 | 70 | 8.66 | 0.98
86 | 50 | 434 | 72 | ∆T | 23 | 25 | 23 | 72 | 8.59 | 0.98
86 | 50 | 434 | 72 | LDB | 63 | 25 | 23 | 75 | 8.43 | 0.99
86 | 50 | 434 | 72 | LWB | 61.9 | 25 | 23 | 77 | 8.35 | 1
86 | 50 | 434 | 72 | kW | 0.87 | 25 | 23 | 81 | 8.19 | 1.01
90 | 50 | 434 | 75 | MBh | 15.93 | 16 | 14 | 59 | 7.84 | 0.91
90 | 50 | 434 | 75 | S/T | 0.66 | 16 | 14 | 70 | 7.36 | 0.93
90 | 50 | 434 | 75 | ∆T | 22.4 | 16 | 14 | 72 | 7.29 | 0.94
90 | 50 | 434 | 75 | LDB | 67.6 | 16 | 14 | 75 | 7.13 | 0.95
90 | 50 | 434 | 75 | LWB | 65.3 | 16 | 14 | 77 | 7.05 | 0.95
90 | 50 | 434 | 75 | kW | 0.98 | 16 | 14 | 81 | 6.89 | 0.96
68 | 68 | 434 | 57 | MBh | 12.08 | 5 | 5 | 59 | 7.35 | 0.89
68 | 68 | 434 | 57 | S/T | 0.802 | 5 | 5 | 70 | 6.8 | 0.92
68 | 68 | 434 | 57 | ∆T | 20.7 | 5 | 5 | 72 | 6.72 | 0.92
68 | 68 | 434 | 57 | LDB | 47.3 | 5 | 5 | 75 | 6.54 | 0.93
68 | 68 | 434 | 57 | LWB | 46.1 | 5 | 5 | 77 | 6.45 | 0.94
68 | 68 | 434 | 57 | kW | 1.05 | 5 | 5 | 81 | 6.27 | 0.95
72 | 68 | 434 | 61 | MBh | 12.63
72 | 68 | 434 | 61 | S/T | 0.755
72 | 68 | 434 | 61 | ∆T | 20.3
72 | 68 | 434 | 61 | LDB | 51.7
72 | 68 | 434 | 61 | LWB | 50.5
72 | 68 | 434 | 61 | kW | 1.06
77 | 68 | 434 | 64 | MBh | 13.18
77 | 68 | 434 | 64 | S/T | 0.766
77 | 68 | 434 | 64 | ∆T | 21.5
77 | 68 | 434 | 64 | LDB | 55.5
77 | 68 | 434 | 64 | LWB | 53.7
77 | 68 | 434 | 64 | kW | 1.06
80 | 68 | 434 | 67 | MBh | 13.56
80 | 68 | 434 | 67 | S/T | 0.75
80 | 68 | 434 | 67 | ∆T | 21.7
80 | 68 | 434 | 67 | LDB | 58.3
80 | 68 | 434 | 67 | LWB | 57.1
80 | 68 | 434 | 67 | kW | 1.07
86 | 68 | 434 | 72 | MBh | 14.28
86 | 68 | 434 | 72 | S/T | 0.728
86 | 68 | 434 | 72 | ∆T | 22.2
86 | 68 | 434 | 72 | LDB | 63.8
86 | 68 | 434 | 72 | LWB | 62.7
86 | 68 | 434 | 72 | kW | 1.07
90 | 68 | 434 | 75 | MBh | 14.82
90 | 68 | 434 | 75 | S/T | 0.686
90 | 68 | 434 | 75 | ∆T | 21.7
90 | 68 | 434 | 75 | LDB | 68.3
90 | 68 | 434 | 75 | LWB | 66
90 | 68 | 434 | 75 | kW | 1.08
68 | 86 | 434 | 57 | MBh | 10.97
68 | 86 | 434 | 57 | S/T | 0.836
68 | 86 | 434 | 57 | ∆T | 19.6
68 | 86 | 434 | 57 | LDB | 48.4
68 | 86 | 434 | 57 | LWB | 47.2
68 | 86 | 434 | 57 | kW | 1.25
72 | 86 | 434 | 61 | MBh | 11.52
72 | 86 | 434 | 61 | S/T | 0.785
72 | 86 | 434 | 61 | ∆T | 19.3
72 | 86 | 434 | 61 | LDB | 52.7
72 | 86 | 434 | 61 | LWB | 51.5
72 | 86 | 434 | 61 | kW | 1.26
77 | 86 | 434 | 64 | MBh | 12.07
77 | 86 | 434 | 64 | S/T | 0.799
77 | 86 | 434 | 64 | ∆T | 20.6
77 | 86 | 434 | 64 | LDB | 56.4
77 | 86 | 434 | 64 | LWB | 54.7
77 | 86 | 434 | 64 | kW | 1.26
80 | 86 | 434 | 67 | MBh | 12.45
80 | 86 | 434 | 67 | S/T | 0.782
80 | 86 | 434 | 67 | ∆T | 20.8
80 | 86 | 434 | 67 | LDB | 59.2
80 | 86 | 434 | 67 | LWB | 58
80 | 86 | 434 | 67 | kW | 1.27
86 | 86 | 434 | 72 | MBh | 13.17
86 | 86 | 434 | 72 | S/T | 0.76
86 | 86 | 434 | 72 | ∆T | 21.4
86 | 86 | 434 | 72 | LDB | 64.6
86 | 86 | 434 | 72 | LWB | 63.5
86 | 86 | 434 | 72 | kW | 1.28
90 | 86 | 434 | 75 | MBh | 13.72
90 | 86 | 434 | 75 | S/T | 0.715
90 | 86 | 434 | 75 | ∆T | 20.9
90 | 86 | 434 | 75 | LDB | 69.1
90 | 86 | 434 | 75 | LWB | 66.8
90 | 86 | 434 | 75 | kW | 1.28
68 | 95 | 434 | 57 | MBh | 10.42
68 | 95 | 434 | 57 | S/T | 0.855
68 | 95 | 434 | 57 | ∆T | 19
68 | 95 | 434 | 57 | LDB | 49
68 | 95 | 434 | 57 | LWB | 47.7
68 | 95 | 434 | 57 | kW | 1.35
72 | 95 | 434 | 61 | MBh | 10.97
72 | 95 | 434 | 61 | S/T | 0.802
72 | 95 | 434 | 61 | ∆T | 18.8
72 | 95 | 434 | 61 | LDB | 53.2
72 | 95 | 434 | 61 | LWB | 52
72 | 95 | 434 | 61 | kW | 1.36
77 | 95 | 434 | 64 | MBh | 11.52
77 | 95 | 434 | 64 | S/T | 0.817
77 | 95 | 434 | 64 | ∆T | 20.1
77 | 95 | 434 | 64 | LDB | 56.9
77 | 95 | 434 | 64 | LWB | 55.1
77 | 95 | 434 | 64 | kW | 1.37
80 | 95 | 434 | 67 | MBh | 11.9
80 | 95 | 434 | 67 | S/T | 0.8
80 | 95 | 434 | 67 | ∆T | 20.3
80 | 95 | 434 | 67 | LDB | 59.7
80 | 95 | 434 | 67 | LWB | 58.4
80 | 95 | 434 | 67 | kW | 1.37
86 | 95 | 434 | 72 | MBh | 12.61
86 | 95 | 434 | 72 | S/T | 0.779
86 | 95 | 434 | 72 | ∆T | 21
86 | 95 | 434 | 72 | LDB | 65
86 | 95 | 434 | 72 | LWB | 63.9
86 | 95 | 434 | 72 | kW | 1.38
90 | 95 | 434 | 75 | MBh | 13.16
90 | 95 | 434 | 75 | S/T | 0.732
90 | 95 | 434 | 75 | ∆T | 20.5
90 | 95 | 434 | 75 | LDB | 69.5
90 | 95 | 434 | 75 | LWB | 67.1
90 | 95 | 434 | 75 | kW | 1.38
68 | 104 | 434 | 57 | MBh | 9.31
68 | 104 | 434 | 57 | S/T | 0.902
68 | 104 | 434 | 57 | ∆T | 17.9
68 | 104 | 434 | 57 | LDB | 50.1
68 | 104 | 434 | 57 | LWB | 48.8
68 | 104 | 434 | 57 | kW | 1.26
72 | 104 | 434 | 61 | MBh | 9.84
72 | 104 | 434 | 61 | S/T | 0.845
72 | 104 | 434 | 61 | ∆T | 17.7
72 | 104 | 434 | 61 | LDB | 54.3
72 | 104 | 434 | 61 | LWB | 53
72 | 104 | 434 | 61 | kW | 1.26
77 | 104 | 434 | 64 | MBh | 10.37
77 | 104 | 434 | 64 | S/T | 0.863
77 | 104 | 434 | 64 | ∆T | 19.1
77 | 104 | 434 | 64 | LDB | 57.9
77 | 104 | 434 | 64 | LWB | 56.1
77 | 104 | 434 | 64 | kW | 1.26
80 | 104 | 434 | 67 | MBh | 10.74
80 | 104 | 434 | 67 | S/T | 0.846
80 | 104 | 434 | 67 | ∆T | 19.4
80 | 104 | 434 | 67 | LDB | 60.6
80 | 104 | 434 | 67 | LWB | 59.3
80 | 104 | 434 | 67 | kW | 1.26
86 | 104 | 434 | 72 | MBh | 11.43
86 | 104 | 434 | 72 | S/T | 0.824
86 | 104 | 434 | 72 | ∆T | 20.1
86 | 104 | 434 | 72 | LDB | 65.9
86 | 104 | 434 | 72 | LWB | 64.7
86 | 104 | 434 | 72 | kW | 1.26
90 | 104 | 434 | 75 | MBh | 11.96
90 | 104 | 434 | 75 | S/T | 0.774
90 | 104 | 434 | 75 | ∆T | 19.8
90 | 104 | 434 | 75 | LDB | 70.2
90 | 104 | 434 | 75 | LWB | 67.9
90 | 104 | 434 | 75 | kW | 1.26
68 | 115 | 434 | 57 | MBh | 7.74
68 | 115 | 434 | 57 | S/T | 0.995
68 | 115 | 434 | 57 | ∆T | 16.4
68 | 115 | 434 | 57 | LDB | 51.6
68 | 115 | 434 | 57 | LWB | 50.2
68 | 115 | 434 | 57 | kW | 1.07
72 | 115 | 434 | 61 | MBh | 8.27
72 | 115 | 434 | 61 | S/T | 0.926
72 | 115 | 434 | 61 | ∆T | 16.3
72 | 115 | 434 | 61 | LDB | 55.7
72 | 115 | 434 | 61 | LWB | 54.4
72 | 115 | 434 | 61 | kW | 1.07
77 | 115 | 434 | 64 | MBh | 8.8
77 | 115 | 434 | 64 | S/T | 0.948
77 | 115 | 434 | 64 | ∆T | 17.8
77 | 115 | 434 | 64 | LDB | 59.2
77 | 115 | 434 | 64 | LWB | 57.4
77 | 115 | 434 | 64 | kW | 1.07
80 | 115 | 434 | 67 | MBh | 9.17
80 | 115 | 434 | 67 | S/T | 0.928
80 | 115 | 434 | 67 | ∆T | 18.2
80 | 115 | 434 | 67 | LDB | 61.8
80 | 115 | 434 | 67 | LWB | 60.5
80 | 115 | 434 | 67 | kW | 1.07
86 | 115 | 434 | 72 | MBh | 9.86
86 | 115 | 434 | 72 | S/T | 0.903
86 | 115 | 434 | 72 | ∆T | 19
86 | 115 | 434 | 72 | LDB | 67
86 | 115 | 434 | 72 | LWB | 65.8
86 | 115 | 434 | 72 | kW | 1.07
90 | 115 | 434 | 75 | MBh | 10.39
90 | 115 | 434 | 75 | S/T | 0.846
90 | 115 | 434 | 75 | ∆T | 18.8
90 | 115 | 434 | 75 | LDB | 71.2
90 | 115 | 434 | 75 | LWB | 68.9
90 | 115 | 434 | 75 | kW | 1.07

## RXC18BVJU9 - FTXC18BVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 378 | 57 | MBh | 14.06 | 75 | 64 | 59 | 27.58 | 2.38
68 | 50 | 378 | 57 | S/T | 0.704 | 75 | 64 | 70 | 26.2 | 2.37
68 | 50 | 378 | 57 | ∆T | 24.3 | 75 | 64 | 72 | 25.48 | 2.3
68 | 50 | 378 | 57 | LDB | 43.7 | 75 | 64 | 75 | 23.89 | 2.14
68 | 50 | 378 | 57 | LWB | 41.9 | 75 | 64 | 77 | 23.09 | 2.06
68 | 50 | 378 | 57 | kW | 0.78 | 75 | 64 | 81 | 21.5 | 1.9
72 | 50 | 378 | 61 | MBh | 17.26 | 59 | 50 | 59 | 23.78 | 2.23
72 | 50 | 378 | 61 | S/T | 0.641 | 59 | 50 | 70 | 22.9 | 2.29
72 | 50 | 378 | 61 | ∆T | 27.1 | 59 | 50 | 72 | 22.77 | 2.3
72 | 50 | 378 | 61 | LDB | 44.9 | 59 | 50 | 75 | 22.48 | 2.32
72 | 50 | 378 | 61 | LWB | 43.5 | 59 | 50 | 77 | 22.33 | 2.33
72 | 50 | 378 | 61 | kW | 1.04 | 59 | 50 | 81 | 21.5 | 2.27
77 | 50 | 378 | 64 | MBh | 20.71 | 47 | 43 | 59 | 21.89 | 2.16
77 | 50 | 378 | 64 | S/T | 0.618 | 47 | 43 | 70 | 21 | 2.22
77 | 50 | 378 | 64 | ∆T | 31.4 | 47 | 43 | 72 | 20.87 | 2.23
77 | 50 | 378 | 64 | LDB | 45.6 | 47 | 43 | 75 | 20.58 | 2.25
77 | 50 | 378 | 64 | LWB | 43.7 | 47 | 43 | 77 | 20.44 | 2.26
77 | 50 | 378 | 64 | kW | 1.37 | 47 | 43 | 81 | 20.15 | 2.28
80 | 50 | 378 | 67 | MBh | 21.82 | 35 | 32 | 59 | 17.71 | 1.91
80 | 50 | 378 | 67 | S/T | 0.596 | 35 | 32 | 70 | 16.88 | 1.96
80 | 50 | 378 | 67 | ∆T | 31.9 | 35 | 32 | 72 | 16.76 | 1.97
80 | 50 | 378 | 67 | LDB | 48.1 | 35 | 32 | 75 | 16.49 | 1.99
80 | 50 | 378 | 67 | LWB | 47 | 35 | 32 | 77 | 16.36 | 2
80 | 50 | 378 | 67 | kW | 1.45 | 35 | 32 | 81 | 16.09 | 2.02
86 | 50 | 378 | 72 | MBh | 22.88 | 25 | 23 | 59 | 15.5 | 1.82
86 | 50 | 378 | 72 | S/T | 0.563 | 25 | 23 | 70 | 14.68 | 1.88
86 | 50 | 378 | 72 | ∆T | 31.6 | 25 | 23 | 72 | 14.56 | 1.89
86 | 50 | 378 | 72 | LDB | 54.4 | 25 | 23 | 75 | 14.29 | 1.9
86 | 50 | 378 | 72 | LWB | 53.3 | 25 | 23 | 77 | 14.15 | 1.91
86 | 50 | 378 | 72 | kW | 1.46 | 25 | 23 | 81 | 13.88 | 1.93
90 | 50 | 378 | 75 | MBh | 23.7 | 16 | 14 | 59 | 13.3 | 1.74
90 | 50 | 378 | 75 | S/T | 0.524 | 16 | 14 | 70 | 12.47 | 1.79
90 | 50 | 378 | 75 | ∆T | 30.4 | 16 | 14 | 72 | 12.35 | 1.8
90 | 50 | 378 | 75 | LDB | 59.6 | 16 | 14 | 75 | 12.08 | 1.82
90 | 50 | 378 | 75 | LWB | 57 | 16 | 14 | 77 | 11.95 | 1.83
90 | 50 | 378 | 75 | kW | 1.47 | 16 | 14 | 81 | 11.68 | 1.85
68 | 68 | 378 | 57 | MBh | 14.06 | 5 | 5 | 59 | 12.64 | 1.6
68 | 68 | 378 | 57 | S/T | 0.704 | 5 | 5 | 70 | 11.7 | 1.65
68 | 68 | 378 | 57 | ∆T | 24.3 | 5 | 5 | 72 | 11.56 | 1.66
68 | 68 | 378 | 57 | LDB | 43.7 | 5 | 5 | 75 | 11.25 | 1.68
68 | 68 | 378 | 57 | LWB | 41.9 | 5 | 5 | 77 | 11.1 | 1.69
68 | 68 | 378 | 57 | kW | 1.07 | 5 | 5 | 81 | 10.79 | 1.71
72 | 68 | 378 | 61 | MBh | 17.26
72 | 68 | 378 | 61 | S/T | 0.641
72 | 68 | 378 | 61 | ∆T | 27.1
72 | 68 | 378 | 61 | LDB | 44.9
72 | 68 | 378 | 61 | LWB | 43.5
72 | 68 | 378 | 61 | kW | 1.47
77 | 68 | 378 | 64 | MBh | 19.6
77 | 68 | 378 | 64 | S/T | 0.623
77 | 68 | 378 | 64 | ∆T | 29.9
77 | 68 | 378 | 64 | LDB | 47.1
77 | 68 | 378 | 64 | LWB | 45
77 | 68 | 378 | 64 | kW | 1.78
80 | 68 | 378 | 67 | MBh | 20.17
80 | 68 | 378 | 67 | S/T | 0.604
80 | 68 | 378 | 67 | ∆T | 29.8
80 | 68 | 378 | 67 | LDB | 50.2
80 | 68 | 378 | 67 | LWB | 48.8
80 | 68 | 378 | 67 | kW | 1.79
86 | 68 | 378 | 72 | MBh | 21.23
86 | 68 | 378 | 72 | S/T | 0.571
86 | 68 | 378 | 72 | ∆T | 29.7
86 | 68 | 378 | 72 | LDB | 56.3
86 | 68 | 378 | 72 | LWB | 54.9
86 | 68 | 378 | 72 | kW | 1.8
90 | 68 | 378 | 75 | MBh | 22.05
90 | 68 | 378 | 75 | S/T | 0.532
90 | 68 | 378 | 75 | ∆T | 28.8
90 | 68 | 378 | 75 | LDB | 61.2
90 | 68 | 378 | 75 | LWB | 58.5
90 | 68 | 378 | 75 | kW | 1.81
68 | 86 | 378 | 57 | MBh | 14.06
68 | 86 | 378 | 57 | S/T | 0.704
68 | 86 | 378 | 57 | ∆T | 24.3
68 | 86 | 378 | 57 | LDB | 43.7
68 | 86 | 378 | 57 | LWB | 41.9
68 | 86 | 378 | 57 | kW | 1.48
72 | 86 | 378 | 61 | MBh | 17.14
72 | 86 | 378 | 61 | S/T | 0.641
72 | 86 | 378 | 61 | ∆T | 26.9
72 | 86 | 378 | 61 | LDB | 45.1
72 | 86 | 378 | 61 | LWB | 43.7
72 | 86 | 378 | 61 | kW | 2.11
77 | 86 | 378 | 64 | MBh | 17.95
77 | 86 | 378 | 64 | S/T | 0.633
77 | 86 | 378 | 64 | ∆T | 27.9
77 | 86 | 378 | 64 | LDB | 49.1
77 | 86 | 378 | 64 | LWB | 46.9
77 | 86 | 378 | 64 | kW | 2.12
80 | 86 | 378 | 67 | MBh | 18.53
80 | 86 | 378 | 67 | S/T | 0.614
80 | 86 | 378 | 67 | ∆T | 27.9
80 | 86 | 378 | 67 | LDB | 52.1
80 | 86 | 378 | 67 | LWB | 50.5
80 | 86 | 378 | 67 | kW | 2.13
86 | 86 | 378 | 72 | MBh | 19.59
86 | 86 | 378 | 72 | S/T | 0.582
86 | 86 | 378 | 72 | ∆T | 27.9
86 | 86 | 378 | 72 | LDB | 58.1
86 | 86 | 378 | 72 | LWB | 56.5
86 | 86 | 378 | 72 | kW | 2.14
90 | 86 | 378 | 75 | MBh | 20.4
90 | 86 | 378 | 75 | S/T | 0.543
90 | 86 | 378 | 75 | ∆T | 27.1
90 | 86 | 378 | 75 | LDB | 62.9
90 | 86 | 378 | 75 | LWB | 60
90 | 86 | 378 | 75 | kW | 2.15
68 | 95 | 378 | 57 | MBh | 14.06
68 | 95 | 378 | 57 | S/T | 0.704
68 | 95 | 378 | 57 | ∆T | 24.3
68 | 95 | 378 | 57 | LDB | 43.7
68 | 95 | 378 | 57 | LWB | 41.9
68 | 95 | 378 | 57 | kW | 1.78
72 | 95 | 378 | 61 | MBh | 16.32
72 | 95 | 378 | 61 | S/T | 0.647
72 | 95 | 378 | 61 | ∆T | 25.9
72 | 95 | 378 | 61 | LDB | 46.1
72 | 95 | 378 | 61 | LWB | 44.6
72 | 95 | 378 | 61 | kW | 2.28
77 | 95 | 378 | 64 | MBh | 17.13
77 | 95 | 378 | 64 | S/T | 0.64
77 | 95 | 378 | 64 | ∆T | 26.8
77 | 95 | 378 | 64 | LDB | 50.2
77 | 95 | 378 | 64 | LWB | 47.8
77 | 95 | 378 | 64 | kW | 2.29
80 | 95 | 378 | 67 | MBh | 17.7
80 | 95 | 378 | 67 | S/T | 0.62
80 | 95 | 378 | 67 | ∆T | 26.9
80 | 95 | 378 | 67 | LDB | 53.1
80 | 95 | 378 | 67 | LWB | 51.4
80 | 95 | 378 | 67 | kW | 2.3
86 | 95 | 378 | 72 | MBh | 18.76
86 | 95 | 378 | 72 | S/T | 0.589
86 | 95 | 378 | 72 | ∆T | 27.1
86 | 95 | 378 | 72 | LDB | 58.9
86 | 95 | 378 | 72 | LWB | 57.3
86 | 95 | 378 | 72 | kW | 2.31
90 | 95 | 378 | 75 | MBh | 19.58
90 | 95 | 378 | 75 | S/T | 0.549
90 | 95 | 378 | 75 | ∆T | 26.3
90 | 95 | 378 | 75 | LDB | 63.7
90 | 95 | 378 | 75 | LWB | 60.7
90 | 95 | 378 | 75 | kW | 2.32
68 | 104 | 378 | 57 | MBh | 14.06
68 | 104 | 378 | 57 | S/T | 0.704
68 | 104 | 378 | 57 | ∆T | 24.3
68 | 104 | 378 | 57 | LDB | 43.7
68 | 104 | 378 | 57 | LWB | 41.9
68 | 104 | 378 | 57 | kW | 2.17
72 | 104 | 378 | 61 | MBh | 15.49
72 | 104 | 378 | 61 | S/T | 0.654
72 | 104 | 378 | 61 | ∆T | 24.8
72 | 104 | 378 | 61 | LDB | 47.2
72 | 104 | 378 | 61 | LWB | 45.6
72 | 104 | 378 | 61 | kW | 2.45
77 | 104 | 378 | 64 | MBh | 16.31
77 | 104 | 378 | 64 | S/T | 0.647
77 | 104 | 378 | 64 | ∆T | 25.9
77 | 104 | 378 | 64 | LDB | 51.1
77 | 104 | 378 | 64 | LWB | 48.7
77 | 104 | 378 | 64 | kW | 2.46
80 | 104 | 378 | 67 | MBh | 16.88
80 | 104 | 378 | 67 | S/T | 0.628
80 | 104 | 378 | 67 | ∆T | 26
80 | 104 | 378 | 67 | LDB | 54
80 | 104 | 378 | 67 | LWB | 52.2
80 | 104 | 378 | 67 | kW | 2.47
86 | 104 | 378 | 72 | MBh | 17.94
86 | 104 | 378 | 72 | S/T | 0.597
86 | 104 | 378 | 72 | ∆T | 26.2
86 | 104 | 378 | 72 | LDB | 59.8
86 | 104 | 378 | 72 | LWB | 58
86 | 104 | 378 | 72 | kW | 2.48
90 | 104 | 378 | 75 | MBh | 18.75
90 | 104 | 378 | 75 | S/T | 0.556
90 | 104 | 378 | 75 | ∆T | 25.5
90 | 104 | 378 | 75 | LDB | 64.5
90 | 104 | 378 | 75 | LWB | 61.4
90 | 104 | 378 | 75 | kW | 2.49
68 | 115 | 378 | 57 | MBh | 11.49
68 | 115 | 378 | 57 | S/T | 0.746
68 | 115 | 378 | 57 | ∆T | 21
68 | 115 | 378 | 57 | LDB | 47
68 | 115 | 378 | 57 | LWB | 45
68 | 115 | 378 | 57 | kW | 2.27
72 | 115 | 378 | 61 | MBh | 12.24
72 | 115 | 378 | 61 | S/T | 0.697
72 | 115 | 378 | 61 | ∆T | 20.9
72 | 115 | 378 | 61 | LDB | 51.1
72 | 115 | 378 | 61 | LWB | 49.2
72 | 115 | 378 | 61 | kW | 2.27
77 | 115 | 378 | 64 | MBh | 13
77 | 115 | 378 | 64 | S/T | 0.695
77 | 115 | 378 | 64 | ∆T | 22.1
77 | 115 | 378 | 64 | LDB | 54.9
77 | 115 | 378 | 64 | LWB | 52.2
77 | 115 | 378 | 64 | kW | 2.27
80 | 115 | 378 | 67 | MBh | 13.53
80 | 115 | 378 | 67 | S/T | 0.675
80 | 115 | 378 | 67 | ∆T | 22.4
80 | 115 | 378 | 67 | LDB | 57.6
80 | 115 | 378 | 67 | LWB | 55.5
80 | 115 | 378 | 67 | kW | 2.27
86 | 115 | 378 | 72 | MBh | 14.51
86 | 115 | 378 | 72 | S/T | 0.644
86 | 115 | 378 | 72 | ∆T | 22.9
86 | 115 | 378 | 72 | LDB | 63.1
86 | 115 | 378 | 72 | LWB | 61
86 | 115 | 378 | 72 | kW | 2.27
90 | 115 | 378 | 75 | MBh | 15.26
90 | 115 | 378 | 75 | S/T | 0.6
90 | 115 | 378 | 75 | ∆T | 22.4
90 | 115 | 378 | 75 | LDB | 67.6
90 | 115 | 378 | 75 | LWB | 64.2
90 | 115 | 378 | 75 | kW | 2.27

## RXC24BVJU9 - FTXC24BVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 689 | 57 | MBh | 21.55 | 75 | 64 | 59 | 34.27 | 2.62
68 | 50 | 689 | 57 | S/T | 0.704 | 75 | 64 | 70 | 33.18 | 2.69
68 | 50 | 689 | 57 | ∆T | 20.4 | 75 | 64 | 72 | 33.01 | 2.7
68 | 50 | 689 | 57 | LDB | 47.6 | 75 | 64 | 75 | 32.65 | 2.72
68 | 50 | 689 | 57 | LWB | 44.6 | 75 | 64 | 77 | 32.47 | 2.74
68 | 50 | 689 | 57 | kW | 1.1 | 75 | 64 | 81 | 32 | 2.74
72 | 50 | 689 | 61 | MBh | 26.47 | 59 | 50 | 59 | 29.56 | 2.46
72 | 50 | 689 | 61 | S/T | 0.641 | 59 | 50 | 70 | 28.46 | 2.53
72 | 50 | 689 | 61 | ∆T | 22.8 | 59 | 50 | 72 | 28.3 | 2.54
72 | 50 | 689 | 61 | LDB | 49.2 | 59 | 50 | 75 | 27.94 | 2.56
72 | 50 | 689 | 61 | LWB | 46.7 | 59 | 50 | 77 | 27.76 | 2.57
72 | 50 | 689 | 61 | kW | 1.5 | 59 | 50 | 81 | 27.4 | 2.6
77 | 50 | 689 | 64 | MBh | 27.97 | 47 | 43 | 59 | 27.2 | 2.38
77 | 50 | 689 | 64 | S/T | 0.631 | 47 | 43 | 70 | 26.1 | 2.45
77 | 50 | 689 | 64 | ∆T | 23.7 | 47 | 43 | 72 | 25.94 | 2.46
77 | 50 | 689 | 64 | LDB | 53.3 | 47 | 43 | 75 | 25.58 | 2.48
77 | 50 | 689 | 64 | LWB | 49.8 | 47 | 43 | 77 | 25.4 | 2.49
77 | 50 | 689 | 64 | kW | 1.56 | 47 | 43 | 81 | 25.04 | 2.52
80 | 50 | 689 | 67 | MBh | 28.73 | 35 | 32 | 59 | 22.01 | 2.22
80 | 50 | 689 | 67 | S/T | 0.612 | 35 | 32 | 70 | 20.99 | 2.28
80 | 50 | 689 | 67 | ∆T | 23.6 | 35 | 32 | 72 | 20.83 | 2.29
80 | 50 | 689 | 67 | LDB | 56.4 | 35 | 32 | 75 | 20.5 | 2.31
80 | 50 | 689 | 67 | LWB | 53.4 | 35 | 32 | 77 | 20.33 | 2.32
80 | 50 | 689 | 67 | kW | 1.56 | 35 | 32 | 81 | 20 | 2.35
86 | 50 | 689 | 72 | MBh | 30.12 | 25 | 23 | 59 | 19.27 | 2.12
86 | 50 | 689 | 72 | S/T | 0.582 | 25 | 23 | 70 | 18.24 | 2.18
86 | 50 | 689 | 72 | ∆T | 23.5 | 25 | 23 | 72 | 18.09 | 2.19
86 | 50 | 689 | 72 | LDB | 62.5 | 25 | 23 | 75 | 17.76 | 2.21
86 | 50 | 689 | 72 | LWB | 59.3 | 25 | 23 | 77 | 17.59 | 2.23
86 | 50 | 689 | 72 | kW | 1.58 | 25 | 23 | 81 | 17.26 | 2.25
90 | 50 | 689 | 75 | MBh | 31.19 | 16 | 14 | 59 | 16.53 | 2.02
90 | 50 | 689 | 75 | S/T | 0.543 | 16 | 14 | 70 | 15.5 | 2.08
90 | 50 | 689 | 75 | ∆T | 22.8 | 16 | 14 | 72 | 15.35 | 2.09
90 | 50 | 689 | 75 | LDB | 67.2 | 16 | 14 | 75 | 15.02 | 2.12
90 | 50 | 689 | 75 | LWB | 62.8 | 16 | 14 | 77 | 14.85 | 2.13
90 | 50 | 689 | 75 | kW | 1.59 | 16 | 14 | 81 | 14.51 | 2.15
68 | 68 | 689 | 57 | MBh | 21.55 | 5 | 5 | 59 | 15.45 | 1.96
68 | 68 | 689 | 57 | S/T | 0.704 | 5 | 5 | 70 | 14.3 | 2.03
68 | 68 | 689 | 57 | ∆T | 20.4 | 5 | 5 | 72 | 14.13 | 2.04
68 | 68 | 689 | 57 | LDB | 47.6 | 5 | 5 | 75 | 13.76 | 2.06
68 | 68 | 689 | 57 | LWB | 44.6 | 5 | 5 | 77 | 13.57 | 2.07
68 | 68 | 689 | 57 | kW | 1.56 | 5 | 5 | 81 | 13.19 | 2.09
72 | 68 | 689 | 61 | MBh | 24.73
72 | 68 | 689 | 61 | S/T | 0.649
72 | 68 | 689 | 61 | ∆T | 21.6
72 | 68 | 689 | 61 | LDB | 50.4
72 | 68 | 689 | 61 | LWB | 47.8
72 | 68 | 689 | 61 | kW | 1.91
77 | 68 | 689 | 64 | MBh | 25.8
77 | 68 | 689 | 64 | S/T | 0.643
77 | 68 | 689 | 64 | ∆T | 22.3
77 | 68 | 689 | 64 | LDB | 54.7
77 | 68 | 689 | 64 | LWB | 51
77 | 68 | 689 | 64 | kW | 1.92
80 | 68 | 689 | 67 | MBh | 26.56
80 | 68 | 689 | 67 | S/T | 0.624
80 | 68 | 689 | 67 | ∆T | 22.3
80 | 68 | 689 | 67 | LDB | 57.7
80 | 68 | 689 | 67 | LWB | 54.5
80 | 68 | 689 | 67 | kW | 1.93
86 | 68 | 689 | 72 | MBh | 27.95
86 | 68 | 689 | 72 | S/T | 0.594
86 | 68 | 689 | 72 | ∆T | 22.3
86 | 68 | 689 | 72 | LDB | 63.7
86 | 68 | 689 | 72 | LWB | 60.3
86 | 68 | 689 | 72 | kW | 1.94
90 | 68 | 689 | 75 | MBh | 29.02
90 | 68 | 689 | 75 | S/T | 0.555
90 | 68 | 689 | 75 | ∆T | 21.6
90 | 68 | 689 | 75 | LDB | 68.4
90 | 68 | 689 | 75 | LWB | 63.7
90 | 68 | 689 | 75 | kW | 1.96
68 | 86 | 689 | 57 | MBh | 21.49
68 | 86 | 689 | 57 | S/T | 0.705
68 | 86 | 689 | 57 | ∆T | 20.3
68 | 86 | 689 | 57 | LDB | 47.7
68 | 86 | 689 | 57 | LWB | 44.7
68 | 86 | 689 | 57 | kW | 2.27
72 | 86 | 689 | 61 | MBh | 22.56
72 | 86 | 689 | 61 | S/T | 0.662
72 | 86 | 689 | 61 | ∆T | 20.1
72 | 86 | 689 | 61 | LDB | 51.9
72 | 86 | 689 | 61 | LWB | 49.1
72 | 86 | 689 | 61 | kW | 2.28
77 | 86 | 689 | 64 | MBh | 23.63
77 | 86 | 689 | 64 | S/T | 0.658
77 | 86 | 689 | 64 | ∆T | 20.9
77 | 86 | 689 | 64 | LDB | 56.1
77 | 86 | 689 | 64 | LWB | 52.3
77 | 86 | 689 | 64 | kW | 2.29
80 | 86 | 689 | 67 | MBh | 24.39
80 | 86 | 689 | 67 | S/T | 0.639
80 | 86 | 689 | 67 | ∆T | 20.9
80 | 86 | 689 | 67 | LDB | 59.1
80 | 86 | 689 | 67 | LWB | 55.7
80 | 86 | 689 | 67 | kW | 2.3
86 | 86 | 689 | 72 | MBh | 25.78
86 | 86 | 689 | 72 | S/T | 0.609
86 | 86 | 689 | 72 | ∆T | 21.1
86 | 86 | 689 | 72 | LDB | 64.9
86 | 86 | 689 | 72 | LWB | 61.3
86 | 86 | 689 | 72 | kW | 2.31
90 | 86 | 689 | 75 | MBh | 26.85
90 | 86 | 689 | 75 | S/T | 0.569
90 | 86 | 689 | 75 | ∆T | 20.5
90 | 86 | 689 | 75 | LDB | 69.5
90 | 86 | 689 | 75 | LWB | 64.7
90 | 86 | 689 | 75 | kW | 2.32
68 | 95 | 689 | 57 | MBh | 20.4
68 | 95 | 689 | 57 | S/T | 0.714
68 | 95 | 689 | 57 | ∆T | 19.6
68 | 95 | 689 | 57 | LDB | 48.4
68 | 95 | 689 | 57 | LWB | 45.4
68 | 95 | 689 | 57 | kW | 2.45
72 | 95 | 689 | 61 | MBh | 21.48
72 | 95 | 689 | 61 | S/T | 0.67
72 | 95 | 689 | 61 | ∆T | 19.3
72 | 95 | 689 | 61 | LDB | 52.7
72 | 95 | 689 | 61 | LWB | 49.7
72 | 95 | 689 | 61 | kW | 2.46
77 | 95 | 689 | 64 | MBh | 22.55
77 | 95 | 689 | 64 | S/T | 0.667
77 | 95 | 689 | 64 | ∆T | 20.2
77 | 95 | 689 | 64 | LDB | 56.8
77 | 95 | 689 | 64 | LWB | 52.9
77 | 95 | 689 | 64 | kW | 2.47
80 | 95 | 689 | 67 | MBh | 23.3
80 | 95 | 689 | 67 | S/T | 0.648
80 | 95 | 689 | 67 | ∆T | 20.3
80 | 95 | 689 | 67 | LDB | 59.7
80 | 95 | 689 | 67 | LWB | 56.2
80 | 95 | 689 | 67 | kW | 2.48
86 | 95 | 689 | 72 | MBh | 24.7
86 | 95 | 689 | 72 | S/T | 0.619
86 | 95 | 689 | 72 | ∆T | 20.5
86 | 95 | 689 | 72 | LDB | 65.5
86 | 95 | 689 | 72 | LWB | 61.8
86 | 95 | 689 | 72 | kW | 2.49
90 | 95 | 689 | 75 | MBh | 25.77
90 | 95 | 689 | 75 | S/T | 0.578
90 | 95 | 689 | 75 | ∆T | 20
90 | 95 | 689 | 75 | LDB | 70
90 | 95 | 689 | 75 | LWB | 65.1
90 | 95 | 689 | 75 | kW | 2.51
68 | 104 | 689 | 57 | MBh | 19.32
68 | 104 | 689 | 57 | S/T | 0.725
68 | 104 | 689 | 57 | ∆T | 18.8
68 | 104 | 689 | 57 | LDB | 49.2
68 | 104 | 689 | 57 | LWB | 46
68 | 104 | 689 | 57 | kW | 2.63
72 | 104 | 689 | 61 | MBh | 20.39
72 | 104 | 689 | 61 | S/T | 0.68
72 | 104 | 689 | 61 | ∆T | 18.6
72 | 104 | 689 | 61 | LDB | 53.4
72 | 104 | 689 | 61 | LWB | 50.3
72 | 104 | 689 | 61 | kW | 2.64
77 | 104 | 689 | 64 | MBh | 21.46
77 | 104 | 689 | 64 | S/T | 0.678
77 | 104 | 689 | 64 | ∆T | 19.5
77 | 104 | 689 | 64 | LDB | 57.5
77 | 104 | 689 | 64 | LWB | 53.5
77 | 104 | 689 | 64 | kW | 2.66
80 | 104 | 689 | 67 | MBh | 22.22
80 | 104 | 689 | 67 | S/T | 0.658
80 | 104 | 689 | 67 | ∆T | 19.7
80 | 104 | 689 | 67 | LDB | 60.3
80 | 104 | 689 | 67 | LWB | 56.8
80 | 104 | 689 | 67 | kW | 2.66
86 | 104 | 689 | 72 | MBh | 23.61
86 | 104 | 689 | 72 | S/T | 0.629
86 | 104 | 689 | 72 | ∆T | 20
86 | 104 | 689 | 72 | LDB | 66
86 | 104 | 689 | 72 | LWB | 62.3
86 | 104 | 689 | 72 | kW | 2.68
90 | 104 | 689 | 75 | MBh | 24.68
90 | 104 | 689 | 75 | S/T | 0.588
90 | 104 | 689 | 75 | ∆T | 19.5
90 | 104 | 689 | 75 | LDB | 70.5
90 | 104 | 689 | 75 | LWB | 65.6
90 | 104 | 689 | 75 | kW | 2.69
68 | 115 | 689 | 57 | MBh | 15.45
68 | 115 | 689 | 57 | S/T | 0.781
68 | 115 | 689 | 57 | ∆T | 16.2
68 | 115 | 689 | 57 | LDB | 51.8
68 | 115 | 689 | 57 | LWB | 48.4
68 | 115 | 689 | 57 | kW | 2.27
72 | 115 | 689 | 61 | MBh | 16.48
72 | 115 | 689 | 61 | S/T | 0.729
72 | 115 | 689 | 61 | ∆T | 16.1
72 | 115 | 689 | 61 | LDB | 55.9
72 | 115 | 689 | 61 | LWB | 52.6
72 | 115 | 689 | 61 | kW | 2.27
77 | 115 | 689 | 64 | MBh | 17.5
77 | 115 | 689 | 64 | S/T | 0.731
77 | 115 | 689 | 64 | ∆T | 17.2
77 | 115 | 689 | 64 | LDB | 59.8
77 | 115 | 689 | 64 | LWB | 55.6
77 | 115 | 689 | 64 | kW | 2.27
80 | 115 | 689 | 67 | MBh | 18.22
80 | 115 | 689 | 67 | S/T | 0.711
80 | 115 | 689 | 67 | ∆T | 17.4
80 | 115 | 689 | 67 | LDB | 62.6
80 | 115 | 689 | 67 | LWB | 58.8
80 | 115 | 689 | 67 | kW | 2.27
86 | 115 | 689 | 72 | MBh | 19.55
86 | 115 | 689 | 72 | S/T | 0.681
86 | 115 | 689 | 72 | ∆T | 17.9
86 | 115 | 689 | 72 | LDB | 68.1
86 | 115 | 689 | 72 | LWB | 64.1
86 | 115 | 689 | 72 | kW | 2.27
90 | 115 | 689 | 75 | MBh | 20.58
90 | 115 | 689 | 75 | S/T | 0.635
90 | 115 | 689 | 75 | ∆T | 17.6
90 | 115 | 689 | 75 | LDB | 72.4
90 | 115 | 689 | 75 | LWB | 67.3
90 | 115 | 689 | 75 | kW | 2.27

## RKF09BVJU9 - FTKF09BVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT
68 | 50 | 381 | 57 | MBh | 12.42
68 | 50 | 381 | 57 | S/T | 0.733
68 | 50 | 381 | 57 | ∆T | 22.1
68 | 50 | 381 | 57 | LDB | 45.9
68 | 50 | 381 | 57 | LWB | 44
68 | 50 | 381 | 57 | kW | 0.6
72 | 50 | 381 | 61 | MBh | 12.93
72 | 50 | 381 | 61 | S/T | 0.689
72 | 50 | 381 | 61 | ∆T | 21.7
72 | 50 | 381 | 61 | LDB | 50.3
72 | 50 | 381 | 61 | LWB | 48.6
72 | 50 | 381 | 61 | kW | 0.61
77 | 50 | 381 | 64 | MBh | 13.45
77 | 50 | 381 | 64 | S/T | 0.691
77 | 50 | 381 | 64 | ∆T | 22.6
77 | 50 | 381 | 64 | LDB | 54.4
77 | 50 | 381 | 64 | LWB | 51.9
77 | 50 | 381 | 64 | kW | 0.61
80 | 50 | 381 | 67 | MBh | 13.81
80 | 50 | 381 | 67 | S/T | 0.675
80 | 50 | 381 | 67 | ∆T | 22.6
80 | 50 | 381 | 67 | LDB | 57.4
80 | 50 | 381 | 67 | LWB | 55.4
80 | 50 | 381 | 67 | kW | 0.61
86 | 50 | 381 | 72 | MBh | 14.48
86 | 50 | 381 | 72 | S/T | 0.65
86 | 50 | 381 | 72 | ∆T | 22.9
86 | 50 | 381 | 72 | LDB | 63.1
86 | 50 | 381 | 72 | LWB | 61.1
86 | 50 | 381 | 72 | kW | 0.76
90 | 50 | 381 | 75 | MBh | 15
90 | 50 | 381 | 75 | S/T | 0.61
90 | 50 | 381 | 75 | ∆T | 22.2
90 | 50 | 381 | 75 | LDB | 67.8
90 | 50 | 381 | 75 | LWB | 64.5
90 | 50 | 381 | 75 | kW | 0.77
68 | 68 | 381 | 57 | MBh | 11.37
68 | 68 | 381 | 57 | S/T | 0.754
68 | 68 | 381 | 57 | ∆T | 20.8
68 | 68 | 381 | 57 | LDB | 47.2
68 | 68 | 381 | 57 | LWB | 45.2
68 | 68 | 381 | 57 | kW | 0.75
72 | 68 | 381 | 61 | MBh | 11.89
72 | 68 | 381 | 61 | S/T | 0.708
72 | 68 | 381 | 61 | ∆T | 20.5
72 | 68 | 381 | 61 | LDB | 51.5
72 | 68 | 381 | 61 | LWB | 49.7
72 | 68 | 381 | 61 | kW | 0.75
77 | 68 | 381 | 64 | MBh | 12.41
77 | 68 | 381 | 64 | S/T | 0.712
77 | 68 | 381 | 64 | ∆T | 21.5
77 | 68 | 381 | 64 | LDB | 55.5
77 | 68 | 381 | 64 | LWB | 52.9
77 | 68 | 381 | 64 | kW | 0.75
80 | 68 | 381 | 67 | MBh | 12.77
80 | 68 | 381 | 67 | S/T | 0.695
80 | 68 | 381 | 67 | ∆T | 21.6
80 | 68 | 381 | 67 | LDB | 58.4
80 | 68 | 381 | 67 | LWB | 56.3
80 | 68 | 381 | 67 | kW | 0.76
86 | 68 | 381 | 72 | MBh | 13.44
86 | 68 | 381 | 72 | S/T | 0.671
86 | 68 | 381 | 72 | ∆T | 21.9
86 | 68 | 381 | 72 | LDB | 64.1
86 | 68 | 381 | 72 | LWB | 62
86 | 68 | 381 | 72 | kW | 0.76
90 | 68 | 381 | 75 | MBh | 13.95
90 | 68 | 381 | 75 | S/T | 0.63
90 | 68 | 381 | 75 | ∆T | 21.4
90 | 68 | 381 | 75 | LDB | 68.6
90 | 68 | 381 | 75 | LWB | 65.3
90 | 68 | 381 | 75 | kW | 0.77
68 | 86 | 381 | 57 | MBh | 10.33
68 | 86 | 381 | 57 | S/T | 0.779
68 | 86 | 381 | 57 | ∆T | 19.6
68 | 86 | 381 | 57 | LDB | 48.4
68 | 86 | 381 | 57 | LWB | 46.4
68 | 86 | 381 | 57 | kW | 0.89
72 | 86 | 381 | 61 | MBh | 10.85
72 | 86 | 381 | 61 | S/T | 0.732
72 | 86 | 381 | 61 | ∆T | 19.3
72 | 86 | 381 | 61 | LDB | 52.7
72 | 86 | 381 | 61 | LWB | 50.8
72 | 86 | 381 | 61 | kW | 0.89
77 | 86 | 381 | 64 | MBh | 11.36
77 | 86 | 381 | 64 | S/T | 0.739
77 | 86 | 381 | 64 | ∆T | 20.4
77 | 86 | 381 | 64 | LDB | 56.6
77 | 86 | 381 | 64 | LWB | 53.9
77 | 86 | 381 | 64 | kW | 0.9
80 | 86 | 381 | 67 | MBh | 11.72
80 | 86 | 381 | 67 | S/T | 0.722
80 | 86 | 381 | 67 | ∆T | 20.6
80 | 86 | 381 | 67 | LDB | 59.4
80 | 86 | 381 | 67 | LWB | 57.3
80 | 86 | 381 | 67 | kW | 0.9
86 | 86 | 381 | 72 | MBh | 12.39
86 | 86 | 381 | 72 | S/T | 0.697
86 | 86 | 381 | 72 | ∆T | 21
86 | 86 | 381 | 72 | LDB | 65
86 | 86 | 381 | 72 | LWB | 62.9
86 | 86 | 381 | 72 | kW | 0.91
90 | 86 | 381 | 75 | MBh | 12.91
90 | 86 | 381 | 75 | S/T | 0.654
90 | 86 | 381 | 75 | ∆T | 20.5
90 | 86 | 381 | 75 | LDB | 69.5
90 | 86 | 381 | 75 | LWB | 66.1
90 | 86 | 381 | 75 | kW | 0.91
68 | 95 | 381 | 57 | MBh | 9.81
68 | 95 | 381 | 57 | S/T | 0.795
68 | 95 | 381 | 57 | ∆T | 19
68 | 95 | 381 | 57 | LDB | 49
68 | 95 | 381 | 57 | LWB | 47
68 | 95 | 381 | 57 | kW | 0.96
72 | 95 | 381 | 61 | MBh | 10.32
72 | 95 | 381 | 61 | S/T | 0.746
72 | 95 | 381 | 61 | ∆T | 18.7
72 | 95 | 381 | 61 | LDB | 53.3
72 | 95 | 381 | 61 | LWB | 51.3
72 | 95 | 381 | 61 | kW | 0.97
77 | 95 | 381 | 64 | MBh | 10.84
77 | 95 | 381 | 64 | S/T | 0.755
77 | 95 | 381 | 64 | ∆T | 19.9
77 | 95 | 381 | 64 | LDB | 57.1
77 | 95 | 381 | 64 | LWB | 54.5
77 | 95 | 381 | 64 | kW | 0.97
80 | 95 | 381 | 67 | MBh | 11.2
80 | 95 | 381 | 67 | S/T | 0.737
80 | 95 | 381 | 67 | ∆T | 20
80 | 95 | 381 | 67 | LDB | 60
80 | 95 | 381 | 67 | LWB | 57.8
80 | 95 | 381 | 67 | kW | 0.97
86 | 95 | 381 | 72 | MBh | 11.87
86 | 95 | 381 | 72 | S/T | 0.712
86 | 95 | 381 | 72 | ∆T | 20.5
86 | 95 | 381 | 72 | LDB | 65.5
86 | 95 | 381 | 72 | LWB | 63.3
86 | 95 | 381 | 72 | kW | 0.98
90 | 95 | 381 | 75 | MBh | 12.39
90 | 95 | 381 | 75 | S/T | 0.667
90 | 95 | 381 | 75 | ∆T | 20.1
90 | 95 | 381 | 75 | LDB | 69.9
90 | 95 | 381 | 75 | LWB | 66.5
90 | 95 | 381 | 75 | kW | 0.98
68 | 104 | 381 | 57 | MBh | 9.29
68 | 104 | 381 | 57 | S/T | 0.813
68 | 104 | 381 | 57 | ∆T | 18.3
68 | 104 | 381 | 57 | LDB | 49.7
68 | 104 | 381 | 57 | LWB | 47.6
68 | 104 | 381 | 57 | kW | 1.03
72 | 104 | 381 | 61 | MBh | 9.8
72 | 104 | 381 | 61 | S/T | 0.762
72 | 104 | 381 | 61 | ∆T | 18.2
72 | 104 | 381 | 61 | LDB | 53.8
72 | 104 | 381 | 61 | LWB | 51.9
72 | 104 | 381 | 61 | kW | 1.04
77 | 104 | 381 | 64 | MBh | 10.32
77 | 104 | 381 | 64 | S/T | 0.771
77 | 104 | 381 | 64 | ∆T | 19.3
77 | 104 | 381 | 64 | LDB | 57.7
77 | 104 | 381 | 64 | LWB | 55
77 | 104 | 381 | 64 | kW | 1.04
80 | 104 | 381 | 67 | MBh | 11.2
80 | 104 | 381 | 67 | S/T | 0.718
80 | 104 | 381 | 67 | ∆T | 19.5
80 | 104 | 381 | 67 | LDB | 60.5
80 | 104 | 381 | 67 | LWB | 57.8
80 | 104 | 381 | 67 | kW | 1.05
86 | 104 | 381 | 72 | MBh | 11.35
86 | 104 | 381 | 72 | S/T | 0.729
86 | 104 | 381 | 72 | ∆T | 20.1
86 | 104 | 381 | 72 | LDB | 65.9
86 | 104 | 381 | 72 | LWB | 63.7
86 | 104 | 381 | 72 | kW | 1.05
90 | 104 | 381 | 75 | MBh | 11.87
90 | 104 | 381 | 75 | S/T | 0.682
90 | 104 | 381 | 75 | ∆T | 19.7
90 | 104 | 381 | 75 | LDB | 70.3
90 | 104 | 381 | 75 | LWB | 66.9
90 | 104 | 381 | 75 | kW | 1.06
68 | 115 | 381 | 57 | MBh | 8.66
68 | 115 | 381 | 57 | S/T | 0.838
68 | 115 | 381 | 57 | ∆T | 17.6
68 | 115 | 381 | 57 | LDB | 50.4
68 | 115 | 381 | 57 | LWB | 48.3
68 | 115 | 381 | 57 | kW | 1.08
72 | 115 | 381 | 61 | MBh | 9.18
72 | 115 | 381 | 61 | S/T | 0.783
72 | 115 | 381 | 61 | ∆T | 17.5
72 | 115 | 381 | 61 | LDB | 54.5
72 | 115 | 381 | 61 | LWB | 52.5
72 | 115 | 381 | 61 | kW | 1.08
77 | 115 | 381 | 64 | MBh | 9.69
77 | 115 | 381 | 64 | S/T | 0.795
77 | 115 | 381 | 64 | ∆T | 18.7
77 | 115 | 381 | 64 | LDB | 58.3
77 | 115 | 381 | 64 | LWB | 55.5
77 | 115 | 381 | 64 | kW | 1.08
80 | 115 | 381 | 67 | MBh | 10.05
80 | 115 | 381 | 67 | S/T | 0.776
80 | 115 | 381 | 67 | ∆T | 19
80 | 115 | 381 | 67 | LDB | 61
80 | 115 | 381 | 67 | LWB | 58.8
80 | 115 | 381 | 67 | kW | 1.08
86 | 115 | 381 | 72 | MBh | 10.73
86 | 115 | 381 | 72 | S/T | 0.75
86 | 115 | 381 | 72 | ∆T | 19.6
86 | 115 | 381 | 72 | LDB | 66.4
86 | 115 | 381 | 72 | LWB | 64.2
86 | 115 | 381 | 72 | kW | 1.08
90 | 115 | 381 | 75 | MBh | 11.24
90 | 115 | 381 | 75 | S/T | 0.703
90 | 115 | 381 | 75 | ∆T | 19.2
90 | 115 | 381 | 75 | LDB | 70.8
90 | 115 | 381 | 75 | LWB | 67.4
90 | 115 | 381 | 75 | kW | 1.08
68 | 118 | 381 | 57 | MBh | 5.63
68 | 118 | 381 | 57 | S/T | 0.698
68 | 118 | 381 | 57 | ∆T | 9.6
68 | 118 | 381 | 57 | LDB | 58.4
68 | 118 | 381 | 57 | LWB | 51.5
68 | 118 | 381 | 57 | kW | 0.64
72 | 118 | 381 | 61 | MBh | 5.98
72 | 118 | 381 | 61 | S/T | 0.652
72 | 118 | 381 | 61 | ∆T | 9.5
72 | 118 | 381 | 61 | LDB | 62.5
72 | 118 | 381 | 61 | LWB | 55.6
72 | 118 | 381 | 61 | kW | 0.64
77 | 118 | 381 | 64 | MBh | 6.32
77 | 118 | 381 | 64 | S/T | 0.672
77 | 118 | 381 | 64 | ∆T | 10.3
77 | 118 | 381 | 64 | LDB | 66.7
77 | 118 | 381 | 64 | LWB | 58.7
77 | 118 | 381 | 64 | kW | 0.64
80 | 118 | 381 | 67 | MBh | 6.56
80 | 118 | 381 | 67 | S/T | 0.662
80 | 118 | 381 | 67 | ∆T | 10.5
80 | 118 | 381 | 67 | LDB | 69.5
80 | 118 | 381 | 67 | LWB | 61.8
80 | 118 | 381 | 67 | kW | 0.64
86 | 118 | 381 | 72 | MBh | 7.01
86 | 118 | 381 | 72 | S/T | 0.648
86 | 118 | 381 | 72 | ∆T | 11
86 | 118 | 381 | 72 | LDB | 75
86 | 118 | 381 | 72 | LWB | 67.1
86 | 118 | 381 | 72 | kW | 0.64
90 | 118 | 381 | 75 | MBh | 7.35
90 | 118 | 381 | 75 | S/T | 0.61
90 | 118 | 381 | 75 | ∆T | 10.9
90 | 118 | 381 | 75 | LDB | 79.1
90 | 118 | 381 | 75 | LWB | 70.2
90 | 118 | 381 | 75 | kW | 0.64

## RKF12BVJU9 - FTKF12BVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT
68 | 50 | 413 | 57 | MBh | 15.29
68 | 50 | 413 | 57 | S/T | 0.704
68 | 50 | 413 | 57 | ∆T | 24.1
68 | 50 | 413 | 57 | LDB | 43.9
68 | 50 | 413 | 57 | LWB | 42
68 | 50 | 413 | 57 | kW | 0.83
72 | 50 | 413 | 61 | MBh | 16.86
72 | 50 | 413 | 61 | S/T | 0.654
72 | 50 | 413 | 61 | ∆T | 24.7
72 | 50 | 413 | 61 | LDB | 47.3
72 | 50 | 413 | 61 | LWB | 45.7
72 | 50 | 413 | 61 | kW | 0.92
77 | 50 | 413 | 64 | MBh | 17.53
77 | 50 | 413 | 64 | S/T | 0.65
77 | 50 | 413 | 64 | ∆T | 25.5
77 | 50 | 413 | 64 | LDB | 51.5
77 | 50 | 413 | 64 | LWB | 49
77 | 50 | 413 | 64 | kW | 0.93
80 | 50 | 413 | 67 | MBh | 18
80 | 50 | 413 | 67 | S/T | 0.632
80 | 50 | 413 | 67 | ∆T | 25.5
80 | 50 | 413 | 67 | LDB | 54.5
80 | 50 | 413 | 67 | LWB | 52.6
80 | 50 | 413 | 67 | kW | 0.93
86 | 50 | 413 | 72 | MBh | 18.87
86 | 50 | 413 | 72 | S/T | 0.603
86 | 50 | 413 | 72 | ∆T | 25.5
86 | 50 | 413 | 72 | LDB | 60.5
86 | 50 | 413 | 72 | LWB | 58.6
86 | 50 | 413 | 72 | kW | 0.94
90 | 50 | 413 | 75 | MBh | 19.55
90 | 50 | 413 | 75 | S/T | 0.564
90 | 50 | 413 | 75 | ∆T | 24.7
90 | 50 | 413 | 75 | LDB | 65.3
90 | 50 | 413 | 75 | LWB | 62.1
90 | 50 | 413 | 75 | kW | 1.17
68 | 68 | 413 | 57 | MBh | 14.82
68 | 68 | 413 | 57 | S/T | 0.71
68 | 68 | 413 | 57 | ∆T | 23.6
68 | 68 | 413 | 57 | LDB | 44.4
68 | 68 | 413 | 57 | LWB | 42.5
68 | 68 | 413 | 57 | kW | 1.13
72 | 68 | 413 | 61 | MBh | 15.5
72 | 68 | 413 | 61 | S/T | 0.667
72 | 68 | 413 | 61 | ∆T | 23.2
72 | 68 | 413 | 61 | LDB | 48.8
72 | 68 | 413 | 61 | LWB | 47.1
72 | 68 | 413 | 61 | kW | 1.14
77 | 68 | 413 | 64 | MBh | 16.17
77 | 68 | 413 | 64 | S/T | 0.665
77 | 68 | 413 | 64 | ∆T | 24.1
77 | 68 | 413 | 64 | LDB | 52.9
77 | 68 | 413 | 64 | LWB | 50.4
77 | 68 | 413 | 64 | kW | 1.15
80 | 68 | 413 | 67 | MBh | 16.64
80 | 68 | 413 | 67 | S/T | 0.647
80 | 68 | 413 | 67 | ∆T | 24.1
80 | 68 | 413 | 67 | LDB | 55.9
80 | 68 | 413 | 67 | LWB | 53.9
80 | 68 | 413 | 67 | kW | 1.15
86 | 68 | 413 | 72 | MBh | 17.51
86 | 68 | 413 | 72 | S/T | 0.619
86 | 68 | 413 | 72 | ∆T | 24.3
86 | 68 | 413 | 72 | LDB | 61.7
86 | 68 | 413 | 72 | LWB | 59.7
86 | 68 | 413 | 72 | kW | 1.16
90 | 68 | 413 | 75 | MBh | 18.19
90 | 68 | 413 | 75 | S/T | 0.579
90 | 68 | 413 | 75 | ∆T | 23.6
90 | 68 | 413 | 75 | LDB | 66.4
90 | 68 | 413 | 75 | LWB | 63.1
90 | 68 | 413 | 75 | kW | 1.17
68 | 86 | 413 | 57 | MBh | 13.46
68 | 86 | 413 | 57 | S/T | 0.729
68 | 86 | 413 | 57 | ∆T | 22
68 | 86 | 413 | 57 | LDB | 46
68 | 86 | 413 | 57 | LWB | 44
68 | 86 | 413 | 57 | kW | 1.35
72 | 86 | 413 | 61 | MBh | 14.14
72 | 86 | 413 | 61 | S/T | 0.684
72 | 86 | 413 | 61 | ∆T | 21.7
72 | 86 | 413 | 61 | LDB | 50.3
72 | 86 | 413 | 61 | LWB | 48.5
72 | 86 | 413 | 61 | kW | 1.36
77 | 86 | 413 | 64 | MBh | 14.81
77 | 86 | 413 | 64 | S/T | 0.684
77 | 86 | 413 | 64 | ∆T | 22.7
77 | 86 | 413 | 64 | LDB | 54.3
77 | 86 | 413 | 64 | LWB | 51.7
77 | 86 | 413 | 64 | kW | 1.37
80 | 86 | 413 | 67 | MBh | 15.28
80 | 86 | 413 | 67 | S/T | 0.666
80 | 86 | 413 | 67 | ∆T | 22.8
80 | 86 | 413 | 67 | LDB | 57.2
80 | 86 | 413 | 67 | LWB | 55.1
80 | 86 | 413 | 67 | kW | 1.37
86 | 86 | 413 | 72 | MBh | 16.15
86 | 86 | 413 | 72 | S/T | 0.638
86 | 86 | 413 | 72 | ∆T | 23.1
86 | 86 | 413 | 72 | LDB | 62.9
86 | 86 | 413 | 72 | LWB | 60.8
86 | 86 | 413 | 72 | kW | 1.38
90 | 86 | 413 | 75 | MBh | 16.83
90 | 86 | 413 | 75 | S/T | 0.597
90 | 86 | 413 | 75 | ∆T | 22.5
90 | 86 | 413 | 75 | LDB | 67.5
90 | 86 | 413 | 75 | LWB | 64.1
90 | 86 | 413 | 75 | kW | 1.39
68 | 95 | 413 | 57 | MBh | 12.78
68 | 95 | 413 | 57 | S/T | 0.74
68 | 95 | 413 | 57 | ∆T | 21.2
68 | 95 | 413 | 57 | LDB | 46.8
68 | 95 | 413 | 57 | LWB | 44.8
68 | 95 | 413 | 57 | kW | 1.46
72 | 95 | 413 | 61 | MBh | 13.46
72 | 95 | 413 | 61 | S/T | 0.694
72 | 95 | 413 | 61 | ∆T | 20.9
72 | 95 | 413 | 61 | LDB | 51.1
72 | 95 | 413 | 61 | LWB | 49.1
72 | 95 | 413 | 61 | kW | 1.47
77 | 95 | 413 | 64 | MBh | 14.13
77 | 95 | 413 | 64 | S/T | 0.695
77 | 95 | 413 | 64 | ∆T | 22
77 | 95 | 413 | 64 | LDB | 55
77 | 95 | 413 | 64 | LWB | 52.3
77 | 95 | 413 | 64 | kW | 1.48
80 | 95 | 413 | 67 | MBh | 14.6
80 | 95 | 413 | 67 | S/T | 0.677
80 | 95 | 413 | 67 | ∆T | 22.2
80 | 95 | 413 | 67 | LDB | 57.8
80 | 95 | 413 | 67 | LWB | 55.7
80 | 95 | 413 | 67 | kW | 1.48
86 | 95 | 413 | 72 | MBh | 15.47
86 | 95 | 413 | 72 | S/T | 0.649
86 | 95 | 413 | 72 | ∆T | 22.5
86 | 95 | 413 | 72 | LDB | 63.5
86 | 95 | 413 | 72 | LWB | 61.3
86 | 95 | 413 | 72 | kW | 1.49
90 | 95 | 413 | 75 | MBh | 16.15
90 | 95 | 413 | 75 | S/T | 0.607
90 | 95 | 413 | 75 | ∆T | 22
90 | 95 | 413 | 75 | LDB | 68
90 | 95 | 413 | 75 | LWB | 64.6
90 | 95 | 413 | 75 | kW | 1.5
68 | 104 | 413 | 57 | MBh | 12.1
68 | 104 | 413 | 57 | S/T | 0.754
68 | 104 | 413 | 57 | ∆T | 20.4
68 | 104 | 413 | 57 | LDB | 47.6
68 | 104 | 413 | 57 | LWB | 45.5
68 | 104 | 413 | 57 | kW | 1.51
72 | 104 | 413 | 61 | MBh | 12.78
72 | 104 | 413 | 61 | S/T | 0.706
72 | 104 | 413 | 61 | ∆T | 20.2
72 | 104 | 413 | 61 | LDB | 51.8
72 | 104 | 413 | 61 | LWB | 49.8
72 | 104 | 413 | 61 | kW | 1.51
77 | 104 | 413 | 64 | MBh | 13.45
77 | 104 | 413 | 64 | S/T | 0.708
77 | 104 | 413 | 64 | ∆T | 21.3
77 | 104 | 413 | 64 | LDB | 55.7
77 | 104 | 413 | 64 | LWB | 52.9
77 | 104 | 413 | 64 | kW | 1.51
80 | 104 | 413 | 67 | MBh | 14.6
80 | 104 | 413 | 67 | S/T | 0.658
80 | 104 | 413 | 67 | ∆T | 21.5
80 | 104 | 413 | 67 | LDB | 58.5
80 | 104 | 413 | 67 | LWB | 55.7
80 | 104 | 413 | 67 | kW | 1.51
86 | 104 | 413 | 72 | MBh | 14.78
86 | 104 | 413 | 72 | S/T | 0.662
86 | 104 | 413 | 72 | ∆T | 21.9
86 | 104 | 413 | 72 | LDB | 64.1
86 | 104 | 413 | 72 | LWB | 61.8
86 | 104 | 413 | 72 | kW | 1.51
90 | 104 | 413 | 75 | MBh | 15.42
90 | 104 | 413 | 75 | S/T | 0.619
90 | 104 | 413 | 75 | ∆T | 21.4
90 | 104 | 413 | 75 | LDB | 68.6
90 | 104 | 413 | 75 | LWB | 65.1
90 | 104 | 413 | 75 | kW | 1.51
68 | 115 | 413 | 57 | MBh | 11.29
68 | 115 | 413 | 57 | S/T | 0.772
68 | 115 | 413 | 57 | ∆T | 19.5
68 | 115 | 413 | 57 | LDB | 48.5
68 | 115 | 413 | 57 | LWB | 46.3
68 | 115 | 413 | 57 | kW | 1.19
72 | 115 | 413 | 61 | MBh | 11.96
72 | 115 | 413 | 61 | S/T | 0.722
72 | 115 | 413 | 61 | ∆T | 19.4
72 | 115 | 413 | 61 | LDB | 52.6
72 | 115 | 413 | 61 | LWB | 50.6
72 | 115 | 413 | 61 | kW | 1.19
77 | 115 | 413 | 64 | MBh | 12.63
77 | 115 | 413 | 64 | S/T | 0.726
77 | 115 | 413 | 64 | ∆T | 20.6
77 | 115 | 413 | 64 | LDB | 56.4
77 | 115 | 413 | 64 | LWB | 53.7
77 | 115 | 413 | 64 | kW | 1.19
80 | 115 | 413 | 67 | MBh | 13.1
80 | 115 | 413 | 67 | S/T | 0.707
80 | 115 | 413 | 67 | ∆T | 20.8
80 | 115 | 413 | 67 | LDB | 59.2
80 | 115 | 413 | 67 | LWB | 57
80 | 115 | 413 | 67 | kW | 1.19
86 | 115 | 413 | 72 | MBh | 13.98
86 | 115 | 413 | 72 | S/T | 0.679
86 | 115 | 413 | 72 | ∆T | 21.3
86 | 115 | 413 | 72 | LDB | 64.7
86 | 115 | 413 | 72 | LWB | 62.4
86 | 115 | 413 | 72 | kW | 1.19
90 | 115 | 413 | 75 | MBh | 14.65
90 | 115 | 413 | 75 | S/T | 0.634
90 | 115 | 413 | 75 | ∆T | 20.8
90 | 115 | 413 | 75 | LDB | 69.2
90 | 115 | 413 | 75 | LWB | 65.7
90 | 115 | 413 | 75 | kW | 1.19
68 | 118 | 413 | 57 | MBh | 6.17
68 | 118 | 413 | 57 | S/T | 0.577
68 | 118 | 413 | 57 | ∆T | 8
68 | 118 | 413 | 57 | LDB | 60
68 | 118 | 413 | 57 | LWB | 51.5
68 | 118 | 413 | 57 | kW | 0.61
72 | 118 | 413 | 61 | MBh | 6.55
72 | 118 | 413 | 61 | S/T | 0.539
72 | 118 | 413 | 61 | ∆T | 7.9
72 | 118 | 413 | 61 | LDB | 64.1
72 | 118 | 413 | 61 | LWB | 55.6
72 | 118 | 413 | 61 | kW | 0.61
77 | 118 | 413 | 64 | MBh | 6.93
77 | 118 | 413 | 64 | S/T | 0.556
77 | 118 | 413 | 64 | ∆T | 8.6
77 | 118 | 413 | 64 | LDB | 68.4
77 | 118 | 413 | 64 | LWB | 58.6
77 | 118 | 413 | 64 | kW | 0.61
80 | 118 | 413 | 67 | MBh | 7.19
80 | 118 | 413 | 67 | S/T | 0.545
80 | 118 | 413 | 67 | ∆T | 8.8
80 | 118 | 413 | 67 | LDB | 71.2
80 | 118 | 413 | 67 | LWB | 61.8
80 | 118 | 413 | 67 | kW | 0.61
86 | 118 | 413 | 72 | MBh | 7.68
86 | 118 | 413 | 72 | S/T | 0.534
86 | 118 | 413 | 72 | ∆T | 9.2
86 | 118 | 413 | 72 | LDB | 76.8
86 | 118 | 413 | 72 | LWB | 67
86 | 118 | 413 | 72 | kW | 0.61
90 | 118 | 413 | 75 | MBh | 8.06
90 | 118 | 413 | 75 | S/T | 0.502
90 | 118 | 413 | 75 | ∆T | 9.1
90 | 118 | 413 | 75 | LDB | 80.9
90 | 118 | 413 | 75 | LWB | 70.1
90 | 118 | 413 | 75 | kW | 0.61

## RKF18BVJU9 - FTKF18BVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT
68 | 50 | 565 | 57 | MBh | 21.8
68 | 50 | 565 | 57 | S/T | 0.704
68 | 50 | 565 | 57 | ∆T | 25.2
68 | 50 | 565 | 57 | LDB | 42.8
68 | 50 | 565 | 57 | LWB | 41.3
68 | 50 | 565 | 57 | kW | 0.92
72 | 50 | 565 | 61 | MBh | 25.41
72 | 50 | 565 | 61 | S/T | 0.647
72 | 50 | 565 | 61 | ∆T | 26.9
72 | 50 | 565 | 61 | LDB | 45.1
72 | 50 | 565 | 61 | LWB | 43.8
72 | 50 | 565 | 61 | kW | 1.12
77 | 50 | 565 | 64 | MBh | 26.42
77 | 50 | 565 | 64 | S/T | 0.641
77 | 50 | 565 | 64 | ∆T | 27.7
77 | 50 | 565 | 64 | LDB | 49.3
77 | 50 | 565 | 64 | LWB | 47.2
77 | 50 | 565 | 64 | kW | 1.13
80 | 50 | 565 | 67 | MBh | 27.13
80 | 50 | 565 | 67 | S/T | 0.622
80 | 50 | 565 | 67 | ∆T | 27.7
80 | 50 | 565 | 67 | LDB | 52.3
80 | 50 | 565 | 67 | LWB | 50.9
80 | 50 | 565 | 67 | kW | 1.13
86 | 50 | 565 | 72 | MBh | 28.45
86 | 50 | 565 | 72 | S/T | 0.593
86 | 50 | 565 | 72 | ∆T | 27.6
86 | 50 | 565 | 72 | LDB | 58.4
86 | 50 | 565 | 72 | LWB | 57
86 | 50 | 565 | 72 | kW | 1.15
90 | 50 | 565 | 75 | MBh | 29.46
90 | 50 | 565 | 75 | S/T | 0.554
90 | 50 | 565 | 75 | ∆T | 26.7
90 | 50 | 565 | 75 | LDB | 63.3
90 | 50 | 565 | 75 | LWB | 60.6
90 | 50 | 565 | 75 | kW | 1.15
68 | 68 | 565 | 57 | MBh | 21.8
68 | 68 | 565 | 57 | S/T | 0.704
68 | 68 | 565 | 57 | ∆T | 25.2
68 | 68 | 565 | 57 | LDB | 42.8
68 | 68 | 565 | 57 | LWB | 41.3
68 | 68 | 565 | 57 | kW | 1.31
72 | 68 | 565 | 61 | MBh | 23.36
72 | 68 | 565 | 61 | S/T | 0.658
72 | 68 | 565 | 61 | ∆T | 25.2
72 | 68 | 565 | 61 | LDB | 46.8
72 | 68 | 565 | 61 | LWB | 45.4
72 | 68 | 565 | 61 | kW | 1.39
77 | 68 | 565 | 64 | MBh | 24.37
77 | 68 | 565 | 64 | S/T | 0.654
77 | 68 | 565 | 64 | ∆T | 26.1
77 | 68 | 565 | 64 | LDB | 50.9
77 | 68 | 565 | 64 | LWB | 48.7
77 | 68 | 565 | 64 | kW | 1.4
80 | 68 | 565 | 67 | MBh | 25.08
80 | 68 | 565 | 67 | S/T | 0.636
80 | 68 | 565 | 67 | ∆T | 26.1
80 | 68 | 565 | 67 | LDB | 53.9
80 | 68 | 565 | 67 | LWB | 52.3
80 | 68 | 565 | 67 | kW | 1.4
86 | 68 | 565 | 72 | MBh | 26.4
86 | 68 | 565 | 72 | S/T | 0.607
86 | 68 | 565 | 72 | ∆T | 26.3
86 | 68 | 565 | 72 | LDB | 59.7
86 | 68 | 565 | 72 | LWB | 58.3
86 | 68 | 565 | 72 | kW | 1.41
90 | 68 | 565 | 75 | MBh | 27.41
90 | 68 | 565 | 75 | S/T | 0.567
90 | 68 | 565 | 75 | ∆T | 25.5
90 | 68 | 565 | 75 | LDB | 64.5
90 | 68 | 565 | 75 | LWB | 61.7
90 | 68 | 565 | 75 | kW | 1.42
68 | 86 | 565 | 57 | MBh | 20.29
68 | 86 | 565 | 57 | S/T | 0.718
68 | 86 | 565 | 57 | ∆T | 23.9
68 | 86 | 565 | 57 | LDB | 44.1
68 | 86 | 565 | 57 | LWB | 42.5
68 | 86 | 565 | 57 | kW | 1.65
72 | 86 | 565 | 61 | MBh | 21.31
72 | 86 | 565 | 61 | S/T | 0.673
72 | 86 | 565 | 61 | ∆T | 23.5
72 | 86 | 565 | 61 | LDB | 48.5
72 | 86 | 565 | 61 | LWB | 47
72 | 86 | 565 | 61 | kW | 1.65
77 | 86 | 565 | 64 | MBh | 22.32
77 | 86 | 565 | 64 | S/T | 0.672
77 | 86 | 565 | 64 | ∆T | 24.6
77 | 86 | 565 | 64 | LDB | 52.4
77 | 86 | 565 | 64 | LWB | 50.2
77 | 86 | 565 | 64 | kW | 1.66
80 | 86 | 565 | 67 | MBh | 23.03
80 | 86 | 565 | 67 | S/T | 0.653
80 | 86 | 565 | 67 | ∆T | 24.6
80 | 86 | 565 | 67 | LDB | 55.4
80 | 86 | 565 | 67 | LWB | 53.7
80 | 86 | 565 | 67 | kW | 1.67
86 | 86 | 565 | 72 | MBh | 24.35
86 | 86 | 565 | 72 | S/T | 0.624
86 | 86 | 565 | 72 | ∆T | 24.9
86 | 86 | 565 | 72 | LDB | 61.1
86 | 86 | 565 | 72 | LWB | 59.5
86 | 86 | 565 | 72 | kW | 1.68
90 | 86 | 565 | 75 | MBh | 25.36
90 | 86 | 565 | 75 | S/T | 0.584
90 | 86 | 565 | 75 | ∆T | 24.3
90 | 86 | 565 | 75 | LDB | 65.7
90 | 86 | 565 | 75 | LWB | 62.9
90 | 86 | 565 | 75 | kW | 1.69
68 | 95 | 565 | 57 | MBh | 19.27
68 | 95 | 565 | 57 | S/T | 0.728
68 | 95 | 565 | 57 | ∆T | 23
68 | 95 | 565 | 57 | LDB | 45
68 | 95 | 565 | 57 | LWB | 43.3
68 | 95 | 565 | 57 | kW | 1.78
72 | 95 | 565 | 61 | MBh | 20.28
72 | 95 | 565 | 61 | S/T | 0.683
72 | 95 | 565 | 61 | ∆T | 22.7
72 | 95 | 565 | 61 | LDB | 49.3
72 | 95 | 565 | 61 | LWB | 47.8
72 | 95 | 565 | 61 | kW | 1.79
77 | 95 | 565 | 64 | MBh | 21.3
77 | 95 | 565 | 64 | S/T | 0.682
77 | 95 | 565 | 64 | ∆T | 23.8
77 | 95 | 565 | 64 | LDB | 53.2
77 | 95 | 565 | 64 | LWB | 50.9
77 | 95 | 565 | 64 | kW | 1.79
80 | 95 | 565 | 67 | MBh | 22
80 | 95 | 565 | 67 | S/T | 0.663
80 | 95 | 565 | 67 | ∆T | 23.9
80 | 95 | 565 | 67 | LDB | 56.1
80 | 95 | 565 | 67 | LWB | 54.4
80 | 95 | 565 | 67 | kW | 1.8
86 | 95 | 565 | 72 | MBh | 23.33
86 | 95 | 565 | 72 | S/T | 0.634
86 | 95 | 565 | 72 | ∆T | 24.3
86 | 95 | 565 | 72 | LDB | 61.7
86 | 95 | 565 | 72 | LWB | 60.1
86 | 95 | 565 | 72 | kW | 1.81
90 | 95 | 565 | 75 | MBh | 24.34
90 | 95 | 565 | 75 | S/T | 0.593
90 | 95 | 565 | 75 | ∆T | 23.7
90 | 95 | 565 | 75 | LDB | 66.3
90 | 95 | 565 | 75 | LWB | 63.4
90 | 95 | 565 | 75 | kW | 1.82
68 | 104 | 565 | 57 | MBh | 18.25
68 | 104 | 565 | 57 | S/T | 0.74
68 | 104 | 565 | 57 | ∆T | 22.1
68 | 104 | 565 | 57 | LDB | 45.9
68 | 104 | 565 | 57 | LWB | 44.2
68 | 104 | 565 | 57 | kW | 1.91
72 | 104 | 565 | 61 | MBh | 19.26
72 | 104 | 565 | 61 | S/T | 0.694
72 | 104 | 565 | 61 | ∆T | 21.9
72 | 104 | 565 | 61 | LDB | 50.1
72 | 104 | 565 | 61 | LWB | 48.5
72 | 104 | 565 | 61 | kW | 1.92
77 | 104 | 565 | 64 | MBh | 20.27
77 | 104 | 565 | 64 | S/T | 0.694
77 | 104 | 565 | 64 | ∆T | 23
77 | 104 | 565 | 64 | LDB | 54
77 | 104 | 565 | 64 | LWB | 51.6
77 | 104 | 565 | 64 | kW | 1.93
80 | 104 | 565 | 67 | MBh | 22
80 | 104 | 565 | 67 | S/T | 0.644
80 | 104 | 565 | 67 | ∆T | 23.2
80 | 104 | 565 | 67 | LDB | 56.8
80 | 104 | 565 | 67 | LWB | 54.4
80 | 104 | 565 | 67 | kW | 1.93
86 | 104 | 565 | 72 | MBh | 22.3
86 | 104 | 565 | 72 | S/T | 0.646
86 | 104 | 565 | 72 | ∆T | 23.6
86 | 104 | 565 | 72 | LDB | 62.4
86 | 104 | 565 | 72 | LWB | 60.7
86 | 104 | 565 | 72 | kW | 1.94
90 | 104 | 565 | 75 | MBh | 23.31
90 | 104 | 565 | 75 | S/T | 0.604
90 | 104 | 565 | 75 | ∆T | 23.1
90 | 104 | 565 | 75 | LDB | 66.9
90 | 104 | 565 | 75 | LWB | 64
90 | 104 | 565 | 75 | kW | 1.95
68 | 115 | 565 | 57 | MBh | 17.02
68 | 115 | 565 | 57 | S/T | 0.757
68 | 115 | 565 | 57 | ∆T | 21.1
68 | 115 | 565 | 57 | LDB | 46.9
68 | 115 | 565 | 57 | LWB | 45.1
68 | 115 | 565 | 57 | kW | 2.07
72 | 115 | 565 | 61 | MBh | 18.03
72 | 115 | 565 | 61 | S/T | 0.709
72 | 115 | 565 | 61 | ∆T | 20.9
72 | 115 | 565 | 61 | LDB | 51.1
72 | 115 | 565 | 61 | LWB | 49.4
72 | 115 | 565 | 61 | kW | 2.08
77 | 115 | 565 | 64 | MBh | 19.04
77 | 115 | 565 | 64 | S/T | 0.71
77 | 115 | 565 | 64 | ∆T | 22.2
77 | 115 | 565 | 64 | LDB | 54.8
77 | 115 | 565 | 64 | LWB | 52.5
77 | 115 | 565 | 64 | kW | 2.09
80 | 115 | 565 | 67 | MBh | 19.75
80 | 115 | 565 | 67 | S/T | 0.691
80 | 115 | 565 | 67 | ∆T | 22.4
80 | 115 | 565 | 67 | LDB | 57.6
80 | 115 | 565 | 67 | LWB | 55.8
80 | 115 | 565 | 67 | kW | 2.09
86 | 115 | 565 | 72 | MBh | 21.07
86 | 115 | 565 | 72 | S/T | 0.662
86 | 115 | 565 | 72 | ∆T | 22.9
86 | 115 | 565 | 72 | LDB | 63.1
86 | 115 | 565 | 72 | LWB | 61.4
86 | 115 | 565 | 72 | kW | 2.1
90 | 115 | 565 | 75 | MBh | 22.09
90 | 115 | 565 | 75 | S/T | 0.618
90 | 115 | 565 | 75 | ∆T | 22.4
90 | 115 | 565 | 75 | LDB | 67.6
90 | 115 | 565 | 75 | LWB | 64.6
90 | 115 | 565 | 75 | kW | 2.11
68 | 122 | 565 | 57 | MBh | 8.1
68 | 122 | 565 | 57 | S/T | 0.54
68 | 122 | 565 | 57 | ∆T | 7.2
68 | 122 | 565 | 57 | LDB | 60.8
68 | 122 | 565 | 57 | LWB | 51.7
68 | 122 | 565 | 57 | kW | 0.87
72 | 122 | 565 | 61 | MBh | 8.6
72 | 122 | 565 | 61 | S/T | 0.505
72 | 122 | 565 | 61 | ∆T | 7.1
72 | 122 | 565 | 61 | LDB | 64.9
72 | 122 | 565 | 61 | LWB | 55.8
72 | 122 | 565 | 61 | kW | 0.87
77 | 122 | 565 | 64 | MBh | 9.11
77 | 122 | 565 | 64 | S/T | 0.521
77 | 122 | 565 | 64 | ∆T | 7.8
77 | 122 | 565 | 64 | LDB | 69.2
77 | 122 | 565 | 64 | LWB | 58.8
77 | 122 | 565 | 64 | kW | 0.87
80 | 122 | 565 | 67 | MBh | 9.47
80 | 122 | 565 | 67 | S/T | 0.512
80 | 122 | 565 | 67 | ∆T | 7.9
80 | 122 | 565 | 67 | LDB | 72.1
80 | 122 | 565 | 67 | LWB | 62
80 | 122 | 565 | 67 | kW | 0.87
86 | 122 | 565 | 72 | MBh | 10.13
86 | 122 | 565 | 72 | S/T | 0.502
86 | 122 | 565 | 72 | ∆T | 8.3
86 | 122 | 565 | 72 | LDB | 77.7
86 | 122 | 565 | 72 | LWB | 67.2
86 | 122 | 565 | 72 | kW | 0.87
90 | 122 | 565 | 75 | MBh | 10.63
90 | 122 | 565 | 75 | S/T | 0.473
90 | 122 | 565 | 75 | ∆T | 8.2
90 | 122 | 565 | 75 | LDB | 81.8
90 | 122 | 565 | 75 | LWB | 70.3
90 | 122 | 565 | 75 | kW | 0.87

## RKF24BVJU9 - FTKF24BVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT
68 | 50 | 629 | 57 | MBh | 22.31
68 | 50 | 629 | 57 | S/T | 0.704
68 | 50 | 629 | 57 | ∆T | 23.1
68 | 50 | 629 | 57 | LDB | 44.9
68 | 50 | 629 | 57 | LWB | 42.7
68 | 50 | 629 | 57 | kW | 1
72 | 50 | 629 | 61 | MBh | 27.4
72 | 50 | 629 | 61 | S/T | 0.641
72 | 50 | 629 | 61 | ∆T | 25.8
72 | 50 | 629 | 61 | LDB | 46.2
72 | 50 | 629 | 61 | LWB | 44.5
72 | 50 | 629 | 61 | kW | 1.29
77 | 50 | 629 | 64 | MBh | 31.71
77 | 50 | 629 | 64 | S/T | 0.621
77 | 50 | 629 | 64 | ∆T | 29
77 | 50 | 629 | 64 | LDB | 48
77 | 50 | 629 | 64 | LWB | 45.7
77 | 50 | 629 | 64 | kW | 1.54
80 | 50 | 629 | 67 | MBh | 32.56
80 | 50 | 629 | 67 | S/T | 0.602
80 | 50 | 629 | 67 | ∆T | 28.8
80 | 50 | 629 | 67 | LDB | 51.2
80 | 50 | 629 | 67 | LWB | 49.4
80 | 50 | 629 | 67 | kW | 1.55
86 | 50 | 629 | 72 | MBh | 34.14
86 | 50 | 629 | 72 | S/T | 0.57
86 | 50 | 629 | 72 | ∆T | 28.6
86 | 50 | 629 | 72 | LDB | 57.4
86 | 50 | 629 | 72 | LWB | 55.6
86 | 50 | 629 | 72 | kW | 1.56
90 | 50 | 629 | 75 | MBh | 35.36
90 | 50 | 629 | 75 | S/T | 0.531
90 | 50 | 629 | 75 | ∆T | 27.6
90 | 50 | 629 | 75 | LDB | 62.4
90 | 50 | 629 | 75 | LWB | 59.2
90 | 50 | 629 | 75 | kW | 1.58
68 | 68 | 629 | 57 | MBh | 22.31
68 | 68 | 629 | 57 | S/T | 0.704
68 | 68 | 629 | 57 | ∆T | 23.1
68 | 68 | 629 | 57 | LDB | 44.9
68 | 68 | 629 | 57 | LWB | 42.7
68 | 68 | 629 | 57 | kW | 1.37
72 | 68 | 629 | 61 | MBh | 27.4
72 | 68 | 629 | 61 | S/T | 0.641
72 | 68 | 629 | 61 | ∆T | 25.8
72 | 68 | 629 | 61 | LDB | 46.2
72 | 68 | 629 | 61 | LWB | 44.5
72 | 68 | 629 | 61 | kW | 1.82
77 | 68 | 629 | 64 | MBh | 29.25
77 | 68 | 629 | 64 | S/T | 0.63
77 | 68 | 629 | 64 | ∆T | 27.1
77 | 68 | 629 | 64 | LDB | 49.9
77 | 68 | 629 | 64 | LWB | 47.3
77 | 68 | 629 | 64 | kW | 1.91
80 | 68 | 629 | 67 | MBh | 30.1
80 | 68 | 629 | 67 | S/T | 0.611
80 | 68 | 629 | 67 | ∆T | 27.1
80 | 68 | 629 | 67 | LDB | 52.9
80 | 68 | 629 | 67 | LWB | 51
80 | 68 | 629 | 67 | kW | 1.91
86 | 68 | 629 | 72 | MBh | 31.68
86 | 68 | 629 | 72 | S/T | 0.58
86 | 68 | 629 | 72 | ∆T | 27
86 | 68 | 629 | 72 | LDB | 59
86 | 68 | 629 | 72 | LWB | 57
86 | 68 | 629 | 72 | kW | 1.93
90 | 68 | 629 | 75 | MBh | 32.9
90 | 68 | 629 | 75 | S/T | 0.54
90 | 68 | 629 | 75 | ∆T | 26.2
90 | 68 | 629 | 75 | LDB | 63.8
90 | 68 | 629 | 75 | LWB | 60.5
90 | 68 | 629 | 75 | kW | 1.94
68 | 86 | 629 | 57 | MBh | 22.31
68 | 86 | 629 | 57 | S/T | 0.704
68 | 86 | 629 | 57 | ∆T | 23.1
68 | 86 | 629 | 57 | LDB | 44.9
68 | 86 | 629 | 57 | LWB | 42.7
68 | 86 | 629 | 57 | kW | 1.9
72 | 86 | 629 | 61 | MBh | 25.57
72 | 86 | 629 | 61 | S/T | 0.649
72 | 86 | 629 | 61 | ∆T | 24.4
72 | 86 | 629 | 61 | LDB | 47.6
72 | 86 | 629 | 61 | LWB | 45.7
72 | 86 | 629 | 61 | kW | 2.26
77 | 86 | 629 | 64 | MBh | 26.79
77 | 86 | 629 | 64 | S/T | 0.642
77 | 86 | 629 | 64 | ∆T | 25.3
77 | 86 | 629 | 64 | LDB | 51.7
77 | 86 | 629 | 64 | LWB | 49
77 | 86 | 629 | 64 | kW | 2.27
80 | 86 | 629 | 67 | MBh | 27.64
80 | 86 | 629 | 67 | S/T | 0.623
80 | 86 | 629 | 67 | ∆T | 25.3
80 | 86 | 629 | 67 | LDB | 54.7
80 | 86 | 629 | 67 | LWB | 52.5
80 | 86 | 629 | 67 | kW | 2.28
86 | 86 | 629 | 72 | MBh | 29.22
86 | 86 | 629 | 72 | S/T | 0.592
86 | 86 | 629 | 72 | ∆T | 25.5
86 | 86 | 629 | 72 | LDB | 60.5
86 | 86 | 629 | 72 | LWB | 58.4
86 | 86 | 629 | 72 | kW | 2.29
90 | 86 | 629 | 75 | MBh | 30.44
90 | 86 | 629 | 75 | S/T | 0.553
90 | 86 | 629 | 75 | ∆T | 24.8
90 | 86 | 629 | 75 | LDB | 65.2
90 | 86 | 629 | 75 | LWB | 61.8
90 | 86 | 629 | 75 | kW | 2.3
68 | 95 | 629 | 57 | MBh | 22.31
68 | 95 | 629 | 57 | S/T | 0.704
68 | 95 | 629 | 57 | ∆T | 23.1
68 | 95 | 629 | 57 | LDB | 44.9
68 | 95 | 629 | 57 | LWB | 42.7
68 | 95 | 629 | 57 | kW | 2.26
72 | 95 | 629 | 61 | MBh | 24.34
72 | 95 | 629 | 61 | S/T | 0.655
72 | 95 | 629 | 61 | ∆T | 23.5
72 | 95 | 629 | 61 | LDB | 48.5
72 | 95 | 629 | 61 | LWB | 46.6
72 | 95 | 629 | 61 | kW | 2.44
77 | 95 | 629 | 64 | MBh | 25.56
77 | 95 | 629 | 64 | S/T | 0.65
77 | 95 | 629 | 64 | ∆T | 24.5
77 | 95 | 629 | 64 | LDB | 52.5
77 | 95 | 629 | 64 | LWB | 49.8
77 | 95 | 629 | 64 | kW | 2.45
80 | 95 | 629 | 67 | MBh | 26.4
80 | 95 | 629 | 67 | S/T | 0.631
80 | 95 | 629 | 67 | ∆T | 24.5
80 | 95 | 629 | 67 | LDB | 55.5
80 | 95 | 629 | 67 | LWB | 53.3
80 | 95 | 629 | 67 | kW | 2.46
86 | 95 | 629 | 72 | MBh | 27.99
86 | 95 | 629 | 72 | S/T | 0.6
86 | 95 | 629 | 72 | ∆T | 24.7
86 | 95 | 629 | 72 | LDB | 61.3
86 | 95 | 629 | 72 | LWB | 59
86 | 95 | 629 | 72 | kW | 2.47
90 | 95 | 629 | 75 | MBh | 29.21
90 | 95 | 629 | 75 | S/T | 0.56
90 | 95 | 629 | 75 | ∆T | 24.1
90 | 95 | 629 | 75 | LDB | 65.9
90 | 95 | 629 | 75 | LWB | 62.4
90 | 95 | 629 | 75 | kW | 2.49
68 | 104 | 629 | 57 | MBh | 21.89
68 | 104 | 629 | 57 | S/T | 0.708
68 | 104 | 629 | 57 | ∆T | 22.8
68 | 104 | 629 | 57 | LDB | 45.2
68 | 104 | 629 | 57 | LWB | 43
68 | 104 | 629 | 57 | kW | 2.61
72 | 104 | 629 | 61 | MBh | 23.11
72 | 104 | 629 | 61 | S/T | 0.663
72 | 104 | 629 | 61 | ∆T | 22.6
72 | 104 | 629 | 61 | LDB | 49.4
72 | 104 | 629 | 61 | LWB | 47.4
72 | 104 | 629 | 61 | kW | 2.62
77 | 104 | 629 | 64 | MBh | 24.33
77 | 104 | 629 | 64 | S/T | 0.659
77 | 104 | 629 | 64 | ∆T | 23.6
77 | 104 | 629 | 64 | LDB | 53.4
77 | 104 | 629 | 64 | LWB | 50.5
77 | 104 | 629 | 64 | kW | 2.63
80 | 104 | 629 | 67 | MBh | 26.4
80 | 104 | 629 | 67 | S/T | 0.61
80 | 104 | 629 | 67 | ∆T | 23.7
80 | 104 | 629 | 67 | LDB | 56.3
80 | 104 | 629 | 67 | LWB | 53.3
80 | 104 | 629 | 67 | kW | 2.64
86 | 104 | 629 | 72 | MBh | 26.76
86 | 104 | 629 | 72 | S/T | 0.609
86 | 104 | 629 | 72 | ∆T | 24
86 | 104 | 629 | 72 | LDB | 62
86 | 104 | 629 | 72 | LWB | 59.7
86 | 104 | 629 | 72 | kW | 2.66
90 | 104 | 629 | 75 | MBh | 27.98
90 | 104 | 629 | 75 | S/T | 0.568
90 | 104 | 629 | 75 | ∆T | 23.4
90 | 104 | 629 | 75 | LDB | 66.6
90 | 104 | 629 | 75 | LWB | 63
90 | 104 | 629 | 75 | kW | 2.67
68 | 115 | 629 | 57 | MBh | 20.42
68 | 115 | 629 | 57 | S/T | 0.72
68 | 115 | 629 | 57 | ∆T | 21.7
68 | 115 | 629 | 57 | LDB | 46.3
68 | 115 | 629 | 57 | LWB | 44.1
68 | 115 | 629 | 57 | kW | 2.26
72 | 115 | 629 | 61 | MBh | 21.64
72 | 115 | 629 | 61 | S/T | 0.675
72 | 115 | 629 | 61 | ∆T | 21.5
72 | 115 | 629 | 61 | LDB | 50.5
72 | 115 | 629 | 61 | LWB | 48.4
72 | 115 | 629 | 61 | kW | 2.26
77 | 115 | 629 | 64 | MBh | 22.85
77 | 115 | 629 | 64 | S/T | 0.671
77 | 115 | 629 | 64 | ∆T | 22.6
77 | 115 | 629 | 64 | LDB | 54.4
77 | 115 | 629 | 64 | LWB | 51.5
77 | 115 | 629 | 64 | kW | 2.26
80 | 115 | 629 | 67 | MBh | 23.7
80 | 115 | 629 | 67 | S/T | 0.652
80 | 115 | 629 | 67 | ∆T | 22.7
80 | 115 | 629 | 67 | LDB | 57.3
80 | 115 | 629 | 67 | LWB | 54.8
80 | 115 | 629 | 67 | kW | 2.26
86 | 115 | 629 | 72 | MBh | 25.29
86 | 115 | 629 | 72 | S/T | 0.621
86 | 115 | 629 | 72 | ∆T | 23.1
86 | 115 | 629 | 72 | LDB | 62.9
86 | 115 | 629 | 72 | LWB | 60.4
86 | 115 | 629 | 72 | kW | 2.26
90 | 115 | 629 | 75 | MBh | 26.5
90 | 115 | 629 | 75 | S/T | 0.579
90 | 115 | 629 | 75 | ∆T | 22.6
90 | 115 | 629 | 75 | LDB | 67.4
90 | 115 | 629 | 75 | LWB | 63.7
90 | 115 | 629 | 75 | kW | 2.26
68 | 122 | 629 | 57 | MBh | 8.16
68 | 122 | 629 | 57 | S/T | 0.458
68 | 122 | 629 | 57 | ∆T | 5.5
68 | 122 | 629 | 57 | LDB | 62.5
68 | 122 | 629 | 57 | LWB | 52.2
68 | 122 | 629 | 57 | kW | 0.78
72 | 122 | 629 | 61 | MBh | 8.67
72 | 122 | 629 | 61 | S/T | 0.428
72 | 122 | 629 | 61 | ∆T | 5.5
72 | 122 | 629 | 61 | LDB | 66.5
72 | 122 | 629 | 61 | LWB | 56.3
72 | 122 | 629 | 61 | kW | 0.78
77 | 122 | 629 | 64 | MBh | 9.18
77 | 122 | 629 | 64 | S/T | 0.442
77 | 122 | 629 | 64 | ∆T | 6
77 | 122 | 629 | 64 | LDB | 71
77 | 122 | 629 | 64 | LWB | 59.4
77 | 122 | 629 | 64 | kW | 0.78
80 | 122 | 629 | 67 | MBh | 9.54
80 | 122 | 629 | 67 | S/T | 0.435
80 | 122 | 629 | 67 | ∆T | 6.1
80 | 122 | 629 | 67 | LDB | 73.9
80 | 122 | 629 | 67 | LWB | 62.5
80 | 122 | 629 | 67 | kW | 0.78
86 | 122 | 629 | 72 | MBh | 10.21
86 | 122 | 629 | 72 | S/T | 0.426
86 | 122 | 629 | 72 | ∆T | 6.4
86 | 122 | 629 | 72 | LDB | 79.6
86 | 122 | 629 | 72 | LWB | 67.7
86 | 122 | 629 | 72 | kW | 0.78
90 | 122 | 629 | 75 | MBh | 10.72
90 | 122 | 629 | 75 | S/T | 0.401
90 | 122 | 629 | 75 | ∆T | 6.3
90 | 122 | 629 | 75 | LDB | 83.7
90 | 122 | 629 | 75 | LWB | 70.8
90 | 122 | 629 | 75 | kW | 0.78

## RXF09BVJU9 - FTXF09BVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 381 | 57 | MBh | 12.42 | 75 | 64 | 59 | 21.06 | 1.61
68 | 50 | 381 | 57 | S/T | 0.733 | 75 | 64 | 70 | 20.38 | 1.65
68 | 50 | 381 | 57 | ∆T | 22.1 | 75 | 64 | 72 | 20.28 | 1.65
68 | 50 | 381 | 57 | LDB | 45.9 | 75 | 64 | 75 | 20.06 | 1.67
68 | 50 | 381 | 57 | LWB | 44 | 75 | 64 | 77 | 19.95 | 1.67
68 | 50 | 381 | 57 | kW | 0.6 | 75 | 64 | 81 | 19.25 | 1.61
72 | 50 | 381 | 61 | MBh | 12.93 | 59 | 50 | 59 | 18.16 | 1.51
72 | 50 | 381 | 61 | S/T | 0.689 | 59 | 50 | 70 | 17.49 | 1.55
72 | 50 | 381 | 61 | ∆T | 21.7 | 59 | 50 | 72 | 17.39 | 1.56
72 | 50 | 381 | 61 | LDB | 50.3 | 59 | 50 | 75 | 17.16 | 1.57
72 | 50 | 381 | 61 | LWB | 48.6 | 59 | 50 | 77 | 17.05 | 1.58
72 | 50 | 381 | 61 | kW | 0.61 | 59 | 50 | 81 | 16.83 | 1.59
77 | 50 | 381 | 64 | MBh | 13.45 | 47 | 43 | 59 | 16.71 | 1.46
77 | 50 | 381 | 64 | S/T | 0.691 | 47 | 43 | 70 | 16 | 1.5
77 | 50 | 381 | 64 | ∆T | 22.6 | 47 | 43 | 72 | 15.94 | 1.51
77 | 50 | 381 | 64 | LDB | 54.4 | 47 | 43 | 75 | 15.72 | 1.52
77 | 50 | 381 | 64 | LWB | 51.9 | 47 | 43 | 77 | 15.6 | 1.53
77 | 50 | 381 | 64 | kW | 0.61 | 47 | 43 | 81 | 15.38 | 1.54
80 | 50 | 381 | 67 | MBh | 13.81 | 35 | 32 | 59 | 13.3 | 1.27
80 | 50 | 381 | 67 | S/T | 0.675 | 35 | 32 | 70 | 12.68 | 1.3
80 | 50 | 381 | 67 | ∆T | 22.6 | 35 | 32 | 72 | 12.59 | 1.31
80 | 50 | 381 | 67 | LDB | 57.4 | 35 | 32 | 75 | 12.39 | 1.32
80 | 50 | 381 | 67 | LWB | 55.4 | 35 | 32 | 77 | 12.28 | 1.33
80 | 50 | 381 | 67 | kW | 0.61 | 35 | 32 | 81 | 12.08 | 1.34
86 | 50 | 381 | 72 | MBh | 14.48 | 25 | 23 | 59 | 11.64 | 1.21
86 | 50 | 381 | 72 | S/T | 0.65 | 25 | 23 | 70 | 11.02 | 1.25
86 | 50 | 381 | 72 | ∆T | 22.9 | 25 | 23 | 72 | 10.93 | 1.25
86 | 50 | 381 | 72 | LDB | 63.1 | 25 | 23 | 75 | 10.73 | 1.27
86 | 50 | 381 | 72 | LWB | 61.1 | 25 | 23 | 77 | 10.63 | 1.27
86 | 50 | 381 | 72 | kW | 0.76 | 25 | 23 | 81 | 10.43 | 1.28
90 | 50 | 381 | 75 | MBh | 15 | 16 | 14 | 59 | 9.98 | 1.15
90 | 50 | 381 | 75 | S/T | 0.61 | 16 | 14 | 70 | 9.37 | 1.19
90 | 50 | 381 | 75 | ∆T | 22.2 | 16 | 14 | 72 | 9.28 | 1.2
90 | 50 | 381 | 75 | LDB | 67.8 | 16 | 14 | 75 | 9.07 | 1.21
90 | 50 | 381 | 75 | LWB | 64.5 | 16 | 14 | 77 | 8.97 | 1.22
90 | 50 | 381 | 75 | kW | 0.77 | 16 | 14 | 81 | 8.77 | 1.23
68 | 68 | 381 | 57 | MBh | 11.37 | 5 | 5 | 59 | 8.33 | 1.1
68 | 68 | 381 | 57 | S/T | 0.754 | 5 | 5 | 70 | 7.71 | 1.13
68 | 68 | 381 | 57 | ∆T | 20.8 | 5 | 5 | 72 | 7.62 | 1.14
68 | 68 | 381 | 57 | LDB | 47.2 | 5 | 5 | 75 | 7.42 | 1.15
68 | 68 | 381 | 57 | LWB | 45.2 | 5 | 5 | 77 | 7.32 | 1.16
68 | 68 | 381 | 57 | kW | 0.75 | 5 | 5 | 81 | 7.11 | 1.17
72 | 68 | 381 | 61 | MBh | 11.89
72 | 68 | 381 | 61 | S/T | 0.708
72 | 68 | 381 | 61 | ∆T | 20.5
72 | 68 | 381 | 61 | LDB | 51.5
72 | 68 | 381 | 61 | LWB | 49.7
72 | 68 | 381 | 61 | kW | 0.75
77 | 68 | 381 | 64 | MBh | 12.41
77 | 68 | 381 | 64 | S/T | 0.712
77 | 68 | 381 | 64 | ∆T | 21.5
77 | 68 | 381 | 64 | LDB | 55.5
77 | 68 | 381 | 64 | LWB | 52.9
77 | 68 | 381 | 64 | kW | 0.75
80 | 68 | 381 | 67 | MBh | 12.77
80 | 68 | 381 | 67 | S/T | 0.695
80 | 68 | 381 | 67 | ∆T | 21.6
80 | 68 | 381 | 67 | LDB | 58.4
80 | 68 | 381 | 67 | LWB | 56.3
80 | 68 | 381 | 67 | kW | 0.76
86 | 68 | 381 | 72 | MBh | 13.44
86 | 68 | 381 | 72 | S/T | 0.671
86 | 68 | 381 | 72 | ∆T | 21.9
86 | 68 | 381 | 72 | LDB | 64.1
86 | 68 | 381 | 72 | LWB | 62
86 | 68 | 381 | 72 | kW | 0.76
90 | 68 | 381 | 75 | MBh | 13.95
90 | 68 | 381 | 75 | S/T | 0.63
90 | 68 | 381 | 75 | ∆T | 21.4
90 | 68 | 381 | 75 | LDB | 68.6
90 | 68 | 381 | 75 | LWB | 65.3
90 | 68 | 381 | 75 | kW | 0.77
68 | 86 | 381 | 57 | MBh | 10.33
68 | 86 | 381 | 57 | S/T | 0.779
68 | 86 | 381 | 57 | ∆T | 19.6
68 | 86 | 381 | 57 | LDB | 48.4
68 | 86 | 381 | 57 | LWB | 46.4
68 | 86 | 381 | 57 | kW | 0.89
72 | 86 | 381 | 61 | MBh | 10.85
72 | 86 | 381 | 61 | S/T | 0.732
72 | 86 | 381 | 61 | ∆T | 19.3
72 | 86 | 381 | 61 | LDB | 52.7
72 | 86 | 381 | 61 | LWB | 50.8
72 | 86 | 381 | 61 | kW | 0.89
77 | 86 | 381 | 64 | MBh | 11.36
77 | 86 | 381 | 64 | S/T | 0.739
77 | 86 | 381 | 64 | ∆T | 20.4
77 | 86 | 381 | 64 | LDB | 56.6
77 | 86 | 381 | 64 | LWB | 53.9
77 | 86 | 381 | 64 | kW | 0.9
80 | 86 | 381 | 67 | MBh | 11.72
80 | 86 | 381 | 67 | S/T | 0.722
80 | 86 | 381 | 67 | ∆T | 20.6
80 | 86 | 381 | 67 | LDB | 59.4
80 | 86 | 381 | 67 | LWB | 57.3
80 | 86 | 381 | 67 | kW | 0.9
86 | 86 | 381 | 72 | MBh | 12.39
86 | 86 | 381 | 72 | S/T | 0.697
86 | 86 | 381 | 72 | ∆T | 21
86 | 86 | 381 | 72 | LDB | 65
86 | 86 | 381 | 72 | LWB | 62.9
86 | 86 | 381 | 72 | kW | 0.91
90 | 86 | 381 | 75 | MBh | 12.91
90 | 86 | 381 | 75 | S/T | 0.654
90 | 86 | 381 | 75 | ∆T | 20.5
90 | 86 | 381 | 75 | LDB | 69.5
90 | 86 | 381 | 75 | LWB | 66.1
90 | 86 | 381 | 75 | kW | 0.91
68 | 95 | 381 | 57 | MBh | 9.81
68 | 95 | 381 | 57 | S/T | 0.795
68 | 95 | 381 | 57 | ∆T | 19
68 | 95 | 381 | 57 | LDB | 49
68 | 95 | 381 | 57 | LWB | 47
68 | 95 | 381 | 57 | kW | 0.96
72 | 95 | 381 | 61 | MBh | 10.32
72 | 95 | 381 | 61 | S/T | 0.746
72 | 95 | 381 | 61 | ∆T | 18.7
72 | 95 | 381 | 61 | LDB | 53.3
72 | 95 | 381 | 61 | LWB | 51.3
72 | 95 | 381 | 61 | kW | 0.97
77 | 95 | 381 | 64 | MBh | 10.84
77 | 95 | 381 | 64 | S/T | 0.755
77 | 95 | 381 | 64 | ∆T | 19.9
77 | 95 | 381 | 64 | LDB | 57.1
77 | 95 | 381 | 64 | LWB | 54.5
77 | 95 | 381 | 64 | kW | 0.97
80 | 95 | 381 | 67 | MBh | 11.2
80 | 95 | 381 | 67 | S/T | 0.737
80 | 95 | 381 | 67 | ∆T | 20
80 | 95 | 381 | 67 | LDB | 60
80 | 95 | 381 | 67 | LWB | 57.8
80 | 95 | 381 | 67 | kW | 0.97
86 | 95 | 381 | 72 | MBh | 11.87
86 | 95 | 381 | 72 | S/T | 0.712
86 | 95 | 381 | 72 | ∆T | 20.5
86 | 95 | 381 | 72 | LDB | 65.5
86 | 95 | 381 | 72 | LWB | 63.3
86 | 95 | 381 | 72 | kW | 0.98
90 | 95 | 381 | 75 | MBh | 12.39
90 | 95 | 381 | 75 | S/T | 0.667
90 | 95 | 381 | 75 | ∆T | 20.1
90 | 95 | 381 | 75 | LDB | 69.9
90 | 95 | 381 | 75 | LWB | 66.5
90 | 95 | 381 | 75 | kW | 0.98
68 | 104 | 381 | 57 | MBh | 9.29
68 | 104 | 381 | 57 | S/T | 0.813
68 | 104 | 381 | 57 | ∆T | 18.3
68 | 104 | 381 | 57 | LDB | 49.7
68 | 104 | 381 | 57 | LWB | 47.6
68 | 104 | 381 | 57 | kW | 1.03
72 | 104 | 381 | 61 | MBh | 9.8
72 | 104 | 381 | 61 | S/T | 0.762
72 | 104 | 381 | 61 | ∆T | 18.2
72 | 104 | 381 | 61 | LDB | 53.8
72 | 104 | 381 | 61 | LWB | 51.9
72 | 104 | 381 | 61 | kW | 1.04
77 | 104 | 381 | 64 | MBh | 10.32
77 | 104 | 381 | 64 | S/T | 0.771
77 | 104 | 381 | 64 | ∆T | 19.3
77 | 104 | 381 | 64 | LDB | 57.7
77 | 104 | 381 | 64 | LWB | 55
77 | 104 | 381 | 64 | kW | 1.04
80 | 104 | 381 | 67 | MBh | 11.2
80 | 104 | 381 | 67 | S/T | 0.718
80 | 104 | 381 | 67 | ∆T | 19.5
80 | 104 | 381 | 67 | LDB | 60.5
80 | 104 | 381 | 67 | LWB | 57.8
80 | 104 | 381 | 67 | kW | 1.05
86 | 104 | 381 | 72 | MBh | 11.35
86 | 104 | 381 | 72 | S/T | 0.729
86 | 104 | 381 | 72 | ∆T | 20.1
86 | 104 | 381 | 72 | LDB | 65.9
86 | 104 | 381 | 72 | LWB | 63.7
86 | 104 | 381 | 72 | kW | 1.05
90 | 104 | 381 | 75 | MBh | 11.87
90 | 104 | 381 | 75 | S/T | 0.682
90 | 104 | 381 | 75 | ∆T | 19.7
90 | 104 | 381 | 75 | LDB | 70.3
90 | 104 | 381 | 75 | LWB | 66.9
90 | 104 | 381 | 75 | kW | 1.06
68 | 115 | 381 | 57 | MBh | 8.66
68 | 115 | 381 | 57 | S/T | 0.838
68 | 115 | 381 | 57 | ∆T | 17.6
68 | 115 | 381 | 57 | LDB | 50.4
68 | 115 | 381 | 57 | LWB | 48.3
68 | 115 | 381 | 57 | kW | 1.08
72 | 115 | 381 | 61 | MBh | 9.18
72 | 115 | 381 | 61 | S/T | 0.783
72 | 115 | 381 | 61 | ∆T | 17.5
72 | 115 | 381 | 61 | LDB | 54.5
72 | 115 | 381 | 61 | LWB | 52.5
72 | 115 | 381 | 61 | kW | 1.08
77 | 115 | 381 | 64 | MBh | 9.69
77 | 115 | 381 | 64 | S/T | 0.795
77 | 115 | 381 | 64 | ∆T | 18.7
77 | 115 | 381 | 64 | LDB | 58.3
77 | 115 | 381 | 64 | LWB | 55.5
77 | 115 | 381 | 64 | kW | 1.08
80 | 115 | 381 | 67 | MBh | 10.05
80 | 115 | 381 | 67 | S/T | 0.776
80 | 115 | 381 | 67 | ∆T | 19
80 | 115 | 381 | 67 | LDB | 61
80 | 115 | 381 | 67 | LWB | 58.8
80 | 115 | 381 | 67 | kW | 1.08
86 | 115 | 381 | 72 | MBh | 10.73
86 | 115 | 381 | 72 | S/T | 0.75
86 | 115 | 381 | 72 | ∆T | 19.6
86 | 115 | 381 | 72 | LDB | 66.4
86 | 115 | 381 | 72 | LWB | 64.2
86 | 115 | 381 | 72 | kW | 1.08
90 | 115 | 381 | 75 | MBh | 11.24
90 | 115 | 381 | 75 | S/T | 0.703
90 | 115 | 381 | 75 | ∆T | 19.2
90 | 115 | 381 | 75 | LDB | 70.8
90 | 115 | 381 | 75 | LWB | 67.4
90 | 115 | 381 | 75 | kW | 1.08
68 | 118 | 381 | 57 | MBh | 5.63
68 | 118 | 381 | 57 | S/T | 0.698
68 | 118 | 381 | 57 | ∆T | 9.6
68 | 118 | 381 | 57 | LDB | 58.4
68 | 118 | 381 | 57 | LWB | 51.5
68 | 118 | 381 | 57 | kW | 0.64
72 | 118 | 381 | 61 | MBh | 5.98
72 | 118 | 381 | 61 | S/T | 0.652
72 | 118 | 381 | 61 | ∆T | 9.5
72 | 118 | 381 | 61 | LDB | 62.5
72 | 118 | 381 | 61 | LWB | 55.6
72 | 118 | 381 | 61 | kW | 0.64
77 | 118 | 381 | 64 | MBh | 6.32
77 | 118 | 381 | 64 | S/T | 0.672
77 | 118 | 381 | 64 | ∆T | 10.3
77 | 118 | 381 | 64 | LDB | 66.7
77 | 118 | 381 | 64 | LWB | 58.7
77 | 118 | 381 | 64 | kW | 0.64
80 | 118 | 381 | 67 | MBh | 6.56
80 | 118 | 381 | 67 | S/T | 0.662
80 | 118 | 381 | 67 | ∆T | 10.5
80 | 118 | 381 | 67 | LDB | 69.5
80 | 118 | 381 | 67 | LWB | 61.8
80 | 118 | 381 | 67 | kW | 0.64
86 | 118 | 381 | 72 | MBh | 7.01
86 | 118 | 381 | 72 | S/T | 0.648
86 | 118 | 381 | 72 | ∆T | 11
86 | 118 | 381 | 72 | LDB | 75
86 | 118 | 381 | 72 | LWB | 67.1
86 | 118 | 381 | 72 | kW | 0.64
90 | 118 | 381 | 75 | MBh | 7.35
90 | 118 | 381 | 75 | S/T | 0.61
90 | 118 | 381 | 75 | ∆T | 10.9
90 | 118 | 381 | 75 | LDB | 79.1
90 | 118 | 381 | 75 | LWB | 70.2
90 | 118 | 381 | 75 | kW | 0.64

## RXF12BVJU9 - FTXF12BVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 413 | 57 | MBh | 15.29 | 75 | 64 | 59 | 23.66 | 1.85
68 | 50 | 413 | 57 | S/T | 0.704 | 75 | 64 | 70 | 22.9 | 1.9
68 | 50 | 413 | 57 | ∆T | 24.1 | 75 | 64 | 72 | 22.79 | 1.91
68 | 50 | 413 | 57 | LDB | 43.9 | 75 | 64 | 75 | 22.54 | 1.92
68 | 50 | 413 | 57 | LWB | 42 | 75 | 64 | 77 | 22.41 | 1.93
68 | 50 | 413 | 57 | kW | 0.83 | 75 | 64 | 81 | 21.11 | 1.77
72 | 50 | 413 | 61 | MBh | 16.86 | 59 | 50 | 59 | 20.4 | 1.74
72 | 50 | 413 | 61 | S/T | 0.654 | 59 | 50 | 70 | 19.64 | 1.78
72 | 50 | 413 | 61 | ∆T | 24.7 | 59 | 50 | 72 | 19.53 | 1.79
72 | 50 | 413 | 61 | LDB | 47.3 | 59 | 50 | 75 | 19.28 | 1.81
72 | 50 | 413 | 61 | LWB | 45.7 | 59 | 50 | 77 | 19.16 | 1.82
72 | 50 | 413 | 61 | kW | 0.92 | 59 | 50 | 81 | 18.91 | 1.83
77 | 50 | 413 | 64 | MBh | 17.53 | 47 | 43 | 59 | 18.77 | 1.68
77 | 50 | 413 | 64 | S/T | 0.65 | 47 | 43 | 70 | 18 | 1.73
77 | 50 | 413 | 64 | ∆T | 25.5 | 47 | 43 | 72 | 17.9 | 1.74
77 | 50 | 413 | 64 | LDB | 51.5 | 47 | 43 | 75 | 17.65 | 1.75
77 | 50 | 413 | 64 | LWB | 49 | 47 | 43 | 77 | 17.53 | 1.76
77 | 50 | 413 | 64 | kW | 0.93 | 47 | 43 | 81 | 17.28 | 1.77
80 | 50 | 413 | 67 | MBh | 18 | 35 | 32 | 59 | 16.38 | 1.6
80 | 50 | 413 | 67 | S/T | 0.632 | 35 | 32 | 70 | 15.62 | 1.65
80 | 50 | 413 | 67 | ∆T | 25.5 | 35 | 32 | 72 | 15.51 | 1.65
80 | 50 | 413 | 67 | LDB | 54.5 | 35 | 32 | 75 | 15.26 | 1.67
80 | 50 | 413 | 67 | LWB | 52.6 | 35 | 32 | 77 | 15.13 | 1.68
80 | 50 | 413 | 67 | kW | 0.93 | 35 | 32 | 81 | 14.88 | 1.69
86 | 50 | 413 | 72 | MBh | 18.87 | 25 | 23 | 59 | 14.34 | 1.53
86 | 50 | 413 | 72 | S/T | 0.603 | 25 | 23 | 70 | 13.58 | 1.58
86 | 50 | 413 | 72 | ∆T | 25.5 | 25 | 23 | 72 | 13.47 | 1.58
86 | 50 | 413 | 72 | LDB | 60.5 | 25 | 23 | 75 | 13.22 | 1.6
86 | 50 | 413 | 72 | LWB | 58.6 | 25 | 23 | 77 | 13.09 | 1.61
86 | 50 | 413 | 72 | kW | 0.94 | 25 | 23 | 81 | 12.84 | 1.62
90 | 50 | 413 | 75 | MBh | 19.55 | 16 | 14 | 59 | 12.3 | 1.46
90 | 50 | 413 | 75 | S/T | 0.564 | 16 | 14 | 70 | 11.54 | 1.5
90 | 50 | 413 | 75 | ∆T | 24.7 | 16 | 14 | 72 | 11.43 | 1.51
90 | 50 | 413 | 75 | LDB | 65.3 | 16 | 14 | 75 | 11.18 | 1.53
90 | 50 | 413 | 75 | LWB | 62.1 | 16 | 14 | 77 | 11.05 | 1.54
90 | 50 | 413 | 75 | kW | 1.17 | 16 | 14 | 81 | 10.8 | 1.55
68 | 68 | 413 | 57 | MBh | 14.82 | 5 | 5 | 59 | 10.26 | 1.28
68 | 68 | 413 | 57 | S/T | 0.71 | 5 | 5 | 70 | 9.5 | 1.32
68 | 68 | 413 | 57 | ∆T | 23.6 | 5 | 5 | 72 | 9.39 | 1.33
68 | 68 | 413 | 57 | LDB | 44.4 | 5 | 5 | 75 | 9.14 | 1.35
68 | 68 | 413 | 57 | LWB | 42.5 | 5 | 5 | 77 | 9.01 | 1.35
68 | 68 | 413 | 57 | kW | 1.13 | 5 | 5 | 81 | 8.76 | 1.37
72 | 68 | 413 | 61 | MBh | 15.5
72 | 68 | 413 | 61 | S/T | 0.667
72 | 68 | 413 | 61 | ∆T | 23.2
72 | 68 | 413 | 61 | LDB | 48.8
72 | 68 | 413 | 61 | LWB | 47.1
72 | 68 | 413 | 61 | kW | 1.14
77 | 68 | 413 | 64 | MBh | 16.17
77 | 68 | 413 | 64 | S/T | 0.665
77 | 68 | 413 | 64 | ∆T | 24.1
77 | 68 | 413 | 64 | LDB | 52.9
77 | 68 | 413 | 64 | LWB | 50.4
77 | 68 | 413 | 64 | kW | 1.15
80 | 68 | 413 | 67 | MBh | 16.64
80 | 68 | 413 | 67 | S/T | 0.647
80 | 68 | 413 | 67 | ∆T | 24.1
80 | 68 | 413 | 67 | LDB | 55.9
80 | 68 | 413 | 67 | LWB | 53.9
80 | 68 | 413 | 67 | kW | 1.15
86 | 68 | 413 | 72 | MBh | 17.51
86 | 68 | 413 | 72 | S/T | 0.619
86 | 68 | 413 | 72 | ∆T | 24.3
86 | 68 | 413 | 72 | LDB | 61.7
86 | 68 | 413 | 72 | LWB | 59.7
86 | 68 | 413 | 72 | kW | 1.16
90 | 68 | 413 | 75 | MBh | 18.19
90 | 68 | 413 | 75 | S/T | 0.579
90 | 68 | 413 | 75 | ∆T | 23.6
90 | 68 | 413 | 75 | LDB | 66.4
90 | 68 | 413 | 75 | LWB | 63.1
90 | 68 | 413 | 75 | kW | 1.17
68 | 86 | 413 | 57 | MBh | 13.46
68 | 86 | 413 | 57 | S/T | 0.729
68 | 86 | 413 | 57 | ∆T | 22
68 | 86 | 413 | 57 | LDB | 46
68 | 86 | 413 | 57 | LWB | 44
68 | 86 | 413 | 57 | kW | 1.35
72 | 86 | 413 | 61 | MBh | 14.14
72 | 86 | 413 | 61 | S/T | 0.684
72 | 86 | 413 | 61 | ∆T | 21.7
72 | 86 | 413 | 61 | LDB | 50.3
72 | 86 | 413 | 61 | LWB | 48.5
72 | 86 | 413 | 61 | kW | 1.36
77 | 86 | 413 | 64 | MBh | 14.81
77 | 86 | 413 | 64 | S/T | 0.684
77 | 86 | 413 | 64 | ∆T | 22.7
77 | 86 | 413 | 64 | LDB | 54.3
77 | 86 | 413 | 64 | LWB | 51.7
77 | 86 | 413 | 64 | kW | 1.37
80 | 86 | 413 | 67 | MBh | 15.28
80 | 86 | 413 | 67 | S/T | 0.666
80 | 86 | 413 | 67 | ∆T | 22.8
80 | 86 | 413 | 67 | LDB | 57.2
80 | 86 | 413 | 67 | LWB | 55.1
80 | 86 | 413 | 67 | kW | 1.37
86 | 86 | 413 | 72 | MBh | 16.15
86 | 86 | 413 | 72 | S/T | 0.638
86 | 86 | 413 | 72 | ∆T | 23.1
86 | 86 | 413 | 72 | LDB | 62.9
86 | 86 | 413 | 72 | LWB | 60.8
86 | 86 | 413 | 72 | kW | 1.38
90 | 86 | 413 | 75 | MBh | 16.83
90 | 86 | 413 | 75 | S/T | 0.597
90 | 86 | 413 | 75 | ∆T | 22.5
90 | 86 | 413 | 75 | LDB | 67.5
90 | 86 | 413 | 75 | LWB | 64.1
90 | 86 | 413 | 75 | kW | 1.39
68 | 95 | 413 | 57 | MBh | 12.78
68 | 95 | 413 | 57 | S/T | 0.74
68 | 95 | 413 | 57 | ∆T | 21.2
68 | 95 | 413 | 57 | LDB | 46.8
68 | 95 | 413 | 57 | LWB | 44.8
68 | 95 | 413 | 57 | kW | 1.46
72 | 95 | 413 | 61 | MBh | 13.46
72 | 95 | 413 | 61 | S/T | 0.694
72 | 95 | 413 | 61 | ∆T | 20.9
72 | 95 | 413 | 61 | LDB | 51.1
72 | 95 | 413 | 61 | LWB | 49.1
72 | 95 | 413 | 61 | kW | 1.47
77 | 95 | 413 | 64 | MBh | 14.13
77 | 95 | 413 | 64 | S/T | 0.695
77 | 95 | 413 | 64 | ∆T | 22
77 | 95 | 413 | 64 | LDB | 55
77 | 95 | 413 | 64 | LWB | 52.3
77 | 95 | 413 | 64 | kW | 1.48
80 | 95 | 413 | 67 | MBh | 14.6
80 | 95 | 413 | 67 | S/T | 0.677
80 | 95 | 413 | 67 | ∆T | 22.2
80 | 95 | 413 | 67 | LDB | 57.8
80 | 95 | 413 | 67 | LWB | 55.7
80 | 95 | 413 | 67 | kW | 1.48
86 | 95 | 413 | 72 | MBh | 15.47
86 | 95 | 413 | 72 | S/T | 0.649
86 | 95 | 413 | 72 | ∆T | 22.5
86 | 95 | 413 | 72 | LDB | 63.5
86 | 95 | 413 | 72 | LWB | 61.3
86 | 95 | 413 | 72 | kW | 1.49
90 | 95 | 413 | 75 | MBh | 16.15
90 | 95 | 413 | 75 | S/T | 0.607
90 | 95 | 413 | 75 | ∆T | 22
90 | 95 | 413 | 75 | LDB | 68
90 | 95 | 413 | 75 | LWB | 64.6
90 | 95 | 413 | 75 | kW | 1.5
68 | 104 | 413 | 57 | MBh | 12.1
68 | 104 | 413 | 57 | S/T | 0.754
68 | 104 | 413 | 57 | ∆T | 20.4
68 | 104 | 413 | 57 | LDB | 47.6
68 | 104 | 413 | 57 | LWB | 45.5
68 | 104 | 413 | 57 | kW | 1.51
72 | 104 | 413 | 61 | MBh | 12.78
72 | 104 | 413 | 61 | S/T | 0.706
72 | 104 | 413 | 61 | ∆T | 20.2
72 | 104 | 413 | 61 | LDB | 51.8
72 | 104 | 413 | 61 | LWB | 49.8
72 | 104 | 413 | 61 | kW | 1.51
77 | 104 | 413 | 64 | MBh | 13.45
77 | 104 | 413 | 64 | S/T | 0.708
77 | 104 | 413 | 64 | ∆T | 21.3
77 | 104 | 413 | 64 | LDB | 55.7
77 | 104 | 413 | 64 | LWB | 52.9
77 | 104 | 413 | 64 | kW | 1.51
80 | 104 | 413 | 67 | MBh | 14.6
80 | 104 | 413 | 67 | S/T | 0.658
80 | 104 | 413 | 67 | ∆T | 21.5
80 | 104 | 413 | 67 | LDB | 58.5
80 | 104 | 413 | 67 | LWB | 55.7
80 | 104 | 413 | 67 | kW | 1.51
86 | 104 | 413 | 72 | MBh | 14.78
86 | 104 | 413 | 72 | S/T | 0.662
86 | 104 | 413 | 72 | ∆T | 21.9
86 | 104 | 413 | 72 | LDB | 64.1
86 | 104 | 413 | 72 | LWB | 61.8
86 | 104 | 413 | 72 | kW | 1.51
90 | 104 | 413 | 75 | MBh | 15.42
90 | 104 | 413 | 75 | S/T | 0.619
90 | 104 | 413 | 75 | ∆T | 21.4
90 | 104 | 413 | 75 | LDB | 68.6
90 | 104 | 413 | 75 | LWB | 65.1
90 | 104 | 413 | 75 | kW | 1.51
68 | 115 | 413 | 57 | MBh | 11.29
68 | 115 | 413 | 57 | S/T | 0.772
68 | 115 | 413 | 57 | ∆T | 19.5
68 | 115 | 413 | 57 | LDB | 48.5
68 | 115 | 413 | 57 | LWB | 46.3
68 | 115 | 413 | 57 | kW | 1.19
72 | 115 | 413 | 61 | MBh | 11.96
72 | 115 | 413 | 61 | S/T | 0.722
72 | 115 | 413 | 61 | ∆T | 19.4
72 | 115 | 413 | 61 | LDB | 52.6
72 | 115 | 413 | 61 | LWB | 50.6
72 | 115 | 413 | 61 | kW | 1.19
77 | 115 | 413 | 64 | MBh | 12.63
77 | 115 | 413 | 64 | S/T | 0.726
77 | 115 | 413 | 64 | ∆T | 20.6
77 | 115 | 413 | 64 | LDB | 56.4
77 | 115 | 413 | 64 | LWB | 53.7
77 | 115 | 413 | 64 | kW | 1.19
80 | 115 | 413 | 67 | MBh | 13.1
80 | 115 | 413 | 67 | S/T | 0.707
80 | 115 | 413 | 67 | ∆T | 20.8
80 | 115 | 413 | 67 | LDB | 59.2
80 | 115 | 413 | 67 | LWB | 57
80 | 115 | 413 | 67 | kW | 1.19
86 | 115 | 413 | 72 | MBh | 13.98
86 | 115 | 413 | 72 | S/T | 0.679
86 | 115 | 413 | 72 | ∆T | 21.3
86 | 115 | 413 | 72 | LDB | 64.7
86 | 115 | 413 | 72 | LWB | 62.4
86 | 115 | 413 | 72 | kW | 1.19
90 | 115 | 413 | 75 | MBh | 14.65
90 | 115 | 413 | 75 | S/T | 0.634
90 | 115 | 413 | 75 | ∆T | 20.8
90 | 115 | 413 | 75 | LDB | 69.2
90 | 115 | 413 | 75 | LWB | 65.7
90 | 115 | 413 | 75 | kW | 1.19
68 | 118 | 413 | 57 | MBh | 6.17
68 | 118 | 413 | 57 | S/T | 0.577
68 | 118 | 413 | 57 | ∆T | 8
68 | 118 | 413 | 57 | LDB | 60
68 | 118 | 413 | 57 | LWB | 51.5
68 | 118 | 413 | 57 | kW | 0.61
72 | 118 | 413 | 61 | MBh | 6.55
72 | 118 | 413 | 61 | S/T | 0.539
72 | 118 | 413 | 61 | ∆T | 7.9
72 | 118 | 413 | 61 | LDB | 64.1
72 | 118 | 413 | 61 | LWB | 55.6
72 | 118 | 413 | 61 | kW | 0.61
77 | 118 | 413 | 64 | MBh | 6.93
77 | 118 | 413 | 64 | S/T | 0.556
77 | 118 | 413 | 64 | ∆T | 8.6
77 | 118 | 413 | 64 | LDB | 68.4
77 | 118 | 413 | 64 | LWB | 58.6
77 | 118 | 413 | 64 | kW | 0.61
80 | 118 | 413 | 67 | MBh | 7.19
80 | 118 | 413 | 67 | S/T | 0.545
80 | 118 | 413 | 67 | ∆T | 8.8
80 | 118 | 413 | 67 | LDB | 71.2
80 | 118 | 413 | 67 | LWB | 61.8
80 | 118 | 413 | 67 | kW | 0.61
86 | 118 | 413 | 72 | MBh | 7.68
86 | 118 | 413 | 72 | S/T | 0.534
86 | 118 | 413 | 72 | ∆T | 9.2
86 | 118 | 413 | 72 | LDB | 76.8
86 | 118 | 413 | 72 | LWB | 67
86 | 118 | 413 | 72 | kW | 0.61
90 | 118 | 413 | 75 | MBh | 8.06
90 | 118 | 413 | 75 | S/T | 0.502
90 | 118 | 413 | 75 | ∆T | 9.1
90 | 118 | 413 | 75 | LDB | 80.9
90 | 118 | 413 | 75 | LWB | 70.1
90 | 118 | 413 | 75 | kW | 0.61

## RXF18BVJU9 - FTXF18BVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 565 | 57 | MBh | 21.8 | 75 | 64 | 59 | 36.78 | 2.59
68 | 50 | 565 | 57 | S/T | 0.704 | 75 | 64 | 70 | 35.6 | 2.66
68 | 50 | 565 | 57 | ∆T | 25.2 | 75 | 64 | 72 | 35.43 | 2.67
68 | 50 | 565 | 57 | LDB | 42.8 | 75 | 64 | 75 | 35.04 | 2.69
68 | 50 | 565 | 57 | LWB | 41.3 | 75 | 64 | 77 | 34.85 | 2.7
68 | 50 | 565 | 57 | kW | 0.92 | 75 | 64 | 81 | 34.46 | 2.72
72 | 50 | 565 | 61 | MBh | 25.41 | 59 | 50 | 59 | 31.72 | 2.43
72 | 50 | 565 | 61 | S/T | 0.647 | 59 | 50 | 70 | 30.54 | 2.5
72 | 50 | 565 | 61 | ∆T | 26.9 | 59 | 50 | 72 | 30.37 | 2.51
72 | 50 | 565 | 61 | LDB | 45.1 | 59 | 50 | 75 | 29.98 | 2.53
72 | 50 | 565 | 61 | LWB | 43.8 | 59 | 50 | 77 | 29.79 | 2.54
72 | 50 | 565 | 61 | kW | 1.12 | 59 | 50 | 81 | 29.4 | 2.56
77 | 50 | 565 | 64 | MBh | 26.42 | 47 | 43 | 59 | 29.19 | 2.35
77 | 50 | 565 | 64 | S/T | 0.641 | 47 | 43 | 70 | 28 | 2.42
77 | 50 | 565 | 64 | ∆T | 27.7 | 47 | 43 | 72 | 27.84 | 2.43
77 | 50 | 565 | 64 | LDB | 49.3 | 47 | 43 | 75 | 27.45 | 2.45
77 | 50 | 565 | 64 | LWB | 47.2 | 47 | 43 | 77 | 27.26 | 2.46
77 | 50 | 565 | 64 | kW | 1.13 | 47 | 43 | 81 | 26.87 | 2.48
80 | 50 | 565 | 67 | MBh | 27.13 | 35 | 32 | 59 | 26.18 | 2.3
80 | 50 | 565 | 67 | S/T | 0.622 | 35 | 32 | 70 | 24.97 | 2.37
80 | 50 | 565 | 67 | ∆T | 27.7 | 35 | 32 | 72 | 24.79 | 2.38
80 | 50 | 565 | 67 | LDB | 52.3 | 35 | 32 | 75 | 24.39 | 2.4
80 | 50 | 565 | 67 | LWB | 50.9 | 35 | 32 | 77 | 24.19 | 2.42
80 | 50 | 565 | 67 | kW | 1.13 | 35 | 32 | 81 | 23.79 | 2.44
86 | 50 | 565 | 72 | MBh | 28.45 | 25 | 23 | 59 | 22.92 | 2.2
86 | 50 | 565 | 72 | S/T | 0.593 | 25 | 23 | 70 | 21.71 | 2.27
86 | 50 | 565 | 72 | ∆T | 27.6 | 25 | 23 | 72 | 21.53 | 2.28
86 | 50 | 565 | 72 | LDB | 58.4 | 25 | 23 | 75 | 21.13 | 2.3
86 | 50 | 565 | 72 | LWB | 57 | 25 | 23 | 77 | 20.93 | 2.31
86 | 50 | 565 | 72 | kW | 1.15 | 25 | 23 | 81 | 20.53 | 2.34
90 | 50 | 565 | 75 | MBh | 29.46 | 16 | 14 | 59 | 19.66 | 2.1
90 | 50 | 565 | 75 | S/T | 0.554 | 16 | 14 | 70 | 18.44 | 2.17
90 | 50 | 565 | 75 | ∆T | 26.7 | 16 | 14 | 72 | 18.27 | 2.18
90 | 50 | 565 | 75 | LDB | 63.3 | 16 | 14 | 75 | 17.87 | 2.2
90 | 50 | 565 | 75 | LWB | 60.6 | 16 | 14 | 77 | 17.67 | 2.21
90 | 50 | 565 | 75 | kW | 1.15 | 16 | 14 | 81 | 17.27 | 2.23
68 | 68 | 565 | 57 | MBh | 21.8 | 5 | 5 | 59 | 16.4 | 2.16
68 | 68 | 565 | 57 | S/T | 0.704 | 5 | 5 | 70 | 15.2 | 2.23
68 | 68 | 565 | 57 | ∆T | 25.2 | 5 | 5 | 72 | 15 | 2.24
68 | 68 | 565 | 57 | LDB | 42.8 | 5 | 5 | 75 | 14.61 | 2.26
68 | 68 | 565 | 57 | LWB | 41.3 | 5 | 5 | 77 | 14.41 | 2.27
68 | 68 | 565 | 57 | kW | 1.31 | 5 | 5 | 81 | 14.01 | 2.29
72 | 68 | 565 | 61 | MBh | 23.36
72 | 68 | 565 | 61 | S/T | 0.658
72 | 68 | 565 | 61 | ∆T | 25.2
72 | 68 | 565 | 61 | LDB | 46.8
72 | 68 | 565 | 61 | LWB | 45.4
72 | 68 | 565 | 61 | kW | 1.39
77 | 68 | 565 | 64 | MBh | 24.37
77 | 68 | 565 | 64 | S/T | 0.654
77 | 68 | 565 | 64 | ∆T | 26.1
77 | 68 | 565 | 64 | LDB | 50.9
77 | 68 | 565 | 64 | LWB | 48.7
77 | 68 | 565 | 64 | kW | 1.4
80 | 68 | 565 | 67 | MBh | 25.08
80 | 68 | 565 | 67 | S/T | 0.636
80 | 68 | 565 | 67 | ∆T | 26.1
80 | 68 | 565 | 67 | LDB | 53.9
80 | 68 | 565 | 67 | LWB | 52.3
80 | 68 | 565 | 67 | kW | 1.4
86 | 68 | 565 | 72 | MBh | 26.4
86 | 68 | 565 | 72 | S/T | 0.607
86 | 68 | 565 | 72 | ∆T | 26.3
86 | 68 | 565 | 72 | LDB | 59.7
86 | 68 | 565 | 72 | LWB | 58.3
86 | 68 | 565 | 72 | kW | 1.41
90 | 68 | 565 | 75 | MBh | 27.41
90 | 68 | 565 | 75 | S/T | 0.567
90 | 68 | 565 | 75 | ∆T | 25.5
90 | 68 | 565 | 75 | LDB | 64.5
90 | 68 | 565 | 75 | LWB | 61.7
90 | 68 | 565 | 75 | kW | 1.42
68 | 86 | 565 | 57 | MBh | 20.29
68 | 86 | 565 | 57 | S/T | 0.718
68 | 86 | 565 | 57 | ∆T | 23.9
68 | 86 | 565 | 57 | LDB | 44.1
68 | 86 | 565 | 57 | LWB | 42.5
68 | 86 | 565 | 57 | kW | 1.65
72 | 86 | 565 | 61 | MBh | 21.31
72 | 86 | 565 | 61 | S/T | 0.673
72 | 86 | 565 | 61 | ∆T | 23.5
72 | 86 | 565 | 61 | LDB | 48.5
72 | 86 | 565 | 61 | LWB | 47
72 | 86 | 565 | 61 | kW | 1.65
77 | 86 | 565 | 64 | MBh | 22.32
77 | 86 | 565 | 64 | S/T | 0.672
77 | 86 | 565 | 64 | ∆T | 24.6
77 | 86 | 565 | 64 | LDB | 52.4
77 | 86 | 565 | 64 | LWB | 50.2
77 | 86 | 565 | 64 | kW | 1.66
80 | 86 | 565 | 67 | MBh | 23.03
80 | 86 | 565 | 67 | S/T | 0.653
80 | 86 | 565 | 67 | ∆T | 24.6
80 | 86 | 565 | 67 | LDB | 55.4
80 | 86 | 565 | 67 | LWB | 53.7
80 | 86 | 565 | 67 | kW | 1.67
86 | 86 | 565 | 72 | MBh | 24.35
86 | 86 | 565 | 72 | S/T | 0.624
86 | 86 | 565 | 72 | ∆T | 24.9
86 | 86 | 565 | 72 | LDB | 61.1
86 | 86 | 565 | 72 | LWB | 59.5
86 | 86 | 565 | 72 | kW | 1.68
90 | 86 | 565 | 75 | MBh | 25.36
90 | 86 | 565 | 75 | S/T | 0.584
90 | 86 | 565 | 75 | ∆T | 24.3
90 | 86 | 565 | 75 | LDB | 65.7
90 | 86 | 565 | 75 | LWB | 62.9
90 | 86 | 565 | 75 | kW | 1.69
68 | 95 | 565 | 57 | MBh | 19.27
68 | 95 | 565 | 57 | S/T | 0.728
68 | 95 | 565 | 57 | ∆T | 23
68 | 95 | 565 | 57 | LDB | 45
68 | 95 | 565 | 57 | LWB | 43.3
68 | 95 | 565 | 57 | kW | 1.78
72 | 95 | 565 | 61 | MBh | 20.28
72 | 95 | 565 | 61 | S/T | 0.683
72 | 95 | 565 | 61 | ∆T | 22.7
72 | 95 | 565 | 61 | LDB | 49.3
72 | 95 | 565 | 61 | LWB | 47.8
72 | 95 | 565 | 61 | kW | 1.79
77 | 95 | 565 | 64 | MBh | 21.3
77 | 95 | 565 | 64 | S/T | 0.682
77 | 95 | 565 | 64 | ∆T | 23.8
77 | 95 | 565 | 64 | LDB | 53.2
77 | 95 | 565 | 64 | LWB | 50.9
77 | 95 | 565 | 64 | kW | 1.79
80 | 95 | 565 | 67 | MBh | 22
80 | 95 | 565 | 67 | S/T | 0.663
80 | 95 | 565 | 67 | ∆T | 23.9
80 | 95 | 565 | 67 | LDB | 56.1
80 | 95 | 565 | 67 | LWB | 54.4
80 | 95 | 565 | 67 | kW | 1.8
86 | 95 | 565 | 72 | MBh | 23.33
86 | 95 | 565 | 72 | S/T | 0.634
86 | 95 | 565 | 72 | ∆T | 24.3
86 | 95 | 565 | 72 | LDB | 61.7
86 | 95 | 565 | 72 | LWB | 60.1
86 | 95 | 565 | 72 | kW | 1.81
90 | 95 | 565 | 75 | MBh | 24.34
90 | 95 | 565 | 75 | S/T | 0.593
90 | 95 | 565 | 75 | ∆T | 23.7
90 | 95 | 565 | 75 | LDB | 66.3
90 | 95 | 565 | 75 | LWB | 63.4
90 | 95 | 565 | 75 | kW | 1.82
68 | 104 | 565 | 57 | MBh | 18.25
68 | 104 | 565 | 57 | S/T | 0.74
68 | 104 | 565 | 57 | ∆T | 22.1
68 | 104 | 565 | 57 | LDB | 45.9
68 | 104 | 565 | 57 | LWB | 44.2
68 | 104 | 565 | 57 | kW | 1.91
72 | 104 | 565 | 61 | MBh | 19.26
72 | 104 | 565 | 61 | S/T | 0.694
72 | 104 | 565 | 61 | ∆T | 21.9
72 | 104 | 565 | 61 | LDB | 50.1
72 | 104 | 565 | 61 | LWB | 48.5
72 | 104 | 565 | 61 | kW | 1.92
77 | 104 | 565 | 64 | MBh | 20.27
77 | 104 | 565 | 64 | S/T | 0.694
77 | 104 | 565 | 64 | ∆T | 23
77 | 104 | 565 | 64 | LDB | 54
77 | 104 | 565 | 64 | LWB | 51.6
77 | 104 | 565 | 64 | kW | 1.93
80 | 104 | 565 | 67 | MBh | 22
80 | 104 | 565 | 67 | S/T | 0.644
80 | 104 | 565 | 67 | ∆T | 23.2
80 | 104 | 565 | 67 | LDB | 56.8
80 | 104 | 565 | 67 | LWB | 54.4
80 | 104 | 565 | 67 | kW | 1.93
86 | 104 | 565 | 72 | MBh | 22.3
86 | 104 | 565 | 72 | S/T | 0.646
86 | 104 | 565 | 72 | ∆T | 23.6
86 | 104 | 565 | 72 | LDB | 62.4
86 | 104 | 565 | 72 | LWB | 60.7
86 | 104 | 565 | 72 | kW | 1.94
90 | 104 | 565 | 75 | MBh | 23.31
90 | 104 | 565 | 75 | S/T | 0.604
90 | 104 | 565 | 75 | ∆T | 23.1
90 | 104 | 565 | 75 | LDB | 66.9
90 | 104 | 565 | 75 | LWB | 64
90 | 104 | 565 | 75 | kW | 1.95
68 | 115 | 565 | 57 | MBh | 17.02
68 | 115 | 565 | 57 | S/T | 0.757
68 | 115 | 565 | 57 | ∆T | 21.1
68 | 115 | 565 | 57 | LDB | 46.9
68 | 115 | 565 | 57 | LWB | 45.1
68 | 115 | 565 | 57 | kW | 2.07
72 | 115 | 565 | 61 | MBh | 18.03
72 | 115 | 565 | 61 | S/T | 0.709
72 | 115 | 565 | 61 | ∆T | 20.9
72 | 115 | 565 | 61 | LDB | 51.1
72 | 115 | 565 | 61 | LWB | 49.4
72 | 115 | 565 | 61 | kW | 2.08
77 | 115 | 565 | 64 | MBh | 19.04
77 | 115 | 565 | 64 | S/T | 0.71
77 | 115 | 565 | 64 | ∆T | 22.2
77 | 115 | 565 | 64 | LDB | 54.8
77 | 115 | 565 | 64 | LWB | 52.5
77 | 115 | 565 | 64 | kW | 2.09
80 | 115 | 565 | 67 | MBh | 19.75
80 | 115 | 565 | 67 | S/T | 0.691
80 | 115 | 565 | 67 | ∆T | 22.4
80 | 115 | 565 | 67 | LDB | 57.6
80 | 115 | 565 | 67 | LWB | 55.8
80 | 115 | 565 | 67 | kW | 2.09
86 | 115 | 565 | 72 | MBh | 21.07
86 | 115 | 565 | 72 | S/T | 0.662
86 | 115 | 565 | 72 | ∆T | 22.9
86 | 115 | 565 | 72 | LDB | 63.1
86 | 115 | 565 | 72 | LWB | 61.4
86 | 115 | 565 | 72 | kW | 2.1
90 | 115 | 565 | 75 | MBh | 22.09
90 | 115 | 565 | 75 | S/T | 0.618
90 | 115 | 565 | 75 | ∆T | 22.4
90 | 115 | 565 | 75 | LDB | 67.6
90 | 115 | 565 | 75 | LWB | 64.6
90 | 115 | 565 | 75 | kW | 2.11
68 | 122 | 565 | 57 | MBh | 8.1
68 | 122 | 565 | 57 | S/T | 0.54
68 | 122 | 565 | 57 | ∆T | 7.2
68 | 122 | 565 | 57 | LDB | 60.8
68 | 122 | 565 | 57 | LWB | 51.7
68 | 122 | 565 | 57 | kW | 0.87
72 | 122 | 565 | 61 | MBh | 8.6
72 | 122 | 565 | 61 | S/T | 0.505
72 | 122 | 565 | 61 | ∆T | 7.1
72 | 122 | 565 | 61 | LDB | 64.9
72 | 122 | 565 | 61 | LWB | 55.8
72 | 122 | 565 | 61 | kW | 0.87
77 | 122 | 565 | 64 | MBh | 9.11
77 | 122 | 565 | 64 | S/T | 0.521
77 | 122 | 565 | 64 | ∆T | 7.8
77 | 122 | 565 | 64 | LDB | 69.2
77 | 122 | 565 | 64 | LWB | 58.8
77 | 122 | 565 | 64 | kW | 0.87
80 | 122 | 565 | 67 | MBh | 9.47
80 | 122 | 565 | 67 | S/T | 0.512
80 | 122 | 565 | 67 | ∆T | 7.9
80 | 122 | 565 | 67 | LDB | 72.1
80 | 122 | 565 | 67 | LWB | 62
80 | 122 | 565 | 67 | kW | 0.87
86 | 122 | 565 | 72 | MBh | 10.13
86 | 122 | 565 | 72 | S/T | 0.502
86 | 122 | 565 | 72 | ∆T | 8.3
86 | 122 | 565 | 72 | LDB | 77.7
86 | 122 | 565 | 72 | LWB | 67.2
86 | 122 | 565 | 72 | kW | 0.87
90 | 122 | 565 | 75 | MBh | 10.63
90 | 122 | 565 | 75 | S/T | 0.473
90 | 122 | 565 | 75 | ∆T | 8.2
90 | 122 | 565 | 75 | LDB | 81.8
90 | 122 | 565 | 75 | LWB | 70.3
90 | 122 | 565 | 75 | kW | 0.87

## RXF24BVJU9 - FTXF24BVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 629 | 57 | MBh | 22.31 | 75 | 64 | 59 | 38.14 | 2.78
68 | 50 | 629 | 57 | S/T | 0.704 | 75 | 64 | 70 | 36.61 | 2.78
68 | 50 | 629 | 57 | ∆T | 23.1 | 75 | 64 | 72 | 36.4 | 2.78
68 | 50 | 629 | 57 | LDB | 44.9 | 75 | 64 | 75 | 35.92 | 2.78
68 | 50 | 629 | 57 | LWB | 42.7 | 75 | 64 | 77 | 35.69 | 2.78
68 | 50 | 629 | 57 | kW | 1 | 75 | 64 | 81 | 34.2 | 2.72
72 | 50 | 629 | 61 | MBh | 27.4 | 59 | 50 | 59 | 36.24 | 3.11
72 | 50 | 629 | 61 | S/T | 0.641 | 59 | 50 | 70 | 34.9 | 3.2
72 | 50 | 629 | 61 | ∆T | 25.8 | 59 | 50 | 72 | 34.7 | 3.21
72 | 50 | 629 | 61 | LDB | 46.2 | 59 | 50 | 75 | 34.25 | 3.24
72 | 50 | 629 | 61 | LWB | 44.5 | 59 | 50 | 77 | 34.03 | 3.25
72 | 50 | 629 | 61 | kW | 1.29 | 59 | 50 | 81 | 33.59 | 3.28
77 | 50 | 629 | 64 | MBh | 31.71 | 47 | 43 | 59 | 33.35 | 3.01
77 | 50 | 629 | 64 | S/T | 0.621 | 47 | 43 | 70 | 32 | 3.1
77 | 50 | 629 | 64 | ∆T | 29 | 47 | 43 | 72 | 31.81 | 3.11
77 | 50 | 629 | 64 | LDB | 48 | 47 | 43 | 75 | 31.36 | 3.14
77 | 50 | 629 | 64 | LWB | 45.7 | 47 | 43 | 77 | 31.14 | 3.15
77 | 50 | 629 | 64 | kW | 1.54 | 47 | 43 | 81 | 30.7 | 3.18
80 | 50 | 629 | 67 | MBh | 32.56 | 35 | 32 | 59 | 28.95 | 2.85
80 | 50 | 629 | 67 | S/T | 0.602 | 35 | 32 | 70 | 27.6 | 2.94
80 | 50 | 629 | 67 | ∆T | 28.8 | 35 | 32 | 72 | 27.41 | 2.95
80 | 50 | 629 | 67 | LDB | 51.2 | 35 | 32 | 75 | 26.96 | 2.98
80 | 50 | 629 | 67 | LWB | 49.4 | 35 | 32 | 77 | 26.74 | 2.99
80 | 50 | 629 | 67 | kW | 1.55 | 35 | 32 | 81 | 26.3 | 3.02
86 | 50 | 629 | 72 | MBh | 34.14 | 25 | 23 | 59 | 25.34 | 2.72
86 | 50 | 629 | 72 | S/T | 0.57 | 25 | 23 | 70 | 24 | 2.81
86 | 50 | 629 | 72 | ∆T | 28.6 | 25 | 23 | 72 | 23.8 | 2.82
86 | 50 | 629 | 72 | LDB | 57.4 | 25 | 23 | 75 | 23.36 | 2.85
86 | 50 | 629 | 72 | LWB | 55.6 | 25 | 23 | 77 | 23.14 | 2.86
86 | 50 | 629 | 72 | kW | 1.56 | 25 | 23 | 81 | 22.7 | 2.89
90 | 50 | 629 | 75 | MBh | 35.36 | 16 | 14 | 59 | 21.74 | 2.6
90 | 50 | 629 | 75 | S/T | 0.531 | 16 | 14 | 70 | 20.39 | 2.68
90 | 50 | 629 | 75 | ∆T | 27.6 | 16 | 14 | 72 | 20.19 | 2.69
90 | 50 | 629 | 75 | LDB | 62.4 | 16 | 14 | 75 | 19.75 | 2.72
90 | 50 | 629 | 75 | LWB | 59.2 | 16 | 14 | 77 | 19.53 | 2.74
90 | 50 | 629 | 75 | kW | 1.58 | 16 | 14 | 81 | 19.09 | 2.76
68 | 68 | 629 | 57 | MBh | 22.31 | 5 | 5 | 59 | 18.13 | 2.5
68 | 68 | 629 | 57 | S/T | 0.704 | 5 | 5 | 70 | 16.8 | 2.59
68 | 68 | 629 | 57 | ∆T | 23.1 | 5 | 5 | 72 | 16.59 | 2.6
68 | 68 | 629 | 57 | LDB | 44.9 | 5 | 5 | 75 | 16.15 | 2.63
68 | 68 | 629 | 57 | LWB | 42.7 | 5 | 5 | 77 | 15.93 | 2.64
68 | 68 | 629 | 57 | kW | 1.37 | 5 | 5 | 81 | 15.49 | 2.67
72 | 68 | 629 | 61 | MBh | 27.4
72 | 68 | 629 | 61 | S/T | 0.641
72 | 68 | 629 | 61 | ∆T | 25.8
72 | 68 | 629 | 61 | LDB | 46.2
72 | 68 | 629 | 61 | LWB | 44.5
72 | 68 | 629 | 61 | kW | 1.82
77 | 68 | 629 | 64 | MBh | 29.25
77 | 68 | 629 | 64 | S/T | 0.63
77 | 68 | 629 | 64 | ∆T | 27.1
77 | 68 | 629 | 64 | LDB | 49.9
77 | 68 | 629 | 64 | LWB | 47.3
77 | 68 | 629 | 64 | kW | 1.91
80 | 68 | 629 | 67 | MBh | 30.1
80 | 68 | 629 | 67 | S/T | 0.611
80 | 68 | 629 | 67 | ∆T | 27.1
80 | 68 | 629 | 67 | LDB | 52.9
80 | 68 | 629 | 67 | LWB | 51
80 | 68 | 629 | 67 | kW | 1.91
86 | 68 | 629 | 72 | MBh | 31.68
86 | 68 | 629 | 72 | S/T | 0.58
86 | 68 | 629 | 72 | ∆T | 27
86 | 68 | 629 | 72 | LDB | 59
86 | 68 | 629 | 72 | LWB | 57
86 | 68 | 629 | 72 | kW | 1.93
90 | 68 | 629 | 75 | MBh | 32.9
90 | 68 | 629 | 75 | S/T | 0.54
90 | 68 | 629 | 75 | ∆T | 26.2
90 | 68 | 629 | 75 | LDB | 63.8
90 | 68 | 629 | 75 | LWB | 60.5
90 | 68 | 629 | 75 | kW | 1.94
68 | 86 | 629 | 57 | MBh | 22.31
68 | 86 | 629 | 57 | S/T | 0.704
68 | 86 | 629 | 57 | ∆T | 23.1
68 | 86 | 629 | 57 | LDB | 44.9
68 | 86 | 629 | 57 | LWB | 42.7
68 | 86 | 629 | 57 | kW | 1.9
72 | 86 | 629 | 61 | MBh | 25.57
72 | 86 | 629 | 61 | S/T | 0.649
72 | 86 | 629 | 61 | ∆T | 24.4
72 | 86 | 629 | 61 | LDB | 47.6
72 | 86 | 629 | 61 | LWB | 45.7
72 | 86 | 629 | 61 | kW | 2.26
77 | 86 | 629 | 64 | MBh | 26.79
77 | 86 | 629 | 64 | S/T | 0.642
77 | 86 | 629 | 64 | ∆T | 25.3
77 | 86 | 629 | 64 | LDB | 51.7
77 | 86 | 629 | 64 | LWB | 49
77 | 86 | 629 | 64 | kW | 2.27
80 | 86 | 629 | 67 | MBh | 27.64
80 | 86 | 629 | 67 | S/T | 0.623
80 | 86 | 629 | 67 | ∆T | 25.3
80 | 86 | 629 | 67 | LDB | 54.7
80 | 86 | 629 | 67 | LWB | 52.5
80 | 86 | 629 | 67 | kW | 2.28
86 | 86 | 629 | 72 | MBh | 29.22
86 | 86 | 629 | 72 | S/T | 0.592
86 | 86 | 629 | 72 | ∆T | 25.5
86 | 86 | 629 | 72 | LDB | 60.5
86 | 86 | 629 | 72 | LWB | 58.4
86 | 86 | 629 | 72 | kW | 2.29
90 | 86 | 629 | 75 | MBh | 30.44
90 | 86 | 629 | 75 | S/T | 0.553
90 | 86 | 629 | 75 | ∆T | 24.8
90 | 86 | 629 | 75 | LDB | 65.2
90 | 86 | 629 | 75 | LWB | 61.8
90 | 86 | 629 | 75 | kW | 2.3
68 | 95 | 629 | 57 | MBh | 22.31
68 | 95 | 629 | 57 | S/T | 0.704
68 | 95 | 629 | 57 | ∆T | 23.1
68 | 95 | 629 | 57 | LDB | 44.9
68 | 95 | 629 | 57 | LWB | 42.7
68 | 95 | 629 | 57 | kW | 2.26
72 | 95 | 629 | 61 | MBh | 24.34
72 | 95 | 629 | 61 | S/T | 0.655
72 | 95 | 629 | 61 | ∆T | 23.5
72 | 95 | 629 | 61 | LDB | 48.5
72 | 95 | 629 | 61 | LWB | 46.6
72 | 95 | 629 | 61 | kW | 2.44
77 | 95 | 629 | 64 | MBh | 25.56
77 | 95 | 629 | 64 | S/T | 0.65
77 | 95 | 629 | 64 | ∆T | 24.5
77 | 95 | 629 | 64 | LDB | 52.5
77 | 95 | 629 | 64 | LWB | 49.8
77 | 95 | 629 | 64 | kW | 2.45
80 | 95 | 629 | 67 | MBh | 26.4
80 | 95 | 629 | 67 | S/T | 0.631
80 | 95 | 629 | 67 | ∆T | 24.5
80 | 95 | 629 | 67 | LDB | 55.5
80 | 95 | 629 | 67 | LWB | 53.3
80 | 95 | 629 | 67 | kW | 2.46
86 | 95 | 629 | 72 | MBh | 27.99
86 | 95 | 629 | 72 | S/T | 0.6
86 | 95 | 629 | 72 | ∆T | 24.7
86 | 95 | 629 | 72 | LDB | 61.3
86 | 95 | 629 | 72 | LWB | 59
86 | 95 | 629 | 72 | kW | 2.47
90 | 95 | 629 | 75 | MBh | 29.21
90 | 95 | 629 | 75 | S/T | 0.56
90 | 95 | 629 | 75 | ∆T | 24.1
90 | 95 | 629 | 75 | LDB | 65.9
90 | 95 | 629 | 75 | LWB | 62.4
90 | 95 | 629 | 75 | kW | 2.49
68 | 104 | 629 | 57 | MBh | 21.89
68 | 104 | 629 | 57 | S/T | 0.708
68 | 104 | 629 | 57 | ∆T | 22.8
68 | 104 | 629 | 57 | LDB | 45.2
68 | 104 | 629 | 57 | LWB | 43
68 | 104 | 629 | 57 | kW | 2.61
72 | 104 | 629 | 61 | MBh | 23.11
72 | 104 | 629 | 61 | S/T | 0.663
72 | 104 | 629 | 61 | ∆T | 22.6
72 | 104 | 629 | 61 | LDB | 49.4
72 | 104 | 629 | 61 | LWB | 47.4
72 | 104 | 629 | 61 | kW | 2.62
77 | 104 | 629 | 64 | MBh | 24.33
77 | 104 | 629 | 64 | S/T | 0.659
77 | 104 | 629 | 64 | ∆T | 23.6
77 | 104 | 629 | 64 | LDB | 53.4
77 | 104 | 629 | 64 | LWB | 50.5
77 | 104 | 629 | 64 | kW | 2.63
80 | 104 | 629 | 67 | MBh | 26.4
80 | 104 | 629 | 67 | S/T | 0.61
80 | 104 | 629 | 67 | ∆T | 23.7
80 | 104 | 629 | 67 | LDB | 56.3
80 | 104 | 629 | 67 | LWB | 53.3
80 | 104 | 629 | 67 | kW | 2.64
86 | 104 | 629 | 72 | MBh | 26.76
86 | 104 | 629 | 72 | S/T | 0.609
86 | 104 | 629 | 72 | ∆T | 24
86 | 104 | 629 | 72 | LDB | 62
86 | 104 | 629 | 72 | LWB | 59.7
86 | 104 | 629 | 72 | kW | 2.66
90 | 104 | 629 | 75 | MBh | 27.98
90 | 104 | 629 | 75 | S/T | 0.568
90 | 104 | 629 | 75 | ∆T | 23.4
90 | 104 | 629 | 75 | LDB | 66.6
90 | 104 | 629 | 75 | LWB | 63
90 | 104 | 629 | 75 | kW | 2.67
68 | 115 | 629 | 57 | MBh | 20.42
68 | 115 | 629 | 57 | S/T | 0.72
68 | 115 | 629 | 57 | ∆T | 21.7
68 | 115 | 629 | 57 | LDB | 46.3
68 | 115 | 629 | 57 | LWB | 44.1
68 | 115 | 629 | 57 | kW | 2.26
72 | 115 | 629 | 61 | MBh | 21.64
72 | 115 | 629 | 61 | S/T | 0.675
72 | 115 | 629 | 61 | ∆T | 21.5
72 | 115 | 629 | 61 | LDB | 50.5
72 | 115 | 629 | 61 | LWB | 48.4
72 | 115 | 629 | 61 | kW | 2.26
77 | 115 | 629 | 64 | MBh | 22.85
77 | 115 | 629 | 64 | S/T | 0.671
77 | 115 | 629 | 64 | ∆T | 22.6
77 | 115 | 629 | 64 | LDB | 54.4
77 | 115 | 629 | 64 | LWB | 51.5
77 | 115 | 629 | 64 | kW | 2.26
80 | 115 | 629 | 67 | MBh | 23.7
80 | 115 | 629 | 67 | S/T | 0.652
80 | 115 | 629 | 67 | ∆T | 22.7
80 | 115 | 629 | 67 | LDB | 57.3
80 | 115 | 629 | 67 | LWB | 54.8
80 | 115 | 629 | 67 | kW | 2.26
86 | 115 | 629 | 72 | MBh | 25.29
86 | 115 | 629 | 72 | S/T | 0.621
86 | 115 | 629 | 72 | ∆T | 23.1
86 | 115 | 629 | 72 | LDB | 62.9
86 | 115 | 629 | 72 | LWB | 60.4
86 | 115 | 629 | 72 | kW | 2.26
90 | 115 | 629 | 75 | MBh | 26.5
90 | 115 | 629 | 75 | S/T | 0.579
90 | 115 | 629 | 75 | ∆T | 22.6
90 | 115 | 629 | 75 | LDB | 67.4
90 | 115 | 629 | 75 | LWB | 63.7
90 | 115 | 629 | 75 | kW | 2.26
68 | 122 | 629 | 57 | MBh | 8.16
68 | 122 | 629 | 57 | S/T | 0.458
68 | 122 | 629 | 57 | ∆T | 5.5
68 | 122 | 629 | 57 | LDB | 62.5
68 | 122 | 629 | 57 | LWB | 52.2
68 | 122 | 629 | 57 | kW | 0.78
72 | 122 | 629 | 61 | MBh | 8.67
72 | 122 | 629 | 61 | S/T | 0.428
72 | 122 | 629 | 61 | ∆T | 5.5
72 | 122 | 629 | 61 | LDB | 66.5
72 | 122 | 629 | 61 | LWB | 56.3
72 | 122 | 629 | 61 | kW | 0.78
77 | 122 | 629 | 64 | MBh | 9.18
77 | 122 | 629 | 64 | S/T | 0.442
77 | 122 | 629 | 64 | ∆T | 6
77 | 122 | 629 | 64 | LDB | 71
77 | 122 | 629 | 64 | LWB | 59.4
77 | 122 | 629 | 64 | kW | 0.78
80 | 122 | 629 | 67 | MBh | 9.54
80 | 122 | 629 | 67 | S/T | 0.435
80 | 122 | 629 | 67 | ∆T | 6.1
80 | 122 | 629 | 67 | LDB | 73.9
80 | 122 | 629 | 67 | LWB | 62.5
80 | 122 | 629 | 67 | kW | 0.78
86 | 122 | 629 | 72 | MBh | 10.21
86 | 122 | 629 | 72 | S/T | 0.426
86 | 122 | 629 | 72 | ∆T | 6.4
86 | 122 | 629 | 72 | LDB | 79.6
86 | 122 | 629 | 72 | LWB | 67.7
86 | 122 | 629 | 72 | kW | 0.78
90 | 122 | 629 | 75 | MBh | 10.72
90 | 122 | 629 | 75 | S/T | 0.401
90 | 122 | 629 | 75 | ∆T | 6.3
90 | 122 | 629 | 75 | LDB | 83.7
90 | 122 | 629 | 75 | LWB | 70.8
90 | 122 | 629 | 75 | kW | 0.78

## RKV30AVJU9 - FTXV30AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT
68 | 50 | 791 | 57 | MBh | 27.54
68 | 50 | 791 | 57 | S/T | 0.704
68 | 50 | 791 | 57 | ∆T | 22.7
68 | 50 | 791 | 57 | LDB | 45.3
68 | 50 | 791 | 57 | LWB | 43
68 | 50 | 791 | 57 | kW | 1.36
72 | 50 | 791 | 61 | MBh | 33.82
72 | 50 | 791 | 61 | S/T | 0.641
72 | 50 | 791 | 61 | ∆T | 25.4
72 | 50 | 791 | 61 | LDB | 46.6
72 | 50 | 791 | 61 | LWB | 44.8
72 | 50 | 791 | 61 | kW | 1.75
77 | 50 | 791 | 64 | MBh | 37.6
77 | 50 | 791 | 64 | S/T | 0.625
77 | 50 | 791 | 64 | ∆T | 27.5
77 | 50 | 791 | 64 | LDB | 49.5
77 | 50 | 791 | 64 | LWB | 46.9
77 | 50 | 791 | 64 | kW | 1.97
80 | 50 | 791 | 67 | MBh | 38.61
80 | 50 | 791 | 67 | S/T | 0.606
80 | 50 | 791 | 67 | ∆T | 27.4
80 | 50 | 791 | 67 | LDB | 52.6
80 | 50 | 791 | 67 | LWB | 50.6
80 | 50 | 791 | 67 | kW | 1.98
86 | 50 | 791 | 72 | MBh | 40.49
86 | 50 | 791 | 72 | S/T | 0.575
86 | 50 | 791 | 72 | ∆T | 27.2
86 | 50 | 791 | 72 | LDB | 58.8
86 | 50 | 791 | 72 | LWB | 56.7
86 | 50 | 791 | 72 | kW | 2
90 | 50 | 791 | 75 | MBh | 41.93
90 | 50 | 791 | 75 | S/T | 0.536
90 | 50 | 791 | 75 | ∆T | 26.3
90 | 50 | 791 | 75 | LDB | 63.7
90 | 50 | 791 | 75 | LWB | 60.3
90 | 50 | 791 | 75 | kW | 2.01
68 | 68 | 791 | 57 | MBh | 27.54
68 | 68 | 791 | 57 | S/T | 0.704
68 | 68 | 791 | 57 | ∆T | 22.7
68 | 68 | 791 | 57 | LDB | 45.3
68 | 68 | 791 | 57 | LWB | 43
68 | 68 | 791 | 57 | kW | 1.88
72 | 68 | 791 | 61 | MBh | 33.24
72 | 68 | 791 | 61 | S/T | 0.643
72 | 68 | 791 | 61 | ∆T | 25
72 | 68 | 791 | 61 | LDB | 47
72 | 68 | 791 | 61 | LWB | 45.1
72 | 68 | 791 | 61 | kW | 2.42
77 | 68 | 791 | 64 | MBh | 34.69
77 | 68 | 791 | 64 | S/T | 0.635
77 | 68 | 791 | 64 | ∆T | 25.8
77 | 68 | 791 | 64 | LDB | 51.2
77 | 68 | 791 | 64 | LWB | 48.5
77 | 68 | 791 | 64 | kW | 2.43
80 | 68 | 791 | 67 | MBh | 35.7
80 | 68 | 791 | 67 | S/T | 0.616
80 | 68 | 791 | 67 | ∆T | 25.8
80 | 68 | 791 | 67 | LDB | 54.2
80 | 68 | 791 | 67 | LWB | 52.1
80 | 68 | 791 | 67 | kW | 2.44
86 | 68 | 791 | 72 | MBh | 37.57
86 | 68 | 791 | 72 | S/T | 0.586
86 | 68 | 791 | 72 | ∆T | 25.8
86 | 68 | 791 | 72 | LDB | 60.2
86 | 68 | 791 | 72 | LWB | 58
86 | 68 | 791 | 72 | kW | 2.46
90 | 68 | 791 | 75 | MBh | 39.02
90 | 68 | 791 | 75 | S/T | 0.546
90 | 68 | 791 | 75 | ∆T | 25
90 | 68 | 791 | 75 | LDB | 65
90 | 68 | 791 | 75 | LWB | 61.5
90 | 68 | 791 | 75 | kW | 2.48
68 | 86 | 791 | 57 | MBh | 27.54
68 | 86 | 791 | 57 | S/T | 0.704
68 | 86 | 791 | 57 | ∆T | 22.7
68 | 86 | 791 | 57 | LDB | 45.3
68 | 86 | 791 | 57 | LWB | 43
68 | 86 | 791 | 57 | kW | 2.62
72 | 86 | 791 | 61 | MBh | 30.33
72 | 86 | 791 | 61 | S/T | 0.654
72 | 86 | 791 | 61 | ∆T | 23.2
72 | 86 | 791 | 61 | LDB | 48.8
72 | 86 | 791 | 61 | LWB | 46.7
72 | 86 | 791 | 61 | kW | 2.88
77 | 86 | 791 | 64 | MBh | 31.77
77 | 86 | 791 | 64 | S/T | 0.649
77 | 86 | 791 | 64 | ∆T | 24.1
77 | 86 | 791 | 64 | LDB | 52.9
77 | 86 | 791 | 64 | LWB | 50
77 | 86 | 791 | 64 | kW | 2.9
80 | 86 | 791 | 67 | MBh | 32.78
80 | 86 | 791 | 67 | S/T | 0.63
80 | 86 | 791 | 67 | ∆T | 24.2
80 | 86 | 791 | 67 | LDB | 55.8
80 | 86 | 791 | 67 | LWB | 53.5
80 | 86 | 791 | 67 | kW | 2.91
86 | 86 | 791 | 72 | MBh | 34.66
86 | 86 | 791 | 72 | S/T | 0.599
86 | 86 | 791 | 72 | ∆T | 24.3
86 | 86 | 791 | 72 | LDB | 61.7
86 | 86 | 791 | 72 | LWB | 59.2
86 | 86 | 791 | 72 | kW | 2.93
90 | 86 | 791 | 75 | MBh | 36.1
90 | 86 | 791 | 75 | S/T | 0.56
90 | 86 | 791 | 75 | ∆T | 23.6
90 | 86 | 791 | 75 | LDB | 66.4
90 | 86 | 791 | 75 | LWB | 62.6
90 | 86 | 791 | 75 | kW | 2.94
68 | 95 | 791 | 57 | MBh | 27.43
68 | 95 | 791 | 57 | S/T | 0.705
68 | 95 | 791 | 57 | ∆T | 22.6
68 | 95 | 791 | 57 | LDB | 45.4
68 | 95 | 791 | 57 | LWB | 43.1
68 | 95 | 791 | 57 | kW | 3.1
72 | 95 | 791 | 61 | MBh | 28.87
72 | 95 | 791 | 61 | S/T | 0.662
72 | 95 | 791 | 61 | ∆T | 22.4
72 | 95 | 791 | 61 | LDB | 49.6
72 | 95 | 791 | 61 | LWB | 47.5
72 | 95 | 791 | 61 | kW | 3.12
77 | 95 | 791 | 64 | MBh | 30.31
77 | 95 | 791 | 64 | S/T | 0.657
77 | 95 | 791 | 64 | ∆T | 23.3
77 | 95 | 791 | 64 | LDB | 53.7
77 | 95 | 791 | 64 | LWB | 50.7
77 | 95 | 791 | 64 | kW | 3.13
80 | 95 | 791 | 67 | MBh | 31.4
80 | 95 | 791 | 67 | S/T | 0.636
80 | 95 | 791 | 67 | ∆T | 23.4
80 | 95 | 791 | 67 | LDB | 56.6
80 | 95 | 791 | 67 | LWB | 54.1
80 | 95 | 791 | 67 | kW | 3.14
86 | 95 | 791 | 72 | MBh | 33.2
86 | 95 | 791 | 72 | S/T | 0.608
86 | 95 | 791 | 72 | ∆T | 23.6
86 | 95 | 791 | 72 | LDB | 62.4
86 | 95 | 791 | 72 | LWB | 59.9
86 | 95 | 791 | 72 | kW | 3.16
90 | 95 | 791 | 75 | MBh | 34.64
90 | 95 | 791 | 75 | S/T | 0.567
90 | 95 | 791 | 75 | ∆T | 23
90 | 95 | 791 | 75 | LDB | 67
90 | 95 | 791 | 75 | LWB | 63.2
90 | 95 | 791 | 75 | kW | 3.17
68 | 104 | 791 | 57 | MBh | 25.97
68 | 104 | 791 | 57 | S/T | 0.715
68 | 104 | 791 | 57 | ∆T | 21.7
68 | 104 | 791 | 57 | LDB | 46.3
68 | 104 | 791 | 57 | LWB | 43.9
68 | 104 | 791 | 57 | kW | 3.33
72 | 104 | 791 | 61 | MBh | 27.41
72 | 104 | 791 | 61 | S/T | 0.67
72 | 104 | 791 | 61 | ∆T | 21.5
72 | 104 | 791 | 61 | LDB | 50.5
72 | 104 | 791 | 61 | LWB | 48.3
72 | 104 | 791 | 61 | kW | 3.35
77 | 104 | 791 | 64 | MBh | 28.85
77 | 104 | 791 | 64 | S/T | 0.667
77 | 104 | 791 | 64 | ∆T | 22.5
77 | 104 | 791 | 64 | LDB | 54.5
77 | 104 | 791 | 64 | LWB | 51.4
77 | 104 | 791 | 64 | kW | 3.36
80 | 104 | 791 | 67 | MBh | 29.86
80 | 104 | 791 | 67 | S/T | 0.647
80 | 104 | 791 | 67 | ∆T | 22.6
80 | 104 | 791 | 67 | LDB | 57.4
80 | 104 | 791 | 67 | LWB | 54.8
80 | 104 | 791 | 67 | kW | 3.37
86 | 104 | 791 | 72 | MBh | 31.74
86 | 104 | 791 | 72 | S/T | 0.617
86 | 104 | 791 | 72 | ∆T | 22.9
86 | 104 | 791 | 72 | LDB | 63.1
86 | 104 | 791 | 72 | LWB | 60.5
86 | 104 | 791 | 72 | kW | 3.39
90 | 104 | 791 | 75 | MBh | 33.18
90 | 104 | 791 | 75 | S/T | 0.576
90 | 104 | 791 | 75 | ∆T | 22.4
90 | 104 | 791 | 75 | LDB | 67.6
90 | 104 | 791 | 75 | LWB | 63.8
90 | 104 | 791 | 75 | kW | 3.4
68 | 115 | 791 | 57 | MBh | 22.45
68 | 115 | 791 | 57 | S/T | 0.747
68 | 115 | 791 | 57 | ∆T | 19.6
68 | 115 | 791 | 57 | LDB | 48.4
68 | 115 | 791 | 57 | LWB | 45.9
68 | 115 | 791 | 57 | kW | 2.51
72 | 115 | 791 | 61 | MBh | 23.46
72 | 115 | 791 | 61 | S/T | 0.702
72 | 115 | 791 | 61 | ∆T | 19.3
72 | 115 | 791 | 61 | LDB | 52.7
72 | 115 | 791 | 61 | LWB | 50.3
72 | 115 | 791 | 61 | kW | 2.51
77 | 115 | 791 | 64 | MBh | 24.45
77 | 115 | 791 | 64 | S/T | 0.706
77 | 115 | 791 | 64 | ∆T | 20.2
77 | 115 | 791 | 64 | LDB | 56.8
77 | 115 | 791 | 64 | LWB | 53.5
77 | 115 | 791 | 64 | kW | 2.51
80 | 115 | 791 | 67 | MBh | 25.15
80 | 115 | 791 | 67 | S/T | 0.689
80 | 115 | 791 | 67 | ∆T | 20.3
80 | 115 | 791 | 67 | LDB | 59.7
80 | 115 | 791 | 67 | LWB | 56.9
80 | 115 | 791 | 67 | kW | 2.51
86 | 115 | 791 | 72 | MBh | 26.43
86 | 115 | 791 | 72 | S/T | 0.664
86 | 115 | 791 | 72 | ∆T | 20.5
86 | 115 | 791 | 72 | LDB | 65.5
86 | 115 | 791 | 72 | LWB | 62.6
86 | 115 | 791 | 72 | kW | 2.51
90 | 115 | 791 | 75 | MBh | 27.41
90 | 115 | 791 | 75 | S/T | 0.623
90 | 115 | 791 | 75 | ∆T | 20
90 | 115 | 791 | 75 | LDB | 70
90 | 115 | 791 | 75 | LWB | 65.9
90 | 115 | 791 | 75 | kW | 2.51

## RKV36AVJU9 - FTXV36AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT
68 | 50 | 826 | 57 | MBh | 30.32
68 | 50 | 826 | 57 | S/T | 0.704
68 | 50 | 826 | 57 | ∆T | 23.9
68 | 50 | 826 | 57 | LDB | 44.1
68 | 50 | 826 | 57 | LWB | 42.1
68 | 50 | 826 | 57 | kW | 1.52
72 | 50 | 826 | 61 | MBh | 37.24
72 | 50 | 826 | 61 | S/T | 0.641
72 | 50 | 826 | 61 | ∆T | 26.7
72 | 50 | 826 | 61 | LDB | 45.3
72 | 50 | 826 | 61 | LWB | 43.8
72 | 50 | 826 | 61 | kW | 1.97
77 | 50 | 826 | 64 | MBh | 41.29
77 | 50 | 826 | 64 | S/T | 0.626
77 | 50 | 826 | 64 | ∆T | 29
77 | 50 | 826 | 64 | LDB | 48
77 | 50 | 826 | 64 | LWB | 45.9
77 | 50 | 826 | 64 | kW | 2.2
80 | 50 | 826 | 67 | MBh | 42.4
80 | 50 | 826 | 67 | S/T | 0.606
80 | 50 | 826 | 67 | ∆T | 28.8
80 | 50 | 826 | 67 | LDB | 51.2
80 | 50 | 826 | 67 | LWB | 49.6
80 | 50 | 826 | 67 | kW | 2.21
86 | 50 | 826 | 72 | MBh | 44.46
86 | 50 | 826 | 72 | S/T | 0.575
86 | 50 | 826 | 72 | ∆T | 28.7
86 | 50 | 826 | 72 | LDB | 57.3
86 | 50 | 826 | 72 | LWB | 55.8
86 | 50 | 826 | 72 | kW | 2.23
90 | 50 | 826 | 75 | MBh | 46.04
90 | 50 | 826 | 75 | S/T | 0.536
90 | 50 | 826 | 75 | ∆T | 27.7
90 | 50 | 826 | 75 | LDB | 62.3
90 | 50 | 826 | 75 | LWB | 59.4
90 | 50 | 826 | 75 | kW | 2.25
68 | 68 | 826 | 57 | MBh | 30.32
68 | 68 | 826 | 57 | S/T | 0.704
68 | 68 | 826 | 57 | ∆T | 23.9
68 | 68 | 826 | 57 | LDB | 44.1
68 | 68 | 826 | 57 | LWB | 42.1
68 | 68 | 826 | 57 | kW | 2.11
72 | 68 | 826 | 61 | MBh | 36.5
72 | 68 | 826 | 61 | S/T | 0.643
72 | 68 | 826 | 61 | ∆T | 26.3
72 | 68 | 826 | 61 | LDB | 45.7
72 | 68 | 826 | 61 | LWB | 44.2
72 | 68 | 826 | 61 | kW | 2.71
77 | 68 | 826 | 64 | MBh | 38.09
77 | 68 | 826 | 64 | S/T | 0.636
77 | 68 | 826 | 64 | ∆T | 27.1
77 | 68 | 826 | 64 | LDB | 49.9
77 | 68 | 826 | 64 | LWB | 47.5
77 | 68 | 826 | 64 | kW | 2.72
80 | 68 | 826 | 67 | MBh | 39.2
80 | 68 | 826 | 67 | S/T | 0.617
80 | 68 | 826 | 67 | ∆T | 27.1
80 | 68 | 826 | 67 | LDB | 52.9
80 | 68 | 826 | 67 | LWB | 51.1
80 | 68 | 826 | 67 | kW | 2.73
86 | 68 | 826 | 72 | MBh | 41.26
86 | 68 | 826 | 72 | S/T | 0.586
86 | 68 | 826 | 72 | ∆T | 27.1
86 | 68 | 826 | 72 | LDB | 58.9
86 | 68 | 826 | 72 | LWB | 57.2
86 | 68 | 826 | 72 | kW | 2.75
90 | 68 | 826 | 75 | MBh | 42.84
90 | 68 | 826 | 75 | S/T | 0.547
90 | 68 | 826 | 75 | ∆T | 26.3
90 | 68 | 826 | 75 | LDB | 63.7
90 | 68 | 826 | 75 | LWB | 60.7
90 | 68 | 826 | 75 | kW | 2.77
68 | 86 | 826 | 57 | MBh | 30.32
68 | 86 | 826 | 57 | S/T | 0.704
68 | 86 | 826 | 57 | ∆T | 23.9
68 | 86 | 826 | 57 | LDB | 44.1
68 | 86 | 826 | 57 | LWB | 42.1
68 | 86 | 826 | 57 | kW | 2.94
72 | 86 | 826 | 61 | MBh | 33.3
72 | 86 | 826 | 61 | S/T | 0.654
72 | 86 | 826 | 61 | ∆T | 24.4
72 | 86 | 826 | 61 | LDB | 47.6
72 | 86 | 826 | 61 | LWB | 45.9
72 | 86 | 826 | 61 | kW | 3.22
77 | 86 | 826 | 64 | MBh | 34.89
77 | 86 | 826 | 64 | S/T | 0.649
77 | 86 | 826 | 64 | ∆T | 25.4
77 | 86 | 826 | 64 | LDB | 51.6
77 | 86 | 826 | 64 | LWB | 49.1
77 | 86 | 826 | 64 | kW | 3.24
80 | 86 | 826 | 67 | MBh | 35.99
80 | 86 | 826 | 67 | S/T | 0.63
80 | 86 | 826 | 67 | ∆T | 25.4
80 | 86 | 826 | 67 | LDB | 54.6
80 | 86 | 826 | 67 | LWB | 52.6
80 | 86 | 826 | 67 | kW | 3.25
86 | 86 | 826 | 72 | MBh | 38.05
86 | 86 | 826 | 72 | S/T | 0.6
86 | 86 | 826 | 72 | ∆T | 25.6
86 | 86 | 826 | 72 | LDB | 60.4
86 | 86 | 826 | 72 | LWB | 58.5
86 | 86 | 826 | 72 | kW | 3.27
90 | 86 | 826 | 75 | MBh | 39.64
90 | 86 | 826 | 75 | S/T | 0.56
90 | 86 | 826 | 75 | ∆T | 24.9
90 | 86 | 826 | 75 | LDB | 65.1
90 | 86 | 826 | 75 | LWB | 61.9
90 | 86 | 826 | 75 | kW | 3.29
68 | 95 | 826 | 57 | MBh | 30.11
68 | 95 | 826 | 57 | S/T | 0.705
68 | 95 | 826 | 57 | ∆T | 23.8
68 | 95 | 826 | 57 | LDB | 44.2
68 | 95 | 826 | 57 | LWB | 42.3
68 | 95 | 826 | 57 | kW | 3.47
72 | 95 | 826 | 61 | MBh | 31.7
72 | 95 | 826 | 61 | S/T | 0.662
72 | 95 | 826 | 61 | ∆T | 23.5
72 | 95 | 826 | 61 | LDB | 48.5
72 | 95 | 826 | 61 | LWB | 46.7
72 | 95 | 826 | 61 | kW | 3.48
77 | 95 | 826 | 64 | MBh | 33.28
77 | 95 | 826 | 64 | S/T | 0.658
77 | 95 | 826 | 64 | ∆T | 24.5
77 | 95 | 826 | 64 | LDB | 52.5
77 | 95 | 826 | 64 | LWB | 49.9
77 | 95 | 826 | 64 | kW | 3.5
80 | 95 | 826 | 67 | MBh | 34.4
80 | 95 | 826 | 67 | S/T | 0.638
80 | 95 | 826 | 67 | ∆T | 24.6
80 | 95 | 826 | 67 | LDB | 55.4
80 | 95 | 826 | 67 | LWB | 53.4
80 | 95 | 826 | 67 | kW | 3.51
86 | 95 | 826 | 72 | MBh | 36.45
86 | 95 | 826 | 72 | S/T | 0.609
86 | 95 | 826 | 72 | ∆T | 24.9
86 | 95 | 826 | 72 | LDB | 61.1
86 | 95 | 826 | 72 | LWB | 59.1
86 | 95 | 826 | 72 | kW | 3.53
90 | 95 | 826 | 75 | MBh | 38.04
90 | 95 | 826 | 75 | S/T | 0.568
90 | 95 | 826 | 75 | ∆T | 24.2
90 | 95 | 826 | 75 | LDB | 65.8
90 | 95 | 826 | 75 | LWB | 62.5
90 | 95 | 826 | 75 | kW | 3.55
68 | 104 | 826 | 57 | MBh | 28.25
68 | 104 | 826 | 57 | S/T | 0.717
68 | 104 | 826 | 57 | ∆T | 22.7
68 | 104 | 826 | 57 | LDB | 45.3
68 | 104 | 826 | 57 | LWB | 43.3
68 | 104 | 826 | 57 | kW | 3.58
72 | 104 | 826 | 61 | MBh | 29.74
72 | 104 | 826 | 61 | S/T | 0.673
72 | 104 | 826 | 61 | ∆T | 22.4
72 | 104 | 826 | 61 | LDB | 49.6
72 | 104 | 826 | 61 | LWB | 47.7
72 | 104 | 826 | 61 | kW | 3.58
77 | 104 | 826 | 64 | MBh | 31.22
77 | 104 | 826 | 64 | S/T | 0.67
77 | 104 | 826 | 64 | ∆T | 23.5
77 | 104 | 826 | 64 | LDB | 53.5
77 | 104 | 826 | 64 | LWB | 50.9
77 | 104 | 826 | 64 | kW | 3.58
80 | 104 | 826 | 67 | MBh | 32.25
80 | 104 | 826 | 67 | S/T | 0.651
80 | 104 | 826 | 67 | ∆T | 23.6
80 | 104 | 826 | 67 | LDB | 56.4
80 | 104 | 826 | 67 | LWB | 54.3
80 | 104 | 826 | 67 | kW | 3.58
86 | 104 | 826 | 72 | MBh | 34.15
86 | 104 | 826 | 72 | S/T | 0.623
86 | 104 | 826 | 72 | ∆T | 23.8
86 | 104 | 826 | 72 | LDB | 62.2
86 | 104 | 826 | 72 | LWB | 60.1
86 | 104 | 826 | 72 | kW | 3.58
90 | 104 | 826 | 75 | MBh | 35.6
90 | 104 | 826 | 75 | S/T | 0.582
90 | 104 | 826 | 75 | ∆T | 23.2
90 | 104 | 826 | 75 | LDB | 66.8
90 | 104 | 826 | 75 | LWB | 63.4
90 | 104 | 826 | 75 | kW | 3.58
68 | 115 | 826 | 57 | MBh | 22.86
68 | 115 | 826 | 57 | S/T | 0.766
68 | 115 | 826 | 57 | ∆T | 19.6
68 | 115 | 826 | 57 | LDB | 48.4
68 | 115 | 826 | 57 | LWB | 46.2
68 | 115 | 826 | 57 | kW | 2.51
72 | 115 | 826 | 61 | MBh | 23.84
72 | 115 | 826 | 61 | S/T | 0.721
72 | 115 | 826 | 61 | ∆T | 19.3
72 | 115 | 826 | 61 | LDB | 52.7
72 | 115 | 826 | 61 | LWB | 50.6
72 | 115 | 826 | 61 | kW | 2.51
77 | 115 | 826 | 64 | MBh | 24.82
77 | 115 | 826 | 64 | S/T | 0.728
77 | 115 | 826 | 64 | ∆T | 20.3
77 | 115 | 826 | 64 | LDB | 56.7
77 | 115 | 826 | 64 | LWB | 53.9
77 | 115 | 826 | 64 | kW | 2.51
80 | 115 | 826 | 67 | MBh | 25.49
80 | 115 | 826 | 67 | S/T | 0.712
80 | 115 | 826 | 67 | ∆T | 20.4
80 | 115 | 826 | 67 | LDB | 59.6
80 | 115 | 826 | 67 | LWB | 57.3
80 | 115 | 826 | 67 | kW | 2.51
86 | 115 | 826 | 72 | MBh | 26.75
86 | 115 | 826 | 72 | S/T | 0.69
86 | 115 | 826 | 72 | ∆T | 20.7
86 | 115 | 826 | 72 | LDB | 65.3
86 | 115 | 826 | 72 | LWB | 62.9
86 | 115 | 826 | 72 | kW | 2.51
90 | 115 | 826 | 75 | MBh | 27.7
90 | 115 | 826 | 75 | S/T | 0.649
90 | 115 | 826 | 75 | ∆T | 20.2
90 | 115 | 826 | 75 | LDB | 69.8
90 | 115 | 826 | 75 | LWB | 66.2
90 | 115 | 826 | 75 | kW | 2.51

## RXV30AVJU9 - FTXV30AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 791 | 57 | MBh | 29.4 | 75 | 64 | 59 | 45.7 | 3.77
68 | 50 | 791 | 57 | S/T | 0.704 | 75 | 64 | 70 | 43.91 | 3.82
68 | 50 | 791 | 57 | ∆T | 24.2 | 75 | 64 | 72 | 43.61 | 3.82
68 | 50 | 791 | 57 | LDB | 43.8 | 75 | 64 | 75 | 42.95 | 3.82
68 | 50 | 791 | 57 | LWB | 41.9 | 75 | 64 | 77 | 42.63 | 3.82
68 | 50 | 791 | 57 | kW | 1.5 | 75 | 64 | 81 | 41.99 | 3.82
72 | 50 | 791 | 61 | MBh | 36.1 | 59 | 50 | 59 | 39.42 | 3.54
72 | 50 | 791 | 61 | S/T | 0.641 | 59 | 50 | 70 | 37.95 | 3.64
72 | 50 | 791 | 61 | ∆T | 27.1 | 59 | 50 | 72 | 37.73 | 3.65
72 | 50 | 791 | 61 | LDB | 44.9 | 59 | 50 | 75 | 37.25 | 3.68
72 | 50 | 791 | 61 | LWB | 43.5 | 59 | 50 | 77 | 37.01 | 3.7
72 | 50 | 791 | 61 | kW | 1.95 | 59 | 50 | 81 | 36.53 | 3.73
77 | 50 | 791 | 64 | MBh | 37.6 | 47 | 43 | 59 | 36.27 | 3.42
77 | 50 | 791 | 64 | S/T | 0.633 | 47 | 43 | 70 | 34.8 | 3.52
77 | 50 | 791 | 64 | ∆T | 27.9 | 47 | 43 | 72 | 34.59 | 3.53
77 | 50 | 791 | 64 | LDB | 49.1 | 47 | 43 | 75 | 34.11 | 3.57
77 | 50 | 791 | 64 | LWB | 46.9 | 47 | 43 | 77 | 33.87 | 3.58
77 | 50 | 791 | 64 | kW | 1.97 | 47 | 43 | 81 | 33.39 | 3.61
80 | 50 | 791 | 67 | MBh | 38.61 | 35 | 32 | 59 | 32.9 | 3.4
80 | 50 | 791 | 67 | S/T | 0.614 | 35 | 32 | 70 | 31.37 | 3.5
80 | 50 | 791 | 67 | ∆T | 27.8 | 35 | 32 | 72 | 31.15 | 3.51
80 | 50 | 791 | 67 | LDB | 52.2 | 35 | 32 | 75 | 30.65 | 3.55
80 | 50 | 791 | 67 | LWB | 50.6 | 35 | 32 | 77 | 30.4 | 3.56
80 | 50 | 791 | 67 | kW | 1.98 | 35 | 32 | 81 | 29.9 | 3.6
86 | 50 | 791 | 72 | MBh | 40.49 | 25 | 23 | 59 | 30.11 | 3.37
86 | 50 | 791 | 72 | S/T | 0.584 | 25 | 23 | 70 | 28.51 | 3.48
86 | 50 | 791 | 72 | ∆T | 27.7 | 25 | 23 | 72 | 28.28 | 3.5
86 | 50 | 791 | 72 | LDB | 58.3 | 25 | 23 | 75 | 27.75 | 3.53
86 | 50 | 791 | 72 | LWB | 56.7 | 25 | 23 | 77 | 27.49 | 3.55
86 | 50 | 791 | 72 | kW | 2 | 25 | 23 | 81 | 26.97 | 3.58
90 | 50 | 791 | 75 | MBh | 41.93 | 16 | 14 | 59 | 27.35 | 3.35
90 | 50 | 791 | 75 | S/T | 0.545 | 16 | 14 | 70 | 25.65 | 3.46
90 | 50 | 791 | 75 | ∆T | 26.8 | 16 | 14 | 72 | 25.4 | 3.48
90 | 50 | 791 | 75 | LDB | 63.2 | 16 | 14 | 75 | 24.85 | 3.51
90 | 50 | 791 | 75 | LWB | 60.3 | 16 | 14 | 77 | 24.57 | 3.53
90 | 50 | 791 | 75 | kW | 2.01 | 16 | 14 | 81 | 24.02 | 3.57
68 | 68 | 791 | 57 | MBh | 29.4 | 5 | 5 | 59 | 24.62 | 3.33
68 | 68 | 791 | 57 | S/T | 0.704 | 5 | 5 | 70 | 22.8 | 3.44
68 | 68 | 791 | 57 | ∆T | 24.2 | 5 | 5 | 72 | 22.52 | 3.46
68 | 68 | 791 | 57 | LDB | 43.8 | 5 | 5 | 75 | 21.93 | 3.5
68 | 68 | 791 | 57 | LWB | 41.9 | 5 | 5 | 77 | 21.63 | 3.52
68 | 68 | 791 | 57 | kW | 2.1 | 5 | 5 | 81 | 21.03 | 3.55
72 | 68 | 791 | 61 | MBh | 33.24
72 | 68 | 791 | 61 | S/T | 0.65
72 | 68 | 791 | 61 | ∆T | 25.3
72 | 68 | 791 | 61 | LDB | 46.7
72 | 68 | 791 | 61 | LWB | 45.1
72 | 68 | 791 | 61 | kW | 2.42
77 | 68 | 791 | 64 | MBh | 34.69
77 | 68 | 791 | 64 | S/T | 0.645
77 | 68 | 791 | 64 | ∆T | 26.2
77 | 68 | 791 | 64 | LDB | 50.8
77 | 68 | 791 | 64 | LWB | 48.5
77 | 68 | 791 | 64 | kW | 2.43
80 | 68 | 791 | 67 | MBh | 35.7
80 | 68 | 791 | 67 | S/T | 0.626
80 | 68 | 791 | 67 | ∆T | 26.2
80 | 68 | 791 | 67 | LDB | 53.8
80 | 68 | 791 | 67 | LWB | 52.1
80 | 68 | 791 | 67 | kW | 2.44
86 | 68 | 791 | 72 | MBh | 37.57
86 | 68 | 791 | 72 | S/T | 0.597
86 | 68 | 791 | 72 | ∆T | 26.2
86 | 68 | 791 | 72 | LDB | 59.8
86 | 68 | 791 | 72 | LWB | 58
86 | 68 | 791 | 72 | kW | 2.46
90 | 68 | 791 | 75 | MBh | 39.02
90 | 68 | 791 | 75 | S/T | 0.557
90 | 68 | 791 | 75 | ∆T | 25.4
90 | 68 | 791 | 75 | LDB | 64.6
90 | 68 | 791 | 75 | LWB | 61.5
90 | 68 | 791 | 75 | kW | 2.48
68 | 86 | 791 | 57 | MBh | 28.88
68 | 86 | 791 | 57 | S/T | 0.707
68 | 86 | 791 | 57 | ∆T | 23.9
68 | 86 | 791 | 57 | LDB | 44.1
68 | 86 | 791 | 57 | LWB | 42.2
68 | 86 | 791 | 57 | kW | 2.87
72 | 86 | 791 | 61 | MBh | 30.33
72 | 86 | 791 | 61 | S/T | 0.664
72 | 86 | 791 | 61 | ∆T | 23.6
72 | 86 | 791 | 61 | LDB | 48.4
72 | 86 | 791 | 61 | LWB | 46.7
72 | 86 | 791 | 61 | kW | 2.88
77 | 86 | 791 | 64 | MBh | 31.77
77 | 86 | 791 | 64 | S/T | 0.661
77 | 86 | 791 | 64 | ∆T | 24.6
77 | 86 | 791 | 64 | LDB | 52.4
77 | 86 | 791 | 64 | LWB | 50
77 | 86 | 791 | 64 | kW | 2.9
80 | 86 | 791 | 67 | MBh | 32.78
80 | 86 | 791 | 67 | S/T | 0.642
80 | 86 | 791 | 67 | ∆T | 24.6
80 | 86 | 791 | 67 | LDB | 55.4
80 | 86 | 791 | 67 | LWB | 53.5
80 | 86 | 791 | 67 | kW | 2.91
86 | 86 | 791 | 72 | MBh | 34.66
86 | 86 | 791 | 72 | S/T | 0.613
86 | 86 | 791 | 72 | ∆T | 24.9
86 | 86 | 791 | 72 | LDB | 61.1
86 | 86 | 791 | 72 | LWB | 59.2
86 | 86 | 791 | 72 | kW | 2.93
90 | 86 | 791 | 75 | MBh | 36.1
90 | 86 | 791 | 75 | S/T | 0.572
90 | 86 | 791 | 75 | ∆T | 24.2
90 | 86 | 791 | 75 | LDB | 65.8
90 | 86 | 791 | 75 | LWB | 62.6
90 | 86 | 791 | 75 | kW | 2.94
68 | 95 | 791 | 57 | MBh | 27.43
68 | 95 | 791 | 57 | S/T | 0.717
68 | 95 | 791 | 57 | ∆T | 23
68 | 95 | 791 | 57 | LDB | 45
68 | 95 | 791 | 57 | LWB | 43.1
68 | 95 | 791 | 57 | kW | 3.1
72 | 95 | 791 | 61 | MBh | 28.87
72 | 95 | 791 | 61 | S/T | 0.673
72 | 95 | 791 | 61 | ∆T | 22.7
72 | 95 | 791 | 61 | LDB | 49.3
72 | 95 | 791 | 61 | LWB | 47.5
72 | 95 | 791 | 61 | kW | 3.12
77 | 95 | 791 | 64 | MBh | 30.31
77 | 95 | 791 | 64 | S/T | 0.67
77 | 95 | 791 | 64 | ∆T | 23.8
77 | 95 | 791 | 64 | LDB | 53.2
77 | 95 | 791 | 64 | LWB | 50.7
77 | 95 | 791 | 64 | kW | 3.13
80 | 95 | 791 | 67 | MBh | 31.4
80 | 95 | 791 | 67 | S/T | 0.649
80 | 95 | 791 | 67 | ∆T | 23.9
80 | 95 | 791 | 67 | LDB | 56.1
80 | 95 | 791 | 67 | LWB | 54.1
80 | 95 | 791 | 67 | kW | 3.14
86 | 95 | 791 | 72 | MBh | 33.2
86 | 95 | 791 | 72 | S/T | 0.622
86 | 95 | 791 | 72 | ∆T | 24.2
86 | 95 | 791 | 72 | LDB | 61.8
86 | 95 | 791 | 72 | LWB | 59.9
86 | 95 | 791 | 72 | kW | 3.16
90 | 95 | 791 | 75 | MBh | 34.64
90 | 95 | 791 | 75 | S/T | 0.581
90 | 95 | 791 | 75 | ∆T | 23.6
90 | 95 | 791 | 75 | LDB | 66.4
90 | 95 | 791 | 75 | LWB | 63.2
90 | 95 | 791 | 75 | kW | 3.17
68 | 104 | 791 | 57 | MBh | 25.97
68 | 104 | 791 | 57 | S/T | 0.728
68 | 104 | 791 | 57 | ∆T | 22.1
68 | 104 | 791 | 57 | LDB | 45.9
68 | 104 | 791 | 57 | LWB | 43.9
68 | 104 | 791 | 57 | kW | 3.33
72 | 104 | 791 | 61 | MBh | 27.41
72 | 104 | 791 | 61 | S/T | 0.682
72 | 104 | 791 | 61 | ∆T | 21.9
72 | 104 | 791 | 61 | LDB | 50.1
72 | 104 | 791 | 61 | LWB | 48.3
72 | 104 | 791 | 61 | kW | 3.35
77 | 104 | 791 | 64 | MBh | 28.85
77 | 104 | 791 | 64 | S/T | 0.681
77 | 104 | 791 | 64 | ∆T | 23
77 | 104 | 791 | 64 | LDB | 54
77 | 104 | 791 | 64 | LWB | 51.4
77 | 104 | 791 | 64 | kW | 3.36
80 | 104 | 791 | 67 | MBh | 29.86
80 | 104 | 791 | 67 | S/T | 0.662
80 | 104 | 791 | 67 | ∆T | 23.1
80 | 104 | 791 | 67 | LDB | 56.9
80 | 104 | 791 | 67 | LWB | 54.8
80 | 104 | 791 | 67 | kW | 3.37
86 | 104 | 791 | 72 | MBh | 31.74
86 | 104 | 791 | 72 | S/T | 0.632
86 | 104 | 791 | 72 | ∆T | 23.5
86 | 104 | 791 | 72 | LDB | 62.5
86 | 104 | 791 | 72 | LWB | 60.5
86 | 104 | 791 | 72 | kW | 3.39
90 | 104 | 791 | 75 | MBh | 33.18
90 | 104 | 791 | 75 | S/T | 0.591
90 | 104 | 791 | 75 | ∆T | 22.9
90 | 104 | 791 | 75 | LDB | 67.1
90 | 104 | 791 | 75 | LWB | 63.8
90 | 104 | 791 | 75 | kW | 3.4
68 | 115 | 791 | 57 | MBh | 21.66
68 | 115 | 791 | 57 | S/T | 0.773
68 | 115 | 791 | 57 | ∆T | 19.6
68 | 115 | 791 | 57 | LDB | 48.4
68 | 115 | 791 | 57 | LWB | 46.3
68 | 115 | 791 | 57 | kW | 2.51
72 | 115 | 791 | 61 | MBh | 22.65
72 | 115 | 791 | 61 | S/T | 0.727
72 | 115 | 791 | 61 | ∆T | 19.3
72 | 115 | 791 | 61 | LDB | 52.7
72 | 115 | 791 | 61 | LWB | 50.7
72 | 115 | 791 | 61 | kW | 2.51
77 | 115 | 791 | 64 | MBh | 23.64
77 | 115 | 791 | 64 | S/T | 0.734
77 | 115 | 791 | 64 | ∆T | 20.3
77 | 115 | 791 | 64 | LDB | 56.7
77 | 115 | 791 | 64 | LWB | 53.9
77 | 115 | 791 | 64 | kW | 2.51
80 | 115 | 791 | 67 | MBh | 24.33
80 | 115 | 791 | 67 | S/T | 0.717
80 | 115 | 791 | 67 | ∆T | 20.4
80 | 115 | 791 | 67 | LDB | 59.6
80 | 115 | 791 | 67 | LWB | 57.3
80 | 115 | 791 | 67 | kW | 2.51
86 | 115 | 791 | 72 | MBh | 25.59
86 | 115 | 791 | 72 | S/T | 0.694
86 | 115 | 791 | 72 | ∆T | 20.8
86 | 115 | 791 | 72 | LDB | 65.2
86 | 115 | 791 | 72 | LWB | 62.9
86 | 115 | 791 | 72 | kW | 2.51
90 | 115 | 791 | 75 | MBh | 26.56
90 | 115 | 791 | 75 | S/T | 0.652
90 | 115 | 791 | 75 | ∆T | 20.3
90 | 115 | 791 | 75 | LDB | 69.7
90 | 115 | 791 | 75 | LWB | 66.2
90 | 115 | 791 | 75 | kW | 2.51

## RXV36AVJU9 - FTXV36AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 826 | 57 | MBh | 30.32 | 75 | 64 | 59 | 46.72 | 3.82
68 | 50 | 826 | 57 | S/T | 0.704 | 75 | 64 | 70 | 44.62 | 3.82
68 | 50 | 826 | 57 | ∆T | 23.9 | 75 | 64 | 72 | 44.32 | 3.82
68 | 50 | 826 | 57 | LDB | 44.1 | 75 | 64 | 75 | 43.67 | 3.82
68 | 50 | 826 | 57 | LWB | 42.1 | 75 | 64 | 77 | 43.34 | 3.82
68 | 50 | 826 | 57 | kW | 1.52 | 75 | 64 | 81 | 42.71 | 3.82
72 | 50 | 826 | 61 | MBh | 37.24 | 59 | 50 | 59 | 40.81 | 3.66
72 | 50 | 826 | 61 | S/T | 0.641 | 59 | 50 | 70 | 39.29 | 3.76
72 | 50 | 826 | 61 | ∆T | 26.7 | 59 | 50 | 72 | 39.07 | 3.77
72 | 50 | 826 | 61 | LDB | 45.3 | 59 | 50 | 75 | 38.57 | 3.81
72 | 50 | 826 | 61 | LWB | 43.8 | 59 | 50 | 77 | 38.32 | 3.82
72 | 50 | 826 | 61 | kW | 1.97 | 59 | 50 | 81 | 37.82 | 3.86
77 | 50 | 826 | 64 | MBh | 41.29 | 47 | 43 | 59 | 37.55 | 3.54
77 | 50 | 826 | 64 | S/T | 0.626 | 47 | 43 | 70 | 36 | 3.64
77 | 50 | 826 | 64 | ∆T | 29 | 47 | 43 | 72 | 35.81 | 3.65
77 | 50 | 826 | 64 | LDB | 48 | 47 | 43 | 75 | 35.31 | 3.69
77 | 50 | 826 | 64 | LWB | 45.9 | 47 | 43 | 77 | 35.06 | 3.7
77 | 50 | 826 | 64 | kW | 2.2 | 47 | 43 | 81 | 34.57 | 3.74
80 | 50 | 826 | 67 | MBh | 42.4 | 35 | 32 | 59 | 34.06 | 3.51
80 | 50 | 826 | 67 | S/T | 0.606 | 35 | 32 | 70 | 32.48 | 3.62
80 | 50 | 826 | 67 | ∆T | 28.8 | 35 | 32 | 72 | 32.25 | 3.63
80 | 50 | 826 | 67 | LDB | 51.2 | 35 | 32 | 75 | 31.73 | 3.67
80 | 50 | 826 | 67 | LWB | 49.6 | 35 | 32 | 77 | 31.47 | 3.69
80 | 50 | 826 | 67 | kW | 2.21 | 35 | 32 | 81 | 30.95 | 3.72
86 | 50 | 826 | 72 | MBh | 44.46 | 25 | 23 | 59 | 31.17 | 3.49
86 | 50 | 826 | 72 | S/T | 0.575 | 25 | 23 | 70 | 29.52 | 3.6
86 | 50 | 826 | 72 | ∆T | 28.7 | 25 | 23 | 72 | 29.28 | 3.62
86 | 50 | 826 | 72 | LDB | 57.3 | 25 | 23 | 75 | 28.73 | 3.65
86 | 50 | 826 | 72 | LWB | 55.8 | 25 | 23 | 77 | 28.46 | 3.67
86 | 50 | 826 | 72 | kW | 2.23 | 25 | 23 | 81 | 27.92 | 3.71
90 | 50 | 826 | 75 | MBh | 46.04 | 16 | 14 | 59 | 28.31 | 3.47
90 | 50 | 826 | 75 | S/T | 0.536 | 16 | 14 | 70 | 26.56 | 3.58
90 | 50 | 826 | 75 | ∆T | 27.7 | 16 | 14 | 72 | 26.3 | 3.6
90 | 50 | 826 | 75 | LDB | 62.3 | 16 | 14 | 75 | 25.73 | 3.64
90 | 50 | 826 | 75 | LWB | 59.4 | 16 | 14 | 77 | 25.44 | 3.66
90 | 50 | 826 | 75 | kW | 2.25 | 16 | 14 | 81 | 24.87 | 3.69
68 | 68 | 826 | 57 | MBh | 30.32 | 5 | 5 | 59 | 25.49 | 3.45
68 | 68 | 826 | 57 | S/T | 0.704 | 5 | 5 | 70 | 23.6 | 3.56
68 | 68 | 826 | 57 | ∆T | 23.9 | 5 | 5 | 72 | 23.32 | 3.58
68 | 68 | 826 | 57 | LDB | 44.1 | 5 | 5 | 75 | 22.7 | 3.62
68 | 68 | 826 | 57 | LWB | 42.1 | 5 | 5 | 77 | 22.39 | 3.64
68 | 68 | 826 | 57 | kW | 2.11 | 5 | 5 | 81 | 21.77 | 3.68
72 | 68 | 826 | 61 | MBh | 36.5
72 | 68 | 826 | 61 | S/T | 0.643
72 | 68 | 826 | 61 | ∆T | 26.3
72 | 68 | 826 | 61 | LDB | 45.7
72 | 68 | 826 | 61 | LWB | 44.2
72 | 68 | 826 | 61 | kW | 2.71
77 | 68 | 826 | 64 | MBh | 38.09
77 | 68 | 826 | 64 | S/T | 0.636
77 | 68 | 826 | 64 | ∆T | 27.1
77 | 68 | 826 | 64 | LDB | 49.9
77 | 68 | 826 | 64 | LWB | 47.5
77 | 68 | 826 | 64 | kW | 2.72
80 | 68 | 826 | 67 | MBh | 39.2
80 | 68 | 826 | 67 | S/T | 0.617
80 | 68 | 826 | 67 | ∆T | 27.1
80 | 68 | 826 | 67 | LDB | 52.9
80 | 68 | 826 | 67 | LWB | 51.1
80 | 68 | 826 | 67 | kW | 2.73
86 | 68 | 826 | 72 | MBh | 41.26
86 | 68 | 826 | 72 | S/T | 0.586
86 | 68 | 826 | 72 | ∆T | 27.1
86 | 68 | 826 | 72 | LDB | 58.9
86 | 68 | 826 | 72 | LWB | 57.2
86 | 68 | 826 | 72 | kW | 2.75
90 | 68 | 826 | 75 | MBh | 42.84
90 | 68 | 826 | 75 | S/T | 0.547
90 | 68 | 826 | 75 | ∆T | 26.3
90 | 68 | 826 | 75 | LDB | 63.7
90 | 68 | 826 | 75 | LWB | 60.7
90 | 68 | 826 | 75 | kW | 2.77
68 | 86 | 826 | 57 | MBh | 30.32
68 | 86 | 826 | 57 | S/T | 0.704
68 | 86 | 826 | 57 | ∆T | 23.9
68 | 86 | 826 | 57 | LDB | 44.1
68 | 86 | 826 | 57 | LWB | 42.1
68 | 86 | 826 | 57 | kW | 2.94
72 | 86 | 826 | 61 | MBh | 33.3
72 | 86 | 826 | 61 | S/T | 0.654
72 | 86 | 826 | 61 | ∆T | 24.4
72 | 86 | 826 | 61 | LDB | 47.6
72 | 86 | 826 | 61 | LWB | 45.9
72 | 86 | 826 | 61 | kW | 3.22
77 | 86 | 826 | 64 | MBh | 34.89
77 | 86 | 826 | 64 | S/T | 0.649
77 | 86 | 826 | 64 | ∆T | 25.4
77 | 86 | 826 | 64 | LDB | 51.6
77 | 86 | 826 | 64 | LWB | 49.1
77 | 86 | 826 | 64 | kW | 3.24
80 | 86 | 826 | 67 | MBh | 35.99
80 | 86 | 826 | 67 | S/T | 0.63
80 | 86 | 826 | 67 | ∆T | 25.4
80 | 86 | 826 | 67 | LDB | 54.6
80 | 86 | 826 | 67 | LWB | 52.6
80 | 86 | 826 | 67 | kW | 3.25
86 | 86 | 826 | 72 | MBh | 38.05
86 | 86 | 826 | 72 | S/T | 0.6
86 | 86 | 826 | 72 | ∆T | 25.6
86 | 86 | 826 | 72 | LDB | 60.4
86 | 86 | 826 | 72 | LWB | 58.5
86 | 86 | 826 | 72 | kW | 3.27
90 | 86 | 826 | 75 | MBh | 39.64
90 | 86 | 826 | 75 | S/T | 0.56
90 | 86 | 826 | 75 | ∆T | 24.9
90 | 86 | 826 | 75 | LDB | 65.1
90 | 86 | 826 | 75 | LWB | 61.9
90 | 86 | 826 | 75 | kW | 3.29
68 | 95 | 826 | 57 | MBh | 30.11
68 | 95 | 826 | 57 | S/T | 0.705
68 | 95 | 826 | 57 | ∆T | 23.8
68 | 95 | 826 | 57 | LDB | 44.2
68 | 95 | 826 | 57 | LWB | 42.3
68 | 95 | 826 | 57 | kW | 3.47
72 | 95 | 826 | 61 | MBh | 31.7
72 | 95 | 826 | 61 | S/T | 0.662
72 | 95 | 826 | 61 | ∆T | 23.5
72 | 95 | 826 | 61 | LDB | 48.5
72 | 95 | 826 | 61 | LWB | 46.7
72 | 95 | 826 | 61 | kW | 3.48
77 | 95 | 826 | 64 | MBh | 33.28
77 | 95 | 826 | 64 | S/T | 0.658
77 | 95 | 826 | 64 | ∆T | 24.5
77 | 95 | 826 | 64 | LDB | 52.5
77 | 95 | 826 | 64 | LWB | 49.9
77 | 95 | 826 | 64 | kW | 3.5
80 | 95 | 826 | 67 | MBh | 34.4
80 | 95 | 826 | 67 | S/T | 0.638
80 | 95 | 826 | 67 | ∆T | 24.6
80 | 95 | 826 | 67 | LDB | 55.4
80 | 95 | 826 | 67 | LWB | 53.4
80 | 95 | 826 | 67 | kW | 3.51
86 | 95 | 826 | 72 | MBh | 36.45
86 | 95 | 826 | 72 | S/T | 0.609
86 | 95 | 826 | 72 | ∆T | 24.9
86 | 95 | 826 | 72 | LDB | 61.1
86 | 95 | 826 | 72 | LWB | 59.1
86 | 95 | 826 | 72 | kW | 3.53
90 | 95 | 826 | 75 | MBh | 38.04
90 | 95 | 826 | 75 | S/T | 0.568
90 | 95 | 826 | 75 | ∆T | 24.2
90 | 95 | 826 | 75 | LDB | 65.8
90 | 95 | 826 | 75 | LWB | 62.5
90 | 95 | 826 | 75 | kW | 3.55
68 | 104 | 826 | 57 | MBh | 28.17
68 | 104 | 826 | 57 | S/T | 0.717
68 | 104 | 826 | 57 | ∆T | 22.7
68 | 104 | 826 | 57 | LDB | 45.3
68 | 104 | 826 | 57 | LWB | 43.3
68 | 104 | 826 | 57 | kW | 3.58
72 | 104 | 826 | 61 | MBh | 29.65
72 | 104 | 826 | 61 | S/T | 0.673
72 | 104 | 826 | 61 | ∆T | 22.4
72 | 104 | 826 | 61 | LDB | 49.6
72 | 104 | 826 | 61 | LWB | 47.8
72 | 104 | 826 | 61 | kW | 3.58
77 | 104 | 826 | 64 | MBh | 31.12
77 | 104 | 826 | 64 | S/T | 0.671
77 | 104 | 826 | 64 | ∆T | 23.4
77 | 104 | 826 | 64 | LDB | 53.6
77 | 104 | 826 | 64 | LWB | 50.9
77 | 104 | 826 | 64 | kW | 3.58
80 | 104 | 826 | 67 | MBh | 32.14
80 | 104 | 826 | 67 | S/T | 0.652
80 | 104 | 826 | 67 | ∆T | 23.5
80 | 104 | 826 | 67 | LDB | 56.5
80 | 104 | 826 | 67 | LWB | 54.4
80 | 104 | 826 | 67 | kW | 3.58
86 | 104 | 826 | 72 | MBh | 34.03
86 | 104 | 826 | 72 | S/T | 0.623
86 | 104 | 826 | 72 | ∆T | 23.8
86 | 104 | 826 | 72 | LDB | 62.2
86 | 104 | 826 | 72 | LWB | 60.1
86 | 104 | 826 | 72 | kW | 3.58
90 | 104 | 826 | 75 | MBh | 35.47
90 | 104 | 826 | 75 | S/T | 0.582
90 | 104 | 826 | 75 | ∆T | 23.2
90 | 104 | 826 | 75 | LDB | 66.8
90 | 104 | 826 | 75 | LWB | 63.5
90 | 104 | 826 | 75 | kW | 3.58
68 | 115 | 826 | 57 | MBh | 22.26
68 | 115 | 826 | 57 | S/T | 0.774
68 | 115 | 826 | 57 | ∆T | 19.3
68 | 115 | 826 | 57 | LDB | 48.7
68 | 115 | 826 | 57 | LWB | 46.5
68 | 115 | 826 | 57 | kW | 2.51
72 | 115 | 826 | 61 | MBh | 23.23
72 | 115 | 826 | 61 | S/T | 0.728
72 | 115 | 826 | 61 | ∆T | 19
72 | 115 | 826 | 61 | LDB | 53
72 | 115 | 826 | 61 | LWB | 50.9
72 | 115 | 826 | 61 | kW | 2.51
77 | 115 | 826 | 64 | MBh | 24.2
77 | 115 | 826 | 64 | S/T | 0.736
77 | 115 | 826 | 64 | ∆T | 20
77 | 115 | 826 | 64 | LDB | 57
77 | 115 | 826 | 64 | LWB | 54.1
77 | 115 | 826 | 64 | kW | 2.51
80 | 115 | 826 | 67 | MBh | 24.88
80 | 115 | 826 | 67 | S/T | 0.72
80 | 115 | 826 | 67 | ∆T | 20.1
80 | 115 | 826 | 67 | LDB | 59.9
80 | 115 | 826 | 67 | LWB | 57.5
80 | 115 | 826 | 67 | kW | 2.51
86 | 115 | 826 | 72 | MBh | 26.12
86 | 115 | 826 | 72 | S/T | 0.698
86 | 115 | 826 | 72 | ∆T | 20.4
86 | 115 | 826 | 72 | LDB | 65.6
86 | 115 | 826 | 72 | LWB | 63.1
86 | 115 | 826 | 72 | kW | 2.51
90 | 115 | 826 | 75 | MBh | 27.07
90 | 115 | 826 | 75 | S/T | 0.656
90 | 115 | 826 | 75 | ∆T | 19.9
90 | 115 | 826 | 75 | LDB | 70.1
90 | 115 | 826 | 75 | LWB | 66.4
90 | 115 | 826 | 75 | kW | 2.51

## RXP09AVJU9 - FDMA09AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 293 | 57 | MBh | 10.42 | 75 | 60 | 59 | 14.13 | 1.36
68 | 50 | 293 | 57 | S/T | 0.731 | 75 | 60 | 70 | 13.66 | 1.39
68 | 50 | 293 | 57 | ∆T | 24.1 | 75 | 60 | 72 | 13.59 | 1.4
68 | 50 | 293 | 57 | LDB | 43.9 | 75 | 60 | 75 | 13.43 | 1.41
68 | 50 | 293 | 57 | LWB | 42.7 | 75 | 60 | 77 | 13.36 | 1.41
68 | 50 | 293 | 57 | kW | 0.53 | 75 | 60 | 81 | 13.2 | 1.43
72 | 50 | 293 | 61 | MBh | 10.85 | 47 | 43 | 59 | 13.34 | 1.25
72 | 50 | 293 | 61 | S/T | 0.688 | 47 | 43 | 70 | 12.8 | 1.29
72 | 50 | 293 | 61 | ∆T | 23.6 | 47 | 43 | 72 | 12.72 | 1.3
72 | 50 | 293 | 61 | LDB | 48.4 | 47 | 43 | 75 | 12.54 | 1.31
72 | 50 | 293 | 61 | LWB | 47.3 | 47 | 43 | 77 | 12.46 | 1.31
72 | 50 | 293 | 61 | kW | 0.53 | 47 | 43 | 81 | 12.28 | 1.32
77 | 50 | 293 | 64 | MBh | 11.29 | 35 | 32 | 59 | 12.85 | 1.39
77 | 50 | 293 | 64 | S/T | 0.691 | 35 | 32 | 70 | 12.26 | 1.43
77 | 50 | 293 | 64 | ∆T | 24.6 | 35 | 32 | 72 | 12.17 | 1.43
77 | 50 | 293 | 64 | LDB | 52.4 | 35 | 32 | 75 | 11.97 | 1.45
77 | 50 | 293 | 64 | LWB | 50.6 | 35 | 32 | 77 | 11.88 | 1.45
77 | 50 | 293 | 64 | kW | 0.54 | 35 | 32 | 81 | 11.68 | 1.47
80 | 50 | 293 | 67 | MBh | 11.59 | 25 | 23 | 59 | 12.47 | 1.5
80 | 50 | 293 | 67 | S/T | 0.674 | 25 | 23 | 70 | 11.8 | 1.54
80 | 50 | 293 | 67 | ∆T | 24.7 | 25 | 23 | 72 | 11.71 | 1.55
80 | 50 | 293 | 67 | LDB | 55.3 | 25 | 23 | 75 | 11.49 | 1.57
80 | 50 | 293 | 67 | LWB | 54.1 | 25 | 23 | 77 | 11.38 | 1.57
80 | 50 | 293 | 67 | kW | 0.54 | 25 | 23 | 81 | 11.17 | 1.59
86 | 50 | 293 | 72 | MBh | 12.15 | 16 | 14 | 59 | 12.1 | 1.61
86 | 50 | 293 | 72 | S/T | 0.649 | 16 | 14 | 70 | 11.35 | 1.66
86 | 50 | 293 | 72 | ∆T | 24.9 | 16 | 14 | 72 | 11.24 | 1.67
86 | 50 | 293 | 72 | LDB | 61.1 | 16 | 14 | 75 | 11 | 1.68
86 | 50 | 293 | 72 | LWB | 60 | 16 | 14 | 77 | 10.87 | 1.69
86 | 50 | 293 | 72 | kW | 0.67 | 16 | 14 | 81 | 10.63 | 1.71
90 | 50 | 293 | 75 | MBh | 12.58 | 5 | 5 | 59 | 11.77 | 1.72
90 | 50 | 293 | 75 | S/T | 0.609 | 5 | 5 | 70 | 10.9 | 1.77
90 | 50 | 293 | 75 | ∆T | 24.2 | 5 | 5 | 72 | 10.77 | 1.78
90 | 50 | 293 | 75 | LDB | 65.8 | 5 | 5 | 75 | 10.48 | 1.8
90 | 50 | 293 | 75 | LWB | 63.4 | 5 | 5 | 77 | 10.34 | 1.81
90 | 50 | 293 | 75 | kW | 0.67 | 5 | 5 | 81 | 10.06 | 1.83
68 | 68 | 293 | 57 | MBh | 9.54 | -4 | -4 | 59 | 9.71 | 1.68
68 | 68 | 293 | 57 | S/T | 0.753 | -4 | -4 | 70 | 8.81 | 1.74
68 | 68 | 293 | 57 | ∆T | 22.7 | -4 | -4 | 72 | 8.68 | 1.74
68 | 68 | 293 | 57 | LDB | 45.3 | -4 | -4 | 75 | 8.38 | 1.76
68 | 68 | 293 | 57 | LWB | 44 | -4 | -4 | 77 | 8.14 | 1.73
68 | 68 | 293 | 57 | kW | 0.66 | -4 | -4 | 81 | 7.04 | 1.43
72 | 68 | 293 | 61 | MBh | 9.98 | -13 | -14 | 59 | 7.57 | 1.64
72 | 68 | 293 | 61 | S/T | 0.707 | -13 | -14 | 70 | 5.53 | 1.24
72 | 68 | 293 | 61 | ∆T | 22.3 | -13 | -14 | 72 | 5.04 | 1.1
72 | 68 | 293 | 61 | LDB | 49.7 | -13 | -14 | 75 | 3.94 | 0.83
72 | 68 | 293 | 61 | LWB | 48.5 | -13 | -14 | 77 | 3.39 | 0.7
72 | 68 | 293 | 61 | kW | 0.66 | -13 | -14 | 81 | 2.3 | 0.45
77 | 68 | 293 | 64 | MBh | 10.41
77 | 68 | 293 | 64 | S/T | 0.712
77 | 68 | 293 | 64 | ∆T | 23.4
77 | 68 | 293 | 64 | LDB | 53.6
77 | 68 | 293 | 64 | LWB | 51.8
77 | 68 | 293 | 64 | kW | 0.66
80 | 68 | 293 | 67 | MBh | 10.71
80 | 68 | 293 | 67 | S/T | 0.695
80 | 68 | 293 | 67 | ∆T | 23.5
80 | 68 | 293 | 67 | LDB | 56.5
80 | 68 | 293 | 67 | LWB | 55.2
80 | 68 | 293 | 67 | kW | 0.67
86 | 68 | 293 | 72 | MBh | 11.28
86 | 68 | 293 | 72 | S/T | 0.67
86 | 68 | 293 | 72 | ∆T | 23.9
86 | 68 | 293 | 72 | LDB | 62.1
86 | 68 | 293 | 72 | LWB | 61
86 | 68 | 293 | 72 | kW | 0.67
90 | 68 | 293 | 75 | MBh | 11.71
90 | 68 | 293 | 75 | S/T | 0.629
90 | 68 | 293 | 75 | ∆T | 23.3
90 | 68 | 293 | 75 | LDB | 66.7
90 | 68 | 293 | 75 | LWB | 64.3
90 | 68 | 293 | 75 | kW | 0.67
68 | 86 | 293 | 57 | MBh | 8.67
68 | 86 | 293 | 57 | S/T | 0.779
68 | 86 | 293 | 57 | ∆T | 21.3
68 | 86 | 293 | 57 | LDB | 46.7
68 | 86 | 293 | 57 | LWB | 45.4
68 | 86 | 293 | 57 | kW | 0.78
72 | 86 | 293 | 61 | MBh | 9.1
72 | 86 | 293 | 61 | S/T | 0.731
72 | 86 | 293 | 61 | ∆T | 21
72 | 86 | 293 | 61 | LDB | 51
72 | 86 | 293 | 61 | LWB | 49.7
72 | 86 | 293 | 61 | kW | 0.79
77 | 86 | 293 | 64 | MBh | 9.53
77 | 86 | 293 | 64 | S/T | 0.738
77 | 86 | 293 | 64 | ∆T | 22.2
77 | 86 | 293 | 64 | LDB | 54.8
77 | 86 | 293 | 64 | LWB | 52.9
77 | 86 | 293 | 64 | kW | 0.79
80 | 86 | 293 | 67 | MBh | 9.84
80 | 86 | 293 | 67 | S/T | 0.721
80 | 86 | 293 | 67 | ∆T | 22.4
80 | 86 | 293 | 67 | LDB | 57.6
80 | 86 | 293 | 67 | LWB | 56.3
80 | 86 | 293 | 67 | kW | 0.79
86 | 86 | 293 | 72 | MBh | 10.4
86 | 86 | 293 | 72 | S/T | 0.696
86 | 86 | 293 | 72 | ∆T | 22.9
86 | 86 | 293 | 72 | LDB | 63.1
86 | 86 | 293 | 72 | LWB | 61.9
86 | 86 | 293 | 72 | kW | 0.8
90 | 86 | 293 | 75 | MBh | 10.83
90 | 86 | 293 | 75 | S/T | 0.653
90 | 86 | 293 | 75 | ∆T | 22.3
90 | 86 | 293 | 75 | LDB | 67.7
90 | 86 | 293 | 75 | LWB | 65.2
90 | 86 | 293 | 75 | kW | 0.8
68 | 95 | 293 | 57 | MBh | 8.23
68 | 95 | 293 | 57 | S/T | 0.795
68 | 95 | 293 | 57 | ∆T | 20.7
68 | 95 | 293 | 57 | LDB | 47.3
68 | 95 | 293 | 57 | LWB | 46
68 | 95 | 293 | 57 | kW | 0.85
72 | 95 | 293 | 61 | MBh | 8.66
72 | 95 | 293 | 61 | S/T | 0.745
72 | 95 | 293 | 61 | ∆T | 20.4
72 | 95 | 293 | 61 | LDB | 51.6
72 | 95 | 293 | 61 | LWB | 50.4
72 | 95 | 293 | 61 | kW | 0.85
77 | 95 | 293 | 64 | MBh | 9.1
77 | 95 | 293 | 64 | S/T | 0.753
77 | 95 | 293 | 64 | ∆T | 21.6
77 | 95 | 293 | 64 | LDB | 55.4
77 | 95 | 293 | 64 | LWB | 53.5
77 | 95 | 293 | 64 | kW | 0.85
80 | 95 | 293 | 67 | MBh | 9.4
80 | 95 | 293 | 67 | S/T | 0.735
80 | 95 | 293 | 67 | ∆T | 21.8
80 | 95 | 293 | 67 | LDB | 58.2
80 | 95 | 293 | 67 | LWB | 56.8
80 | 95 | 293 | 67 | kW | 0.86
86 | 95 | 293 | 72 | MBh | 9.96
86 | 95 | 293 | 72 | S/T | 0.711
86 | 95 | 293 | 72 | ∆T | 22.4
86 | 95 | 293 | 72 | LDB | 63.6
86 | 95 | 293 | 72 | LWB | 62.4
86 | 95 | 293 | 72 | kW | 0.86
90 | 95 | 293 | 75 | MBh | 10.4
90 | 95 | 293 | 75 | S/T | 0.666
90 | 95 | 293 | 75 | ∆T | 21.9
90 | 95 | 293 | 75 | LDB | 68.1
90 | 95 | 293 | 75 | LWB | 65.6
90 | 95 | 293 | 75 | kW | 0.86
68 | 104 | 293 | 57 | MBh | 7.79
68 | 104 | 293 | 57 | S/T | 0.813
68 | 104 | 293 | 57 | ∆T | 20
68 | 104 | 293 | 57 | LDB | 48
68 | 104 | 293 | 57 | LWB | 46.7
68 | 104 | 293 | 57 | kW | 0.91
72 | 104 | 293 | 61 | MBh | 8.23
72 | 104 | 293 | 61 | S/T | 0.761
72 | 104 | 293 | 61 | ∆T | 19.8
72 | 104 | 293 | 61 | LDB | 52.2
72 | 104 | 293 | 61 | LWB | 50.9
72 | 104 | 293 | 61 | kW | 0.91
77 | 104 | 293 | 64 | MBh | 8.66
77 | 104 | 293 | 64 | S/T | 0.77
77 | 104 | 293 | 64 | ∆T | 21.1
77 | 104 | 293 | 64 | LDB | 55.9
77 | 104 | 293 | 64 | LWB | 54
77 | 104 | 293 | 64 | kW | 0.92
80 | 104 | 293 | 67 | MBh | 2.76
80 | 104 | 293 | 67 | S/T | 1
80 | 104 | 293 | 67 | ∆T | 8.7
80 | 104 | 293 | 67 | LDB | 71.3
80 | 104 | 293 | 67 | LWB | 64.2
80 | 104 | 293 | 67 | kW | 0.92
86 | 104 | 293 | 72 | MBh | 9.53
86 | 104 | 293 | 72 | S/T | 0.726
86 | 104 | 293 | 72 | ∆T | 21.9
86 | 104 | 293 | 72 | LDB | 64.1
86 | 104 | 293 | 72 | LWB | 62.8
86 | 104 | 293 | 72 | kW | 0.92
90 | 104 | 293 | 75 | MBh | 9.96
90 | 104 | 293 | 75 | S/T | 0.682
90 | 104 | 293 | 75 | ∆T | 21.5
90 | 104 | 293 | 75 | LDB | 68.5
90 | 104 | 293 | 75 | LWB | 66.1
90 | 104 | 293 | 75 | kW | 0.93
68 | 115 | 293 | 57 | MBh | 7.27
68 | 115 | 293 | 57 | S/T | 0.836
68 | 115 | 293 | 57 | ∆T | 19.2
68 | 115 | 293 | 57 | LDB | 48.8
68 | 115 | 293 | 57 | LWB | 47.4
68 | 115 | 293 | 57 | kW | 0.99
72 | 115 | 293 | 61 | MBh | 7.7
72 | 115 | 293 | 61 | S/T | 0.783
72 | 115 | 293 | 61 | ∆T | 19.1
72 | 115 | 293 | 61 | LDB | 52.9
72 | 115 | 293 | 61 | LWB | 51.6
72 | 115 | 293 | 61 | kW | 0.99
77 | 115 | 293 | 64 | MBh | 8.13
77 | 115 | 293 | 64 | S/T | 0.793
77 | 115 | 293 | 64 | ∆T | 20.4
77 | 115 | 293 | 64 | LDB | 56.6
77 | 115 | 293 | 64 | LWB | 54.7
77 | 115 | 293 | 64 | kW | 0.99
80 | 115 | 293 | 67 | MBh | 8.44
80 | 115 | 293 | 67 | S/T | 0.774
80 | 115 | 293 | 67 | ∆T | 20.6
80 | 115 | 293 | 67 | LDB | 59.4
80 | 115 | 293 | 67 | LWB | 58
80 | 115 | 293 | 67 | kW | 1
86 | 115 | 293 | 72 | MBh | 9
86 | 115 | 293 | 72 | S/T | 0.749
86 | 115 | 293 | 72 | ∆T | 21.3
86 | 115 | 293 | 72 | LDB | 64.7
86 | 115 | 293 | 72 | LWB | 63.4
86 | 115 | 293 | 72 | kW | 1
90 | 115 | 293 | 75 | MBh | 9.43
90 | 115 | 293 | 75 | S/T | 0.702
90 | 115 | 293 | 75 | ∆T | 20.9
90 | 115 | 293 | 75 | LDB | 69.1
90 | 115 | 293 | 75 | LWB | 66.6
90 | 115 | 293 | 75 | kW | 1

## RXP12AVJU9 - FDMA12AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 318 | 57 | MBh | 13.75 | 75 | 60 | 59 | 20.03 | 1.81
68 | 50 | 318 | 57 | S/T | 0.692 | 75 | 60 | 70 | 19.36 | 1.85
68 | 50 | 318 | 57 | ∆T | 27.7 | 75 | 60 | 72 | 19.11 | 1.84
68 | 50 | 318 | 57 | LDB | 40.3 | 75 | 60 | 75 | 17.92 | 1.68
68 | 50 | 318 | 57 | LWB | 39 | 75 | 60 | 77 | 17.32 | 1.61
68 | 50 | 318 | 57 | kW | 0.77 | 75 | 60 | 81 | 16.13 | 1.46
72 | 50 | 318 | 61 | MBh | 14.32 | 47 | 43 | 59 | 17.72 | 1.67
72 | 50 | 318 | 61 | S/T | 0.651 | 47 | 43 | 70 | 17 | 1.72
72 | 50 | 318 | 61 | ∆T | 27.1 | 47 | 43 | 72 | 16.9 | 1.73
72 | 50 | 318 | 61 | LDB | 44.9 | 47 | 43 | 75 | 16.66 | 1.74
72 | 50 | 318 | 61 | LWB | 43.8 | 47 | 43 | 77 | 16.54 | 1.75
72 | 50 | 318 | 61 | kW | 0.78 | 47 | 43 | 81 | 16.13 | 1.73
77 | 50 | 318 | 64 | MBh | 14.89 | 35 | 32 | 59 | 16.27 | 1.73
77 | 50 | 318 | 64 | S/T | 0.646 | 35 | 32 | 70 | 15.52 | 1.78
77 | 50 | 318 | 64 | ∆T | 28 | 35 | 32 | 72 | 15.4 | 1.79
77 | 50 | 318 | 64 | LDB | 49 | 35 | 32 | 75 | 15.16 | 1.8
77 | 50 | 318 | 64 | LWB | 47.2 | 35 | 32 | 77 | 15.03 | 1.81
77 | 50 | 318 | 64 | kW | 0.78 | 35 | 32 | 81 | 14.78 | 1.83
80 | 50 | 318 | 67 | MBh | 15.29 | 25 | 23 | 59 | 15.08 | 1.77
80 | 50 | 318 | 67 | S/T | 0.628 | 25 | 23 | 70 | 14.28 | 1.83
80 | 50 | 318 | 67 | ∆T | 28 | 25 | 23 | 72 | 14.16 | 1.83
80 | 50 | 318 | 67 | LDB | 52 | 25 | 23 | 75 | 13.9 | 1.85
80 | 50 | 318 | 67 | LWB | 50.9 | 25 | 23 | 77 | 13.77 | 1.86
80 | 50 | 318 | 67 | kW | 0.79 | 25 | 23 | 81 | 13.5 | 1.88
86 | 50 | 318 | 72 | MBh | 16.03 | 16 | 14 | 59 | 13.9 | 1.81
86 | 50 | 318 | 72 | S/T | 0.599 | 16 | 14 | 70 | 13.04 | 1.87
86 | 50 | 318 | 72 | ∆T | 28 | 16 | 14 | 72 | 12.91 | 1.88
86 | 50 | 318 | 72 | LDB | 58 | 16 | 14 | 75 | 12.63 | 1.9
86 | 50 | 318 | 72 | LWB | 57 | 16 | 14 | 77 | 12.49 | 1.91
86 | 50 | 318 | 72 | kW | 0.8 | 16 | 14 | 81 | 12.21 | 1.93
90 | 50 | 318 | 75 | MBh | 16.6 | 5 | 5 | 59 | 12.74 | 1.86
90 | 50 | 318 | 75 | S/T | 0.56 | 5 | 5 | 70 | 11.8 | 1.92
90 | 50 | 318 | 75 | ∆T | 27.1 | 5 | 5 | 72 | 11.66 | 1.93
90 | 50 | 318 | 75 | LDB | 62.9 | 5 | 5 | 75 | 11.35 | 1.95
90 | 50 | 318 | 75 | LWB | 60.5 | 5 | 5 | 77 | 11.2 | 1.96
90 | 50 | 318 | 75 | kW | 0.99 | 5 | 5 | 81 | 10.89 | 1.98
68 | 68 | 318 | 57 | MBh | 12.59 | -4 | -4 | 59 | 10.51 | 1.81
68 | 68 | 318 | 57 | S/T | 0.706 | -4 | -4 | 70 | 9.54 | 1.88
68 | 68 | 318 | 57 | ∆T | 25.9 | -4 | -4 | 72 | 9.4 | 1.89
68 | 68 | 318 | 57 | LDB | 42.1 | -4 | -4 | 75 | 9.08 | 1.91
68 | 68 | 318 | 57 | LWB | 40.8 | -4 | -4 | 77 | 8.85 | 1.89
68 | 68 | 318 | 57 | kW | 0.96 | -4 | -4 | 81 | 7.66 | 1.58
72 | 68 | 318 | 61 | MBh | 13.16 | -13 | -14 | 59 | 8.19 | 1.78
72 | 68 | 318 | 61 | S/T | 0.663 | -13 | -14 | 70 | 6.02 | 1.36
72 | 68 | 318 | 61 | ∆T | 25.4 | -13 | -14 | 72 | 5.48 | 1.22
72 | 68 | 318 | 61 | LDB | 46.6 | -13 | -14 | 75 | 4.29 | 0.92
72 | 68 | 318 | 61 | LWB | 45.4 | -13 | -14 | 77 | 3.69 | 0.78
72 | 68 | 318 | 61 | kW | 0.96 | -13 | -14 | 81 | 2.5 | 0.51
77 | 68 | 318 | 64 | MBh | 13.74
77 | 68 | 318 | 64 | S/T | 0.66
77 | 68 | 318 | 64 | ∆T | 26.4
77 | 68 | 318 | 64 | LDB | 50.6
77 | 68 | 318 | 64 | LWB | 48.7
77 | 68 | 318 | 64 | kW | 0.97
80 | 68 | 318 | 67 | MBh | 14.14
80 | 68 | 318 | 67 | S/T | 0.642
80 | 68 | 318 | 67 | ∆T | 26.4
80 | 68 | 318 | 67 | LDB | 53.6
80 | 68 | 318 | 67 | LWB | 52.3
80 | 68 | 318 | 67 | kW | 0.97
86 | 68 | 318 | 72 | MBh | 14.88
86 | 68 | 318 | 72 | S/T | 0.614
86 | 68 | 318 | 72 | ∆T | 26.6
86 | 68 | 318 | 72 | LDB | 59.4
86 | 68 | 318 | 72 | LWB | 58.2
86 | 68 | 318 | 72 | kW | 0.98
90 | 68 | 318 | 75 | MBh | 15.45
90 | 68 | 318 | 75 | S/T | 0.574
90 | 68 | 318 | 75 | ∆T | 25.8
90 | 68 | 318 | 75 | LDB | 64.2
90 | 68 | 318 | 75 | LWB | 61.7
90 | 68 | 318 | 75 | kW | 0.99
68 | 86 | 318 | 57 | MBh | 11.44
68 | 86 | 318 | 57 | S/T | 0.724
68 | 86 | 318 | 57 | ∆T | 24.1
68 | 86 | 318 | 57 | LDB | 43.9
68 | 86 | 318 | 57 | LWB | 42.5
68 | 86 | 318 | 57 | kW | 1.14
72 | 86 | 318 | 61 | MBh | 12.01
72 | 86 | 318 | 61 | S/T | 0.679
72 | 86 | 318 | 61 | ∆T | 23.8
72 | 86 | 318 | 61 | LDB | 48.2
72 | 86 | 318 | 61 | LWB | 47
72 | 86 | 318 | 61 | kW | 1.15
77 | 86 | 318 | 64 | MBh | 12.58
77 | 86 | 318 | 64 | S/T | 0.679
77 | 86 | 318 | 64 | ∆T | 24.9
77 | 86 | 318 | 64 | LDB | 52.1
77 | 86 | 318 | 64 | LWB | 50.2
77 | 86 | 318 | 64 | kW | 1.15
80 | 86 | 318 | 67 | MBh | 12.98
80 | 86 | 318 | 67 | S/T | 0.66
80 | 86 | 318 | 67 | ∆T | 25
80 | 86 | 318 | 67 | LDB | 55
80 | 86 | 318 | 67 | LWB | 53.7
80 | 86 | 318 | 67 | kW | 1.16
86 | 86 | 318 | 72 | MBh | 13.72
86 | 86 | 318 | 72 | S/T | 0.633
86 | 86 | 318 | 72 | ∆T | 25.3
86 | 86 | 318 | 72 | LDB | 60.7
86 | 86 | 318 | 72 | LWB | 59.5
86 | 86 | 318 | 72 | kW | 1.16
90 | 86 | 318 | 75 | MBh | 14.29
90 | 86 | 318 | 75 | S/T | 0.592
90 | 86 | 318 | 75 | ∆T | 24.6
90 | 86 | 318 | 75 | LDB | 65.4
90 | 86 | 318 | 75 | LWB | 62.8
90 | 86 | 318 | 75 | kW | 1.17
68 | 95 | 318 | 57 | MBh | 10.86
68 | 95 | 318 | 57 | S/T | 0.735
68 | 95 | 318 | 57 | ∆T | 23.2
68 | 95 | 318 | 57 | LDB | 44.8
68 | 95 | 318 | 57 | LWB | 43.3
68 | 95 | 318 | 57 | kW | 1.24
72 | 95 | 318 | 61 | MBh | 11.43
72 | 95 | 318 | 61 | S/T | 0.689
72 | 95 | 318 | 61 | ∆T | 22.9
72 | 95 | 318 | 61 | LDB | 49.1
72 | 95 | 318 | 61 | LWB | 47.7
72 | 95 | 318 | 61 | kW | 1.24
77 | 95 | 318 | 64 | MBh | 12
77 | 95 | 318 | 64 | S/T | 0.69
77 | 95 | 318 | 64 | ∆T | 24.1
77 | 95 | 318 | 64 | LDB | 52.9
77 | 95 | 318 | 64 | LWB | 50.9
77 | 95 | 318 | 64 | kW | 1.25
80 | 95 | 318 | 67 | MBh | 12.4
80 | 95 | 318 | 67 | S/T | 0.672
80 | 95 | 318 | 67 | ∆T | 24.3
80 | 95 | 318 | 67 | LDB | 55.7
80 | 95 | 318 | 67 | LWB | 54.4
80 | 95 | 318 | 67 | kW | 1.25
86 | 95 | 318 | 72 | MBh | 13.15
86 | 95 | 318 | 72 | S/T | 0.643
86 | 95 | 318 | 72 | ∆T | 24.6
86 | 95 | 318 | 72 | LDB | 61.4
86 | 95 | 318 | 72 | LWB | 60
86 | 95 | 318 | 72 | kW | 1.26
90 | 95 | 318 | 75 | MBh | 13.72
90 | 95 | 318 | 75 | S/T | 0.601
90 | 95 | 318 | 75 | ∆T | 24
90 | 95 | 318 | 75 | LDB | 66
90 | 95 | 318 | 75 | LWB | 63.4
90 | 95 | 318 | 75 | kW | 1.26
68 | 104 | 318 | 57 | MBh | 10.28
68 | 104 | 318 | 57 | S/T | 0.748
68 | 104 | 318 | 57 | ∆T | 22.4
68 | 104 | 318 | 57 | LDB | 45.6
68 | 104 | 318 | 57 | LWB | 44.1
68 | 104 | 318 | 57 | kW | 1.33
72 | 104 | 318 | 61 | MBh | 10.85
72 | 104 | 318 | 61 | S/T | 0.701
72 | 104 | 318 | 61 | ∆T | 22.2
72 | 104 | 318 | 61 | LDB | 49.8
72 | 104 | 318 | 61 | LWB | 48.5
72 | 104 | 318 | 61 | kW | 1.33
77 | 104 | 318 | 64 | MBh | 11.43
77 | 104 | 318 | 64 | S/T | 0.702
77 | 104 | 318 | 64 | ∆T | 23.4
77 | 104 | 318 | 64 | LDB | 53.6
77 | 104 | 318 | 64 | LWB | 51.6
77 | 104 | 318 | 64 | kW | 1.34
80 | 104 | 318 | 67 | MBh | 3.64
80 | 104 | 318 | 67 | S/T | 1
80 | 104 | 318 | 67 | ∆T | 10.6
80 | 104 | 318 | 67 | LDB | 69.4
80 | 104 | 318 | 67 | LWB | 63.5
80 | 104 | 318 | 67 | kW | 1.34
86 | 104 | 318 | 72 | MBh | 12.57
86 | 104 | 318 | 72 | S/T | 0.656
86 | 104 | 318 | 72 | ∆T | 24
86 | 104 | 318 | 72 | LDB | 62
86 | 104 | 318 | 72 | LWB | 60.6
86 | 104 | 318 | 72 | kW | 1.35
90 | 104 | 318 | 75 | MBh | 13.14
90 | 104 | 318 | 75 | S/T | 0.613
90 | 104 | 318 | 75 | ∆T | 23.4
90 | 104 | 318 | 75 | LDB | 66.6
90 | 104 | 318 | 75 | LWB | 63.9
90 | 104 | 318 | 75 | kW | 1.36
68 | 115 | 318 | 57 | MBh | 9.59
68 | 115 | 318 | 57 | S/T | 0.766
68 | 115 | 318 | 57 | ∆T | 21.4
68 | 115 | 318 | 57 | LDB | 46.6
68 | 115 | 318 | 57 | LWB | 45.1
68 | 115 | 318 | 57 | kW | 1.2
72 | 115 | 318 | 61 | MBh | 10.16
72 | 115 | 318 | 61 | S/T | 0.718
72 | 115 | 318 | 61 | ∆T | 21.2
72 | 115 | 318 | 61 | LDB | 50.8
72 | 115 | 318 | 61 | LWB | 49.4
72 | 115 | 318 | 61 | kW | 1.2
77 | 115 | 318 | 64 | MBh | 10.73
77 | 115 | 318 | 64 | S/T | 0.719
77 | 115 | 318 | 64 | ∆T | 22.5
77 | 115 | 318 | 64 | LDB | 54.5
77 | 115 | 318 | 64 | LWB | 52.5
77 | 115 | 318 | 64 | kW | 1.2
80 | 115 | 318 | 67 | MBh | 11.13
80 | 115 | 318 | 67 | S/T | 0.701
80 | 115 | 318 | 67 | ∆T | 22.7
80 | 115 | 318 | 67 | LDB | 57.3
80 | 115 | 318 | 67 | LWB | 55.8
80 | 115 | 318 | 67 | kW | 1.2
86 | 115 | 318 | 72 | MBh | 11.87
86 | 115 | 318 | 72 | S/T | 0.672
86 | 115 | 318 | 72 | ∆T | 23.2
86 | 115 | 318 | 72 | LDB | 62.8
86 | 115 | 318 | 72 | LWB | 61.3
86 | 115 | 318 | 72 | kW | 1.2
90 | 115 | 318 | 75 | MBh | 12.45
90 | 115 | 318 | 75 | S/T | 0.627
90 | 115 | 318 | 75 | ∆T | 22.7
90 | 115 | 318 | 75 | LDB | 67.3
90 | 115 | 318 | 75 | LWB | 64.6
90 | 115 | 318 | 75 | kW | 1.2

## RXP15AVJU9 - FDMA15AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 466 | 57 | MBh | 17.4 | 75 | 60 | 59 | 23.11 | 1.95
68 | 50 | 466 | 57 | S/T | 0.719 | 75 | 60 | 70 | 22.47 | 1.99
68 | 50 | 466 | 57 | ∆T | 24.9 | 75 | 60 | 72 | 22.21 | 2.01
68 | 50 | 466 | 57 | LDB | 43.1 | 75 | 60 | 75 | 21.96 | 2.03
68 | 50 | 466 | 57 | LWB | 41.9 | 75 | 60 | 77 | 21.83 | 2.04
68 | 50 | 466 | 57 | kW | 0.83 | 75 | 60 | 81 | 21.58 | 2.05
72 | 50 | 466 | 61 | MBh | 18.13 | 47 | 43 | 59 | 19.14 | 1.81
72 | 50 | 466 | 61 | S/T | 0.676 | 47 | 43 | 70 | 18.5 | 1.85
72 | 50 | 466 | 61 | ∆T | 24.4 | 47 | 43 | 72 | 18.24 | 1.87
72 | 50 | 466 | 61 | LDB | 47.6 | 47 | 43 | 75 | 17.99 | 1.88
72 | 50 | 466 | 61 | LWB | 46.5 | 47 | 43 | 77 | 17.86 | 1.89
72 | 50 | 466 | 61 | kW | 0.84 | 47 | 43 | 81 | 17.61 | 1.91
77 | 50 | 466 | 64 | MBh | 18.85 | 35 | 32 | 59 | 19.09 | 2.11
77 | 50 | 466 | 64 | S/T | 0.676 | 35 | 32 | 70 | 18.36 | 2.16
77 | 50 | 466 | 64 | ∆T | 25.3 | 35 | 32 | 72 | 18.06 | 2.18
77 | 50 | 466 | 64 | LDB | 51.7 | 35 | 32 | 75 | 17.77 | 2.2
77 | 50 | 466 | 64 | LWB | 49.8 | 35 | 32 | 77 | 17.62 | 2.21
77 | 50 | 466 | 64 | kW | 0.85 | 35 | 32 | 81 | 17.33 | 2.23
80 | 50 | 466 | 67 | MBh | 19.36 | 25 | 23 | 59 | 19.08 | 2.36
80 | 50 | 466 | 67 | S/T | 0.659 | 25 | 23 | 70 | 18.24 | 2.42
80 | 50 | 466 | 67 | ∆T | 25.4 | 25 | 23 | 72 | 17.9 | 2.44
80 | 50 | 466 | 67 | LDB | 54.6 | 25 | 23 | 75 | 17.57 | 2.46
80 | 50 | 466 | 67 | LWB | 53.4 | 25 | 23 | 77 | 17.4 | 2.48
80 | 50 | 466 | 67 | kW | 0.85 | 25 | 23 | 81 | 17.07 | 2.5
86 | 50 | 466 | 72 | MBh | 20.3 | 16 | 14 | 59 | 19.1 | 2.6
86 | 50 | 466 | 72 | S/T | 0.633 | 16 | 14 | 70 | 18.12 | 2.67
86 | 50 | 466 | 72 | ∆T | 25.5 | 16 | 14 | 72 | 17.73 | 2.7
86 | 50 | 466 | 72 | LDB | 60.5 | 16 | 14 | 75 | 17.34 | 2.73
86 | 50 | 466 | 72 | LWB | 59.3 | 16 | 14 | 77 | 17.14 | 2.74
86 | 50 | 466 | 72 | kW | 0.86 | 16 | 14 | 81 | 16.75 | 2.77
90 | 50 | 466 | 75 | MBh | 21.02 | 5 | 5 | 59 | 19.18 | 2.85
90 | 50 | 466 | 75 | S/T | 0.594 | 5 | 5 | 70 | 18 | 2.93
90 | 50 | 466 | 75 | ∆T | 24.8 | 5 | 5 | 72 | 17.53 | 2.96
90 | 50 | 466 | 75 | LDB | 65.2 | 5 | 5 | 75 | 17.05 | 2.99
90 | 50 | 466 | 75 | LWB | 62.8 | 5 | 5 | 77 | 16.82 | 3.01
90 | 50 | 466 | 75 | kW | 0.86 | 5 | 5 | 81 | 15.5 | 2.77
68 | 68 | 466 | 57 | MBh | 15.94 | -4 | -4 | 59 | 16.58 | 2.56
68 | 68 | 466 | 57 | S/T | 0.738 | -4 | -4 | 70 | 15.3 | 2.64
68 | 68 | 466 | 57 | ∆T | 23.4 | -4 | -4 | 72 | 14.79 | 2.67
68 | 68 | 466 | 57 | LDB | 44.6 | -4 | -4 | 75 | 14.28 | 2.7
68 | 68 | 466 | 57 | LWB | 43.3 | -4 | -4 | 77 | 14.02 | 2.71
68 | 68 | 466 | 57 | kW | 1.03 | -4 | -4 | 81 | 12.54 | 2.42
72 | 68 | 466 | 61 | MBh | 16.66 | -13 | -14 | 59 | 14.05 | 2.27
72 | 68 | 466 | 61 | S/T | 0.694 | -13 | -14 | 70 | 12.6 | 2.34
72 | 68 | 466 | 61 | ∆T | 23 | -13 | -14 | 72 | 12.02 | 2.37
72 | 68 | 466 | 61 | LDB | 49 | -13 | -14 | 75 | 11.44 | 2.4
72 | 68 | 466 | 61 | LWB | 47.8 | -13 | -14 | 77 | 11.15 | 2.42
72 | 68 | 466 | 61 | kW | 1.04 | -13 | -14 | 81 | 10.57 | 2.44
77 | 68 | 466 | 64 | MBh | 17.39
77 | 68 | 466 | 64 | S/T | 0.696
77 | 68 | 466 | 64 | ∆T | 24
77 | 68 | 466 | 64 | LDB | 53
77 | 68 | 466 | 64 | LWB | 51.1
77 | 68 | 466 | 64 | kW | 1.05
80 | 68 | 466 | 67 | MBh | 17.89
80 | 68 | 466 | 67 | S/T | 0.679
80 | 68 | 466 | 67 | ∆T | 24.1
80 | 68 | 466 | 67 | LDB | 55.9
80 | 68 | 466 | 67 | LWB | 54.6
80 | 68 | 466 | 67 | kW | 1.05
86 | 68 | 466 | 72 | MBh | 18.83
86 | 68 | 466 | 72 | S/T | 0.653
86 | 68 | 466 | 72 | ∆T | 24.4
86 | 68 | 466 | 72 | LDB | 61.6
86 | 68 | 466 | 72 | LWB | 60.4
86 | 68 | 466 | 72 | kW | 1.06
90 | 68 | 466 | 75 | MBh | 19.56
90 | 68 | 466 | 75 | S/T | 0.612
90 | 68 | 466 | 75 | ∆T | 23.8
90 | 68 | 466 | 75 | LDB | 66.2
90 | 68 | 466 | 75 | LWB | 63.7
90 | 68 | 466 | 75 | kW | 1.06
68 | 86 | 466 | 57 | MBh | 14.48
68 | 86 | 466 | 57 | S/T | 0.762
68 | 86 | 466 | 57 | ∆T | 21.9
68 | 86 | 466 | 57 | LDB | 46.1
68 | 86 | 466 | 57 | LWB | 44.7
68 | 86 | 466 | 57 | kW | 1.23
72 | 86 | 466 | 61 | MBh | 15.2
72 | 86 | 466 | 61 | S/T | 0.715
72 | 86 | 466 | 61 | ∆T | 21.6
72 | 86 | 466 | 61 | LDB | 50.4
72 | 86 | 466 | 61 | LWB | 49.1
72 | 86 | 466 | 61 | kW | 1.24
77 | 86 | 466 | 64 | MBh | 15.92
77 | 86 | 466 | 64 | S/T | 0.72
77 | 86 | 466 | 64 | ∆T | 22.8
77 | 86 | 466 | 64 | LDB | 54.2
77 | 86 | 466 | 64 | LWB | 52.3
77 | 86 | 466 | 64 | kW | 1.25
80 | 86 | 466 | 67 | MBh | 16.43
80 | 86 | 466 | 67 | S/T | 0.702
80 | 86 | 466 | 67 | ∆T | 22.9
80 | 86 | 466 | 67 | LDB | 57.1
80 | 86 | 466 | 67 | LWB | 55.7
80 | 86 | 466 | 67 | kW | 1.25
86 | 86 | 466 | 72 | MBh | 17.37
86 | 86 | 466 | 72 | S/T | 0.676
86 | 86 | 466 | 72 | ∆T | 23.3
86 | 86 | 466 | 72 | LDB | 62.7
86 | 86 | 466 | 72 | LWB | 61.4
86 | 86 | 466 | 72 | kW | 1.26
90 | 86 | 466 | 75 | MBh | 18.09
90 | 86 | 466 | 75 | S/T | 0.634
90 | 86 | 466 | 75 | ∆T | 22.8
90 | 86 | 466 | 75 | LDB | 67.2
90 | 86 | 466 | 75 | LWB | 64.7
90 | 86 | 466 | 75 | kW | 1.26
68 | 95 | 466 | 57 | MBh | 13.75
68 | 95 | 466 | 57 | S/T | 0.776
68 | 95 | 466 | 57 | ∆T | 21.2
68 | 95 | 466 | 57 | LDB | 46.8
68 | 95 | 466 | 57 | LWB | 45.4
68 | 95 | 466 | 57 | kW | 1.33
72 | 95 | 466 | 61 | MBh | 14.47
72 | 95 | 466 | 61 | S/T | 0.728
72 | 95 | 466 | 61 | ∆T | 20.9
72 | 95 | 466 | 61 | LDB | 51.1
72 | 95 | 466 | 61 | LWB | 49.8
72 | 95 | 466 | 61 | kW | 1.34
77 | 95 | 466 | 64 | MBh | 15.19
77 | 95 | 466 | 64 | S/T | 0.733
77 | 95 | 466 | 64 | ∆T | 22.1
77 | 95 | 466 | 64 | LDB | 54.9
77 | 95 | 466 | 64 | LWB | 52.9
77 | 95 | 466 | 64 | kW | 1.35
80 | 95 | 466 | 67 | MBh | 15.7
80 | 95 | 466 | 67 | S/T | 0.715
80 | 95 | 466 | 67 | ∆T | 22.3
80 | 95 | 466 | 67 | LDB | 57.7
80 | 95 | 466 | 67 | LWB | 56.3
80 | 95 | 466 | 67 | kW | 1.35
86 | 95 | 466 | 72 | MBh | 16.64
86 | 95 | 466 | 72 | S/T | 0.69
86 | 95 | 466 | 72 | ∆T | 22.8
86 | 95 | 466 | 72 | LDB | 63.2
86 | 95 | 466 | 72 | LWB | 61.9
86 | 95 | 466 | 72 | kW | 1.36
90 | 95 | 466 | 75 | MBh | 17.36
90 | 95 | 466 | 75 | S/T | 0.647
90 | 95 | 466 | 75 | ∆T | 22.3
90 | 95 | 466 | 75 | LDB | 67.7
90 | 95 | 466 | 75 | LWB | 65.1
90 | 95 | 466 | 75 | kW | 1.36
68 | 104 | 466 | 57 | MBh | 13.02
68 | 104 | 466 | 57 | S/T | 0.792
68 | 104 | 466 | 57 | ∆T | 20.5
68 | 104 | 466 | 57 | LDB | 47.5
68 | 104 | 466 | 57 | LWB | 46.1
68 | 104 | 466 | 57 | kW | 1.43
72 | 104 | 466 | 61 | MBh | 13.74
72 | 104 | 466 | 61 | S/T | 0.742
72 | 104 | 466 | 61 | ∆T | 20.3
72 | 104 | 466 | 61 | LDB | 51.7
72 | 104 | 466 | 61 | LWB | 50.4
72 | 104 | 466 | 61 | kW | 1.44
77 | 104 | 466 | 64 | MBh | 14.46
77 | 104 | 466 | 64 | S/T | 0.749
77 | 104 | 466 | 64 | ∆T | 21.5
77 | 104 | 466 | 64 | LDB | 55.5
77 | 104 | 466 | 64 | LWB | 53.5
77 | 104 | 466 | 64 | kW | 1.45
80 | 104 | 466 | 67 | MBh | 14.97
80 | 104 | 466 | 67 | S/T | 0.731
80 | 104 | 466 | 67 | ∆T | 21.7
80 | 104 | 466 | 67 | LDB | 58.3
80 | 104 | 466 | 67 | LWB | 56.8
80 | 104 | 466 | 67 | kW | 1.45
86 | 104 | 466 | 72 | MBh | 15.91
86 | 104 | 466 | 72 | S/T | 0.705
86 | 104 | 466 | 72 | ∆T | 22.3
86 | 104 | 466 | 72 | LDB | 63.7
86 | 104 | 466 | 72 | LWB | 62.3
86 | 104 | 466 | 72 | kW | 1.46
90 | 104 | 466 | 75 | MBh | 16.63
90 | 104 | 466 | 75 | S/T | 0.66
90 | 104 | 466 | 75 | ∆T | 21.8
90 | 104 | 466 | 75 | LDB | 68.2
90 | 104 | 466 | 75 | LWB | 65.6
90 | 104 | 466 | 75 | kW | 1.46
68 | 115 | 466 | 57 | MBh | 12.14
68 | 115 | 466 | 57 | S/T | 0.815
68 | 115 | 466 | 57 | ∆T | 19.7
68 | 115 | 466 | 57 | LDB | 48.3
68 | 115 | 466 | 57 | LWB | 46.9
68 | 115 | 466 | 57 | kW | 1.55
72 | 115 | 466 | 61 | MBh | 12.86
72 | 115 | 466 | 61 | S/T | 0.763
72 | 115 | 466 | 61 | ∆T | 19.5
72 | 115 | 466 | 61 | LDB | 52.5
72 | 115 | 466 | 61 | LWB | 51.1
72 | 115 | 466 | 61 | kW | 1.56
77 | 115 | 466 | 64 | MBh | 13.59
77 | 115 | 466 | 64 | S/T | 0.77
77 | 115 | 466 | 64 | ∆T | 20.8
77 | 115 | 466 | 64 | LDB | 56.2
77 | 115 | 466 | 64 | LWB | 54.2
77 | 115 | 466 | 64 | kW | 1.57
80 | 115 | 466 | 67 | MBh | 14.09
80 | 115 | 466 | 67 | S/T | 0.752
80 | 115 | 466 | 67 | ∆T | 21
80 | 115 | 466 | 67 | LDB | 59
80 | 115 | 466 | 67 | LWB | 57.5
80 | 115 | 466 | 67 | kW | 1.57
86 | 115 | 466 | 72 | MBh | 15.03
86 | 115 | 466 | 72 | S/T | 0.725
86 | 115 | 466 | 72 | ∆T | 21.7
86 | 115 | 466 | 72 | LDB | 64.3
86 | 115 | 466 | 72 | LWB | 62.9
86 | 115 | 466 | 72 | kW | 1.58
90 | 115 | 466 | 75 | MBh | 15.76
90 | 115 | 466 | 75 | S/T | 0.679
90 | 115 | 466 | 75 | ∆T | 21.3
90 | 115 | 466 | 75 | LDB | 68.7
90 | 115 | 466 | 75 | LWB | 66.1
90 | 115 | 466 | 75 | kW | 1.58

## RXP18AVJU9 - FDMA18AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 653 | 57 | MBh | 21.72 | 75 | 60 | 59 | 31.23 | 2.67
68 | 50 | 653 | 57 | S/T | 0.733 | 75 | 60 | 70 | 30.36 | 2.73
68 | 50 | 653 | 57 | ∆T | 22.6 | 75 | 60 | 72 | 30.02 | 2.75
68 | 50 | 653 | 57 | LDB | 45.4 | 75 | 60 | 75 | 29.67 | 2.77
68 | 50 | 653 | 57 | LWB | 43.7 | 75 | 60 | 77 | 29.5 | 2.78
68 | 50 | 653 | 57 | kW | 1.04 | 75 | 60 | 81 | 29.16 | 2.81
72 | 50 | 653 | 61 | MBh | 22.63 | 47 | 43 | 59 | 25.86 | 2.47
72 | 50 | 653 | 61 | S/T | 0.69 | 47 | 43 | 70 | 25 | 2.53
72 | 50 | 653 | 61 | ∆T | 22.1 | 47 | 43 | 72 | 24.65 | 2.55
72 | 50 | 653 | 61 | LDB | 49.9 | 47 | 43 | 75 | 24.31 | 2.58
72 | 50 | 653 | 61 | LWB | 48.3 | 47 | 43 | 77 | 24.14 | 2.59
72 | 50 | 653 | 61 | kW | 1.05 | 47 | 43 | 81 | 23.79 | 2.61
77 | 50 | 653 | 64 | MBh | 23.53 | 35 | 32 | 59 | 24.99 | 2.75
77 | 50 | 653 | 64 | S/T | 0.693 | 35 | 32 | 70 | 24.03 | 2.81
77 | 50 | 653 | 64 | ∆T | 23.1 | 35 | 32 | 72 | 23.64 | 2.84
77 | 50 | 653 | 64 | LDB | 53.9 | 35 | 32 | 75 | 23.26 | 2.87
77 | 50 | 653 | 64 | LWB | 51.6 | 35 | 32 | 77 | 23.07 | 2.88
77 | 50 | 653 | 64 | kW | 1.05 | 35 | 32 | 81 | 22.69 | 2.91
80 | 50 | 653 | 67 | MBh | 24.16 | 25 | 23 | 59 | 24.29 | 2.97
80 | 50 | 653 | 67 | S/T | 0.676 | 25 | 23 | 70 | 23.22 | 3.05
80 | 50 | 653 | 67 | ∆T | 23.2 | 25 | 23 | 72 | 22.79 | 3.08
80 | 50 | 653 | 67 | LDB | 56.8 | 25 | 23 | 75 | 22.37 | 3.11
80 | 50 | 653 | 67 | LWB | 55.1 | 25 | 23 | 77 | 22.15 | 3.12
80 | 50 | 653 | 67 | kW | 1.06 | 25 | 23 | 81 | 21.73 | 3.15
86 | 50 | 653 | 72 | MBh | 25.34 | 16 | 14 | 59 | 23.62 | 3.2
86 | 50 | 653 | 72 | S/T | 0.651 | 16 | 14 | 70 | 22.41 | 3.28
86 | 50 | 653 | 72 | ∆T | 23.4 | 16 | 14 | 72 | 21.93 | 3.32
86 | 50 | 653 | 72 | LDB | 62.6 | 16 | 14 | 75 | 21.44 | 3.35
86 | 50 | 653 | 72 | LWB | 60.9 | 16 | 14 | 77 | 21.2 | 3.37
86 | 50 | 653 | 72 | kW | 1.07 | 16 | 14 | 81 | 20.71 | 3.4
90 | 50 | 653 | 75 | MBh | 26.24 | 5 | 5 | 59 | 23.02 | 3.42
90 | 50 | 653 | 75 | S/T | 0.611 | 5 | 5 | 70 | 21.6 | 3.52
90 | 50 | 653 | 75 | ∆T | 22.7 | 5 | 5 | 72 | 21.03 | 3.56
90 | 50 | 653 | 75 | LDB | 67.3 | 5 | 5 | 75 | 20.47 | 3.59
90 | 50 | 653 | 75 | LWB | 64.3 | 5 | 5 | 77 | 20.18 | 3.61
90 | 50 | 653 | 75 | kW | 1.08 | 5 | 5 | 81 | 19.61 | 3.65
68 | 68 | 653 | 57 | MBh | 19.9 | -4 | -4 | 59 | 19.9 | 3.07
68 | 68 | 653 | 57 | S/T | 0.754 | -4 | -4 | 70 | 18.36 | 3.17
68 | 68 | 653 | 57 | ∆T | 21.3 | -4 | -4 | 72 | 17.75 | 3.2
68 | 68 | 653 | 57 | LDB | 46.7 | -4 | -4 | 75 | 17.13 | 3.24
68 | 68 | 653 | 57 | LWB | 45 | -4 | -4 | 77 | 16.82 | 3.26
68 | 68 | 653 | 57 | kW | 1.29 | -4 | -4 | 81 | 16.21 | 3.29
72 | 68 | 653 | 61 | MBh | 20.8 | -13 | -14 | 59 | 16.86 | 2.73
72 | 68 | 653 | 61 | S/T | 0.709 | -13 | -14 | 70 | 15.12 | 2.81
72 | 68 | 653 | 61 | ∆T | 20.9 | -13 | -14 | 72 | 14.42 | 2.85
72 | 68 | 653 | 61 | LDB | 51.1 | -13 | -14 | 75 | 13.73 | 2.88
72 | 68 | 653 | 61 | LWB | 49.4 | -13 | -14 | 77 | 13.38 | 2.9
72 | 68 | 653 | 61 | kW | 1.29 | -13 | -14 | 81 | 12.68 | 2.93
77 | 68 | 653 | 64 | MBh | 21.71
77 | 68 | 653 | 64 | S/T | 0.713
77 | 68 | 653 | 64 | ∆T | 22
77 | 68 | 653 | 64 | LDB | 55
77 | 68 | 653 | 64 | LWB | 52.7
77 | 68 | 653 | 64 | kW | 1.3
80 | 68 | 653 | 67 | MBh | 22.34
80 | 68 | 653 | 67 | S/T | 0.697
80 | 68 | 653 | 67 | ∆T | 22.1
80 | 68 | 653 | 67 | LDB | 57.9
80 | 68 | 653 | 67 | LWB | 56.1
80 | 68 | 653 | 67 | kW | 1.31
86 | 68 | 653 | 72 | MBh | 23.51
86 | 68 | 653 | 72 | S/T | 0.672
86 | 68 | 653 | 72 | ∆T | 22.4
86 | 68 | 653 | 72 | LDB | 63.6
86 | 68 | 653 | 72 | LWB | 61.8
86 | 68 | 653 | 72 | kW | 1.32
90 | 68 | 653 | 75 | MBh | 24.41
90 | 68 | 653 | 75 | S/T | 0.631
90 | 68 | 653 | 75 | ∆T | 21.9
90 | 68 | 653 | 75 | LDB | 68.1
90 | 68 | 653 | 75 | LWB | 65.1
90 | 68 | 653 | 75 | kW | 1.32
68 | 86 | 653 | 57 | MBh | 18.07
68 | 86 | 653 | 57 | S/T | 0.781
68 | 86 | 653 | 57 | ∆T | 20
68 | 86 | 653 | 57 | LDB | 48
68 | 86 | 653 | 57 | LWB | 46.2
68 | 86 | 653 | 57 | kW | 1.54
72 | 86 | 653 | 61 | MBh | 18.98
72 | 86 | 653 | 61 | S/T | 0.733
72 | 86 | 653 | 61 | ∆T | 19.7
72 | 86 | 653 | 61 | LDB | 52.3
72 | 86 | 653 | 61 | LWB | 50.5
72 | 86 | 653 | 61 | kW | 1.54
77 | 86 | 653 | 64 | MBh | 19.88
77 | 86 | 653 | 64 | S/T | 0.74
77 | 86 | 653 | 64 | ∆T | 20.9
77 | 86 | 653 | 64 | LDB | 56.1
77 | 86 | 653 | 64 | LWB | 53.7
77 | 86 | 653 | 64 | kW | 1.55
80 | 86 | 653 | 67 | MBh | 20.51
80 | 86 | 653 | 67 | S/T | 0.723
80 | 86 | 653 | 67 | ∆T | 21
80 | 86 | 653 | 67 | LDB | 59
80 | 86 | 653 | 67 | LWB | 57.1
80 | 86 | 653 | 67 | kW | 1.56
86 | 86 | 653 | 72 | MBh | 21.69
86 | 86 | 653 | 72 | S/T | 0.698
86 | 86 | 653 | 72 | ∆T | 21.5
86 | 86 | 653 | 72 | LDB | 64.5
86 | 86 | 653 | 72 | LWB | 62.6
86 | 86 | 653 | 72 | kW | 1.57
90 | 86 | 653 | 75 | MBh | 22.59
90 | 86 | 653 | 75 | S/T | 0.655
90 | 86 | 653 | 75 | ∆T | 21
90 | 86 | 653 | 75 | LDB | 69
90 | 86 | 653 | 75 | LWB | 65.9
90 | 86 | 653 | 75 | kW | 1.57
68 | 95 | 653 | 57 | MBh | 17.16
68 | 95 | 653 | 57 | S/T | 0.797
68 | 95 | 653 | 57 | ∆T | 19.4
68 | 95 | 653 | 57 | LDB | 48.6
68 | 95 | 653 | 57 | LWB | 46.8
68 | 95 | 653 | 57 | kW | 1.66
72 | 95 | 653 | 61 | MBh | 18.06
72 | 95 | 653 | 61 | S/T | 0.748
72 | 95 | 653 | 61 | ∆T | 19.1
72 | 95 | 653 | 61 | LDB | 52.9
72 | 95 | 653 | 61 | LWB | 51.1
72 | 95 | 653 | 61 | kW | 1.67
77 | 95 | 653 | 64 | MBh | 18.97
77 | 95 | 653 | 64 | S/T | 0.755
77 | 95 | 653 | 64 | ∆T | 20.3
77 | 95 | 653 | 64 | LDB | 56.7
77 | 95 | 653 | 64 | LWB | 54.2
77 | 95 | 653 | 64 | kW | 1.67
80 | 95 | 653 | 67 | MBh | 19.6
80 | 95 | 653 | 67 | S/T | 0.738
80 | 95 | 653 | 67 | ∆T | 20.5
80 | 95 | 653 | 67 | LDB | 59.5
80 | 95 | 653 | 67 | LWB | 57.6
80 | 95 | 653 | 67 | kW | 1.68
86 | 95 | 653 | 72 | MBh | 20.77
86 | 95 | 653 | 72 | S/T | 0.713
86 | 95 | 653 | 72 | ∆T | 21
86 | 95 | 653 | 72 | LDB | 65
86 | 95 | 653 | 72 | LWB | 63.1
86 | 95 | 653 | 72 | kW | 1.69
90 | 95 | 653 | 75 | MBh | 21.68
90 | 95 | 653 | 75 | S/T | 0.669
90 | 95 | 653 | 75 | ∆T | 20.6
90 | 95 | 653 | 75 | LDB | 69.4
90 | 95 | 653 | 75 | LWB | 66.3
90 | 95 | 653 | 75 | kW | 1.7
68 | 104 | 653 | 57 | MBh | 16.25
68 | 104 | 653 | 57 | S/T | 0.815
68 | 104 | 653 | 57 | ∆T | 18.8
68 | 104 | 653 | 57 | LDB | 49.2
68 | 104 | 653 | 57 | LWB | 47.4
68 | 104 | 653 | 57 | kW | 1.78
72 | 104 | 653 | 61 | MBh | 17.15
72 | 104 | 653 | 61 | S/T | 0.763
72 | 104 | 653 | 61 | ∆T | 18.6
72 | 104 | 653 | 61 | LDB | 53.4
72 | 104 | 653 | 61 | LWB | 51.6
72 | 104 | 653 | 61 | kW | 1.79
77 | 104 | 653 | 64 | MBh | 18.06
77 | 104 | 653 | 64 | S/T | 0.772
77 | 104 | 653 | 64 | ∆T | 19.8
77 | 104 | 653 | 64 | LDB | 57.2
77 | 104 | 653 | 64 | LWB | 54.7
77 | 104 | 653 | 64 | kW | 1.8
80 | 104 | 653 | 67 | MBh | 18.69
80 | 104 | 653 | 67 | S/T | 0.754
80 | 104 | 653 | 67 | ∆T | 20
80 | 104 | 653 | 67 | LDB | 60
80 | 104 | 653 | 67 | LWB | 58
80 | 104 | 653 | 67 | kW | 1.8
86 | 104 | 653 | 72 | MBh | 19.86
86 | 104 | 653 | 72 | S/T | 0.73
86 | 104 | 653 | 72 | ∆T | 20.5
86 | 104 | 653 | 72 | LDB | 65.5
86 | 104 | 653 | 72 | LWB | 63.5
86 | 104 | 653 | 72 | kW | 1.81
90 | 104 | 653 | 75 | MBh | 20.76
90 | 104 | 653 | 75 | S/T | 0.684
90 | 104 | 653 | 75 | ∆T | 20.1
90 | 104 | 653 | 75 | LDB | 69.9
90 | 104 | 653 | 75 | LWB | 66.7
90 | 104 | 653 | 75 | kW | 1.82
68 | 115 | 653 | 57 | MBh | 15.15
68 | 115 | 653 | 57 | S/T | 0.84
68 | 115 | 653 | 57 | ∆T | 18
68 | 115 | 653 | 57 | LDB | 50
68 | 115 | 653 | 57 | LWB | 48.1
68 | 115 | 653 | 57 | kW | 1.93
72 | 115 | 653 | 61 | MBh | 16.06
72 | 115 | 653 | 61 | S/T | 0.785
72 | 115 | 653 | 61 | ∆T | 17.9
72 | 115 | 653 | 61 | LDB | 54.1
72 | 115 | 653 | 61 | LWB | 52.3
72 | 115 | 653 | 61 | kW | 1.94
77 | 115 | 653 | 64 | MBh | 16.96
77 | 115 | 653 | 64 | S/T | 0.796
77 | 115 | 653 | 64 | ∆T | 19.1
77 | 115 | 653 | 64 | LDB | 57.9
77 | 115 | 653 | 64 | LWB | 55.4
77 | 115 | 653 | 64 | kW | 1.95
80 | 115 | 653 | 67 | MBh | 17.59
80 | 115 | 653 | 67 | S/T | 0.777
80 | 115 | 653 | 67 | ∆T | 19.4
80 | 115 | 653 | 67 | LDB | 60.6
80 | 115 | 653 | 67 | LWB | 58.6
80 | 115 | 653 | 67 | kW | 1.95
86 | 115 | 653 | 72 | MBh | 18.77
86 | 115 | 653 | 72 | S/T | 0.752
86 | 115 | 653 | 72 | ∆T | 20
86 | 115 | 653 | 72 | LDB | 66
86 | 115 | 653 | 72 | LWB | 64
86 | 115 | 653 | 72 | kW | 1.96
90 | 115 | 653 | 75 | MBh | 19.67
90 | 115 | 653 | 75 | S/T | 0.704
90 | 115 | 653 | 75 | ∆T | 19.6
90 | 115 | 653 | 75 | LDB | 70.4
90 | 115 | 653 | 75 | LWB | 67.2
90 | 115 | 653 | 75 | kW | 1.97

## RXP24AVJU9 - FDMA24AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 667 | 57 | MBh | 25.49 | 75 | 60 | 59 | 34.47 | 2.95
68 | 50 | 667 | 57 | S/T | 0.7 | 75 | 60 | 70 | 33.52 | 3.01
68 | 50 | 667 | 57 | ∆T | 24.8 | 75 | 60 | 72 | 33.14 | 3.03
68 | 50 | 667 | 57 | LDB | 43.2 | 75 | 60 | 75 | 32.76 | 3.06
68 | 50 | 667 | 57 | LWB | 41.4 | 75 | 60 | 77 | 32.57 | 3.07
68 | 50 | 667 | 57 | kW | 1.37 | 75 | 60 | 81 | 32.19 | 3.1
72 | 50 | 667 | 61 | MBh | 26.55 | 47 | 43 | 59 | 28.55 | 2.73
72 | 50 | 667 | 61 | S/T | 0.658 | 47 | 43 | 70 | 27.6 | 2.79
72 | 50 | 667 | 61 | ∆T | 24.3 | 47 | 43 | 72 | 27.22 | 2.82
72 | 50 | 667 | 61 | LDB | 47.7 | 47 | 43 | 75 | 26.84 | 2.84
72 | 50 | 667 | 61 | LWB | 46.1 | 47 | 43 | 77 | 26.65 | 2.85
72 | 50 | 667 | 61 | kW | 1.38 | 47 | 43 | 81 | 26.27 | 2.88
77 | 50 | 667 | 64 | MBh | 27.61 | 35 | 32 | 59 | 27.63 | 3.03
77 | 50 | 667 | 64 | S/T | 0.655 | 35 | 32 | 70 | 26.57 | 3.11
77 | 50 | 667 | 64 | ∆T | 25.1 | 35 | 32 | 72 | 26.15 | 3.14
77 | 50 | 667 | 64 | LDB | 51.9 | 35 | 32 | 75 | 25.72 | 3.17
77 | 50 | 667 | 64 | LWB | 49.5 | 35 | 32 | 77 | 25.51 | 3.18
77 | 50 | 667 | 64 | kW | 1.39 | 35 | 32 | 81 | 25.09 | 3.21
80 | 50 | 667 | 67 | MBh | 28.35 | 25 | 23 | 59 | 26.9 | 3.29
80 | 50 | 667 | 67 | S/T | 0.637 | 25 | 23 | 70 | 25.71 | 3.37
80 | 50 | 667 | 67 | ∆T | 25.1 | 25 | 23 | 72 | 25.24 | 3.41
80 | 50 | 667 | 67 | LDB | 54.9 | 25 | 23 | 75 | 24.77 | 3.44
80 | 50 | 667 | 67 | LWB | 53.1 | 25 | 23 | 77 | 24.53 | 3.46
80 | 50 | 667 | 67 | kW | 1.39 | 25 | 23 | 81 | 24.06 | 3.49
86 | 50 | 667 | 72 | MBh | 29.73 | 16 | 14 | 59 | 26.2 | 3.54
86 | 50 | 667 | 72 | S/T | 0.609 | 16 | 14 | 70 | 24.86 | 3.64
86 | 50 | 667 | 72 | ∆T | 25.1 | 16 | 14 | 72 | 24.32 | 3.68
86 | 50 | 667 | 72 | LDB | 60.9 | 16 | 14 | 75 | 23.78 | 3.71
86 | 50 | 667 | 72 | LWB | 59 | 16 | 14 | 77 | 23.51 | 3.73
86 | 50 | 667 | 72 | kW | 1.41 | 16 | 14 | 81 | 22.98 | 3.77
90 | 50 | 667 | 75 | MBh | 30.79 | 5 | 5 | 59 | 25.58 | 3.8
90 | 50 | 667 | 75 | S/T | 0.57 | 5 | 5 | 70 | 24 | 3.9
90 | 50 | 667 | 75 | ∆T | 24.4 | 5 | 5 | 72 | 23.37 | 3.95
90 | 50 | 667 | 75 | LDB | 65.6 | 5 | 5 | 75 | 22.73 | 3.96
90 | 50 | 667 | 75 | LWB | 62.5 | 5 | 5 | 77 | 22.42 | 3.96
90 | 50 | 667 | 75 | kW | 1.42 | 5 | 5 | 81 | 20.91 | 3.77
68 | 68 | 667 | 57 | MBh | 23.35 | -4 | -4 | 59 | 22.11 | 3.41
68 | 68 | 667 | 57 | S/T | 0.715 | -4 | -4 | 70 | 20.4 | 3.51
68 | 68 | 667 | 57 | ∆T | 23.2 | -4 | -4 | 72 | 19.72 | 3.55
68 | 68 | 667 | 57 | LDB | 44.8 | -4 | -4 | 75 | 19.04 | 3.59
68 | 68 | 667 | 57 | LWB | 42.9 | -4 | -4 | 77 | 18.69 | 3.61
68 | 68 | 667 | 57 | kW | 1.69 | -4 | -4 | 81 | 16.92 | 3.29
72 | 68 | 667 | 61 | MBh | 24.41 | -13 | -14 | 59 | 18.73 | 3.03
72 | 68 | 667 | 61 | S/T | 0.672 | -13 | -14 | 70 | 16.8 | 3.12
72 | 68 | 667 | 61 | ∆T | 22.8 | -13 | -14 | 72 | 16.03 | 3.16
72 | 68 | 667 | 61 | LDB | 49.2 | -13 | -14 | 75 | 15.25 | 3.2
72 | 68 | 667 | 61 | LWB | 47.5 | -13 | -14 | 77 | 14.87 | 3.22
72 | 68 | 667 | 61 | kW | 1.7 | -13 | -14 | 81 | 14.09 | 3.25
77 | 68 | 667 | 64 | MBh | 25.47
77 | 68 | 667 | 64 | S/T | 0.671
77 | 68 | 667 | 64 | ∆T | 23.7
77 | 68 | 667 | 64 | LDB | 53.3
77 | 68 | 667 | 64 | LWB | 50.7
77 | 68 | 667 | 64 | kW | 1.71
80 | 68 | 667 | 67 | MBh | 26.21
80 | 68 | 667 | 67 | S/T | 0.653
80 | 68 | 667 | 67 | ∆T | 23.8
80 | 68 | 667 | 67 | LDB | 56.2
80 | 68 | 667 | 67 | LWB | 54.3
80 | 68 | 667 | 67 | kW | 1.72
86 | 68 | 667 | 72 | MBh | 27.59
86 | 68 | 667 | 72 | S/T | 0.625
86 | 68 | 667 | 72 | ∆T | 23.9
86 | 68 | 667 | 72 | LDB | 62.1
86 | 68 | 667 | 72 | LWB | 60.1
86 | 68 | 667 | 72 | kW | 1.73
90 | 68 | 667 | 75 | MBh | 28.65
90 | 68 | 667 | 75 | S/T | 0.585
90 | 68 | 667 | 75 | ∆T | 23.3
90 | 68 | 667 | 75 | LDB | 66.7
90 | 68 | 667 | 75 | LWB | 63.4
90 | 68 | 667 | 75 | kW | 1.74
68 | 86 | 667 | 57 | MBh | 21.21
68 | 86 | 667 | 57 | S/T | 0.735
68 | 86 | 667 | 57 | ∆T | 21.6
68 | 86 | 667 | 57 | LDB | 46.4
68 | 86 | 667 | 57 | LWB | 44.4
68 | 86 | 667 | 57 | kW | 2.02
72 | 86 | 667 | 61 | MBh | 22.27
72 | 86 | 667 | 61 | S/T | 0.69
72 | 86 | 667 | 61 | ∆T | 21.3
72 | 86 | 667 | 61 | LDB | 50.7
72 | 86 | 667 | 61 | LWB | 48.8
72 | 86 | 667 | 61 | kW | 2.03
77 | 86 | 667 | 64 | MBh | 23.33
77 | 86 | 667 | 64 | S/T | 0.691
77 | 86 | 667 | 64 | ∆T | 22.4
77 | 86 | 667 | 64 | LDB | 54.6
77 | 86 | 667 | 64 | LWB | 52
77 | 86 | 667 | 64 | kW | 2.04
80 | 86 | 667 | 67 | MBh | 24.07
80 | 86 | 667 | 67 | S/T | 0.673
80 | 86 | 667 | 67 | ∆T | 22.5
80 | 86 | 667 | 67 | LDB | 57.5
80 | 86 | 667 | 67 | LWB | 55.4
80 | 86 | 667 | 67 | kW | 2.05
86 | 86 | 667 | 72 | MBh | 25.45
86 | 86 | 667 | 72 | S/T | 0.646
86 | 86 | 667 | 72 | ∆T | 22.8
86 | 86 | 667 | 72 | LDB | 63.2
86 | 86 | 667 | 72 | LWB | 61.1
86 | 86 | 667 | 72 | kW | 2.06
90 | 86 | 667 | 75 | MBh | 26.51
90 | 86 | 667 | 75 | S/T | 0.604
90 | 86 | 667 | 75 | ∆T | 22.2
90 | 86 | 667 | 75 | LDB | 67.8
90 | 86 | 667 | 75 | LWB | 64.4
90 | 86 | 667 | 75 | kW | 2.07
68 | 95 | 667 | 57 | MBh | 20.14
68 | 95 | 667 | 57 | S/T | 0.747
68 | 95 | 667 | 57 | ∆T | 20.9
68 | 95 | 667 | 57 | LDB | 47.1
68 | 95 | 667 | 57 | LWB | 45.1
68 | 95 | 667 | 57 | kW | 2.18
72 | 95 | 667 | 61 | MBh | 21.2
72 | 95 | 667 | 61 | S/T | 0.701
72 | 95 | 667 | 61 | ∆T | 20.6
72 | 95 | 667 | 61 | LDB | 51.4
72 | 95 | 667 | 61 | LWB | 49.5
72 | 95 | 667 | 61 | kW | 2.19
77 | 95 | 667 | 64 | MBh | 22.26
77 | 95 | 667 | 64 | S/T | 0.703
77 | 95 | 667 | 64 | ∆T | 21.7
77 | 95 | 667 | 64 | LDB | 55.3
77 | 95 | 667 | 64 | LWB | 52.6
77 | 95 | 667 | 64 | kW | 2.2
80 | 95 | 667 | 67 | MBh | 23
80 | 95 | 667 | 67 | S/T | 0.684
80 | 95 | 667 | 67 | ∆T | 21.9
80 | 95 | 667 | 67 | LDB | 58.1
80 | 95 | 667 | 67 | LWB | 56
80 | 95 | 667 | 67 | kW | 2.21
86 | 95 | 667 | 72 | MBh | 24.38
86 | 95 | 667 | 72 | S/T | 0.657
86 | 95 | 667 | 72 | ∆T | 22.2
86 | 95 | 667 | 72 | LDB | 63.8
86 | 95 | 667 | 72 | LWB | 61.6
86 | 95 | 667 | 72 | kW | 2.22
90 | 95 | 667 | 75 | MBh | 25.44
90 | 95 | 667 | 75 | S/T | 0.615
90 | 95 | 667 | 75 | ∆T | 21.7
90 | 95 | 667 | 75 | LDB | 68.3
90 | 95 | 667 | 75 | LWB | 64.9
90 | 95 | 667 | 75 | kW | 2.23
68 | 104 | 667 | 57 | MBh | 19.07
68 | 104 | 667 | 57 | S/T | 0.761
68 | 104 | 667 | 57 | ∆T | 20.2
68 | 104 | 667 | 57 | LDB | 47.8
68 | 104 | 667 | 57 | LWB | 45.8
68 | 104 | 667 | 57 | kW | 2.35
72 | 104 | 667 | 61 | MBh | 20.13
72 | 104 | 667 | 61 | S/T | 0.713
72 | 104 | 667 | 61 | ∆T | 19.9
72 | 104 | 667 | 61 | LDB | 52.1
72 | 104 | 667 | 61 | LWB | 50.1
72 | 104 | 667 | 61 | kW | 2.36
77 | 104 | 667 | 64 | MBh | 21.19
77 | 104 | 667 | 64 | S/T | 0.716
77 | 104 | 667 | 64 | ∆T | 21.1
77 | 104 | 667 | 64 | LDB | 55.9
77 | 104 | 667 | 64 | LWB | 53.2
77 | 104 | 667 | 64 | kW | 2.37
80 | 104 | 667 | 67 | MBh | 21.93
80 | 104 | 667 | 67 | S/T | 0.698
80 | 104 | 667 | 67 | ∆T | 21.2
80 | 104 | 667 | 67 | LDB | 58.8
80 | 104 | 667 | 67 | LWB | 56.6
80 | 104 | 667 | 67 | kW | 2.37
86 | 104 | 667 | 72 | MBh | 23.31
86 | 104 | 667 | 72 | S/T | 0.67
86 | 104 | 667 | 72 | ∆T | 21.7
86 | 104 | 667 | 72 | LDB | 64.3
86 | 104 | 667 | 72 | LWB | 62.1
86 | 104 | 667 | 72 | kW | 2.39
90 | 104 | 667 | 75 | MBh | 24.37
90 | 104 | 667 | 75 | S/T | 0.627
90 | 104 | 667 | 75 | ∆T | 21.2
90 | 104 | 667 | 75 | LDB | 68.8
90 | 104 | 667 | 75 | LWB | 65.4
90 | 104 | 667 | 75 | kW | 2.4
68 | 115 | 667 | 57 | MBh | 17.78
68 | 115 | 667 | 57 | S/T | 0.781
68 | 115 | 667 | 57 | ∆T | 19.3
68 | 115 | 667 | 57 | LDB | 48.7
68 | 115 | 667 | 57 | LWB | 46.6
68 | 115 | 667 | 57 | kW | 2.54
72 | 115 | 667 | 61 | MBh | 18.84
72 | 115 | 667 | 61 | S/T | 0.731
72 | 115 | 667 | 61 | ∆T | 19.1
72 | 115 | 667 | 61 | LDB | 52.9
72 | 115 | 667 | 61 | LWB | 50.9
72 | 115 | 667 | 61 | kW | 2.54
77 | 115 | 667 | 64 | MBh | 19.9
77 | 115 | 667 | 64 | S/T | 0.735
77 | 115 | 667 | 64 | ∆T | 20.3
77 | 115 | 667 | 64 | LDB | 56.7
77 | 115 | 667 | 64 | LWB | 53.9
77 | 115 | 667 | 64 | kW | 2.54
80 | 115 | 667 | 67 | MBh | 20.64
80 | 115 | 667 | 67 | S/T | 0.716
80 | 115 | 667 | 67 | ∆T | 20.5
80 | 115 | 667 | 67 | LDB | 59.5
80 | 115 | 667 | 67 | LWB | 57.2
80 | 115 | 667 | 67 | kW | 2.54
86 | 115 | 667 | 72 | MBh | 22.02
86 | 115 | 667 | 72 | S/T | 0.688
86 | 115 | 667 | 72 | ∆T | 21
86 | 115 | 667 | 72 | LDB | 65
86 | 115 | 667 | 72 | LWB | 62.7
86 | 115 | 667 | 72 | kW | 2.54
90 | 115 | 667 | 75 | MBh | 23.08
90 | 115 | 667 | 75 | S/T | 0.643
90 | 115 | 667 | 75 | ∆T | 20.6
90 | 115 | 667 | 75 | LDB | 69.4
90 | 115 | 667 | 75 | LWB | 65.9
90 | 115 | 667 | 75 | kW | 2.54

## RXP09AVJU9 - FVXV09AVJUW9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 297 | 57 | MBh | 12.08 | 75 | 60 | 59 | 20.6 | 1.76
68 | 50 | 297 | 57 | S/T | 0.692 | 75 | 60 | 70 | 19.69 | 1.76
68 | 50 | 297 | 57 | ∆T | 26.1 | 75 | 60 | 72 | 19.15 | 1.69
68 | 50 | 297 | 57 | LDB | 41.9 | 75 | 60 | 75 | 17.96 | 1.53
68 | 50 | 297 | 57 | LWB | 40.3 | 75 | 60 | 77 | 17.36 | 1.46
68 | 50 | 297 | 57 | kW | 0.53 | 75 | 60 | 81 | 16.16 | 1.31
72 | 50 | 297 | 61 | MBh | 12.59 | 47 | 43 | 59 | 17.82 | 1.63
72 | 50 | 297 | 61 | S/T | 0.651 | 47 | 43 | 70 | 17.1 | 1.67
72 | 50 | 297 | 61 | ∆T | 25.5 | 47 | 43 | 72 | 16.99 | 1.68
72 | 50 | 297 | 61 | LDB | 46.5 | 47 | 43 | 75 | 16.76 | 1.69
72 | 50 | 297 | 61 | LWB | 45 | 47 | 43 | 77 | 16.64 | 1.7
72 | 50 | 297 | 61 | kW | 0.54 | 47 | 43 | 81 | 16.16 | 1.66
77 | 50 | 297 | 64 | MBh | 13.09 | 35 | 32 | 59 | 16.08 | 1.65
77 | 50 | 297 | 64 | S/T | 0.646 | 35 | 32 | 70 | 15.33 | 1.7
77 | 50 | 297 | 64 | ∆T | 26.3 | 35 | 32 | 72 | 15.22 | 1.71
77 | 50 | 297 | 64 | LDB | 50.7 | 35 | 32 | 75 | 14.97 | 1.72
77 | 50 | 297 | 64 | LWB | 48.4 | 35 | 32 | 77 | 14.85 | 1.73
77 | 50 | 297 | 64 | kW | 0.54 | 35 | 32 | 81 | 14.61 | 1.75
80 | 50 | 297 | 67 | MBh | 13.44 | 25 | 23 | 59 | 14.63 | 1.67
80 | 50 | 297 | 67 | S/T | 0.627 | 25 | 23 | 70 | 13.85 | 1.73
80 | 50 | 297 | 67 | ∆T | 26.3 | 25 | 23 | 72 | 13.74 | 1.73
80 | 50 | 297 | 67 | LDB | 53.7 | 25 | 23 | 75 | 13.48 | 1.75
80 | 50 | 297 | 67 | LWB | 52 | 25 | 23 | 77 | 13.36 | 1.76
80 | 50 | 297 | 67 | kW | 0.54 | 25 | 23 | 81 | 13.1 | 1.78
86 | 50 | 297 | 72 | MBh | 14.09 | 16 | 14 | 59 | 13.19 | 1.69
86 | 50 | 297 | 72 | S/T | 0.598 | 16 | 14 | 70 | 12.38 | 1.75
86 | 50 | 297 | 72 | ∆T | 26.3 | 16 | 14 | 72 | 12.26 | 1.76
86 | 50 | 297 | 72 | LDB | 59.7 | 16 | 14 | 75 | 11.99 | 1.78
86 | 50 | 297 | 72 | LWB | 58 | 16 | 14 | 77 | 11.85 | 1.79
86 | 50 | 297 | 72 | kW | 0.55 | 16 | 14 | 81 | 11.59 | 1.8
90 | 50 | 297 | 75 | MBh | 14.59 | 5 | 5 | 59 | 11.77 | 1.72
90 | 50 | 297 | 75 | S/T | 0.559 | 5 | 5 | 70 | 10.9 | 1.77
90 | 50 | 297 | 75 | ∆T | 25.4 | 5 | 5 | 72 | 10.77 | 1.78
90 | 50 | 297 | 75 | LDB | 64.6 | 5 | 5 | 75 | 10.48 | 1.8
90 | 50 | 297 | 75 | LWB | 61.5 | 5 | 5 | 77 | 10.34 | 1.81
90 | 50 | 297 | 75 | kW | 0.68 | 5 | 5 | 81 | 10.06 | 1.83
68 | 68 | 297 | 57 | MBh | 11.07 | -4 | -4 | 59 | 9.71 | 1.68
68 | 68 | 297 | 57 | S/T | 0.705 | -4 | -4 | 70 | 8.81 | 1.74
68 | 68 | 297 | 57 | ∆T | 24.3 | -4 | -4 | 72 | 8.68 | 1.74
68 | 68 | 297 | 57 | LDB | 43.7 | -4 | -4 | 75 | 8.38 | 1.76
68 | 68 | 297 | 57 | LWB | 41.9 | -4 | -4 | 77 | 8.24 | 1.77
68 | 68 | 297 | 57 | kW | 0.66 | -4 | -4 | 81 | 7.67 | 1.67
72 | 68 | 297 | 61 | MBh | 11.57 | -13 | -14 | 59 | 7.57 | 1.64
72 | 68 | 297 | 61 | S/T | 0.663 | -13 | -14 | 70 | 6.03 | 1.42
72 | 68 | 297 | 61 | ∆T | 23.9 | -13 | -14 | 72 | 5.5 | 1.25
72 | 68 | 297 | 61 | LDB | 48.1 | -13 | -14 | 75 | 4.3 | 0.91
72 | 68 | 297 | 61 | LWB | 46.5 | -13 | -14 | 77 | 3.7 | 0.76
72 | 68 | 297 | 61 | kW | 0.66 | -13 | -14 | 81 | 2.5 | 0.48
77 | 68 | 297 | 64 | MBh | 12.07
77 | 68 | 297 | 64 | S/T | 0.66
77 | 68 | 297 | 64 | ∆T | 24.8
77 | 68 | 297 | 64 | LDB | 52.2
77 | 68 | 297 | 64 | LWB | 49.8
77 | 68 | 297 | 64 | kW | 0.67
80 | 68 | 297 | 67 | MBh | 12.42
80 | 68 | 297 | 67 | S/T | 0.642
80 | 68 | 297 | 67 | ∆T | 24.8
80 | 68 | 297 | 67 | LDB | 55.2
80 | 68 | 297 | 67 | LWB | 53.3
80 | 68 | 297 | 67 | kW | 0.67
86 | 68 | 297 | 72 | MBh | 13.08
86 | 68 | 297 | 72 | S/T | 0.613
86 | 68 | 297 | 72 | ∆T | 25
86 | 68 | 297 | 72 | LDB | 61
86 | 68 | 297 | 72 | LWB | 59.2
86 | 68 | 297 | 72 | kW | 0.67
90 | 68 | 297 | 75 | MBh | 13.58
90 | 68 | 297 | 75 | S/T | 0.574
90 | 68 | 297 | 75 | ∆T | 24.3
90 | 68 | 297 | 75 | LDB | 65.7
90 | 68 | 297 | 75 | LWB | 62.6
90 | 68 | 297 | 75 | kW | 0.68
68 | 86 | 297 | 57 | MBh | 10.05
68 | 86 | 297 | 57 | S/T | 0.723
68 | 86 | 297 | 57 | ∆T | 22.7
68 | 86 | 297 | 57 | LDB | 45.3
68 | 86 | 297 | 57 | LWB | 43.5
68 | 86 | 297 | 57 | kW | 0.79
72 | 86 | 297 | 61 | MBh | 10.56
72 | 86 | 297 | 61 | S/T | 0.679
72 | 86 | 297 | 61 | ∆T | 22.4
72 | 86 | 297 | 61 | LDB | 49.6
72 | 86 | 297 | 61 | LWB | 47.9
72 | 86 | 297 | 61 | kW | 0.79
77 | 86 | 297 | 64 | MBh | 11.06
77 | 86 | 297 | 64 | S/T | 0.678
77 | 86 | 297 | 64 | ∆T | 23.4
77 | 86 | 297 | 64 | LDB | 53.6
77 | 86 | 297 | 64 | LWB | 51.1
77 | 86 | 297 | 64 | kW | 0.79
80 | 86 | 297 | 67 | MBh | 11.41
80 | 86 | 297 | 67 | S/T | 0.66
80 | 86 | 297 | 67 | ∆T | 23.5
80 | 86 | 297 | 67 | LDB | 56.5
80 | 86 | 297 | 67 | LWB | 54.6
80 | 86 | 297 | 67 | kW | 0.8
86 | 86 | 297 | 72 | MBh | 12.06
86 | 86 | 297 | 72 | S/T | 0.632
86 | 86 | 297 | 72 | ∆T | 23.8
86 | 86 | 297 | 72 | LDB | 62.2
86 | 86 | 297 | 72 | LWB | 60.3
86 | 86 | 297 | 72 | kW | 0.8
90 | 86 | 297 | 75 | MBh | 12.56
90 | 86 | 297 | 75 | S/T | 0.591
90 | 86 | 297 | 75 | ∆T | 23.1
90 | 86 | 297 | 75 | LDB | 66.9
90 | 86 | 297 | 75 | LWB | 63.7
90 | 86 | 297 | 75 | kW | 0.8
68 | 95 | 297 | 57 | MBh | 9.55
68 | 95 | 297 | 57 | S/T | 0.734
68 | 95 | 297 | 57 | ∆T | 21.9
68 | 95 | 297 | 57 | LDB | 46.1
68 | 95 | 297 | 57 | LWB | 44.2
68 | 95 | 297 | 57 | kW | 0.85
72 | 95 | 297 | 61 | MBh | 10.05
72 | 95 | 297 | 61 | S/T | 0.689
72 | 95 | 297 | 61 | ∆T | 21.6
72 | 95 | 297 | 61 | LDB | 50.4
72 | 95 | 297 | 61 | LWB | 48.6
72 | 95 | 297 | 61 | kW | 0.85
77 | 95 | 297 | 64 | MBh | 10.55
77 | 95 | 297 | 64 | S/T | 0.689
77 | 95 | 297 | 64 | ∆T | 22.7
77 | 95 | 297 | 64 | LDB | 54.3
77 | 95 | 297 | 64 | LWB | 51.8
77 | 95 | 297 | 64 | kW | 0.86
80 | 95 | 297 | 67 | MBh | 10.9
80 | 95 | 297 | 67 | S/T | 0.671
80 | 95 | 297 | 67 | ∆T | 22.8
80 | 95 | 297 | 67 | LDB | 57.2
80 | 95 | 297 | 67 | LWB | 55.2
80 | 95 | 297 | 67 | kW | 0.86
86 | 95 | 297 | 72 | MBh | 11.55
86 | 95 | 297 | 72 | S/T | 0.642
86 | 95 | 297 | 72 | ∆T | 23.1
86 | 95 | 297 | 72 | LDB | 62.9
86 | 95 | 297 | 72 | LWB | 60.9
86 | 95 | 297 | 72 | kW | 0.86
90 | 95 | 297 | 75 | MBh | 12.06
90 | 95 | 297 | 75 | S/T | 0.6
90 | 95 | 297 | 75 | ∆T | 22.6
90 | 95 | 297 | 75 | LDB | 67.4
90 | 95 | 297 | 75 | LWB | 64.2
90 | 95 | 297 | 75 | kW | 0.87
68 | 104 | 297 | 57 | MBh | 9.04
68 | 104 | 297 | 57 | S/T | 0.747
68 | 104 | 297 | 57 | ∆T | 21
68 | 104 | 297 | 57 | LDB | 47
68 | 104 | 297 | 57 | LWB | 45
68 | 104 | 297 | 57 | kW | 0.91
72 | 104 | 297 | 61 | MBh | 9.54
72 | 104 | 297 | 61 | S/T | 0.7
72 | 104 | 297 | 61 | ∆T | 20.8
72 | 104 | 297 | 61 | LDB | 51.2
72 | 104 | 297 | 61 | LWB | 49.3
72 | 104 | 297 | 61 | kW | 0.92
77 | 104 | 297 | 64 | MBh | 10.04
77 | 104 | 297 | 64 | S/T | 0.701
77 | 104 | 297 | 64 | ∆T | 21.9
77 | 104 | 297 | 64 | LDB | 55.1
77 | 104 | 297 | 64 | LWB | 52.4
77 | 104 | 297 | 64 | kW | 0.92
80 | 104 | 297 | 67 | MBh | 3.2
80 | 104 | 297 | 67 | S/T | 1
80 | 104 | 297 | 67 | ∆T | 10
80 | 104 | 297 | 67 | LDB | 70
80 | 104 | 297 | 67 | LWB | 63.7
80 | 104 | 297 | 67 | kW | 0.92
86 | 104 | 297 | 72 | MBh | 11.05
86 | 104 | 297 | 72 | S/T | 0.654
86 | 104 | 297 | 72 | ∆T | 22.5
86 | 104 | 297 | 72 | LDB | 63.5
86 | 104 | 297 | 72 | LWB | 61.4
86 | 104 | 297 | 72 | kW | 0.93
90 | 104 | 297 | 75 | MBh | 11.55
90 | 104 | 297 | 75 | S/T | 0.611
90 | 104 | 297 | 75 | ∆T | 22
90 | 104 | 297 | 75 | LDB | 68
90 | 104 | 297 | 75 | LWB | 64.7
90 | 104 | 297 | 75 | kW | 0.93
68 | 115 | 297 | 57 | MBh | 8.43
68 | 115 | 297 | 57 | S/T | 0.765
68 | 115 | 297 | 57 | ∆T | 20.1
68 | 115 | 297 | 57 | LDB | 47.9
68 | 115 | 297 | 57 | LWB | 45.9
68 | 115 | 297 | 57 | kW | 0.99
72 | 115 | 297 | 61 | MBh | 8.93
72 | 115 | 297 | 61 | S/T | 0.717
72 | 115 | 297 | 61 | ∆T | 20
72 | 115 | 297 | 61 | LDB | 52
72 | 115 | 297 | 61 | LWB | 50.2
72 | 115 | 297 | 61 | kW | 0.99
77 | 115 | 297 | 64 | MBh | 9.43
77 | 115 | 297 | 64 | S/T | 0.719
77 | 115 | 297 | 64 | ∆T | 21.1
77 | 115 | 297 | 64 | LDB | 55.9
77 | 115 | 297 | 64 | LWB | 53.2
77 | 115 | 297 | 64 | kW | 1
80 | 115 | 297 | 67 | MBh | 9.78
80 | 115 | 297 | 67 | S/T | 0.699
80 | 115 | 297 | 67 | ∆T | 21.3
80 | 115 | 297 | 67 | LDB | 58.7
80 | 115 | 297 | 67 | LWB | 56.5
80 | 115 | 297 | 67 | kW | 1
86 | 115 | 297 | 72 | MBh | 10.44
86 | 115 | 297 | 72 | S/T | 0.67
86 | 115 | 297 | 72 | ∆T | 21.8
86 | 115 | 297 | 72 | LDB | 64.2
86 | 115 | 297 | 72 | LWB | 62
86 | 115 | 297 | 72 | kW | 1
90 | 115 | 297 | 75 | MBh | 10.94
90 | 115 | 297 | 75 | S/T | 0.627
90 | 115 | 297 | 75 | ∆T | 21.4
90 | 115 | 297 | 75 | LDB | 68.6
90 | 115 | 297 | 75 | LWB | 65.3
90 | 115 | 297 | 75 | kW | 1.01

## RXP09AVJU9 - FVXV09AVJUT9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 297 | 57 | MBh | 12.08 | 75 | 60 | 59 | 20.6 | 1.76
68 | 50 | 297 | 57 | S/T | 0.692 | 75 | 60 | 70 | 19.69 | 1.76
68 | 50 | 297 | 57 | ∆T | 26.1 | 75 | 60 | 72 | 19.15 | 1.69
68 | 50 | 297 | 57 | LDB | 41.9 | 75 | 60 | 75 | 17.96 | 1.53
68 | 50 | 297 | 57 | LWB | 40.3 | 75 | 60 | 77 | 17.36 | 1.46
68 | 50 | 297 | 57 | kW | 0.53 | 75 | 60 | 81 | 16.16 | 1.31
72 | 50 | 297 | 61 | MBh | 12.59 | 47 | 43 | 59 | 17.82 | 1.63
72 | 50 | 297 | 61 | S/T | 0.651 | 47 | 43 | 70 | 17.1 | 1.67
72 | 50 | 297 | 61 | ∆T | 25.5 | 47 | 43 | 72 | 16.99 | 1.68
72 | 50 | 297 | 61 | LDB | 46.5 | 47 | 43 | 75 | 16.76 | 1.69
72 | 50 | 297 | 61 | LWB | 45 | 47 | 43 | 77 | 16.64 | 1.7
72 | 50 | 297 | 61 | kW | 0.54 | 47 | 43 | 81 | 16.16 | 1.66
77 | 50 | 297 | 64 | MBh | 13.09 | 35 | 32 | 59 | 16.08 | 1.65
77 | 50 | 297 | 64 | S/T | 0.646 | 35 | 32 | 70 | 15.33 | 1.7
77 | 50 | 297 | 64 | ∆T | 26.3 | 35 | 32 | 72 | 15.22 | 1.71
77 | 50 | 297 | 64 | LDB | 50.7 | 35 | 32 | 75 | 14.97 | 1.72
77 | 50 | 297 | 64 | LWB | 48.4 | 35 | 32 | 77 | 14.85 | 1.73
77 | 50 | 297 | 64 | kW | 0.54 | 35 | 32 | 81 | 14.61 | 1.75
80 | 50 | 297 | 67 | MBh | 13.44 | 25 | 23 | 59 | 14.63 | 1.67
80 | 50 | 297 | 67 | S/T | 0.627 | 25 | 23 | 70 | 13.85 | 1.73
80 | 50 | 297 | 67 | ∆T | 26.3 | 25 | 23 | 72 | 13.74 | 1.73
80 | 50 | 297 | 67 | LDB | 53.7 | 25 | 23 | 75 | 13.48 | 1.75
80 | 50 | 297 | 67 | LWB | 52 | 25 | 23 | 77 | 13.36 | 1.76
80 | 50 | 297 | 67 | kW | 0.54 | 25 | 23 | 81 | 13.1 | 1.78
86 | 50 | 297 | 72 | MBh | 14.09 | 16 | 14 | 59 | 13.19 | 1.69
86 | 50 | 297 | 72 | S/T | 0.598 | 16 | 14 | 70 | 12.38 | 1.75
86 | 50 | 297 | 72 | ∆T | 26.3 | 16 | 14 | 72 | 12.26 | 1.76
86 | 50 | 297 | 72 | LDB | 59.7 | 16 | 14 | 75 | 11.99 | 1.78
86 | 50 | 297 | 72 | LWB | 58 | 16 | 14 | 77 | 11.85 | 1.79
86 | 50 | 297 | 72 | kW | 0.55 | 16 | 14 | 81 | 11.59 | 1.8
90 | 50 | 297 | 75 | MBh | 14.59 | 5 | 5 | 59 | 11.77 | 1.72
90 | 50 | 297 | 75 | S/T | 0.559 | 5 | 5 | 70 | 10.9 | 1.77
90 | 50 | 297 | 75 | ∆T | 25.4 | 5 | 5 | 72 | 10.77 | 1.78
90 | 50 | 297 | 75 | LDB | 64.6 | 5 | 5 | 75 | 10.48 | 1.8
90 | 50 | 297 | 75 | LWB | 61.5 | 5 | 5 | 77 | 10.34 | 1.81
90 | 50 | 297 | 75 | kW | 0.68 | 5 | 5 | 81 | 10.06 | 1.83
68 | 68 | 297 | 57 | MBh | 11.07 | -4 | -4 | 59 | 9.71 | 1.68
68 | 68 | 297 | 57 | S/T | 0.705 | -4 | -4 | 70 | 8.81 | 1.74
68 | 68 | 297 | 57 | ∆T | 24.3 | -4 | -4 | 72 | 8.68 | 1.74
68 | 68 | 297 | 57 | LDB | 43.7 | -4 | -4 | 75 | 8.38 | 1.76
68 | 68 | 297 | 57 | LWB | 41.9 | -4 | -4 | 77 | 8.24 | 1.77
68 | 68 | 297 | 57 | kW | 0.66 | -4 | -4 | 81 | 7.67 | 1.67
72 | 68 | 297 | 61 | MBh | 11.57 | -13 | -14 | 59 | 7.57 | 1.64
72 | 68 | 297 | 61 | S/T | 0.663 | -13 | -14 | 70 | 6.03 | 1.42
72 | 68 | 297 | 61 | ∆T | 23.9 | -13 | -14 | 72 | 5.5 | 1.25
72 | 68 | 297 | 61 | LDB | 48.1 | -13 | -14 | 75 | 4.3 | 0.91
72 | 68 | 297 | 61 | LWB | 46.5 | -13 | -14 | 77 | 3.7 | 0.76
72 | 68 | 297 | 61 | kW | 0.66 | -13 | -14 | 81 | 2.5 | 0.48
77 | 68 | 297 | 64 | MBh | 12.07
77 | 68 | 297 | 64 | S/T | 0.66
77 | 68 | 297 | 64 | ∆T | 24.8
77 | 68 | 297 | 64 | LDB | 52.2
77 | 68 | 297 | 64 | LWB | 49.8
77 | 68 | 297 | 64 | kW | 0.67
80 | 68 | 297 | 67 | MBh | 12.42
80 | 68 | 297 | 67 | S/T | 0.642
80 | 68 | 297 | 67 | ∆T | 24.8
80 | 68 | 297 | 67 | LDB | 55.2
80 | 68 | 297 | 67 | LWB | 53.3
80 | 68 | 297 | 67 | kW | 0.67
86 | 68 | 297 | 72 | MBh | 13.08
86 | 68 | 297 | 72 | S/T | 0.613
86 | 68 | 297 | 72 | ∆T | 25
86 | 68 | 297 | 72 | LDB | 61
86 | 68 | 297 | 72 | LWB | 59.2
86 | 68 | 297 | 72 | kW | 0.67
90 | 68 | 297 | 75 | MBh | 13.58
90 | 68 | 297 | 75 | S/T | 0.574
90 | 68 | 297 | 75 | ∆T | 24.3
90 | 68 | 297 | 75 | LDB | 65.7
90 | 68 | 297 | 75 | LWB | 62.6
90 | 68 | 297 | 75 | kW | 0.68
68 | 86 | 297 | 57 | MBh | 10.05
68 | 86 | 297 | 57 | S/T | 0.723
68 | 86 | 297 | 57 | ∆T | 22.7
68 | 86 | 297 | 57 | LDB | 45.3
68 | 86 | 297 | 57 | LWB | 43.5
68 | 86 | 297 | 57 | kW | 0.79
72 | 86 | 297 | 61 | MBh | 10.56
72 | 86 | 297 | 61 | S/T | 0.679
72 | 86 | 297 | 61 | ∆T | 22.4
72 | 86 | 297 | 61 | LDB | 49.6
72 | 86 | 297 | 61 | LWB | 47.9
72 | 86 | 297 | 61 | kW | 0.79
77 | 86 | 297 | 64 | MBh | 11.06
77 | 86 | 297 | 64 | S/T | 0.678
77 | 86 | 297 | 64 | ∆T | 23.4
77 | 86 | 297 | 64 | LDB | 53.6
77 | 86 | 297 | 64 | LWB | 51.1
77 | 86 | 297 | 64 | kW | 0.79
80 | 86 | 297 | 67 | MBh | 11.41
80 | 86 | 297 | 67 | S/T | 0.66
80 | 86 | 297 | 67 | ∆T | 23.5
80 | 86 | 297 | 67 | LDB | 56.5
80 | 86 | 297 | 67 | LWB | 54.6
80 | 86 | 297 | 67 | kW | 0.8
86 | 86 | 297 | 72 | MBh | 12.06
86 | 86 | 297 | 72 | S/T | 0.632
86 | 86 | 297 | 72 | ∆T | 23.8
86 | 86 | 297 | 72 | LDB | 62.2
86 | 86 | 297 | 72 | LWB | 60.3
86 | 86 | 297 | 72 | kW | 0.8
90 | 86 | 297 | 75 | MBh | 12.56
90 | 86 | 297 | 75 | S/T | 0.591
90 | 86 | 297 | 75 | ∆T | 23.1
90 | 86 | 297 | 75 | LDB | 66.9
90 | 86 | 297 | 75 | LWB | 63.7
90 | 86 | 297 | 75 | kW | 0.8
68 | 95 | 297 | 57 | MBh | 9.55
68 | 95 | 297 | 57 | S/T | 0.734
68 | 95 | 297 | 57 | ∆T | 21.9
68 | 95 | 297 | 57 | LDB | 46.1
68 | 95 | 297 | 57 | LWB | 44.2
68 | 95 | 297 | 57 | kW | 0.85
72 | 95 | 297 | 61 | MBh | 10.05
72 | 95 | 297 | 61 | S/T | 0.689
72 | 95 | 297 | 61 | ∆T | 21.6
72 | 95 | 297 | 61 | LDB | 50.4
72 | 95 | 297 | 61 | LWB | 48.6
72 | 95 | 297 | 61 | kW | 0.85
77 | 95 | 297 | 64 | MBh | 10.55
77 | 95 | 297 | 64 | S/T | 0.689
77 | 95 | 297 | 64 | ∆T | 22.7
77 | 95 | 297 | 64 | LDB | 54.3
77 | 95 | 297 | 64 | LWB | 51.8
77 | 95 | 297 | 64 | kW | 0.86
80 | 95 | 297 | 67 | MBh | 10.9
80 | 95 | 297 | 67 | S/T | 0.671
80 | 95 | 297 | 67 | ∆T | 22.8
80 | 95 | 297 | 67 | LDB | 57.2
80 | 95 | 297 | 67 | LWB | 55.2
80 | 95 | 297 | 67 | kW | 0.86
86 | 95 | 297 | 72 | MBh | 11.55
86 | 95 | 297 | 72 | S/T | 0.642
86 | 95 | 297 | 72 | ∆T | 23.1
86 | 95 | 297 | 72 | LDB | 62.9
86 | 95 | 297 | 72 | LWB | 60.9
86 | 95 | 297 | 72 | kW | 0.86
90 | 95 | 297 | 75 | MBh | 12.06
90 | 95 | 297 | 75 | S/T | 0.6
90 | 95 | 297 | 75 | ∆T | 22.6
90 | 95 | 297 | 75 | LDB | 67.4
90 | 95 | 297 | 75 | LWB | 64.2
90 | 95 | 297 | 75 | kW | 0.87
68 | 104 | 297 | 57 | MBh | 9.04
68 | 104 | 297 | 57 | S/T | 0.747
68 | 104 | 297 | 57 | ∆T | 21
68 | 104 | 297 | 57 | LDB | 47
68 | 104 | 297 | 57 | LWB | 45
68 | 104 | 297 | 57 | kW | 0.91
72 | 104 | 297 | 61 | MBh | 9.54
72 | 104 | 297 | 61 | S/T | 0.7
72 | 104 | 297 | 61 | ∆T | 20.8
72 | 104 | 297 | 61 | LDB | 51.2
72 | 104 | 297 | 61 | LWB | 49.3
72 | 104 | 297 | 61 | kW | 0.92
77 | 104 | 297 | 64 | MBh | 10.04
77 | 104 | 297 | 64 | S/T | 0.701
77 | 104 | 297 | 64 | ∆T | 21.9
77 | 104 | 297 | 64 | LDB | 55.1
77 | 104 | 297 | 64 | LWB | 52.4
77 | 104 | 297 | 64 | kW | 0.92
80 | 104 | 297 | 67 | MBh | 3.2
80 | 104 | 297 | 67 | S/T | 1
80 | 104 | 297 | 67 | ∆T | 10
80 | 104 | 297 | 67 | LDB | 70
80 | 104 | 297 | 67 | LWB | 63.7
80 | 104 | 297 | 67 | kW | 0.92
86 | 104 | 297 | 72 | MBh | 11.05
86 | 104 | 297 | 72 | S/T | 0.654
86 | 104 | 297 | 72 | ∆T | 22.5
86 | 104 | 297 | 72 | LDB | 63.5
86 | 104 | 297 | 72 | LWB | 61.4
86 | 104 | 297 | 72 | kW | 0.93
90 | 104 | 297 | 75 | MBh | 11.55
90 | 104 | 297 | 75 | S/T | 0.611
90 | 104 | 297 | 75 | ∆T | 22
90 | 104 | 297 | 75 | LDB | 68
90 | 104 | 297 | 75 | LWB | 64.7
90 | 104 | 297 | 75 | kW | 0.93
68 | 115 | 297 | 57 | MBh | 8.43
68 | 115 | 297 | 57 | S/T | 0.765
68 | 115 | 297 | 57 | ∆T | 20.1
68 | 115 | 297 | 57 | LDB | 47.9
68 | 115 | 297 | 57 | LWB | 45.9
68 | 115 | 297 | 57 | kW | 0.99
72 | 115 | 297 | 61 | MBh | 8.93
72 | 115 | 297 | 61 | S/T | 0.717
72 | 115 | 297 | 61 | ∆T | 20
72 | 115 | 297 | 61 | LDB | 52
72 | 115 | 297 | 61 | LWB | 50.2
72 | 115 | 297 | 61 | kW | 0.99
77 | 115 | 297 | 64 | MBh | 9.43
77 | 115 | 297 | 64 | S/T | 0.719
77 | 115 | 297 | 64 | ∆T | 21.1
77 | 115 | 297 | 64 | LDB | 55.9
77 | 115 | 297 | 64 | LWB | 53.2
77 | 115 | 297 | 64 | kW | 1
80 | 115 | 297 | 67 | MBh | 9.78
80 | 115 | 297 | 67 | S/T | 0.699
80 | 115 | 297 | 67 | ∆T | 21.3
80 | 115 | 297 | 67 | LDB | 58.7
80 | 115 | 297 | 67 | LWB | 56.5
80 | 115 | 297 | 67 | kW | 1
86 | 115 | 297 | 72 | MBh | 10.44
86 | 115 | 297 | 72 | S/T | 0.67
86 | 115 | 297 | 72 | ∆T | 21.8
86 | 115 | 297 | 72 | LDB | 64.2
86 | 115 | 297 | 72 | LWB | 62
86 | 115 | 297 | 72 | kW | 1
90 | 115 | 297 | 75 | MBh | 10.94
90 | 115 | 297 | 75 | S/T | 0.627
90 | 115 | 297 | 75 | ∆T | 21.4
90 | 115 | 297 | 75 | LDB | 68.6
90 | 115 | 297 | 75 | LWB | 65.3
90 | 115 | 297 | 75 | kW | 1.01

## RXP12AVJU9 - FVXV12AVJUW9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 321 | 57 | MBh | 13.92 | 75 | 60 | 59 | 24.8 | 2.04
68 | 50 | 321 | 57 | S/T | 0.677 | 75 | 60 | 70 | 23 | 1.93
68 | 50 | 321 | 57 | ∆T | 27.2 | 75 | 60 | 72 | 22.37 | 1.85
68 | 50 | 321 | 57 | LDB | 40.8 | 75 | 60 | 75 | 20.97 | 1.69
68 | 50 | 321 | 57 | LWB | 39 | 75 | 60 | 77 | 20.28 | 1.61
68 | 50 | 321 | 57 | kW | 0.72 | 75 | 60 | 81 | 18.88 | 1.46
72 | 50 | 321 | 61 | MBh | 14.55 | 47 | 43 | 59 | 20.74 | 1.89
72 | 50 | 321 | 61 | S/T | 0.637 | 47 | 43 | 70 | 19.9 | 1.94
72 | 50 | 321 | 61 | ∆T | 26.7 | 47 | 43 | 72 | 19.78 | 1.95
72 | 50 | 321 | 61 | LDB | 45.3 | 47 | 43 | 75 | 19.5 | 1.97
72 | 50 | 321 | 61 | LWB | 43.7 | 47 | 43 | 77 | 19.36 | 1.98
72 | 50 | 321 | 61 | kW | 0.73 | 47 | 43 | 81 | 18.88 | 1.95
77 | 50 | 321 | 64 | MBh | 15.13 | 35 | 32 | 59 | 18.17 | 1.84
77 | 50 | 321 | 64 | S/T | 0.629 | 35 | 32 | 70 | 17.33 | 1.9
77 | 50 | 321 | 64 | ∆T | 27.4 | 35 | 32 | 72 | 17.2 | 1.9
77 | 50 | 321 | 64 | LDB | 49.6 | 35 | 32 | 75 | 16.93 | 1.92
77 | 50 | 321 | 64 | LWB | 47.1 | 35 | 32 | 77 | 16.79 | 1.93
77 | 50 | 321 | 64 | kW | 0.73 | 35 | 32 | 81 | 16.51 | 1.95
80 | 50 | 321 | 67 | MBh | 15.53 | 25 | 23 | 59 | 16.04 | 1.8
80 | 50 | 321 | 67 | S/T | 0.61 | 25 | 23 | 70 | 15.19 | 1.86
80 | 50 | 321 | 67 | ∆T | 27.3 | 25 | 23 | 72 | 15.06 | 1.86
80 | 50 | 321 | 67 | LDB | 52.7 | 25 | 23 | 75 | 14.78 | 1.88
80 | 50 | 321 | 67 | LWB | 50.8 | 25 | 23 | 77 | 14.64 | 1.89
80 | 50 | 321 | 67 | kW | 0.74 | 25 | 23 | 81 | 14.36 | 1.91
86 | 50 | 321 | 72 | MBh | 16.29 | 16 | 14 | 59 | 13.9 | 1.76
86 | 50 | 321 | 72 | S/T | 0.579 | 16 | 14 | 70 | 13.04 | 1.81
86 | 50 | 321 | 72 | ∆T | 27.2 | 16 | 14 | 72 | 12.92 | 1.82
86 | 50 | 321 | 72 | LDB | 58.8 | 16 | 14 | 75 | 12.63 | 1.84
86 | 50 | 321 | 72 | LWB | 56.9 | 16 | 14 | 77 | 12.49 | 1.85
86 | 50 | 321 | 72 | kW | 0.74 | 16 | 14 | 81 | 12.21 | 1.87
90 | 50 | 321 | 75 | MBh | 16.87 | 5 | 5 | 59 | 11.77 | 1.72
90 | 50 | 321 | 75 | S/T | 0.54 | 5 | 5 | 70 | 10.9 | 1.77
90 | 50 | 321 | 75 | ∆T | 26.3 | 5 | 5 | 72 | 10.77 | 1.78
90 | 50 | 321 | 75 | LDB | 63.7 | 5 | 5 | 75 | 10.48 | 1.8
90 | 50 | 321 | 75 | LWB | 60.4 | 5 | 5 | 77 | 10.34 | 1.81
90 | 50 | 321 | 75 | kW | 0.75 | 5 | 5 | 81 | 10.06 | 1.83
68 | 68 | 321 | 57 | MBh | 12.79 | -4 | -4 | 59 | 9.71 | 1.68
68 | 68 | 321 | 57 | S/T | 0.687 | -4 | -4 | 70 | 8.81 | 1.74
68 | 68 | 321 | 57 | ∆T | 25.4 | -4 | -4 | 72 | 8.68 | 1.74
68 | 68 | 321 | 57 | LDB | 42.6 | -4 | -4 | 75 | 8.38 | 1.76
68 | 68 | 321 | 57 | LWB | 40.7 | -4 | -4 | 77 | 8.24 | 1.77
68 | 68 | 321 | 57 | kW | 0.9 | -4 | -4 | 81 | 7.94 | 1.79
72 | 68 | 321 | 61 | MBh | 13.37 | -13 | -14 | 59 | 7.57 | 1.64
72 | 68 | 321 | 61 | S/T | 0.646 | -13 | -14 | 70 | 6.63 | 1.7
72 | 68 | 321 | 61 | ∆T | 24.9 | -13 | -14 | 72 | 6.42 | 1.68
72 | 68 | 321 | 61 | LDB | 47.1 | -13 | -14 | 75 | 5.02 | 1.21
72 | 68 | 321 | 61 | LWB | 45.3 | -13 | -14 | 77 | 4.32 | 1
72 | 68 | 321 | 61 | kW | 0.9 | -13 | -14 | 81 | 2.92 | 0.63
77 | 68 | 321 | 64 | MBh | 13.95
77 | 68 | 321 | 64 | S/T | 0.64
77 | 68 | 321 | 64 | ∆T | 25.8
77 | 68 | 321 | 64 | LDB | 51.2
77 | 68 | 321 | 64 | LWB | 48.6
77 | 68 | 321 | 64 | kW | 0.91
80 | 68 | 321 | 67 | MBh | 14.36
80 | 68 | 321 | 67 | S/T | 0.621
80 | 68 | 321 | 67 | ∆T | 25.7
80 | 68 | 321 | 67 | LDB | 54.3
80 | 68 | 321 | 67 | LWB | 52.2
80 | 68 | 321 | 67 | kW | 0.91
86 | 68 | 321 | 72 | MBh | 15.12
86 | 68 | 321 | 72 | S/T | 0.591
86 | 68 | 321 | 72 | ∆T | 25.8
86 | 68 | 321 | 72 | LDB | 60.2
86 | 68 | 321 | 72 | LWB | 58.1
86 | 68 | 321 | 72 | kW | 0.92
90 | 68 | 321 | 75 | MBh | 15.7
90 | 68 | 321 | 75 | S/T | 0.551
90 | 68 | 321 | 75 | ∆T | 25
90 | 68 | 321 | 75 | LDB | 65
90 | 68 | 321 | 75 | LWB | 61.6
90 | 68 | 321 | 75 | kW | 0.92
68 | 86 | 321 | 57 | MBh | 11.62
68 | 86 | 321 | 57 | S/T | 0.701
68 | 86 | 321 | 57 | ∆T | 23.5
68 | 86 | 321 | 57 | LDB | 44.5
68 | 86 | 321 | 57 | LWB | 42.4
68 | 86 | 321 | 57 | kW | 1.07
72 | 86 | 321 | 61 | MBh | 12.2
72 | 86 | 321 | 61 | S/T | 0.659
72 | 86 | 321 | 61 | ∆T | 23.2
72 | 86 | 321 | 61 | LDB | 48.8
72 | 86 | 321 | 61 | LWB | 46.9
72 | 86 | 321 | 61 | kW | 1.07
77 | 86 | 321 | 64 | MBh | 12.78
77 | 86 | 321 | 64 | S/T | 0.654
77 | 86 | 321 | 64 | ∆T | 24.1
77 | 86 | 321 | 64 | LDB | 52.9
77 | 86 | 321 | 64 | LWB | 50.1
77 | 86 | 321 | 64 | kW | 1.08
80 | 86 | 321 | 67 | MBh | 13.19
80 | 86 | 321 | 67 | S/T | 0.635
80 | 86 | 321 | 67 | ∆T | 24.2
80 | 86 | 321 | 67 | LDB | 55.8
80 | 86 | 321 | 67 | LWB | 53.6
80 | 86 | 321 | 67 | kW | 1.08
86 | 86 | 321 | 72 | MBh | 13.94
86 | 86 | 321 | 72 | S/T | 0.605
86 | 86 | 321 | 72 | ∆T | 24.3
86 | 86 | 321 | 72 | LDB | 61.7
86 | 86 | 321 | 72 | LWB | 59.4
86 | 86 | 321 | 72 | kW | 1.09
90 | 86 | 321 | 75 | MBh | 14.52
90 | 86 | 321 | 75 | S/T | 0.565
90 | 86 | 321 | 75 | ∆T | 23.7
90 | 86 | 321 | 75 | LDB | 66.3
90 | 86 | 321 | 75 | LWB | 62.8
90 | 86 | 321 | 75 | kW | 1.09
68 | 95 | 321 | 57 | MBh | 11.03
68 | 95 | 321 | 57 | S/T | 0.711
68 | 95 | 321 | 57 | ∆T | 22.6
68 | 95 | 321 | 57 | LDB | 45.4
68 | 95 | 321 | 57 | LWB | 43.2
68 | 95 | 321 | 57 | kW | 1.16
72 | 95 | 321 | 61 | MBh | 11.61
72 | 95 | 321 | 61 | S/T | 0.667
72 | 95 | 321 | 61 | ∆T | 22.3
72 | 95 | 321 | 61 | LDB | 49.7
72 | 95 | 321 | 61 | LWB | 47.7
72 | 95 | 321 | 61 | kW | 1.16
77 | 95 | 321 | 64 | MBh | 12.19
77 | 95 | 321 | 64 | S/T | 0.663
77 | 95 | 321 | 64 | ∆T | 23.3
77 | 95 | 321 | 64 | LDB | 53.7
77 | 95 | 321 | 64 | LWB | 50.8
77 | 95 | 321 | 64 | kW | 1.17
80 | 95 | 321 | 67 | MBh | 12.6
80 | 95 | 321 | 67 | S/T | 0.644
80 | 95 | 321 | 67 | ∆T | 23.4
80 | 95 | 321 | 67 | LDB | 56.6
80 | 95 | 321 | 67 | LWB | 54.3
80 | 95 | 321 | 67 | kW | 1.17
86 | 95 | 321 | 72 | MBh | 13.36
86 | 95 | 321 | 72 | S/T | 0.614
86 | 95 | 321 | 72 | ∆T | 23.7
86 | 95 | 321 | 72 | LDB | 62.3
86 | 95 | 321 | 72 | LWB | 60
86 | 95 | 321 | 72 | kW | 1.18
90 | 95 | 321 | 75 | MBh | 13.94
90 | 95 | 321 | 75 | S/T | 0.573
90 | 95 | 321 | 75 | ∆T | 23
90 | 95 | 321 | 75 | LDB | 67
90 | 95 | 321 | 75 | LWB | 63.3
90 | 95 | 321 | 75 | kW | 1.18
68 | 104 | 321 | 57 | MBh | 10.45
68 | 104 | 321 | 57 | S/T | 0.721
68 | 104 | 321 | 57 | ∆T | 21.7
68 | 104 | 321 | 57 | LDB | 46.3
68 | 104 | 321 | 57 | LWB | 44
68 | 104 | 321 | 57 | kW | 1.24
72 | 104 | 321 | 61 | MBh | 11.03
72 | 104 | 321 | 61 | S/T | 0.675
72 | 104 | 321 | 61 | ∆T | 21.5
72 | 104 | 321 | 61 | LDB | 50.5
72 | 104 | 321 | 61 | LWB | 48.4
72 | 104 | 321 | 61 | kW | 1.25
77 | 104 | 321 | 64 | MBh | 11.61
77 | 104 | 321 | 64 | S/T | 0.673
77 | 104 | 321 | 64 | ∆T | 22.5
77 | 104 | 321 | 64 | LDB | 54.5
77 | 104 | 321 | 64 | LWB | 51.5
77 | 104 | 321 | 64 | kW | 1.25
80 | 104 | 321 | 67 | MBh | 3.69
80 | 104 | 321 | 67 | S/T | 1
80 | 104 | 321 | 67 | ∆T | 10.6
80 | 104 | 321 | 67 | LDB | 69.4
80 | 104 | 321 | 67 | LWB | 63.5
80 | 104 | 321 | 67 | kW | 1.26
86 | 104 | 321 | 72 | MBh | 12.77
86 | 104 | 321 | 72 | S/T | 0.624
86 | 104 | 321 | 72 | ∆T | 23
86 | 104 | 321 | 72 | LDB | 63
86 | 104 | 321 | 72 | LWB | 60.6
86 | 104 | 321 | 72 | kW | 1.26
90 | 104 | 321 | 75 | MBh | 13.35
90 | 104 | 321 | 75 | S/T | 0.583
90 | 104 | 321 | 75 | ∆T | 22.4
90 | 104 | 321 | 75 | LDB | 67.6
90 | 104 | 321 | 75 | LWB | 63.9
90 | 104 | 321 | 75 | kW | 1.27
68 | 115 | 321 | 57 | MBh | 9.74
68 | 115 | 321 | 57 | S/T | 0.736
68 | 115 | 321 | 57 | ∆T | 20.7
68 | 115 | 321 | 57 | LDB | 47.3
68 | 115 | 321 | 57 | LWB | 45
68 | 115 | 321 | 57 | kW | 1.17
72 | 115 | 321 | 61 | MBh | 10.32
72 | 115 | 321 | 61 | S/T | 0.689
72 | 115 | 321 | 61 | ∆T | 20.5
72 | 115 | 321 | 61 | LDB | 51.5
72 | 115 | 321 | 61 | LWB | 49.3
72 | 115 | 321 | 61 | kW | 1.17
77 | 115 | 321 | 64 | MBh | 10.9
77 | 115 | 321 | 64 | S/T | 0.687
77 | 115 | 321 | 64 | ∆T | 21.6
77 | 115 | 321 | 64 | LDB | 55.4
77 | 115 | 321 | 64 | LWB | 52.4
77 | 115 | 321 | 64 | kW | 1.17
80 | 115 | 321 | 67 | MBh | 11.31
80 | 115 | 321 | 67 | S/T | 0.668
80 | 115 | 321 | 67 | ∆T | 21.8
80 | 115 | 321 | 67 | LDB | 58.2
80 | 115 | 321 | 67 | LWB | 55.7
80 | 115 | 321 | 67 | kW | 1.17
86 | 115 | 321 | 72 | MBh | 12.06
86 | 115 | 321 | 72 | S/T | 0.638
86 | 115 | 321 | 72 | ∆T | 22.2
86 | 115 | 321 | 72 | LDB | 63.8
86 | 115 | 321 | 72 | LWB | 61.3
86 | 115 | 321 | 72 | kW | 1.17
90 | 115 | 321 | 75 | MBh | 12.64
90 | 115 | 321 | 75 | S/T | 0.596
90 | 115 | 321 | 75 | ∆T | 21.7
90 | 115 | 321 | 75 | LDB | 68.3
90 | 115 | 321 | 75 | LWB | 64.5
90 | 115 | 321 | 75 | kW | 1.17

## RXP12AVJU9 - FVXV12AVJUT9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 321 | 57 | MBh | 13.92 | 75 | 60 | 59 | 24.8 | 2.04
68 | 50 | 321 | 57 | S/T | 0.677 | 75 | 60 | 70 | 23 | 1.93
68 | 50 | 321 | 57 | ∆T | 27.2 | 75 | 60 | 72 | 22.37 | 1.85
68 | 50 | 321 | 57 | LDB | 40.8 | 75 | 60 | 75 | 20.97 | 1.69
68 | 50 | 321 | 57 | LWB | 39 | 75 | 60 | 77 | 20.28 | 1.61
68 | 50 | 321 | 57 | kW | 0.72 | 75 | 60 | 81 | 18.88 | 1.46
72 | 50 | 321 | 61 | MBh | 14.55 | 47 | 43 | 59 | 20.74 | 1.89
72 | 50 | 321 | 61 | S/T | 0.637 | 47 | 43 | 70 | 19.9 | 1.94
72 | 50 | 321 | 61 | ∆T | 26.7 | 47 | 43 | 72 | 19.78 | 1.95
72 | 50 | 321 | 61 | LDB | 45.3 | 47 | 43 | 75 | 19.5 | 1.97
72 | 50 | 321 | 61 | LWB | 43.7 | 47 | 43 | 77 | 19.36 | 1.98
72 | 50 | 321 | 61 | kW | 0.73 | 47 | 43 | 81 | 18.88 | 1.95
77 | 50 | 321 | 64 | MBh | 15.13 | 35 | 32 | 59 | 18.17 | 1.84
77 | 50 | 321 | 64 | S/T | 0.629 | 35 | 32 | 70 | 17.33 | 1.9
77 | 50 | 321 | 64 | ∆T | 27.4 | 35 | 32 | 72 | 17.2 | 1.9
77 | 50 | 321 | 64 | LDB | 49.6 | 35 | 32 | 75 | 16.93 | 1.92
77 | 50 | 321 | 64 | LWB | 47.1 | 35 | 32 | 77 | 16.79 | 1.93
77 | 50 | 321 | 64 | kW | 0.73 | 35 | 32 | 81 | 16.51 | 1.95
80 | 50 | 321 | 67 | MBh | 15.53 | 25 | 23 | 59 | 16.04 | 1.8
80 | 50 | 321 | 67 | S/T | 0.61 | 25 | 23 | 70 | 15.19 | 1.86
80 | 50 | 321 | 67 | ∆T | 27.3 | 25 | 23 | 72 | 15.06 | 1.86
80 | 50 | 321 | 67 | LDB | 52.7 | 25 | 23 | 75 | 14.78 | 1.88
80 | 50 | 321 | 67 | LWB | 50.8 | 25 | 23 | 77 | 14.64 | 1.89
80 | 50 | 321 | 67 | kW | 0.74 | 25 | 23 | 81 | 14.36 | 1.91
86 | 50 | 321 | 72 | MBh | 16.29 | 16 | 14 | 59 | 13.9 | 1.76
86 | 50 | 321 | 72 | S/T | 0.579 | 16 | 14 | 70 | 13.04 | 1.81
86 | 50 | 321 | 72 | ∆T | 27.2 | 16 | 14 | 72 | 12.92 | 1.82
86 | 50 | 321 | 72 | LDB | 58.8 | 16 | 14 | 75 | 12.63 | 1.84
86 | 50 | 321 | 72 | LWB | 56.9 | 16 | 14 | 77 | 12.49 | 1.85
86 | 50 | 321 | 72 | kW | 0.74 | 16 | 14 | 81 | 12.21 | 1.87
90 | 50 | 321 | 75 | MBh | 16.87 | 5 | 5 | 59 | 11.77 | 1.72
90 | 50 | 321 | 75 | S/T | 0.54 | 5 | 5 | 70 | 10.9 | 1.77
90 | 50 | 321 | 75 | ∆T | 26.3 | 5 | 5 | 72 | 10.77 | 1.78
90 | 50 | 321 | 75 | LDB | 63.7 | 5 | 5 | 75 | 10.48 | 1.8
90 | 50 | 321 | 75 | LWB | 60.4 | 5 | 5 | 77 | 10.34 | 1.81
90 | 50 | 321 | 75 | kW | 0.75 | 5 | 5 | 81 | 10.06 | 1.83
68 | 68 | 321 | 57 | MBh | 12.79 | -4 | -4 | 59 | 9.71 | 1.68
68 | 68 | 321 | 57 | S/T | 0.687 | -4 | -4 | 70 | 8.81 | 1.74
68 | 68 | 321 | 57 | ∆T | 25.4 | -4 | -4 | 72 | 8.68 | 1.74
68 | 68 | 321 | 57 | LDB | 42.6 | -4 | -4 | 75 | 8.38 | 1.76
68 | 68 | 321 | 57 | LWB | 40.7 | -4 | -4 | 77 | 8.24 | 1.77
68 | 68 | 321 | 57 | kW | 0.9 | -4 | -4 | 81 | 7.94 | 1.79
72 | 68 | 321 | 61 | MBh | 13.37 | -13 | -14 | 59 | 7.57 | 1.64
72 | 68 | 321 | 61 | S/T | 0.646 | -13 | -14 | 70 | 6.63 | 1.7
72 | 68 | 321 | 61 | ∆T | 24.9 | -13 | -14 | 72 | 6.42 | 1.68
72 | 68 | 321 | 61 | LDB | 47.1 | -13 | -14 | 75 | 5.02 | 1.21
72 | 68 | 321 | 61 | LWB | 45.3 | -13 | -14 | 77 | 4.32 | 1
72 | 68 | 321 | 61 | kW | 0.9 | -13 | -14 | 81 | 2.92 | 0.63
77 | 68 | 321 | 64 | MBh | 13.95
77 | 68 | 321 | 64 | S/T | 0.64
77 | 68 | 321 | 64 | ∆T | 25.8
77 | 68 | 321 | 64 | LDB | 51.2
77 | 68 | 321 | 64 | LWB | 48.6
77 | 68 | 321 | 64 | kW | 0.91
80 | 68 | 321 | 67 | MBh | 14.36
80 | 68 | 321 | 67 | S/T | 0.621
80 | 68 | 321 | 67 | ∆T | 25.7
80 | 68 | 321 | 67 | LDB | 54.3
80 | 68 | 321 | 67 | LWB | 52.2
80 | 68 | 321 | 67 | kW | 0.91
86 | 68 | 321 | 72 | MBh | 15.12
86 | 68 | 321 | 72 | S/T | 0.591
86 | 68 | 321 | 72 | ∆T | 25.8
86 | 68 | 321 | 72 | LDB | 60.2
86 | 68 | 321 | 72 | LWB | 58.1
86 | 68 | 321 | 72 | kW | 0.92
90 | 68 | 321 | 75 | MBh | 15.7
90 | 68 | 321 | 75 | S/T | 0.551
90 | 68 | 321 | 75 | ∆T | 25
90 | 68 | 321 | 75 | LDB | 65
90 | 68 | 321 | 75 | LWB | 61.6
90 | 68 | 321 | 75 | kW | 0.92
68 | 86 | 321 | 57 | MBh | 11.62
68 | 86 | 321 | 57 | S/T | 0.701
68 | 86 | 321 | 57 | ∆T | 23.5
68 | 86 | 321 | 57 | LDB | 44.5
68 | 86 | 321 | 57 | LWB | 42.4
68 | 86 | 321 | 57 | kW | 1.07
72 | 86 | 321 | 61 | MBh | 12.2
72 | 86 | 321 | 61 | S/T | 0.659
72 | 86 | 321 | 61 | ∆T | 23.2
72 | 86 | 321 | 61 | LDB | 48.8
72 | 86 | 321 | 61 | LWB | 46.9
72 | 86 | 321 | 61 | kW | 1.07
77 | 86 | 321 | 64 | MBh | 12.78
77 | 86 | 321 | 64 | S/T | 0.654
77 | 86 | 321 | 64 | ∆T | 24.1
77 | 86 | 321 | 64 | LDB | 52.9
77 | 86 | 321 | 64 | LWB | 50.1
77 | 86 | 321 | 64 | kW | 1.08
80 | 86 | 321 | 67 | MBh | 13.19
80 | 86 | 321 | 67 | S/T | 0.635
80 | 86 | 321 | 67 | ∆T | 24.2
80 | 86 | 321 | 67 | LDB | 55.8
80 | 86 | 321 | 67 | LWB | 53.6
80 | 86 | 321 | 67 | kW | 1.08
86 | 86 | 321 | 72 | MBh | 13.94
86 | 86 | 321 | 72 | S/T | 0.605
86 | 86 | 321 | 72 | ∆T | 24.3
86 | 86 | 321 | 72 | LDB | 61.7
86 | 86 | 321 | 72 | LWB | 59.4
86 | 86 | 321 | 72 | kW | 1.09
90 | 86 | 321 | 75 | MBh | 14.52
90 | 86 | 321 | 75 | S/T | 0.565
90 | 86 | 321 | 75 | ∆T | 23.7
90 | 86 | 321 | 75 | LDB | 66.3
90 | 86 | 321 | 75 | LWB | 62.8
90 | 86 | 321 | 75 | kW | 1.09
68 | 95 | 321 | 57 | MBh | 11.03
68 | 95 | 321 | 57 | S/T | 0.711
68 | 95 | 321 | 57 | ∆T | 22.6
68 | 95 | 321 | 57 | LDB | 45.4
68 | 95 | 321 | 57 | LWB | 43.2
68 | 95 | 321 | 57 | kW | 1.16
72 | 95 | 321 | 61 | MBh | 11.61
72 | 95 | 321 | 61 | S/T | 0.667
72 | 95 | 321 | 61 | ∆T | 22.3
72 | 95 | 321 | 61 | LDB | 49.7
72 | 95 | 321 | 61 | LWB | 47.7
72 | 95 | 321 | 61 | kW | 1.16
77 | 95 | 321 | 64 | MBh | 12.19
77 | 95 | 321 | 64 | S/T | 0.663
77 | 95 | 321 | 64 | ∆T | 23.3
77 | 95 | 321 | 64 | LDB | 53.7
77 | 95 | 321 | 64 | LWB | 50.8
77 | 95 | 321 | 64 | kW | 1.17
80 | 95 | 321 | 67 | MBh | 12.6
80 | 95 | 321 | 67 | S/T | 0.644
80 | 95 | 321 | 67 | ∆T | 23.4
80 | 95 | 321 | 67 | LDB | 56.6
80 | 95 | 321 | 67 | LWB | 54.3
80 | 95 | 321 | 67 | kW | 1.17
86 | 95 | 321 | 72 | MBh | 13.36
86 | 95 | 321 | 72 | S/T | 0.614
86 | 95 | 321 | 72 | ∆T | 23.7
86 | 95 | 321 | 72 | LDB | 62.3
86 | 95 | 321 | 72 | LWB | 60
86 | 95 | 321 | 72 | kW | 1.18
90 | 95 | 321 | 75 | MBh | 13.94
90 | 95 | 321 | 75 | S/T | 0.573
90 | 95 | 321 | 75 | ∆T | 23
90 | 95 | 321 | 75 | LDB | 67
90 | 95 | 321 | 75 | LWB | 63.3
90 | 95 | 321 | 75 | kW | 1.18
68 | 104 | 321 | 57 | MBh | 10.45
68 | 104 | 321 | 57 | S/T | 0.721
68 | 104 | 321 | 57 | ∆T | 21.7
68 | 104 | 321 | 57 | LDB | 46.3
68 | 104 | 321 | 57 | LWB | 44
68 | 104 | 321 | 57 | kW | 1.24
72 | 104 | 321 | 61 | MBh | 11.03
72 | 104 | 321 | 61 | S/T | 0.675
72 | 104 | 321 | 61 | ∆T | 21.5
72 | 104 | 321 | 61 | LDB | 50.5
72 | 104 | 321 | 61 | LWB | 48.4
72 | 104 | 321 | 61 | kW | 1.25
77 | 104 | 321 | 64 | MBh | 11.61
77 | 104 | 321 | 64 | S/T | 0.673
77 | 104 | 321 | 64 | ∆T | 22.5
77 | 104 | 321 | 64 | LDB | 54.5
77 | 104 | 321 | 64 | LWB | 51.5
77 | 104 | 321 | 64 | kW | 1.25
80 | 104 | 321 | 67 | MBh | 3.69
80 | 104 | 321 | 67 | S/T | 1
80 | 104 | 321 | 67 | ∆T | 10.6
80 | 104 | 321 | 67 | LDB | 69.4
80 | 104 | 321 | 67 | LWB | 63.5
80 | 104 | 321 | 67 | kW | 1.26
86 | 104 | 321 | 72 | MBh | 12.77
86 | 104 | 321 | 72 | S/T | 0.624
86 | 104 | 321 | 72 | ∆T | 23
86 | 104 | 321 | 72 | LDB | 63
86 | 104 | 321 | 72 | LWB | 60.6
86 | 104 | 321 | 72 | kW | 1.26
90 | 104 | 321 | 75 | MBh | 13.35
90 | 104 | 321 | 75 | S/T | 0.583
90 | 104 | 321 | 75 | ∆T | 22.4
90 | 104 | 321 | 75 | LDB | 67.6
90 | 104 | 321 | 75 | LWB | 63.9
90 | 104 | 321 | 75 | kW | 1.27
68 | 115 | 321 | 57 | MBh | 9.74
68 | 115 | 321 | 57 | S/T | 0.736
68 | 115 | 321 | 57 | ∆T | 20.7
68 | 115 | 321 | 57 | LDB | 47.3
68 | 115 | 321 | 57 | LWB | 45
68 | 115 | 321 | 57 | kW | 1.17
72 | 115 | 321 | 61 | MBh | 10.32
72 | 115 | 321 | 61 | S/T | 0.689
72 | 115 | 321 | 61 | ∆T | 20.5
72 | 115 | 321 | 61 | LDB | 51.5
72 | 115 | 321 | 61 | LWB | 49.3
72 | 115 | 321 | 61 | kW | 1.17
77 | 115 | 321 | 64 | MBh | 10.9
77 | 115 | 321 | 64 | S/T | 0.687
77 | 115 | 321 | 64 | ∆T | 21.6
77 | 115 | 321 | 64 | LDB | 55.4
77 | 115 | 321 | 64 | LWB | 52.4
77 | 115 | 321 | 64 | kW | 1.17
80 | 115 | 321 | 67 | MBh | 11.31
80 | 115 | 321 | 67 | S/T | 0.668
80 | 115 | 321 | 67 | ∆T | 21.8
80 | 115 | 321 | 67 | LDB | 58.2
80 | 115 | 321 | 67 | LWB | 55.7
80 | 115 | 321 | 67 | kW | 1.17
86 | 115 | 321 | 72 | MBh | 12.06
86 | 115 | 321 | 72 | S/T | 0.638
86 | 115 | 321 | 72 | ∆T | 22.2
86 | 115 | 321 | 72 | LDB | 63.8
86 | 115 | 321 | 72 | LWB | 61.3
86 | 115 | 321 | 72 | kW | 1.17
90 | 115 | 321 | 75 | MBh | 12.64
90 | 115 | 321 | 75 | S/T | 0.596
90 | 115 | 321 | 75 | ∆T | 21.7
90 | 115 | 321 | 75 | LDB | 68.3
90 | 115 | 321 | 75 | LWB | 64.5
90 | 115 | 321 | 75 | kW | 1.17

## RXP15AVJU9 - FVXV15AVJUW9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 392 | 57 | MBh | 16.82 | 75 | 60 | 59 | 25.48 | 2.04
68 | 50 | 392 | 57 | S/T | 0.678 | 75 | 60 | 70 | 24.66 | 2.06
68 | 50 | 392 | 57 | ∆T | 26.9 | 75 | 60 | 72 | 23.25 | 1.91
68 | 50 | 392 | 57 | LDB | 41.1 | 75 | 60 | 75 | 21.84 | 1.77
68 | 50 | 392 | 57 | LWB | 39.2 | 75 | 60 | 77 | 21.14 | 1.7
68 | 50 | 392 | 57 | kW | 0.75 | 75 | 60 | 81 | 19.73 | 1.56
72 | 50 | 392 | 61 | MBh | 19.97 | 47 | 43 | 59 | 21.1 | 1.89
72 | 50 | 392 | 61 | S/T | 0.628 | 47 | 43 | 70 | 20.4 | 1.93
72 | 50 | 392 | 61 | ∆T | 29.6 | 47 | 43 | 72 | 20.12 | 1.95
72 | 50 | 392 | 61 | LDB | 42.4 | 47 | 43 | 75 | 19.84 | 1.96
72 | 50 | 392 | 61 | LWB | 41.1 | 47 | 43 | 77 | 19.7 | 1.97
72 | 50 | 392 | 61 | kW | 0.9 | 47 | 43 | 81 | 19.41 | 1.99
77 | 50 | 392 | 64 | MBh | 22.93 | 35 | 32 | 59 | 20.5 | 2.16
77 | 50 | 392 | 64 | S/T | 0.611 | 35 | 32 | 70 | 19.71 | 2.22
77 | 50 | 392 | 64 | ∆T | 33.1 | 35 | 32 | 72 | 19.4 | 2.24
77 | 50 | 392 | 64 | LDB | 43.9 | 35 | 32 | 75 | 19.08 | 2.26
77 | 50 | 392 | 64 | LWB | 42 | 35 | 32 | 77 | 18.93 | 2.27
77 | 50 | 392 | 64 | kW | 1.04 | 35 | 32 | 81 | 18.61 | 2.29
80 | 50 | 392 | 67 | MBh | 23.55 | 25 | 23 | 59 | 20.02 | 2.39
80 | 50 | 392 | 67 | S/T | 0.59 | 25 | 23 | 70 | 19.14 | 2.45
80 | 50 | 392 | 67 | ∆T | 32.8 | 25 | 23 | 72 | 18.79 | 2.48
80 | 50 | 392 | 67 | LDB | 47.2 | 25 | 23 | 75 | 18.44 | 2.5
80 | 50 | 392 | 67 | LWB | 45.9 | 25 | 23 | 77 | 18.26 | 2.51
80 | 50 | 392 | 67 | kW | 1.05 | 25 | 23 | 81 | 17.91 | 2.54
86 | 50 | 392 | 72 | MBh | 24.69 | 16 | 14 | 59 | 19.58 | 2.62
86 | 50 | 392 | 72 | S/T | 0.556 | 16 | 14 | 70 | 18.57 | 2.69
86 | 50 | 392 | 72 | ∆T | 32.4 | 16 | 14 | 72 | 18.17 | 2.72
86 | 50 | 392 | 72 | LDB | 53.6 | 16 | 14 | 75 | 17.77 | 2.75
86 | 50 | 392 | 72 | LWB | 52.4 | 16 | 14 | 77 | 17.57 | 2.76
86 | 50 | 392 | 72 | kW | 1.06 | 16 | 14 | 81 | 17.17 | 2.79
90 | 50 | 392 | 75 | MBh | 25.57 | 5 | 5 | 59 | 19.18 | 2.85
90 | 50 | 392 | 75 | S/T | 0.517 | 5 | 5 | 70 | 18 | 2.93
90 | 50 | 392 | 75 | ∆T | 31.2 | 5 | 5 | 72 | 17.21 | 2.85
90 | 50 | 392 | 75 | LDB | 58.8 | 5 | 5 | 75 | 15.8 | 2.56
90 | 50 | 392 | 75 | LWB | 56.1 | 5 | 5 | 77 | 15.1 | 2.42
90 | 50 | 392 | 75 | kW | 1.06 | 5 | 5 | 81 | 13.69 | 2.15
68 | 68 | 392 | 57 | MBh | 16.82 | -4 | -4 | 59 | 16.58 | 2.56
68 | 68 | 392 | 57 | S/T | 0.678 | -4 | -4 | 70 | 15.3 | 2.64
68 | 68 | 392 | 57 | ∆T | 26.9 | -4 | -4 | 72 | 14.68 | 2.63
68 | 68 | 392 | 57 | LDB | 41.1 | -4 | -4 | 75 | 13.27 | 2.34
68 | 68 | 392 | 57 | LWB | 39.2 | -4 | -4 | 77 | 12.57 | 2.2
68 | 68 | 392 | 57 | kW | 1.03 | -4 | -4 | 81 | 11.16 | 1.92
72 | 68 | 392 | 61 | MBh | 19.97 | -13 | -14 | 59 | 14.05 | 2.27
72 | 68 | 392 | 61 | S/T | 0.628 | -13 | -14 | 70 | 12.6 | 2.34
72 | 68 | 392 | 61 | ∆T | 29.6 | -13 | -14 | 72 | 12.02 | 2.37
72 | 68 | 392 | 61 | LDB | 42.4 | -13 | -14 | 75 | 11.36 | 2.37
72 | 68 | 392 | 61 | LWB | 41.1 | -13 | -14 | 77 | 10.66 | 2.22
72 | 68 | 392 | 61 | kW | 1.25 | -13 | -14 | 81 | 9.25 | 1.92
77 | 68 | 392 | 64 | MBh | 21.15
77 | 68 | 392 | 64 | S/T | 0.615
77 | 68 | 392 | 64 | ∆T | 30.7
77 | 68 | 392 | 64 | LDB | 46.3
77 | 68 | 392 | 64 | LWB | 44.1
77 | 68 | 392 | 64 | kW | 1.29
80 | 68 | 392 | 67 | MBh | 21.77
80 | 68 | 392 | 67 | S/T | 0.595
80 | 68 | 392 | 67 | ∆T | 30.6
80 | 68 | 392 | 67 | LDB | 49.4
80 | 68 | 392 | 67 | LWB | 47.9
80 | 68 | 392 | 67 | kW | 1.29
86 | 68 | 392 | 72 | MBh | 22.91
86 | 68 | 392 | 72 | S/T | 0.561
86 | 68 | 392 | 72 | ∆T | 30.4
86 | 68 | 392 | 72 | LDB | 55.6
86 | 68 | 392 | 72 | LWB | 54.1
86 | 68 | 392 | 72 | kW | 1.3
90 | 68 | 392 | 75 | MBh | 23.79
90 | 68 | 392 | 75 | S/T | 0.522
90 | 68 | 392 | 75 | ∆T | 29.4
90 | 68 | 392 | 75 | LDB | 60.6
90 | 68 | 392 | 75 | LWB | 57.7
90 | 68 | 392 | 75 | kW | 1.31
68 | 86 | 392 | 57 | MBh | 16.82
68 | 86 | 392 | 57 | S/T | 0.678
68 | 86 | 392 | 57 | ∆T | 26.9
68 | 86 | 392 | 57 | LDB | 41.1
68 | 86 | 392 | 57 | LWB | 39.2
68 | 86 | 392 | 57 | kW | 1.41
72 | 86 | 392 | 61 | MBh | 18.49
72 | 86 | 392 | 61 | S/T | 0.633
72 | 86 | 392 | 61 | ∆T | 27.6
72 | 86 | 392 | 61 | LDB | 44.4
72 | 86 | 392 | 61 | LWB | 42.8
72 | 86 | 392 | 61 | kW | 1.53
77 | 86 | 392 | 64 | MBh | 19.37
77 | 86 | 392 | 64 | S/T | 0.623
77 | 86 | 392 | 64 | ∆T | 28.5
77 | 86 | 392 | 64 | LDB | 48.5
77 | 86 | 392 | 64 | LWB | 46.1
77 | 86 | 392 | 64 | kW | 1.53
80 | 86 | 392 | 67 | MBh | 19.99
80 | 86 | 392 | 67 | S/T | 0.603
80 | 86 | 392 | 67 | ∆T | 28.5
80 | 86 | 392 | 67 | LDB | 51.5
80 | 86 | 392 | 67 | LWB | 49.7
80 | 86 | 392 | 67 | kW | 1.54
86 | 86 | 392 | 72 | MBh | 21.13
86 | 86 | 392 | 72 | S/T | 0.57
86 | 86 | 392 | 72 | ∆T | 28.4
86 | 86 | 392 | 72 | LDB | 57.6
86 | 86 | 392 | 72 | LWB | 55.8
86 | 86 | 392 | 72 | kW | 1.55
90 | 86 | 392 | 75 | MBh | 22.01
90 | 86 | 392 | 75 | S/T | 0.531
90 | 86 | 392 | 75 | ∆T | 27.6
90 | 86 | 392 | 75 | LDB | 62.4
90 | 86 | 392 | 75 | LWB | 59.3
90 | 86 | 392 | 75 | kW | 1.56
68 | 95 | 392 | 57 | MBh | 16.72
68 | 95 | 392 | 57 | S/T | 0.678
68 | 95 | 392 | 57 | ∆T | 26.8
68 | 95 | 392 | 57 | LDB | 41.2
68 | 95 | 392 | 57 | LWB | 39.3
68 | 95 | 392 | 57 | kW | 1.64
72 | 95 | 392 | 61 | MBh | 17.6
72 | 95 | 392 | 61 | S/T | 0.637
72 | 95 | 392 | 61 | ∆T | 26.5
72 | 95 | 392 | 61 | LDB | 45.5
72 | 95 | 392 | 61 | LWB | 43.9
72 | 95 | 392 | 61 | kW | 1.65
77 | 95 | 392 | 64 | MBh | 18.48
77 | 95 | 392 | 64 | S/T | 0.628
77 | 95 | 392 | 64 | ∆T | 27.4
77 | 95 | 392 | 64 | LDB | 49.6
77 | 95 | 392 | 64 | LWB | 47.1
77 | 95 | 392 | 64 | kW | 1.66
80 | 95 | 392 | 67 | MBh | 19.1
80 | 95 | 392 | 67 | S/T | 0.608
80 | 95 | 392 | 67 | ∆T | 27.4
80 | 95 | 392 | 67 | LDB | 52.6
80 | 95 | 392 | 67 | LWB | 50.7
80 | 95 | 392 | 67 | kW | 1.66
86 | 95 | 392 | 72 | MBh | 20.24
86 | 95 | 392 | 72 | S/T | 0.575
86 | 95 | 392 | 72 | ∆T | 27.5
86 | 95 | 392 | 72 | LDB | 58.5
86 | 95 | 392 | 72 | LWB | 56.6
86 | 95 | 392 | 72 | kW | 1.67
90 | 95 | 392 | 75 | MBh | 21.12
90 | 95 | 392 | 75 | S/T | 0.536
90 | 95 | 392 | 75 | ∆T | 26.7
90 | 95 | 392 | 75 | LDB | 63.3
90 | 95 | 392 | 75 | LWB | 60
90 | 95 | 392 | 75 | kW | 1.68
68 | 104 | 392 | 57 | MBh | 15.84
68 | 104 | 392 | 57 | S/T | 0.684
68 | 104 | 392 | 57 | ∆T | 25.6
68 | 104 | 392 | 57 | LDB | 42.4
68 | 104 | 392 | 57 | LWB | 40.4
68 | 104 | 392 | 57 | kW | 1.76
72 | 104 | 392 | 61 | MBh | 16.72
72 | 104 | 392 | 61 | S/T | 0.642
72 | 104 | 392 | 61 | ∆T | 25.3
72 | 104 | 392 | 61 | LDB | 46.7
72 | 104 | 392 | 61 | LWB | 44.9
72 | 104 | 392 | 61 | kW | 1.77
77 | 104 | 392 | 64 | MBh | 17.6
77 | 104 | 392 | 64 | S/T | 0.634
77 | 104 | 392 | 64 | ∆T | 26.3
77 | 104 | 392 | 64 | LDB | 50.7
77 | 104 | 392 | 64 | LWB | 48
77 | 104 | 392 | 64 | kW | 1.78
80 | 104 | 392 | 67 | MBh | 18.21
80 | 104 | 392 | 67 | S/T | 0.614
80 | 104 | 392 | 67 | ∆T | 26.4
80 | 104 | 392 | 67 | LDB | 53.6
80 | 104 | 392 | 67 | LWB | 51.5
80 | 104 | 392 | 67 | kW | 1.78
86 | 104 | 392 | 72 | MBh | 19.35
86 | 104 | 392 | 72 | S/T | 0.581
86 | 104 | 392 | 72 | ∆T | 26.6
86 | 104 | 392 | 72 | LDB | 59.4
86 | 104 | 392 | 72 | LWB | 57.4
86 | 104 | 392 | 72 | kW | 1.79
90 | 104 | 392 | 75 | MBh | 20.23
90 | 104 | 392 | 75 | S/T | 0.541
90 | 104 | 392 | 75 | ∆T | 25.9
90 | 104 | 392 | 75 | LDB | 64.1
90 | 104 | 392 | 75 | LWB | 60.7
90 | 104 | 392 | 75 | kW | 1.8
68 | 115 | 392 | 57 | MBh | 14.77
68 | 115 | 392 | 57 | S/T | 0.693
68 | 115 | 392 | 57 | ∆T | 24.2
68 | 115 | 392 | 57 | LDB | 43.8
68 | 115 | 392 | 57 | LWB | 41.7
68 | 115 | 392 | 57 | kW | 1.91
72 | 115 | 392 | 61 | MBh | 15.65
72 | 115 | 392 | 61 | S/T | 0.65
72 | 115 | 392 | 61 | ∆T | 24
72 | 115 | 392 | 61 | LDB | 48
72 | 115 | 392 | 61 | LWB | 46.1
72 | 115 | 392 | 61 | kW | 1.92
77 | 115 | 392 | 64 | MBh | 16.53
77 | 115 | 392 | 64 | S/T | 0.642
77 | 115 | 392 | 64 | ∆T | 25.1
77 | 115 | 392 | 64 | LDB | 51.9
77 | 115 | 392 | 64 | LWB | 49.1
77 | 115 | 392 | 64 | kW | 1.93
80 | 115 | 392 | 67 | MBh | 17.14
80 | 115 | 392 | 67 | S/T | 0.623
80 | 115 | 392 | 67 | ∆T | 25.2
80 | 115 | 392 | 67 | LDB | 54.8
80 | 115 | 392 | 67 | LWB | 52.6
80 | 115 | 392 | 67 | kW | 1.93
86 | 115 | 392 | 72 | MBh | 18.29
86 | 115 | 392 | 72 | S/T | 0.59
86 | 115 | 392 | 72 | ∆T | 25.5
86 | 115 | 392 | 72 | LDB | 60.5
86 | 115 | 392 | 72 | LWB | 58.3
86 | 115 | 392 | 72 | kW | 1.94
90 | 115 | 392 | 75 | MBh | 19.17
90 | 115 | 392 | 75 | S/T | 0.549
90 | 115 | 392 | 75 | ∆T | 24.9
90 | 115 | 392 | 75 | LDB | 65.1
90 | 115 | 392 | 75 | LWB | 61.6
90 | 115 | 392 | 75 | kW | 1.95

## RXP15AVJU9 - FVXV15AVJUT9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 392 | 57 | MBh | 16.82 | 75 | 60 | 59 | 25.48 | 2.04
68 | 50 | 392 | 57 | S/T | 0.678 | 75 | 60 | 70 | 24.66 | 2.06
68 | 50 | 392 | 57 | ∆T | 26.9 | 75 | 60 | 72 | 23.25 | 1.91
68 | 50 | 392 | 57 | LDB | 41.1 | 75 | 60 | 75 | 21.84 | 1.77
68 | 50 | 392 | 57 | LWB | 39.2 | 75 | 60 | 77 | 21.14 | 1.7
68 | 50 | 392 | 57 | kW | 0.75 | 75 | 60 | 81 | 19.73 | 1.56
72 | 50 | 392 | 61 | MBh | 19.97 | 47 | 43 | 59 | 21.1 | 1.89
72 | 50 | 392 | 61 | S/T | 0.628 | 47 | 43 | 70 | 20.4 | 1.93
72 | 50 | 392 | 61 | ∆T | 29.6 | 47 | 43 | 72 | 20.12 | 1.95
72 | 50 | 392 | 61 | LDB | 42.4 | 47 | 43 | 75 | 19.84 | 1.96
72 | 50 | 392 | 61 | LWB | 41.1 | 47 | 43 | 77 | 19.7 | 1.97
72 | 50 | 392 | 61 | kW | 0.9 | 47 | 43 | 81 | 19.41 | 1.99
77 | 50 | 392 | 64 | MBh | 22.93 | 35 | 32 | 59 | 20.5 | 2.16
77 | 50 | 392 | 64 | S/T | 0.611 | 35 | 32 | 70 | 19.71 | 2.22
77 | 50 | 392 | 64 | ∆T | 33.1 | 35 | 32 | 72 | 19.4 | 2.24
77 | 50 | 392 | 64 | LDB | 43.9 | 35 | 32 | 75 | 19.08 | 2.26
77 | 50 | 392 | 64 | LWB | 42 | 35 | 32 | 77 | 18.93 | 2.27
77 | 50 | 392 | 64 | kW | 1.04 | 35 | 32 | 81 | 18.61 | 2.29
80 | 50 | 392 | 67 | MBh | 23.55 | 25 | 23 | 59 | 20.02 | 2.39
80 | 50 | 392 | 67 | S/T | 0.59 | 25 | 23 | 70 | 19.14 | 2.45
80 | 50 | 392 | 67 | ∆T | 32.8 | 25 | 23 | 72 | 18.79 | 2.48
80 | 50 | 392 | 67 | LDB | 47.2 | 25 | 23 | 75 | 18.44 | 2.5
80 | 50 | 392 | 67 | LWB | 45.9 | 25 | 23 | 77 | 18.26 | 2.51
80 | 50 | 392 | 67 | kW | 1.05 | 25 | 23 | 81 | 17.91 | 2.54
86 | 50 | 392 | 72 | MBh | 24.69 | 16 | 14 | 59 | 19.58 | 2.62
86 | 50 | 392 | 72 | S/T | 0.556 | 16 | 14 | 70 | 18.57 | 2.69
86 | 50 | 392 | 72 | ∆T | 32.4 | 16 | 14 | 72 | 18.17 | 2.72
86 | 50 | 392 | 72 | LDB | 53.6 | 16 | 14 | 75 | 17.77 | 2.75
86 | 50 | 392 | 72 | LWB | 52.4 | 16 | 14 | 77 | 17.57 | 2.76
86 | 50 | 392 | 72 | kW | 1.06 | 16 | 14 | 81 | 17.17 | 2.79
90 | 50 | 392 | 75 | MBh | 25.57 | 5 | 5 | 59 | 19.18 | 2.85
90 | 50 | 392 | 75 | S/T | 0.517 | 5 | 5 | 70 | 18 | 2.93
90 | 50 | 392 | 75 | ∆T | 31.2 | 5 | 5 | 72 | 17.21 | 2.85
90 | 50 | 392 | 75 | LDB | 58.8 | 5 | 5 | 75 | 15.8 | 2.56
90 | 50 | 392 | 75 | LWB | 56.1 | 5 | 5 | 77 | 15.1 | 2.42
90 | 50 | 392 | 75 | kW | 1.06 | 5 | 5 | 81 | 13.69 | 2.15
68 | 68 | 392 | 57 | MBh | 16.82 | -4 | -4 | 59 | 16.58 | 2.56
68 | 68 | 392 | 57 | S/T | 0.678 | -4 | -4 | 70 | 15.3 | 2.64
68 | 68 | 392 | 57 | ∆T | 26.9 | -4 | -4 | 72 | 14.68 | 2.63
68 | 68 | 392 | 57 | LDB | 41.1 | -4 | -4 | 75 | 13.27 | 2.34
68 | 68 | 392 | 57 | LWB | 39.2 | -4 | -4 | 77 | 12.57 | 2.2
68 | 68 | 392 | 57 | kW | 1.03 | -4 | -4 | 81 | 11.16 | 1.92
72 | 68 | 392 | 61 | MBh | 19.97 | -13 | -14 | 59 | 14.05 | 2.27
72 | 68 | 392 | 61 | S/T | 0.628 | -13 | -14 | 70 | 12.6 | 2.34
72 | 68 | 392 | 61 | ∆T | 29.6 | -13 | -14 | 72 | 12.02 | 2.37
72 | 68 | 392 | 61 | LDB | 42.4 | -13 | -14 | 75 | 11.36 | 2.37
72 | 68 | 392 | 61 | LWB | 41.1 | -13 | -14 | 77 | 10.66 | 2.22
72 | 68 | 392 | 61 | kW | 1.25 | -13 | -14 | 81 | 9.25 | 1.92
77 | 68 | 392 | 64 | MBh | 21.15
77 | 68 | 392 | 64 | S/T | 0.615
77 | 68 | 392 | 64 | ∆T | 30.7
77 | 68 | 392 | 64 | LDB | 46.3
77 | 68 | 392 | 64 | LWB | 44.1
77 | 68 | 392 | 64 | kW | 1.29
80 | 68 | 392 | 67 | MBh | 21.77
80 | 68 | 392 | 67 | S/T | 0.595
80 | 68 | 392 | 67 | ∆T | 30.6
80 | 68 | 392 | 67 | LDB | 49.4
80 | 68 | 392 | 67 | LWB | 47.9
80 | 68 | 392 | 67 | kW | 1.29
86 | 68 | 392 | 72 | MBh | 22.91
86 | 68 | 392 | 72 | S/T | 0.561
86 | 68 | 392 | 72 | ∆T | 30.4
86 | 68 | 392 | 72 | LDB | 55.6
86 | 68 | 392 | 72 | LWB | 54.1
86 | 68 | 392 | 72 | kW | 1.3
90 | 68 | 392 | 75 | MBh | 23.79
90 | 68 | 392 | 75 | S/T | 0.522
90 | 68 | 392 | 75 | ∆T | 29.4
90 | 68 | 392 | 75 | LDB | 60.6
90 | 68 | 392 | 75 | LWB | 57.7
90 | 68 | 392 | 75 | kW | 1.31
68 | 86 | 392 | 57 | MBh | 16.82
68 | 86 | 392 | 57 | S/T | 0.678
68 | 86 | 392 | 57 | ∆T | 26.9
68 | 86 | 392 | 57 | LDB | 41.1
68 | 86 | 392 | 57 | LWB | 39.2
68 | 86 | 392 | 57 | kW | 1.41
72 | 86 | 392 | 61 | MBh | 18.49
72 | 86 | 392 | 61 | S/T | 0.633
72 | 86 | 392 | 61 | ∆T | 27.6
72 | 86 | 392 | 61 | LDB | 44.4
72 | 86 | 392 | 61 | LWB | 42.8
72 | 86 | 392 | 61 | kW | 1.53
77 | 86 | 392 | 64 | MBh | 19.37
77 | 86 | 392 | 64 | S/T | 0.623
77 | 86 | 392 | 64 | ∆T | 28.5
77 | 86 | 392 | 64 | LDB | 48.5
77 | 86 | 392 | 64 | LWB | 46.1
77 | 86 | 392 | 64 | kW | 1.53
80 | 86 | 392 | 67 | MBh | 19.99
80 | 86 | 392 | 67 | S/T | 0.603
80 | 86 | 392 | 67 | ∆T | 28.5
80 | 86 | 392 | 67 | LDB | 51.5
80 | 86 | 392 | 67 | LWB | 49.7
80 | 86 | 392 | 67 | kW | 1.54
86 | 86 | 392 | 72 | MBh | 21.13
86 | 86 | 392 | 72 | S/T | 0.57
86 | 86 | 392 | 72 | ∆T | 28.4
86 | 86 | 392 | 72 | LDB | 57.6
86 | 86 | 392 | 72 | LWB | 55.8
86 | 86 | 392 | 72 | kW | 1.55
90 | 86 | 392 | 75 | MBh | 22.01
90 | 86 | 392 | 75 | S/T | 0.531
90 | 86 | 392 | 75 | ∆T | 27.6
90 | 86 | 392 | 75 | LDB | 62.4
90 | 86 | 392 | 75 | LWB | 59.3
90 | 86 | 392 | 75 | kW | 1.56
68 | 95 | 392 | 57 | MBh | 16.72
68 | 95 | 392 | 57 | S/T | 0.678
68 | 95 | 392 | 57 | ∆T | 26.8
68 | 95 | 392 | 57 | LDB | 41.2
68 | 95 | 392 | 57 | LWB | 39.3
68 | 95 | 392 | 57 | kW | 1.64
72 | 95 | 392 | 61 | MBh | 17.6
72 | 95 | 392 | 61 | S/T | 0.637
72 | 95 | 392 | 61 | ∆T | 26.5
72 | 95 | 392 | 61 | LDB | 45.5
72 | 95 | 392 | 61 | LWB | 43.9
72 | 95 | 392 | 61 | kW | 1.65
77 | 95 | 392 | 64 | MBh | 18.48
77 | 95 | 392 | 64 | S/T | 0.628
77 | 95 | 392 | 64 | ∆T | 27.4
77 | 95 | 392 | 64 | LDB | 49.6
77 | 95 | 392 | 64 | LWB | 47.1
77 | 95 | 392 | 64 | kW | 1.66
80 | 95 | 392 | 67 | MBh | 19.1
80 | 95 | 392 | 67 | S/T | 0.608
80 | 95 | 392 | 67 | ∆T | 27.4
80 | 95 | 392 | 67 | LDB | 52.6
80 | 95 | 392 | 67 | LWB | 50.7
80 | 95 | 392 | 67 | kW | 1.66
86 | 95 | 392 | 72 | MBh | 20.24
86 | 95 | 392 | 72 | S/T | 0.575
86 | 95 | 392 | 72 | ∆T | 27.5
86 | 95 | 392 | 72 | LDB | 58.5
86 | 95 | 392 | 72 | LWB | 56.6
86 | 95 | 392 | 72 | kW | 1.67
90 | 95 | 392 | 75 | MBh | 21.12
90 | 95 | 392 | 75 | S/T | 0.536
90 | 95 | 392 | 75 | ∆T | 26.7
90 | 95 | 392 | 75 | LDB | 63.3
90 | 95 | 392 | 75 | LWB | 60
90 | 95 | 392 | 75 | kW | 1.68
68 | 104 | 392 | 57 | MBh | 15.84
68 | 104 | 392 | 57 | S/T | 0.684
68 | 104 | 392 | 57 | ∆T | 25.6
68 | 104 | 392 | 57 | LDB | 42.4
68 | 104 | 392 | 57 | LWB | 40.4
68 | 104 | 392 | 57 | kW | 1.76
72 | 104 | 392 | 61 | MBh | 16.72
72 | 104 | 392 | 61 | S/T | 0.642
72 | 104 | 392 | 61 | ∆T | 25.3
72 | 104 | 392 | 61 | LDB | 46.7
72 | 104 | 392 | 61 | LWB | 44.9
72 | 104 | 392 | 61 | kW | 1.77
77 | 104 | 392 | 64 | MBh | 17.6
77 | 104 | 392 | 64 | S/T | 0.634
77 | 104 | 392 | 64 | ∆T | 26.3
77 | 104 | 392 | 64 | LDB | 50.7
77 | 104 | 392 | 64 | LWB | 48
77 | 104 | 392 | 64 | kW | 1.78
80 | 104 | 392 | 67 | MBh | 18.21
80 | 104 | 392 | 67 | S/T | 0.614
80 | 104 | 392 | 67 | ∆T | 26.4
80 | 104 | 392 | 67 | LDB | 53.6
80 | 104 | 392 | 67 | LWB | 51.5
80 | 104 | 392 | 67 | kW | 1.78
86 | 104 | 392 | 72 | MBh | 19.35
86 | 104 | 392 | 72 | S/T | 0.581
86 | 104 | 392 | 72 | ∆T | 26.6
86 | 104 | 392 | 72 | LDB | 59.4
86 | 104 | 392 | 72 | LWB | 57.4
86 | 104 | 392 | 72 | kW | 1.79
90 | 104 | 392 | 75 | MBh | 20.23
90 | 104 | 392 | 75 | S/T | 0.541
90 | 104 | 392 | 75 | ∆T | 25.9
90 | 104 | 392 | 75 | LDB | 64.1
90 | 104 | 392 | 75 | LWB | 60.7
90 | 104 | 392 | 75 | kW | 1.8
68 | 115 | 392 | 57 | MBh | 14.77
68 | 115 | 392 | 57 | S/T | 0.693
68 | 115 | 392 | 57 | ∆T | 24.2
68 | 115 | 392 | 57 | LDB | 43.8
68 | 115 | 392 | 57 | LWB | 41.7
68 | 115 | 392 | 57 | kW | 1.91
72 | 115 | 392 | 61 | MBh | 15.65
72 | 115 | 392 | 61 | S/T | 0.65
72 | 115 | 392 | 61 | ∆T | 24
72 | 115 | 392 | 61 | LDB | 48
72 | 115 | 392 | 61 | LWB | 46.1
72 | 115 | 392 | 61 | kW | 1.92
77 | 115 | 392 | 64 | MBh | 16.53
77 | 115 | 392 | 64 | S/T | 0.642
77 | 115 | 392 | 64 | ∆T | 25.1
77 | 115 | 392 | 64 | LDB | 51.9
77 | 115 | 392 | 64 | LWB | 49.1
77 | 115 | 392 | 64 | kW | 1.93
80 | 115 | 392 | 67 | MBh | 17.14
80 | 115 | 392 | 67 | S/T | 0.623
80 | 115 | 392 | 67 | ∆T | 25.2
80 | 115 | 392 | 67 | LDB | 54.8
80 | 115 | 392 | 67 | LWB | 52.6
80 | 115 | 392 | 67 | kW | 1.93
86 | 115 | 392 | 72 | MBh | 18.29
86 | 115 | 392 | 72 | S/T | 0.59
86 | 115 | 392 | 72 | ∆T | 25.5
86 | 115 | 392 | 72 | LDB | 60.5
86 | 115 | 392 | 72 | LWB | 58.3
86 | 115 | 392 | 72 | kW | 1.94
90 | 115 | 392 | 75 | MBh | 19.17
90 | 115 | 392 | 75 | S/T | 0.549
90 | 115 | 392 | 75 | ∆T | 24.9
90 | 115 | 392 | 75 | LDB | 65.1
90 | 115 | 392 | 75 | LWB | 61.6
90 | 115 | 392 | 75 | kW | 1.95

## RXP18AVJU9 - FVXV18AVJUW9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 448 | 57 | MBh | 18.82 | 75 | 60 | 59 | 27.23 | 1.99
68 | 50 | 448 | 57 | S/T | 0.677 | 75 | 60 | 70 | 26.4 | 2.02
68 | 50 | 448 | 57 | ∆T | 26.4 | 75 | 60 | 72 | 24.89 | 1.91
68 | 50 | 448 | 57 | LDB | 41.6 | 75 | 60 | 75 | 23.39 | 1.79
68 | 50 | 448 | 57 | LWB | 39.6 | 75 | 60 | 77 | 22.63 | 1.74
68 | 50 | 448 | 57 | kW | 0.83 | 75 | 60 | 81 | 21.12 | 1.62
72 | 50 | 448 | 61 | MBh | 22.34 | 47 | 43 | 59 | 22.55 | 1.84
72 | 50 | 448 | 61 | S/T | 0.628 | 47 | 43 | 70 | 21.8 | 1.89
72 | 50 | 448 | 61 | ∆T | 29 | 47 | 43 | 72 | 21.5 | 1.9
72 | 50 | 448 | 61 | LDB | 43 | 47 | 43 | 75 | 21.2 | 1.92
72 | 50 | 448 | 61 | LWB | 41.6 | 47 | 43 | 77 | 21.05 | 1.93
72 | 50 | 448 | 61 | kW | 1.03 | 47 | 43 | 81 | 20.75 | 1.94
77 | 50 | 448 | 64 | MBh | 25.69 | 35 | 32 | 59 | 21.54 | 2.13
77 | 50 | 448 | 64 | S/T | 0.611 | 35 | 32 | 70 | 20.71 | 2.18
77 | 50 | 448 | 64 | ∆T | 32.4 | 35 | 32 | 72 | 20.38 | 2.2
77 | 50 | 448 | 64 | LDB | 44.6 | 35 | 32 | 75 | 20.05 | 2.23
77 | 50 | 448 | 64 | LWB | 42.6 | 35 | 32 | 77 | 19.89 | 2.24
77 | 50 | 448 | 64 | kW | 1.23 | 35 | 32 | 81 | 19.56 | 2.26
80 | 50 | 448 | 67 | MBh | 26.38 | 25 | 23 | 59 | 20.72 | 2.37
80 | 50 | 448 | 67 | S/T | 0.59 | 25 | 23 | 70 | 19.81 | 2.43
80 | 50 | 448 | 67 | ∆T | 32.2 | 25 | 23 | 72 | 19.45 | 2.46
80 | 50 | 448 | 67 | LDB | 47.8 | 25 | 23 | 75 | 19.08 | 2.48
80 | 50 | 448 | 67 | LWB | 46.5 | 25 | 23 | 77 | 18.9 | 2.49
80 | 50 | 448 | 67 | kW | 1.24 | 25 | 23 | 81 | 18.54 | 2.52
86 | 50 | 448 | 72 | MBh | 27.66 | 16 | 14 | 59 | 19.93 | 2.61
86 | 50 | 448 | 72 | S/T | 0.556 | 16 | 14 | 70 | 18.9 | 2.68
86 | 50 | 448 | 72 | ∆T | 31.8 | 16 | 14 | 72 | 18.5 | 2.71
86 | 50 | 448 | 72 | LDB | 54.2 | 16 | 14 | 75 | 18.09 | 2.74
86 | 50 | 448 | 72 | LWB | 52.9 | 16 | 14 | 77 | 17.88 | 2.75
86 | 50 | 448 | 72 | kW | 1.25 | 16 | 14 | 81 | 17.47 | 2.78
90 | 50 | 448 | 75 | MBh | 28.65 | 5 | 5 | 59 | 19.18 | 2.85
90 | 50 | 448 | 75 | S/T | 0.517 | 5 | 5 | 70 | 18 | 2.93
90 | 50 | 448 | 75 | ∆T | 30.6 | 5 | 5 | 72 | 17.53 | 2.96
90 | 50 | 448 | 75 | LDB | 59.4 | 5 | 5 | 75 | 16.92 | 2.96
90 | 50 | 448 | 75 | LWB | 56.6 | 5 | 5 | 77 | 16.17 | 2.83
90 | 50 | 448 | 75 | kW | 1.26 | 5 | 5 | 81 | 14.66 | 2.56
68 | 68 | 448 | 57 | MBh | 18.82 | -4 | -4 | 59 | 16.58 | 2.56
68 | 68 | 448 | 57 | S/T | 0.677 | -4 | -4 | 70 | 15.3 | 2.64
68 | 68 | 448 | 57 | ∆T | 26.4 | -4 | -4 | 72 | 14.79 | 2.67
68 | 68 | 448 | 57 | LDB | 41.6 | -4 | -4 | 75 | 14.21 | 2.68
68 | 68 | 448 | 57 | LWB | 39.6 | -4 | -4 | 77 | 13.45 | 2.55
68 | 68 | 448 | 57 | kW | 1.16 | -4 | -4 | 81 | 11.94 | 2.28
72 | 68 | 448 | 61 | MBh | 22.34 | -13 | -14 | 59 | 14.05 | 2.27
72 | 68 | 448 | 61 | S/T | 0.628 | -13 | -14 | 70 | 12.6 | 2.34
72 | 68 | 448 | 61 | ∆T | 29 | -13 | -14 | 72 | 12.02 | 2.37
72 | 68 | 448 | 61 | LDB | 43 | -13 | -14 | 75 | 11.44 | 2.4
72 | 68 | 448 | 61 | LWB | 41.6 | -13 | -14 | 77 | 11.15 | 2.42
72 | 68 | 448 | 61 | kW | 1.47 | -13 | -14 | 81 | 9.9 | 2.22
77 | 68 | 448 | 64 | MBh | 23.7
77 | 68 | 448 | 64 | S/T | 0.615
77 | 68 | 448 | 64 | ∆T | 30.1
77 | 68 | 448 | 64 | LDB | 46.9
77 | 68 | 448 | 64 | LWB | 44.6
77 | 68 | 448 | 64 | kW | 1.52
80 | 68 | 448 | 67 | MBh | 24.39
80 | 68 | 448 | 67 | S/T | 0.595
80 | 68 | 448 | 67 | ∆T | 30
80 | 68 | 448 | 67 | LDB | 50
80 | 68 | 448 | 67 | LWB | 48.3
80 | 68 | 448 | 67 | kW | 1.53
86 | 68 | 448 | 72 | MBh | 25.67
86 | 68 | 448 | 72 | S/T | 0.561
86 | 68 | 448 | 72 | ∆T | 29.8
86 | 68 | 448 | 72 | LDB | 56.2
86 | 68 | 448 | 72 | LWB | 54.5
86 | 68 | 448 | 72 | kW | 1.54
90 | 68 | 448 | 75 | MBh | 26.66
90 | 68 | 448 | 75 | S/T | 0.522
90 | 68 | 448 | 75 | ∆T | 28.8
90 | 68 | 448 | 75 | LDB | 61.2
90 | 68 | 448 | 75 | LWB | 58.1
90 | 68 | 448 | 75 | kW | 1.55
68 | 86 | 448 | 57 | MBh | 18.82
68 | 86 | 448 | 57 | S/T | 0.677
68 | 86 | 448 | 57 | ∆T | 26.4
68 | 86 | 448 | 57 | LDB | 41.6
68 | 86 | 448 | 57 | LWB | 39.6
68 | 86 | 448 | 57 | kW | 1.63
72 | 86 | 448 | 61 | MBh | 20.72
72 | 86 | 448 | 61 | S/T | 0.633
72 | 86 | 448 | 61 | ∆T | 27.1
72 | 86 | 448 | 61 | LDB | 44.9
72 | 86 | 448 | 61 | LWB | 43.3
72 | 86 | 448 | 61 | kW | 1.81
77 | 86 | 448 | 64 | MBh | 21.71
77 | 86 | 448 | 64 | S/T | 0.622
77 | 86 | 448 | 64 | ∆T | 27.9
77 | 86 | 448 | 64 | LDB | 49.1
77 | 86 | 448 | 64 | LWB | 46.5
77 | 86 | 448 | 64 | kW | 1.81
80 | 86 | 448 | 67 | MBh | 22.4
80 | 86 | 448 | 67 | S/T | 0.602
80 | 86 | 448 | 67 | ∆T | 27.9
80 | 86 | 448 | 67 | LDB | 52.1
80 | 86 | 448 | 67 | LWB | 50.1
80 | 86 | 448 | 67 | kW | 1.82
86 | 86 | 448 | 72 | MBh | 23.68
86 | 86 | 448 | 72 | S/T | 0.569
86 | 86 | 448 | 72 | ∆T | 27.9
86 | 86 | 448 | 72 | LDB | 58.1
86 | 86 | 448 | 72 | LWB | 56.1
86 | 86 | 448 | 72 | kW | 1.83
90 | 86 | 448 | 75 | MBh | 24.66
90 | 86 | 448 | 75 | S/T | 0.53
90 | 86 | 448 | 75 | ∆T | 27
90 | 86 | 448 | 75 | LDB | 63
90 | 86 | 448 | 75 | LWB | 59.6
90 | 86 | 448 | 75 | kW | 1.84
68 | 95 | 448 | 57 | MBh | 18.74
68 | 95 | 448 | 57 | S/T | 0.678
68 | 95 | 448 | 57 | ∆T | 26.2
68 | 95 | 448 | 57 | LDB | 41.8
68 | 95 | 448 | 57 | LWB | 39.7
68 | 95 | 448 | 57 | kW | 1.94
72 | 95 | 448 | 61 | MBh | 19.72
72 | 95 | 448 | 61 | S/T | 0.637
72 | 95 | 448 | 61 | ∆T | 26
72 | 95 | 448 | 61 | LDB | 46
72 | 95 | 448 | 61 | LWB | 44.3
72 | 95 | 448 | 61 | kW | 1.95
77 | 95 | 448 | 64 | MBh | 20.71
77 | 95 | 448 | 64 | S/T | 0.627
77 | 95 | 448 | 64 | ∆T | 26.8
77 | 95 | 448 | 64 | LDB | 50.2
77 | 95 | 448 | 64 | LWB | 47.5
77 | 95 | 448 | 64 | kW | 1.96
80 | 95 | 448 | 67 | MBh | 21.4
80 | 95 | 448 | 67 | S/T | 0.607
80 | 95 | 448 | 67 | ∆T | 26.9
80 | 95 | 448 | 67 | LDB | 53.1
80 | 95 | 448 | 67 | LWB | 51
80 | 95 | 448 | 67 | kW | 1.97
86 | 95 | 448 | 72 | MBh | 22.68
86 | 95 | 448 | 72 | S/T | 0.575
86 | 95 | 448 | 72 | ∆T | 27
86 | 95 | 448 | 72 | LDB | 59
86 | 95 | 448 | 72 | LWB | 56.9
86 | 95 | 448 | 72 | kW | 1.98
90 | 95 | 448 | 75 | MBh | 23.67
90 | 95 | 448 | 75 | S/T | 0.535
90 | 95 | 448 | 75 | ∆T | 26.2
90 | 95 | 448 | 75 | LDB | 63.8
90 | 95 | 448 | 75 | LWB | 60.4
90 | 95 | 448 | 75 | kW | 1.99
68 | 104 | 448 | 57 | MBh | 17.74
68 | 104 | 448 | 57 | S/T | 0.684
68 | 104 | 448 | 57 | ∆T | 25.1
68 | 104 | 448 | 57 | LDB | 42.9
68 | 104 | 448 | 57 | LWB | 40.8
68 | 104 | 448 | 57 | kW | 2.09
72 | 104 | 448 | 61 | MBh | 18.73
72 | 104 | 448 | 61 | S/T | 0.642
72 | 104 | 448 | 61 | ∆T | 24.8
72 | 104 | 448 | 61 | LDB | 47.2
72 | 104 | 448 | 61 | LWB | 45.2
72 | 104 | 448 | 61 | kW | 2.1
77 | 104 | 448 | 64 | MBh | 19.71
77 | 104 | 448 | 64 | S/T | 0.634
77 | 104 | 448 | 64 | ∆T | 25.8
77 | 104 | 448 | 64 | LDB | 51.2
77 | 104 | 448 | 64 | LWB | 48.4
77 | 104 | 448 | 64 | kW | 2.11
80 | 104 | 448 | 67 | MBh | 20.4
80 | 104 | 448 | 67 | S/T | 0.614
80 | 104 | 448 | 67 | ∆T | 25.9
80 | 104 | 448 | 67 | LDB | 54.1
80 | 104 | 448 | 67 | LWB | 51.9
80 | 104 | 448 | 67 | kW | 2.11
86 | 104 | 448 | 72 | MBh | 21.69
86 | 104 | 448 | 72 | S/T | 0.581
86 | 104 | 448 | 72 | ∆T | 26
86 | 104 | 448 | 72 | LDB | 60
86 | 104 | 448 | 72 | LWB | 57.7
86 | 104 | 448 | 72 | kW | 2.12
90 | 104 | 448 | 75 | MBh | 22.67
90 | 104 | 448 | 75 | S/T | 0.541
90 | 104 | 448 | 75 | ∆T | 25.4
90 | 104 | 448 | 75 | LDB | 64.6
90 | 104 | 448 | 75 | LWB | 61.1
90 | 104 | 448 | 75 | kW | 2.13
68 | 115 | 448 | 57 | MBh | 16.55
68 | 115 | 448 | 57 | S/T | 0.693
68 | 115 | 448 | 57 | ∆T | 23.7
68 | 115 | 448 | 57 | LDB | 44.3
68 | 115 | 448 | 57 | LWB | 42
68 | 115 | 448 | 57 | kW | 2.26
72 | 115 | 448 | 61 | MBh | 17.53
72 | 115 | 448 | 61 | S/T | 0.65
72 | 115 | 448 | 61 | ∆T | 23.5
72 | 115 | 448 | 61 | LDB | 48.5
72 | 115 | 448 | 61 | LWB | 46.4
72 | 115 | 448 | 61 | kW | 2.27
77 | 115 | 448 | 64 | MBh | 18.52
77 | 115 | 448 | 64 | S/T | 0.643
77 | 115 | 448 | 64 | ∆T | 24.6
77 | 115 | 448 | 64 | LDB | 52.4
77 | 115 | 448 | 64 | LWB | 49.5
77 | 115 | 448 | 64 | kW | 2.28
80 | 115 | 448 | 67 | MBh | 19.21
80 | 115 | 448 | 67 | S/T | 0.623
80 | 115 | 448 | 67 | ∆T | 24.7
80 | 115 | 448 | 67 | LDB | 55.3
80 | 115 | 448 | 67 | LWB | 52.9
80 | 115 | 448 | 67 | kW | 2.29
86 | 115 | 448 | 72 | MBh | 20.49
86 | 115 | 448 | 72 | S/T | 0.59
86 | 115 | 448 | 72 | ∆T | 25
86 | 115 | 448 | 72 | LDB | 61
86 | 115 | 448 | 72 | LWB | 58.6
86 | 115 | 448 | 72 | kW | 2.3
90 | 115 | 448 | 75 | MBh | 21.48
90 | 115 | 448 | 75 | S/T | 0.549
90 | 115 | 448 | 75 | ∆T | 24.4
90 | 115 | 448 | 75 | LDB | 65.6
90 | 115 | 448 | 75 | LWB | 61.9
90 | 115 | 448 | 75 | kW | 2.31

## RXP18AVJU9 - FVXV18AVJUT9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 448 | 57 | MBh | 18.82 | 75 | 60 | 59 | 27.23 | 1.99
68 | 50 | 448 | 57 | S/T | 0.677 | 75 | 60 | 70 | 26.4 | 2.02
68 | 50 | 448 | 57 | ∆T | 26.4 | 75 | 60 | 72 | 24.89 | 1.91
68 | 50 | 448 | 57 | LDB | 41.6 | 75 | 60 | 75 | 23.39 | 1.79
68 | 50 | 448 | 57 | LWB | 39.6 | 75 | 60 | 77 | 22.63 | 1.74
68 | 50 | 448 | 57 | kW | 0.83 | 75 | 60 | 81 | 21.12 | 1.62
72 | 50 | 448 | 61 | MBh | 22.34 | 47 | 43 | 59 | 22.55 | 1.84
72 | 50 | 448 | 61 | S/T | 0.628 | 47 | 43 | 70 | 21.8 | 1.89
72 | 50 | 448 | 61 | ∆T | 29 | 47 | 43 | 72 | 21.5 | 1.9
72 | 50 | 448 | 61 | LDB | 43 | 47 | 43 | 75 | 21.2 | 1.92
72 | 50 | 448 | 61 | LWB | 41.6 | 47 | 43 | 77 | 21.05 | 1.93
72 | 50 | 448 | 61 | kW | 1.03 | 47 | 43 | 81 | 20.75 | 1.94
77 | 50 | 448 | 64 | MBh | 25.69 | 35 | 32 | 59 | 21.54 | 2.13
77 | 50 | 448 | 64 | S/T | 0.611 | 35 | 32 | 70 | 20.71 | 2.18
77 | 50 | 448 | 64 | ∆T | 32.4 | 35 | 32 | 72 | 20.38 | 2.2
77 | 50 | 448 | 64 | LDB | 44.6 | 35 | 32 | 75 | 20.05 | 2.23
77 | 50 | 448 | 64 | LWB | 42.6 | 35 | 32 | 77 | 19.89 | 2.24
77 | 50 | 448 | 64 | kW | 1.23 | 35 | 32 | 81 | 19.56 | 2.26
80 | 50 | 448 | 67 | MBh | 26.38 | 25 | 23 | 59 | 20.72 | 2.37
80 | 50 | 448 | 67 | S/T | 0.59 | 25 | 23 | 70 | 19.81 | 2.43
80 | 50 | 448 | 67 | ∆T | 32.2 | 25 | 23 | 72 | 19.45 | 2.46
80 | 50 | 448 | 67 | LDB | 47.8 | 25 | 23 | 75 | 19.08 | 2.48
80 | 50 | 448 | 67 | LWB | 46.5 | 25 | 23 | 77 | 18.9 | 2.49
80 | 50 | 448 | 67 | kW | 1.24 | 25 | 23 | 81 | 18.54 | 2.52
86 | 50 | 448 | 72 | MBh | 27.66 | 16 | 14 | 59 | 19.93 | 2.61
86 | 50 | 448 | 72 | S/T | 0.556 | 16 | 14 | 70 | 18.9 | 2.68
86 | 50 | 448 | 72 | ∆T | 31.8 | 16 | 14 | 72 | 18.5 | 2.71
86 | 50 | 448 | 72 | LDB | 54.2 | 16 | 14 | 75 | 18.09 | 2.74
86 | 50 | 448 | 72 | LWB | 52.9 | 16 | 14 | 77 | 17.88 | 2.75
86 | 50 | 448 | 72 | kW | 1.25 | 16 | 14 | 81 | 17.47 | 2.78
90 | 50 | 448 | 75 | MBh | 28.65 | 5 | 5 | 59 | 19.18 | 2.85
90 | 50 | 448 | 75 | S/T | 0.517 | 5 | 5 | 70 | 18 | 2.93
90 | 50 | 448 | 75 | ∆T | 30.6 | 5 | 5 | 72 | 17.53 | 2.96
90 | 50 | 448 | 75 | LDB | 59.4 | 5 | 5 | 75 | 16.92 | 2.96
90 | 50 | 448 | 75 | LWB | 56.6 | 5 | 5 | 77 | 16.17 | 2.83
90 | 50 | 448 | 75 | kW | 1.26 | 5 | 5 | 81 | 14.66 | 2.56
68 | 68 | 448 | 57 | MBh | 18.82 | -4 | -4 | 59 | 16.58 | 2.56
68 | 68 | 448 | 57 | S/T | 0.677 | -4 | -4 | 70 | 15.3 | 2.64
68 | 68 | 448 | 57 | ∆T | 26.4 | -4 | -4 | 72 | 14.79 | 2.67
68 | 68 | 448 | 57 | LDB | 41.6 | -4 | -4 | 75 | 14.21 | 2.68
68 | 68 | 448 | 57 | LWB | 39.6 | -4 | -4 | 77 | 13.45 | 2.55
68 | 68 | 448 | 57 | kW | 1.16 | -4 | -4 | 81 | 11.94 | 2.28
72 | 68 | 448 | 61 | MBh | 22.34 | -13 | -14 | 59 | 14.05 | 2.27
72 | 68 | 448 | 61 | S/T | 0.628 | -13 | -14 | 70 | 12.6 | 2.34
72 | 68 | 448 | 61 | ∆T | 29 | -13 | -14 | 72 | 12.02 | 2.37
72 | 68 | 448 | 61 | LDB | 43 | -13 | -14 | 75 | 11.44 | 2.4
72 | 68 | 448 | 61 | LWB | 41.6 | -13 | -14 | 77 | 11.15 | 2.42
72 | 68 | 448 | 61 | kW | 1.47 | -13 | -14 | 81 | 9.9 | 2.22
77 | 68 | 448 | 64 | MBh | 23.7
77 | 68 | 448 | 64 | S/T | 0.615
77 | 68 | 448 | 64 | ∆T | 30.1
77 | 68 | 448 | 64 | LDB | 46.9
77 | 68 | 448 | 64 | LWB | 44.6
77 | 68 | 448 | 64 | kW | 1.52
80 | 68 | 448 | 67 | MBh | 24.39
80 | 68 | 448 | 67 | S/T | 0.595
80 | 68 | 448 | 67 | ∆T | 30
80 | 68 | 448 | 67 | LDB | 50
80 | 68 | 448 | 67 | LWB | 48.3
80 | 68 | 448 | 67 | kW | 1.53
86 | 68 | 448 | 72 | MBh | 25.67
86 | 68 | 448 | 72 | S/T | 0.561
86 | 68 | 448 | 72 | ∆T | 29.8
86 | 68 | 448 | 72 | LDB | 56.2
86 | 68 | 448 | 72 | LWB | 54.5
86 | 68 | 448 | 72 | kW | 1.54
90 | 68 | 448 | 75 | MBh | 26.66
90 | 68 | 448 | 75 | S/T | 0.522
90 | 68 | 448 | 75 | ∆T | 28.8
90 | 68 | 448 | 75 | LDB | 61.2
90 | 68 | 448 | 75 | LWB | 58.1
90 | 68 | 448 | 75 | kW | 1.55
68 | 86 | 448 | 57 | MBh | 18.82
68 | 86 | 448 | 57 | S/T | 0.677
68 | 86 | 448 | 57 | ∆T | 26.4
68 | 86 | 448 | 57 | LDB | 41.6
68 | 86 | 448 | 57 | LWB | 39.6
68 | 86 | 448 | 57 | kW | 1.63
72 | 86 | 448 | 61 | MBh | 20.72
72 | 86 | 448 | 61 | S/T | 0.633
72 | 86 | 448 | 61 | ∆T | 27.1
72 | 86 | 448 | 61 | LDB | 44.9
72 | 86 | 448 | 61 | LWB | 43.3
72 | 86 | 448 | 61 | kW | 1.81
77 | 86 | 448 | 64 | MBh | 21.71
77 | 86 | 448 | 64 | S/T | 0.622
77 | 86 | 448 | 64 | ∆T | 27.9
77 | 86 | 448 | 64 | LDB | 49.1
77 | 86 | 448 | 64 | LWB | 46.5
77 | 86 | 448 | 64 | kW | 1.81
80 | 86 | 448 | 67 | MBh | 22.4
80 | 86 | 448 | 67 | S/T | 0.602
80 | 86 | 448 | 67 | ∆T | 27.9
80 | 86 | 448 | 67 | LDB | 52.1
80 | 86 | 448 | 67 | LWB | 50.1
80 | 86 | 448 | 67 | kW | 1.82
86 | 86 | 448 | 72 | MBh | 23.68
86 | 86 | 448 | 72 | S/T | 0.569
86 | 86 | 448 | 72 | ∆T | 27.9
86 | 86 | 448 | 72 | LDB | 58.1
86 | 86 | 448 | 72 | LWB | 56.1
86 | 86 | 448 | 72 | kW | 1.83
90 | 86 | 448 | 75 | MBh | 24.66
90 | 86 | 448 | 75 | S/T | 0.53
90 | 86 | 448 | 75 | ∆T | 27
90 | 86 | 448 | 75 | LDB | 63
90 | 86 | 448 | 75 | LWB | 59.6
90 | 86 | 448 | 75 | kW | 1.84
68 | 95 | 448 | 57 | MBh | 18.74
68 | 95 | 448 | 57 | S/T | 0.678
68 | 95 | 448 | 57 | ∆T | 26.2
68 | 95 | 448 | 57 | LDB | 41.8
68 | 95 | 448 | 57 | LWB | 39.7
68 | 95 | 448 | 57 | kW | 1.94
72 | 95 | 448 | 61 | MBh | 19.72
72 | 95 | 448 | 61 | S/T | 0.637
72 | 95 | 448 | 61 | ∆T | 26
72 | 95 | 448 | 61 | LDB | 46
72 | 95 | 448 | 61 | LWB | 44.3
72 | 95 | 448 | 61 | kW | 1.95
77 | 95 | 448 | 64 | MBh | 20.71
77 | 95 | 448 | 64 | S/T | 0.627
77 | 95 | 448 | 64 | ∆T | 26.8
77 | 95 | 448 | 64 | LDB | 50.2
77 | 95 | 448 | 64 | LWB | 47.5
77 | 95 | 448 | 64 | kW | 1.96
80 | 95 | 448 | 67 | MBh | 21.4
80 | 95 | 448 | 67 | S/T | 0.607
80 | 95 | 448 | 67 | ∆T | 26.9
80 | 95 | 448 | 67 | LDB | 53.1
80 | 95 | 448 | 67 | LWB | 51
80 | 95 | 448 | 67 | kW | 1.97
86 | 95 | 448 | 72 | MBh | 22.68
86 | 95 | 448 | 72 | S/T | 0.575
86 | 95 | 448 | 72 | ∆T | 27
86 | 95 | 448 | 72 | LDB | 59
86 | 95 | 448 | 72 | LWB | 56.9
86 | 95 | 448 | 72 | kW | 1.98
90 | 95 | 448 | 75 | MBh | 23.67
90 | 95 | 448 | 75 | S/T | 0.535
90 | 95 | 448 | 75 | ∆T | 26.2
90 | 95 | 448 | 75 | LDB | 63.8
90 | 95 | 448 | 75 | LWB | 60.4
90 | 95 | 448 | 75 | kW | 1.99
68 | 104 | 448 | 57 | MBh | 17.74
68 | 104 | 448 | 57 | S/T | 0.684
68 | 104 | 448 | 57 | ∆T | 25.1
68 | 104 | 448 | 57 | LDB | 42.9
68 | 104 | 448 | 57 | LWB | 40.8
68 | 104 | 448 | 57 | kW | 2.09
72 | 104 | 448 | 61 | MBh | 18.73
72 | 104 | 448 | 61 | S/T | 0.642
72 | 104 | 448 | 61 | ∆T | 24.8
72 | 104 | 448 | 61 | LDB | 47.2
72 | 104 | 448 | 61 | LWB | 45.2
72 | 104 | 448 | 61 | kW | 2.1
77 | 104 | 448 | 64 | MBh | 19.71
77 | 104 | 448 | 64 | S/T | 0.634
77 | 104 | 448 | 64 | ∆T | 25.8
77 | 104 | 448 | 64 | LDB | 51.2
77 | 104 | 448 | 64 | LWB | 48.4
77 | 104 | 448 | 64 | kW | 2.11
80 | 104 | 448 | 67 | MBh | 20.4
80 | 104 | 448 | 67 | S/T | 0.614
80 | 104 | 448 | 67 | ∆T | 25.9
80 | 104 | 448 | 67 | LDB | 54.1
80 | 104 | 448 | 67 | LWB | 51.9
80 | 104 | 448 | 67 | kW | 2.11
86 | 104 | 448 | 72 | MBh | 21.69
86 | 104 | 448 | 72 | S/T | 0.581
86 | 104 | 448 | 72 | ∆T | 26
86 | 104 | 448 | 72 | LDB | 60
86 | 104 | 448 | 72 | LWB | 57.7
86 | 104 | 448 | 72 | kW | 2.12
90 | 104 | 448 | 75 | MBh | 22.67
90 | 104 | 448 | 75 | S/T | 0.541
90 | 104 | 448 | 75 | ∆T | 25.4
90 | 104 | 448 | 75 | LDB | 64.6
90 | 104 | 448 | 75 | LWB | 61.1
90 | 104 | 448 | 75 | kW | 2.13
68 | 115 | 448 | 57 | MBh | 16.55
68 | 115 | 448 | 57 | S/T | 0.693
68 | 115 | 448 | 57 | ∆T | 23.7
68 | 115 | 448 | 57 | LDB | 44.3
68 | 115 | 448 | 57 | LWB | 42
68 | 115 | 448 | 57 | kW | 2.26
72 | 115 | 448 | 61 | MBh | 17.53
72 | 115 | 448 | 61 | S/T | 0.65
72 | 115 | 448 | 61 | ∆T | 23.5
72 | 115 | 448 | 61 | LDB | 48.5
72 | 115 | 448 | 61 | LWB | 46.4
72 | 115 | 448 | 61 | kW | 2.27
77 | 115 | 448 | 64 | MBh | 18.52
77 | 115 | 448 | 64 | S/T | 0.643
77 | 115 | 448 | 64 | ∆T | 24.6
77 | 115 | 448 | 64 | LDB | 52.4
77 | 115 | 448 | 64 | LWB | 49.5
77 | 115 | 448 | 64 | kW | 2.28
80 | 115 | 448 | 67 | MBh | 19.21
80 | 115 | 448 | 67 | S/T | 0.623
80 | 115 | 448 | 67 | ∆T | 24.7
80 | 115 | 448 | 67 | LDB | 55.3
80 | 115 | 448 | 67 | LWB | 52.9
80 | 115 | 448 | 67 | kW | 2.29
86 | 115 | 448 | 72 | MBh | 20.49
86 | 115 | 448 | 72 | S/T | 0.59
86 | 115 | 448 | 72 | ∆T | 25
86 | 115 | 448 | 72 | LDB | 61
86 | 115 | 448 | 72 | LWB | 58.6
86 | 115 | 448 | 72 | kW | 2.3
90 | 115 | 448 | 75 | MBh | 21.48
90 | 115 | 448 | 75 | S/T | 0.549
90 | 115 | 448 | 75 | ∆T | 24.4
90 | 115 | 448 | 75 | LDB | 65.6
90 | 115 | 448 | 75 | LWB | 61.9
90 | 115 | 448 | 75 | kW | 2.31

## RXV09AVJU9 - FFA09AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 378 | 57 | MBh | 12.25 | 75 | 64 | 59 | 18.6 | 1.31
68 | 50 | 378 | 57 | S/T | 0.739 | 75 | 64 | 70 | 18 | 1.34
68 | 50 | 378 | 57 | ∆T | 22.2 | 75 | 64 | 72 | 17.91 | 1.35
68 | 50 | 378 | 57 | LDB | 45.8 | 75 | 64 | 75 | 17.72 | 1.36
68 | 50 | 378 | 57 | LWB | 44.1 | 75 | 64 | 77 | 17.62 | 1.36
68 | 50 | 378 | 57 | kW | 0.57 | 75 | 64 | 81 | 17.42 | 1.37
72 | 50 | 378 | 61 | MBh | 12.76 | 59 | 50 | 59 | 15.93 | 1.23
72 | 50 | 378 | 61 | S/T | 0.695 | 59 | 50 | 70 | 15.33 | 1.26
72 | 50 | 378 | 61 | ∆T | 21.7 | 59 | 50 | 72 | 15.25 | 1.26
72 | 50 | 378 | 61 | LDB | 50.3 | 59 | 50 | 75 | 15.05 | 1.28
72 | 50 | 378 | 61 | LWB | 48.7 | 59 | 50 | 77 | 14.95 | 1.28
72 | 50 | 378 | 61 | kW | 0.57 | 59 | 50 | 81 | 14.76 | 1.29
77 | 50 | 378 | 64 | MBh | 13.27 | 47 | 43 | 59 | 14.59 | 1.19
77 | 50 | 378 | 64 | S/T | 0.699 | 47 | 43 | 70 | 14 | 1.22
77 | 50 | 378 | 64 | ∆T | 22.7 | 47 | 43 | 72 | 13.91 | 1.22
77 | 50 | 378 | 64 | LDB | 54.3 | 47 | 43 | 75 | 13.72 | 1.24
77 | 50 | 378 | 64 | LWB | 51.9 | 47 | 43 | 77 | 13.62 | 1.24
77 | 50 | 378 | 64 | kW | 0.58 | 47 | 43 | 81 | 13.43 | 1.25
80 | 50 | 378 | 67 | MBh | 13.63 | 35 | 32 | 59 | 12.58 | 1.16
80 | 50 | 378 | 67 | S/T | 0.682 | 35 | 32 | 70 | 12 | 1.2
80 | 50 | 378 | 67 | ∆T | 22.8 | 35 | 32 | 72 | 11.91 | 1.2
80 | 50 | 378 | 67 | LDB | 57.2 | 35 | 32 | 75 | 11.72 | 1.21
80 | 50 | 378 | 67 | LWB | 55.4 | 35 | 32 | 77 | 11.63 | 1.22
80 | 50 | 378 | 67 | kW | 0.58 | 35 | 32 | 81 | 11.43 | 1.23
86 | 50 | 378 | 72 | MBh | 14.29 | 25 | 23 | 59 | 10.91 | 1.14
86 | 50 | 378 | 72 | S/T | 0.658 | 25 | 23 | 70 | 10.33 | 1.18
86 | 50 | 378 | 72 | ∆T | 23 | 25 | 23 | 72 | 10.25 | 1.18
86 | 50 | 378 | 72 | LDB | 63 | 25 | 23 | 75 | 10.06 | 1.19
86 | 50 | 378 | 72 | LWB | 61.2 | 25 | 23 | 77 | 9.96 | 1.2
86 | 50 | 378 | 72 | kW | 0.72 | 25 | 23 | 81 | 9.77 | 1.21
90 | 50 | 378 | 75 | MBh | 14.8 | 16 | 14 | 59 | 9.24 | 1.12
90 | 50 | 378 | 75 | S/T | 0.618 | 16 | 14 | 70 | 8.67 | 1.16
90 | 50 | 378 | 75 | ∆T | 22.4 | 16 | 14 | 72 | 8.58 | 1.16
90 | 50 | 378 | 75 | LDB | 67.6 | 16 | 14 | 75 | 8.39 | 1.18
90 | 50 | 378 | 75 | LWB | 64.6 | 16 | 14 | 77 | 8.3 | 1.18
90 | 50 | 378 | 75 | kW | 0.73 | 16 | 14 | 81 | 8.11 | 1.19
68 | 68 | 378 | 57 | MBh | 11.22 | 5 | 5 | 59 | 7.56 | 1.1
68 | 68 | 378 | 57 | S/T | 0.761 | 5 | 5 | 70 | 7 | 1.14
68 | 68 | 378 | 57 | ∆T | 20.9 | 5 | 5 | 72 | 6.92 | 1.15
68 | 68 | 378 | 57 | LDB | 47.1 | 5 | 5 | 75 | 6.73 | 1.16
68 | 68 | 378 | 57 | LWB | 45.3 | 5 | 5 | 77 | 6.64 | 1.16
68 | 68 | 378 | 57 | kW | 0.71 | 5 | 5 | 81 | 6.46 | 1.18
72 | 68 | 378 | 61 | MBh | 11.73
72 | 68 | 378 | 61 | S/T | 0.715
72 | 68 | 378 | 61 | ∆T | 20.6
72 | 68 | 378 | 61 | LDB | 51.4
72 | 68 | 378 | 61 | LWB | 49.8
72 | 68 | 378 | 61 | kW | 0.71
77 | 68 | 378 | 64 | MBh | 12.24
77 | 68 | 378 | 64 | S/T | 0.721
77 | 68 | 378 | 64 | ∆T | 21.6
77 | 68 | 378 | 64 | LDB | 55.4
77 | 68 | 378 | 64 | LWB | 53
77 | 68 | 378 | 64 | kW | 0.72
80 | 68 | 378 | 67 | MBh | 12.6
80 | 68 | 378 | 67 | S/T | 0.704
80 | 68 | 378 | 67 | ∆T | 21.7
80 | 68 | 378 | 67 | LDB | 58.3
80 | 68 | 378 | 67 | LWB | 56.4
80 | 68 | 378 | 67 | kW | 0.72
86 | 68 | 378 | 72 | MBh | 13.26
86 | 68 | 378 | 72 | S/T | 0.679
86 | 68 | 378 | 72 | ∆T | 22.1
86 | 68 | 378 | 72 | LDB | 63.9
86 | 68 | 378 | 72 | LWB | 62.1
86 | 68 | 378 | 72 | kW | 0.72
90 | 68 | 378 | 75 | MBh | 13.77
90 | 68 | 378 | 75 | S/T | 0.638
90 | 68 | 378 | 75 | ∆T | 21.5
90 | 68 | 378 | 75 | LDB | 68.5
90 | 68 | 378 | 75 | LWB | 65.4
90 | 68 | 378 | 75 | kW | 0.73
68 | 86 | 378 | 57 | MBh | 10.19
68 | 86 | 378 | 57 | S/T | 0.788
68 | 86 | 378 | 57 | ∆T | 19.7
68 | 86 | 378 | 57 | LDB | 48.3
68 | 86 | 378 | 57 | LWB | 46.5
68 | 86 | 378 | 57 | kW | 0.84
72 | 86 | 378 | 61 | MBh | 10.7
72 | 86 | 378 | 61 | S/T | 0.74
72 | 86 | 378 | 61 | ∆T | 19.4
72 | 86 | 378 | 61 | LDB | 52.6
72 | 86 | 378 | 61 | LWB | 50.8
72 | 86 | 378 | 61 | kW | 0.85
77 | 86 | 378 | 64 | MBh | 11.21
77 | 86 | 378 | 64 | S/T | 0.748
77 | 86 | 378 | 64 | ∆T | 20.5
77 | 86 | 378 | 64 | LDB | 56.5
77 | 86 | 378 | 64 | LWB | 54
77 | 86 | 378 | 64 | kW | 0.85
80 | 86 | 378 | 67 | MBh | 11.57
80 | 86 | 378 | 67 | S/T | 0.73
80 | 86 | 378 | 67 | ∆T | 20.7
80 | 86 | 378 | 67 | LDB | 59.3
80 | 86 | 378 | 67 | LWB | 57.4
80 | 86 | 378 | 67 | kW | 0.85
86 | 86 | 378 | 72 | MBh | 12.23
86 | 86 | 378 | 72 | S/T | 0.706
86 | 86 | 378 | 72 | ∆T | 21.2
86 | 86 | 378 | 72 | LDB | 64.8
86 | 86 | 378 | 72 | LWB | 62.9
86 | 86 | 378 | 72 | kW | 0.86
90 | 86 | 378 | 75 | MBh | 12.74
90 | 86 | 378 | 75 | S/T | 0.663
90 | 86 | 378 | 75 | ∆T | 20.7
90 | 86 | 378 | 75 | LDB | 69.3
90 | 86 | 378 | 75 | LWB | 66.2
90 | 86 | 378 | 75 | kW | 0.86
68 | 95 | 378 | 57 | MBh | 9.68
68 | 95 | 378 | 57 | S/T | 0.805
68 | 95 | 378 | 57 | ∆T | 19.1
68 | 95 | 378 | 57 | LDB | 48.9
68 | 95 | 378 | 57 | LWB | 47.1
68 | 95 | 378 | 57 | kW | 0.91
72 | 95 | 378 | 61 | MBh | 10.19
72 | 95 | 378 | 61 | S/T | 0.755
72 | 95 | 378 | 61 | ∆T | 18.8
72 | 95 | 378 | 61 | LDB | 53.2
72 | 95 | 378 | 61 | LWB | 51.4
72 | 95 | 378 | 61 | kW | 0.92
77 | 95 | 378 | 64 | MBh | 10.7
77 | 95 | 378 | 64 | S/T | 0.764
77 | 95 | 378 | 64 | ∆T | 20
77 | 95 | 378 | 64 | LDB | 57
77 | 95 | 378 | 64 | LWB | 54.5
77 | 95 | 378 | 64 | kW | 0.92
80 | 95 | 378 | 67 | MBh | 11
80 | 95 | 378 | 67 | S/T | 0.75
80 | 95 | 378 | 67 | ∆T | 20.2
80 | 95 | 378 | 67 | LDB | 59.8
80 | 95 | 378 | 67 | LWB | 57.9
80 | 95 | 378 | 67 | kW | 0.92
86 | 95 | 378 | 72 | MBh | 11.72
86 | 95 | 378 | 72 | S/T | 0.722
86 | 95 | 378 | 72 | ∆T | 20.7
86 | 95 | 378 | 72 | LDB | 65.3
86 | 95 | 378 | 72 | LWB | 63.3
86 | 95 | 378 | 72 | kW | 0.93
90 | 95 | 378 | 75 | MBh | 12.23
90 | 95 | 378 | 75 | S/T | 0.677
90 | 95 | 378 | 75 | ∆T | 20.3
90 | 95 | 378 | 75 | LDB | 69.7
90 | 95 | 378 | 75 | LWB | 66.6
90 | 95 | 378 | 75 | kW | 0.93
68 | 104 | 378 | 57 | MBh | 9.16
68 | 104 | 378 | 57 | S/T | 0.823
68 | 104 | 378 | 57 | ∆T | 18.5
68 | 104 | 378 | 57 | LDB | 49.5
68 | 104 | 378 | 57 | LWB | 47.7
68 | 104 | 378 | 57 | kW | 0.98
72 | 104 | 378 | 61 | MBh | 9.67
72 | 104 | 378 | 61 | S/T | 0.771
72 | 104 | 378 | 61 | ∆T | 18.3
72 | 104 | 378 | 61 | LDB | 53.7
72 | 104 | 378 | 61 | LWB | 51.9
72 | 104 | 378 | 61 | kW | 0.98
77 | 104 | 378 | 64 | MBh | 10.18
77 | 104 | 378 | 64 | S/T | 0.782
77 | 104 | 378 | 64 | ∆T | 19.5
77 | 104 | 378 | 64 | LDB | 57.5
77 | 104 | 378 | 64 | LWB | 55
77 | 104 | 378 | 64 | kW | 0.99
80 | 104 | 378 | 67 | MBh | 10.54
80 | 104 | 378 | 67 | S/T | 0.764
80 | 104 | 378 | 67 | ∆T | 19.7
80 | 104 | 378 | 67 | LDB | 60.3
80 | 104 | 378 | 67 | LWB | 58.3
80 | 104 | 378 | 67 | kW | 0.99
86 | 104 | 378 | 72 | MBh | 11.2
86 | 104 | 378 | 72 | S/T | 0.739
86 | 104 | 378 | 72 | ∆T | 20.3
86 | 104 | 378 | 72 | LDB | 65.7
86 | 104 | 378 | 72 | LWB | 63.7
86 | 104 | 378 | 72 | kW | 1
90 | 104 | 378 | 75 | MBh | 11.71
90 | 104 | 378 | 75 | S/T | 0.693
90 | 104 | 378 | 75 | ∆T | 19.9
90 | 104 | 378 | 75 | LDB | 70.1
90 | 104 | 378 | 75 | LWB | 66.9
90 | 104 | 378 | 75 | kW | 1
68 | 115 | 378 | 57 | MBh | 8.55
68 | 115 | 378 | 57 | S/T | 0.848
68 | 115 | 378 | 57 | ∆T | 17.8
68 | 115 | 378 | 57 | LDB | 50.2
68 | 115 | 378 | 57 | LWB | 48.3
68 | 115 | 378 | 57 | kW | 1.06
72 | 115 | 378 | 61 | MBh | 9.06
72 | 115 | 378 | 61 | S/T | 0.794
72 | 115 | 378 | 61 | ∆T | 17.6
72 | 115 | 378 | 61 | LDB | 54.4
72 | 115 | 378 | 61 | LWB | 52.5
72 | 115 | 378 | 61 | kW | 1.07
77 | 115 | 378 | 64 | MBh | 9.57
77 | 115 | 378 | 64 | S/T | 0.805
77 | 115 | 378 | 64 | ∆T | 18.9
77 | 115 | 378 | 64 | LDB | 58.1
77 | 115 | 378 | 64 | LWB | 55.6
77 | 115 | 378 | 64 | kW | 1.07
80 | 115 | 378 | 67 | MBh | 9.92
80 | 115 | 378 | 67 | S/T | 0.787
80 | 115 | 378 | 67 | ∆T | 19.1
80 | 115 | 378 | 67 | LDB | 60.9
80 | 115 | 378 | 67 | LWB | 58.8
80 | 115 | 378 | 67 | kW | 1.07
86 | 115 | 378 | 72 | MBh | 10.58
86 | 115 | 378 | 72 | S/T | 0.762
86 | 115 | 378 | 72 | ∆T | 19.7
86 | 115 | 378 | 72 | LDB | 66.3
86 | 115 | 378 | 72 | LWB | 64.2
86 | 115 | 378 | 72 | kW | 1.08
90 | 115 | 378 | 75 | MBh | 11.09
90 | 115 | 378 | 75 | S/T | 0.714
90 | 115 | 378 | 75 | ∆T | 19.4
90 | 115 | 378 | 75 | LDB | 70.6
90 | 115 | 378 | 75 | LWB | 67.4
90 | 115 | 378 | 75 | kW | 1.08

## RXV12AVJU9 - FFA12AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 392 | 57 | MBh | 14.75 | 75 | 64 | 59 | 21.67 | 1.75
68 | 50 | 392 | 57 | S/T | 0.729 | 75 | 64 | 70 | 20.97 | 1.79
68 | 50 | 392 | 57 | ∆T | 25.4 | 75 | 64 | 72 | 20.87 | 1.8
68 | 50 | 392 | 57 | LDB | 42.6 | 75 | 64 | 75 | 20.64 | 1.82
68 | 50 | 392 | 57 | LWB | 41.7 | 75 | 64 | 77 | 20.53 | 1.82
68 | 50 | 392 | 57 | kW | 0.79 | 75 | 64 | 81 | 20.3 | 1.84
72 | 50 | 392 | 61 | MBh | 15.36 | 59 | 50 | 59 | 18.89 | 1.64
72 | 50 | 392 | 61 | S/T | 0.686 | 59 | 50 | 70 | 18.19 | 1.69
72 | 50 | 392 | 61 | ∆T | 24.9 | 59 | 50 | 72 | 18.09 | 1.69
72 | 50 | 392 | 61 | LDB | 47.1 | 59 | 50 | 75 | 17.86 | 1.71
72 | 50 | 392 | 61 | LWB | 46.4 | 59 | 50 | 77 | 17.74 | 1.71
72 | 50 | 392 | 61 | kW | 0.79 | 59 | 50 | 81 | 17.51 | 1.73
77 | 50 | 392 | 64 | MBh | 15.98 | 47 | 43 | 59 | 17.51 | 1.59
77 | 50 | 392 | 64 | S/T | 0.688 | 47 | 43 | 70 | 16.8 | 1.63
77 | 50 | 392 | 64 | ∆T | 26 | 47 | 43 | 72 | 16.7 | 1.64
77 | 50 | 392 | 64 | LDB | 51 | 47 | 43 | 75 | 16.46 | 1.65
77 | 50 | 392 | 64 | LWB | 49.7 | 47 | 43 | 77 | 16.35 | 1.66
77 | 50 | 392 | 64 | kW | 0.8 | 47 | 43 | 81 | 16.12 | 1.68
80 | 50 | 392 | 67 | MBh | 16.4 | 35 | 32 | 59 | 15.43 | 1.56
80 | 50 | 392 | 67 | S/T | 0.671 | 35 | 32 | 70 | 14.71 | 1.61
80 | 50 | 392 | 67 | ∆T | 26 | 35 | 32 | 72 | 14.61 | 1.61
80 | 50 | 392 | 67 | LDB | 54 | 35 | 32 | 75 | 14.37 | 1.63
80 | 50 | 392 | 67 | LWB | 53.3 | 35 | 32 | 77 | 14.26 | 1.64
80 | 50 | 392 | 67 | kW | 0.8 | 35 | 32 | 81 | 14.02 | 1.65
86 | 50 | 392 | 72 | MBh | 17.2 | 25 | 23 | 59 | 13.7 | 1.54
86 | 50 | 392 | 72 | S/T | 0.646 | 25 | 23 | 70 | 12.98 | 1.59
86 | 50 | 392 | 72 | ∆T | 26.2 | 25 | 23 | 72 | 12.87 | 1.59
86 | 50 | 392 | 72 | LDB | 59.8 | 25 | 23 | 75 | 12.63 | 1.61
86 | 50 | 392 | 72 | LWB | 59.2 | 25 | 23 | 77 | 12.51 | 1.62
86 | 50 | 392 | 72 | kW | 1 | 25 | 23 | 81 | 12.27 | 1.63
90 | 50 | 392 | 75 | MBh | 17.81 | 16 | 14 | 59 | 11.98 | 1.52
90 | 50 | 392 | 75 | S/T | 0.606 | 16 | 14 | 70 | 11.24 | 1.57
90 | 50 | 392 | 75 | ∆T | 25.5 | 16 | 14 | 72 | 11.13 | 1.57
90 | 50 | 392 | 75 | LDB | 64.5 | 16 | 14 | 75 | 10.89 | 1.59
90 | 50 | 392 | 75 | LWB | 62.7 | 16 | 14 | 77 | 10.76 | 1.6
90 | 50 | 392 | 75 | kW | 1 | 16 | 14 | 81 | 10.52 | 1.62
68 | 68 | 392 | 57 | MBh | 13.51 | 5 | 5 | 59 | 10.26 | 1.5
68 | 68 | 392 | 57 | S/T | 0.75 | 5 | 5 | 70 | 9.5 | 1.55
68 | 68 | 392 | 57 | ∆T | 23.9 | 5 | 5 | 72 | 9.39 | 1.55
68 | 68 | 392 | 57 | LDB | 44.1 | 5 | 5 | 75 | 9.14 | 1.57
68 | 68 | 392 | 57 | LWB | 43.2 | 5 | 5 | 77 | 9.01 | 1.58
68 | 68 | 392 | 57 | kW | 0.98 | 5 | 5 | 81 | 8.76 | 1.6
72 | 68 | 392 | 61 | MBh | 14.12
72 | 68 | 392 | 61 | S/T | 0.705
72 | 68 | 392 | 61 | ∆T | 23.5
72 | 68 | 392 | 61 | LDB | 48.5
72 | 68 | 392 | 61 | LWB | 47.7
72 | 68 | 392 | 61 | kW | 0.98
77 | 68 | 392 | 64 | MBh | 14.74
77 | 68 | 392 | 64 | S/T | 0.709
77 | 68 | 392 | 64 | ∆T | 24.7
77 | 68 | 392 | 64 | LDB | 52.3
77 | 68 | 392 | 64 | LWB | 51
77 | 68 | 392 | 64 | kW | 0.99
80 | 68 | 392 | 67 | MBh | 15.17
80 | 68 | 392 | 67 | S/T | 0.691
80 | 68 | 392 | 67 | ∆T | 24.8
80 | 68 | 392 | 67 | LDB | 55.2
80 | 68 | 392 | 67 | LWB | 54.5
80 | 68 | 392 | 67 | kW | 0.99
86 | 68 | 392 | 72 | MBh | 15.96
86 | 68 | 392 | 72 | S/T | 0.667
86 | 68 | 392 | 72 | ∆T | 25.2
86 | 68 | 392 | 72 | LDB | 60.8
86 | 68 | 392 | 72 | LWB | 60.2
86 | 68 | 392 | 72 | kW | 1
90 | 68 | 392 | 75 | MBh | 16.58
90 | 68 | 392 | 75 | S/T | 0.625
90 | 68 | 392 | 75 | ∆T | 24.5
90 | 68 | 392 | 75 | LDB | 65.5
90 | 68 | 392 | 75 | LWB | 63.6
90 | 68 | 392 | 75 | kW | 1
68 | 86 | 392 | 57 | MBh | 12.27
68 | 86 | 392 | 57 | S/T | 0.776
68 | 86 | 392 | 57 | ∆T | 22.5
68 | 86 | 392 | 57 | LDB | 45.5
68 | 86 | 392 | 57 | LWB | 44.6
68 | 86 | 392 | 57 | kW | 1.16
72 | 86 | 392 | 61 | MBh | 12.88
72 | 86 | 392 | 61 | S/T | 0.728
72 | 86 | 392 | 61 | ∆T | 22.2
72 | 86 | 392 | 61 | LDB | 49.8
72 | 86 | 392 | 61 | LWB | 49
72 | 86 | 392 | 61 | kW | 1.17
77 | 86 | 392 | 64 | MBh | 13.5
77 | 86 | 392 | 64 | S/T | 0.734
77 | 86 | 392 | 64 | ∆T | 23.4
77 | 86 | 392 | 64 | LDB | 53.6
77 | 86 | 392 | 64 | LWB | 52.2
77 | 86 | 392 | 64 | kW | 1.17
80 | 86 | 392 | 67 | MBh | 13.93
80 | 86 | 392 | 67 | S/T | 0.716
80 | 86 | 392 | 67 | ∆T | 23.6
80 | 86 | 392 | 67 | LDB | 56.4
80 | 86 | 392 | 67 | LWB | 55.6
80 | 86 | 392 | 67 | kW | 1.18
86 | 86 | 392 | 72 | MBh | 14.72
86 | 86 | 392 | 72 | S/T | 0.692
86 | 86 | 392 | 72 | ∆T | 24.1
86 | 86 | 392 | 72 | LDB | 61.9
86 | 86 | 392 | 72 | LWB | 61.3
86 | 86 | 392 | 72 | kW | 1.19
90 | 86 | 392 | 75 | MBh | 15.34
90 | 86 | 392 | 75 | S/T | 0.649
90 | 86 | 392 | 75 | ∆T | 23.5
90 | 86 | 392 | 75 | LDB | 66.5
90 | 86 | 392 | 75 | LWB | 64.6
90 | 86 | 392 | 75 | kW | 1.19
68 | 95 | 392 | 57 | MBh | 11.65
68 | 95 | 392 | 57 | S/T | 0.791
68 | 95 | 392 | 57 | ∆T | 21.8
68 | 95 | 392 | 57 | LDB | 46.2
68 | 95 | 392 | 57 | LWB | 45.3
68 | 95 | 392 | 57 | kW | 1.26
72 | 95 | 392 | 61 | MBh | 12.26
72 | 95 | 392 | 61 | S/T | 0.742
72 | 95 | 392 | 61 | ∆T | 21.5
72 | 95 | 392 | 61 | LDB | 50.5
72 | 95 | 392 | 61 | LWB | 49.7
72 | 95 | 392 | 61 | kW | 1.26
77 | 95 | 392 | 64 | MBh | 12.88
77 | 95 | 392 | 64 | S/T | 0.749
77 | 95 | 392 | 64 | ∆T | 22.8
77 | 95 | 392 | 64 | LDB | 54.2
77 | 95 | 392 | 64 | LWB | 52.8
77 | 95 | 392 | 64 | kW | 1.27
80 | 95 | 392 | 67 | MBh | 13.3
80 | 95 | 392 | 67 | S/T | 0.732
80 | 95 | 392 | 67 | ∆T | 23
80 | 95 | 392 | 67 | LDB | 57
80 | 95 | 392 | 67 | LWB | 56.2
80 | 95 | 392 | 67 | kW | 1.27
86 | 95 | 392 | 72 | MBh | 14.1
86 | 95 | 392 | 72 | S/T | 0.707
86 | 95 | 392 | 72 | ∆T | 23.5
86 | 95 | 392 | 72 | LDB | 62.5
86 | 95 | 392 | 72 | LWB | 61.8
86 | 95 | 392 | 72 | kW | 1.28
90 | 95 | 392 | 75 | MBh | 14.72
90 | 95 | 392 | 75 | S/T | 0.662
90 | 95 | 392 | 75 | ∆T | 23
90 | 95 | 392 | 75 | LDB | 67
90 | 95 | 392 | 75 | LWB | 65
90 | 95 | 392 | 75 | kW | 1.29
68 | 104 | 392 | 57 | MBh | 11.03
68 | 104 | 392 | 57 | S/T | 0.809
68 | 104 | 392 | 57 | ∆T | 21.1
68 | 104 | 392 | 57 | LDB | 46.9
68 | 104 | 392 | 57 | LWB | 46
68 | 104 | 392 | 57 | kW | 1.35
72 | 104 | 392 | 61 | MBh | 11.64
72 | 104 | 392 | 61 | S/T | 0.758
72 | 104 | 392 | 61 | ∆T | 20.8
72 | 104 | 392 | 61 | LDB | 51.2
72 | 104 | 392 | 61 | LWB | 50.3
72 | 104 | 392 | 61 | kW | 1.36
77 | 104 | 392 | 64 | MBh | 12.26
77 | 104 | 392 | 64 | S/T | 0.766
77 | 104 | 392 | 64 | ∆T | 22.2
77 | 104 | 392 | 64 | LDB | 54.8
77 | 104 | 392 | 64 | LWB | 53.4
77 | 104 | 392 | 64 | kW | 1.36
80 | 104 | 392 | 67 | MBh | 12.69
80 | 104 | 392 | 67 | S/T | 0.748
80 | 104 | 392 | 67 | ∆T | 22.4
80 | 104 | 392 | 67 | LDB | 57.6
80 | 104 | 392 | 67 | LWB | 56.7
80 | 104 | 392 | 67 | kW | 1.37
86 | 104 | 392 | 72 | MBh | 13.48
86 | 104 | 392 | 72 | S/T | 0.723
86 | 104 | 392 | 72 | ∆T | 23
86 | 104 | 392 | 72 | LDB | 63
86 | 104 | 392 | 72 | LWB | 62.3
86 | 104 | 392 | 72 | kW | 1.37
90 | 104 | 392 | 75 | MBh | 14.1
90 | 104 | 392 | 75 | S/T | 0.677
90 | 104 | 392 | 75 | ∆T | 22.6
90 | 104 | 392 | 75 | LDB | 67.4
90 | 104 | 392 | 75 | LWB | 65.5
90 | 104 | 392 | 75 | kW | 1.38
68 | 115 | 392 | 57 | MBh | 10.29
68 | 115 | 392 | 57 | S/T | 0.833
68 | 115 | 392 | 57 | ∆T | 20.2
68 | 115 | 392 | 57 | LDB | 47.8
68 | 115 | 392 | 57 | LWB | 46.8
68 | 115 | 392 | 57 | kW | 1.08
72 | 115 | 392 | 61 | MBh | 10.9
72 | 115 | 392 | 61 | S/T | 0.779
72 | 115 | 392 | 61 | ∆T | 20.1
72 | 115 | 392 | 61 | LDB | 51.9
72 | 115 | 392 | 61 | LWB | 51
72 | 115 | 392 | 61 | kW | 1.08
77 | 115 | 392 | 64 | MBh | 11.51
77 | 115 | 392 | 64 | S/T | 0.789
77 | 115 | 392 | 64 | ∆T | 21.4
77 | 115 | 392 | 64 | LDB | 55.6
77 | 115 | 392 | 64 | LWB | 54.1
77 | 115 | 392 | 64 | kW | 1.08
80 | 115 | 392 | 67 | MBh | 11.94
80 | 115 | 392 | 67 | S/T | 0.771
80 | 115 | 392 | 67 | ∆T | 21.7
80 | 115 | 392 | 67 | LDB | 58.3
80 | 115 | 392 | 67 | LWB | 57.4
80 | 115 | 392 | 67 | kW | 1.08
86 | 115 | 392 | 72 | MBh | 12.74
86 | 115 | 392 | 72 | S/T | 0.745
86 | 115 | 392 | 72 | ∆T | 22.4
86 | 115 | 392 | 72 | LDB | 63.6
86 | 115 | 392 | 72 | LWB | 62.8
86 | 115 | 392 | 72 | kW | 1.08
90 | 115 | 392 | 75 | MBh | 13.35
90 | 115 | 392 | 75 | S/T | 0.697
90 | 115 | 392 | 75 | ∆T | 22
90 | 115 | 392 | 75 | LDB | 68
90 | 115 | 392 | 75 | LWB | 66.1
90 | 115 | 392 | 75 | kW | 1.08

## RXV15AVJU9 - FFA15AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 413 | 57 | MBh | 15.23 | 75 | 64 | 59 | 19.73 | 2.01
68 | 50 | 413 | 57 | S/T | 0.705 | 75 | 64 | 70 | 19.1 | 2.06
68 | 50 | 413 | 57 | ∆T | 24.1 | 75 | 64 | 72 | 19.01 | 2.07
68 | 50 | 413 | 57 | LDB | 43.9 | 75 | 64 | 75 | 18.8 | 2.09
68 | 50 | 413 | 57 | LWB | 42.1 | 75 | 64 | 77 | 18.7 | 2.09
68 | 50 | 413 | 57 | kW | 0.72 | 75 | 64 | 81 | 18.49 | 2.11
72 | 50 | 413 | 61 | MBh | 18.67 | 59 | 50 | 59 | 17.9 | 1.89
72 | 50 | 413 | 61 | S/T | 0.641 | 59 | 50 | 70 | 17.23 | 1.94
72 | 50 | 413 | 61 | ∆T | 26.8 | 59 | 50 | 72 | 17.14 | 1.95
72 | 50 | 413 | 61 | LDB | 45.2 | 59 | 50 | 75 | 16.92 | 1.96
72 | 50 | 413 | 61 | LWB | 43.7 | 59 | 50 | 77 | 16.81 | 1.97
72 | 50 | 413 | 61 | kW | 0.91 | 59 | 50 | 81 | 16.59 | 1.99
77 | 50 | 413 | 64 | MBh | 19.42 | 47 | 43 | 59 | 16.99 | 1.82
77 | 50 | 413 | 64 | S/T | 0.633 | 47 | 43 | 70 | 16.3 | 1.88
77 | 50 | 413 | 64 | ∆T | 27.6 | 47 | 43 | 72 | 16.2 | 1.88
77 | 50 | 413 | 64 | LDB | 49.4 | 47 | 43 | 75 | 15.97 | 1.9
77 | 50 | 413 | 64 | LWB | 47.1 | 47 | 43 | 77 | 15.86 | 1.91
77 | 50 | 413 | 64 | kW | 0.91 | 47 | 43 | 81 | 15.64 | 1.93
80 | 50 | 413 | 67 | MBh | 19.94 | 35 | 32 | 59 | 15.63 | 1.79
80 | 50 | 413 | 67 | S/T | 0.615 | 35 | 32 | 70 | 14.9 | 1.85
80 | 50 | 413 | 67 | ∆T | 27.5 | 35 | 32 | 72 | 14.79 | 1.85
80 | 50 | 413 | 67 | LDB | 52.5 | 35 | 32 | 75 | 14.55 | 1.87
80 | 50 | 413 | 67 | LWB | 50.8 | 35 | 32 | 77 | 14.44 | 1.88
80 | 50 | 413 | 67 | kW | 0.92 | 35 | 32 | 81 | 14.2 | 1.9
86 | 50 | 413 | 72 | MBh | 20.91 | 25 | 23 | 59 | 14.5 | 1.76
86 | 50 | 413 | 72 | S/T | 0.584 | 25 | 23 | 70 | 13.73 | 1.82
86 | 50 | 413 | 72 | ∆T | 27.4 | 25 | 23 | 72 | 13.62 | 1.83
86 | 50 | 413 | 72 | LDB | 58.6 | 25 | 23 | 75 | 13.37 | 1.85
86 | 50 | 413 | 72 | LWB | 56.9 | 25 | 23 | 77 | 13.24 | 1.85
86 | 50 | 413 | 72 | kW | 0.92 | 25 | 23 | 81 | 12.99 | 1.87
90 | 50 | 413 | 75 | MBh | 21.65 | 16 | 14 | 59 | 13.53 | 1.74
90 | 50 | 413 | 75 | S/T | 0.546 | 16 | 14 | 70 | 12.71 | 1.8
90 | 50 | 413 | 75 | ∆T | 26.5 | 16 | 14 | 72 | 12.59 | 1.8
90 | 50 | 413 | 75 | LDB | 63.5 | 16 | 14 | 75 | 12.32 | 1.82
90 | 50 | 413 | 75 | LWB | 60.5 | 16 | 14 | 77 | 12.18 | 1.83
90 | 50 | 413 | 75 | kW | 0.93 | 16 | 14 | 81 | 11.91 | 1.85
68 | 68 | 413 | 57 | MBh | 15.23 | 5 | 5 | 59 | 12.31 | 1.71
68 | 68 | 413 | 57 | S/T | 0.705 | 5 | 5 | 70 | 11.4 | 1.77
68 | 68 | 413 | 57 | ∆T | 24.1 | 5 | 5 | 72 | 11.27 | 1.78
68 | 68 | 413 | 57 | LDB | 43.9 | 5 | 5 | 75 | 10.97 | 1.8
68 | 68 | 413 | 57 | LWB | 42.1 | 5 | 5 | 77 | 10.82 | 1.81
68 | 68 | 413 | 57 | kW | 1 | 5 | 5 | 81 | 10.52 | 1.82
72 | 68 | 413 | 61 | MBh | 17.17
72 | 68 | 413 | 61 | S/T | 0.651
72 | 68 | 413 | 61 | ∆T | 25
72 | 68 | 413 | 61 | LDB | 47
72 | 68 | 413 | 61 | LWB | 45.3
72 | 68 | 413 | 61 | kW | 1.12
77 | 68 | 413 | 64 | MBh | 17.91
77 | 68 | 413 | 64 | S/T | 0.645
77 | 68 | 413 | 64 | ∆T | 25.9
77 | 68 | 413 | 64 | LDB | 51.1
77 | 68 | 413 | 64 | LWB | 48.7
77 | 68 | 413 | 64 | kW | 1.13
80 | 68 | 413 | 67 | MBh | 18.43
80 | 68 | 413 | 67 | S/T | 0.627
80 | 68 | 413 | 67 | ∆T | 25.9
80 | 68 | 413 | 67 | LDB | 54.1
80 | 68 | 413 | 67 | LWB | 52.2
80 | 68 | 413 | 67 | kW | 1.13
86 | 68 | 413 | 72 | MBh | 19.4
86 | 68 | 413 | 72 | S/T | 0.597
86 | 68 | 413 | 72 | ∆T | 26
86 | 68 | 413 | 72 | LDB | 60
86 | 68 | 413 | 72 | LWB | 58.2
86 | 68 | 413 | 72 | kW | 1.14
90 | 68 | 413 | 75 | MBh | 20.15
90 | 68 | 413 | 75 | S/T | 0.558
90 | 68 | 413 | 75 | ∆T | 25.2
90 | 68 | 413 | 75 | LDB | 64.8
90 | 68 | 413 | 75 | LWB | 61.6
90 | 68 | 413 | 75 | kW | 1.15
68 | 86 | 413 | 57 | MBh | 15.23
68 | 86 | 413 | 57 | S/T | 0.705
68 | 86 | 413 | 57 | ∆T | 24.1
68 | 86 | 413 | 57 | LDB | 43.9
68 | 86 | 413 | 57 | LWB | 42.1
68 | 86 | 413 | 57 | kW | 1.28
72 | 86 | 413 | 61 | MBh | 15.99
72 | 86 | 413 | 61 | S/T | 0.661
72 | 86 | 413 | 61 | ∆T | 23.7
72 | 86 | 413 | 61 | LDB | 48.3
72 | 86 | 413 | 61 | LWB | 46.6
72 | 86 | 413 | 61 | kW | 1.29
77 | 86 | 413 | 64 | MBh | 16.74
77 | 86 | 413 | 64 | S/T | 0.657
77 | 86 | 413 | 64 | ∆T | 24.7
77 | 86 | 413 | 64 | LDB | 52.3
77 | 86 | 413 | 64 | LWB | 49.8
77 | 86 | 413 | 64 | kW | 1.29
80 | 86 | 413 | 67 | MBh | 17.26
80 | 86 | 413 | 67 | S/T | 0.638
80 | 86 | 413 | 67 | ∆T | 24.7
80 | 86 | 413 | 67 | LDB | 55.3
80 | 86 | 413 | 67 | LWB | 53.3
80 | 86 | 413 | 67 | kW | 1.3
86 | 86 | 413 | 72 | MBh | 18.23
86 | 86 | 413 | 72 | S/T | 0.609
86 | 86 | 413 | 72 | ∆T | 24.9
86 | 86 | 413 | 72 | LDB | 61.1
86 | 86 | 413 | 72 | LWB | 59.1
86 | 86 | 413 | 72 | kW | 1.31
90 | 86 | 413 | 75 | MBh | 18.97
90 | 86 | 413 | 75 | S/T | 0.569
90 | 86 | 413 | 75 | ∆T | 24.2
90 | 86 | 413 | 75 | LDB | 65.8
90 | 86 | 413 | 75 | LWB | 62.5
90 | 86 | 413 | 75 | kW | 1.31
68 | 95 | 413 | 57 | MBh | 14.16
68 | 95 | 413 | 57 | S/T | 0.718
68 | 95 | 413 | 57 | ∆T | 22.8
68 | 95 | 413 | 57 | LDB | 45.2
68 | 95 | 413 | 57 | LWB | 43.3
68 | 95 | 413 | 57 | kW | 1.44
72 | 95 | 413 | 61 | MBh | 14.91
72 | 95 | 413 | 61 | S/T | 0.673
72 | 95 | 413 | 61 | ∆T | 22.5
72 | 95 | 413 | 61 | LDB | 49.5
72 | 95 | 413 | 61 | LWB | 47.7
72 | 95 | 413 | 61 | kW | 1.44
77 | 95 | 413 | 64 | MBh | 15.65
77 | 95 | 413 | 64 | S/T | 0.671
77 | 95 | 413 | 64 | ∆T | 23.5
77 | 95 | 413 | 64 | LDB | 53.5
77 | 95 | 413 | 64 | LWB | 50.9
77 | 95 | 413 | 64 | kW | 1.45
80 | 95 | 413 | 67 | MBh | 16.2
80 | 95 | 413 | 67 | S/T | 0.651
80 | 95 | 413 | 67 | ∆T | 23.6
80 | 95 | 413 | 67 | LDB | 56.4
80 | 95 | 413 | 67 | LWB | 54.3
80 | 95 | 413 | 67 | kW | 1.45
86 | 95 | 413 | 72 | MBh | 17.14
86 | 95 | 413 | 72 | S/T | 0.623
86 | 95 | 413 | 72 | ∆T | 23.9
86 | 95 | 413 | 72 | LDB | 62.1
86 | 95 | 413 | 72 | LWB | 60
86 | 95 | 413 | 72 | kW | 1.46
90 | 95 | 413 | 75 | MBh | 17.89
90 | 95 | 413 | 75 | S/T | 0.581
90 | 95 | 413 | 75 | ∆T | 23.3
90 | 95 | 413 | 75 | LDB | 66.7
90 | 95 | 413 | 75 | LWB | 63.3
90 | 95 | 413 | 75 | kW | 1.47
68 | 104 | 413 | 57 | MBh | 13.41
68 | 104 | 413 | 57 | S/T | 0.729
68 | 104 | 413 | 57 | ∆T | 21.9
68 | 104 | 413 | 57 | LDB | 46.1
68 | 104 | 413 | 57 | LWB | 44.1
68 | 104 | 413 | 57 | kW | 1.54
72 | 104 | 413 | 61 | MBh | 14.15
72 | 104 | 413 | 61 | S/T | 0.683
72 | 104 | 413 | 61 | ∆T | 21.7
72 | 104 | 413 | 61 | LDB | 50.3
72 | 104 | 413 | 61 | LWB | 48.4
72 | 104 | 413 | 61 | kW | 1.55
77 | 104 | 413 | 64 | MBh | 14.9
77 | 104 | 413 | 64 | S/T | 0.681
77 | 104 | 413 | 64 | ∆T | 22.8
77 | 104 | 413 | 64 | LDB | 54.2
77 | 104 | 413 | 64 | LWB | 51.6
77 | 104 | 413 | 64 | kW | 1.56
80 | 104 | 413 | 67 | MBh | 15.42
80 | 104 | 413 | 67 | S/T | 0.663
80 | 104 | 413 | 67 | ∆T | 22.9
80 | 104 | 413 | 67 | LDB | 57.1
80 | 104 | 413 | 67 | LWB | 55
80 | 104 | 413 | 67 | kW | 1.56
86 | 104 | 413 | 72 | MBh | 16.39
86 | 104 | 413 | 72 | S/T | 0.633
86 | 104 | 413 | 72 | ∆T | 23.3
86 | 104 | 413 | 72 | LDB | 62.7
86 | 104 | 413 | 72 | LWB | 60.6
86 | 104 | 413 | 72 | kW | 1.57
90 | 104 | 413 | 75 | MBh | 17.13
90 | 104 | 413 | 75 | S/T | 0.591
90 | 104 | 413 | 75 | ∆T | 22.7
90 | 104 | 413 | 75 | LDB | 67.3
90 | 104 | 413 | 75 | LWB | 63.9
90 | 104 | 413 | 75 | kW | 1.58
68 | 115 | 413 | 57 | MBh | 12.5
68 | 115 | 413 | 57 | S/T | 0.745
68 | 115 | 413 | 57 | ∆T | 20.9
68 | 115 | 413 | 57 | LDB | 47.1
68 | 115 | 413 | 57 | LWB | 45.1
68 | 115 | 413 | 57 | kW | 1.67
72 | 115 | 413 | 61 | MBh | 13.25
72 | 115 | 413 | 61 | S/T | 0.697
72 | 115 | 413 | 61 | ∆T | 20.7
72 | 115 | 413 | 61 | LDB | 51.3
72 | 115 | 413 | 61 | LWB | 49.3
72 | 115 | 413 | 61 | kW | 1.68
77 | 115 | 413 | 64 | MBh | 13.99
77 | 115 | 413 | 64 | S/T | 0.697
77 | 115 | 413 | 64 | ∆T | 21.9
77 | 115 | 413 | 64 | LDB | 55.1
77 | 115 | 413 | 64 | LWB | 52.4
77 | 115 | 413 | 64 | kW | 1.69
80 | 115 | 413 | 67 | MBh | 14.52
80 | 115 | 413 | 67 | S/T | 0.677
80 | 115 | 413 | 67 | ∆T | 22
80 | 115 | 413 | 67 | LDB | 58
80 | 115 | 413 | 67 | LWB | 55.8
80 | 115 | 413 | 67 | kW | 1.69
86 | 115 | 413 | 72 | MBh | 15.48
86 | 115 | 413 | 72 | S/T | 0.648
86 | 115 | 413 | 72 | ∆T | 22.5
86 | 115 | 413 | 72 | LDB | 63.5
86 | 115 | 413 | 72 | LWB | 61.3
86 | 115 | 413 | 72 | kW | 1.7
90 | 115 | 413 | 75 | MBh | 16.23
90 | 115 | 413 | 75 | S/T | 0.605
90 | 115 | 413 | 75 | ∆T | 22
90 | 115 | 413 | 75 | LDB | 68
90 | 115 | 413 | 75 | LWB | 64.5
90 | 115 | 413 | 75 | kW | 1.7

## RXV18AVJU9 - FFA18AVJU9
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 50 | 501 | 57 | MBh | 17.9 | 75 | 64 | 59 | 26.42 | 2.31
68 | 50 | 501 | 57 | S/T | 0.704 | 75 | 64 | 70 | 25.57 | 2.37
68 | 50 | 501 | 57 | ∆T | 23.3 | 75 | 64 | 72 | 25.45 | 2.38
68 | 50 | 501 | 57 | LDB | 44.7 | 75 | 64 | 75 | 25.17 | 2.4
68 | 50 | 501 | 57 | LWB | 42.6 | 75 | 64 | 77 | 25.03 | 2.41
68 | 50 | 501 | 57 | kW | 0.83 | 75 | 64 | 81 | 24.75 | 2.42
72 | 50 | 501 | 61 | MBh | 21.63 | 59 | 50 | 59 | 23.95 | 2.17
72 | 50 | 501 | 61 | S/T | 0.642 | 59 | 50 | 70 | 23.06 | 2.23
72 | 50 | 501 | 61 | ∆T | 25.7 | 59 | 50 | 72 | 22.93 | 2.23
72 | 50 | 501 | 61 | LDB | 46.3 | 59 | 50 | 75 | 22.63 | 2.25
72 | 50 | 501 | 61 | LWB | 44.6 | 59 | 50 | 77 | 22.49 | 2.26
72 | 50 | 501 | 61 | kW | 1.04 | 59 | 50 | 81 | 22.2 | 2.28
77 | 50 | 501 | 64 | MBh | 22.49 | 47 | 43 | 59 | 22.72 | 2.1
77 | 50 | 501 | 64 | S/T | 0.636 | 47 | 43 | 70 | 21.8 | 2.15
77 | 50 | 501 | 64 | ∆T | 26.4 | 47 | 43 | 72 | 21.66 | 2.16
77 | 50 | 501 | 64 | LDB | 50.6 | 47 | 43 | 75 | 21.36 | 2.18
77 | 50 | 501 | 64 | LWB | 48 | 47 | 43 | 77 | 21.21 | 2.19
77 | 50 | 501 | 64 | kW | 1.05 | 47 | 43 | 81 | 20.91 | 2.21
80 | 50 | 501 | 67 | MBh | 23.09 | 35 | 32 | 59 | 20.88 | 2.08
80 | 50 | 501 | 67 | S/T | 0.617 | 35 | 32 | 70 | 19.91 | 2.15
80 | 50 | 501 | 67 | ∆T | 26.3 | 35 | 32 | 72 | 19.77 | 2.15
80 | 50 | 501 | 67 | LDB | 53.7 | 35 | 32 | 75 | 19.45 | 2.17
80 | 50 | 501 | 67 | LWB | 51.7 | 35 | 32 | 77 | 19.29 | 2.18
80 | 50 | 501 | 67 | kW | 1.05 | 35 | 32 | 81 | 18.98 | 2.21
86 | 50 | 501 | 72 | MBh | 24.21 | 25 | 23 | 59 | 19.37 | 2.07
86 | 50 | 501 | 72 | S/T | 0.587 | 25 | 23 | 70 | 18.34 | 2.14
86 | 50 | 501 | 72 | ∆T | 26.3 | 25 | 23 | 72 | 18.19 | 2.15
86 | 50 | 501 | 72 | LDB | 59.7 | 25 | 23 | 75 | 17.85 | 2.17
86 | 50 | 501 | 72 | LWB | 57.7 | 25 | 23 | 77 | 17.69 | 2.18
86 | 50 | 501 | 72 | kW | 1.06 | 25 | 23 | 81 | 17.35 | 2.2
90 | 50 | 501 | 75 | MBh | 25.08 | 16 | 14 | 59 | 17.88 | 2.06
90 | 50 | 501 | 75 | S/T | 0.548 | 16 | 14 | 70 | 16.77 | 2.13
90 | 50 | 501 | 75 | ∆T | 25.4 | 16 | 14 | 72 | 16.61 | 2.14
90 | 50 | 501 | 75 | LDB | 64.6 | 16 | 14 | 75 | 16.25 | 2.16
90 | 50 | 501 | 75 | LWB | 61.2 | 16 | 14 | 77 | 16.06 | 2.17
90 | 50 | 501 | 75 | kW | 1.07 | 16 | 14 | 81 | 15.7 | 2.19
68 | 68 | 501 | 57 | MBh | 17.9 | 5 | 5 | 59 | 16.42 | 2.05
68 | 68 | 501 | 57 | S/T | 0.704 | 5 | 5 | 70 | 15.2 | 2.12
68 | 68 | 501 | 57 | ∆T | 23.3 | 5 | 5 | 72 | 15.02 | 2.13
68 | 68 | 501 | 57 | LDB | 44.7 | 5 | 5 | 75 | 14.62 | 2.15
68 | 68 | 501 | 57 | LWB | 42.6 | 5 | 5 | 77 | 14.42 | 2.17
68 | 68 | 501 | 57 | kW | 1.16 | 5 | 5 | 81 | 14.02 | 2.19
72 | 68 | 501 | 61 | MBh | 19.88
72 | 68 | 501 | 61 | S/T | 0.653
72 | 68 | 501 | 61 | ∆T | 24
72 | 68 | 501 | 61 | LDB | 48
72 | 68 | 501 | 61 | LWB | 46.2
72 | 68 | 501 | 61 | kW | 1.29
77 | 68 | 501 | 64 | MBh | 20.74
77 | 68 | 501 | 64 | S/T | 0.648
77 | 68 | 501 | 64 | ∆T | 24.8
77 | 68 | 501 | 64 | LDB | 52.2
77 | 68 | 501 | 64 | LWB | 49.5
77 | 68 | 501 | 64 | kW | 1.29
80 | 68 | 501 | 67 | MBh | 21.35
80 | 68 | 501 | 67 | S/T | 0.63
80 | 68 | 501 | 67 | ∆T | 24.8
80 | 68 | 501 | 67 | LDB | 55.2
80 | 68 | 501 | 67 | LWB | 53
80 | 68 | 501 | 67 | kW | 1.3
86 | 68 | 501 | 72 | MBh | 22.47
86 | 68 | 501 | 72 | S/T | 0.6
86 | 68 | 501 | 72 | ∆T | 24.9
86 | 68 | 501 | 72 | LDB | 61.1
86 | 68 | 501 | 72 | LWB | 58.9
86 | 68 | 501 | 72 | kW | 1.31
90 | 68 | 501 | 75 | MBh | 23.33
90 | 68 | 501 | 75 | S/T | 0.561
90 | 68 | 501 | 75 | ∆T | 24.2
90 | 68 | 501 | 75 | LDB | 65.8
90 | 68 | 501 | 75 | LWB | 62.3
90 | 68 | 501 | 75 | kW | 1.32
68 | 86 | 501 | 57 | MBh | 17.27
68 | 86 | 501 | 57 | S/T | 0.71
68 | 86 | 501 | 57 | ∆T | 22.7
68 | 86 | 501 | 57 | LDB | 45.3
68 | 86 | 501 | 57 | LWB | 43.2
68 | 86 | 501 | 57 | kW | 1.53
72 | 86 | 501 | 61 | MBh | 18.14
72 | 86 | 501 | 61 | S/T | 0.667
72 | 86 | 501 | 61 | ∆T | 22.4
72 | 86 | 501 | 61 | LDB | 49.6
72 | 86 | 501 | 61 | LWB | 47.6
72 | 86 | 501 | 61 | kW | 1.53
77 | 86 | 501 | 64 | MBh | 19
77 | 86 | 501 | 64 | S/T | 0.664
77 | 86 | 501 | 64 | ∆T | 23.3
77 | 86 | 501 | 64 | LDB | 53.7
77 | 86 | 501 | 64 | LWB | 50.8
77 | 86 | 501 | 64 | kW | 1.54
80 | 86 | 501 | 67 | MBh | 19.6
80 | 86 | 501 | 67 | S/T | 0.645
80 | 86 | 501 | 67 | ∆T | 23.4
80 | 86 | 501 | 67 | LDB | 56.6
80 | 86 | 501 | 67 | LWB | 54.3
80 | 86 | 501 | 67 | kW | 1.55
86 | 86 | 501 | 72 | MBh | 20.73
86 | 86 | 501 | 72 | S/T | 0.616
86 | 86 | 501 | 72 | ∆T | 23.6
86 | 86 | 501 | 72 | LDB | 62.4
86 | 86 | 501 | 72 | LWB | 60.1
86 | 86 | 501 | 72 | kW | 1.56
90 | 86 | 501 | 75 | MBh | 21.59
90 | 86 | 501 | 75 | S/T | 0.576
90 | 86 | 501 | 75 | ∆T | 23
90 | 86 | 501 | 75 | LDB | 67
90 | 86 | 501 | 75 | LWB | 63.4
90 | 86 | 501 | 75 | kW | 1.56
68 | 95 | 501 | 57 | MBh | 16.4
68 | 95 | 501 | 57 | S/T | 0.721
68 | 95 | 501 | 57 | ∆T | 21.8
68 | 95 | 501 | 57 | LDB | 46.2
68 | 95 | 501 | 57 | LWB | 44
68 | 95 | 501 | 57 | kW | 1.65
72 | 95 | 501 | 61 | MBh | 17.26
72 | 95 | 501 | 61 | S/T | 0.676
72 | 95 | 501 | 61 | ∆T | 21.6
72 | 95 | 501 | 61 | LDB | 50.4
72 | 95 | 501 | 61 | LWB | 48.4
72 | 95 | 501 | 61 | kW | 1.66
77 | 95 | 501 | 64 | MBh | 18.13
77 | 95 | 501 | 64 | S/T | 0.674
77 | 95 | 501 | 64 | ∆T | 22.6
77 | 95 | 501 | 64 | LDB | 54.4
77 | 95 | 501 | 64 | LWB | 51.5
77 | 95 | 501 | 64 | kW | 1.67
80 | 95 | 501 | 67 | MBh | 18.8
80 | 95 | 501 | 67 | S/T | 0.653
80 | 95 | 501 | 67 | ∆T | 22.7
80 | 95 | 501 | 67 | LDB | 57.3
80 | 95 | 501 | 67 | LWB | 54.9
80 | 95 | 501 | 67 | kW | 1.67
86 | 95 | 501 | 72 | MBh | 19.85
86 | 95 | 501 | 72 | S/T | 0.626
86 | 95 | 501 | 72 | ∆T | 23
86 | 95 | 501 | 72 | LDB | 63
86 | 95 | 501 | 72 | LWB | 60.6
86 | 95 | 501 | 72 | kW | 1.68
90 | 95 | 501 | 75 | MBh | 20.72
90 | 95 | 501 | 75 | S/T | 0.585
90 | 95 | 501 | 75 | ∆T | 22.4
90 | 95 | 501 | 75 | LDB | 67.6
90 | 95 | 501 | 75 | LWB | 63.9
90 | 95 | 501 | 75 | kW | 1.69
68 | 104 | 501 | 57 | MBh | 15.53
68 | 104 | 501 | 57 | S/T | 0.732
68 | 104 | 501 | 57 | ∆T | 21
68 | 104 | 501 | 57 | LDB | 47
68 | 104 | 501 | 57 | LWB | 44.7
68 | 104 | 501 | 57 | kW | 1.77
72 | 104 | 501 | 61 | MBh | 16.39
72 | 104 | 501 | 61 | S/T | 0.686
72 | 104 | 501 | 61 | ∆T | 20.8
72 | 104 | 501 | 61 | LDB | 51.2
72 | 104 | 501 | 61 | LWB | 49.1
72 | 104 | 501 | 61 | kW | 1.78
77 | 104 | 501 | 64 | MBh | 17.26
77 | 104 | 501 | 64 | S/T | 0.685
77 | 104 | 501 | 64 | ∆T | 21.8
77 | 104 | 501 | 64 | LDB | 55.2
77 | 104 | 501 | 64 | LWB | 52.2
77 | 104 | 501 | 64 | kW | 1.79
80 | 104 | 501 | 67 | MBh | 17.86
80 | 104 | 501 | 67 | S/T | 0.666
80 | 104 | 501 | 67 | ∆T | 22
80 | 104 | 501 | 67 | LDB | 58
80 | 104 | 501 | 67 | LWB | 55.6
80 | 104 | 501 | 67 | kW | 1.79
86 | 104 | 501 | 72 | MBh | 18.98
86 | 104 | 501 | 72 | S/T | 0.637
86 | 104 | 501 | 72 | ∆T | 22.3
86 | 104 | 501 | 72 | LDB | 63.7
86 | 104 | 501 | 72 | LWB | 61.2
86 | 104 | 501 | 72 | kW | 1.8
90 | 104 | 501 | 75 | MBh | 19.84
90 | 104 | 501 | 75 | S/T | 0.595
90 | 104 | 501 | 75 | ∆T | 21.8
90 | 104 | 501 | 75 | LDB | 68.2
90 | 104 | 501 | 75 | LWB | 64.5
90 | 104 | 501 | 75 | kW | 1.81
68 | 115 | 501 | 57 | MBh | 14.48
68 | 115 | 501 | 57 | S/T | 0.749
68 | 115 | 501 | 57 | ∆T | 20
68 | 115 | 501 | 57 | LDB | 48
68 | 115 | 501 | 57 | LWB | 45.7
68 | 115 | 501 | 57 | kW | 1.72
72 | 115 | 501 | 61 | MBh | 15.35
72 | 115 | 501 | 61 | S/T | 0.7
72 | 115 | 501 | 61 | ∆T | 19.9
72 | 115 | 501 | 61 | LDB | 52.1
72 | 115 | 501 | 61 | LWB | 49.9
72 | 115 | 501 | 61 | kW | 1.72
77 | 115 | 501 | 64 | MBh | 16.21
77 | 115 | 501 | 64 | S/T | 0.7
77 | 115 | 501 | 64 | ∆T | 21
77 | 115 | 501 | 64 | LDB | 56
77 | 115 | 501 | 64 | LWB | 53
77 | 115 | 501 | 64 | kW | 1.72
80 | 115 | 501 | 67 | MBh | 16.81
80 | 115 | 501 | 67 | S/T | 0.681
80 | 115 | 501 | 67 | ∆T | 21.2
80 | 115 | 501 | 67 | LDB | 58.8
80 | 115 | 501 | 67 | LWB | 56.3
80 | 115 | 501 | 67 | kW | 1.72
86 | 115 | 501 | 72 | MBh | 17.93
86 | 115 | 501 | 72 | S/T | 0.652
86 | 115 | 501 | 72 | ∆T | 21.6
86 | 115 | 501 | 72 | LDB | 64.4
86 | 115 | 501 | 72 | LWB | 61.8
86 | 115 | 501 | 72 | kW | 1.72
90 | 115 | 501 | 75 | MBh | 18.8
90 | 115 | 501 | 75 | S/T | 0.609
90 | 115 | 501 | 75 | ∆T | 21.1
90 | 115 | 501 | 75 | LDB | 68.9
90 | 115 | 501 | 75 | LWB | 65.1
90 | 115 | 501 | 75 | kW | 1.72

## RZA18AAVJU - FAA18AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 512 | 57 | MBh | 11.7 | 64 | 60 | 61 | 24 | 2.06
68 | 23 | 512 | 57 | S/T | 0.872 | 64 | 60 | 65 | 22.2 | 1.88
68 | 23 | 512 | 57 | ∆T | 18.4 | 64 | 60 | 68 | 20.9 | 1.75
68 | 23 | 512 | 57 | LDB | 49.6 | 64 | 60 | 70 | 20 | 1.66
68 | 23 | 512 | 57 | LWB | 48.2 | 64 | 60 | 72 | 19.1 | 1.58
68 | 23 | 512 | 57 | kW | 0.41 | 64 | 60 | 75 | 17.8 | 1.45
72 | 23 | 512 | 61 | MBh | 14.2 | 60 | 56 | 61 | 24 | 2.15
72 | 23 | 512 | 61 | S/T | 0.824 | 60 | 56 | 65 | 22.2 | 1.96
72 | 23 | 512 | 61 | ∆T | 21.2 | 60 | 56 | 68 | 20.9 | 1.82
72 | 23 | 512 | 61 | LDB | 50.8 | 60 | 56 | 70 | 20 | 1.73
72 | 23 | 512 | 61 | LWB | 50.8 | 60 | 56 | 72 | 19.1 | 1.64
72 | 23 | 512 | 61 | kW | 0.51 | 60 | 56 | 75 | 17.8 | 1.51
77 | 23 | 512 | 64 | MBh | 16.1 | 57 | 53 | 61 | 24 | 2.21
77 | 23 | 512 | 64 | S/T | 0.789 | 57 | 53 | 65 | 22.2 | 2.02
77 | 23 | 512 | 64 | ∆T | 23 | 57 | 53 | 68 | 20.9 | 1.87
77 | 23 | 512 | 64 | LDB | 54 | 57 | 53 | 70 | 20 | 1.78
77 | 23 | 512 | 64 | LWB | 53.3 | 57 | 53 | 72 | 19.1 | 1.69
77 | 23 | 512 | 64 | kW | 0.58 | 57 | 53 | 75 | 17.8 | 1.55
80 | 23 | 512 | 67 | MBh | 18 | 54 | 50 | 61 | 24 | 2.29
80 | 23 | 512 | 67 | S/T | 0.761 | 54 | 50 | 65 | 22.2 | 2.08
80 | 23 | 512 | 67 | ∆T | 24.8 | 54 | 50 | 68 | 20.9 | 1.93
80 | 23 | 512 | 67 | LDB | 55.2 | 54 | 50 | 70 | 20 | 1.84
80 | 23 | 512 | 67 | LWB | 55.2 | 54 | 50 | 72 | 19.1 | 1.74
80 | 23 | 512 | 67 | kW | 0.66 | 54 | 50 | 75 | 17.8 | 1.6
84 | 23 | 512 | 70 | MBh | 19.9 | 51 | 47 | 61 | 24 | 2.36
84 | 23 | 512 | 70 | S/T | 0.719 | 51 | 47 | 65 | 22.2 | 2.15
84 | 23 | 512 | 70 | ∆T | 25.9 | 51 | 47 | 68 | 20.9 | 2
84 | 23 | 512 | 70 | LDB | 58.1 | 51 | 47 | 70 | 20 | 1.89
84 | 23 | 512 | 70 | LWB | 58.1 | 51 | 47 | 72 | 19.1 | 1.8
84 | 23 | 512 | 70 | kW | 0.74 | 51 | 47 | 75 | 17.8 | 1.65
86 | 23 | 512 | 72 | MBh | 21.2 | 47 | 43 | 61 | 24 | 2.48
86 | 23 | 512 | 72 | S/T | 0.703 | 47 | 43 | 65 | 22.2 | 2.25
86 | 23 | 512 | 72 | ∆T | 26.9 | 47 | 43 | 68 | 20.9 | 2.09
86 | 23 | 512 | 72 | LDB | 59.1 | 47 | 43 | 70 | 20 | 1.98
86 | 23 | 512 | 72 | LWB | 59.1 | 47 | 43 | 72 | 19.1 | 1.87
86 | 23 | 512 | 72 | kW | 0.8 | 47 | 43 | 75 | 17.8 | 1.72
90 | 23 | 512 | 75 | MBh | 23.1 | 44 | 40 | 61 | 24 | 2.57
90 | 23 | 512 | 75 | S/T | 0.628 | 44 | 40 | 65 | 22.2 | 2.33
90 | 23 | 512 | 75 | ∆T | 26.2 | 44 | 40 | 68 | 20.9 | 2.16
90 | 23 | 512 | 75 | LDB | 63.8 | 44 | 40 | 70 | 20 | 2.05
90 | 23 | 512 | 75 | LWB | 62.8 | 44 | 40 | 72 | 19.1 | 1.94
90 | 23 | 512 | 75 | kW | 0.88 | 44 | 40 | 75 | 17.8 | 1.78
68 | 30 | 512 | 57 | MBh | 11.7 | 39 | 36 | 61 | 24 | 2.7
68 | 30 | 512 | 57 | S/T | 0.872 | 39 | 36 | 65 | 22.2 | 2.45
68 | 30 | 512 | 57 | ∆T | 18.4 | 39 | 36 | 68 | 20.9 | 2.27
68 | 30 | 512 | 57 | LDB | 49.6 | 39 | 36 | 70 | 20 | 2.15
68 | 30 | 512 | 57 | LWB | 48.2 | 39 | 36 | 72 | 19.1 | 2.03
68 | 30 | 512 | 57 | kW | 0.43 | 39 | 36 | 75 | 17.8 | 1.87
72 | 30 | 512 | 61 | MBh | 14.2 | 35 | 32 | 61 | 24 | 2.85
72 | 30 | 512 | 61 | S/T | 0.824 | 35 | 32 | 65 | 22.2 | 2.58
72 | 30 | 512 | 61 | ∆T | 21.2 | 35 | 32 | 68 | 20.9 | 2.39
72 | 30 | 512 | 61 | LDB | 50.8 | 35 | 32 | 70 | 20 | 2.26
72 | 30 | 512 | 61 | LWB | 50.8 | 35 | 32 | 72 | 19.1 | 2.14
72 | 30 | 512 | 61 | kW | 0.52 | 35 | 32 | 75 | 17.8 | 1.96
77 | 30 | 512 | 64 | MBh | 16.1 | 30 | 28 | 61 | 24 | 3.01
77 | 30 | 512 | 64 | S/T | 0.789 | 30 | 28 | 65 | 22.2 | 2.73
77 | 30 | 512 | 64 | ∆T | 23 | 30 | 28 | 68 | 20.9 | 2.52
77 | 30 | 512 | 64 | LDB | 54 | 30 | 28 | 70 | 20 | 2.39
77 | 30 | 512 | 64 | LWB | 53.3 | 30 | 28 | 72 | 19.1 | 2.26
77 | 30 | 512 | 64 | kW | 0.6 | 30 | 28 | 75 | 17.8 | 2.06
80 | 30 | 512 | 67 | MBh | 18 | 26 | 24 | 61 | 24 | 3.19
80 | 30 | 512 | 67 | S/T | 0.761 | 26 | 24 | 65 | 22.2 | 2.89
80 | 30 | 512 | 67 | ∆T | 24.8 | 26 | 24 | 68 | 20.9 | 2.67
80 | 30 | 512 | 67 | LDB | 55.2 | 26 | 24 | 70 | 20 | 2.52
80 | 30 | 512 | 67 | LWB | 55.2 | 26 | 24 | 72 | 19.1 | 2.39
80 | 30 | 512 | 67 | kW | 0.68 | 26 | 24 | 75 | 17.8 | 2.18
84 | 30 | 512 | 70 | MBh | 19.9 | 22 | 20 | 61 | 24 | 3.39
84 | 30 | 512 | 70 | S/T | 0.719 | 22 | 20 | 65 | 22.2 | 3.07
84 | 30 | 512 | 70 | ∆T | 25.9 | 22 | 20 | 68 | 20.9 | 2.83
84 | 30 | 512 | 70 | LDB | 58.1 | 22 | 20 | 70 | 20 | 2.68
84 | 30 | 512 | 70 | LWB | 58.1 | 22 | 20 | 72 | 19.1 | 2.53
84 | 30 | 512 | 70 | kW | 0.77 | 22 | 20 | 75 | 17.8 | 2.31
86 | 30 | 512 | 72 | MBh | 21.2 | 19 | 18 | 61 | 24 | 3.37
86 | 30 | 512 | 72 | S/T | 0.703 | 19 | 18 | 65 | 22.2 | 3.17
86 | 30 | 512 | 72 | ∆T | 26.9 | 19 | 18 | 68 | 20.9 | 2.93
86 | 30 | 512 | 72 | LDB | 59.1 | 19 | 18 | 70 | 20 | 2.77
86 | 30 | 512 | 72 | LWB | 59.1 | 19 | 18 | 72 | 19.1 | 2.61
86 | 30 | 512 | 72 | kW | 0.82 | 19 | 18 | 75 | 17.8 | 2.38
90 | 30 | 512 | 75 | MBh | 23.1 | 17 | 16 | 61 | 24 | 3.35
90 | 30 | 512 | 75 | S/T | 0.628 | 17 | 16 | 65 | 22.2 | 3.31
90 | 30 | 512 | 75 | ∆T | 26.2 | 17 | 16 | 68 | 20.9 | 3.05
90 | 30 | 512 | 75 | LDB | 63.8 | 17 | 16 | 70 | 20 | 2.88
90 | 30 | 512 | 75 | LWB | 62.8 | 17 | 16 | 72 | 19.1 | 2.72
90 | 30 | 512 | 75 | kW | 0.91 | 17 | 16 | 75 | 17.8 | 2.48
68 | 40 | 512 | 57 | MBh | 11.7 | 15 | 14 | 61 | 24 | 3.33
68 | 40 | 512 | 57 | S/T | 0.872 | 15 | 14 | 65 | 22.2 | 3.39
68 | 40 | 512 | 57 | ∆T | 18.4 | 15 | 14 | 68 | 20.9 | 3.13
68 | 40 | 512 | 57 | LDB | 49.6 | 15 | 14 | 70 | 20 | 2.96
68 | 40 | 512 | 57 | LWB | 48.2 | 15 | 14 | 72 | 19.1 | 2.79
68 | 40 | 512 | 57 | kW | 0.44 | 15 | 14 | 75 | 17.8 | 2.54
72 | 40 | 512 | 61 | MBh | 14.2 | 13 | 12 | 61 | 24 | 3.31
72 | 40 | 512 | 61 | S/T | 0.824 | 13 | 12 | 65 | 22.2 | 3.37
72 | 40 | 512 | 61 | ∆T | 21.2 | 13 | 12 | 68 | 20.9 | 3.24
72 | 40 | 512 | 61 | LDB | 50.8 | 13 | 12 | 70 | 20 | 3.06
72 | 40 | 512 | 61 | LWB | 50.8 | 13 | 12 | 72 | 19.1 | 2.88
72 | 40 | 512 | 61 | kW | 0.55 | 13 | 12 | 75 | 17.8 | 2.63
77 | 40 | 512 | 64 | MBh | 16.1 | 10 | 9 | 61 | 22.5 | 3.27
77 | 40 | 512 | 64 | S/T | 0.789 | 10 | 9 | 65 | 22.2 | 3.33
77 | 40 | 512 | 64 | ∆T | 23 | 10 | 9 | 68 | 20.9 | 3.37
77 | 40 | 512 | 64 | LDB | 54 | 10 | 9 | 70 | 20 | 3.26
77 | 40 | 512 | 64 | LWB | 53.3 | 10 | 9 | 72 | 19.1 | 3.07
77 | 40 | 512 | 64 | kW | 0.63 | 10 | 9 | 75 | 17.8 | 2.8
80 | 40 | 512 | 67 | MBh | 18 | 6 | 5 | 61 | 21.1 | 3.23
80 | 40 | 512 | 67 | S/T | 0.761 | 6 | 5 | 65 | 21.1 | 3.29
80 | 40 | 512 | 67 | ∆T | 24.8 | 6 | 5 | 68 | 20.9 | 3.34
80 | 40 | 512 | 67 | LDB | 55.2 | 6 | 5 | 70 | 20 | 3.37
80 | 40 | 512 | 67 | LWB | 55.2 | 6 | 5 | 72 | 19.1 | 3.28
80 | 40 | 512 | 67 | kW | 0.72 | 6 | 5 | 75 | 17.8 | 2.99
84 | 40 | 512 | 70 | MBh | 19.9 | -2 | -2 | 61 | 18.1 | 3.12
84 | 40 | 512 | 70 | S/T | 0.719 | -2 | -2 | 65 | 18.1 | 3.19
84 | 40 | 512 | 70 | ∆T | 25.9 | -2 | -2 | 68 | 18.1 | 3.24
84 | 40 | 512 | 70 | LDB | 58.1 | -2 | -2 | 70 | 18.1 | 3.28
84 | 40 | 512 | 70 | LWB | 58.1 | -2 | -2 | 72 | 18.1 | 3.31
84 | 40 | 512 | 70 | kW | 0.8 | -2 | -2 | 75 | 17.8 | 3.36
86 | 40 | 512 | 72 | MBh | 21.2 | -4 | -4 | 61 | 17.3 | 3.09
86 | 40 | 512 | 72 | S/T | 0.703 | -4 | -4 | 65 | 17.3 | 3.16
86 | 40 | 512 | 72 | ∆T | 26.9 | -4 | -4 | 68 | 17.3 | 3.22
86 | 40 | 512 | 72 | LDB | 59.1 | -4 | -4 | 70 | 17.3 | 3.25
86 | 40 | 512 | 72 | LWB | 59.1 | -4 | -4 | 72 | 17.3 | 3.29
86 | 40 | 512 | 72 | kW | 0.86 | -4 | -4 | 75 | 17.3 | 3.34
90 | 40 | 512 | 75 | MBh | 23.1
90 | 40 | 512 | 75 | S/T | 0.628
90 | 40 | 512 | 75 | ∆T | 26.2
90 | 40 | 512 | 75 | LDB | 63.8
90 | 40 | 512 | 75 | LWB | 62.8
90 | 40 | 512 | 75 | kW | 0.95
68 | 50 | 512 | 57 | MBh | 11.7
68 | 50 | 512 | 57 | S/T | 0.872
68 | 50 | 512 | 57 | ∆T | 18.4
68 | 50 | 512 | 57 | LDB | 49.6
68 | 50 | 512 | 57 | LWB | 48.2
68 | 50 | 512 | 57 | kW | 0.46
72 | 50 | 512 | 61 | MBh | 14.2
72 | 50 | 512 | 61 | S/T | 0.824
72 | 50 | 512 | 61 | ∆T | 21.2
72 | 50 | 512 | 61 | LDB | 50.8
72 | 50 | 512 | 61 | LWB | 50.8
72 | 50 | 512 | 61 | kW | 0.57
77 | 50 | 512 | 64 | MBh | 16.1
77 | 50 | 512 | 64 | S/T | 0.789
77 | 50 | 512 | 64 | ∆T | 23
77 | 50 | 512 | 64 | LDB | 54
77 | 50 | 512 | 64 | LWB | 53.3
77 | 50 | 512 | 64 | kW | 0.66
80 | 50 | 512 | 67 | MBh | 18
80 | 50 | 512 | 67 | S/T | 0.761
80 | 50 | 512 | 67 | ∆T | 24.8
80 | 50 | 512 | 67 | LDB | 55.2
80 | 50 | 512 | 67 | LWB | 55.2
80 | 50 | 512 | 67 | kW | 0.75
84 | 50 | 512 | 70 | MBh | 19.9
84 | 50 | 512 | 70 | S/T | 0.719
84 | 50 | 512 | 70 | ∆T | 25.9
84 | 50 | 512 | 70 | LDB | 58.1
84 | 50 | 512 | 70 | LWB | 58.1
84 | 50 | 512 | 70 | kW | 0.84
86 | 50 | 512 | 72 | MBh | 21.2
86 | 50 | 512 | 72 | S/T | 0.703
86 | 50 | 512 | 72 | ∆T | 26.9
86 | 50 | 512 | 72 | LDB | 59.1
86 | 50 | 512 | 72 | LWB | 59.1
86 | 50 | 512 | 72 | kW | 0.91
90 | 50 | 512 | 75 | MBh | 23.1
90 | 50 | 512 | 75 | S/T | 0.628
90 | 50 | 512 | 75 | ∆T | 26.2
90 | 50 | 512 | 75 | LDB | 63.8
90 | 50 | 512 | 75 | LWB | 62.8
90 | 50 | 512 | 75 | kW | 1
68 | 54 | 512 | 57 | MBh | 11.7
68 | 54 | 512 | 57 | S/T | 0.872
68 | 54 | 512 | 57 | ∆T | 18.4
68 | 54 | 512 | 57 | LDB | 49.6
68 | 54 | 512 | 57 | LWB | 48.2
68 | 54 | 512 | 57 | kW | 0.47
72 | 54 | 512 | 61 | MBh | 14.2
72 | 54 | 512 | 61 | S/T | 0.824
72 | 54 | 512 | 61 | ∆T | 21.2
72 | 54 | 512 | 61 | LDB | 50.8
72 | 54 | 512 | 61 | LWB | 50.8
72 | 54 | 512 | 61 | kW | 0.59
77 | 54 | 512 | 64 | MBh | 16.1
77 | 54 | 512 | 64 | S/T | 0.789
77 | 54 | 512 | 64 | ∆T | 23
77 | 54 | 512 | 64 | LDB | 54
77 | 54 | 512 | 64 | LWB | 53.3
77 | 54 | 512 | 64 | kW | 0.68
80 | 54 | 512 | 67 | MBh | 18
80 | 54 | 512 | 67 | S/T | 0.761
80 | 54 | 512 | 67 | ∆T | 24.8
80 | 54 | 512 | 67 | LDB | 55.2
80 | 54 | 512 | 67 | LWB | 55.2
80 | 54 | 512 | 67 | kW | 0.77
84 | 54 | 512 | 70 | MBh | 19.9
84 | 54 | 512 | 70 | S/T | 0.719
84 | 54 | 512 | 70 | ∆T | 25.9
84 | 54 | 512 | 70 | LDB | 58.1
84 | 54 | 512 | 70 | LWB | 58.1
84 | 54 | 512 | 70 | kW | 0.86
86 | 54 | 512 | 72 | MBh | 21.2
86 | 54 | 512 | 72 | S/T | 0.703
86 | 54 | 512 | 72 | ∆T | 26.9
86 | 54 | 512 | 72 | LDB | 59.1
86 | 54 | 512 | 72 | LWB | 59.1
86 | 54 | 512 | 72 | kW | 0.93
90 | 54 | 512 | 75 | MBh | 23.1
90 | 54 | 512 | 75 | S/T | 0.628
90 | 54 | 512 | 75 | ∆T | 26.2
90 | 54 | 512 | 75 | LDB | 63.8
90 | 54 | 512 | 75 | LWB | 62.8
90 | 54 | 512 | 75 | kW | 1.02
68 | 58 | 512 | 57 | MBh | 11.7
68 | 58 | 512 | 57 | S/T | 0.872
68 | 58 | 512 | 57 | ∆T | 18.4
68 | 58 | 512 | 57 | LDB | 49.6
68 | 58 | 512 | 57 | LWB | 48.2
68 | 58 | 512 | 57 | kW | 0.48
72 | 58 | 512 | 61 | MBh | 14.2
72 | 58 | 512 | 61 | S/T | 0.824
72 | 58 | 512 | 61 | ∆T | 21.2
72 | 58 | 512 | 61 | LDB | 50.8
72 | 58 | 512 | 61 | LWB | 50.8
72 | 58 | 512 | 61 | kW | 0.6
77 | 58 | 512 | 64 | MBh | 16.1
77 | 58 | 512 | 64 | S/T | 0.789
77 | 58 | 512 | 64 | ∆T | 23
77 | 58 | 512 | 64 | LDB | 54
77 | 58 | 512 | 64 | LWB | 53.3
77 | 58 | 512 | 64 | kW | 0.69
80 | 58 | 512 | 67 | MBh | 18
80 | 58 | 512 | 67 | S/T | 0.761
80 | 58 | 512 | 67 | ∆T | 24.8
80 | 58 | 512 | 67 | LDB | 55.2
80 | 58 | 512 | 67 | LWB | 55.2
80 | 58 | 512 | 67 | kW | 0.78
84 | 58 | 512 | 70 | MBh | 19.9
84 | 58 | 512 | 70 | S/T | 0.719
84 | 58 | 512 | 70 | ∆T | 25.9
84 | 58 | 512 | 70 | LDB | 58.1
84 | 58 | 512 | 70 | LWB | 58.1
84 | 58 | 512 | 70 | kW | 0.88
86 | 58 | 512 | 72 | MBh | 21.2
86 | 58 | 512 | 72 | S/T | 0.703
86 | 58 | 512 | 72 | ∆T | 26.9
86 | 58 | 512 | 72 | LDB | 59.1
86 | 58 | 512 | 72 | LWB | 59.1
86 | 58 | 512 | 72 | kW | 0.95
90 | 58 | 512 | 75 | MBh | 22.8
90 | 58 | 512 | 75 | S/T | 0.632
90 | 58 | 512 | 75 | ∆T | 26
90 | 58 | 512 | 75 | LDB | 64
90 | 58 | 512 | 75 | LWB | 62.9
90 | 58 | 512 | 75 | kW | 1.03
68 | 62 | 512 | 57 | MBh | 11.7
68 | 62 | 512 | 57 | S/T | 0.872
68 | 62 | 512 | 57 | ∆T | 18.4
68 | 62 | 512 | 57 | LDB | 49.6
68 | 62 | 512 | 57 | LWB | 48.2
68 | 62 | 512 | 57 | kW | 0.49
72 | 62 | 512 | 61 | MBh | 14.2
72 | 62 | 512 | 61 | S/T | 0.824
72 | 62 | 512 | 61 | ∆T | 21.2
72 | 62 | 512 | 61 | LDB | 50.8
72 | 62 | 512 | 61 | LWB | 50.8
72 | 62 | 512 | 61 | kW | 0.61
77 | 62 | 512 | 64 | MBh | 16.1
77 | 62 | 512 | 64 | S/T | 0.789
77 | 62 | 512 | 64 | ∆T | 23
77 | 62 | 512 | 64 | LDB | 54
77 | 62 | 512 | 64 | LWB | 53.3
77 | 62 | 512 | 64 | kW | 0.7
80 | 62 | 512 | 67 | MBh | 18
80 | 62 | 512 | 67 | S/T | 0.761
80 | 62 | 512 | 67 | ∆T | 24.8
80 | 62 | 512 | 67 | LDB | 55.2
80 | 62 | 512 | 67 | LWB | 55.2
80 | 62 | 512 | 67 | kW | 0.8
84 | 62 | 512 | 70 | MBh | 19.9
84 | 62 | 512 | 70 | S/T | 0.719
84 | 62 | 512 | 70 | ∆T | 25.9
84 | 62 | 512 | 70 | LDB | 58.1
84 | 62 | 512 | 70 | LWB | 58.1
84 | 62 | 512 | 70 | kW | 0.9
86 | 62 | 512 | 72 | MBh | 21.2
86 | 62 | 512 | 72 | S/T | 0.703
86 | 62 | 512 | 72 | ∆T | 26.9
86 | 62 | 512 | 72 | LDB | 59.1
86 | 62 | 512 | 72 | LWB | 59.1
86 | 62 | 512 | 72 | kW | 0.97
90 | 62 | 512 | 75 | MBh | 22.5
90 | 62 | 512 | 75 | S/T | 0.631
90 | 62 | 512 | 75 | ∆T | 25.7
90 | 62 | 512 | 75 | LDB | 64.3
90 | 62 | 512 | 75 | LWB | 63.1
90 | 62 | 512 | 75 | kW | 1.02
68 | 66 | 512 | 57 | MBh | 11.7
68 | 66 | 512 | 57 | S/T | 0.872
68 | 66 | 512 | 57 | ∆T | 18.4
68 | 66 | 512 | 57 | LDB | 49.6
68 | 66 | 512 | 57 | LWB | 48.2
68 | 66 | 512 | 57 | kW | 0.5
72 | 66 | 512 | 61 | MBh | 14.2
72 | 66 | 512 | 61 | S/T | 0.824
72 | 66 | 512 | 61 | ∆T | 21.2
72 | 66 | 512 | 61 | LDB | 50.8
72 | 66 | 512 | 61 | LWB | 50.8
72 | 66 | 512 | 61 | kW | 0.62
77 | 66 | 512 | 64 | MBh | 16.1
77 | 66 | 512 | 64 | S/T | 0.789
77 | 66 | 512 | 64 | ∆T | 23
77 | 66 | 512 | 64 | LDB | 54
77 | 66 | 512 | 64 | LWB | 53.3
77 | 66 | 512 | 64 | kW | 0.72
80 | 66 | 512 | 67 | MBh | 18
80 | 66 | 512 | 67 | S/T | 0.761
80 | 66 | 512 | 67 | ∆T | 24.8
80 | 66 | 512 | 67 | LDB | 55.2
80 | 66 | 512 | 67 | LWB | 55.2
80 | 66 | 512 | 67 | kW | 0.82
84 | 66 | 512 | 70 | MBh | 19.9
84 | 66 | 512 | 70 | S/T | 0.719
84 | 66 | 512 | 70 | ∆T | 25.9
84 | 66 | 512 | 70 | LDB | 58.1
84 | 66 | 512 | 70 | LWB | 58.1
84 | 66 | 512 | 70 | kW | 0.92
86 | 66 | 512 | 72 | MBh | 21.2
86 | 66 | 512 | 72 | S/T | 0.703
86 | 66 | 512 | 72 | ∆T | 26.9
86 | 66 | 512 | 72 | LDB | 59.1
86 | 66 | 512 | 72 | LWB | 59.1
86 | 66 | 512 | 72 | kW | 0.99
90 | 66 | 512 | 75 | MBh | 22.2
90 | 66 | 512 | 75 | S/T | 0.631
90 | 66 | 512 | 75 | ∆T | 25.3
90 | 66 | 512 | 75 | LDB | 64.7
90 | 66 | 512 | 75 | LWB | 63.3
90 | 66 | 512 | 75 | kW | 1.01
68 | 70 | 512 | 57 | MBh | 11.7
68 | 70 | 512 | 57 | S/T | 0.872
68 | 70 | 512 | 57 | ∆T | 18.4
68 | 70 | 512 | 57 | LDB | 49.6
68 | 70 | 512 | 57 | LWB | 48.2
68 | 70 | 512 | 57 | kW | 0.51
72 | 70 | 512 | 61 | MBh | 14.2
72 | 70 | 512 | 61 | S/T | 0.824
72 | 70 | 512 | 61 | ∆T | 21.2
72 | 70 | 512 | 61 | LDB | 50.8
72 | 70 | 512 | 61 | LWB | 50.8
72 | 70 | 512 | 61 | kW | 0.64
77 | 70 | 512 | 64 | MBh | 16.1
77 | 70 | 512 | 64 | S/T | 0.789
77 | 70 | 512 | 64 | ∆T | 23
77 | 70 | 512 | 64 | LDB | 54
77 | 70 | 512 | 64 | LWB | 53.3
77 | 70 | 512 | 64 | kW | 0.74
80 | 70 | 512 | 67 | MBh | 18
80 | 70 | 512 | 67 | S/T | 0.761
80 | 70 | 512 | 67 | ∆T | 24.8
80 | 70 | 512 | 67 | LDB | 55.2
80 | 70 | 512 | 67 | LWB | 55.2
80 | 70 | 512 | 67 | kW | 0.84
84 | 70 | 512 | 70 | MBh | 19.9
84 | 70 | 512 | 70 | S/T | 0.719
84 | 70 | 512 | 70 | ∆T | 25.9
84 | 70 | 512 | 70 | LDB | 58.1
84 | 70 | 512 | 70 | LWB | 58.1
84 | 70 | 512 | 70 | kW | 0.94
86 | 70 | 512 | 72 | MBh | 21.2
86 | 70 | 512 | 72 | S/T | 0.703
86 | 70 | 512 | 72 | ∆T | 26.9
86 | 70 | 512 | 72 | LDB | 59.1
86 | 70 | 512 | 72 | LWB | 59.1
86 | 70 | 512 | 72 | kW | 1.01
90 | 70 | 512 | 75 | MBh | 21.8
90 | 70 | 512 | 75 | S/T | 0.628
90 | 70 | 512 | 75 | ∆T | 24.8
90 | 70 | 512 | 75 | LDB | 65.2
90 | 70 | 512 | 75 | LWB | 63.5
90 | 70 | 512 | 75 | kW | 1.01
68 | 72 | 512 | 57 | MBh | 11.7
68 | 72 | 512 | 57 | S/T | 0.872
68 | 72 | 512 | 57 | ∆T | 18.4
68 | 72 | 512 | 57 | LDB | 49.6
68 | 72 | 512 | 57 | LWB | 48.2
68 | 72 | 512 | 57 | kW | 0.52
72 | 72 | 512 | 61 | MBh | 14.2
72 | 72 | 512 | 61 | S/T | 0.824
72 | 72 | 512 | 61 | ∆T | 21.2
72 | 72 | 512 | 61 | LDB | 50.8
72 | 72 | 512 | 61 | LWB | 50.8
72 | 72 | 512 | 61 | kW | 0.65
77 | 72 | 512 | 64 | MBh | 16.1
77 | 72 | 512 | 64 | S/T | 0.789
77 | 72 | 512 | 64 | ∆T | 23
77 | 72 | 512 | 64 | LDB | 54
77 | 72 | 512 | 64 | LWB | 53.3
77 | 72 | 512 | 64 | kW | 0.74
80 | 72 | 512 | 67 | MBh | 18
80 | 72 | 512 | 67 | S/T | 0.761
80 | 72 | 512 | 67 | ∆T | 24.8
80 | 72 | 512 | 67 | LDB | 55.2
80 | 72 | 512 | 67 | LWB | 55.2
80 | 72 | 512 | 67 | kW | 0.85
84 | 72 | 512 | 70 | MBh | 19.9
84 | 72 | 512 | 70 | S/T | 0.719
84 | 72 | 512 | 70 | ∆T | 25.9
84 | 72 | 512 | 70 | LDB | 58.1
84 | 72 | 512 | 70 | LWB | 58.1
84 | 72 | 512 | 70 | kW | 0.95
86 | 72 | 512 | 72 | MBh | 21.2
86 | 72 | 512 | 72 | S/T | 0.703
86 | 72 | 512 | 72 | ∆T | 26.9
86 | 72 | 512 | 72 | LDB | 59.1
86 | 72 | 512 | 72 | LWB | 59.1
86 | 72 | 512 | 72 | kW | 1.03
90 | 72 | 512 | 75 | MBh | 21.7
90 | 72 | 512 | 75 | S/T | 0.627
90 | 72 | 512 | 75 | ∆T | 24.6
90 | 72 | 512 | 75 | LDB | 65.4
90 | 72 | 512 | 75 | LWB | 63.6
90 | 72 | 512 | 75 | kW | 1.04
68 | 75 | 512 | 57 | MBh | 11.7
68 | 75 | 512 | 57 | S/T | 0.872
68 | 75 | 512 | 57 | ∆T | 18.4
68 | 75 | 512 | 57 | LDB | 49.6
68 | 75 | 512 | 57 | LWB | 48.2
68 | 75 | 512 | 57 | kW | 0.53
72 | 75 | 512 | 61 | MBh | 14.2
72 | 75 | 512 | 61 | S/T | 0.824
72 | 75 | 512 | 61 | ∆T | 21.2
72 | 75 | 512 | 61 | LDB | 50.8
72 | 75 | 512 | 61 | LWB | 50.8
72 | 75 | 512 | 61 | kW | 0.66
77 | 75 | 512 | 64 | MBh | 16.1
77 | 75 | 512 | 64 | S/T | 0.789
77 | 75 | 512 | 64 | ∆T | 23
77 | 75 | 512 | 64 | LDB | 54
77 | 75 | 512 | 64 | LWB | 53.3
77 | 75 | 512 | 64 | kW | 0.76
80 | 75 | 512 | 67 | MBh | 18
80 | 75 | 512 | 67 | S/T | 0.761
80 | 75 | 512 | 67 | ∆T | 24.8
80 | 75 | 512 | 67 | LDB | 55.2
80 | 75 | 512 | 67 | LWB | 55.2
80 | 75 | 512 | 67 | kW | 0.87
84 | 75 | 512 | 70 | MBh | 19.9
84 | 75 | 512 | 70 | S/T | 0.719
84 | 75 | 512 | 70 | ∆T | 25.9
84 | 75 | 512 | 70 | LDB | 58.1
84 | 75 | 512 | 70 | LWB | 58.1
84 | 75 | 512 | 70 | kW | 1.01
86 | 75 | 512 | 72 | MBh | 21
86 | 75 | 512 | 72 | S/T | 0.705
86 | 75 | 512 | 72 | ∆T | 26.8
86 | 75 | 512 | 72 | LDB | 59.2
86 | 75 | 512 | 72 | LWB | 59.2
86 | 75 | 512 | 72 | kW | 1.1
90 | 75 | 512 | 75 | MBh | 21.4
90 | 75 | 512 | 75 | S/T | 0.631
90 | 75 | 512 | 75 | ∆T | 24.4
90 | 75 | 512 | 75 | LDB | 65.6
90 | 75 | 512 | 75 | LWB | 63.8
90 | 75 | 512 | 75 | kW | 1.11
68 | 79 | 512 | 57 | MBh | 11.7
68 | 79 | 512 | 57 | S/T | 0.872
68 | 79 | 512 | 57 | ∆T | 18.4
68 | 79 | 512 | 57 | LDB | 49.6
68 | 79 | 512 | 57 | LWB | 48.2
68 | 79 | 512 | 57 | kW | 0.54
72 | 79 | 512 | 61 | MBh | 14.2
72 | 79 | 512 | 61 | S/T | 0.824
72 | 79 | 512 | 61 | ∆T | 21.2
72 | 79 | 512 | 61 | LDB | 50.8
72 | 79 | 512 | 61 | LWB | 50.8
72 | 79 | 512 | 61 | kW | 0.69
77 | 79 | 512 | 64 | MBh | 16.1
77 | 79 | 512 | 64 | S/T | 0.789
77 | 79 | 512 | 64 | ∆T | 23
77 | 79 | 512 | 64 | LDB | 54
77 | 79 | 512 | 64 | LWB | 53.3
77 | 79 | 512 | 64 | kW | 0.82
80 | 79 | 512 | 67 | MBh | 18
80 | 79 | 512 | 67 | S/T | 0.761
80 | 79 | 512 | 67 | ∆T | 24.8
80 | 79 | 512 | 67 | LDB | 55.2
80 | 79 | 512 | 67 | LWB | 55.2
80 | 79 | 512 | 67 | kW | 0.97
84 | 79 | 512 | 70 | MBh | 19.9
84 | 79 | 512 | 70 | S/T | 0.719
84 | 79 | 512 | 70 | ∆T | 25.9
84 | 79 | 512 | 70 | LDB | 58.1
84 | 79 | 512 | 70 | LWB | 58.1
84 | 79 | 512 | 70 | kW | 1.13
86 | 79 | 512 | 72 | MBh | 20.7
86 | 79 | 512 | 72 | S/T | 0.705
86 | 79 | 512 | 72 | ∆T | 26.4
86 | 79 | 512 | 72 | LDB | 59.6
86 | 79 | 512 | 72 | LWB | 59.6
86 | 79 | 512 | 72 | kW | 1.19
90 | 79 | 512 | 75 | MBh | 21.1
90 | 79 | 512 | 75 | S/T | 0.63
90 | 79 | 512 | 75 | ∆T | 24.1
90 | 79 | 512 | 75 | LDB | 65.9
90 | 79 | 512 | 75 | LWB | 64
90 | 79 | 512 | 75 | kW | 1.2
68 | 83 | 512 | 57 | MBh | 11.7
68 | 83 | 512 | 57 | S/T | 0.872
68 | 83 | 512 | 57 | ∆T | 18.4
68 | 83 | 512 | 57 | LDB | 49.6
68 | 83 | 512 | 57 | LWB | 48.2
68 | 83 | 512 | 57 | kW | 0.59
72 | 83 | 512 | 61 | MBh | 14.2
72 | 83 | 512 | 61 | S/T | 0.824
72 | 83 | 512 | 61 | ∆T | 21.2
72 | 83 | 512 | 61 | LDB | 50.8
72 | 83 | 512 | 61 | LWB | 50.8
72 | 83 | 512 | 61 | kW | 0.76
77 | 83 | 512 | 64 | MBh | 16.1
77 | 83 | 512 | 64 | S/T | 0.789
77 | 83 | 512 | 64 | ∆T | 23
77 | 83 | 512 | 64 | LDB | 54
77 | 83 | 512 | 64 | LWB | 53.3
77 | 83 | 512 | 64 | kW | 0.91
80 | 83 | 512 | 67 | MBh | 18
80 | 83 | 512 | 67 | S/T | 0.761
80 | 83 | 512 | 67 | ∆T | 24.8
80 | 83 | 512 | 67 | LDB | 55.2
80 | 83 | 512 | 67 | LWB | 55.2
80 | 83 | 512 | 67 | kW | 1.07
84 | 83 | 512 | 70 | MBh | 19.9
84 | 83 | 512 | 70 | S/T | 0.719
84 | 83 | 512 | 70 | ∆T | 25.9
84 | 83 | 512 | 70 | LDB | 58.1
84 | 83 | 512 | 70 | LWB | 58.1
84 | 83 | 512 | 70 | kW | 1.24
86 | 83 | 512 | 72 | MBh | 20.4
86 | 83 | 512 | 72 | S/T | 0.701
86 | 83 | 512 | 72 | ∆T | 25.9
86 | 83 | 512 | 72 | LDB | 60.1
86 | 83 | 512 | 72 | LWB | 60.1
86 | 83 | 512 | 72 | kW | 1.27
90 | 83 | 512 | 75 | MBh | 20.7
90 | 83 | 512 | 75 | S/T | 0.628
90 | 83 | 512 | 75 | ∆T | 23.5
90 | 83 | 512 | 75 | LDB | 66.5
90 | 83 | 512 | 75 | LWB | 64.2
90 | 83 | 512 | 75 | kW | 1.28
68 | 87 | 512 | 57 | MBh | 11.7
68 | 87 | 512 | 57 | S/T | 0.872
68 | 87 | 512 | 57 | ∆T | 18.4
68 | 87 | 512 | 57 | LDB | 49.6
68 | 87 | 512 | 57 | LWB | 48.2
68 | 87 | 512 | 57 | kW | 0.64
72 | 87 | 512 | 61 | MBh | 14.2
72 | 87 | 512 | 61 | S/T | 0.824
72 | 87 | 512 | 61 | ∆T | 21.2
72 | 87 | 512 | 61 | LDB | 50.8
72 | 87 | 512 | 61 | LWB | 50.8
72 | 87 | 512 | 61 | kW | 0.84
77 | 87 | 512 | 64 | MBh | 16.1
77 | 87 | 512 | 64 | S/T | 0.789
77 | 87 | 512 | 64 | ∆T | 23
77 | 87 | 512 | 64 | LDB | 54
77 | 87 | 512 | 64 | LWB | 53.3
77 | 87 | 512 | 64 | kW | 1
80 | 87 | 512 | 67 | MBh | 18
80 | 87 | 512 | 67 | S/T | 0.761
80 | 87 | 512 | 67 | ∆T | 24.8
80 | 87 | 512 | 67 | LDB | 55.2
80 | 87 | 512 | 67 | LWB | 55.2
80 | 87 | 512 | 67 | kW | 1.18
84 | 87 | 512 | 70 | MBh | 19.8
84 | 87 | 512 | 70 | S/T | 0.717
84 | 87 | 512 | 70 | ∆T | 25.7
84 | 87 | 512 | 70 | LDB | 58.3
84 | 87 | 512 | 70 | LWB | 58.3
84 | 87 | 512 | 70 | kW | 1.36
86 | 87 | 512 | 72 | MBh | 20
86 | 87 | 512 | 72 | S/T | 0.705
86 | 87 | 512 | 72 | ∆T | 25.5
86 | 87 | 512 | 72 | LDB | 60.5
86 | 87 | 512 | 72 | LWB | 60.5
86 | 87 | 512 | 72 | kW | 1.36
90 | 87 | 512 | 75 | MBh | 20.4
90 | 87 | 512 | 75 | S/T | 0.627
90 | 87 | 512 | 75 | ∆T | 23.1
90 | 87 | 512 | 75 | LDB | 66.9
90 | 87 | 512 | 75 | LWB | 64.4
90 | 87 | 512 | 75 | kW | 1.37
68 | 91 | 512 | 57 | MBh | 11.7
68 | 91 | 512 | 57 | S/T | 0.872
68 | 91 | 512 | 57 | ∆T | 18.4
68 | 91 | 512 | 57 | LDB | 49.6
68 | 91 | 512 | 57 | LWB | 48.2
68 | 91 | 512 | 57 | kW | 0.7
72 | 91 | 512 | 61 | MBh | 14.2
72 | 91 | 512 | 61 | S/T | 0.824
72 | 91 | 512 | 61 | ∆T | 21.2
72 | 91 | 512 | 61 | LDB | 50.8
72 | 91 | 512 | 61 | LWB | 50.8
72 | 91 | 512 | 61 | kW | 0.92
77 | 91 | 512 | 64 | MBh | 16.1
77 | 91 | 512 | 64 | S/T | 0.789
77 | 91 | 512 | 64 | ∆T | 23
77 | 91 | 512 | 64 | LDB | 54
77 | 91 | 512 | 64 | LWB | 53.3
77 | 91 | 512 | 64 | kW | 1.1
80 | 91 | 512 | 67 | MBh | 18
80 | 91 | 512 | 67 | S/T | 0.761
80 | 91 | 512 | 67 | ∆T | 24.8
80 | 91 | 512 | 67 | LDB | 55.2
80 | 91 | 512 | 67 | LWB | 55.2
80 | 91 | 512 | 67 | kW | 1.29
84 | 91 | 512 | 70 | MBh | 19.4
84 | 91 | 512 | 70 | S/T | 0.716
84 | 91 | 512 | 70 | ∆T | 25.1
84 | 91 | 512 | 70 | LDB | 58.9
84 | 91 | 512 | 70 | LWB | 58.6
84 | 91 | 512 | 70 | kW | 1.44
86 | 91 | 512 | 72 | MBh | 19.7
86 | 91 | 512 | 72 | S/T | 0.706
86 | 91 | 512 | 72 | ∆T | 25.1
86 | 91 | 512 | 72 | LDB | 60.9
86 | 91 | 512 | 72 | LWB | 60.9
86 | 91 | 512 | 72 | kW | 1.45
90 | 91 | 512 | 75 | MBh | 20.1
90 | 91 | 512 | 75 | S/T | 0.627
90 | 91 | 512 | 75 | ∆T | 22.8
90 | 91 | 512 | 75 | LDB | 67.2
90 | 91 | 512 | 75 | LWB | 64.6
90 | 91 | 512 | 75 | kW | 1.46
68 | 93 | 512 | 57 | MBh | 11.7
68 | 93 | 512 | 57 | S/T | 0.872
68 | 93 | 512 | 57 | ∆T | 18.4
68 | 93 | 512 | 57 | LDB | 49.6
68 | 93 | 512 | 57 | LWB | 48.2
68 | 93 | 512 | 57 | kW | 0.73
72 | 93 | 512 | 61 | MBh | 14.2
72 | 93 | 512 | 61 | S/T | 0.824
72 | 93 | 512 | 61 | ∆T | 21.2
72 | 93 | 512 | 61 | LDB | 50.8
72 | 93 | 512 | 61 | LWB | 50.8
72 | 93 | 512 | 61 | kW | 0.96
77 | 93 | 512 | 64 | MBh | 16.1
77 | 93 | 512 | 64 | S/T | 0.789
77 | 93 | 512 | 64 | ∆T | 23
77 | 93 | 512 | 64 | LDB | 54
77 | 93 | 512 | 64 | LWB | 53.3
77 | 93 | 512 | 64 | kW | 1.15
80 | 93 | 512 | 67 | MBh | 18
80 | 93 | 512 | 67 | S/T | 0.761
80 | 93 | 512 | 67 | ∆T | 24.8
80 | 93 | 512 | 67 | LDB | 55.2
80 | 93 | 512 | 67 | LWB | 55.2
80 | 93 | 512 | 67 | kW | 1.35
84 | 93 | 512 | 70 | MBh | 19.3
84 | 93 | 512 | 70 | S/T | 0.715
84 | 93 | 512 | 70 | ∆T | 25
84 | 93 | 512 | 70 | LDB | 59
84 | 93 | 512 | 70 | LWB | 58.7
84 | 93 | 512 | 70 | kW | 1.49
86 | 93 | 512 | 72 | MBh | 19.5
86 | 93 | 512 | 72 | S/T | 0.703
86 | 93 | 512 | 72 | ∆T | 24.8
86 | 93 | 512 | 72 | LDB | 61.2
86 | 93 | 512 | 72 | LWB | 61.1
86 | 93 | 512 | 72 | kW | 1.49
90 | 93 | 512 | 75 | MBh | 19.9
90 | 93 | 512 | 75 | S/T | 0.628
90 | 93 | 512 | 75 | ∆T | 22.6
90 | 93 | 512 | 75 | LDB | 67.4
90 | 93 | 512 | 75 | LWB | 64.7
90 | 93 | 512 | 75 | kW | 1.5
68 | 95 | 512 | 57 | MBh | 11.7
68 | 95 | 512 | 57 | S/T | 0.872
68 | 95 | 512 | 57 | ∆T | 18.4
68 | 95 | 512 | 57 | LDB | 49.6
68 | 95 | 512 | 57 | LWB | 48.2
68 | 95 | 512 | 57 | kW | 0.76
72 | 95 | 512 | 61 | MBh | 14.2
72 | 95 | 512 | 61 | S/T | 0.824
72 | 95 | 512 | 61 | ∆T | 21.2
72 | 95 | 512 | 61 | LDB | 50.8
72 | 95 | 512 | 61 | LWB | 50.8
72 | 95 | 512 | 61 | kW | 1
77 | 95 | 512 | 64 | MBh | 16.1
77 | 95 | 512 | 64 | S/T | 0.789
77 | 95 | 512 | 64 | ∆T | 23
77 | 95 | 512 | 64 | LDB | 54
77 | 95 | 512 | 64 | LWB | 53.3
77 | 95 | 512 | 64 | kW | 1.2
80 | 95 | 512 | 67 | MBh | 18
80 | 95 | 512 | 67 | S/T | 0.761
80 | 95 | 512 | 67 | ∆T | 24.8
80 | 95 | 512 | 67 | LDB | 55.2
80 | 95 | 512 | 67 | LWB | 55.2
80 | 95 | 512 | 67 | kW | 1.41
84 | 95 | 512 | 70 | MBh | 19.1
84 | 95 | 512 | 70 | S/T | 0.717
84 | 95 | 512 | 70 | ∆T | 24.8
84 | 95 | 512 | 70 | LDB | 59.2
84 | 95 | 512 | 70 | LWB | 58.8
84 | 95 | 512 | 70 | kW | 1.53
86 | 95 | 512 | 72 | MBh | 19.3
86 | 95 | 512 | 72 | S/T | 0.705
86 | 95 | 512 | 72 | ∆T | 24.6
86 | 95 | 512 | 72 | LDB | 61.4
86 | 95 | 512 | 72 | LWB | 61.2
86 | 95 | 512 | 72 | kW | 1.54
90 | 95 | 512 | 75 | MBh | 19.7
90 | 95 | 512 | 75 | S/T | 0.629
90 | 95 | 512 | 75 | ∆T | 22.4
90 | 95 | 512 | 75 | LDB | 67.6
90 | 95 | 512 | 75 | LWB | 64.8
90 | 95 | 512 | 75 | kW | 1.55
68 | 99 | 512 | 57 | MBh | 11.7
68 | 99 | 512 | 57 | S/T | 0.872
68 | 99 | 512 | 57 | ∆T | 18.4
68 | 99 | 512 | 57 | LDB | 49.6
68 | 99 | 512 | 57 | LWB | 48.2
68 | 99 | 512 | 57 | kW | 0.83
72 | 99 | 512 | 61 | MBh | 14.2
72 | 99 | 512 | 61 | S/T | 0.824
72 | 99 | 512 | 61 | ∆T | 21.2
72 | 99 | 512 | 61 | LDB | 50.8
72 | 99 | 512 | 61 | LWB | 50.8
72 | 99 | 512 | 61 | kW | 1.09
77 | 99 | 512 | 64 | MBh | 16.1
77 | 99 | 512 | 64 | S/T | 0.789
77 | 99 | 512 | 64 | ∆T | 23
77 | 99 | 512 | 64 | LDB | 54
77 | 99 | 512 | 64 | LWB | 53.3
77 | 99 | 512 | 64 | kW | 1.31
80 | 99 | 512 | 67 | MBh | 18
80 | 99 | 512 | 67 | S/T | 0.761
80 | 99 | 512 | 67 | ∆T | 24.8
80 | 99 | 512 | 67 | LDB | 55.2
80 | 99 | 512 | 67 | LWB | 55.2
80 | 99 | 512 | 67 | kW | 1.55
84 | 99 | 512 | 70 | MBh | 18.8
84 | 99 | 512 | 70 | S/T | 0.718
84 | 99 | 512 | 70 | ∆T | 24.4
84 | 99 | 512 | 70 | LDB | 59.6
84 | 99 | 512 | 70 | LWB | 59
84 | 99 | 512 | 70 | kW | 1.62
86 | 99 | 512 | 72 | MBh | 19
86 | 99 | 512 | 72 | S/T | 0.705
86 | 99 | 512 | 72 | ∆T | 24.2
86 | 99 | 512 | 72 | LDB | 61.8
86 | 99 | 512 | 72 | LWB | 61.4
86 | 99 | 512 | 72 | kW | 1.62
90 | 99 | 512 | 75 | MBh | 19.4
90 | 99 | 512 | 75 | S/T | 0.629
90 | 99 | 512 | 75 | ∆T | 22.1
90 | 99 | 512 | 75 | LDB | 67.9
90 | 99 | 512 | 75 | LWB | 65
90 | 99 | 512 | 75 | kW | 1.64
68 | 103 | 512 | 57 | MBh | 11.7
68 | 103 | 512 | 57 | S/T | 0.872
68 | 103 | 512 | 57 | ∆T | 18.4
68 | 103 | 512 | 57 | LDB | 49.6
68 | 103 | 512 | 57 | LWB | 48.2
68 | 103 | 512 | 57 | kW | 0.9
72 | 103 | 512 | 61 | MBh | 14.2
72 | 103 | 512 | 61 | S/T | 0.824
72 | 103 | 512 | 61 | ∆T | 21.2
72 | 103 | 512 | 61 | LDB | 50.8
72 | 103 | 512 | 61 | LWB | 50.8
72 | 103 | 512 | 61 | kW | 1.19
77 | 103 | 512 | 64 | MBh | 16.1
77 | 103 | 512 | 64 | S/T | 0.789
77 | 103 | 512 | 64 | ∆T | 23
77 | 103 | 512 | 64 | LDB | 54
77 | 103 | 512 | 64 | LWB | 53.3
77 | 103 | 512 | 64 | kW | 1.42
80 | 103 | 512 | 67 | MBh | 18
80 | 103 | 512 | 67 | S/T | 0.761
80 | 103 | 512 | 67 | ∆T | 24.8
80 | 103 | 512 | 67 | LDB | 55.2
80 | 103 | 512 | 67 | LWB | 55.2
80 | 103 | 512 | 67 | kW | 1.68
84 | 103 | 512 | 70 | MBh | 18.4
84 | 103 | 512 | 70 | S/T | 0.717
84 | 103 | 512 | 70 | ∆T | 23.9
84 | 103 | 512 | 70 | LDB | 60.1
84 | 103 | 512 | 70 | LWB | 59.3
84 | 103 | 512 | 70 | kW | 1.71
86 | 103 | 512 | 72 | MBh | 18.7
86 | 103 | 512 | 72 | S/T | 0.706
86 | 103 | 512 | 72 | ∆T | 23.9
86 | 103 | 512 | 72 | LDB | 62.1
86 | 103 | 512 | 72 | LWB | 61.6
86 | 103 | 512 | 72 | kW | 1.71
90 | 103 | 512 | 75 | MBh | 19
90 | 103 | 512 | 75 | S/T | 0.632
90 | 103 | 512 | 75 | ∆T | 21.7
90 | 103 | 512 | 75 | LDB | 68.3
90 | 103 | 512 | 75 | LWB | 65.2
90 | 103 | 512 | 75 | kW | 1.73
68 | 106 | 512 | 57 | MBh | 11.7
68 | 106 | 512 | 57 | S/T | 0.872
68 | 106 | 512 | 57 | ∆T | 18.4
68 | 106 | 512 | 57 | LDB | 49.6
68 | 106 | 512 | 57 | LWB | 48.2
68 | 106 | 512 | 57 | kW | 0.96
72 | 106 | 512 | 61 | MBh | 14.2
72 | 106 | 512 | 61 | S/T | 0.824
72 | 106 | 512 | 61 | ∆T | 21.2
72 | 106 | 512 | 61 | LDB | 50.8
72 | 106 | 512 | 61 | LWB | 50.8
72 | 106 | 512 | 61 | kW | 1.26
77 | 106 | 512 | 64 | MBh | 16.1
77 | 106 | 512 | 64 | S/T | 0.789
77 | 106 | 512 | 64 | ∆T | 23
77 | 106 | 512 | 64 | LDB | 54
77 | 106 | 512 | 64 | LWB | 53.3
77 | 106 | 512 | 64 | kW | 1.52
80 | 106 | 512 | 67 | MBh | 17.8
80 | 106 | 512 | 67 | S/T | 0.758
80 | 106 | 512 | 67 | ∆T | 24.4
80 | 106 | 512 | 67 | LDB | 55.6
80 | 106 | 512 | 67 | LWB | 55.6
80 | 106 | 512 | 67 | kW | 1.76
84 | 106 | 512 | 70 | MBh | 18.2
84 | 106 | 512 | 70 | S/T | 0.714
84 | 106 | 512 | 70 | ∆T | 23.5
84 | 106 | 512 | 70 | LDB | 60.5
84 | 106 | 512 | 70 | LWB | 59.4
84 | 106 | 512 | 70 | kW | 1.77
86 | 106 | 512 | 72 | MBh | 18.4
86 | 106 | 512 | 72 | S/T | 0.707
86 | 106 | 512 | 72 | ∆T | 23.5
86 | 106 | 512 | 72 | LDB | 62.5
86 | 106 | 512 | 72 | LWB | 61.8
86 | 106 | 512 | 72 | kW | 1.78
90 | 106 | 512 | 75 | MBh | 18.8
90 | 106 | 512 | 75 | S/T | 0.628
90 | 106 | 512 | 75 | ∆T | 21.3
90 | 106 | 512 | 75 | LDB | 68.7
90 | 106 | 512 | 75 | LWB | 65.3
90 | 106 | 512 | 75 | kW | 1.79
68 | 110 | 512 | 57 | MBh | 11.7
68 | 110 | 512 | 57 | S/T | 0.872
68 | 110 | 512 | 57 | ∆T | 18.4
68 | 110 | 512 | 57 | LDB | 49.6
68 | 110 | 512 | 57 | LWB | 48.2
68 | 110 | 512 | 57 | kW | 1.09
72 | 110 | 512 | 61 | MBh | 14.2
72 | 110 | 512 | 61 | S/T | 0.824
72 | 110 | 512 | 61 | ∆T | 21.2
72 | 110 | 512 | 61 | LDB | 50.8
72 | 110 | 512 | 61 | LWB | 50.8
72 | 110 | 512 | 61 | kW | 1.44
77 | 110 | 512 | 64 | MBh | 16.1
77 | 110 | 512 | 64 | S/T | 0.789
77 | 110 | 512 | 64 | ∆T | 23
77 | 110 | 512 | 64 | LDB | 54
77 | 110 | 512 | 64 | LWB | 53.3
77 | 110 | 512 | 64 | kW | 1.74
80 | 110 | 512 | 67 | MBh | 17.5
80 | 110 | 512 | 67 | S/T | 0.76
80 | 110 | 512 | 67 | ∆T | 24.1
80 | 110 | 512 | 67 | LDB | 55.9
80 | 110 | 512 | 67 | LWB | 55.9
80 | 110 | 512 | 67 | kW | 1.94
84 | 110 | 512 | 70 | MBh | 17.8
84 | 110 | 512 | 70 | S/T | 0.719
84 | 110 | 512 | 70 | ∆T | 23.1
84 | 110 | 512 | 70 | LDB | 60.9
84 | 110 | 512 | 70 | LWB | 59.7
84 | 110 | 512 | 70 | kW | 1.96
86 | 110 | 512 | 72 | MBh | 18.1
86 | 110 | 512 | 72 | S/T | 0.702
86 | 110 | 512 | 72 | ∆T | 23
86 | 110 | 512 | 72 | LDB | 63
86 | 110 | 512 | 72 | LWB | 62
86 | 110 | 512 | 72 | kW | 1.97
90 | 110 | 512 | 75 | MBh | 18.1
90 | 110 | 512 | 75 | S/T | 0.63
90 | 110 | 512 | 75 | ∆T | 20.6
90 | 110 | 512 | 75 | LDB | 69.4
90 | 110 | 512 | 75 | LWB | 65.7
90 | 110 | 512 | 75 | kW | 1.97
68 | 115 | 512 | 57 | MBh | 11.7
68 | 115 | 512 | 57 | S/T | 0.872
68 | 115 | 512 | 57 | ∆T | 18.4
68 | 115 | 512 | 57 | LDB | 49.6
68 | 115 | 512 | 57 | LWB | 48.2
68 | 115 | 512 | 57 | kW | 1.28
72 | 115 | 512 | 61 | MBh | 14.2
72 | 115 | 512 | 61 | S/T | 0.824
72 | 115 | 512 | 61 | ∆T | 21.2
72 | 115 | 512 | 61 | LDB | 50.8
72 | 115 | 512 | 61 | LWB | 50.8
72 | 115 | 512 | 61 | kW | 1.69
77 | 115 | 512 | 64 | MBh | 16.1
77 | 115 | 512 | 64 | S/T | 0.789
77 | 115 | 512 | 64 | ∆T | 23
77 | 115 | 512 | 64 | LDB | 54
77 | 115 | 512 | 64 | LWB | 53.3
77 | 115 | 512 | 64 | kW | 2.04
80 | 115 | 512 | 67 | MBh | 16.8
80 | 115 | 512 | 67 | S/T | 0.762
80 | 115 | 512 | 67 | ∆T | 23.1
80 | 115 | 512 | 67 | LDB | 56.9
80 | 115 | 512 | 67 | LWB | 56.6
80 | 115 | 512 | 67 | kW | 2.18
84 | 115 | 512 | 70 | MBh | 16.8
84 | 115 | 512 | 70 | S/T | 0.72
84 | 115 | 512 | 70 | ∆T | 21.9
84 | 115 | 512 | 70 | LDB | 62.1
84 | 115 | 512 | 70 | LWB | 60.3
84 | 115 | 512 | 70 | kW | 2.18
86 | 115 | 512 | 72 | MBh | 16.8
86 | 115 | 512 | 72 | S/T | 0.708
86 | 115 | 512 | 72 | ∆T | 21.5
86 | 115 | 512 | 72 | LDB | 64.5
86 | 115 | 512 | 72 | LWB | 62.8
86 | 115 | 512 | 72 | kW | 2.18
90 | 115 | 512 | 75 | MBh | 16.8
90 | 115 | 512 | 75 | S/T | 0.631
90 | 115 | 512 | 75 | ∆T | 19.2
90 | 115 | 512 | 75 | LDB | 70.8
90 | 115 | 512 | 75 | LWB | 66.4
90 | 115 | 512 | 75 | kW | 2.18
68 | 118 | 512 | 57 | MBh | 11.7
68 | 118 | 512 | 57 | S/T | 0.872
68 | 118 | 512 | 57 | ∆T | 18.4
68 | 118 | 512 | 57 | LDB | 49.6
68 | 118 | 512 | 57 | LWB | 48.2
68 | 118 | 512 | 57 | kW | 1.4
72 | 118 | 512 | 61 | MBh | 14.2
72 | 118 | 512 | 61 | S/T | 0.824
72 | 118 | 512 | 61 | ∆T | 21.2
72 | 118 | 512 | 61 | LDB | 50.8
72 | 118 | 512 | 61 | LWB | 50.8
72 | 118 | 512 | 61 | kW | 1.85
77 | 118 | 512 | 64 | MBh | 14.3
77 | 118 | 512 | 64 | S/T | 0.79
77 | 118 | 512 | 64 | ∆T | 20.4
77 | 118 | 512 | 64 | LDB | 56.6
77 | 118 | 512 | 64 | LWB | 54.6
77 | 118 | 512 | 64 | kW | 1.88
80 | 118 | 512 | 67 | MBh | 14.3
80 | 118 | 512 | 67 | S/T | 0.762
80 | 118 | 512 | 67 | ∆T | 19.7
80 | 118 | 512 | 67 | LDB | 60.3
80 | 118 | 512 | 67 | LWB | 58.3
80 | 118 | 512 | 67 | kW | 1.88
84 | 118 | 512 | 70 | MBh | 14.3
84 | 118 | 512 | 70 | S/T | 0.72
84 | 118 | 512 | 70 | ∆T | 18.6
84 | 118 | 512 | 70 | LDB | 65.4
84 | 118 | 512 | 70 | LWB | 61.9
84 | 118 | 512 | 70 | kW | 1.88
86 | 118 | 512 | 72 | MBh | 14.3
86 | 118 | 512 | 72 | S/T | 0.706
86 | 118 | 512 | 72 | ∆T | 18.3
86 | 118 | 512 | 72 | LDB | 67.7
86 | 118 | 512 | 72 | LWB | 64.3
86 | 118 | 512 | 72 | kW | 1.88
90 | 118 | 512 | 75 | MBh | 14.3
90 | 118 | 512 | 75 | S/T | 0.631
90 | 118 | 512 | 75 | ∆T | 16.3
90 | 118 | 512 | 75 | LDB | 73.7
90 | 118 | 512 | 75 | LWB | 67.8
90 | 118 | 512 | 75 | kW | 1.88
68 | 122 | 512 | 57 | MBh | 10.7
68 | 122 | 512 | 57 | S/T | 0.875
68 | 122 | 512 | 57 | ∆T | 16.9
68 | 122 | 512 | 57 | LDB | 51.1
68 | 122 | 512 | 57 | LWB | 49
68 | 122 | 512 | 57 | kW | 1.4
72 | 122 | 512 | 61 | MBh | 10.7
72 | 122 | 512 | 61 | S/T | 0.828
72 | 122 | 512 | 61 | ∆T | 16
72 | 122 | 512 | 61 | LDB | 56
72 | 122 | 512 | 61 | LWB | 53.7
72 | 122 | 512 | 61 | kW | 1.4
77 | 122 | 512 | 64 | MBh | 10.7
77 | 122 | 512 | 64 | S/T | 0.793
77 | 122 | 512 | 64 | ∆T | 15.3
77 | 122 | 512 | 64 | LDB | 61.7
77 | 122 | 512 | 64 | LWB | 57.2
77 | 122 | 512 | 64 | kW | 1.4
80 | 122 | 512 | 67 | MBh | 10.7
80 | 122 | 512 | 67 | S/T | 0.764
80 | 122 | 512 | 67 | ∆T | 14.8
80 | 122 | 512 | 67 | LDB | 65.2
80 | 122 | 512 | 67 | LWB | 60.6
80 | 122 | 512 | 67 | kW | 1.4
84 | 122 | 512 | 70 | MBh | 10.7
84 | 122 | 512 | 70 | S/T | 0.721
84 | 122 | 512 | 70 | ∆T | 13.9
84 | 122 | 512 | 70 | LDB | 70.1
84 | 122 | 512 | 70 | LWB | 64.1
84 | 122 | 512 | 70 | kW | 1.4
86 | 122 | 512 | 72 | MBh | 10.7
86 | 122 | 512 | 72 | S/T | 0.707
86 | 122 | 512 | 72 | ∆T | 13.7
86 | 122 | 512 | 72 | LDB | 72.3
86 | 122 | 512 | 72 | LWB | 66.3
86 | 122 | 512 | 72 | kW | 1.4
90 | 122 | 512 | 75 | MBh | 10.7
90 | 122 | 512 | 75 | S/T | 0.633
90 | 122 | 512 | 75 | ∆T | 12.2
90 | 122 | 512 | 75 | LDB | 77.8
90 | 122 | 512 | 75 | LWB | 69.7
90 | 122 | 512 | 75 | kW | 1.4

## RZA24AAVJU - FAA24AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 670 | 57 | MBh | 15.6 | 64 | 60 | 61 | 32.4 | 3.09
68 | 23 | 670 | 57 | S/T | 0.865 | 64 | 60 | 65 | 30 | 2.82
68 | 23 | 670 | 57 | ∆T | 18.7 | 64 | 60 | 68 | 28.2 | 2.62
68 | 23 | 670 | 57 | LDB | 49.3 | 64 | 60 | 70 | 27 | 2.49
68 | 23 | 670 | 57 | LWB | 48 | 64 | 60 | 72 | 25.8 | 2.36
68 | 23 | 670 | 57 | kW | 0.6 | 64 | 60 | 75 | 24 | 2.18
72 | 23 | 670 | 61 | MBh | 18.9 | 60 | 56 | 61 | 32.4 | 3.21
72 | 23 | 670 | 61 | S/T | 0.81 | 60 | 56 | 65 | 30 | 2.93
72 | 23 | 670 | 61 | ∆T | 21.1 | 60 | 56 | 68 | 28.2 | 2.72
72 | 23 | 670 | 61 | LDB | 50.9 | 60 | 56 | 70 | 27 | 2.59
72 | 23 | 670 | 61 | LWB | 50.9 | 60 | 56 | 72 | 25.8 | 2.45
72 | 23 | 670 | 61 | kW | 0.73 | 60 | 56 | 75 | 24 | 2.26
77 | 23 | 670 | 64 | MBh | 21.5 | 57 | 53 | 61 | 32.4 | 3.32
77 | 23 | 670 | 64 | S/T | 0.767 | 57 | 53 | 65 | 30 | 3.02
77 | 23 | 670 | 64 | ∆T | 22.8 | 57 | 53 | 68 | 28.2 | 2.8
77 | 23 | 670 | 64 | LDB | 54.2 | 57 | 53 | 70 | 27 | 2.66
77 | 23 | 670 | 64 | LWB | 53.1 | 57 | 53 | 72 | 25.8 | 2.53
77 | 23 | 670 | 64 | kW | 0.84 | 57 | 53 | 75 | 24 | 2.32
80 | 23 | 670 | 67 | MBh | 24 | 54 | 50 | 61 | 32.4 | 3.42
80 | 23 | 670 | 67 | S/T | 0.75 | 54 | 50 | 65 | 30 | 3.12
80 | 23 | 670 | 67 | ∆T | 24.9 | 54 | 50 | 68 | 28.2 | 2.89
80 | 23 | 670 | 67 | LDB | 55.1 | 54 | 50 | 70 | 27 | 2.75
80 | 23 | 670 | 67 | LWB | 55.1 | 54 | 50 | 72 | 25.8 | 2.6
80 | 23 | 670 | 67 | kW | 0.96 | 54 | 50 | 75 | 24 | 2.4
84 | 23 | 670 | 70 | MBh | 26.5 | 51 | 47 | 61 | 32.4 | 3.54
84 | 23 | 670 | 70 | S/T | 0.698 | 51 | 47 | 65 | 30 | 3.22
84 | 23 | 670 | 70 | ∆T | 25.6 | 51 | 47 | 68 | 28.2 | 2.99
84 | 23 | 670 | 70 | LDB | 58.4 | 51 | 47 | 70 | 27 | 2.84
84 | 23 | 670 | 70 | LWB | 58 | 51 | 47 | 72 | 25.8 | 2.69
84 | 23 | 670 | 70 | kW | 1.07 | 51 | 47 | 75 | 24 | 2.47
86 | 23 | 670 | 72 | MBh | 28.2 | 47 | 43 | 61 | 32.4 | 3.71
86 | 23 | 670 | 72 | S/T | 0.674 | 47 | 43 | 65 | 30 | 3.37
86 | 23 | 670 | 72 | ∆T | 26.3 | 47 | 43 | 68 | 28.2 | 3.12
86 | 23 | 670 | 72 | LDB | 59.7 | 47 | 43 | 70 | 27 | 2.96
86 | 23 | 670 | 72 | LWB | 59.7 | 47 | 43 | 72 | 25.8 | 2.81
86 | 23 | 670 | 72 | kW | 1.15 | 47 | 43 | 75 | 24 | 2.58
90 | 23 | 670 | 75 | MBh | 30.7 | 44 | 40 | 61 | 32.4 | 3.83
90 | 23 | 670 | 75 | S/T | 0.612 | 44 | 40 | 65 | 30 | 3.49
90 | 23 | 670 | 75 | ∆T | 26 | 44 | 40 | 68 | 28.2 | 3.23
90 | 23 | 670 | 75 | LDB | 64 | 44 | 40 | 70 | 27 | 3.07
90 | 23 | 670 | 75 | LWB | 62.6 | 44 | 40 | 72 | 25.8 | 2.9
90 | 23 | 670 | 75 | kW | 1.27 | 44 | 40 | 75 | 24 | 2.67
68 | 30 | 670 | 57 | MBh | 15.6 | 39 | 36 | 61 | 32.4 | 3.8
68 | 30 | 670 | 57 | S/T | 0.865 | 39 | 36 | 65 | 30 | 3.67
68 | 30 | 670 | 57 | ∆T | 18.7 | 39 | 36 | 68 | 28.2 | 3.39
68 | 30 | 670 | 57 | LDB | 49.3 | 39 | 36 | 70 | 27 | 3.22
68 | 30 | 670 | 57 | LWB | 48 | 39 | 36 | 72 | 25.8 | 3.05
68 | 30 | 670 | 57 | kW | 0.62 | 39 | 36 | 75 | 24 | 2.79
72 | 30 | 670 | 61 | MBh | 18.9 | 35 | 32 | 61 | 31.2 | 3.76
72 | 30 | 670 | 61 | S/T | 0.81 | 35 | 32 | 65 | 30 | 3.82
72 | 30 | 670 | 61 | ∆T | 21.1 | 35 | 32 | 68 | 28.2 | 3.57
72 | 30 | 670 | 61 | LDB | 50.9 | 35 | 32 | 70 | 27 | 3.39
72 | 30 | 670 | 61 | LWB | 50.9 | 35 | 32 | 72 | 25.8 | 3.2
72 | 30 | 670 | 61 | kW | 0.76 | 35 | 32 | 75 | 24 | 2.93
77 | 30 | 670 | 64 | MBh | 21.5 | 30 | 28 | 61 | 29.8 | 3.72
77 | 30 | 670 | 64 | S/T | 0.767 | 30 | 28 | 65 | 29.8 | 3.78
77 | 30 | 670 | 64 | ∆T | 22.8 | 30 | 28 | 68 | 28.2 | 3.77
77 | 30 | 670 | 64 | LDB | 54.2 | 30 | 28 | 70 | 27 | 3.57
77 | 30 | 670 | 64 | LWB | 53.1 | 30 | 28 | 72 | 25.8 | 3.38
77 | 30 | 670 | 64 | kW | 0.87 | 30 | 28 | 75 | 24 | 3.09
80 | 30 | 670 | 67 | MBh | 24 | 26 | 24 | 61 | 28.4 | 3.68
80 | 30 | 670 | 67 | S/T | 0.75 | 26 | 24 | 65 | 28.4 | 3.74
80 | 30 | 670 | 67 | ∆T | 24.9 | 26 | 24 | 68 | 28.2 | 3.79
80 | 30 | 670 | 67 | LDB | 55.1 | 26 | 24 | 70 | 27 | 3.78
80 | 30 | 670 | 67 | LWB | 55.1 | 26 | 24 | 72 | 25.8 | 3.57
80 | 30 | 670 | 67 | kW | 0.99 | 26 | 24 | 75 | 24 | 3.26
84 | 30 | 670 | 70 | MBh | 26.5 | 22 | 20 | 61 | 27 | 3.63
84 | 30 | 670 | 70 | S/T | 0.698 | 22 | 20 | 65 | 27 | 3.7
84 | 30 | 670 | 70 | ∆T | 25.6 | 22 | 20 | 68 | 27 | 3.75
84 | 30 | 670 | 70 | LDB | 58.4 | 22 | 20 | 70 | 27 | 3.79
84 | 30 | 670 | 70 | LWB | 58 | 22 | 20 | 72 | 25.8 | 3.79
84 | 30 | 670 | 70 | kW | 1.11 | 22 | 20 | 75 | 24 | 3.46
86 | 30 | 670 | 72 | MBh | 28.2 | 19 | 18 | 61 | 26.3 | 3.61
86 | 30 | 670 | 72 | S/T | 0.674 | 19 | 18 | 65 | 26.3 | 3.68
86 | 30 | 670 | 72 | ∆T | 26.3 | 19 | 18 | 68 | 26.3 | 3.73
86 | 30 | 670 | 72 | LDB | 59.7 | 19 | 18 | 70 | 26.3 | 3.76
86 | 30 | 670 | 72 | LWB | 59.7 | 19 | 18 | 72 | 25.8 | 3.8
86 | 30 | 670 | 72 | kW | 1.19 | 19 | 18 | 75 | 24 | 3.57
90 | 30 | 670 | 75 | MBh | 30.7 | 17 | 16 | 61 | 25.4 | 3.57
90 | 30 | 670 | 75 | S/T | 0.612 | 17 | 16 | 65 | 25.4 | 3.65
90 | 30 | 670 | 75 | ∆T | 26 | 17 | 16 | 68 | 25.4 | 3.7
90 | 30 | 670 | 75 | LDB | 64 | 17 | 16 | 70 | 25.4 | 3.74
90 | 30 | 670 | 75 | LWB | 62.6 | 17 | 16 | 72 | 25.4 | 3.77
90 | 30 | 670 | 75 | kW | 1.31 | 17 | 16 | 75 | 24 | 3.71
68 | 40 | 670 | 57 | MBh | 15.6 | 15 | 14 | 61 | 24.8 | 3.55
68 | 40 | 670 | 57 | S/T | 0.865 | 15 | 14 | 65 | 24.8 | 3.63
68 | 40 | 670 | 57 | ∆T | 18.7 | 15 | 14 | 68 | 24.8 | 3.68
68 | 40 | 670 | 57 | LDB | 49.3 | 15 | 14 | 70 | 24.8 | 3.72
68 | 40 | 670 | 57 | LWB | 48 | 15 | 14 | 72 | 24.8 | 3.76
68 | 40 | 670 | 57 | kW | 0.64 | 15 | 14 | 75 | 24 | 3.81
72 | 40 | 670 | 61 | MBh | 18.9 | 13 | 12 | 61 | 24.1 | 3.52
72 | 40 | 670 | 61 | S/T | 0.81 | 13 | 12 | 65 | 24.1 | 3.6
72 | 40 | 670 | 61 | ∆T | 21.1 | 13 | 12 | 68 | 24.1 | 3.66
72 | 40 | 670 | 61 | LDB | 50.9 | 13 | 12 | 70 | 24.1 | 3.7
72 | 40 | 670 | 61 | LWB | 50.9 | 13 | 12 | 72 | 24.1 | 3.73
72 | 40 | 670 | 61 | kW | 0.79 | 13 | 12 | 75 | 24 | 3.79
77 | 40 | 670 | 64 | MBh | 21.5 | 10 | 9 | 61 | 22.9 | 3.47
77 | 40 | 670 | 64 | S/T | 0.767 | 10 | 9 | 65 | 22.9 | 3.55
77 | 40 | 670 | 64 | ∆T | 22.8 | 10 | 9 | 68 | 22.9 | 3.61
77 | 40 | 670 | 64 | LDB | 54.2 | 10 | 9 | 70 | 22.9 | 3.65
77 | 40 | 670 | 64 | LWB | 53.1 | 10 | 9 | 72 | 22.9 | 3.69
77 | 40 | 670 | 64 | kW | 0.91 | 10 | 9 | 75 | 22.9 | 3.75
80 | 40 | 670 | 67 | MBh | 24 | 6 | 5 | 61 | 21.6 | 3.41
80 | 40 | 670 | 67 | S/T | 0.75 | 6 | 5 | 65 | 21.6 | 3.49
80 | 40 | 670 | 67 | ∆T | 24.9 | 6 | 5 | 68 | 21.6 | 3.56
80 | 40 | 670 | 67 | LDB | 55.1 | 6 | 5 | 70 | 21.6 | 3.6
80 | 40 | 670 | 67 | LWB | 55.1 | 6 | 5 | 72 | 21.6 | 3.64
80 | 40 | 670 | 67 | kW | 1.03 | 6 | 5 | 75 | 21.6 | 3.7
84 | 40 | 670 | 70 | MBh | 26.5 | -2 | -2 | 61 | 19.1 | 3.27
84 | 40 | 670 | 70 | S/T | 0.698 | -2 | -2 | 65 | 19.1 | 3.36
84 | 40 | 670 | 70 | ∆T | 25.6 | -2 | -2 | 68 | 19.1 | 3.43
84 | 40 | 670 | 70 | LDB | 58.4 | -2 | -2 | 70 | 19.1 | 3.48
84 | 40 | 670 | 70 | LWB | 58 | -2 | -2 | 72 | 19.1 | 3.53
84 | 40 | 670 | 70 | kW | 1.16 | -2 | -2 | 75 | 19.1 | 3.6
86 | 40 | 670 | 72 | MBh | 28.2 | -4 | -4 | 61 | 18.4 | 3.23
86 | 40 | 670 | 72 | S/T | 0.674 | -4 | -4 | 65 | 18.4 | 3.32
86 | 40 | 670 | 72 | ∆T | 26.3 | -4 | -4 | 68 | 18.4 | 3.4
86 | 40 | 670 | 72 | LDB | 59.7 | -4 | -4 | 70 | 18.4 | 3.44
86 | 40 | 670 | 72 | LWB | 59.7 | -4 | -4 | 72 | 18.4 | 3.49
86 | 40 | 670 | 72 | kW | 1.25 | -4 | -4 | 75 | 18.4 | 3.57
90 | 40 | 670 | 75 | MBh | 30.7
90 | 40 | 670 | 75 | S/T | 0.612
90 | 40 | 670 | 75 | ∆T | 26
90 | 40 | 670 | 75 | LDB | 64
90 | 40 | 670 | 75 | LWB | 62.6
90 | 40 | 670 | 75 | kW | 1.38
68 | 50 | 670 | 57 | MBh | 15.6
68 | 50 | 670 | 57 | S/T | 0.865
68 | 50 | 670 | 57 | ∆T | 18.7
68 | 50 | 670 | 57 | LDB | 49.3
68 | 50 | 670 | 57 | LWB | 48
68 | 50 | 670 | 57 | kW | 0.67
72 | 50 | 670 | 61 | MBh | 18.9
72 | 50 | 670 | 61 | S/T | 0.81
72 | 50 | 670 | 61 | ∆T | 21.1
72 | 50 | 670 | 61 | LDB | 50.9
72 | 50 | 670 | 61 | LWB | 50.9
72 | 50 | 670 | 61 | kW | 0.83
77 | 50 | 670 | 64 | MBh | 21.5
77 | 50 | 670 | 64 | S/T | 0.767
77 | 50 | 670 | 64 | ∆T | 22.8
77 | 50 | 670 | 64 | LDB | 54.2
77 | 50 | 670 | 64 | LWB | 53.1
77 | 50 | 670 | 64 | kW | 0.96
80 | 50 | 670 | 67 | MBh | 24
80 | 50 | 670 | 67 | S/T | 0.75
80 | 50 | 670 | 67 | ∆T | 24.9
80 | 50 | 670 | 67 | LDB | 55.1
80 | 50 | 670 | 67 | LWB | 55.1
80 | 50 | 670 | 67 | kW | 1.09
84 | 50 | 670 | 70 | MBh | 26.5
84 | 50 | 670 | 70 | S/T | 0.698
84 | 50 | 670 | 70 | ∆T | 25.6
84 | 50 | 670 | 70 | LDB | 58.4
84 | 50 | 670 | 70 | LWB | 58
84 | 50 | 670 | 70 | kW | 1.22
86 | 50 | 670 | 72 | MBh | 28.2
86 | 50 | 670 | 72 | S/T | 0.674
86 | 50 | 670 | 72 | ∆T | 26.3
86 | 50 | 670 | 72 | LDB | 59.7
86 | 50 | 670 | 72 | LWB | 59.7
86 | 50 | 670 | 72 | kW | 1.31
90 | 50 | 670 | 75 | MBh | 30.7
90 | 50 | 670 | 75 | S/T | 0.612
90 | 50 | 670 | 75 | ∆T | 26
90 | 50 | 670 | 75 | LDB | 64
90 | 50 | 670 | 75 | LWB | 62.6
90 | 50 | 670 | 75 | kW | 1.45
68 | 54 | 670 | 57 | MBh | 15.6
68 | 54 | 670 | 57 | S/T | 0.865
68 | 54 | 670 | 57 | ∆T | 18.7
68 | 54 | 670 | 57 | LDB | 49.3
68 | 54 | 670 | 57 | LWB | 48
68 | 54 | 670 | 57 | kW | 0.69
72 | 54 | 670 | 61 | MBh | 18.9
72 | 54 | 670 | 61 | S/T | 0.81
72 | 54 | 670 | 61 | ∆T | 21.1
72 | 54 | 670 | 61 | LDB | 50.9
72 | 54 | 670 | 61 | LWB | 50.9
72 | 54 | 670 | 61 | kW | 0.85
77 | 54 | 670 | 64 | MBh | 21.5
77 | 54 | 670 | 64 | S/T | 0.767
77 | 54 | 670 | 64 | ∆T | 22.8
77 | 54 | 670 | 64 | LDB | 54.2
77 | 54 | 670 | 64 | LWB | 53.1
77 | 54 | 670 | 64 | kW | 0.98
80 | 54 | 670 | 67 | MBh | 24
80 | 54 | 670 | 67 | S/T | 0.75
80 | 54 | 670 | 67 | ∆T | 24.9
80 | 54 | 670 | 67 | LDB | 55.1
80 | 54 | 670 | 67 | LWB | 55.1
80 | 54 | 670 | 67 | kW | 1.11
84 | 54 | 670 | 70 | MBh | 26.5
84 | 54 | 670 | 70 | S/T | 0.698
84 | 54 | 670 | 70 | ∆T | 25.6
84 | 54 | 670 | 70 | LDB | 58.4
84 | 54 | 670 | 70 | LWB | 58
84 | 54 | 670 | 70 | kW | 1.25
86 | 54 | 670 | 72 | MBh | 28.2
86 | 54 | 670 | 72 | S/T | 0.674
86 | 54 | 670 | 72 | ∆T | 26.3
86 | 54 | 670 | 72 | LDB | 59.7
86 | 54 | 670 | 72 | LWB | 59.7
86 | 54 | 670 | 72 | kW | 1.34
90 | 54 | 670 | 75 | MBh | 30.7
90 | 54 | 670 | 75 | S/T | 0.612
90 | 54 | 670 | 75 | ∆T | 26
90 | 54 | 670 | 75 | LDB | 64
90 | 54 | 670 | 75 | LWB | 62.6
90 | 54 | 670 | 75 | kW | 1.48
68 | 58 | 670 | 57 | MBh | 15.6
68 | 58 | 670 | 57 | S/T | 0.865
68 | 58 | 670 | 57 | ∆T | 18.7
68 | 58 | 670 | 57 | LDB | 49.3
68 | 58 | 670 | 57 | LWB | 48
68 | 58 | 670 | 57 | kW | 0.7
72 | 58 | 670 | 61 | MBh | 18.9
72 | 58 | 670 | 61 | S/T | 0.81
72 | 58 | 670 | 61 | ∆T | 21.1
72 | 58 | 670 | 61 | LDB | 50.9
72 | 58 | 670 | 61 | LWB | 50.9
72 | 58 | 670 | 61 | kW | 0.87
77 | 58 | 670 | 64 | MBh | 21.5
77 | 58 | 670 | 64 | S/T | 0.767
77 | 58 | 670 | 64 | ∆T | 22.8
77 | 58 | 670 | 64 | LDB | 54.2
77 | 58 | 670 | 64 | LWB | 53.1
77 | 58 | 670 | 64 | kW | 1
80 | 58 | 670 | 67 | MBh | 24
80 | 58 | 670 | 67 | S/T | 0.75
80 | 58 | 670 | 67 | ∆T | 24.9
80 | 58 | 670 | 67 | LDB | 55.1
80 | 58 | 670 | 67 | LWB | 55.1
80 | 58 | 670 | 67 | kW | 1.13
84 | 58 | 670 | 70 | MBh | 26.5
84 | 58 | 670 | 70 | S/T | 0.698
84 | 58 | 670 | 70 | ∆T | 25.6
84 | 58 | 670 | 70 | LDB | 58.4
84 | 58 | 670 | 70 | LWB | 58
84 | 58 | 670 | 70 | kW | 1.27
86 | 58 | 670 | 72 | MBh | 28.2
86 | 58 | 670 | 72 | S/T | 0.674
86 | 58 | 670 | 72 | ∆T | 26.3
86 | 58 | 670 | 72 | LDB | 59.7
86 | 58 | 670 | 72 | LWB | 59.7
86 | 58 | 670 | 72 | kW | 1.37
90 | 58 | 670 | 75 | MBh | 30.5
90 | 58 | 670 | 75 | S/T | 0.61
90 | 58 | 670 | 75 | ∆T | 25.7
90 | 58 | 670 | 75 | LDB | 64.3
90 | 58 | 670 | 75 | LWB | 62.6
90 | 58 | 670 | 75 | kW | 1.48
68 | 62 | 670 | 57 | MBh | 15.6
68 | 62 | 670 | 57 | S/T | 0.865
68 | 62 | 670 | 57 | ∆T | 18.7
68 | 62 | 670 | 57 | LDB | 49.3
68 | 62 | 670 | 57 | LWB | 48
68 | 62 | 670 | 57 | kW | 0.71
72 | 62 | 670 | 61 | MBh | 18.9
72 | 62 | 670 | 61 | S/T | 0.81
72 | 62 | 670 | 61 | ∆T | 21.1
72 | 62 | 670 | 61 | LDB | 50.9
72 | 62 | 670 | 61 | LWB | 50.9
72 | 62 | 670 | 61 | kW | 0.88
77 | 62 | 670 | 64 | MBh | 21.5
77 | 62 | 670 | 64 | S/T | 0.767
77 | 62 | 670 | 64 | ∆T | 22.8
77 | 62 | 670 | 64 | LDB | 54.2
77 | 62 | 670 | 64 | LWB | 53.1
77 | 62 | 670 | 64 | kW | 1.02
80 | 62 | 670 | 67 | MBh | 24
80 | 62 | 670 | 67 | S/T | 0.75
80 | 62 | 670 | 67 | ∆T | 24.9
80 | 62 | 670 | 67 | LDB | 55.1
80 | 62 | 670 | 67 | LWB | 55.1
80 | 62 | 670 | 67 | kW | 1.16
84 | 62 | 670 | 70 | MBh | 26.5
84 | 62 | 670 | 70 | S/T | 0.698
84 | 62 | 670 | 70 | ∆T | 25.6
84 | 62 | 670 | 70 | LDB | 58.4
84 | 62 | 670 | 70 | LWB | 58
84 | 62 | 670 | 70 | kW | 1.3
86 | 62 | 670 | 72 | MBh | 28.2
86 | 62 | 670 | 72 | S/T | 0.674
86 | 62 | 670 | 72 | ∆T | 26.3
86 | 62 | 670 | 72 | LDB | 59.7
86 | 62 | 670 | 72 | LWB | 59.7
86 | 62 | 670 | 72 | kW | 1.4
90 | 62 | 670 | 75 | MBh | 30
90 | 62 | 670 | 75 | S/T | 0.613
90 | 62 | 670 | 75 | ∆T | 25.4
90 | 62 | 670 | 75 | LDB | 64.6
90 | 62 | 670 | 75 | LWB | 62.9
90 | 62 | 670 | 75 | kW | 1.48
68 | 66 | 670 | 57 | MBh | 15.6
68 | 66 | 670 | 57 | S/T | 0.865
68 | 66 | 670 | 57 | ∆T | 18.7
68 | 66 | 670 | 57 | LDB | 49.3
68 | 66 | 670 | 57 | LWB | 48
68 | 66 | 670 | 57 | kW | 0.73
72 | 66 | 670 | 61 | MBh | 18.9
72 | 66 | 670 | 61 | S/T | 0.81
72 | 66 | 670 | 61 | ∆T | 21.1
72 | 66 | 670 | 61 | LDB | 50.9
72 | 66 | 670 | 61 | LWB | 50.9
72 | 66 | 670 | 61 | kW | 0.9
77 | 66 | 670 | 64 | MBh | 21.5
77 | 66 | 670 | 64 | S/T | 0.767
77 | 66 | 670 | 64 | ∆T | 22.8
77 | 66 | 670 | 64 | LDB | 54.2
77 | 66 | 670 | 64 | LWB | 53.1
77 | 66 | 670 | 64 | kW | 1.04
80 | 66 | 670 | 67 | MBh | 24
80 | 66 | 670 | 67 | S/T | 0.75
80 | 66 | 670 | 67 | ∆T | 24.9
80 | 66 | 670 | 67 | LDB | 55.1
80 | 66 | 670 | 67 | LWB | 55.1
80 | 66 | 670 | 67 | kW | 1.18
84 | 66 | 670 | 70 | MBh | 26.5
84 | 66 | 670 | 70 | S/T | 0.698
84 | 66 | 670 | 70 | ∆T | 25.6
84 | 66 | 670 | 70 | LDB | 58.4
84 | 66 | 670 | 70 | LWB | 58
84 | 66 | 670 | 70 | kW | 1.33
86 | 66 | 670 | 72 | MBh | 28.2
86 | 66 | 670 | 72 | S/T | 0.674
86 | 66 | 670 | 72 | ∆T | 26.3
86 | 66 | 670 | 72 | LDB | 59.7
86 | 66 | 670 | 72 | LWB | 59.7
86 | 66 | 670 | 72 | kW | 1.43
90 | 66 | 670 | 75 | MBh | 29.6
90 | 66 | 670 | 75 | S/T | 0.611
90 | 66 | 670 | 75 | ∆T | 25
90 | 66 | 670 | 75 | LDB | 65
90 | 66 | 670 | 75 | LWB | 63.1
90 | 66 | 670 | 75 | kW | 1.47
68 | 70 | 670 | 57 | MBh | 15.6
68 | 70 | 670 | 57 | S/T | 0.865
68 | 70 | 670 | 57 | ∆T | 18.7
68 | 70 | 670 | 57 | LDB | 49.3
68 | 70 | 670 | 57 | LWB | 48
68 | 70 | 670 | 57 | kW | 0.74
72 | 70 | 670 | 61 | MBh | 18.9
72 | 70 | 670 | 61 | S/T | 0.81
72 | 70 | 670 | 61 | ∆T | 21.1
72 | 70 | 670 | 61 | LDB | 50.9
72 | 70 | 670 | 61 | LWB | 50.9
72 | 70 | 670 | 61 | kW | 0.92
77 | 70 | 670 | 64 | MBh | 21.5
77 | 70 | 670 | 64 | S/T | 0.767
77 | 70 | 670 | 64 | ∆T | 22.8
77 | 70 | 670 | 64 | LDB | 54.2
77 | 70 | 670 | 64 | LWB | 53.1
77 | 70 | 670 | 64 | kW | 1.07
80 | 70 | 670 | 67 | MBh | 24
80 | 70 | 670 | 67 | S/T | 0.75
80 | 70 | 670 | 67 | ∆T | 24.9
80 | 70 | 670 | 67 | LDB | 55.1
80 | 70 | 670 | 67 | LWB | 55.1
80 | 70 | 670 | 67 | kW | 1.21
84 | 70 | 670 | 70 | MBh | 26.5
84 | 70 | 670 | 70 | S/T | 0.698
84 | 70 | 670 | 70 | ∆T | 25.6
84 | 70 | 670 | 70 | LDB | 58.4
84 | 70 | 670 | 70 | LWB | 58
84 | 70 | 670 | 70 | kW | 1.36
86 | 70 | 670 | 72 | MBh | 28.2
86 | 70 | 670 | 72 | S/T | 0.674
86 | 70 | 670 | 72 | ∆T | 26.3
86 | 70 | 670 | 72 | LDB | 59.7
86 | 70 | 670 | 72 | LWB | 59.7
86 | 70 | 670 | 72 | kW | 1.46
90 | 70 | 670 | 75 | MBh | 29.1
90 | 70 | 670 | 75 | S/T | 0.612
90 | 70 | 670 | 75 | ∆T | 24.6
90 | 70 | 670 | 75 | LDB | 65.4
90 | 70 | 670 | 75 | LWB | 63.3
90 | 70 | 670 | 75 | kW | 1.46
68 | 72 | 670 | 57 | MBh | 15.6
68 | 72 | 670 | 57 | S/T | 0.865
68 | 72 | 670 | 57 | ∆T | 18.7
68 | 72 | 670 | 57 | LDB | 49.3
68 | 72 | 670 | 57 | LWB | 48
68 | 72 | 670 | 57 | kW | 0.75
72 | 72 | 670 | 61 | MBh | 18.9
72 | 72 | 670 | 61 | S/T | 0.81
72 | 72 | 670 | 61 | ∆T | 21.1
72 | 72 | 670 | 61 | LDB | 50.9
72 | 72 | 670 | 61 | LWB | 50.9
72 | 72 | 670 | 61 | kW | 0.93
77 | 72 | 670 | 64 | MBh | 21.5
77 | 72 | 670 | 64 | S/T | 0.767
77 | 72 | 670 | 64 | ∆T | 22.8
77 | 72 | 670 | 64 | LDB | 54.2
77 | 72 | 670 | 64 | LWB | 53.1
77 | 72 | 670 | 64 | kW | 1.08
80 | 72 | 670 | 67 | MBh | 24
80 | 72 | 670 | 67 | S/T | 0.75
80 | 72 | 670 | 67 | ∆T | 24.9
80 | 72 | 670 | 67 | LDB | 55.1
80 | 72 | 670 | 67 | LWB | 55.1
80 | 72 | 670 | 67 | kW | 1.23
84 | 72 | 670 | 70 | MBh | 26.5
84 | 72 | 670 | 70 | S/T | 0.698
84 | 72 | 670 | 70 | ∆T | 25.6
84 | 72 | 670 | 70 | LDB | 58.4
84 | 72 | 670 | 70 | LWB | 58
84 | 72 | 670 | 70 | kW | 1.38
86 | 72 | 670 | 72 | MBh | 28.2
86 | 72 | 670 | 72 | S/T | 0.674
86 | 72 | 670 | 72 | ∆T | 26.3
86 | 72 | 670 | 72 | LDB | 59.7
86 | 72 | 670 | 72 | LWB | 59.7
86 | 72 | 670 | 72 | kW | 1.48
90 | 72 | 670 | 75 | MBh | 28.9
90 | 72 | 670 | 75 | S/T | 0.612
90 | 72 | 670 | 75 | ∆T | 24.5
90 | 72 | 670 | 75 | LDB | 65.5
90 | 72 | 670 | 75 | LWB | 63.4
90 | 72 | 670 | 75 | kW | 1.45
68 | 75 | 670 | 57 | MBh | 15.6
68 | 75 | 670 | 57 | S/T | 0.865
68 | 75 | 670 | 57 | ∆T | 18.7
68 | 75 | 670 | 57 | LDB | 49.3
68 | 75 | 670 | 57 | LWB | 48
68 | 75 | 670 | 57 | kW | 0.76
72 | 75 | 670 | 61 | MBh | 18.9
72 | 75 | 670 | 61 | S/T | 0.81
72 | 75 | 670 | 61 | ∆T | 21.1
72 | 75 | 670 | 61 | LDB | 50.9
72 | 75 | 670 | 61 | LWB | 50.9
72 | 75 | 670 | 61 | kW | 0.95
77 | 75 | 670 | 64 | MBh | 21.5
77 | 75 | 670 | 64 | S/T | 0.767
77 | 75 | 670 | 64 | ∆T | 22.8
77 | 75 | 670 | 64 | LDB | 54.2
77 | 75 | 670 | 64 | LWB | 53.1
77 | 75 | 670 | 64 | kW | 1.1
80 | 75 | 670 | 67 | MBh | 24
80 | 75 | 670 | 67 | S/T | 0.75
80 | 75 | 670 | 67 | ∆T | 24.9
80 | 75 | 670 | 67 | LDB | 55.1
80 | 75 | 670 | 67 | LWB | 55.1
80 | 75 | 670 | 67 | kW | 1.25
84 | 75 | 670 | 70 | MBh | 26.5
84 | 75 | 670 | 70 | S/T | 0.698
84 | 75 | 670 | 70 | ∆T | 25.6
84 | 75 | 670 | 70 | LDB | 58.4
84 | 75 | 670 | 70 | LWB | 58
84 | 75 | 670 | 70 | kW | 1.4
86 | 75 | 670 | 72 | MBh | 28
86 | 75 | 670 | 72 | S/T | 0.675
86 | 75 | 670 | 72 | ∆T | 26.1
86 | 75 | 670 | 72 | LDB | 59.9
86 | 75 | 670 | 72 | LWB | 59.9
86 | 75 | 670 | 72 | kW | 1.49
90 | 75 | 670 | 75 | MBh | 28.5
90 | 75 | 670 | 75 | S/T | 0.614
90 | 75 | 670 | 75 | ∆T | 24.2
90 | 75 | 670 | 75 | LDB | 65.8
90 | 75 | 670 | 75 | LWB | 63.6
90 | 75 | 670 | 75 | kW | 1.49
68 | 79 | 670 | 57 | MBh | 15.6
68 | 79 | 670 | 57 | S/T | 0.865
68 | 79 | 670 | 57 | ∆T | 18.7
68 | 79 | 670 | 57 | LDB | 49.3
68 | 79 | 670 | 57 | LWB | 48
68 | 79 | 670 | 57 | kW | 0.78
72 | 79 | 670 | 61 | MBh | 18.9
72 | 79 | 670 | 61 | S/T | 0.81
72 | 79 | 670 | 61 | ∆T | 21.1
72 | 79 | 670 | 61 | LDB | 50.9
72 | 79 | 670 | 61 | LWB | 50.9
72 | 79 | 670 | 61 | kW | 0.97
77 | 79 | 670 | 64 | MBh | 21.5
77 | 79 | 670 | 64 | S/T | 0.767
77 | 79 | 670 | 64 | ∆T | 22.8
77 | 79 | 670 | 64 | LDB | 54.2
77 | 79 | 670 | 64 | LWB | 53.1
77 | 79 | 670 | 64 | kW | 1.14
80 | 79 | 670 | 67 | MBh | 24
80 | 79 | 670 | 67 | S/T | 0.75
80 | 79 | 670 | 67 | ∆T | 24.9
80 | 79 | 670 | 67 | LDB | 55.1
80 | 79 | 670 | 67 | LWB | 55.1
80 | 79 | 670 | 67 | kW | 1.34
84 | 79 | 670 | 70 | MBh | 26.5
84 | 79 | 670 | 70 | S/T | 0.698
84 | 79 | 670 | 70 | ∆T | 25.6
84 | 79 | 670 | 70 | LDB | 58.4
84 | 79 | 670 | 70 | LWB | 58
84 | 79 | 670 | 70 | kW | 1.55
86 | 79 | 670 | 72 | MBh | 27.6
86 | 79 | 670 | 72 | S/T | 0.674
86 | 79 | 670 | 72 | ∆T | 25.7
86 | 79 | 670 | 72 | LDB | 60.3
86 | 79 | 670 | 72 | LWB | 60.1
86 | 79 | 670 | 72 | kW | 1.64
90 | 79 | 670 | 75 | MBh | 28.1
90 | 79 | 670 | 75 | S/T | 0.612
90 | 79 | 670 | 75 | ∆T | 23.8
90 | 79 | 670 | 75 | LDB | 66.2
90 | 79 | 670 | 75 | LWB | 63.7
90 | 79 | 670 | 75 | kW | 1.65
68 | 83 | 670 | 57 | MBh | 15.6
68 | 83 | 670 | 57 | S/T | 0.865
68 | 83 | 670 | 57 | ∆T | 18.7
68 | 83 | 670 | 57 | LDB | 49.3
68 | 83 | 670 | 57 | LWB | 48
68 | 83 | 670 | 57 | kW | 0.83
72 | 83 | 670 | 61 | MBh | 18.9
72 | 83 | 670 | 61 | S/T | 0.81
72 | 83 | 670 | 61 | ∆T | 21.1
72 | 83 | 670 | 61 | LDB | 50.9
72 | 83 | 670 | 61 | LWB | 50.9
72 | 83 | 670 | 61 | kW | 1.08
77 | 83 | 670 | 64 | MBh | 21.5
77 | 83 | 670 | 64 | S/T | 0.767
77 | 83 | 670 | 64 | ∆T | 22.8
77 | 83 | 670 | 64 | LDB | 54.2
77 | 83 | 670 | 64 | LWB | 53.1
77 | 83 | 670 | 64 | kW | 1.28
80 | 83 | 670 | 67 | MBh | 24
80 | 83 | 670 | 67 | S/T | 0.75
80 | 83 | 670 | 67 | ∆T | 24.9
80 | 83 | 670 | 67 | LDB | 55.1
80 | 83 | 670 | 67 | LWB | 55.1
80 | 83 | 670 | 67 | kW | 1.51
84 | 83 | 670 | 70 | MBh | 26.5
84 | 83 | 670 | 70 | S/T | 0.698
84 | 83 | 670 | 70 | ∆T | 25.6
84 | 83 | 670 | 70 | LDB | 58.4
84 | 83 | 670 | 70 | LWB | 58
84 | 83 | 670 | 70 | kW | 1.76
86 | 83 | 670 | 72 | MBh | 27.1
86 | 83 | 670 | 72 | S/T | 0.675
86 | 83 | 670 | 72 | ∆T | 25.3
86 | 83 | 670 | 72 | LDB | 60.7
86 | 83 | 670 | 72 | LWB | 60.3
86 | 83 | 670 | 72 | kW | 1.8
90 | 83 | 670 | 75 | MBh | 27.6
90 | 83 | 670 | 75 | S/T | 0.612
90 | 83 | 670 | 75 | ∆T | 23.4
90 | 83 | 670 | 75 | LDB | 66.6
90 | 83 | 670 | 75 | LWB | 64
90 | 83 | 670 | 75 | kW | 1.81
68 | 87 | 670 | 57 | MBh | 15.6
68 | 87 | 670 | 57 | S/T | 0.865
68 | 87 | 670 | 57 | ∆T | 18.7
68 | 87 | 670 | 57 | LDB | 49.3
68 | 87 | 670 | 57 | LWB | 48
68 | 87 | 670 | 57 | kW | 0.92
72 | 87 | 670 | 61 | MBh | 18.9
72 | 87 | 670 | 61 | S/T | 0.81
72 | 87 | 670 | 61 | ∆T | 21.1
72 | 87 | 670 | 61 | LDB | 50.9
72 | 87 | 670 | 61 | LWB | 50.9
72 | 87 | 670 | 61 | kW | 1.2
77 | 87 | 670 | 64 | MBh | 21.5
77 | 87 | 670 | 64 | S/T | 0.767
77 | 87 | 670 | 64 | ∆T | 22.8
77 | 87 | 670 | 64 | LDB | 54.2
77 | 87 | 670 | 64 | LWB | 53.1
77 | 87 | 670 | 64 | kW | 1.44
80 | 87 | 670 | 67 | MBh | 24
80 | 87 | 670 | 67 | S/T | 0.75
80 | 87 | 670 | 67 | ∆T | 24.9
80 | 87 | 670 | 67 | LDB | 55.1
80 | 87 | 670 | 67 | LWB | 55.1
80 | 87 | 670 | 67 | kW | 1.7
84 | 87 | 670 | 70 | MBh | 26.4
84 | 87 | 670 | 70 | S/T | 0.697
84 | 87 | 670 | 70 | ∆T | 25.4
84 | 87 | 670 | 70 | LDB | 58.6
84 | 87 | 670 | 70 | LWB | 58.1
84 | 87 | 670 | 70 | kW | 1.95
86 | 87 | 670 | 72 | MBh | 26.7
86 | 87 | 670 | 72 | S/T | 0.674
86 | 87 | 670 | 72 | ∆T | 24.9
86 | 87 | 670 | 72 | LDB | 61.1
86 | 87 | 670 | 72 | LWB | 60.5
86 | 87 | 670 | 72 | kW | 1.96
90 | 87 | 670 | 75 | MBh | 27.2
90 | 87 | 670 | 75 | S/T | 0.61
90 | 87 | 670 | 75 | ∆T | 22.9
90 | 87 | 670 | 75 | LDB | 67.1
90 | 87 | 670 | 75 | LWB | 64.2
90 | 87 | 670 | 75 | kW | 1.97
68 | 91 | 670 | 57 | MBh | 15.6
68 | 91 | 670 | 57 | S/T | 0.865
68 | 91 | 670 | 57 | ∆T | 18.7
68 | 91 | 670 | 57 | LDB | 49.3
68 | 91 | 670 | 57 | LWB | 48
68 | 91 | 670 | 57 | kW | 1.03
72 | 91 | 670 | 61 | MBh | 18.9
72 | 91 | 670 | 61 | S/T | 0.81
72 | 91 | 670 | 61 | ∆T | 21.1
72 | 91 | 670 | 61 | LDB | 50.9
72 | 91 | 670 | 61 | LWB | 50.9
72 | 91 | 670 | 61 | kW | 1.34
77 | 91 | 670 | 64 | MBh | 21.5
77 | 91 | 670 | 64 | S/T | 0.767
77 | 91 | 670 | 64 | ∆T | 22.8
77 | 91 | 670 | 64 | LDB | 54.2
77 | 91 | 670 | 64 | LWB | 53.1
77 | 91 | 670 | 64 | kW | 1.61
80 | 91 | 670 | 67 | MBh | 24
80 | 91 | 670 | 67 | S/T | 0.75
80 | 91 | 670 | 67 | ∆T | 24.9
80 | 91 | 670 | 67 | LDB | 55.1
80 | 91 | 670 | 67 | LWB | 55.1
80 | 91 | 670 | 67 | kW | 1.89
84 | 91 | 670 | 70 | MBh | 25.9
84 | 91 | 670 | 70 | S/T | 0.699
84 | 91 | 670 | 70 | ∆T | 25
84 | 91 | 670 | 70 | LDB | 59
84 | 91 | 670 | 70 | LWB | 58.3
84 | 91 | 670 | 70 | kW | 2.11
86 | 91 | 670 | 72 | MBh | 26.2
86 | 91 | 670 | 72 | S/T | 0.676
86 | 91 | 670 | 72 | ∆T | 24.5
86 | 91 | 670 | 72 | LDB | 61.5
86 | 91 | 670 | 72 | LWB | 60.8
86 | 91 | 670 | 72 | kW | 2.12
90 | 91 | 670 | 75 | MBh | 26.7
90 | 91 | 670 | 75 | S/T | 0.614
90 | 91 | 670 | 75 | ∆T | 22.7
90 | 91 | 670 | 75 | LDB | 67.3
90 | 91 | 670 | 75 | LWB | 64.4
90 | 91 | 670 | 75 | kW | 2.14
68 | 93 | 670 | 57 | MBh | 15.6
68 | 93 | 670 | 57 | S/T | 0.865
68 | 93 | 670 | 57 | ∆T | 18.7
68 | 93 | 670 | 57 | LDB | 49.3
68 | 93 | 670 | 57 | LWB | 48
68 | 93 | 670 | 57 | kW | 1.08
72 | 93 | 670 | 61 | MBh | 18.9
72 | 93 | 670 | 61 | S/T | 0.81
72 | 93 | 670 | 61 | ∆T | 21.1
72 | 93 | 670 | 61 | LDB | 50.9
72 | 93 | 670 | 61 | LWB | 50.9
72 | 93 | 670 | 61 | kW | 1.41
77 | 93 | 670 | 64 | MBh | 21.5
77 | 93 | 670 | 64 | S/T | 0.767
77 | 93 | 670 | 64 | ∆T | 22.8
77 | 93 | 670 | 64 | LDB | 54.2
77 | 93 | 670 | 64 | LWB | 53.1
77 | 93 | 670 | 64 | kW | 1.69
80 | 93 | 670 | 67 | MBh | 24
80 | 93 | 670 | 67 | S/T | 0.75
80 | 93 | 670 | 67 | ∆T | 24.9
80 | 93 | 670 | 67 | LDB | 55.1
80 | 93 | 670 | 67 | LWB | 55.1
80 | 93 | 670 | 67 | kW | 2
84 | 93 | 670 | 70 | MBh | 25.7
84 | 93 | 670 | 70 | S/T | 0.696
84 | 93 | 670 | 70 | ∆T | 24.7
84 | 93 | 670 | 70 | LDB | 59.3
84 | 93 | 670 | 70 | LWB | 58.5
84 | 93 | 670 | 70 | kW | 2.19
86 | 93 | 670 | 72 | MBh | 26
86 | 93 | 670 | 72 | S/T | 0.673
86 | 93 | 670 | 72 | ∆T | 24.2
86 | 93 | 670 | 72 | LDB | 61.8
86 | 93 | 670 | 72 | LWB | 60.9
86 | 93 | 670 | 72 | kW | 2.2
90 | 93 | 670 | 75 | MBh | 26.5
90 | 93 | 670 | 75 | S/T | 0.611
90 | 93 | 670 | 75 | ∆T | 22.4
90 | 93 | 670 | 75 | LDB | 67.6
90 | 93 | 670 | 75 | LWB | 64.5
90 | 93 | 670 | 75 | kW | 2.22
68 | 95 | 670 | 57 | MBh | 15.6
68 | 95 | 670 | 57 | S/T | 0.865
68 | 95 | 670 | 57 | ∆T | 18.7
68 | 95 | 670 | 57 | LDB | 49.3
68 | 95 | 670 | 57 | LWB | 48
68 | 95 | 670 | 57 | kW | 1.14
72 | 95 | 670 | 61 | MBh | 18.9
72 | 95 | 670 | 61 | S/T | 0.81
72 | 95 | 670 | 61 | ∆T | 21.1
72 | 95 | 670 | 61 | LDB | 50.9
72 | 95 | 670 | 61 | LWB | 50.9
72 | 95 | 670 | 61 | kW | 1.49
77 | 95 | 670 | 64 | MBh | 21.5
77 | 95 | 670 | 64 | S/T | 0.767
77 | 95 | 670 | 64 | ∆T | 22.8
77 | 95 | 670 | 64 | LDB | 54.2
77 | 95 | 670 | 64 | LWB | 53.1
77 | 95 | 670 | 64 | kW | 1.78
80 | 95 | 670 | 67 | MBh | 24
80 | 95 | 670 | 67 | S/T | 0.75
80 | 95 | 670 | 67 | ∆T | 24.9
80 | 95 | 670 | 67 | LDB | 55.1
80 | 95 | 670 | 67 | LWB | 55.1
80 | 95 | 670 | 67 | kW | 2.1
84 | 95 | 670 | 70 | MBh | 25.5
84 | 95 | 670 | 70 | S/T | 0.698
84 | 95 | 670 | 70 | ∆T | 24.6
84 | 95 | 670 | 70 | LDB | 59.4
84 | 95 | 670 | 70 | LWB | 58.6
84 | 95 | 670 | 70 | kW | 2.28
86 | 95 | 670 | 72 | MBh | 25.8
86 | 95 | 670 | 72 | S/T | 0.674
86 | 95 | 670 | 72 | ∆T | 24
86 | 95 | 670 | 72 | LDB | 62
86 | 95 | 670 | 72 | LWB | 61
86 | 95 | 670 | 72 | kW | 2.29
90 | 95 | 670 | 75 | MBh | 26.3
90 | 95 | 670 | 75 | S/T | 0.612
90 | 95 | 670 | 75 | ∆T | 22.2
90 | 95 | 670 | 75 | LDB | 67.8
90 | 95 | 670 | 75 | LWB | 64.6
90 | 95 | 670 | 75 | kW | 2.3
68 | 99 | 670 | 57 | MBh | 15.6
68 | 99 | 670 | 57 | S/T | 0.865
68 | 99 | 670 | 57 | ∆T | 18.7
68 | 99 | 670 | 57 | LDB | 49.3
68 | 99 | 670 | 57 | LWB | 48
68 | 99 | 670 | 57 | kW | 1.25
72 | 99 | 670 | 61 | MBh | 18.9
72 | 99 | 670 | 61 | S/T | 0.81
72 | 99 | 670 | 61 | ∆T | 21.1
72 | 99 | 670 | 61 | LDB | 50.9
72 | 99 | 670 | 61 | LWB | 50.9
72 | 99 | 670 | 61 | kW | 1.64
77 | 99 | 670 | 64 | MBh | 21.5
77 | 99 | 670 | 64 | S/T | 0.767
77 | 99 | 670 | 64 | ∆T | 22.8
77 | 99 | 670 | 64 | LDB | 54.2
77 | 99 | 670 | 64 | LWB | 53.1
77 | 99 | 670 | 64 | kW | 1.97
80 | 99 | 670 | 67 | MBh | 24
80 | 99 | 670 | 67 | S/T | 0.75
80 | 99 | 670 | 67 | ∆T | 24.9
80 | 99 | 670 | 67 | LDB | 55.1
80 | 99 | 670 | 67 | LWB | 55.1
80 | 99 | 670 | 67 | kW | 2.33
84 | 99 | 670 | 70 | MBh | 25
84 | 99 | 670 | 70 | S/T | 0.7
84 | 99 | 670 | 70 | ∆T | 24.2
84 | 99 | 670 | 70 | LDB | 59.8
84 | 99 | 670 | 70 | LWB | 58.8
84 | 99 | 670 | 70 | kW | 2.44
86 | 99 | 670 | 72 | MBh | 25.3
86 | 99 | 670 | 72 | S/T | 0.676
86 | 99 | 670 | 72 | ∆T | 23.6
86 | 99 | 670 | 72 | LDB | 62.4
86 | 99 | 670 | 72 | LWB | 61.2
86 | 99 | 670 | 72 | kW | 2.45
90 | 99 | 670 | 75 | MBh | 25.8
90 | 99 | 670 | 75 | S/T | 0.612
90 | 99 | 670 | 75 | ∆T | 21.8
90 | 99 | 670 | 75 | LDB | 68.2
90 | 99 | 670 | 75 | LWB | 64.8
90 | 99 | 670 | 75 | kW | 2.47
68 | 103 | 670 | 57 | MBh | 15.6
68 | 103 | 670 | 57 | S/T | 0.865
68 | 103 | 670 | 57 | ∆T | 18.7
68 | 103 | 670 | 57 | LDB | 49.3
68 | 103 | 670 | 57 | LWB | 48
68 | 103 | 670 | 57 | kW | 1.38
72 | 103 | 670 | 61 | MBh | 18.9
72 | 103 | 670 | 61 | S/T | 0.81
72 | 103 | 670 | 61 | ∆T | 21.1
72 | 103 | 670 | 61 | LDB | 50.9
72 | 103 | 670 | 61 | LWB | 50.9
72 | 103 | 670 | 61 | kW | 1.81
77 | 103 | 670 | 64 | MBh | 21.5
77 | 103 | 670 | 64 | S/T | 0.767
77 | 103 | 670 | 64 | ∆T | 22.8
77 | 103 | 670 | 64 | LDB | 54.2
77 | 103 | 670 | 64 | LWB | 53.1
77 | 103 | 670 | 64 | kW | 2.17
80 | 103 | 670 | 67 | MBh | 24
80 | 103 | 670 | 67 | S/T | 0.75
80 | 103 | 670 | 67 | ∆T | 24.9
80 | 103 | 670 | 67 | LDB | 55.1
80 | 103 | 670 | 67 | LWB | 55.1
80 | 103 | 670 | 67 | kW | 2.57
84 | 103 | 670 | 70 | MBh | 24.6
84 | 103 | 670 | 70 | S/T | 0.695
84 | 103 | 670 | 70 | ∆T | 23.6
84 | 103 | 670 | 70 | LDB | 60.4
84 | 103 | 670 | 70 | LWB | 59
84 | 103 | 670 | 70 | kW | 2.6
86 | 103 | 670 | 72 | MBh | 24.9
86 | 103 | 670 | 72 | S/T | 0.675
86 | 103 | 670 | 72 | ∆T | 23.2
86 | 103 | 670 | 72 | LDB | 62.8
86 | 103 | 670 | 72 | LWB | 61.4
86 | 103 | 670 | 72 | kW | 2.61
90 | 103 | 670 | 75 | MBh | 25.4
90 | 103 | 670 | 75 | S/T | 0.61
90 | 103 | 670 | 75 | ∆T | 21.4
90 | 103 | 670 | 75 | LDB | 68.6
90 | 103 | 670 | 75 | LWB | 65
90 | 103 | 670 | 75 | kW | 2.63
68 | 106 | 670 | 57 | MBh | 15.6
68 | 106 | 670 | 57 | S/T | 0.865
68 | 106 | 670 | 57 | ∆T | 18.7
68 | 106 | 670 | 57 | LDB | 49.3
68 | 106 | 670 | 57 | LWB | 48
68 | 106 | 670 | 57 | kW | 1.47
72 | 106 | 670 | 61 | MBh | 18.9
72 | 106 | 670 | 61 | S/T | 0.81
72 | 106 | 670 | 61 | ∆T | 21.1
72 | 106 | 670 | 61 | LDB | 50.9
72 | 106 | 670 | 61 | LWB | 50.9
72 | 106 | 670 | 61 | kW | 1.94
77 | 106 | 670 | 64 | MBh | 21.5
77 | 106 | 670 | 64 | S/T | 0.767
77 | 106 | 670 | 64 | ∆T | 22.8
77 | 106 | 670 | 64 | LDB | 54.2
77 | 106 | 670 | 64 | LWB | 53.1
77 | 106 | 670 | 64 | kW | 2.33
80 | 106 | 670 | 67 | MBh | 23.7
80 | 106 | 670 | 67 | S/T | 0.751
80 | 106 | 670 | 67 | ∆T | 24.6
80 | 106 | 670 | 67 | LDB | 55.4
80 | 106 | 670 | 67 | LWB | 55.4
80 | 106 | 670 | 67 | kW | 2.7
84 | 106 | 670 | 70 | MBh | 24.2
84 | 106 | 670 | 70 | S/T | 0.698
84 | 106 | 670 | 70 | ∆T | 23.4
84 | 106 | 670 | 70 | LDB | 60.6
84 | 106 | 670 | 70 | LWB | 59.2
84 | 106 | 670 | 70 | kW | 2.72
86 | 106 | 670 | 72 | MBh | 24.6
86 | 106 | 670 | 72 | S/T | 0.675
86 | 106 | 670 | 72 | ∆T | 22.9
86 | 106 | 670 | 72 | LDB | 63.1
86 | 106 | 670 | 72 | LWB | 61.5
86 | 106 | 670 | 72 | kW | 2.74
90 | 106 | 670 | 75 | MBh | 25.1
90 | 106 | 670 | 75 | S/T | 0.61
90 | 106 | 670 | 75 | ∆T | 21.1
90 | 106 | 670 | 75 | LDB | 68.9
90 | 106 | 670 | 75 | LWB | 65.1
90 | 106 | 670 | 75 | kW | 2.76
68 | 110 | 670 | 57 | MBh | 15.6
68 | 110 | 670 | 57 | S/T | 0.865
68 | 110 | 670 | 57 | ∆T | 18.7
68 | 110 | 670 | 57 | LDB | 49.3
68 | 110 | 670 | 57 | LWB | 48
68 | 110 | 670 | 57 | kW | 1.61
72 | 110 | 670 | 61 | MBh | 18.9
72 | 110 | 670 | 61 | S/T | 0.81
72 | 110 | 670 | 61 | ∆T | 21.1
72 | 110 | 670 | 61 | LDB | 50.9
72 | 110 | 670 | 61 | LWB | 50.9
72 | 110 | 670 | 61 | kW | 2.12
77 | 110 | 670 | 64 | MBh | 21.5
77 | 110 | 670 | 64 | S/T | 0.767
77 | 110 | 670 | 64 | ∆T | 22.8
77 | 110 | 670 | 64 | LDB | 54.2
77 | 110 | 670 | 64 | LWB | 53.1
77 | 110 | 670 | 64 | kW | 2.56
80 | 110 | 670 | 67 | MBh | 23.3
80 | 110 | 670 | 67 | S/T | 0.751
80 | 110 | 670 | 67 | ∆T | 24.2
80 | 110 | 670 | 67 | LDB | 55.8
80 | 110 | 670 | 67 | LWB | 55.8
80 | 110 | 670 | 67 | kW | 2.87
84 | 110 | 670 | 70 | MBh | 23.8
84 | 110 | 670 | 70 | S/T | 0.697
84 | 110 | 670 | 70 | ∆T | 22.9
84 | 110 | 670 | 70 | LDB | 61.1
84 | 110 | 670 | 70 | LWB | 59.4
84 | 110 | 670 | 70 | kW | 2.89
86 | 110 | 670 | 72 | MBh | 24.1
86 | 110 | 670 | 72 | S/T | 0.676
86 | 110 | 670 | 72 | ∆T | 22.5
86 | 110 | 670 | 72 | LDB | 63.5
86 | 110 | 670 | 72 | LWB | 61.8
86 | 110 | 670 | 72 | kW | 2.9
90 | 110 | 670 | 75 | MBh | 24.1
90 | 110 | 670 | 75 | S/T | 0.614
90 | 110 | 670 | 75 | ∆T | 20.5
90 | 110 | 670 | 75 | LDB | 69.5
90 | 110 | 670 | 75 | LWB | 65.5
90 | 110 | 670 | 75 | kW | 2.9
68 | 115 | 670 | 57 | MBh | 15.6
68 | 115 | 670 | 57 | S/T | 0.865
68 | 115 | 670 | 57 | ∆T | 18.7
68 | 115 | 670 | 57 | LDB | 49.3
68 | 115 | 670 | 57 | LWB | 48
68 | 115 | 670 | 57 | kW | 1.8
72 | 115 | 670 | 61 | MBh | 18.9
72 | 115 | 670 | 61 | S/T | 0.81
72 | 115 | 670 | 61 | ∆T | 21.1
72 | 115 | 670 | 61 | LDB | 50.9
72 | 115 | 670 | 61 | LWB | 50.9
72 | 115 | 670 | 61 | kW | 2.38
77 | 115 | 670 | 64 | MBh | 21.5
77 | 115 | 670 | 64 | S/T | 0.767
77 | 115 | 670 | 64 | ∆T | 22.8
77 | 115 | 670 | 64 | LDB | 54.2
77 | 115 | 670 | 64 | LWB | 53.1
77 | 115 | 670 | 64 | kW | 2.86
80 | 115 | 670 | 67 | MBh | 22.5
80 | 115 | 670 | 67 | S/T | 0.747
80 | 115 | 670 | 67 | ∆T | 23.2
80 | 115 | 670 | 67 | LDB | 56.8
80 | 115 | 670 | 67 | LWB | 56.3
80 | 115 | 670 | 67 | kW | 3.06
84 | 115 | 670 | 70 | MBh | 22.5
84 | 115 | 670 | 70 | S/T | 0.698
84 | 115 | 670 | 70 | ∆T | 21.7
84 | 115 | 670 | 70 | LDB | 62.3
84 | 115 | 670 | 70 | LWB | 60.1
84 | 115 | 670 | 70 | kW | 3.06
86 | 115 | 670 | 72 | MBh | 22.5
86 | 115 | 670 | 72 | S/T | 0.671
86 | 115 | 670 | 72 | ∆T | 20.9
86 | 115 | 670 | 72 | LDB | 65.1
86 | 115 | 670 | 72 | LWB | 62.5
86 | 115 | 670 | 72 | kW | 3.06
90 | 115 | 670 | 75 | MBh | 22.5
90 | 115 | 670 | 75 | S/T | 0.609
90 | 115 | 670 | 75 | ∆T | 18.9
90 | 115 | 670 | 75 | LDB | 71.1
90 | 115 | 670 | 75 | LWB | 66.2
90 | 115 | 670 | 75 | kW | 3.06
68 | 118 | 670 | 57 | MBh | 15.6
68 | 118 | 670 | 57 | S/T | 0.865
68 | 118 | 670 | 57 | ∆T | 18.7
68 | 118 | 670 | 57 | LDB | 49.3
68 | 118 | 670 | 57 | LWB | 48
68 | 118 | 670 | 57 | kW | 1.92
72 | 118 | 670 | 61 | MBh | 18.9
72 | 118 | 670 | 61 | S/T | 0.81
72 | 118 | 670 | 61 | ∆T | 21.1
72 | 118 | 670 | 61 | LDB | 50.9
72 | 118 | 670 | 61 | LWB | 50.9
72 | 118 | 670 | 61 | kW | 2.54
77 | 118 | 670 | 64 | MBh | 19.3
77 | 118 | 670 | 64 | S/T | 0.767
77 | 118 | 670 | 64 | ∆T | 20.5
77 | 118 | 670 | 64 | LDB | 56.5
77 | 118 | 670 | 64 | LWB | 54.3
77 | 118 | 670 | 64 | kW | 2.6
80 | 118 | 670 | 67 | MBh | 19.3
80 | 118 | 670 | 67 | S/T | 0.746
80 | 118 | 670 | 67 | ∆T | 19.9
80 | 118 | 670 | 67 | LDB | 60.1
80 | 118 | 670 | 67 | LWB | 58
80 | 118 | 670 | 67 | kW | 2.6
84 | 118 | 670 | 70 | MBh | 19.3
84 | 118 | 670 | 70 | S/T | 0.694
84 | 118 | 670 | 70 | ∆T | 18.5
84 | 118 | 670 | 70 | LDB | 65.5
84 | 118 | 670 | 70 | LWB | 61.6
84 | 118 | 670 | 70 | kW | 2.6
86 | 118 | 670 | 72 | MBh | 19.3
86 | 118 | 670 | 72 | S/T | 0.674
86 | 118 | 670 | 72 | ∆T | 18
86 | 118 | 670 | 72 | LDB | 68
86 | 118 | 670 | 72 | LWB | 64
86 | 118 | 670 | 72 | kW | 2.6
90 | 118 | 670 | 75 | MBh | 19.3
90 | 118 | 670 | 75 | S/T | 0.611
90 | 118 | 670 | 75 | ∆T | 16.3
90 | 118 | 670 | 75 | LDB | 73.7
90 | 118 | 670 | 75 | LWB | 67.6
90 | 118 | 670 | 75 | kW | 2.6
68 | 122 | 670 | 57 | MBh | 14.7
68 | 122 | 670 | 57 | S/T | 0.864
68 | 122 | 670 | 57 | ∆T | 17.6
68 | 122 | 670 | 57 | LDB | 50.4
68 | 122 | 670 | 57 | LWB | 48.6
68 | 122 | 670 | 57 | kW | 1.92
72 | 122 | 670 | 61 | MBh | 14.7
72 | 122 | 670 | 61 | S/T | 0.81
72 | 122 | 670 | 61 | ∆T | 16.4
72 | 122 | 670 | 61 | LDB | 55.6
72 | 122 | 670 | 61 | LWB | 53.3
72 | 122 | 670 | 61 | kW | 1.92
77 | 122 | 670 | 64 | MBh | 14.7
77 | 122 | 670 | 64 | S/T | 0.769
77 | 122 | 670 | 64 | ∆T | 15.6
77 | 122 | 670 | 64 | LDB | 61.4
77 | 122 | 670 | 64 | LWB | 56.8
77 | 122 | 670 | 64 | kW | 1.92
80 | 122 | 670 | 67 | MBh | 14.7
80 | 122 | 670 | 67 | S/T | 0.748
80 | 122 | 670 | 67 | ∆T | 15.2
80 | 122 | 670 | 67 | LDB | 64.8
80 | 122 | 670 | 67 | LWB | 60.3
80 | 122 | 670 | 67 | kW | 1.92
84 | 122 | 670 | 70 | MBh | 14.7
84 | 122 | 670 | 70 | S/T | 0.694
84 | 122 | 670 | 70 | ∆T | 14.1
84 | 122 | 670 | 70 | LDB | 69.9
84 | 122 | 670 | 70 | LWB | 63.7
84 | 122 | 670 | 70 | kW | 1.92
86 | 122 | 670 | 72 | MBh | 14.7
86 | 122 | 670 | 72 | S/T | 0.673
86 | 122 | 670 | 72 | ∆T | 13.7
86 | 122 | 670 | 72 | LDB | 72.3
86 | 122 | 670 | 72 | LWB | 66
86 | 122 | 670 | 72 | kW | 1.92
90 | 122 | 670 | 75 | MBh | 14.7
90 | 122 | 670 | 75 | S/T | 0.611
90 | 122 | 670 | 75 | ∆T | 12.4
90 | 122 | 670 | 75 | LDB | 77.6
90 | 122 | 670 | 75 | LWB | 69.5
90 | 122 | 670 | 75 | kW | 1.92

## RZA18AAVJU - FCA18AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 742 | 57 | MBh | 11.7 | 64 | 60 | 61 | 24 | 1.42
68 | 23 | 742 | 57 | S/T | 1 | 64 | 60 | 65 | 22.2 | 1.29
68 | 23 | 742 | 57 | ∆T | 14.6 | 64 | 60 | 68 | 20.9 | 1.2
68 | 23 | 742 | 57 | LDB | 53.4 | 64 | 60 | 70 | 20 | 1.15
68 | 23 | 742 | 57 | LWB | 51 | 64 | 60 | 72 | 19.1 | 1.1
68 | 23 | 742 | 57 | kW | 0.38 | 64 | 60 | 75 | 17.8 | 1.03
72 | 23 | 742 | 61 | MBh | 14.2 | 60 | 56 | 61 | 24 | 1.48
72 | 23 | 742 | 61 | S/T | 0.979 | 60 | 56 | 65 | 22.2 | 1.34
72 | 23 | 742 | 61 | ∆T | 17.3 | 60 | 56 | 68 | 20.9 | 1.25
72 | 23 | 742 | 61 | LDB | 54.7 | 60 | 56 | 70 | 20 | 1.19
72 | 23 | 742 | 61 | LWB | 54.3 | 60 | 56 | 72 | 19.1 | 1.13
72 | 23 | 742 | 61 | kW | 0.46 | 60 | 56 | 75 | 17.8 | 1.06
77 | 23 | 742 | 64 | MBh | 16.1 | 57 | 53 | 61 | 24 | 1.53
77 | 23 | 742 | 64 | S/T | 0.963 | 57 | 53 | 65 | 22.2 | 1.38
77 | 23 | 742 | 64 | ∆T | 19.3 | 57 | 53 | 68 | 20.9 | 1.28
77 | 23 | 742 | 64 | LDB | 57.7 | 57 | 53 | 70 | 20 | 1.22
77 | 23 | 742 | 64 | LWB | 56.9 | 57 | 53 | 72 | 19.1 | 1.16
77 | 23 | 742 | 64 | kW | 0.53 | 57 | 53 | 75 | 17.8 | 1.09
80 | 23 | 742 | 67 | MBh | 18 | 54 | 50 | 61 | 24 | 1.59
80 | 23 | 742 | 67 | S/T | 0.894 | 54 | 50 | 65 | 22.2 | 1.43
80 | 23 | 742 | 67 | ∆T | 20.1 | 54 | 50 | 68 | 20.9 | 1.32
80 | 23 | 742 | 67 | LDB | 59.9 | 54 | 50 | 70 | 20 | 1.26
80 | 23 | 742 | 67 | LWB | 59.5 | 54 | 50 | 72 | 19.1 | 1.2
80 | 23 | 742 | 67 | kW | 0.6 | 54 | 50 | 75 | 17.8 | 1.11
84 | 23 | 742 | 70 | MBh | 19.9 | 51 | 47 | 61 | 24 | 1.65
84 | 23 | 742 | 70 | S/T | 0.874 | 51 | 47 | 65 | 22.2 | 1.48
84 | 23 | 742 | 70 | ∆T | 21.7 | 51 | 47 | 68 | 20.9 | 1.37
84 | 23 | 742 | 70 | LDB | 62.3 | 51 | 47 | 70 | 20 | 1.3
84 | 23 | 742 | 70 | LWB | 62.2 | 51 | 47 | 72 | 19.1 | 1.23
84 | 23 | 742 | 70 | kW | 0.68 | 51 | 47 | 75 | 17.8 | 1.14
86 | 23 | 742 | 72 | MBh | 21.2 | 47 | 43 | 61 | 24 | 1.75
86 | 23 | 742 | 72 | S/T | 0.825 | 47 | 43 | 65 | 22.2 | 1.56
86 | 23 | 742 | 72 | ∆T | 21.8 | 47 | 43 | 68 | 20.9 | 1.43
86 | 23 | 742 | 72 | LDB | 64.2 | 47 | 43 | 70 | 20 | 1.36
86 | 23 | 742 | 72 | LWB | 64 | 47 | 43 | 72 | 19.1 | 1.28
86 | 23 | 742 | 72 | kW | 0.73 | 47 | 43 | 75 | 17.8 | 1.18
90 | 23 | 742 | 75 | MBh | 23.1 | 44 | 40 | 61 | 24 | 1.83
90 | 23 | 742 | 75 | S/T | 0.797 | 44 | 40 | 65 | 22.2 | 1.63
90 | 23 | 742 | 75 | ∆T | 23 | 44 | 40 | 68 | 20.9 | 1.49
90 | 23 | 742 | 75 | LDB | 67 | 44 | 40 | 70 | 20 | 1.41
90 | 23 | 742 | 75 | LWB | 66.9 | 44 | 40 | 72 | 19.1 | 1.33
90 | 23 | 742 | 75 | kW | 0.8 | 44 | 40 | 75 | 17.8 | 1.22
68 | 30 | 742 | 57 | MBh | 11.7 | 39 | 36 | 61 | 24 | 1.95
68 | 30 | 742 | 57 | S/T | 1 | 39 | 36 | 65 | 22.2 | 1.73
68 | 30 | 742 | 57 | ∆T | 14.6 | 39 | 36 | 68 | 20.9 | 1.58
68 | 30 | 742 | 57 | LDB | 53.4 | 39 | 36 | 70 | 20 | 1.48
68 | 30 | 742 | 57 | LWB | 51 | 39 | 36 | 72 | 19.1 | 1.4
68 | 30 | 742 | 57 | kW | 0.39 | 39 | 36 | 75 | 17.8 | 1.28
72 | 30 | 742 | 61 | MBh | 14.2 | 35 | 32 | 61 | 24 | 2.09
72 | 30 | 742 | 61 | S/T | 0.979 | 35 | 32 | 65 | 22.2 | 1.84
72 | 30 | 742 | 61 | ∆T | 17.3 | 35 | 32 | 68 | 20.9 | 1.67
72 | 30 | 742 | 61 | LDB | 54.7 | 35 | 32 | 70 | 20 | 1.57
72 | 30 | 742 | 61 | LWB | 54.3 | 35 | 32 | 72 | 19.1 | 1.48
72 | 30 | 742 | 61 | kW | 0.48 | 35 | 32 | 75 | 17.8 | 1.34
77 | 30 | 742 | 64 | MBh | 16.1 | 30 | 28 | 61 | 24 | 2.25
77 | 30 | 742 | 64 | S/T | 0.963 | 30 | 28 | 65 | 22.2 | 1.97
77 | 30 | 742 | 64 | ∆T | 19.3 | 30 | 28 | 68 | 20.9 | 1.79
77 | 30 | 742 | 64 | LDB | 57.7 | 30 | 28 | 70 | 20 | 1.67
77 | 30 | 742 | 64 | LWB | 56.9 | 30 | 28 | 72 | 19.1 | 1.57
77 | 30 | 742 | 64 | kW | 0.55 | 30 | 28 | 75 | 17.8 | 1.42
80 | 30 | 742 | 67 | MBh | 18 | 26 | 24 | 61 | 24 | 2.43
80 | 30 | 742 | 67 | S/T | 0.894 | 26 | 24 | 65 | 22.2 | 2.13
80 | 30 | 742 | 67 | ∆T | 20.1 | 26 | 24 | 68 | 20.9 | 1.92
80 | 30 | 742 | 67 | LDB | 59.9 | 26 | 24 | 70 | 20 | 1.79
80 | 30 | 742 | 67 | LWB | 59.5 | 26 | 24 | 72 | 19.1 | 1.67
80 | 30 | 742 | 67 | kW | 0.62 | 26 | 24 | 75 | 17.8 | 1.51
84 | 30 | 742 | 70 | MBh | 19.9 | 22 | 20 | 61 | 24 | 2.65
84 | 30 | 742 | 70 | S/T | 0.874 | 22 | 20 | 65 | 22.2 | 2.31
84 | 30 | 742 | 70 | ∆T | 21.7 | 22 | 20 | 68 | 20.9 | 2.08
84 | 30 | 742 | 70 | LDB | 62.3 | 22 | 20 | 70 | 20 | 1.94
84 | 30 | 742 | 70 | LWB | 62.2 | 22 | 20 | 72 | 19.1 | 1.8
84 | 30 | 742 | 70 | kW | 0.7 | 22 | 20 | 75 | 17.8 | 1.61
86 | 30 | 742 | 72 | MBh | 21.2 | 19 | 18 | 61 | 24 | 2.77
86 | 30 | 742 | 72 | S/T | 0.825 | 19 | 18 | 65 | 22.2 | 2.41
86 | 30 | 742 | 72 | ∆T | 21.8 | 19 | 18 | 68 | 20.9 | 2.17
86 | 30 | 742 | 72 | LDB | 64.2 | 19 | 18 | 70 | 20 | 2.01
86 | 30 | 742 | 72 | LWB | 64 | 19 | 18 | 72 | 19.1 | 1.87
86 | 30 | 742 | 72 | kW | 0.75 | 19 | 18 | 75 | 17.8 | 1.67
90 | 30 | 742 | 75 | MBh | 23.1 | 17 | 16 | 61 | 24 | 2.92
90 | 30 | 742 | 75 | S/T | 0.797 | 17 | 16 | 65 | 22.2 | 2.55
90 | 30 | 742 | 75 | ∆T | 23 | 17 | 16 | 68 | 20.9 | 2.29
90 | 30 | 742 | 75 | LDB | 67 | 17 | 16 | 70 | 20 | 2.12
90 | 30 | 742 | 75 | LWB | 66.9 | 17 | 16 | 72 | 19.1 | 1.97
90 | 30 | 742 | 75 | kW | 0.83 | 17 | 16 | 75 | 17.8 | 1.76
68 | 40 | 742 | 57 | MBh | 11.7 | 15 | 14 | 61 | 24 | 2.94
68 | 40 | 742 | 57 | S/T | 1 | 15 | 14 | 65 | 22.2 | 2.65
68 | 40 | 742 | 57 | ∆T | 14.6 | 15 | 14 | 68 | 20.9 | 2.37
68 | 40 | 742 | 57 | LDB | 53.4 | 15 | 14 | 70 | 20 | 2.2
68 | 40 | 742 | 57 | LWB | 51 | 15 | 14 | 72 | 19.1 | 2.03
68 | 40 | 742 | 57 | kW | 0.41 | 15 | 14 | 75 | 17.8 | 1.81
72 | 40 | 742 | 61 | MBh | 14.2 | 13 | 12 | 61 | 24 | 2.97
72 | 40 | 742 | 61 | S/T | 0.979 | 13 | 12 | 65 | 22.2 | 2.78
72 | 40 | 742 | 61 | ∆T | 17.3 | 13 | 12 | 68 | 20.9 | 2.48
72 | 40 | 742 | 61 | LDB | 54.7 | 13 | 12 | 70 | 20 | 2.3
72 | 40 | 742 | 61 | LWB | 54.3 | 13 | 12 | 72 | 19.1 | 2.13
72 | 40 | 742 | 61 | kW | 0.5 | 13 | 12 | 75 | 17.8 | 1.89
77 | 40 | 742 | 64 | MBh | 16.1 | 10 | 9 | 61 | 24 | 3.02
77 | 40 | 742 | 64 | S/T | 0.963 | 10 | 9 | 65 | 22.2 | 2.93
77 | 40 | 742 | 64 | ∆T | 19.3 | 10 | 9 | 68 | 20.9 | 2.71
77 | 40 | 742 | 64 | LDB | 57.7 | 10 | 9 | 70 | 20 | 2.51
77 | 40 | 742 | 64 | LWB | 56.9 | 10 | 9 | 72 | 19.1 | 2.31
77 | 40 | 742 | 64 | kW | 0.58 | 10 | 9 | 75 | 17.8 | 2.04
80 | 40 | 742 | 67 | MBh | 18 | 6 | 5 | 61 | 23.4 | 3.06
80 | 40 | 742 | 67 | S/T | 0.894 | 6 | 5 | 65 | 22.2 | 2.99
80 | 40 | 742 | 67 | ∆T | 20.1 | 6 | 5 | 68 | 20.9 | 2.92
80 | 40 | 742 | 67 | LDB | 59.9 | 6 | 5 | 70 | 20 | 2.75
80 | 40 | 742 | 67 | LWB | 59.5 | 6 | 5 | 72 | 19.1 | 2.53
80 | 40 | 742 | 67 | kW | 0.65 | 6 | 5 | 75 | 17.8 | 2.23
84 | 40 | 742 | 70 | MBh | 19.9 | -2 | -2 | 61 | 20.1 | 2.88
84 | 40 | 742 | 70 | S/T | 0.874 | -2 | -2 | 65 | 20.1 | 2.88
84 | 40 | 742 | 70 | ∆T | 21.7 | -2 | -2 | 68 | 20.1 | 2.88
84 | 40 | 742 | 70 | LDB | 62.3 | -2 | -2 | 70 | 20 | 2.88
84 | 40 | 742 | 70 | LWB | 62.2 | -2 | -2 | 72 | 19.1 | 2.88
84 | 40 | 742 | 70 | kW | 0.73 | -2 | -2 | 75 | 17.8 | 2.73
86 | 40 | 742 | 72 | MBh | 21.2 | -4 | -4 | 61 | 19.3 | 2.84
86 | 40 | 742 | 72 | S/T | 0.825 | -4 | -4 | 65 | 19.3 | 2.84
86 | 40 | 742 | 72 | ∆T | 21.8 | -4 | -4 | 68 | 19.3 | 2.84
86 | 40 | 742 | 72 | LDB | 64.2 | -4 | -4 | 70 | 19.3 | 2.84
86 | 40 | 742 | 72 | LWB | 64 | -4 | -4 | 72 | 19.1 | 2.84
86 | 40 | 742 | 72 | kW | 0.79 | -4 | -4 | 75 | 17.8 | 2.84
90 | 40 | 742 | 75 | MBh | 23.1
90 | 40 | 742 | 75 | S/T | 0.797
90 | 40 | 742 | 75 | ∆T | 23
90 | 40 | 742 | 75 | LDB | 67
90 | 40 | 742 | 75 | LWB | 66.9
90 | 40 | 742 | 75 | kW | 0.87
68 | 50 | 742 | 57 | MBh | 11.7
68 | 50 | 742 | 57 | S/T | 1
68 | 50 | 742 | 57 | ∆T | 14.6
68 | 50 | 742 | 57 | LDB | 53.4
68 | 50 | 742 | 57 | LWB | 51
68 | 50 | 742 | 57 | kW | 0.42
72 | 50 | 742 | 61 | MBh | 14.2
72 | 50 | 742 | 61 | S/T | 0.979
72 | 50 | 742 | 61 | ∆T | 17.3
72 | 50 | 742 | 61 | LDB | 54.7
72 | 50 | 742 | 61 | LWB | 54.3
72 | 50 | 742 | 61 | kW | 0.53
77 | 50 | 742 | 64 | MBh | 16.1
77 | 50 | 742 | 64 | S/T | 0.963
77 | 50 | 742 | 64 | ∆T | 19.3
77 | 50 | 742 | 64 | LDB | 57.7
77 | 50 | 742 | 64 | LWB | 56.9
77 | 50 | 742 | 64 | kW | 0.61
80 | 50 | 742 | 67 | MBh | 18
80 | 50 | 742 | 67 | S/T | 0.894
80 | 50 | 742 | 67 | ∆T | 20.1
80 | 50 | 742 | 67 | LDB | 59.9
80 | 50 | 742 | 67 | LWB | 59.5
80 | 50 | 742 | 67 | kW | 0.69
84 | 50 | 742 | 70 | MBh | 19.9
84 | 50 | 742 | 70 | S/T | 0.874
84 | 50 | 742 | 70 | ∆T | 21.7
84 | 50 | 742 | 70 | LDB | 62.3
84 | 50 | 742 | 70 | LWB | 62.2
84 | 50 | 742 | 70 | kW | 0.77
86 | 50 | 742 | 72 | MBh | 21.2
86 | 50 | 742 | 72 | S/T | 0.825
86 | 50 | 742 | 72 | ∆T | 21.8
86 | 50 | 742 | 72 | LDB | 64.2
86 | 50 | 742 | 72 | LWB | 64
86 | 50 | 742 | 72 | kW | 0.83
90 | 50 | 742 | 75 | MBh | 23.1
90 | 50 | 742 | 75 | S/T | 0.797
90 | 50 | 742 | 75 | ∆T | 23
90 | 50 | 742 | 75 | LDB | 67
90 | 50 | 742 | 75 | LWB | 66.9
90 | 50 | 742 | 75 | kW | 0.92
68 | 54 | 742 | 57 | MBh | 11.7
68 | 54 | 742 | 57 | S/T | 1
68 | 54 | 742 | 57 | ∆T | 14.6
68 | 54 | 742 | 57 | LDB | 53.4
68 | 54 | 742 | 57 | LWB | 51
68 | 54 | 742 | 57 | kW | 0.43
72 | 54 | 742 | 61 | MBh | 14.2
72 | 54 | 742 | 61 | S/T | 0.979
72 | 54 | 742 | 61 | ∆T | 17.3
72 | 54 | 742 | 61 | LDB | 54.7
72 | 54 | 742 | 61 | LWB | 54.3
72 | 54 | 742 | 61 | kW | 0.54
77 | 54 | 742 | 64 | MBh | 16.1
77 | 54 | 742 | 64 | S/T | 0.963
77 | 54 | 742 | 64 | ∆T | 19.3
77 | 54 | 742 | 64 | LDB | 57.7
77 | 54 | 742 | 64 | LWB | 56.9
77 | 54 | 742 | 64 | kW | 0.62
80 | 54 | 742 | 67 | MBh | 18
80 | 54 | 742 | 67 | S/T | 0.894
80 | 54 | 742 | 67 | ∆T | 20.1
80 | 54 | 742 | 67 | LDB | 59.9
80 | 54 | 742 | 67 | LWB | 59.5
80 | 54 | 742 | 67 | kW | 0.7
84 | 54 | 742 | 70 | MBh | 19.9
84 | 54 | 742 | 70 | S/T | 0.874
84 | 54 | 742 | 70 | ∆T | 21.7
84 | 54 | 742 | 70 | LDB | 62.3
84 | 54 | 742 | 70 | LWB | 62.2
84 | 54 | 742 | 70 | kW | 0.79
86 | 54 | 742 | 72 | MBh | 21.2
86 | 54 | 742 | 72 | S/T | 0.825
86 | 54 | 742 | 72 | ∆T | 21.8
86 | 54 | 742 | 72 | LDB | 64.2
86 | 54 | 742 | 72 | LWB | 64
86 | 54 | 742 | 72 | kW | 0.85
90 | 54 | 742 | 75 | MBh | 23.1
90 | 54 | 742 | 75 | S/T | 0.797
90 | 54 | 742 | 75 | ∆T | 23
90 | 54 | 742 | 75 | LDB | 67
90 | 54 | 742 | 75 | LWB | 66.9
90 | 54 | 742 | 75 | kW | 0.93
68 | 58 | 742 | 57 | MBh | 11.7
68 | 58 | 742 | 57 | S/T | 1
68 | 58 | 742 | 57 | ∆T | 14.6
68 | 58 | 742 | 57 | LDB | 53.4
68 | 58 | 742 | 57 | LWB | 51
68 | 58 | 742 | 57 | kW | 0.44
72 | 58 | 742 | 61 | MBh | 14.2
72 | 58 | 742 | 61 | S/T | 0.979
72 | 58 | 742 | 61 | ∆T | 17.3
72 | 58 | 742 | 61 | LDB | 54.7
72 | 58 | 742 | 61 | LWB | 54.3
72 | 58 | 742 | 61 | kW | 0.55
77 | 58 | 742 | 64 | MBh | 16.1
77 | 58 | 742 | 64 | S/T | 0.963
77 | 58 | 742 | 64 | ∆T | 19.3
77 | 58 | 742 | 64 | LDB | 57.7
77 | 58 | 742 | 64 | LWB | 56.9
77 | 58 | 742 | 64 | kW | 0.63
80 | 58 | 742 | 67 | MBh | 18
80 | 58 | 742 | 67 | S/T | 0.894
80 | 58 | 742 | 67 | ∆T | 20.1
80 | 58 | 742 | 67 | LDB | 59.9
80 | 58 | 742 | 67 | LWB | 59.5
80 | 58 | 742 | 67 | kW | 0.72
84 | 58 | 742 | 70 | MBh | 19.9
84 | 58 | 742 | 70 | S/T | 0.874
84 | 58 | 742 | 70 | ∆T | 21.7
84 | 58 | 742 | 70 | LDB | 62.3
84 | 58 | 742 | 70 | LWB | 62.2
84 | 58 | 742 | 70 | kW | 0.81
86 | 58 | 742 | 72 | MBh | 21.2
86 | 58 | 742 | 72 | S/T | 0.825
86 | 58 | 742 | 72 | ∆T | 21.8
86 | 58 | 742 | 72 | LDB | 64.2
86 | 58 | 742 | 72 | LWB | 64
86 | 58 | 742 | 72 | kW | 0.86
90 | 58 | 742 | 75 | MBh | 22.8
90 | 58 | 742 | 75 | S/T | 0.798
90 | 58 | 742 | 75 | ∆T | 22.7
90 | 58 | 742 | 75 | LDB | 67.3
90 | 58 | 742 | 75 | LWB | 67
90 | 58 | 742 | 75 | kW | 0.94
68 | 62 | 742 | 57 | MBh | 11.7
68 | 62 | 742 | 57 | S/T | 1
68 | 62 | 742 | 57 | ∆T | 14.6
68 | 62 | 742 | 57 | LDB | 53.4
68 | 62 | 742 | 57 | LWB | 51
68 | 62 | 742 | 57 | kW | 0.45
72 | 62 | 742 | 61 | MBh | 14.2
72 | 62 | 742 | 61 | S/T | 0.979
72 | 62 | 742 | 61 | ∆T | 17.3
72 | 62 | 742 | 61 | LDB | 54.7
72 | 62 | 742 | 61 | LWB | 54.3
72 | 62 | 742 | 61 | kW | 0.56
77 | 62 | 742 | 64 | MBh | 16.1
77 | 62 | 742 | 64 | S/T | 0.963
77 | 62 | 742 | 64 | ∆T | 19.3
77 | 62 | 742 | 64 | LDB | 57.7
77 | 62 | 742 | 64 | LWB | 56.9
77 | 62 | 742 | 64 | kW | 0.64
80 | 62 | 742 | 67 | MBh | 18
80 | 62 | 742 | 67 | S/T | 0.894
80 | 62 | 742 | 67 | ∆T | 20.1
80 | 62 | 742 | 67 | LDB | 59.9
80 | 62 | 742 | 67 | LWB | 59.5
80 | 62 | 742 | 67 | kW | 0.73
84 | 62 | 742 | 70 | MBh | 19.9
84 | 62 | 742 | 70 | S/T | 0.874
84 | 62 | 742 | 70 | ∆T | 21.7
84 | 62 | 742 | 70 | LDB | 62.3
84 | 62 | 742 | 70 | LWB | 62.2
84 | 62 | 742 | 70 | kW | 0.82
86 | 62 | 742 | 72 | MBh | 21.2
86 | 62 | 742 | 72 | S/T | 0.825
86 | 62 | 742 | 72 | ∆T | 21.8
86 | 62 | 742 | 72 | LDB | 64.2
86 | 62 | 742 | 72 | LWB | 64
86 | 62 | 742 | 72 | kW | 0.88
90 | 62 | 742 | 75 | MBh | 22.5
90 | 62 | 742 | 75 | S/T | 0.8
90 | 62 | 742 | 75 | ∆T | 22.5
90 | 62 | 742 | 75 | LDB | 67.5
90 | 62 | 742 | 75 | LWB | 67.1
90 | 62 | 742 | 75 | kW | 0.96
68 | 66 | 742 | 57 | MBh | 11.7
68 | 66 | 742 | 57 | S/T | 1
68 | 66 | 742 | 57 | ∆T | 14.6
68 | 66 | 742 | 57 | LDB | 53.4
68 | 66 | 742 | 57 | LWB | 51
68 | 66 | 742 | 57 | kW | 0.46
72 | 66 | 742 | 61 | MBh | 14.2
72 | 66 | 742 | 61 | S/T | 0.979
72 | 66 | 742 | 61 | ∆T | 17.3
72 | 66 | 742 | 61 | LDB | 54.7
72 | 66 | 742 | 61 | LWB | 54.3
72 | 66 | 742 | 61 | kW | 0.57
77 | 66 | 742 | 64 | MBh | 16.1
77 | 66 | 742 | 64 | S/T | 0.963
77 | 66 | 742 | 64 | ∆T | 19.3
77 | 66 | 742 | 64 | LDB | 57.7
77 | 66 | 742 | 64 | LWB | 56.9
77 | 66 | 742 | 64 | kW | 0.66
80 | 66 | 742 | 67 | MBh | 18
80 | 66 | 742 | 67 | S/T | 0.894
80 | 66 | 742 | 67 | ∆T | 20.1
80 | 66 | 742 | 67 | LDB | 59.9
80 | 66 | 742 | 67 | LWB | 59.5
80 | 66 | 742 | 67 | kW | 0.75
84 | 66 | 742 | 70 | MBh | 19.9
84 | 66 | 742 | 70 | S/T | 0.874
84 | 66 | 742 | 70 | ∆T | 21.7
84 | 66 | 742 | 70 | LDB | 62.3
84 | 66 | 742 | 70 | LWB | 62.2
84 | 66 | 742 | 70 | kW | 0.87
86 | 66 | 742 | 72 | MBh | 21.2
86 | 66 | 742 | 72 | S/T | 0.825
86 | 66 | 742 | 72 | ∆T | 21.8
86 | 66 | 742 | 72 | LDB | 64.2
86 | 66 | 742 | 72 | LWB | 64
86 | 66 | 742 | 72 | kW | 0.95
90 | 66 | 742 | 75 | MBh | 22.2
90 | 66 | 742 | 75 | S/T | 0.797
90 | 66 | 742 | 75 | ∆T | 22.1
90 | 66 | 742 | 75 | LDB | 67.9
90 | 66 | 742 | 75 | LWB | 67.2
90 | 66 | 742 | 75 | kW | 1.01
68 | 70 | 742 | 57 | MBh | 11.7
68 | 70 | 742 | 57 | S/T | 1
68 | 70 | 742 | 57 | ∆T | 14.6
68 | 70 | 742 | 57 | LDB | 53.4
68 | 70 | 742 | 57 | LWB | 51
68 | 70 | 742 | 57 | kW | 0.47
72 | 70 | 742 | 61 | MBh | 14.2
72 | 70 | 742 | 61 | S/T | 0.979
72 | 70 | 742 | 61 | ∆T | 17.3
72 | 70 | 742 | 61 | LDB | 54.7
72 | 70 | 742 | 61 | LWB | 54.3
72 | 70 | 742 | 61 | kW | 0.58
77 | 70 | 742 | 64 | MBh | 16.1
77 | 70 | 742 | 64 | S/T | 0.963
77 | 70 | 742 | 64 | ∆T | 19.3
77 | 70 | 742 | 64 | LDB | 57.7
77 | 70 | 742 | 64 | LWB | 56.9
77 | 70 | 742 | 64 | kW | 0.69
80 | 70 | 742 | 67 | MBh | 18
80 | 70 | 742 | 67 | S/T | 0.894
80 | 70 | 742 | 67 | ∆T | 20.1
80 | 70 | 742 | 67 | LDB | 59.9
80 | 70 | 742 | 67 | LWB | 59.5
80 | 70 | 742 | 67 | kW | 0.81
84 | 70 | 742 | 70 | MBh | 19.9
84 | 70 | 742 | 70 | S/T | 0.874
84 | 70 | 742 | 70 | ∆T | 21.7
84 | 70 | 742 | 70 | LDB | 62.3
84 | 70 | 742 | 70 | LWB | 62.2
84 | 70 | 742 | 70 | kW | 0.94
86 | 70 | 742 | 72 | MBh | 21.2
86 | 70 | 742 | 72 | S/T | 0.825
86 | 70 | 742 | 72 | ∆T | 21.8
86 | 70 | 742 | 72 | LDB | 64.2
86 | 70 | 742 | 72 | LWB | 64
86 | 70 | 742 | 72 | kW | 1.03
90 | 70 | 742 | 75 | MBh | 21.8
90 | 70 | 742 | 75 | S/T | 0.798
90 | 70 | 742 | 75 | ∆T | 21.7
90 | 70 | 742 | 75 | LDB | 68.3
90 | 70 | 742 | 75 | LWB | 67.4
90 | 70 | 742 | 75 | kW | 1.07
68 | 72 | 742 | 57 | MBh | 11.7
68 | 72 | 742 | 57 | S/T | 1
68 | 72 | 742 | 57 | ∆T | 14.6
68 | 72 | 742 | 57 | LDB | 53.4
68 | 72 | 742 | 57 | LWB | 51
68 | 72 | 742 | 57 | kW | 0.47
72 | 72 | 742 | 61 | MBh | 14.2
72 | 72 | 742 | 61 | S/T | 0.979
72 | 72 | 742 | 61 | ∆T | 17.3
72 | 72 | 742 | 61 | LDB | 54.7
72 | 72 | 742 | 61 | LWB | 54.3
72 | 72 | 742 | 61 | kW | 0.6
77 | 72 | 742 | 64 | MBh | 16.1
77 | 72 | 742 | 64 | S/T | 0.963
77 | 72 | 742 | 64 | ∆T | 19.3
77 | 72 | 742 | 64 | LDB | 57.7
77 | 72 | 742 | 64 | LWB | 56.9
77 | 72 | 742 | 64 | kW | 0.72
80 | 72 | 742 | 67 | MBh | 18
80 | 72 | 742 | 67 | S/T | 0.894
80 | 72 | 742 | 67 | ∆T | 20.1
80 | 72 | 742 | 67 | LDB | 59.9
80 | 72 | 742 | 67 | LWB | 59.5
80 | 72 | 742 | 67 | kW | 0.84
84 | 72 | 742 | 70 | MBh | 19.9
84 | 72 | 742 | 70 | S/T | 0.874
84 | 72 | 742 | 70 | ∆T | 21.7
84 | 72 | 742 | 70 | LDB | 62.3
84 | 72 | 742 | 70 | LWB | 62.2
84 | 72 | 742 | 70 | kW | 0.98
86 | 72 | 742 | 72 | MBh | 21.2
86 | 72 | 742 | 72 | S/T | 0.825
86 | 72 | 742 | 72 | ∆T | 21.8
86 | 72 | 742 | 72 | LDB | 64.2
86 | 72 | 742 | 72 | LWB | 64
86 | 72 | 742 | 72 | kW | 1.07
90 | 72 | 742 | 75 | MBh | 21.7
90 | 72 | 742 | 75 | S/T | 0.797
90 | 72 | 742 | 75 | ∆T | 21.6
90 | 72 | 742 | 75 | LDB | 68.4
90 | 72 | 742 | 75 | LWB | 67.4
90 | 72 | 742 | 75 | kW | 1.09
68 | 75 | 742 | 57 | MBh | 11.7
68 | 75 | 742 | 57 | S/T | 1
68 | 75 | 742 | 57 | ∆T | 14.6
68 | 75 | 742 | 57 | LDB | 53.4
68 | 75 | 742 | 57 | LWB | 51
68 | 75 | 742 | 57 | kW | 0.49
72 | 75 | 742 | 61 | MBh | 14.2
72 | 75 | 742 | 61 | S/T | 0.979
72 | 75 | 742 | 61 | ∆T | 17.3
72 | 75 | 742 | 61 | LDB | 54.7
72 | 75 | 742 | 61 | LWB | 54.3
72 | 75 | 742 | 61 | kW | 0.64
77 | 75 | 742 | 64 | MBh | 16.1
77 | 75 | 742 | 64 | S/T | 0.963
77 | 75 | 742 | 64 | ∆T | 19.3
77 | 75 | 742 | 64 | LDB | 57.7
77 | 75 | 742 | 64 | LWB | 56.9
77 | 75 | 742 | 64 | kW | 0.76
80 | 75 | 742 | 67 | MBh | 18
80 | 75 | 742 | 67 | S/T | 0.894
80 | 75 | 742 | 67 | ∆T | 20.1
80 | 75 | 742 | 67 | LDB | 59.9
80 | 75 | 742 | 67 | LWB | 59.5
80 | 75 | 742 | 67 | kW | 0.89
84 | 75 | 742 | 70 | MBh | 19.9
84 | 75 | 742 | 70 | S/T | 0.874
84 | 75 | 742 | 70 | ∆T | 21.7
84 | 75 | 742 | 70 | LDB | 62.3
84 | 75 | 742 | 70 | LWB | 62.2
84 | 75 | 742 | 70 | kW | 1.04
86 | 75 | 742 | 72 | MBh | 21
86 | 75 | 742 | 72 | S/T | 0.829
86 | 75 | 742 | 72 | ∆T | 21.7
86 | 75 | 742 | 72 | LDB | 64.3
86 | 75 | 742 | 72 | LWB | 64.1
86 | 75 | 742 | 72 | kW | 1.13
90 | 75 | 742 | 75 | MBh | 21.4
90 | 75 | 742 | 75 | S/T | 0.799
90 | 75 | 742 | 75 | ∆T | 21.3
90 | 75 | 742 | 75 | LDB | 68.7
90 | 75 | 742 | 75 | LWB | 67.5
90 | 75 | 742 | 75 | kW | 1.13
68 | 79 | 742 | 57 | MBh | 11.7
68 | 79 | 742 | 57 | S/T | 1
68 | 79 | 742 | 57 | ∆T | 14.6
68 | 79 | 742 | 57 | LDB | 53.4
68 | 79 | 742 | 57 | LWB | 51
68 | 79 | 742 | 57 | kW | 0.53
72 | 79 | 742 | 61 | MBh | 14.2
72 | 79 | 742 | 61 | S/T | 0.979
72 | 79 | 742 | 61 | ∆T | 17.3
72 | 79 | 742 | 61 | LDB | 54.7
72 | 79 | 742 | 61 | LWB | 54.3
72 | 79 | 742 | 61 | kW | 0.69
77 | 79 | 742 | 64 | MBh | 16.1
77 | 79 | 742 | 64 | S/T | 0.963
77 | 79 | 742 | 64 | ∆T | 19.3
77 | 79 | 742 | 64 | LDB | 57.7
77 | 79 | 742 | 64 | LWB | 56.9
77 | 79 | 742 | 64 | kW | 0.82
80 | 79 | 742 | 67 | MBh | 18
80 | 79 | 742 | 67 | S/T | 0.894
80 | 79 | 742 | 67 | ∆T | 20.1
80 | 79 | 742 | 67 | LDB | 59.9
80 | 79 | 742 | 67 | LWB | 59.5
80 | 79 | 742 | 67 | kW | 0.96
84 | 79 | 742 | 70 | MBh | 19.9
84 | 79 | 742 | 70 | S/T | 0.874
84 | 79 | 742 | 70 | ∆T | 21.7
84 | 79 | 742 | 70 | LDB | 62.3
84 | 79 | 742 | 70 | LWB | 62.2
84 | 79 | 742 | 70 | kW | 1.12
86 | 79 | 742 | 72 | MBh | 20.7
86 | 79 | 742 | 72 | S/T | 0.826
86 | 79 | 742 | 72 | ∆T | 21.3
86 | 79 | 742 | 72 | LDB | 64.7
86 | 79 | 742 | 72 | LWB | 64.2
86 | 79 | 742 | 72 | kW | 1.18
90 | 79 | 742 | 75 | MBh | 21.1
90 | 79 | 742 | 75 | S/T | 0.796
90 | 79 | 742 | 75 | ∆T | 21
90 | 79 | 742 | 75 | LDB | 69
90 | 79 | 742 | 75 | LWB | 67.6
90 | 79 | 742 | 75 | kW | 1.19
68 | 83 | 742 | 57 | MBh | 11.7
68 | 83 | 742 | 57 | S/T | 1
68 | 83 | 742 | 57 | ∆T | 14.6
68 | 83 | 742 | 57 | LDB | 53.4
68 | 83 | 742 | 57 | LWB | 51
68 | 83 | 742 | 57 | kW | 0.57
72 | 83 | 742 | 61 | MBh | 14.2
72 | 83 | 742 | 61 | S/T | 0.979
72 | 83 | 742 | 61 | ∆T | 17.3
72 | 83 | 742 | 61 | LDB | 54.7
72 | 83 | 742 | 61 | LWB | 54.3
72 | 83 | 742 | 61 | kW | 0.74
77 | 83 | 742 | 64 | MBh | 16.1
77 | 83 | 742 | 64 | S/T | 0.963
77 | 83 | 742 | 64 | ∆T | 19.3
77 | 83 | 742 | 64 | LDB | 57.7
77 | 83 | 742 | 64 | LWB | 56.9
77 | 83 | 742 | 64 | kW | 0.88
80 | 83 | 742 | 67 | MBh | 18
80 | 83 | 742 | 67 | S/T | 0.894
80 | 83 | 742 | 67 | ∆T | 20.1
80 | 83 | 742 | 67 | LDB | 59.9
80 | 83 | 742 | 67 | LWB | 59.5
80 | 83 | 742 | 67 | kW | 1.04
84 | 83 | 742 | 70 | MBh | 19.9
84 | 83 | 742 | 70 | S/T | 0.874
84 | 83 | 742 | 70 | ∆T | 21.7
84 | 83 | 742 | 70 | LDB | 62.3
84 | 83 | 742 | 70 | LWB | 62.2
84 | 83 | 742 | 70 | kW | 1.2
86 | 83 | 742 | 72 | MBh | 20.4
86 | 83 | 742 | 72 | S/T | 0.828
86 | 83 | 742 | 72 | ∆T | 21.1
86 | 83 | 742 | 72 | LDB | 64.9
86 | 83 | 742 | 72 | LWB | 64.4
86 | 83 | 742 | 72 | kW | 1.23
90 | 83 | 742 | 75 | MBh | 20.7
90 | 83 | 742 | 75 | S/T | 0.802
90 | 83 | 742 | 75 | ∆T | 20.7
90 | 83 | 742 | 75 | LDB | 69.3
90 | 83 | 742 | 75 | LWB | 67.8
90 | 83 | 742 | 75 | kW | 1.24
68 | 87 | 742 | 57 | MBh | 11.7
68 | 87 | 742 | 57 | S/T | 1
68 | 87 | 742 | 57 | ∆T | 14.6
68 | 87 | 742 | 57 | LDB | 53.4
68 | 87 | 742 | 57 | LWB | 51
68 | 87 | 742 | 57 | kW | 0.61
72 | 87 | 742 | 61 | MBh | 14.2
72 | 87 | 742 | 61 | S/T | 0.979
72 | 87 | 742 | 61 | ∆T | 17.3
72 | 87 | 742 | 61 | LDB | 54.7
72 | 87 | 742 | 61 | LWB | 54.3
72 | 87 | 742 | 61 | kW | 0.79
77 | 87 | 742 | 64 | MBh | 16.1
77 | 87 | 742 | 64 | S/T | 0.963
77 | 87 | 742 | 64 | ∆T | 19.3
77 | 87 | 742 | 64 | LDB | 57.7
77 | 87 | 742 | 64 | LWB | 56.9
77 | 87 | 742 | 64 | kW | 0.95
80 | 87 | 742 | 67 | MBh | 18
80 | 87 | 742 | 67 | S/T | 0.894
80 | 87 | 742 | 67 | ∆T | 20.1
80 | 87 | 742 | 67 | LDB | 59.9
80 | 87 | 742 | 67 | LWB | 59.5
80 | 87 | 742 | 67 | kW | 1.11
84 | 87 | 742 | 70 | MBh | 19.8
84 | 87 | 742 | 70 | S/T | 0.874
84 | 87 | 742 | 70 | ∆T | 21.6
84 | 87 | 742 | 70 | LDB | 62.4
84 | 87 | 742 | 70 | LWB | 62.2
84 | 87 | 742 | 70 | kW | 1.28
86 | 87 | 742 | 72 | MBh | 20
86 | 87 | 742 | 72 | S/T | 0.83
86 | 87 | 742 | 72 | ∆T | 20.7
86 | 87 | 742 | 72 | LDB | 65.3
86 | 87 | 742 | 72 | LWB | 64.5
86 | 87 | 742 | 72 | kW | 1.29
90 | 87 | 742 | 75 | MBh | 20.4
90 | 87 | 742 | 75 | S/T | 0.799
90 | 87 | 742 | 75 | ∆T | 20.3
90 | 87 | 742 | 75 | LDB | 69.7
90 | 87 | 742 | 75 | LWB | 67.9
90 | 87 | 742 | 75 | kW | 1.3
68 | 91 | 742 | 57 | MBh | 11.7
68 | 91 | 742 | 57 | S/T | 1
68 | 91 | 742 | 57 | ∆T | 14.6
68 | 91 | 742 | 57 | LDB | 53.4
68 | 91 | 742 | 57 | LWB | 51
68 | 91 | 742 | 57 | kW | 0.65
72 | 91 | 742 | 61 | MBh | 14.2
72 | 91 | 742 | 61 | S/T | 0.979
72 | 91 | 742 | 61 | ∆T | 17.3
72 | 91 | 742 | 61 | LDB | 54.7
72 | 91 | 742 | 61 | LWB | 54.3
72 | 91 | 742 | 61 | kW | 0.85
77 | 91 | 742 | 64 | MBh | 16.1
77 | 91 | 742 | 64 | S/T | 0.963
77 | 91 | 742 | 64 | ∆T | 19.3
77 | 91 | 742 | 64 | LDB | 57.7
77 | 91 | 742 | 64 | LWB | 56.9
77 | 91 | 742 | 64 | kW | 1.01
80 | 91 | 742 | 67 | MBh | 18
80 | 91 | 742 | 67 | S/T | 0.894
80 | 91 | 742 | 67 | ∆T | 20.1
80 | 91 | 742 | 67 | LDB | 59.9
80 | 91 | 742 | 67 | LWB | 59.5
80 | 91 | 742 | 67 | kW | 1.2
84 | 91 | 742 | 70 | MBh | 19.4
84 | 91 | 742 | 70 | S/T | 0.876
84 | 91 | 742 | 70 | ∆T | 21.2
84 | 91 | 742 | 70 | LDB | 62.8
84 | 91 | 742 | 70 | LWB | 62.4
84 | 91 | 742 | 70 | kW | 1.34
86 | 91 | 742 | 72 | MBh | 19.7
86 | 91 | 742 | 72 | S/T | 0.827
86 | 91 | 742 | 72 | ∆T | 20.3
86 | 91 | 742 | 72 | LDB | 65.7
86 | 91 | 742 | 72 | LWB | 64.6
86 | 91 | 742 | 72 | kW | 1.34
90 | 91 | 742 | 75 | MBh | 20.1
90 | 91 | 742 | 75 | S/T | 0.796
90 | 91 | 742 | 75 | ∆T | 20
90 | 91 | 742 | 75 | LDB | 70
90 | 91 | 742 | 75 | LWB | 68
90 | 91 | 742 | 75 | kW | 1.35
68 | 93 | 742 | 57 | MBh | 11.7
68 | 93 | 742 | 57 | S/T | 1
68 | 93 | 742 | 57 | ∆T | 14.6
68 | 93 | 742 | 57 | LDB | 53.4
68 | 93 | 742 | 57 | LWB | 51
68 | 93 | 742 | 57 | kW | 0.67
72 | 93 | 742 | 61 | MBh | 14.2
72 | 93 | 742 | 61 | S/T | 0.979
72 | 93 | 742 | 61 | ∆T | 17.3
72 | 93 | 742 | 61 | LDB | 54.7
72 | 93 | 742 | 61 | LWB | 54.3
72 | 93 | 742 | 61 | kW | 0.88
77 | 93 | 742 | 64 | MBh | 16.1
77 | 93 | 742 | 64 | S/T | 0.963
77 | 93 | 742 | 64 | ∆T | 19.3
77 | 93 | 742 | 64 | LDB | 57.7
77 | 93 | 742 | 64 | LWB | 56.9
77 | 93 | 742 | 64 | kW | 1.05
80 | 93 | 742 | 67 | MBh | 18
80 | 93 | 742 | 67 | S/T | 0.894
80 | 93 | 742 | 67 | ∆T | 20.1
80 | 93 | 742 | 67 | LDB | 59.9
80 | 93 | 742 | 67 | LWB | 59.5
80 | 93 | 742 | 67 | kW | 1.24
84 | 93 | 742 | 70 | MBh | 19.3
84 | 93 | 742 | 70 | S/T | 0.876
84 | 93 | 742 | 70 | ∆T | 21.1
84 | 93 | 742 | 70 | LDB | 62.9
84 | 93 | 742 | 70 | LWB | 62.4
84 | 93 | 742 | 70 | kW | 1.36
86 | 93 | 742 | 72 | MBh | 19.5
86 | 93 | 742 | 72 | S/T | 0.831
86 | 93 | 742 | 72 | ∆T | 20.2
86 | 93 | 742 | 72 | LDB | 65.8
86 | 93 | 742 | 72 | LWB | 64.7
86 | 93 | 742 | 72 | kW | 1.37
90 | 93 | 742 | 75 | MBh | 19.9
90 | 93 | 742 | 75 | S/T | 0.799
90 | 93 | 742 | 75 | ∆T | 19.8
90 | 93 | 742 | 75 | LDB | 70.2
90 | 93 | 742 | 75 | LWB | 68.1
90 | 93 | 742 | 75 | kW | 1.38
68 | 95 | 742 | 57 | MBh | 11.7
68 | 95 | 742 | 57 | S/T | 1
68 | 95 | 742 | 57 | ∆T | 14.6
68 | 95 | 742 | 57 | LDB | 53.4
68 | 95 | 742 | 57 | LWB | 51
68 | 95 | 742 | 57 | kW | 0.69
72 | 95 | 742 | 61 | MBh | 14.2
72 | 95 | 742 | 61 | S/T | 0.979
72 | 95 | 742 | 61 | ∆T | 17.3
72 | 95 | 742 | 61 | LDB | 54.7
72 | 95 | 742 | 61 | LWB | 54.3
72 | 95 | 742 | 61 | kW | 0.91
77 | 95 | 742 | 64 | MBh | 16.1
77 | 95 | 742 | 64 | S/T | 0.963
77 | 95 | 742 | 64 | ∆T | 19.3
77 | 95 | 742 | 64 | LDB | 57.7
77 | 95 | 742 | 64 | LWB | 56.9
77 | 95 | 742 | 64 | kW | 1.09
80 | 95 | 742 | 67 | MBh | 18
80 | 95 | 742 | 67 | S/T | 0.894
80 | 95 | 742 | 67 | ∆T | 20.1
80 | 95 | 742 | 67 | LDB | 59.9
80 | 95 | 742 | 67 | LWB | 59.5
80 | 95 | 742 | 67 | kW | 1.29
84 | 95 | 742 | 70 | MBh | 19.1
84 | 95 | 742 | 70 | S/T | 0.874
84 | 95 | 742 | 70 | ∆T | 20.8
84 | 95 | 742 | 70 | LDB | 63.2
84 | 95 | 742 | 70 | LWB | 62.5
84 | 95 | 742 | 70 | kW | 1.39
86 | 95 | 742 | 72 | MBh | 19.3
86 | 95 | 742 | 72 | S/T | 0.829
86 | 95 | 742 | 72 | ∆T | 20
86 | 95 | 742 | 72 | LDB | 66
86 | 95 | 742 | 72 | LWB | 64.8
86 | 95 | 742 | 72 | kW | 1.4
90 | 95 | 742 | 75 | MBh | 19.7
90 | 95 | 742 | 75 | S/T | 0.802
90 | 95 | 742 | 75 | ∆T | 19.7
90 | 95 | 742 | 75 | LDB | 70.3
90 | 95 | 742 | 75 | LWB | 68.2
90 | 95 | 742 | 75 | kW | 1.41
68 | 99 | 742 | 57 | MBh | 11.7
68 | 99 | 742 | 57 | S/T | 1
68 | 99 | 742 | 57 | ∆T | 14.6
68 | 99 | 742 | 57 | LDB | 53.4
68 | 99 | 742 | 57 | LWB | 51
68 | 99 | 742 | 57 | kW | 0.74
72 | 99 | 742 | 61 | MBh | 14.2
72 | 99 | 742 | 61 | S/T | 0.979
72 | 99 | 742 | 61 | ∆T | 17.3
72 | 99 | 742 | 61 | LDB | 54.7
72 | 99 | 742 | 61 | LWB | 54.3
72 | 99 | 742 | 61 | kW | 0.97
77 | 99 | 742 | 64 | MBh | 16.1
77 | 99 | 742 | 64 | S/T | 0.963
77 | 99 | 742 | 64 | ∆T | 19.3
77 | 99 | 742 | 64 | LDB | 57.7
77 | 99 | 742 | 64 | LWB | 56.9
77 | 99 | 742 | 64 | kW | 1.17
80 | 99 | 742 | 67 | MBh | 18
80 | 99 | 742 | 67 | S/T | 0.894
80 | 99 | 742 | 67 | ∆T | 20.1
80 | 99 | 742 | 67 | LDB | 59.9
80 | 99 | 742 | 67 | LWB | 59.5
80 | 99 | 742 | 67 | kW | 1.38
84 | 99 | 742 | 70 | MBh | 18.8
84 | 99 | 742 | 70 | S/T | 0.872
84 | 99 | 742 | 70 | ∆T | 20.5
84 | 99 | 742 | 70 | LDB | 63.5
84 | 99 | 742 | 70 | LWB | 62.7
84 | 99 | 742 | 70 | kW | 1.44
86 | 99 | 742 | 72 | MBh | 19
86 | 99 | 742 | 72 | S/T | 0.826
86 | 99 | 742 | 72 | ∆T | 19.6
86 | 99 | 742 | 72 | LDB | 66.4
86 | 99 | 742 | 72 | LWB | 64.9
86 | 99 | 742 | 72 | kW | 1.45
90 | 99 | 742 | 75 | MBh | 19.4
90 | 99 | 742 | 75 | S/T | 0.799
90 | 99 | 742 | 75 | ∆T | 19.3
90 | 99 | 742 | 75 | LDB | 70.7
90 | 99 | 742 | 75 | LWB | 68.3
90 | 99 | 742 | 75 | kW | 1.46
68 | 103 | 742 | 57 | MBh | 11.7
68 | 103 | 742 | 57 | S/T | 1
68 | 103 | 742 | 57 | ∆T | 14.6
68 | 103 | 742 | 57 | LDB | 53.4
68 | 103 | 742 | 57 | LWB | 51
68 | 103 | 742 | 57 | kW | 0.79
72 | 103 | 742 | 61 | MBh | 14.2
72 | 103 | 742 | 61 | S/T | 0.979
72 | 103 | 742 | 61 | ∆T | 17.3
72 | 103 | 742 | 61 | LDB | 54.7
72 | 103 | 742 | 61 | LWB | 54.3
72 | 103 | 742 | 61 | kW | 1.04
77 | 103 | 742 | 64 | MBh | 16.1
77 | 103 | 742 | 64 | S/T | 0.963
77 | 103 | 742 | 64 | ∆T | 19.3
77 | 103 | 742 | 64 | LDB | 57.7
77 | 103 | 742 | 64 | LWB | 56.9
77 | 103 | 742 | 64 | kW | 1.25
80 | 103 | 742 | 67 | MBh | 18
80 | 103 | 742 | 67 | S/T | 0.894
80 | 103 | 742 | 67 | ∆T | 20.1
80 | 103 | 742 | 67 | LDB | 59.9
80 | 103 | 742 | 67 | LWB | 59.5
80 | 103 | 742 | 67 | kW | 1.48
84 | 103 | 742 | 70 | MBh | 18.4
84 | 103 | 742 | 70 | S/T | 0.875
84 | 103 | 742 | 70 | ∆T | 20.1
84 | 103 | 742 | 70 | LDB | 63.9
84 | 103 | 742 | 70 | LWB | 62.8
84 | 103 | 742 | 70 | kW | 1.5
86 | 103 | 742 | 72 | MBh | 18.7
86 | 103 | 742 | 72 | S/T | 0.829
86 | 103 | 742 | 72 | ∆T | 19.3
86 | 103 | 742 | 72 | LDB | 66.7
86 | 103 | 742 | 72 | LWB | 65
86 | 103 | 742 | 72 | kW | 1.51
90 | 103 | 742 | 75 | MBh | 19
90 | 103 | 742 | 75 | S/T | 0.8
90 | 103 | 742 | 75 | ∆T | 19
90 | 103 | 742 | 75 | LDB | 71
90 | 103 | 742 | 75 | LWB | 68.4
90 | 103 | 742 | 75 | kW | 1.52
68 | 106 | 742 | 57 | MBh | 11.7
68 | 106 | 742 | 57 | S/T | 1
68 | 106 | 742 | 57 | ∆T | 14.6
68 | 106 | 742 | 57 | LDB | 53.4
68 | 106 | 742 | 57 | LWB | 51
68 | 106 | 742 | 57 | kW | 0.87
72 | 106 | 742 | 61 | MBh | 14.2
72 | 106 | 742 | 61 | S/T | 0.979
72 | 106 | 742 | 61 | ∆T | 17.3
72 | 106 | 742 | 61 | LDB | 54.7
72 | 106 | 742 | 61 | LWB | 54.3
72 | 106 | 742 | 61 | kW | 1.15
77 | 106 | 742 | 64 | MBh | 16.1
77 | 106 | 742 | 64 | S/T | 0.963
77 | 106 | 742 | 64 | ∆T | 19.3
77 | 106 | 742 | 64 | LDB | 57.7
77 | 106 | 742 | 64 | LWB | 56.9
77 | 106 | 742 | 64 | kW | 1.38
80 | 106 | 742 | 67 | MBh | 17.8
80 | 106 | 742 | 67 | S/T | 0.893
80 | 106 | 742 | 67 | ∆T | 19.8
80 | 106 | 742 | 67 | LDB | 60.2
80 | 106 | 742 | 67 | LWB | 59.6
80 | 106 | 742 | 67 | kW | 1.6
84 | 106 | 742 | 70 | MBh | 18.2
84 | 106 | 742 | 70 | S/T | 0.874
84 | 106 | 742 | 70 | ∆T | 19.8
84 | 106 | 742 | 70 | LDB | 64.2
84 | 106 | 742 | 70 | LWB | 62.9
84 | 106 | 742 | 70 | kW | 1.61
86 | 106 | 742 | 72 | MBh | 18.4
86 | 106 | 742 | 72 | S/T | 0.826
86 | 106 | 742 | 72 | ∆T | 19
86 | 106 | 742 | 72 | LDB | 67
86 | 106 | 742 | 72 | LWB | 65.2
86 | 106 | 742 | 72 | kW | 1.62
90 | 106 | 742 | 75 | MBh | 18.8
90 | 106 | 742 | 75 | S/T | 0.798
90 | 106 | 742 | 75 | ∆T | 18.7
90 | 106 | 742 | 75 | LDB | 71.3
90 | 106 | 742 | 75 | LWB | 68.5
90 | 106 | 742 | 75 | kW | 1.63
68 | 110 | 742 | 57 | MBh | 11.7
68 | 110 | 742 | 57 | S/T | 1
68 | 110 | 742 | 57 | ∆T | 14.6
68 | 110 | 742 | 57 | LDB | 53.4
68 | 110 | 742 | 57 | LWB | 51
68 | 110 | 742 | 57 | kW | 1
72 | 110 | 742 | 61 | MBh | 14.2
72 | 110 | 742 | 61 | S/T | 0.979
72 | 110 | 742 | 61 | ∆T | 17.3
72 | 110 | 742 | 61 | LDB | 54.7
72 | 110 | 742 | 61 | LWB | 54.3
72 | 110 | 742 | 61 | kW | 1.32
77 | 110 | 742 | 64 | MBh | 16.1
77 | 110 | 742 | 64 | S/T | 0.963
77 | 110 | 742 | 64 | ∆T | 19.3
77 | 110 | 742 | 64 | LDB | 57.7
77 | 110 | 742 | 64 | LWB | 56.9
77 | 110 | 742 | 64 | kW | 1.59
80 | 110 | 742 | 67 | MBh | 17.5
80 | 110 | 742 | 67 | S/T | 0.891
80 | 110 | 742 | 67 | ∆T | 19.5
80 | 110 | 742 | 67 | LDB | 60.5
80 | 110 | 742 | 67 | LWB | 59.7
80 | 110 | 742 | 67 | kW | 1.78
84 | 110 | 742 | 70 | MBh | 17.8
84 | 110 | 742 | 70 | S/T | 0.876
84 | 110 | 742 | 70 | ∆T | 19.5
84 | 110 | 742 | 70 | LDB | 64.5
84 | 110 | 742 | 70 | LWB | 63.1
84 | 110 | 742 | 70 | kW | 1.79
86 | 110 | 742 | 72 | MBh | 18.1
86 | 110 | 742 | 72 | S/T | 0.829
86 | 110 | 742 | 72 | ∆T | 18.7
86 | 110 | 742 | 72 | LDB | 67.3
86 | 110 | 742 | 72 | LWB | 65.3
86 | 110 | 742 | 72 | kW | 1.8
90 | 110 | 742 | 75 | MBh | 18.1
90 | 110 | 742 | 75 | S/T | 0.801
90 | 110 | 742 | 75 | ∆T | 18.1
90 | 110 | 742 | 75 | LDB | 71.9
90 | 110 | 742 | 75 | LWB | 68.8
90 | 110 | 742 | 75 | kW | 1.8
68 | 115 | 742 | 57 | MBh | 11.7
68 | 115 | 742 | 57 | S/T | 1
68 | 115 | 742 | 57 | ∆T | 14.6
68 | 115 | 742 | 57 | LDB | 53.4
68 | 115 | 742 | 57 | LWB | 51
68 | 115 | 742 | 57 | kW | 1.17
72 | 115 | 742 | 61 | MBh | 14.2
72 | 115 | 742 | 61 | S/T | 0.979
72 | 115 | 742 | 61 | ∆T | 17.3
72 | 115 | 742 | 61 | LDB | 54.7
72 | 115 | 742 | 61 | LWB | 54.3
72 | 115 | 742 | 61 | kW | 1.55
77 | 115 | 742 | 64 | MBh | 16.1
77 | 115 | 742 | 64 | S/T | 0.963
77 | 115 | 742 | 64 | ∆T | 19.3
77 | 115 | 742 | 64 | LDB | 57.7
77 | 115 | 742 | 64 | LWB | 56.9
77 | 115 | 742 | 64 | kW | 1.86
80 | 115 | 742 | 67 | MBh | 16.8
80 | 115 | 742 | 67 | S/T | 0.899
80 | 115 | 742 | 67 | ∆T | 18.8
80 | 115 | 742 | 67 | LDB | 61.2
80 | 115 | 742 | 67 | LWB | 60
80 | 115 | 742 | 67 | kW | 1.99
84 | 115 | 742 | 70 | MBh | 16.8
84 | 115 | 742 | 70 | S/T | 0.875
84 | 115 | 742 | 70 | ∆T | 18.3
84 | 115 | 742 | 70 | LDB | 65.7
84 | 115 | 742 | 70 | LWB | 63.5
84 | 115 | 742 | 70 | kW | 1.99
86 | 115 | 742 | 72 | MBh | 16.8
86 | 115 | 742 | 72 | S/T | 0.827
86 | 115 | 742 | 72 | ∆T | 17.3
86 | 115 | 742 | 72 | LDB | 68.7
86 | 115 | 742 | 72 | LWB | 65.8
86 | 115 | 742 | 72 | kW | 1.99
90 | 115 | 742 | 75 | MBh | 16.8
90 | 115 | 742 | 75 | S/T | 0.804
90 | 115 | 742 | 75 | ∆T | 16.8
90 | 115 | 742 | 75 | LDB | 73.2
90 | 115 | 742 | 75 | LWB | 69.2
90 | 115 | 742 | 75 | kW | 1.99
68 | 118 | 742 | 57 | MBh | 11.7
68 | 118 | 742 | 57 | S/T | 1
68 | 118 | 742 | 57 | ∆T | 14.6
68 | 118 | 742 | 57 | LDB | 53.4
68 | 118 | 742 | 57 | LWB | 51
68 | 118 | 742 | 57 | kW | 1.28
72 | 118 | 742 | 61 | MBh | 14.2
72 | 118 | 742 | 61 | S/T | 0.979
72 | 118 | 742 | 61 | ∆T | 17.3
72 | 118 | 742 | 61 | LDB | 54.7
72 | 118 | 742 | 61 | LWB | 54.3
72 | 118 | 742 | 61 | kW | 1.69
77 | 118 | 742 | 64 | MBh | 14.3
77 | 118 | 742 | 64 | S/T | 0.965
77 | 118 | 742 | 64 | ∆T | 17.2
77 | 118 | 742 | 64 | LDB | 59.8
77 | 118 | 742 | 64 | LWB | 57.7
77 | 118 | 742 | 64 | kW | 1.71
80 | 118 | 742 | 67 | MBh | 14.3
80 | 118 | 742 | 67 | S/T | 0.895
80 | 118 | 742 | 67 | ∆T | 16
80 | 118 | 742 | 67 | LDB | 64
80 | 118 | 742 | 67 | LWB | 61.1
80 | 118 | 742 | 67 | kW | 1.71
84 | 118 | 742 | 70 | MBh | 14.3
84 | 118 | 742 | 70 | S/T | 0.874
84 | 118 | 742 | 70 | ∆T | 15.6
84 | 118 | 742 | 70 | LDB | 68.4
84 | 118 | 742 | 70 | LWB | 64.5
84 | 118 | 742 | 70 | kW | 1.71
86 | 118 | 742 | 72 | MBh | 14.3
86 | 118 | 742 | 72 | S/T | 0.832
86 | 118 | 742 | 72 | ∆T | 14.8
86 | 118 | 742 | 72 | LDB | 71.2
86 | 118 | 742 | 72 | LWB | 66.8
86 | 118 | 742 | 72 | kW | 1.71
90 | 118 | 742 | 75 | MBh | 14.3
90 | 118 | 742 | 75 | S/T | 0.804
90 | 118 | 742 | 75 | ∆T | 14.4
90 | 118 | 742 | 75 | LDB | 75.6
90 | 118 | 742 | 75 | LWB | 70.1
90 | 118 | 742 | 75 | kW | 1.71
68 | 122 | 742 | 57 | MBh | 10.7
68 | 122 | 742 | 57 | S/T | 1
68 | 122 | 742 | 57 | ∆T | 13.4
68 | 122 | 742 | 57 | LDB | 54.6
68 | 122 | 742 | 57 | LWB | 51.5
68 | 122 | 742 | 57 | kW | 1.28
72 | 122 | 742 | 61 | MBh | 10.7
72 | 122 | 742 | 61 | S/T | 0.981
72 | 122 | 742 | 61 | ∆T | 13.1
72 | 122 | 742 | 61 | LDB | 58.9
72 | 122 | 742 | 61 | LWB | 56.1
72 | 122 | 742 | 61 | kW | 1.28
77 | 122 | 742 | 64 | MBh | 10.7
77 | 122 | 742 | 64 | S/T | 0.963
77 | 122 | 742 | 64 | ∆T | 12.9
77 | 122 | 742 | 64 | LDB | 64.1
77 | 122 | 742 | 64 | LWB | 59.4
77 | 122 | 742 | 64 | kW | 1.28
80 | 122 | 742 | 67 | MBh | 10.7
80 | 122 | 742 | 67 | S/T | 0.898
80 | 122 | 742 | 67 | ∆T | 12
80 | 122 | 742 | 67 | LDB | 68
80 | 122 | 742 | 67 | LWB | 62.7
80 | 122 | 742 | 67 | kW | 1.28
84 | 122 | 742 | 70 | MBh | 10.7
84 | 122 | 742 | 70 | S/T | 0.879
84 | 122 | 742 | 70 | ∆T | 11.7
84 | 122 | 742 | 70 | LDB | 72.3
84 | 122 | 742 | 70 | LWB | 66
84 | 122 | 742 | 70 | kW | 1.28
86 | 122 | 742 | 72 | MBh | 10.7
86 | 122 | 742 | 72 | S/T | 0.832
86 | 122 | 742 | 72 | ∆T | 11.1
86 | 122 | 742 | 72 | LDB | 74.9
86 | 122 | 742 | 72 | LWB | 68.1
86 | 122 | 742 | 72 | kW | 1.28
90 | 122 | 742 | 75 | MBh | 10.7
90 | 122 | 742 | 75 | S/T | 0.803
90 | 122 | 742 | 75 | ∆T | 10.7
90 | 122 | 742 | 75 | LDB | 79.3
90 | 122 | 742 | 75 | LWB | 71.4
90 | 122 | 742 | 75 | kW | 1.28

## RZA24AAVJU - FCA24AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 777 | 57 | MBh | 15.6 | 64 | 60 | 61 | 32.4 | 1.93
68 | 23 | 777 | 57 | S/T | 0.949 | 64 | 60 | 65 | 30 | 1.76
68 | 23 | 777 | 57 | ∆T | 17.6 | 64 | 60 | 68 | 28.2 | 1.64
68 | 23 | 777 | 57 | LDB | 50.4 | 64 | 60 | 70 | 27 | 1.56
68 | 23 | 777 | 57 | LWB | 49.4 | 64 | 60 | 72 | 25.8 | 1.49
68 | 23 | 777 | 57 | kW | 0.53 | 64 | 60 | 75 | 24 | 1.4
72 | 23 | 777 | 61 | MBh | 18.9 | 60 | 56 | 61 | 32.4 | 2.02
72 | 23 | 777 | 61 | S/T | 0.91 | 60 | 56 | 65 | 30 | 1.83
72 | 23 | 777 | 61 | ∆T | 20.5 | 60 | 56 | 68 | 28.2 | 1.7
72 | 23 | 777 | 61 | LDB | 51.5 | 60 | 56 | 70 | 27 | 1.62
72 | 23 | 777 | 61 | LWB | 51.5 | 60 | 56 | 72 | 25.8 | 1.54
72 | 23 | 777 | 61 | kW | 0.65 | 60 | 56 | 75 | 24 | 1.44
77 | 23 | 777 | 64 | MBh | 21.5 | 57 | 53 | 61 | 32.4 | 2.09
77 | 23 | 777 | 64 | S/T | 0.879 | 57 | 53 | 65 | 30 | 1.89
77 | 23 | 777 | 64 | ∆T | 22.5 | 57 | 53 | 68 | 28.2 | 1.75
77 | 23 | 777 | 64 | LDB | 54.5 | 57 | 53 | 70 | 27 | 1.66
77 | 23 | 777 | 64 | LWB | 54.5 | 57 | 53 | 72 | 25.8 | 1.58
77 | 23 | 777 | 64 | kW | 0.74 | 57 | 53 | 75 | 24 | 1.47
80 | 23 | 777 | 67 | MBh | 24 | 54 | 50 | 61 | 32.4 | 2.17
80 | 23 | 777 | 67 | S/T | 0.829 | 54 | 50 | 65 | 30 | 1.95
80 | 23 | 777 | 67 | ∆T | 23.7 | 54 | 50 | 68 | 28.2 | 1.8
80 | 23 | 777 | 67 | LDB | 56.3 | 54 | 50 | 70 | 27 | 1.71
80 | 23 | 777 | 67 | LWB | 56.3 | 54 | 50 | 72 | 25.8 | 1.63
80 | 23 | 777 | 67 | kW | 0.84 | 54 | 50 | 75 | 24 | 1.51
84 | 23 | 777 | 70 | MBh | 26.5 | 51 | 47 | 61 | 32.4 | 2.26
84 | 23 | 777 | 70 | S/T | 0.804 | 51 | 47 | 65 | 30 | 2.03
84 | 23 | 777 | 70 | ∆T | 25.4 | 51 | 47 | 68 | 28.2 | 1.87
84 | 23 | 777 | 70 | LDB | 58.6 | 51 | 47 | 70 | 27 | 1.77
84 | 23 | 777 | 70 | LWB | 58.6 | 51 | 47 | 72 | 25.8 | 1.68
84 | 23 | 777 | 70 | kW | 0.94 | 51 | 47 | 75 | 24 | 1.55
86 | 23 | 777 | 72 | MBh | 28.2 | 47 | 43 | 61 | 32.4 | 2.39
86 | 23 | 777 | 72 | S/T | 0.759 | 47 | 43 | 65 | 30 | 2.13
86 | 23 | 777 | 72 | ∆T | 25.5 | 47 | 43 | 68 | 28.2 | 1.96
86 | 23 | 777 | 72 | LDB | 60.5 | 47 | 43 | 70 | 27 | 1.85
86 | 23 | 777 | 72 | LWB | 60.5 | 47 | 43 | 72 | 25.8 | 1.75
86 | 23 | 777 | 72 | kW | 1.01 | 47 | 43 | 75 | 24 | 1.61
90 | 23 | 777 | 75 | MBh | 30.7 | 44 | 40 | 61 | 32.4 | 2.5
90 | 23 | 777 | 75 | S/T | 0.733 | 44 | 40 | 65 | 30 | 2.22
90 | 23 | 777 | 75 | ∆T | 26.8 | 44 | 40 | 68 | 28.2 | 2.04
90 | 23 | 777 | 75 | LDB | 63.2 | 44 | 40 | 70 | 27 | 1.92
90 | 23 | 777 | 75 | LWB | 63.2 | 44 | 40 | 72 | 25.8 | 1.81
90 | 23 | 777 | 75 | kW | 1.12 | 44 | 40 | 75 | 24 | 1.66
68 | 30 | 777 | 57 | MBh | 15.6 | 39 | 36 | 61 | 32.4 | 2.66
68 | 30 | 777 | 57 | S/T | 0.949 | 39 | 36 | 65 | 30 | 2.36
68 | 30 | 777 | 57 | ∆T | 17.6 | 39 | 36 | 68 | 28.2 | 2.15
68 | 30 | 777 | 57 | LDB | 50.4 | 39 | 36 | 70 | 27 | 2.02
68 | 30 | 777 | 57 | LWB | 49.4 | 39 | 36 | 72 | 25.8 | 1.91
68 | 30 | 777 | 57 | kW | 0.54 | 39 | 36 | 75 | 24 | 1.74
72 | 30 | 777 | 61 | MBh | 18.9 | 35 | 32 | 61 | 32.4 | 2.74
72 | 30 | 777 | 61 | S/T | 0.91 | 35 | 32 | 65 | 30 | 2.51
72 | 30 | 777 | 61 | ∆T | 20.5 | 35 | 32 | 68 | 28.2 | 2.29
72 | 30 | 777 | 61 | LDB | 51.5 | 35 | 32 | 70 | 27 | 2.15
72 | 30 | 777 | 61 | LWB | 51.5 | 35 | 32 | 72 | 25.8 | 2.01
72 | 30 | 777 | 61 | kW | 0.67 | 35 | 32 | 75 | 24 | 1.83
77 | 30 | 777 | 64 | MBh | 21.5 | 30 | 28 | 61 | 31.8 | 2.75
77 | 30 | 777 | 64 | S/T | 0.879 | 30 | 28 | 65 | 30 | 2.69
77 | 30 | 777 | 64 | ∆T | 22.5 | 30 | 28 | 68 | 28.2 | 2.44
77 | 30 | 777 | 64 | LDB | 54.5 | 30 | 28 | 70 | 27 | 2.28
77 | 30 | 777 | 64 | LWB | 54.5 | 30 | 28 | 72 | 25.8 | 2.14
77 | 30 | 777 | 64 | kW | 0.77 | 30 | 28 | 75 | 24 | 1.94
80 | 30 | 777 | 67 | MBh | 24 | 26 | 24 | 61 | 30.4 | 2.77
80 | 30 | 777 | 67 | S/T | 0.829 | 26 | 24 | 65 | 30 | 2.74
80 | 30 | 777 | 67 | ∆T | 23.7 | 26 | 24 | 68 | 28.2 | 2.62
80 | 30 | 777 | 67 | LDB | 56.3 | 26 | 24 | 70 | 27 | 2.45
80 | 30 | 777 | 67 | LWB | 56.3 | 26 | 24 | 72 | 25.8 | 2.28
80 | 30 | 777 | 67 | kW | 0.87 | 26 | 24 | 75 | 24 | 2.06
84 | 30 | 777 | 70 | MBh | 26.5 | 22 | 20 | 61 | 29 | 2.8
84 | 30 | 777 | 70 | S/T | 0.804 | 22 | 20 | 65 | 29 | 2.76
84 | 30 | 777 | 70 | ∆T | 25.4 | 22 | 20 | 68 | 28.2 | 2.73
84 | 30 | 777 | 70 | LDB | 58.6 | 22 | 20 | 70 | 27 | 2.64
84 | 30 | 777 | 70 | LWB | 58.6 | 22 | 20 | 72 | 25.8 | 2.46
84 | 30 | 777 | 70 | kW | 0.97 | 22 | 20 | 75 | 24 | 2.2
86 | 30 | 777 | 72 | MBh | 28.2 | 19 | 18 | 61 | 28.3 | 2.81
86 | 30 | 777 | 72 | S/T | 0.759 | 19 | 18 | 65 | 28.3 | 2.77
86 | 30 | 777 | 72 | ∆T | 25.5 | 19 | 18 | 68 | 28.2 | 2.74
86 | 30 | 777 | 72 | LDB | 60.5 | 19 | 18 | 70 | 27 | 2.72
86 | 30 | 777 | 72 | LWB | 60.5 | 19 | 18 | 72 | 25.8 | 2.55
86 | 30 | 777 | 72 | kW | 1.05 | 19 | 18 | 75 | 24 | 2.28
90 | 30 | 777 | 75 | MBh | 30.7 | 17 | 16 | 61 | 27.5 | 2.82
90 | 30 | 777 | 75 | S/T | 0.733 | 17 | 16 | 65 | 27.5 | 2.78
90 | 30 | 777 | 75 | ∆T | 26.8 | 17 | 16 | 68 | 27.5 | 2.75
90 | 30 | 777 | 75 | LDB | 63.2 | 17 | 16 | 70 | 27 | 2.73
90 | 30 | 777 | 75 | LWB | 63.2 | 17 | 16 | 72 | 25.8 | 2.68
90 | 30 | 777 | 75 | kW | 1.16 | 17 | 16 | 75 | 24 | 2.39
68 | 40 | 777 | 57 | MBh | 15.6 | 15 | 14 | 61 | 26.9 | 2.83
68 | 40 | 777 | 57 | S/T | 0.949 | 15 | 14 | 65 | 26.9 | 2.79
68 | 40 | 777 | 57 | ∆T | 17.6 | 15 | 14 | 68 | 26.9 | 2.76
68 | 40 | 777 | 57 | LDB | 50.4 | 15 | 14 | 70 | 26.9 | 2.74
68 | 40 | 777 | 57 | LWB | 49.4 | 15 | 14 | 72 | 25.8 | 2.72
68 | 40 | 777 | 57 | kW | 0.57 | 15 | 14 | 75 | 24 | 2.47
72 | 40 | 777 | 61 | MBh | 18.9 | 13 | 12 | 61 | 26.3 | 2.85
72 | 40 | 777 | 61 | S/T | 0.91 | 13 | 12 | 65 | 26.3 | 2.81
72 | 40 | 777 | 61 | ∆T | 20.5 | 13 | 12 | 68 | 26.3 | 2.77
72 | 40 | 777 | 61 | LDB | 51.5 | 13 | 12 | 70 | 26.3 | 2.75
72 | 40 | 777 | 61 | LWB | 51.5 | 13 | 12 | 72 | 25.8 | 2.73
72 | 40 | 777 | 61 | kW | 0.7 | 13 | 12 | 75 | 24 | 2.57
77 | 40 | 777 | 64 | MBh | 21.5 | 10 | 9 | 61 | 25.1 | 2.88
77 | 40 | 777 | 64 | S/T | 0.879 | 10 | 9 | 65 | 25.1 | 2.83
77 | 40 | 777 | 64 | ∆T | 22.5 | 10 | 9 | 68 | 25.1 | 2.8
77 | 40 | 777 | 64 | LDB | 54.5 | 10 | 9 | 70 | 25.1 | 2.77
77 | 40 | 777 | 64 | LWB | 54.5 | 10 | 9 | 72 | 25.1 | 2.75
77 | 40 | 777 | 64 | kW | 0.8 | 10 | 9 | 75 | 24 | 2.72
80 | 40 | 777 | 67 | MBh | 24 | 6 | 5 | 61 | 23.8 | 2.91
80 | 40 | 777 | 67 | S/T | 0.829 | 6 | 5 | 65 | 23.8 | 2.86
80 | 40 | 777 | 67 | ∆T | 23.7 | 6 | 5 | 68 | 23.8 | 2.82
80 | 40 | 777 | 67 | LDB | 56.3 | 6 | 5 | 70 | 23.8 | 2.8
80 | 40 | 777 | 67 | LWB | 56.3 | 6 | 5 | 72 | 23.8 | 2.77
80 | 40 | 777 | 67 | kW | 0.91 | 6 | 5 | 75 | 23.8 | 2.74
84 | 40 | 777 | 70 | MBh | 26.5 | -2 | -2 | 61 | 21.4 | 2.98
84 | 40 | 777 | 70 | S/T | 0.804 | -2 | -2 | 65 | 21.4 | 2.93
84 | 40 | 777 | 70 | ∆T | 25.4 | -2 | -2 | 68 | 21.4 | 2.89
84 | 40 | 777 | 70 | LDB | 58.6 | -2 | -2 | 70 | 21.4 | 2.86
84 | 40 | 777 | 70 | LWB | 58.6 | -2 | -2 | 72 | 21.4 | 2.83
84 | 40 | 777 | 70 | kW | 1.02 | -2 | -2 | 75 | 21.4 | 2.79
86 | 40 | 777 | 72 | MBh | 28.2 | -4 | -4 | 61 | 20.8 | 3
86 | 40 | 777 | 72 | S/T | 0.759 | -4 | -4 | 65 | 20.8 | 2.95
86 | 40 | 777 | 72 | ∆T | 25.5 | -4 | -4 | 68 | 20.8 | 2.91
86 | 40 | 777 | 72 | LDB | 60.5 | -4 | -4 | 70 | 20.8 | 2.88
86 | 40 | 777 | 72 | LWB | 60.5 | -4 | -4 | 72 | 20.8 | 2.85
86 | 40 | 777 | 72 | kW | 1.1 | -4 | -4 | 75 | 20.8 | 2.81
90 | 40 | 777 | 75 | MBh | 30.7
90 | 40 | 777 | 75 | S/T | 0.733
90 | 40 | 777 | 75 | ∆T | 26.8
90 | 40 | 777 | 75 | LDB | 63.2
90 | 40 | 777 | 75 | LWB | 63.2
90 | 40 | 777 | 75 | kW | 1.21
68 | 50 | 777 | 57 | MBh | 15.6
68 | 50 | 777 | 57 | S/T | 0.949
68 | 50 | 777 | 57 | ∆T | 17.6
68 | 50 | 777 | 57 | LDB | 50.4
68 | 50 | 777 | 57 | LWB | 49.4
68 | 50 | 777 | 57 | kW | 0.59
72 | 50 | 777 | 61 | MBh | 18.9
72 | 50 | 777 | 61 | S/T | 0.91
72 | 50 | 777 | 61 | ∆T | 20.5
72 | 50 | 777 | 61 | LDB | 51.5
72 | 50 | 777 | 61 | LWB | 51.5
72 | 50 | 777 | 61 | kW | 0.73
77 | 50 | 777 | 64 | MBh | 21.5
77 | 50 | 777 | 64 | S/T | 0.879
77 | 50 | 777 | 64 | ∆T | 22.5
77 | 50 | 777 | 64 | LDB | 54.5
77 | 50 | 777 | 64 | LWB | 54.5
77 | 50 | 777 | 64 | kW | 0.84
80 | 50 | 777 | 67 | MBh | 24
80 | 50 | 777 | 67 | S/T | 0.829
80 | 50 | 777 | 67 | ∆T | 23.7
80 | 50 | 777 | 67 | LDB | 56.3
80 | 50 | 777 | 67 | LWB | 56.3
80 | 50 | 777 | 67 | kW | 0.96
84 | 50 | 777 | 70 | MBh | 26.5
84 | 50 | 777 | 70 | S/T | 0.804
84 | 50 | 777 | 70 | ∆T | 25.4
84 | 50 | 777 | 70 | LDB | 58.6
84 | 50 | 777 | 70 | LWB | 58.6
84 | 50 | 777 | 70 | kW | 1.08
86 | 50 | 777 | 72 | MBh | 28.2
86 | 50 | 777 | 72 | S/T | 0.759
86 | 50 | 777 | 72 | ∆T | 25.5
86 | 50 | 777 | 72 | LDB | 60.5
86 | 50 | 777 | 72 | LWB | 60.5
86 | 50 | 777 | 72 | kW | 1.16
90 | 50 | 777 | 75 | MBh | 30.7
90 | 50 | 777 | 75 | S/T | 0.733
90 | 50 | 777 | 75 | ∆T | 26.8
90 | 50 | 777 | 75 | LDB | 63.2
90 | 50 | 777 | 75 | LWB | 63.2
90 | 50 | 777 | 75 | kW | 1.28
68 | 54 | 777 | 57 | MBh | 15.6
68 | 54 | 777 | 57 | S/T | 0.949
68 | 54 | 777 | 57 | ∆T | 17.6
68 | 54 | 777 | 57 | LDB | 50.4
68 | 54 | 777 | 57 | LWB | 49.4
68 | 54 | 777 | 57 | kW | 0.6
72 | 54 | 777 | 61 | MBh | 18.9
72 | 54 | 777 | 61 | S/T | 0.91
72 | 54 | 777 | 61 | ∆T | 20.5
72 | 54 | 777 | 61 | LDB | 51.5
72 | 54 | 777 | 61 | LWB | 51.5
72 | 54 | 777 | 61 | kW | 0.75
77 | 54 | 777 | 64 | MBh | 21.5
77 | 54 | 777 | 64 | S/T | 0.879
77 | 54 | 777 | 64 | ∆T | 22.5
77 | 54 | 777 | 64 | LDB | 54.5
77 | 54 | 777 | 64 | LWB | 54.5
77 | 54 | 777 | 64 | kW | 0.86
80 | 54 | 777 | 67 | MBh | 24
80 | 54 | 777 | 67 | S/T | 0.829
80 | 54 | 777 | 67 | ∆T | 23.7
80 | 54 | 777 | 67 | LDB | 56.3
80 | 54 | 777 | 67 | LWB | 56.3
80 | 54 | 777 | 67 | kW | 0.98
84 | 54 | 777 | 70 | MBh | 26.5
84 | 54 | 777 | 70 | S/T | 0.804
84 | 54 | 777 | 70 | ∆T | 25.4
84 | 54 | 777 | 70 | LDB | 58.6
84 | 54 | 777 | 70 | LWB | 58.6
84 | 54 | 777 | 70 | kW | 1.1
86 | 54 | 777 | 72 | MBh | 28.2
86 | 54 | 777 | 72 | S/T | 0.759
86 | 54 | 777 | 72 | ∆T | 25.5
86 | 54 | 777 | 72 | LDB | 60.5
86 | 54 | 777 | 72 | LWB | 60.5
86 | 54 | 777 | 72 | kW | 1.18
90 | 54 | 777 | 75 | MBh | 30.7
90 | 54 | 777 | 75 | S/T | 0.733
90 | 54 | 777 | 75 | ∆T | 26.8
90 | 54 | 777 | 75 | LDB | 63.2
90 | 54 | 777 | 75 | LWB | 63.2
90 | 54 | 777 | 75 | kW | 1.3
68 | 58 | 777 | 57 | MBh | 15.6
68 | 58 | 777 | 57 | S/T | 0.949
68 | 58 | 777 | 57 | ∆T | 17.6
68 | 58 | 777 | 57 | LDB | 50.4
68 | 58 | 777 | 57 | LWB | 49.4
68 | 58 | 777 | 57 | kW | 0.62
72 | 58 | 777 | 61 | MBh | 18.9
72 | 58 | 777 | 61 | S/T | 0.91
72 | 58 | 777 | 61 | ∆T | 20.5
72 | 58 | 777 | 61 | LDB | 51.5
72 | 58 | 777 | 61 | LWB | 51.5
72 | 58 | 777 | 61 | kW | 0.76
77 | 58 | 777 | 64 | MBh | 21.5
77 | 58 | 777 | 64 | S/T | 0.879
77 | 58 | 777 | 64 | ∆T | 22.5
77 | 58 | 777 | 64 | LDB | 54.5
77 | 58 | 777 | 64 | LWB | 54.5
77 | 58 | 777 | 64 | kW | 0.88
80 | 58 | 777 | 67 | MBh | 24
80 | 58 | 777 | 67 | S/T | 0.829
80 | 58 | 777 | 67 | ∆T | 23.7
80 | 58 | 777 | 67 | LDB | 56.3
80 | 58 | 777 | 67 | LWB | 56.3
80 | 58 | 777 | 67 | kW | 1
84 | 58 | 777 | 70 | MBh | 26.5
84 | 58 | 777 | 70 | S/T | 0.804
84 | 58 | 777 | 70 | ∆T | 25.4
84 | 58 | 777 | 70 | LDB | 58.6
84 | 58 | 777 | 70 | LWB | 58.6
84 | 58 | 777 | 70 | kW | 1.12
86 | 58 | 777 | 72 | MBh | 28.2
86 | 58 | 777 | 72 | S/T | 0.759
86 | 58 | 777 | 72 | ∆T | 25.5
86 | 58 | 777 | 72 | LDB | 60.5
86 | 58 | 777 | 72 | LWB | 60.5
86 | 58 | 777 | 72 | kW | 1.2
90 | 58 | 777 | 75 | MBh | 30.5
90 | 58 | 777 | 75 | S/T | 0.731
90 | 58 | 777 | 75 | ∆T | 26.6
90 | 58 | 777 | 75 | LDB | 63.4
90 | 58 | 777 | 75 | LWB | 63.4
90 | 58 | 777 | 75 | kW | 1.31
68 | 62 | 777 | 57 | MBh | 15.6
68 | 62 | 777 | 57 | S/T | 0.949
68 | 62 | 777 | 57 | ∆T | 17.6
68 | 62 | 777 | 57 | LDB | 50.4
68 | 62 | 777 | 57 | LWB | 49.4
68 | 62 | 777 | 57 | kW | 0.63
72 | 62 | 777 | 61 | MBh | 18.9
72 | 62 | 777 | 61 | S/T | 0.91
72 | 62 | 777 | 61 | ∆T | 20.5
72 | 62 | 777 | 61 | LDB | 51.5
72 | 62 | 777 | 61 | LWB | 51.5
72 | 62 | 777 | 61 | kW | 0.78
77 | 62 | 777 | 64 | MBh | 21.5
77 | 62 | 777 | 64 | S/T | 0.879
77 | 62 | 777 | 64 | ∆T | 22.5
77 | 62 | 777 | 64 | LDB | 54.5
77 | 62 | 777 | 64 | LWB | 54.5
77 | 62 | 777 | 64 | kW | 0.9
80 | 62 | 777 | 67 | MBh | 24
80 | 62 | 777 | 67 | S/T | 0.829
80 | 62 | 777 | 67 | ∆T | 23.7
80 | 62 | 777 | 67 | LDB | 56.3
80 | 62 | 777 | 67 | LWB | 56.3
80 | 62 | 777 | 67 | kW | 1.02
84 | 62 | 777 | 70 | MBh | 26.5
84 | 62 | 777 | 70 | S/T | 0.804
84 | 62 | 777 | 70 | ∆T | 25.4
84 | 62 | 777 | 70 | LDB | 58.6
84 | 62 | 777 | 70 | LWB | 58.6
84 | 62 | 777 | 70 | kW | 1.15
86 | 62 | 777 | 72 | MBh | 28.2
86 | 62 | 777 | 72 | S/T | 0.759
86 | 62 | 777 | 72 | ∆T | 25.5
86 | 62 | 777 | 72 | LDB | 60.5
86 | 62 | 777 | 72 | LWB | 60.5
86 | 62 | 777 | 72 | kW | 1.23
90 | 62 | 777 | 75 | MBh | 30
90 | 62 | 777 | 75 | S/T | 0.73
90 | 62 | 777 | 75 | ∆T | 26.1
90 | 62 | 777 | 75 | LDB | 63.9
90 | 62 | 777 | 75 | LWB | 63.9
90 | 62 | 777 | 75 | kW | 1.3
68 | 66 | 777 | 57 | MBh | 15.6
68 | 66 | 777 | 57 | S/T | 0.949
68 | 66 | 777 | 57 | ∆T | 17.6
68 | 66 | 777 | 57 | LDB | 50.4
68 | 66 | 777 | 57 | LWB | 49.4
68 | 66 | 777 | 57 | kW | 0.64
72 | 66 | 777 | 61 | MBh | 18.9
72 | 66 | 777 | 61 | S/T | 0.91
72 | 66 | 777 | 61 | ∆T | 20.5
72 | 66 | 777 | 61 | LDB | 51.5
72 | 66 | 777 | 61 | LWB | 51.5
72 | 66 | 777 | 61 | kW | 0.8
77 | 66 | 777 | 64 | MBh | 21.5
77 | 66 | 777 | 64 | S/T | 0.879
77 | 66 | 777 | 64 | ∆T | 22.5
77 | 66 | 777 | 64 | LDB | 54.5
77 | 66 | 777 | 64 | LWB | 54.5
77 | 66 | 777 | 64 | kW | 0.92
80 | 66 | 777 | 67 | MBh | 24
80 | 66 | 777 | 67 | S/T | 0.829
80 | 66 | 777 | 67 | ∆T | 23.7
80 | 66 | 777 | 67 | LDB | 56.3
80 | 66 | 777 | 67 | LWB | 56.3
80 | 66 | 777 | 67 | kW | 1.04
84 | 66 | 777 | 70 | MBh | 26.5
84 | 66 | 777 | 70 | S/T | 0.804
84 | 66 | 777 | 70 | ∆T | 25.4
84 | 66 | 777 | 70 | LDB | 58.6
84 | 66 | 777 | 70 | LWB | 58.6
84 | 66 | 777 | 70 | kW | 1.17
86 | 66 | 777 | 72 | MBh | 28.2
86 | 66 | 777 | 72 | S/T | 0.759
86 | 66 | 777 | 72 | ∆T | 25.5
86 | 66 | 777 | 72 | LDB | 60.5
86 | 66 | 777 | 72 | LWB | 60.5
86 | 66 | 777 | 72 | kW | 1.26
90 | 66 | 777 | 75 | MBh | 29.6
90 | 66 | 777 | 75 | S/T | 0.73
90 | 66 | 777 | 75 | ∆T | 25.7
90 | 66 | 777 | 75 | LDB | 64.3
90 | 66 | 777 | 75 | LWB | 64.3
90 | 66 | 777 | 75 | kW | 1.29
68 | 70 | 777 | 57 | MBh | 15.6
68 | 70 | 777 | 57 | S/T | 0.949
68 | 70 | 777 | 57 | ∆T | 17.6
68 | 70 | 777 | 57 | LDB | 50.4
68 | 70 | 777 | 57 | LWB | 49.4
68 | 70 | 777 | 57 | kW | 0.65
72 | 70 | 777 | 61 | MBh | 18.9
72 | 70 | 777 | 61 | S/T | 0.91
72 | 70 | 777 | 61 | ∆T | 20.5
72 | 70 | 777 | 61 | LDB | 51.5
72 | 70 | 777 | 61 | LWB | 51.5
72 | 70 | 777 | 61 | kW | 0.81
77 | 70 | 777 | 64 | MBh | 21.5
77 | 70 | 777 | 64 | S/T | 0.879
77 | 70 | 777 | 64 | ∆T | 22.5
77 | 70 | 777 | 64 | LDB | 54.5
77 | 70 | 777 | 64 | LWB | 54.5
77 | 70 | 777 | 64 | kW | 0.94
80 | 70 | 777 | 67 | MBh | 24
80 | 70 | 777 | 67 | S/T | 0.829
80 | 70 | 777 | 67 | ∆T | 23.7
80 | 70 | 777 | 67 | LDB | 56.3
80 | 70 | 777 | 67 | LWB | 56.3
80 | 70 | 777 | 67 | kW | 1.07
84 | 70 | 777 | 70 | MBh | 26.5
84 | 70 | 777 | 70 | S/T | 0.804
84 | 70 | 777 | 70 | ∆T | 25.4
84 | 70 | 777 | 70 | LDB | 58.6
84 | 70 | 777 | 70 | LWB | 58.6
84 | 70 | 777 | 70 | kW | 1.2
86 | 70 | 777 | 72 | MBh | 28.2
86 | 70 | 777 | 72 | S/T | 0.759
86 | 70 | 777 | 72 | ∆T | 25.5
86 | 70 | 777 | 72 | LDB | 60.5
86 | 70 | 777 | 72 | LWB | 60.5
86 | 70 | 777 | 72 | kW | 1.29
90 | 70 | 777 | 75 | MBh | 29.1
90 | 70 | 777 | 75 | S/T | 0.732
90 | 70 | 777 | 75 | ∆T | 25.4
90 | 70 | 777 | 75 | LDB | 64.6
90 | 70 | 777 | 75 | LWB | 64.6
90 | 70 | 777 | 75 | kW | 1.28
68 | 72 | 777 | 57 | MBh | 15.6
68 | 72 | 777 | 57 | S/T | 0.949
68 | 72 | 777 | 57 | ∆T | 17.6
68 | 72 | 777 | 57 | LDB | 50.4
68 | 72 | 777 | 57 | LWB | 49.4
68 | 72 | 777 | 57 | kW | 0.66
72 | 72 | 777 | 61 | MBh | 18.9
72 | 72 | 777 | 61 | S/T | 0.91
72 | 72 | 777 | 61 | ∆T | 20.5
72 | 72 | 777 | 61 | LDB | 51.5
72 | 72 | 777 | 61 | LWB | 51.5
72 | 72 | 777 | 61 | kW | 0.82
77 | 72 | 777 | 64 | MBh | 21.5
77 | 72 | 777 | 64 | S/T | 0.879
77 | 72 | 777 | 64 | ∆T | 22.5
77 | 72 | 777 | 64 | LDB | 54.5
77 | 72 | 777 | 64 | LWB | 54.5
77 | 72 | 777 | 64 | kW | 0.95
80 | 72 | 777 | 67 | MBh | 24
80 | 72 | 777 | 67 | S/T | 0.829
80 | 72 | 777 | 67 | ∆T | 23.7
80 | 72 | 777 | 67 | LDB | 56.3
80 | 72 | 777 | 67 | LWB | 56.3
80 | 72 | 777 | 67 | kW | 1.08
84 | 72 | 777 | 70 | MBh | 26.5
84 | 72 | 777 | 70 | S/T | 0.804
84 | 72 | 777 | 70 | ∆T | 25.4
84 | 72 | 777 | 70 | LDB | 58.6
84 | 72 | 777 | 70 | LWB | 58.6
84 | 72 | 777 | 70 | kW | 1.21
86 | 72 | 777 | 72 | MBh | 28.2
86 | 72 | 777 | 72 | S/T | 0.759
86 | 72 | 777 | 72 | ∆T | 25.5
86 | 72 | 777 | 72 | LDB | 60.5
86 | 72 | 777 | 72 | LWB | 60.5
86 | 72 | 777 | 72 | kW | 1.3
90 | 72 | 777 | 75 | MBh | 28.9
90 | 72 | 777 | 75 | S/T | 0.73
90 | 72 | 777 | 75 | ∆T | 25.1
90 | 72 | 777 | 75 | LDB | 64.9
90 | 72 | 777 | 75 | LWB | 64.9
90 | 72 | 777 | 75 | kW | 1.28
68 | 75 | 777 | 57 | MBh | 15.6
68 | 75 | 777 | 57 | S/T | 0.949
68 | 75 | 777 | 57 | ∆T | 17.6
68 | 75 | 777 | 57 | LDB | 50.4
68 | 75 | 777 | 57 | LWB | 49.4
68 | 75 | 777 | 57 | kW | 0.67
72 | 75 | 777 | 61 | MBh | 18.9
72 | 75 | 777 | 61 | S/T | 0.91
72 | 75 | 777 | 61 | ∆T | 20.5
72 | 75 | 777 | 61 | LDB | 51.5
72 | 75 | 777 | 61 | LWB | 51.5
72 | 75 | 777 | 61 | kW | 0.84
77 | 75 | 777 | 64 | MBh | 21.5
77 | 75 | 777 | 64 | S/T | 0.879
77 | 75 | 777 | 64 | ∆T | 22.5
77 | 75 | 777 | 64 | LDB | 54.5
77 | 75 | 777 | 64 | LWB | 54.5
77 | 75 | 777 | 64 | kW | 0.97
80 | 75 | 777 | 67 | MBh | 24
80 | 75 | 777 | 67 | S/T | 0.829
80 | 75 | 777 | 67 | ∆T | 23.7
80 | 75 | 777 | 67 | LDB | 56.3
80 | 75 | 777 | 67 | LWB | 56.3
80 | 75 | 777 | 67 | kW | 1.1
84 | 75 | 777 | 70 | MBh | 26.5
84 | 75 | 777 | 70 | S/T | 0.804
84 | 75 | 777 | 70 | ∆T | 25.4
84 | 75 | 777 | 70 | LDB | 58.6
84 | 75 | 777 | 70 | LWB | 58.6
84 | 75 | 777 | 70 | kW | 1.23
86 | 75 | 777 | 72 | MBh | 28
86 | 75 | 777 | 72 | S/T | 0.761
86 | 75 | 777 | 72 | ∆T | 25.4
86 | 75 | 777 | 72 | LDB | 60.6
86 | 75 | 777 | 72 | LWB | 60.6
86 | 75 | 777 | 72 | kW | 1.31
90 | 75 | 777 | 75 | MBh | 28.5
90 | 75 | 777 | 75 | S/T | 0.733
90 | 75 | 777 | 75 | ∆T | 24.9
90 | 75 | 777 | 75 | LDB | 65.1
90 | 75 | 777 | 75 | LWB | 65.1
90 | 75 | 777 | 75 | kW | 1.31
68 | 79 | 777 | 57 | MBh | 15.6
68 | 79 | 777 | 57 | S/T | 0.949
68 | 79 | 777 | 57 | ∆T | 17.6
68 | 79 | 777 | 57 | LDB | 50.4
68 | 79 | 777 | 57 | LWB | 49.4
68 | 79 | 777 | 57 | kW | 0.69
72 | 79 | 777 | 61 | MBh | 18.9
72 | 79 | 777 | 61 | S/T | 0.91
72 | 79 | 777 | 61 | ∆T | 20.5
72 | 79 | 777 | 61 | LDB | 51.5
72 | 79 | 777 | 61 | LWB | 51.5
72 | 79 | 777 | 61 | kW | 0.86
77 | 79 | 777 | 64 | MBh | 21.5
77 | 79 | 777 | 64 | S/T | 0.879
77 | 79 | 777 | 64 | ∆T | 22.5
77 | 79 | 777 | 64 | LDB | 54.5
77 | 79 | 777 | 64 | LWB | 54.5
77 | 79 | 777 | 64 | kW | 1
80 | 79 | 777 | 67 | MBh | 24
80 | 79 | 777 | 67 | S/T | 0.829
80 | 79 | 777 | 67 | ∆T | 23.7
80 | 79 | 777 | 67 | LDB | 56.3
80 | 79 | 777 | 67 | LWB | 56.3
80 | 79 | 777 | 67 | kW | 1.18
84 | 79 | 777 | 70 | MBh | 26.5
84 | 79 | 777 | 70 | S/T | 0.804
84 | 79 | 777 | 70 | ∆T | 25.4
84 | 79 | 777 | 70 | LDB | 58.6
84 | 79 | 777 | 70 | LWB | 58.6
84 | 79 | 777 | 70 | kW | 1.37
86 | 79 | 777 | 72 | MBh | 27.6
86 | 79 | 777 | 72 | S/T | 0.757
86 | 79 | 777 | 72 | ∆T | 24.9
86 | 79 | 777 | 72 | LDB | 61.1
86 | 79 | 777 | 72 | LWB | 61.1
86 | 79 | 777 | 72 | kW | 1.44
90 | 79 | 777 | 75 | MBh | 28.1
90 | 79 | 777 | 75 | S/T | 0.73
90 | 79 | 777 | 75 | ∆T | 24.4
90 | 79 | 777 | 75 | LDB | 65.6
90 | 79 | 777 | 75 | LWB | 65.4
90 | 79 | 777 | 75 | kW | 1.45
68 | 83 | 777 | 57 | MBh | 15.6
68 | 83 | 777 | 57 | S/T | 0.949
68 | 83 | 777 | 57 | ∆T | 17.6
68 | 83 | 777 | 57 | LDB | 50.4
68 | 83 | 777 | 57 | LWB | 49.4
68 | 83 | 777 | 57 | kW | 0.73
72 | 83 | 777 | 61 | MBh | 18.9
72 | 83 | 777 | 61 | S/T | 0.91
72 | 83 | 777 | 61 | ∆T | 20.5
72 | 83 | 777 | 61 | LDB | 51.5
72 | 83 | 777 | 61 | LWB | 51.5
72 | 83 | 777 | 61 | kW | 0.95
77 | 83 | 777 | 64 | MBh | 21.5
77 | 83 | 777 | 64 | S/T | 0.879
77 | 83 | 777 | 64 | ∆T | 22.5
77 | 83 | 777 | 64 | LDB | 54.5
77 | 83 | 777 | 64 | LWB | 54.5
77 | 83 | 777 | 64 | kW | 1.13
80 | 83 | 777 | 67 | MBh | 24
80 | 83 | 777 | 67 | S/T | 0.829
80 | 83 | 777 | 67 | ∆T | 23.7
80 | 83 | 777 | 67 | LDB | 56.3
80 | 83 | 777 | 67 | LWB | 56.3
80 | 83 | 777 | 67 | kW | 1.33
84 | 83 | 777 | 70 | MBh | 26.5
84 | 83 | 777 | 70 | S/T | 0.804
84 | 83 | 777 | 70 | ∆T | 25.4
84 | 83 | 777 | 70 | LDB | 58.6
84 | 83 | 777 | 70 | LWB | 58.6
84 | 83 | 777 | 70 | kW | 1.55
86 | 83 | 777 | 72 | MBh | 27.1
86 | 83 | 777 | 72 | S/T | 0.76
86 | 83 | 777 | 72 | ∆T | 24.5
86 | 83 | 777 | 72 | LDB | 61.5
86 | 83 | 777 | 72 | LWB | 61.5
86 | 83 | 777 | 72 | kW | 1.59
90 | 83 | 777 | 75 | MBh | 27.6
90 | 83 | 777 | 75 | S/T | 0.732
90 | 83 | 777 | 75 | ∆T | 24.1
90 | 83 | 777 | 75 | LDB | 65.9
90 | 83 | 777 | 75 | LWB | 65.6
90 | 83 | 777 | 75 | kW | 1.6
68 | 87 | 777 | 57 | MBh | 15.6
68 | 87 | 777 | 57 | S/T | 0.949
68 | 87 | 777 | 57 | ∆T | 17.6
68 | 87 | 777 | 57 | LDB | 50.4
68 | 87 | 777 | 57 | LWB | 49.4
68 | 87 | 777 | 57 | kW | 0.81
72 | 87 | 777 | 61 | MBh | 18.9
72 | 87 | 777 | 61 | S/T | 0.91
72 | 87 | 777 | 61 | ∆T | 20.5
72 | 87 | 777 | 61 | LDB | 51.5
72 | 87 | 777 | 61 | LWB | 51.5
72 | 87 | 777 | 61 | kW | 1.06
77 | 87 | 777 | 64 | MBh | 21.5
77 | 87 | 777 | 64 | S/T | 0.879
77 | 87 | 777 | 64 | ∆T | 22.5
77 | 87 | 777 | 64 | LDB | 54.5
77 | 87 | 777 | 64 | LWB | 54.5
77 | 87 | 777 | 64 | kW | 1.27
80 | 87 | 777 | 67 | MBh | 24
80 | 87 | 777 | 67 | S/T | 0.829
80 | 87 | 777 | 67 | ∆T | 23.7
80 | 87 | 777 | 67 | LDB | 56.3
80 | 87 | 777 | 67 | LWB | 56.3
80 | 87 | 777 | 67 | kW | 1.49
84 | 87 | 777 | 70 | MBh | 26.4
84 | 87 | 777 | 70 | S/T | 0.803
84 | 87 | 777 | 70 | ∆T | 25.3
84 | 87 | 777 | 70 | LDB | 58.7
84 | 87 | 777 | 70 | LWB | 58.7
84 | 87 | 777 | 70 | kW | 1.72
86 | 87 | 777 | 72 | MBh | 26.7
86 | 87 | 777 | 72 | S/T | 0.757
86 | 87 | 777 | 72 | ∆T | 24.1
86 | 87 | 777 | 72 | LDB | 61.9
86 | 87 | 777 | 72 | LWB | 61.9
86 | 87 | 777 | 72 | kW | 1.73
90 | 87 | 777 | 75 | MBh | 27.2
90 | 87 | 777 | 75 | S/T | 0.732
90 | 87 | 777 | 75 | ∆T | 23.7
90 | 87 | 777 | 75 | LDB | 66.3
90 | 87 | 777 | 75 | LWB | 65.8
90 | 87 | 777 | 75 | kW | 1.74
68 | 91 | 777 | 57 | MBh | 15.6
68 | 91 | 777 | 57 | S/T | 0.949
68 | 91 | 777 | 57 | ∆T | 17.6
68 | 91 | 777 | 57 | LDB | 50.4
68 | 91 | 777 | 57 | LWB | 49.4
68 | 91 | 777 | 57 | kW | 0.9
72 | 91 | 777 | 61 | MBh | 18.9
72 | 91 | 777 | 61 | S/T | 0.91
72 | 91 | 777 | 61 | ∆T | 20.5
72 | 91 | 777 | 61 | LDB | 51.5
72 | 91 | 777 | 61 | LWB | 51.5
72 | 91 | 777 | 61 | kW | 1.18
77 | 91 | 777 | 64 | MBh | 21.5
77 | 91 | 777 | 64 | S/T | 0.879
77 | 91 | 777 | 64 | ∆T | 22.5
77 | 91 | 777 | 64 | LDB | 54.5
77 | 91 | 777 | 64 | LWB | 54.5
77 | 91 | 777 | 64 | kW | 1.41
80 | 91 | 777 | 67 | MBh | 24
80 | 91 | 777 | 67 | S/T | 0.829
80 | 91 | 777 | 67 | ∆T | 23.7
80 | 91 | 777 | 67 | LDB | 56.3
80 | 91 | 777 | 67 | LWB | 56.3
80 | 91 | 777 | 67 | kW | 1.67
84 | 91 | 777 | 70 | MBh | 25.9
84 | 91 | 777 | 70 | S/T | 0.803
84 | 91 | 777 | 70 | ∆T | 24.8
84 | 91 | 777 | 70 | LDB | 59.2
84 | 91 | 777 | 70 | LWB | 59.2
84 | 91 | 777 | 70 | kW | 1.86
86 | 91 | 777 | 72 | MBh | 26.2
86 | 91 | 777 | 72 | S/T | 0.76
86 | 91 | 777 | 72 | ∆T | 23.7
86 | 91 | 777 | 72 | LDB | 62.3
86 | 91 | 777 | 72 | LWB | 62.3
86 | 91 | 777 | 72 | kW | 1.87
90 | 91 | 777 | 75 | MBh | 26.7
90 | 91 | 777 | 75 | S/T | 0.734
90 | 91 | 777 | 75 | ∆T | 23.4
90 | 91 | 777 | 75 | LDB | 66.6
90 | 91 | 777 | 75 | LWB | 66
90 | 91 | 777 | 75 | kW | 1.88
68 | 93 | 777 | 57 | MBh | 15.6
68 | 93 | 777 | 57 | S/T | 0.949
68 | 93 | 777 | 57 | ∆T | 17.6
68 | 93 | 777 | 57 | LDB | 50.4
68 | 93 | 777 | 57 | LWB | 49.4
68 | 93 | 777 | 57 | kW | 0.95
72 | 93 | 777 | 61 | MBh | 18.9
72 | 93 | 777 | 61 | S/T | 0.91
72 | 93 | 777 | 61 | ∆T | 20.5
72 | 93 | 777 | 61 | LDB | 51.5
72 | 93 | 777 | 61 | LWB | 51.5
72 | 93 | 777 | 61 | kW | 1.24
77 | 93 | 777 | 64 | MBh | 21.5
77 | 93 | 777 | 64 | S/T | 0.879
77 | 93 | 777 | 64 | ∆T | 22.5
77 | 93 | 777 | 64 | LDB | 54.5
77 | 93 | 777 | 64 | LWB | 54.5
77 | 93 | 777 | 64 | kW | 1.49
80 | 93 | 777 | 67 | MBh | 24
80 | 93 | 777 | 67 | S/T | 0.829
80 | 93 | 777 | 67 | ∆T | 23.7
80 | 93 | 777 | 67 | LDB | 56.3
80 | 93 | 777 | 67 | LWB | 56.3
80 | 93 | 777 | 67 | kW | 1.76
84 | 93 | 777 | 70 | MBh | 25.7
84 | 93 | 777 | 70 | S/T | 0.805
84 | 93 | 777 | 70 | ∆T | 24.7
84 | 93 | 777 | 70 | LDB | 59.3
84 | 93 | 777 | 70 | LWB | 59.3
84 | 93 | 777 | 70 | kW | 1.93
86 | 93 | 777 | 72 | MBh | 26
86 | 93 | 777 | 72 | S/T | 0.758
86 | 93 | 777 | 72 | ∆T | 23.5
86 | 93 | 777 | 72 | LDB | 62.5
86 | 93 | 777 | 72 | LWB | 62.5
86 | 93 | 777 | 72 | kW | 1.94
90 | 93 | 777 | 75 | MBh | 26.5
90 | 93 | 777 | 75 | S/T | 0.732
90 | 93 | 777 | 75 | ∆T | 23.1
90 | 93 | 777 | 75 | LDB | 66.9
90 | 93 | 777 | 75 | LWB | 66
90 | 93 | 777 | 75 | kW | 1.95
68 | 95 | 777 | 57 | MBh | 15.6
68 | 95 | 777 | 57 | S/T | 0.949
68 | 95 | 777 | 57 | ∆T | 17.6
68 | 95 | 777 | 57 | LDB | 50.4
68 | 95 | 777 | 57 | LWB | 49.4
68 | 95 | 777 | 57 | kW | 1
72 | 95 | 777 | 61 | MBh | 18.9
72 | 95 | 777 | 61 | S/T | 0.91
72 | 95 | 777 | 61 | ∆T | 20.5
72 | 95 | 777 | 61 | LDB | 51.5
72 | 95 | 777 | 61 | LWB | 51.5
72 | 95 | 777 | 61 | kW | 1.31
77 | 95 | 777 | 64 | MBh | 21.5
77 | 95 | 777 | 64 | S/T | 0.879
77 | 95 | 777 | 64 | ∆T | 22.5
77 | 95 | 777 | 64 | LDB | 54.5
77 | 95 | 777 | 64 | LWB | 54.5
77 | 95 | 777 | 64 | kW | 1.57
80 | 95 | 777 | 67 | MBh | 24
80 | 95 | 777 | 67 | S/T | 0.829
80 | 95 | 777 | 67 | ∆T | 23.7
80 | 95 | 777 | 67 | LDB | 56.3
80 | 95 | 777 | 67 | LWB | 56.3
80 | 95 | 777 | 67 | kW | 1.85
84 | 95 | 777 | 70 | MBh | 25.5
84 | 95 | 777 | 70 | S/T | 0.804
84 | 95 | 777 | 70 | ∆T | 24.4
84 | 95 | 777 | 70 | LDB | 59.6
84 | 95 | 777 | 70 | LWB | 59.6
84 | 95 | 777 | 70 | kW | 2
86 | 95 | 777 | 72 | MBh | 25.8
86 | 95 | 777 | 72 | S/T | 0.76
86 | 95 | 777 | 72 | ∆T | 23.4
86 | 95 | 777 | 72 | LDB | 62.6
86 | 95 | 777 | 72 | LWB | 62.6
86 | 95 | 777 | 72 | kW | 2.01
90 | 95 | 777 | 75 | MBh | 26.3
90 | 95 | 777 | 75 | S/T | 0.73
90 | 95 | 777 | 75 | ∆T | 22.9
90 | 95 | 777 | 75 | LDB | 67.1
90 | 95 | 777 | 75 | LWB | 66.1
90 | 95 | 777 | 75 | kW | 2.03
68 | 99 | 777 | 57 | MBh | 15.6
68 | 99 | 777 | 57 | S/T | 0.949
68 | 99 | 777 | 57 | ∆T | 17.6
68 | 99 | 777 | 57 | LDB | 50.4
68 | 99 | 777 | 57 | LWB | 49.4
68 | 99 | 777 | 57 | kW | 1.1
72 | 99 | 777 | 61 | MBh | 18.9
72 | 99 | 777 | 61 | S/T | 0.91
72 | 99 | 777 | 61 | ∆T | 20.5
72 | 99 | 777 | 61 | LDB | 51.5
72 | 99 | 777 | 61 | LWB | 51.5
72 | 99 | 777 | 61 | kW | 1.45
77 | 99 | 777 | 64 | MBh | 21.5
77 | 99 | 777 | 64 | S/T | 0.879
77 | 99 | 777 | 64 | ∆T | 22.5
77 | 99 | 777 | 64 | LDB | 54.5
77 | 99 | 777 | 64 | LWB | 54.5
77 | 99 | 777 | 64 | kW | 1.74
80 | 99 | 777 | 67 | MBh | 24
80 | 99 | 777 | 67 | S/T | 0.829
80 | 99 | 777 | 67 | ∆T | 23.7
80 | 99 | 777 | 67 | LDB | 56.3
80 | 99 | 777 | 67 | LWB | 56.3
80 | 99 | 777 | 67 | kW | 2.05
84 | 99 | 777 | 70 | MBh | 25
84 | 99 | 777 | 70 | S/T | 0.804
84 | 99 | 777 | 70 | ∆T | 24
84 | 99 | 777 | 70 | LDB | 60
84 | 99 | 777 | 70 | LWB | 60
84 | 99 | 777 | 70 | kW | 2.15
86 | 99 | 777 | 72 | MBh | 25.3
86 | 99 | 777 | 72 | S/T | 0.759
86 | 99 | 777 | 72 | ∆T | 22.9
86 | 99 | 777 | 72 | LDB | 63.1
86 | 99 | 777 | 72 | LWB | 62.8
86 | 99 | 777 | 72 | kW | 2.16
90 | 99 | 777 | 75 | MBh | 25.8
90 | 99 | 777 | 75 | S/T | 0.733
90 | 99 | 777 | 75 | ∆T | 22.5
90 | 99 | 777 | 75 | LDB | 67.5
90 | 99 | 777 | 75 | LWB | 66.3
90 | 99 | 777 | 75 | kW | 2.17
68 | 103 | 777 | 57 | MBh | 15.6
68 | 103 | 777 | 57 | S/T | 0.949
68 | 103 | 777 | 57 | ∆T | 17.6
68 | 103 | 777 | 57 | LDB | 50.4
68 | 103 | 777 | 57 | LWB | 49.4
68 | 103 | 777 | 57 | kW | 1.21
72 | 103 | 777 | 61 | MBh | 18.9
72 | 103 | 777 | 61 | S/T | 0.91
72 | 103 | 777 | 61 | ∆T | 20.5
72 | 103 | 777 | 61 | LDB | 51.5
72 | 103 | 777 | 61 | LWB | 51.5
72 | 103 | 777 | 61 | kW | 1.59
77 | 103 | 777 | 64 | MBh | 21.5
77 | 103 | 777 | 64 | S/T | 0.879
77 | 103 | 777 | 64 | ∆T | 22.5
77 | 103 | 777 | 64 | LDB | 54.5
77 | 103 | 777 | 64 | LWB | 54.5
77 | 103 | 777 | 64 | kW | 1.91
80 | 103 | 777 | 67 | MBh | 24
80 | 103 | 777 | 67 | S/T | 0.829
80 | 103 | 777 | 67 | ∆T | 23.7
80 | 103 | 777 | 67 | LDB | 56.3
80 | 103 | 777 | 67 | LWB | 56.3
80 | 103 | 777 | 67 | kW | 2.26
84 | 103 | 777 | 70 | MBh | 24.6
84 | 103 | 777 | 70 | S/T | 0.801
84 | 103 | 777 | 70 | ∆T | 23.5
84 | 103 | 777 | 70 | LDB | 60.5
84 | 103 | 777 | 70 | LWB | 60.5
84 | 103 | 777 | 70 | kW | 2.29
86 | 103 | 777 | 72 | MBh | 24.9
86 | 103 | 777 | 72 | S/T | 0.759
86 | 103 | 777 | 72 | ∆T | 22.5
86 | 103 | 777 | 72 | LDB | 63.5
86 | 103 | 777 | 72 | LWB | 63
86 | 103 | 777 | 72 | kW | 2.3
90 | 103 | 777 | 75 | MBh | 25.4
90 | 103 | 777 | 75 | S/T | 0.732
90 | 103 | 777 | 75 | ∆T | 22.2
90 | 103 | 777 | 75 | LDB | 67.8
90 | 103 | 777 | 75 | LWB | 66.4
90 | 103 | 777 | 75 | kW | 2.32
68 | 106 | 777 | 57 | MBh | 15.6
68 | 106 | 777 | 57 | S/T | 0.949
68 | 106 | 777 | 57 | ∆T | 17.6
68 | 106 | 777 | 57 | LDB | 50.4
68 | 106 | 777 | 57 | LWB | 49.4
68 | 106 | 777 | 57 | kW | 1.3
72 | 106 | 777 | 61 | MBh | 18.9
72 | 106 | 777 | 61 | S/T | 0.91
72 | 106 | 777 | 61 | ∆T | 20.5
72 | 106 | 777 | 61 | LDB | 51.5
72 | 106 | 777 | 61 | LWB | 51.5
72 | 106 | 777 | 61 | kW | 1.71
77 | 106 | 777 | 64 | MBh | 21.5
77 | 106 | 777 | 64 | S/T | 0.879
77 | 106 | 777 | 64 | ∆T | 22.5
77 | 106 | 777 | 64 | LDB | 54.5
77 | 106 | 777 | 64 | LWB | 54.5
77 | 106 | 777 | 64 | kW | 2.05
80 | 106 | 777 | 67 | MBh | 23.7
80 | 106 | 777 | 67 | S/T | 0.831
80 | 106 | 777 | 67 | ∆T | 23.5
80 | 106 | 777 | 67 | LDB | 56.5
80 | 106 | 777 | 67 | LWB | 56.5
80 | 106 | 777 | 67 | kW | 2.38
84 | 106 | 777 | 70 | MBh | 24.2
84 | 106 | 777 | 70 | S/T | 0.806
84 | 106 | 777 | 70 | ∆T | 23.2
84 | 106 | 777 | 70 | LDB | 60.8
84 | 106 | 777 | 70 | LWB | 60.8
84 | 106 | 777 | 70 | kW | 2.4
86 | 106 | 777 | 72 | MBh | 24.6
86 | 106 | 777 | 72 | S/T | 0.756
86 | 106 | 777 | 72 | ∆T | 22.2
86 | 106 | 777 | 72 | LDB | 63.8
86 | 106 | 777 | 72 | LWB | 63.1
86 | 106 | 777 | 72 | kW | 2.41
90 | 106 | 777 | 75 | MBh | 25.1
90 | 106 | 777 | 75 | S/T | 0.729
90 | 106 | 777 | 75 | ∆T | 21.8
90 | 106 | 777 | 75 | LDB | 68.2
90 | 106 | 777 | 75 | LWB | 66.6
90 | 106 | 777 | 75 | kW | 2.43
68 | 110 | 777 | 57 | MBh | 15.6
68 | 110 | 777 | 57 | S/T | 0.949
68 | 110 | 777 | 57 | ∆T | 17.6
68 | 110 | 777 | 57 | LDB | 50.4
68 | 110 | 777 | 57 | LWB | 49.4
68 | 110 | 777 | 57 | kW | 1.42
72 | 110 | 777 | 61 | MBh | 18.9
72 | 110 | 777 | 61 | S/T | 0.91
72 | 110 | 777 | 61 | ∆T | 20.5
72 | 110 | 777 | 61 | LDB | 51.5
72 | 110 | 777 | 61 | LWB | 51.5
72 | 110 | 777 | 61 | kW | 1.87
77 | 110 | 777 | 64 | MBh | 21.5
77 | 110 | 777 | 64 | S/T | 0.879
77 | 110 | 777 | 64 | ∆T | 22.5
77 | 110 | 777 | 64 | LDB | 54.5
77 | 110 | 777 | 64 | LWB | 54.5
77 | 110 | 777 | 64 | kW | 2.25
80 | 110 | 777 | 67 | MBh | 23.3
80 | 110 | 777 | 67 | S/T | 0.828
80 | 110 | 777 | 67 | ∆T | 23
80 | 110 | 777 | 67 | LDB | 57
80 | 110 | 777 | 67 | LWB | 57
80 | 110 | 777 | 67 | kW | 2.52
84 | 110 | 777 | 70 | MBh | 23.8
84 | 110 | 777 | 70 | S/T | 0.803
84 | 110 | 777 | 70 | ∆T | 22.8
84 | 110 | 777 | 70 | LDB | 61.2
84 | 110 | 777 | 70 | LWB | 61
84 | 110 | 777 | 70 | kW | 2.54
86 | 110 | 777 | 72 | MBh | 24.1
86 | 110 | 777 | 72 | S/T | 0.759
86 | 110 | 777 | 72 | ∆T | 21.8
86 | 110 | 777 | 72 | LDB | 64.2
86 | 110 | 777 | 72 | LWB | 63.3
86 | 110 | 777 | 72 | kW | 2.56
90 | 110 | 777 | 75 | MBh | 24.1
90 | 110 | 777 | 75 | S/T | 0.734
90 | 110 | 777 | 75 | ∆T | 21.1
90 | 110 | 777 | 75 | LDB | 68.9
90 | 110 | 777 | 75 | LWB | 66.9
90 | 110 | 777 | 75 | kW | 2.56
68 | 115 | 777 | 57 | MBh | 15.6
68 | 115 | 777 | 57 | S/T | 0.949
68 | 115 | 777 | 57 | ∆T | 17.6
68 | 115 | 777 | 57 | LDB | 50.4
68 | 115 | 777 | 57 | LWB | 49.4
68 | 115 | 777 | 57 | kW | 1.58
72 | 115 | 777 | 61 | MBh | 18.9
72 | 115 | 777 | 61 | S/T | 0.91
72 | 115 | 777 | 61 | ∆T | 20.5
72 | 115 | 777 | 61 | LDB | 51.5
72 | 115 | 777 | 61 | LWB | 51.5
72 | 115 | 777 | 61 | kW | 2.09
77 | 115 | 777 | 64 | MBh | 21.5
77 | 115 | 777 | 64 | S/T | 0.879
77 | 115 | 777 | 64 | ∆T | 22.5
77 | 115 | 777 | 64 | LDB | 54.5
77 | 115 | 777 | 64 | LWB | 54.5
77 | 115 | 777 | 64 | kW | 2.52
80 | 115 | 777 | 67 | MBh | 22.5
80 | 115 | 777 | 67 | S/T | 0.827
80 | 115 | 777 | 67 | ∆T | 22.2
80 | 115 | 777 | 67 | LDB | 57.8
80 | 115 | 777 | 67 | LWB | 57.8
80 | 115 | 777 | 67 | kW | 2.69
84 | 115 | 777 | 70 | MBh | 22.5
84 | 115 | 777 | 70 | S/T | 0.804
84 | 115 | 777 | 70 | ∆T | 21.6
84 | 115 | 777 | 70 | LDB | 62.4
84 | 115 | 777 | 70 | LWB | 61.5
84 | 115 | 777 | 70 | kW | 2.69
86 | 115 | 777 | 72 | MBh | 22.5
86 | 115 | 777 | 72 | S/T | 0.756
86 | 115 | 777 | 72 | ∆T | 20.3
86 | 115 | 777 | 72 | LDB | 65.7
86 | 115 | 777 | 72 | LWB | 63.9
86 | 115 | 777 | 72 | kW | 2.69
90 | 115 | 777 | 75 | MBh | 22.5
90 | 115 | 777 | 75 | S/T | 0.729
90 | 115 | 777 | 75 | ∆T | 19.5
90 | 115 | 777 | 75 | LDB | 70.5
90 | 115 | 777 | 75 | LWB | 67.5
90 | 115 | 777 | 75 | kW | 2.69
68 | 118 | 777 | 57 | MBh | 15.6
68 | 118 | 777 | 57 | S/T | 0.949
68 | 118 | 777 | 57 | ∆T | 17.6
68 | 118 | 777 | 57 | LDB | 50.4
68 | 118 | 777 | 57 | LWB | 49.4
68 | 118 | 777 | 57 | kW | 1.69
72 | 118 | 777 | 61 | MBh | 18.9
72 | 118 | 777 | 61 | S/T | 0.91
72 | 118 | 777 | 61 | ∆T | 20.5
72 | 118 | 777 | 61 | LDB | 51.5
72 | 118 | 777 | 61 | LWB | 51.5
72 | 118 | 777 | 61 | kW | 2.23
77 | 118 | 777 | 64 | MBh | 19.3
77 | 118 | 777 | 64 | S/T | 0.876
77 | 118 | 777 | 64 | ∆T | 20.1
77 | 118 | 777 | 64 | LDB | 56.9
77 | 118 | 777 | 64 | LWB | 55.7
77 | 118 | 777 | 64 | kW | 2.29
80 | 118 | 777 | 67 | MBh | 19.3
80 | 118 | 777 | 67 | S/T | 0.829
80 | 118 | 777 | 67 | ∆T | 19.1
80 | 118 | 777 | 67 | LDB | 60.9
80 | 118 | 777 | 67 | LWB | 59.3
80 | 118 | 777 | 67 | kW | 2.29
84 | 118 | 777 | 70 | MBh | 19.3
84 | 118 | 777 | 70 | S/T | 0.803
84 | 118 | 777 | 70 | ∆T | 18.5
84 | 118 | 777 | 70 | LDB | 65.5
84 | 118 | 777 | 70 | LWB | 62.8
84 | 118 | 777 | 70 | kW | 2.29
86 | 118 | 777 | 72 | MBh | 19.3
86 | 118 | 777 | 72 | S/T | 0.756
86 | 118 | 777 | 72 | ∆T | 17.4
86 | 118 | 777 | 72 | LDB | 68.6
86 | 118 | 777 | 72 | LWB | 65.2
86 | 118 | 777 | 72 | kW | 2.29
90 | 118 | 777 | 75 | MBh | 19.3
90 | 118 | 777 | 75 | S/T | 0.731
90 | 118 | 777 | 75 | ∆T | 16.8
90 | 118 | 777 | 75 | LDB | 73.2
90 | 118 | 777 | 75 | LWB | 68.6
90 | 118 | 777 | 75 | kW | 2.29
68 | 122 | 777 | 57 | MBh | 14.7
68 | 122 | 777 | 57 | S/T | 0.952
68 | 122 | 777 | 57 | ∆T | 16.7
68 | 122 | 777 | 57 | LDB | 51.3
68 | 122 | 777 | 57 | LWB | 49.8
68 | 122 | 777 | 57 | kW | 1.69
72 | 122 | 777 | 61 | MBh | 14.7
72 | 122 | 777 | 61 | S/T | 0.912
72 | 122 | 777 | 61 | ∆T | 16
72 | 122 | 777 | 61 | LDB | 56
72 | 122 | 777 | 61 | LWB | 54.4
72 | 122 | 777 | 61 | kW | 1.69
77 | 122 | 777 | 64 | MBh | 14.7
77 | 122 | 777 | 64 | S/T | 0.878
77 | 122 | 777 | 64 | ∆T | 15.4
77 | 122 | 777 | 64 | LDB | 61.6
77 | 122 | 777 | 64 | LWB | 57.8
77 | 122 | 777 | 64 | kW | 1.69
80 | 122 | 777 | 67 | MBh | 14.7
80 | 122 | 777 | 67 | S/T | 0.83
80 | 122 | 777 | 67 | ∆T | 14.5
80 | 122 | 777 | 67 | LDB | 65.5
80 | 122 | 777 | 67 | LWB | 61.3
80 | 122 | 777 | 67 | kW | 1.69
84 | 122 | 777 | 70 | MBh | 14.7
84 | 122 | 777 | 70 | S/T | 0.803
84 | 122 | 777 | 70 | ∆T | 14.1
84 | 122 | 777 | 70 | LDB | 69.9
84 | 122 | 777 | 70 | LWB | 64.6
84 | 122 | 777 | 70 | kW | 1.69
86 | 122 | 777 | 72 | MBh | 14.7
86 | 122 | 777 | 72 | S/T | 0.755
86 | 122 | 777 | 72 | ∆T | 13.2
86 | 122 | 777 | 72 | LDB | 72.8
86 | 122 | 777 | 72 | LWB | 66.9
86 | 122 | 777 | 72 | kW | 1.69
90 | 122 | 777 | 75 | MBh | 14.7
90 | 122 | 777 | 75 | S/T | 0.728
90 | 122 | 777 | 75 | ∆T | 12.8
90 | 122 | 777 | 75 | LDB | 77.2
90 | 122 | 777 | 75 | LWB | 70.2
90 | 122 | 777 | 75 | kW | 1.69

## RZA30AAVJU - FCA30AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1059 | 57 | MBh | 19.5 | 64 | 60 | 61 | 40.8 | 2.33
68 | 23 | 1059 | 57 | S/T | 0.856 | 64 | 60 | 65 | 37.8 | 2.11
68 | 23 | 1059 | 57 | ∆T | 14.6 | 64 | 60 | 68 | 35.5 | 1.95
68 | 23 | 1059 | 57 | LDB | 53.4 | 64 | 60 | 70 | 34 | 1.86
68 | 23 | 1059 | 57 | LWB | 50 | 64 | 60 | 72 | 32.5 | 1.76
68 | 23 | 1059 | 57 | kW | 0.67 | 64 | 60 | 75 | 30.2 | 1.63
72 | 23 | 1059 | 61 | MBh | 23.7 | 60 | 56 | 61 | 40.8 | 2.43
72 | 23 | 1059 | 61 | S/T | 0.819 | 60 | 56 | 65 | 37.8 | 2.2
72 | 23 | 1059 | 61 | ∆T | 17 | 60 | 56 | 68 | 35.5 | 2.03
72 | 23 | 1059 | 61 | LDB | 55 | 60 | 56 | 70 | 34 | 1.93
72 | 23 | 1059 | 61 | LWB | 53.1 | 60 | 56 | 72 | 32.5 | 1.83
72 | 23 | 1059 | 61 | kW | 0.82 | 60 | 56 | 75 | 30.2 | 1.69
77 | 23 | 1059 | 64 | MBh | 26.8 | 57 | 53 | 61 | 40.8 | 2.52
77 | 23 | 1059 | 64 | S/T | 0.787 | 57 | 53 | 65 | 37.8 | 2.27
77 | 23 | 1059 | 64 | ∆T | 18.4 | 57 | 53 | 68 | 35.5 | 2.1
77 | 23 | 1059 | 64 | LDB | 58.6 | 57 | 53 | 70 | 34 | 1.99
77 | 23 | 1059 | 64 | LWB | 55.6 | 57 | 53 | 72 | 32.5 | 1.88
77 | 23 | 1059 | 64 | kW | 0.94 | 57 | 53 | 75 | 30.2 | 1.74
80 | 23 | 1059 | 67 | MBh | 30 | 54 | 50 | 61 | 40.8 | 2.62
80 | 23 | 1059 | 67 | S/T | 0.743 | 54 | 50 | 65 | 37.8 | 2.35
80 | 23 | 1059 | 67 | ∆T | 19.5 | 54 | 50 | 68 | 35.5 | 2.17
80 | 23 | 1059 | 67 | LDB | 60.5 | 54 | 50 | 70 | 34 | 2.05
80 | 23 | 1059 | 67 | LWB | 58.1 | 54 | 50 | 72 | 32.5 | 1.94
80 | 23 | 1059 | 67 | kW | 1.07 | 54 | 50 | 75 | 30.2 | 1.79
84 | 23 | 1059 | 70 | MBh | 33.2 | 51 | 47 | 61 | 40.8 | 2.72
84 | 23 | 1059 | 70 | S/T | 0.726 | 51 | 47 | 65 | 37.8 | 2.44
84 | 23 | 1059 | 70 | ∆T | 21.1 | 51 | 47 | 68 | 35.5 | 2.24
84 | 23 | 1059 | 70 | LDB | 62.9 | 51 | 47 | 70 | 34 | 2.12
84 | 23 | 1059 | 70 | LWB | 60.8 | 51 | 47 | 72 | 32.5 | 2.01
84 | 23 | 1059 | 70 | kW | 1.2 | 51 | 47 | 75 | 30.2 | 1.84
86 | 23 | 1059 | 72 | MBh | 35.3 | 47 | 43 | 61 | 40.8 | 2.87
86 | 23 | 1059 | 72 | S/T | 0.686 | 47 | 43 | 65 | 37.8 | 2.57
86 | 23 | 1059 | 72 | ∆T | 21.2 | 47 | 43 | 68 | 35.5 | 2.36
86 | 23 | 1059 | 72 | LDB | 64.8 | 47 | 43 | 70 | 34 | 2.23
86 | 23 | 1059 | 72 | LWB | 62.6 | 47 | 43 | 72 | 32.5 | 2.1
86 | 23 | 1059 | 72 | kW | 1.29 | 47 | 43 | 75 | 30.2 | 1.92
90 | 23 | 1059 | 75 | MBh | 38.4 | 44 | 40 | 61 | 40.8 | 2.99
90 | 23 | 1059 | 75 | S/T | 0.651 | 44 | 40 | 65 | 37.8 | 2.67
90 | 23 | 1059 | 75 | ∆T | 21.9 | 44 | 40 | 68 | 35.5 | 2.45
90 | 23 | 1059 | 75 | LDB | 68.1 | 44 | 40 | 70 | 34 | 2.31
90 | 23 | 1059 | 75 | LWB | 65.4 | 44 | 40 | 72 | 32.5 | 2.18
90 | 23 | 1059 | 75 | kW | 1.42 | 44 | 40 | 75 | 30.2 | 1.99
68 | 30 | 1059 | 57 | MBh | 19.5 | 39 | 36 | 61 | 40.8 | 3.18
68 | 30 | 1059 | 57 | S/T | 0.856 | 39 | 36 | 65 | 37.8 | 2.83
68 | 30 | 1059 | 57 | ∆T | 14.6 | 39 | 36 | 68 | 35.5 | 2.59
68 | 30 | 1059 | 57 | LDB | 53.4 | 39 | 36 | 70 | 34 | 2.44
68 | 30 | 1059 | 57 | LWB | 50 | 39 | 36 | 72 | 32.5 | 2.29
68 | 30 | 1059 | 57 | kW | 0.69 | 39 | 36 | 75 | 30.2 | 2.09
72 | 30 | 1059 | 61 | MBh | 23.7 | 35 | 32 | 61 | 40.8 | 3.39
72 | 30 | 1059 | 61 | S/T | 0.819 | 35 | 32 | 65 | 37.8 | 3.01
72 | 30 | 1059 | 61 | ∆T | 17 | 35 | 32 | 68 | 35.5 | 2.75
72 | 30 | 1059 | 61 | LDB | 55 | 35 | 32 | 70 | 34 | 2.58
72 | 30 | 1059 | 61 | LWB | 53.1 | 35 | 32 | 72 | 32.5 | 2.42
72 | 30 | 1059 | 61 | kW | 0.85 | 35 | 32 | 75 | 30.2 | 2.2
77 | 30 | 1059 | 64 | MBh | 26.8 | 30 | 28 | 61 | 40.8 | 3.64
77 | 30 | 1059 | 64 | S/T | 0.787 | 30 | 28 | 65 | 37.8 | 3.22
77 | 30 | 1059 | 64 | ∆T | 18.4 | 30 | 28 | 68 | 35.5 | 2.93
77 | 30 | 1059 | 64 | LDB | 58.6 | 30 | 28 | 70 | 34 | 2.75
77 | 30 | 1059 | 64 | LWB | 55.6 | 30 | 28 | 72 | 32.5 | 2.58
77 | 30 | 1059 | 64 | kW | 0.97 | 30 | 28 | 75 | 30.2 | 2.33
80 | 30 | 1059 | 67 | MBh | 30 | 26 | 24 | 61 | 40.8 | 3.91
80 | 30 | 1059 | 67 | S/T | 0.743 | 26 | 24 | 65 | 37.8 | 3.46
80 | 30 | 1059 | 67 | ∆T | 19.5 | 26 | 24 | 68 | 35.5 | 3.14
80 | 30 | 1059 | 67 | LDB | 60.5 | 26 | 24 | 70 | 34 | 2.94
80 | 30 | 1059 | 67 | LWB | 58.1 | 26 | 24 | 72 | 32.5 | 2.75
80 | 30 | 1059 | 67 | kW | 1.1 | 26 | 24 | 75 | 30.2 | 2.48
84 | 30 | 1059 | 70 | MBh | 33.2 | 22 | 20 | 61 | 40.8 | 4.23
84 | 30 | 1059 | 70 | S/T | 0.726 | 22 | 20 | 65 | 37.8 | 3.73
84 | 30 | 1059 | 70 | ∆T | 21.1 | 22 | 20 | 68 | 35.5 | 3.38
84 | 30 | 1059 | 70 | LDB | 62.9 | 22 | 20 | 70 | 34 | 3.16
84 | 30 | 1059 | 70 | LWB | 60.8 | 22 | 20 | 72 | 32.5 | 2.95
84 | 30 | 1059 | 70 | kW | 1.24 | 22 | 20 | 75 | 30.2 | 2.65
86 | 30 | 1059 | 72 | MBh | 35.3 | 19 | 18 | 61 | 40.8 | 4.23
86 | 30 | 1059 | 72 | S/T | 0.686 | 19 | 18 | 65 | 37.8 | 3.88
86 | 30 | 1059 | 72 | ∆T | 21.2 | 19 | 18 | 68 | 35.5 | 3.51
86 | 30 | 1059 | 72 | LDB | 64.8 | 19 | 18 | 70 | 34 | 3.28
86 | 30 | 1059 | 72 | LWB | 62.6 | 19 | 18 | 72 | 32.5 | 3.06
86 | 30 | 1059 | 72 | kW | 1.33 | 19 | 18 | 75 | 30.2 | 2.75
90 | 30 | 1059 | 75 | MBh | 38.4 | 17 | 16 | 61 | 40.8 | 4.23
90 | 30 | 1059 | 75 | S/T | 0.651 | 17 | 16 | 65 | 37.8 | 4.09
90 | 30 | 1059 | 75 | ∆T | 21.9 | 17 | 16 | 68 | 35.5 | 3.7
90 | 30 | 1059 | 75 | LDB | 68.1 | 17 | 16 | 70 | 34 | 3.45
90 | 30 | 1059 | 75 | LWB | 65.4 | 17 | 16 | 72 | 32.5 | 3.21
90 | 30 | 1059 | 75 | kW | 1.47 | 17 | 16 | 75 | 30.2 | 2.88
68 | 40 | 1059 | 57 | MBh | 19.5 | 15 | 14 | 61 | 40.8 | 4.23
68 | 40 | 1059 | 57 | S/T | 0.856 | 15 | 14 | 65 | 37.8 | 4.22
68 | 40 | 1059 | 57 | ∆T | 14.6 | 15 | 14 | 68 | 35.5 | 3.82
68 | 40 | 1059 | 57 | LDB | 53.4 | 15 | 14 | 70 | 34 | 3.56
68 | 40 | 1059 | 57 | LWB | 50 | 15 | 14 | 72 | 32.5 | 3.31
68 | 40 | 1059 | 57 | kW | 0.72 | 15 | 14 | 75 | 30.2 | 2.96
72 | 40 | 1059 | 61 | MBh | 23.7 | 13 | 12 | 61 | 40 | 4.24
72 | 40 | 1059 | 61 | S/T | 0.819 | 13 | 12 | 65 | 37.8 | 4.22
72 | 40 | 1059 | 61 | ∆T | 17 | 13 | 12 | 68 | 35.5 | 3.99
72 | 40 | 1059 | 61 | LDB | 55 | 13 | 12 | 70 | 34 | 3.71
72 | 40 | 1059 | 61 | LWB | 53.1 | 13 | 12 | 72 | 32.5 | 3.45
72 | 40 | 1059 | 61 | kW | 0.89 | 13 | 12 | 75 | 30.2 | 3.09
77 | 40 | 1059 | 64 | MBh | 26.8 | 10 | 9 | 61 | 38.1 | 4.24
77 | 40 | 1059 | 64 | S/T | 0.787 | 10 | 9 | 65 | 37.8 | 4.23
77 | 40 | 1059 | 64 | ∆T | 18.4 | 10 | 9 | 68 | 35.5 | 4.22
77 | 40 | 1059 | 64 | LDB | 58.6 | 10 | 9 | 70 | 34 | 4.02
77 | 40 | 1059 | 64 | LWB | 55.6 | 10 | 9 | 72 | 32.5 | 3.73
77 | 40 | 1059 | 64 | kW | 1.02 | 10 | 9 | 75 | 30.2 | 3.33
80 | 40 | 1059 | 67 | MBh | 30 | 6 | 5 | 61 | 35.5 | 4.25
80 | 40 | 1059 | 67 | S/T | 0.743 | 6 | 5 | 65 | 35.5 | 4.23
80 | 40 | 1059 | 67 | ∆T | 19.5 | 6 | 5 | 68 | 35.5 | 4.22
80 | 40 | 1059 | 67 | LDB | 60.5 | 6 | 5 | 70 | 34 | 4.22
80 | 40 | 1059 | 67 | LWB | 58.1 | 6 | 5 | 72 | 32.5 | 4.06
80 | 40 | 1059 | 67 | kW | 1.16 | 6 | 5 | 75 | 30.2 | 3.61
84 | 40 | 1059 | 70 | MBh | 33.2 | -2 | -2 | 61 | 30.1 | 4.27
84 | 40 | 1059 | 70 | S/T | 0.726 | -2 | -2 | 65 | 30.1 | 4.25
84 | 40 | 1059 | 70 | ∆T | 21.1 | -2 | -2 | 68 | 30.1 | 4.24
84 | 40 | 1059 | 70 | LDB | 62.9 | -2 | -2 | 70 | 30.1 | 4.23
84 | 40 | 1059 | 70 | LWB | 60.8 | -2 | -2 | 72 | 30.1 | 4.22
84 | 40 | 1059 | 70 | kW | 1.3 | -2 | -2 | 75 | 30.1 | 4.21
86 | 40 | 1059 | 72 | MBh | 35.3 | -4 | -4 | 61 | 28.7 | 4.27
86 | 40 | 1059 | 72 | S/T | 0.686 | -4 | -4 | 65 | 28.7 | 4.25
86 | 40 | 1059 | 72 | ∆T | 21.2 | -4 | -4 | 68 | 28.7 | 4.24
86 | 40 | 1059 | 72 | LDB | 64.8 | -4 | -4 | 70 | 28.7 | 4.23
86 | 40 | 1059 | 72 | LWB | 62.6 | -4 | -4 | 72 | 28.7 | 4.23
86 | 40 | 1059 | 72 | kW | 1.39 | -4 | -4 | 75 | 28.7 | 4.21
90 | 40 | 1059 | 75 | MBh | 38.4
90 | 40 | 1059 | 75 | S/T | 0.651
90 | 40 | 1059 | 75 | ∆T | 21.9
90 | 40 | 1059 | 75 | LDB | 68.1
90 | 40 | 1059 | 75 | LWB | 65.4
90 | 40 | 1059 | 75 | kW | 1.54
68 | 50 | 1059 | 57 | MBh | 19.5
68 | 50 | 1059 | 57 | S/T | 0.856
68 | 50 | 1059 | 57 | ∆T | 14.6
68 | 50 | 1059 | 57 | LDB | 53.4
68 | 50 | 1059 | 57 | LWB | 50
68 | 50 | 1059 | 57 | kW | 0.75
72 | 50 | 1059 | 61 | MBh | 23.7
72 | 50 | 1059 | 61 | S/T | 0.819
72 | 50 | 1059 | 61 | ∆T | 17
72 | 50 | 1059 | 61 | LDB | 55
72 | 50 | 1059 | 61 | LWB | 53.1
72 | 50 | 1059 | 61 | kW | 0.93
77 | 50 | 1059 | 64 | MBh | 26.8
77 | 50 | 1059 | 64 | S/T | 0.787
77 | 50 | 1059 | 64 | ∆T | 18.4
77 | 50 | 1059 | 64 | LDB | 58.6
77 | 50 | 1059 | 64 | LWB | 55.6
77 | 50 | 1059 | 64 | kW | 1.07
80 | 50 | 1059 | 67 | MBh | 30
80 | 50 | 1059 | 67 | S/T | 0.743
80 | 50 | 1059 | 67 | ∆T | 19.5
80 | 50 | 1059 | 67 | LDB | 60.5
80 | 50 | 1059 | 67 | LWB | 58.1
80 | 50 | 1059 | 67 | kW | 1.22
84 | 50 | 1059 | 70 | MBh | 33.2
84 | 50 | 1059 | 70 | S/T | 0.726
84 | 50 | 1059 | 70 | ∆T | 21.1
84 | 50 | 1059 | 70 | LDB | 62.9
84 | 50 | 1059 | 70 | LWB | 60.8
84 | 50 | 1059 | 70 | kW | 1.36
86 | 50 | 1059 | 72 | MBh | 35.3
86 | 50 | 1059 | 72 | S/T | 0.686
86 | 50 | 1059 | 72 | ∆T | 21.2
86 | 50 | 1059 | 72 | LDB | 64.8
86 | 50 | 1059 | 72 | LWB | 62.6
86 | 50 | 1059 | 72 | kW | 1.47
90 | 50 | 1059 | 75 | MBh | 38.4
90 | 50 | 1059 | 75 | S/T | 0.651
90 | 50 | 1059 | 75 | ∆T | 21.9
90 | 50 | 1059 | 75 | LDB | 68.1
90 | 50 | 1059 | 75 | LWB | 65.4
90 | 50 | 1059 | 75 | kW | 1.62
68 | 54 | 1059 | 57 | MBh | 19.5
68 | 54 | 1059 | 57 | S/T | 0.856
68 | 54 | 1059 | 57 | ∆T | 14.6
68 | 54 | 1059 | 57 | LDB | 53.4
68 | 54 | 1059 | 57 | LWB | 50
68 | 54 | 1059 | 57 | kW | 0.77
72 | 54 | 1059 | 61 | MBh | 23.7
72 | 54 | 1059 | 61 | S/T | 0.819
72 | 54 | 1059 | 61 | ∆T | 17
72 | 54 | 1059 | 61 | LDB | 55
72 | 54 | 1059 | 61 | LWB | 53.1
72 | 54 | 1059 | 61 | kW | 0.95
77 | 54 | 1059 | 64 | MBh | 26.8
77 | 54 | 1059 | 64 | S/T | 0.787
77 | 54 | 1059 | 64 | ∆T | 18.4
77 | 54 | 1059 | 64 | LDB | 58.6
77 | 54 | 1059 | 64 | LWB | 55.6
77 | 54 | 1059 | 64 | kW | 1.09
80 | 54 | 1059 | 67 | MBh | 30
80 | 54 | 1059 | 67 | S/T | 0.743
80 | 54 | 1059 | 67 | ∆T | 19.5
80 | 54 | 1059 | 67 | LDB | 60.5
80 | 54 | 1059 | 67 | LWB | 58.1
80 | 54 | 1059 | 67 | kW | 1.24
84 | 54 | 1059 | 70 | MBh | 33.2
84 | 54 | 1059 | 70 | S/T | 0.726
84 | 54 | 1059 | 70 | ∆T | 21.1
84 | 54 | 1059 | 70 | LDB | 62.9
84 | 54 | 1059 | 70 | LWB | 60.8
84 | 54 | 1059 | 70 | kW | 1.39
86 | 54 | 1059 | 72 | MBh | 35.3
86 | 54 | 1059 | 72 | S/T | 0.686
86 | 54 | 1059 | 72 | ∆T | 21.2
86 | 54 | 1059 | 72 | LDB | 64.8
86 | 54 | 1059 | 72 | LWB | 62.6
86 | 54 | 1059 | 72 | kW | 1.5
90 | 54 | 1059 | 75 | MBh | 38.4
90 | 54 | 1059 | 75 | S/T | 0.651
90 | 54 | 1059 | 75 | ∆T | 21.9
90 | 54 | 1059 | 75 | LDB | 68.1
90 | 54 | 1059 | 75 | LWB | 65.4
90 | 54 | 1059 | 75 | kW | 1.65
68 | 58 | 1059 | 57 | MBh | 19.5
68 | 58 | 1059 | 57 | S/T | 0.856
68 | 58 | 1059 | 57 | ∆T | 14.6
68 | 58 | 1059 | 57 | LDB | 53.4
68 | 58 | 1059 | 57 | LWB | 50
68 | 58 | 1059 | 57 | kW | 0.78
72 | 58 | 1059 | 61 | MBh | 23.7
72 | 58 | 1059 | 61 | S/T | 0.819
72 | 58 | 1059 | 61 | ∆T | 17
72 | 58 | 1059 | 61 | LDB | 55
72 | 58 | 1059 | 61 | LWB | 53.1
72 | 58 | 1059 | 61 | kW | 0.97
77 | 58 | 1059 | 64 | MBh | 26.8
77 | 58 | 1059 | 64 | S/T | 0.787
77 | 58 | 1059 | 64 | ∆T | 18.4
77 | 58 | 1059 | 64 | LDB | 58.6
77 | 58 | 1059 | 64 | LWB | 55.6
77 | 58 | 1059 | 64 | kW | 1.12
80 | 58 | 1059 | 67 | MBh | 30
80 | 58 | 1059 | 67 | S/T | 0.743
80 | 58 | 1059 | 67 | ∆T | 19.5
80 | 58 | 1059 | 67 | LDB | 60.5
80 | 58 | 1059 | 67 | LWB | 58.1
80 | 58 | 1059 | 67 | kW | 1.27
84 | 58 | 1059 | 70 | MBh | 33.2
84 | 58 | 1059 | 70 | S/T | 0.726
84 | 58 | 1059 | 70 | ∆T | 21.1
84 | 58 | 1059 | 70 | LDB | 62.9
84 | 58 | 1059 | 70 | LWB | 60.8
84 | 58 | 1059 | 70 | kW | 1.42
86 | 58 | 1059 | 72 | MBh | 35.3
86 | 58 | 1059 | 72 | S/T | 0.686
86 | 58 | 1059 | 72 | ∆T | 21.2
86 | 58 | 1059 | 72 | LDB | 64.8
86 | 58 | 1059 | 72 | LWB | 62.6
86 | 58 | 1059 | 72 | kW | 1.53
90 | 58 | 1059 | 75 | MBh | 38.1
90 | 58 | 1059 | 75 | S/T | 0.651
90 | 58 | 1059 | 75 | ∆T | 21.7
90 | 58 | 1059 | 75 | LDB | 68.3
90 | 58 | 1059 | 75 | LWB | 65.5
90 | 58 | 1059 | 75 | kW | 1.66
68 | 62 | 1059 | 57 | MBh | 19.5
68 | 62 | 1059 | 57 | S/T | 0.856
68 | 62 | 1059 | 57 | ∆T | 14.6
68 | 62 | 1059 | 57 | LDB | 53.4
68 | 62 | 1059 | 57 | LWB | 50
68 | 62 | 1059 | 57 | kW | 0.8
72 | 62 | 1059 | 61 | MBh | 23.7
72 | 62 | 1059 | 61 | S/T | 0.819
72 | 62 | 1059 | 61 | ∆T | 17
72 | 62 | 1059 | 61 | LDB | 55
72 | 62 | 1059 | 61 | LWB | 53.1
72 | 62 | 1059 | 61 | kW | 0.99
77 | 62 | 1059 | 64 | MBh | 26.8
77 | 62 | 1059 | 64 | S/T | 0.787
77 | 62 | 1059 | 64 | ∆T | 18.4
77 | 62 | 1059 | 64 | LDB | 58.6
77 | 62 | 1059 | 64 | LWB | 55.6
77 | 62 | 1059 | 64 | kW | 1.14
80 | 62 | 1059 | 67 | MBh | 30
80 | 62 | 1059 | 67 | S/T | 0.743
80 | 62 | 1059 | 67 | ∆T | 19.5
80 | 62 | 1059 | 67 | LDB | 60.5
80 | 62 | 1059 | 67 | LWB | 58.1
80 | 62 | 1059 | 67 | kW | 1.3
84 | 62 | 1059 | 70 | MBh | 33.2
84 | 62 | 1059 | 70 | S/T | 0.726
84 | 62 | 1059 | 70 | ∆T | 21.1
84 | 62 | 1059 | 70 | LDB | 62.9
84 | 62 | 1059 | 70 | LWB | 60.8
84 | 62 | 1059 | 70 | kW | 1.45
86 | 62 | 1059 | 72 | MBh | 35.3
86 | 62 | 1059 | 72 | S/T | 0.686
86 | 62 | 1059 | 72 | ∆T | 21.2
86 | 62 | 1059 | 72 | LDB | 64.8
86 | 62 | 1059 | 72 | LWB | 62.6
86 | 62 | 1059 | 72 | kW | 1.56
90 | 62 | 1059 | 75 | MBh | 37.5
90 | 62 | 1059 | 75 | S/T | 0.651
90 | 62 | 1059 | 75 | ∆T | 21.3
90 | 62 | 1059 | 75 | LDB | 68.7
90 | 62 | 1059 | 75 | LWB | 65.7
90 | 62 | 1059 | 75 | kW | 1.65
68 | 66 | 1059 | 57 | MBh | 19.5
68 | 66 | 1059 | 57 | S/T | 0.856
68 | 66 | 1059 | 57 | ∆T | 14.6
68 | 66 | 1059 | 57 | LDB | 53.4
68 | 66 | 1059 | 57 | LWB | 50
68 | 66 | 1059 | 57 | kW | 0.81
72 | 66 | 1059 | 61 | MBh | 23.7
72 | 66 | 1059 | 61 | S/T | 0.819
72 | 66 | 1059 | 61 | ∆T | 17
72 | 66 | 1059 | 61 | LDB | 55
72 | 66 | 1059 | 61 | LWB | 53.1
72 | 66 | 1059 | 61 | kW | 1.01
77 | 66 | 1059 | 64 | MBh | 26.8
77 | 66 | 1059 | 64 | S/T | 0.787
77 | 66 | 1059 | 64 | ∆T | 18.4
77 | 66 | 1059 | 64 | LDB | 58.6
77 | 66 | 1059 | 64 | LWB | 55.6
77 | 66 | 1059 | 64 | kW | 1.16
80 | 66 | 1059 | 67 | MBh | 30
80 | 66 | 1059 | 67 | S/T | 0.743
80 | 66 | 1059 | 67 | ∆T | 19.5
80 | 66 | 1059 | 67 | LDB | 60.5
80 | 66 | 1059 | 67 | LWB | 58.1
80 | 66 | 1059 | 67 | kW | 1.32
84 | 66 | 1059 | 70 | MBh | 33.2
84 | 66 | 1059 | 70 | S/T | 0.726
84 | 66 | 1059 | 70 | ∆T | 21.1
84 | 66 | 1059 | 70 | LDB | 62.9
84 | 66 | 1059 | 70 | LWB | 60.8
84 | 66 | 1059 | 70 | kW | 1.49
86 | 66 | 1059 | 72 | MBh | 35.3
86 | 66 | 1059 | 72 | S/T | 0.686
86 | 66 | 1059 | 72 | ∆T | 21.2
86 | 66 | 1059 | 72 | LDB | 64.8
86 | 66 | 1059 | 72 | LWB | 62.6
86 | 66 | 1059 | 72 | kW | 1.6
90 | 66 | 1059 | 75 | MBh | 36.9
90 | 66 | 1059 | 75 | S/T | 0.653
90 | 66 | 1059 | 75 | ∆T | 21.1
90 | 66 | 1059 | 75 | LDB | 68.9
90 | 66 | 1059 | 75 | LWB | 65.8
90 | 66 | 1059 | 75 | kW | 1.64
68 | 70 | 1059 | 57 | MBh | 19.5
68 | 70 | 1059 | 57 | S/T | 0.856
68 | 70 | 1059 | 57 | ∆T | 14.6
68 | 70 | 1059 | 57 | LDB | 53.4
68 | 70 | 1059 | 57 | LWB | 50
68 | 70 | 1059 | 57 | kW | 0.83
72 | 70 | 1059 | 61 | MBh | 23.7
72 | 70 | 1059 | 61 | S/T | 0.819
72 | 70 | 1059 | 61 | ∆T | 17
72 | 70 | 1059 | 61 | LDB | 55
72 | 70 | 1059 | 61 | LWB | 53.1
72 | 70 | 1059 | 61 | kW | 1.03
77 | 70 | 1059 | 64 | MBh | 26.8
77 | 70 | 1059 | 64 | S/T | 0.787
77 | 70 | 1059 | 64 | ∆T | 18.4
77 | 70 | 1059 | 64 | LDB | 58.6
77 | 70 | 1059 | 64 | LWB | 55.6
77 | 70 | 1059 | 64 | kW | 1.19
80 | 70 | 1059 | 67 | MBh | 30
80 | 70 | 1059 | 67 | S/T | 0.743
80 | 70 | 1059 | 67 | ∆T | 19.5
80 | 70 | 1059 | 67 | LDB | 60.5
80 | 70 | 1059 | 67 | LWB | 58.1
80 | 70 | 1059 | 67 | kW | 1.35
84 | 70 | 1059 | 70 | MBh | 33.2
84 | 70 | 1059 | 70 | S/T | 0.726
84 | 70 | 1059 | 70 | ∆T | 21.1
84 | 70 | 1059 | 70 | LDB | 62.9
84 | 70 | 1059 | 70 | LWB | 60.8
84 | 70 | 1059 | 70 | kW | 1.52
86 | 70 | 1059 | 72 | MBh | 35.3
86 | 70 | 1059 | 72 | S/T | 0.686
86 | 70 | 1059 | 72 | ∆T | 21.2
86 | 70 | 1059 | 72 | LDB | 64.8
86 | 70 | 1059 | 72 | LWB | 62.6
86 | 70 | 1059 | 72 | kW | 1.63
90 | 70 | 1059 | 75 | MBh | 36.4
90 | 70 | 1059 | 75 | S/T | 0.651
90 | 70 | 1059 | 75 | ∆T | 20.7
90 | 70 | 1059 | 75 | LDB | 69.3
90 | 70 | 1059 | 75 | LWB | 66
90 | 70 | 1059 | 75 | kW | 1.63
68 | 72 | 1059 | 57 | MBh | 19.5
68 | 72 | 1059 | 57 | S/T | 0.856
68 | 72 | 1059 | 57 | ∆T | 14.6
68 | 72 | 1059 | 57 | LDB | 53.4
68 | 72 | 1059 | 57 | LWB | 50
68 | 72 | 1059 | 57 | kW | 0.84
72 | 72 | 1059 | 61 | MBh | 23.7
72 | 72 | 1059 | 61 | S/T | 0.819
72 | 72 | 1059 | 61 | ∆T | 17
72 | 72 | 1059 | 61 | LDB | 55
72 | 72 | 1059 | 61 | LWB | 53.1
72 | 72 | 1059 | 61 | kW | 1.04
77 | 72 | 1059 | 64 | MBh | 26.8
77 | 72 | 1059 | 64 | S/T | 0.787
77 | 72 | 1059 | 64 | ∆T | 18.4
77 | 72 | 1059 | 64 | LDB | 58.6
77 | 72 | 1059 | 64 | LWB | 55.6
77 | 72 | 1059 | 64 | kW | 1.2
80 | 72 | 1059 | 67 | MBh | 30
80 | 72 | 1059 | 67 | S/T | 0.743
80 | 72 | 1059 | 67 | ∆T | 19.5
80 | 72 | 1059 | 67 | LDB | 60.5
80 | 72 | 1059 | 67 | LWB | 58.1
80 | 72 | 1059 | 67 | kW | 1.37
84 | 72 | 1059 | 70 | MBh | 33.2
84 | 72 | 1059 | 70 | S/T | 0.726
84 | 72 | 1059 | 70 | ∆T | 21.1
84 | 72 | 1059 | 70 | LDB | 62.9
84 | 72 | 1059 | 70 | LWB | 60.8
84 | 72 | 1059 | 70 | kW | 1.54
86 | 72 | 1059 | 72 | MBh | 35.3
86 | 72 | 1059 | 72 | S/T | 0.686
86 | 72 | 1059 | 72 | ∆T | 21.2
86 | 72 | 1059 | 72 | LDB | 64.8
86 | 72 | 1059 | 72 | LWB | 62.6
86 | 72 | 1059 | 72 | kW | 1.65
90 | 72 | 1059 | 75 | MBh | 36.1
90 | 72 | 1059 | 75 | S/T | 0.651
90 | 72 | 1059 | 75 | ∆T | 20.5
90 | 72 | 1059 | 75 | LDB | 69.5
90 | 72 | 1059 | 75 | LWB | 66.1
90 | 72 | 1059 | 75 | kW | 1.62
68 | 75 | 1059 | 57 | MBh | 19.5
68 | 75 | 1059 | 57 | S/T | 0.856
68 | 75 | 1059 | 57 | ∆T | 14.6
68 | 75 | 1059 | 57 | LDB | 53.4
68 | 75 | 1059 | 57 | LWB | 50
68 | 75 | 1059 | 57 | kW | 0.85
72 | 75 | 1059 | 61 | MBh | 23.7
72 | 75 | 1059 | 61 | S/T | 0.819
72 | 75 | 1059 | 61 | ∆T | 17
72 | 75 | 1059 | 61 | LDB | 55
72 | 75 | 1059 | 61 | LWB | 53.1
72 | 75 | 1059 | 61 | kW | 1.06
77 | 75 | 1059 | 64 | MBh | 26.8
77 | 75 | 1059 | 64 | S/T | 0.787
77 | 75 | 1059 | 64 | ∆T | 18.4
77 | 75 | 1059 | 64 | LDB | 58.6
77 | 75 | 1059 | 64 | LWB | 55.6
77 | 75 | 1059 | 64 | kW | 1.22
80 | 75 | 1059 | 67 | MBh | 30
80 | 75 | 1059 | 67 | S/T | 0.743
80 | 75 | 1059 | 67 | ∆T | 19.5
80 | 75 | 1059 | 67 | LDB | 60.5
80 | 75 | 1059 | 67 | LWB | 58.1
80 | 75 | 1059 | 67 | kW | 1.39
84 | 75 | 1059 | 70 | MBh | 33.2
84 | 75 | 1059 | 70 | S/T | 0.726
84 | 75 | 1059 | 70 | ∆T | 21.1
84 | 75 | 1059 | 70 | LDB | 62.9
84 | 75 | 1059 | 70 | LWB | 60.8
84 | 75 | 1059 | 70 | kW | 1.57
86 | 75 | 1059 | 72 | MBh | 35.1
86 | 75 | 1059 | 72 | S/T | 0.687
86 | 75 | 1059 | 72 | ∆T | 21.1
86 | 75 | 1059 | 72 | LDB | 64.9
86 | 75 | 1059 | 72 | LWB | 62.7
86 | 75 | 1059 | 72 | kW | 1.7
90 | 75 | 1059 | 75 | MBh | 35.7
90 | 75 | 1059 | 75 | S/T | 0.653
90 | 75 | 1059 | 75 | ∆T | 20.4
90 | 75 | 1059 | 75 | LDB | 69.6
90 | 75 | 1059 | 75 | LWB | 66.2
90 | 75 | 1059 | 75 | kW | 1.71
68 | 79 | 1059 | 57 | MBh | 19.5
68 | 79 | 1059 | 57 | S/T | 0.856
68 | 79 | 1059 | 57 | ∆T | 14.6
68 | 79 | 1059 | 57 | LDB | 53.4
68 | 79 | 1059 | 57 | LWB | 50
68 | 79 | 1059 | 57 | kW | 0.87
72 | 79 | 1059 | 61 | MBh | 23.7
72 | 79 | 1059 | 61 | S/T | 0.819
72 | 79 | 1059 | 61 | ∆T | 17
72 | 79 | 1059 | 61 | LDB | 55
72 | 79 | 1059 | 61 | LWB | 53.1
72 | 79 | 1059 | 61 | kW | 1.09
77 | 79 | 1059 | 64 | MBh | 26.8
77 | 79 | 1059 | 64 | S/T | 0.787
77 | 79 | 1059 | 64 | ∆T | 18.4
77 | 79 | 1059 | 64 | LDB | 58.6
77 | 79 | 1059 | 64 | LWB | 55.6
77 | 79 | 1059 | 64 | kW | 1.28
80 | 79 | 1059 | 67 | MBh | 30
80 | 79 | 1059 | 67 | S/T | 0.743
80 | 79 | 1059 | 67 | ∆T | 19.5
80 | 79 | 1059 | 67 | LDB | 60.5
80 | 79 | 1059 | 67 | LWB | 58.1
80 | 79 | 1059 | 67 | kW | 1.51
84 | 79 | 1059 | 70 | MBh | 33.2
84 | 79 | 1059 | 70 | S/T | 0.726
84 | 79 | 1059 | 70 | ∆T | 21.1
84 | 79 | 1059 | 70 | LDB | 62.9
84 | 79 | 1059 | 70 | LWB | 60.8
84 | 79 | 1059 | 70 | kW | 1.75
86 | 79 | 1059 | 72 | MBh | 34.5
86 | 79 | 1059 | 72 | S/T | 0.687
86 | 79 | 1059 | 72 | ∆T | 20.7
86 | 79 | 1059 | 72 | LDB | 65.3
86 | 79 | 1059 | 72 | LWB | 62.8
86 | 79 | 1059 | 72 | kW | 1.85
90 | 79 | 1059 | 75 | MBh | 35.1
90 | 79 | 1059 | 75 | S/T | 0.652
90 | 79 | 1059 | 75 | ∆T | 20
90 | 79 | 1059 | 75 | LDB | 70
90 | 79 | 1059 | 75 | LWB | 66.3
90 | 79 | 1059 | 75 | kW | 1.86
68 | 83 | 1059 | 57 | MBh | 19.5
68 | 83 | 1059 | 57 | S/T | 0.856
68 | 83 | 1059 | 57 | ∆T | 14.6
68 | 83 | 1059 | 57 | LDB | 53.4
68 | 83 | 1059 | 57 | LWB | 50
68 | 83 | 1059 | 57 | kW | 0.92
72 | 83 | 1059 | 61 | MBh | 23.7
72 | 83 | 1059 | 61 | S/T | 0.819
72 | 83 | 1059 | 61 | ∆T | 17
72 | 83 | 1059 | 61 | LDB | 55
72 | 83 | 1059 | 61 | LWB | 53.1
72 | 83 | 1059 | 61 | kW | 1.19
77 | 83 | 1059 | 64 | MBh | 26.8
77 | 83 | 1059 | 64 | S/T | 0.787
77 | 83 | 1059 | 64 | ∆T | 18.4
77 | 83 | 1059 | 64 | LDB | 58.6
77 | 83 | 1059 | 64 | LWB | 55.6
77 | 83 | 1059 | 64 | kW | 1.43
80 | 83 | 1059 | 67 | MBh | 30
80 | 83 | 1059 | 67 | S/T | 0.743
80 | 83 | 1059 | 67 | ∆T | 19.5
80 | 83 | 1059 | 67 | LDB | 60.5
80 | 83 | 1059 | 67 | LWB | 58.1
80 | 83 | 1059 | 67 | kW | 1.68
84 | 83 | 1059 | 70 | MBh | 33.2
84 | 83 | 1059 | 70 | S/T | 0.726
84 | 83 | 1059 | 70 | ∆T | 21.1
84 | 83 | 1059 | 70 | LDB | 62.9
84 | 83 | 1059 | 70 | LWB | 60.8
84 | 83 | 1059 | 70 | kW | 1.95
86 | 83 | 1059 | 72 | MBh | 33.9
86 | 83 | 1059 | 72 | S/T | 0.687
86 | 83 | 1059 | 72 | ∆T | 20.4
86 | 83 | 1059 | 72 | LDB | 65.6
86 | 83 | 1059 | 72 | LWB | 63
86 | 83 | 1059 | 72 | kW | 2
90 | 83 | 1059 | 75 | MBh | 34.5
90 | 83 | 1059 | 75 | S/T | 0.652
90 | 83 | 1059 | 75 | ∆T | 19.7
90 | 83 | 1059 | 75 | LDB | 70.3
90 | 83 | 1059 | 75 | LWB | 66.5
90 | 83 | 1059 | 75 | kW | 2.01
68 | 87 | 1059 | 57 | MBh | 19.5
68 | 87 | 1059 | 57 | S/T | 0.856
68 | 87 | 1059 | 57 | ∆T | 14.6
68 | 87 | 1059 | 57 | LDB | 53.4
68 | 87 | 1059 | 57 | LWB | 50
68 | 87 | 1059 | 57 | kW | 1.01
72 | 87 | 1059 | 61 | MBh | 23.7
72 | 87 | 1059 | 61 | S/T | 0.819
72 | 87 | 1059 | 61 | ∆T | 17
72 | 87 | 1059 | 61 | LDB | 55
72 | 87 | 1059 | 61 | LWB | 53.1
72 | 87 | 1059 | 61 | kW | 1.32
77 | 87 | 1059 | 64 | MBh | 26.8
77 | 87 | 1059 | 64 | S/T | 0.787
77 | 87 | 1059 | 64 | ∆T | 18.4
77 | 87 | 1059 | 64 | LDB | 58.6
77 | 87 | 1059 | 64 | LWB | 55.6
77 | 87 | 1059 | 64 | kW | 1.58
80 | 87 | 1059 | 67 | MBh | 30
80 | 87 | 1059 | 67 | S/T | 0.743
80 | 87 | 1059 | 67 | ∆T | 19.5
80 | 87 | 1059 | 67 | LDB | 60.5
80 | 87 | 1059 | 67 | LWB | 58.1
80 | 87 | 1059 | 67 | kW | 1.86
84 | 87 | 1059 | 70 | MBh | 33
84 | 87 | 1059 | 70 | S/T | 0.724
84 | 87 | 1059 | 70 | ∆T | 20.9
84 | 87 | 1059 | 70 | LDB | 63.1
84 | 87 | 1059 | 70 | LWB | 60.8
84 | 87 | 1059 | 70 | kW | 2.14
86 | 87 | 1059 | 72 | MBh | 33.4
86 | 87 | 1059 | 72 | S/T | 0.686
86 | 87 | 1059 | 72 | ∆T | 20
86 | 87 | 1059 | 72 | LDB | 66
86 | 87 | 1059 | 72 | LWB | 63.2
86 | 87 | 1059 | 72 | kW | 2.15
90 | 87 | 1059 | 75 | MBh | 34
90 | 87 | 1059 | 75 | S/T | 0.653
90 | 87 | 1059 | 75 | ∆T | 19.4
90 | 87 | 1059 | 75 | LDB | 70.6
90 | 87 | 1059 | 75 | LWB | 66.6
90 | 87 | 1059 | 75 | kW | 2.17
68 | 91 | 1059 | 57 | MBh | 19.5
68 | 91 | 1059 | 57 | S/T | 0.856
68 | 91 | 1059 | 57 | ∆T | 14.6
68 | 91 | 1059 | 57 | LDB | 53.4
68 | 91 | 1059 | 57 | LWB | 50
68 | 91 | 1059 | 57 | kW | 1.11
72 | 91 | 1059 | 61 | MBh | 23.7
72 | 91 | 1059 | 61 | S/T | 0.819
72 | 91 | 1059 | 61 | ∆T | 17
72 | 91 | 1059 | 61 | LDB | 55
72 | 91 | 1059 | 61 | LWB | 53.1
72 | 91 | 1059 | 61 | kW | 1.45
77 | 91 | 1059 | 64 | MBh | 26.8
77 | 91 | 1059 | 64 | S/T | 0.787
77 | 91 | 1059 | 64 | ∆T | 18.4
77 | 91 | 1059 | 64 | LDB | 58.6
77 | 91 | 1059 | 64 | LWB | 55.6
77 | 91 | 1059 | 64 | kW | 1.74
80 | 91 | 1059 | 67 | MBh | 30
80 | 91 | 1059 | 67 | S/T | 0.743
80 | 91 | 1059 | 67 | ∆T | 19.5
80 | 91 | 1059 | 67 | LDB | 60.5
80 | 91 | 1059 | 67 | LWB | 58.1
80 | 91 | 1059 | 67 | kW | 2.05
84 | 91 | 1059 | 70 | MBh | 32.4
84 | 91 | 1059 | 70 | S/T | 0.725
84 | 91 | 1059 | 70 | ∆T | 20.5
84 | 91 | 1059 | 70 | LDB | 63.5
84 | 91 | 1059 | 70 | LWB | 61
84 | 91 | 1059 | 70 | kW | 2.29
86 | 91 | 1059 | 72 | MBh | 32.8
86 | 91 | 1059 | 72 | S/T | 0.686
86 | 91 | 1059 | 72 | ∆T | 19.7
86 | 91 | 1059 | 72 | LDB | 66.3
86 | 91 | 1059 | 72 | LWB | 63.3
86 | 91 | 1059 | 72 | kW | 2.3
90 | 91 | 1059 | 75 | MBh | 33.4
90 | 91 | 1059 | 75 | S/T | 0.653
90 | 91 | 1059 | 75 | ∆T | 19.1
90 | 91 | 1059 | 75 | LDB | 70.9
90 | 91 | 1059 | 75 | LWB | 66.8
90 | 91 | 1059 | 75 | kW | 2.32
68 | 93 | 1059 | 57 | MBh | 19.5
68 | 93 | 1059 | 57 | S/T | 0.856
68 | 93 | 1059 | 57 | ∆T | 14.6
68 | 93 | 1059 | 57 | LDB | 53.4
68 | 93 | 1059 | 57 | LWB | 50
68 | 93 | 1059 | 57 | kW | 1.17
72 | 93 | 1059 | 61 | MBh | 23.7
72 | 93 | 1059 | 61 | S/T | 0.819
72 | 93 | 1059 | 61 | ∆T | 17
72 | 93 | 1059 | 61 | LDB | 55
72 | 93 | 1059 | 61 | LWB | 53.1
72 | 93 | 1059 | 61 | kW | 1.52
77 | 93 | 1059 | 64 | MBh | 26.8
77 | 93 | 1059 | 64 | S/T | 0.787
77 | 93 | 1059 | 64 | ∆T | 18.4
77 | 93 | 1059 | 64 | LDB | 58.6
77 | 93 | 1059 | 64 | LWB | 55.6
77 | 93 | 1059 | 64 | kW | 1.83
80 | 93 | 1059 | 67 | MBh | 30
80 | 93 | 1059 | 67 | S/T | 0.743
80 | 93 | 1059 | 67 | ∆T | 19.5
80 | 93 | 1059 | 67 | LDB | 60.5
80 | 93 | 1059 | 67 | LWB | 58.1
80 | 93 | 1059 | 67 | kW | 2.15
84 | 93 | 1059 | 70 | MBh | 32.1
84 | 93 | 1059 | 70 | S/T | 0.726
84 | 93 | 1059 | 70 | ∆T | 20.4
84 | 93 | 1059 | 70 | LDB | 63.6
84 | 93 | 1059 | 70 | LWB | 61.1
84 | 93 | 1059 | 70 | kW | 2.37
86 | 93 | 1059 | 72 | MBh | 32.5
86 | 93 | 1059 | 72 | S/T | 0.686
86 | 93 | 1059 | 72 | ∆T | 19.5
86 | 93 | 1059 | 72 | LDB | 66.5
86 | 93 | 1059 | 72 | LWB | 63.4
86 | 93 | 1059 | 72 | kW | 2.38
90 | 93 | 1059 | 75 | MBh | 33.1
90 | 93 | 1059 | 75 | S/T | 0.653
90 | 93 | 1059 | 75 | ∆T | 18.9
90 | 93 | 1059 | 75 | LDB | 71.1
90 | 93 | 1059 | 75 | LWB | 66.9
90 | 93 | 1059 | 75 | kW | 2.39
68 | 95 | 1059 | 57 | MBh | 19.5
68 | 95 | 1059 | 57 | S/T | 0.856
68 | 95 | 1059 | 57 | ∆T | 14.6
68 | 95 | 1059 | 57 | LDB | 53.4
68 | 95 | 1059 | 57 | LWB | 50
68 | 95 | 1059 | 57 | kW | 1.23
72 | 95 | 1059 | 61 | MBh | 23.7
72 | 95 | 1059 | 61 | S/T | 0.819
72 | 95 | 1059 | 61 | ∆T | 17
72 | 95 | 1059 | 61 | LDB | 55
72 | 95 | 1059 | 61 | LWB | 53.1
72 | 95 | 1059 | 61 | kW | 1.61
77 | 95 | 1059 | 64 | MBh | 26.8
77 | 95 | 1059 | 64 | S/T | 0.787
77 | 95 | 1059 | 64 | ∆T | 18.4
77 | 95 | 1059 | 64 | LDB | 58.6
77 | 95 | 1059 | 64 | LWB | 55.6
77 | 95 | 1059 | 64 | kW | 1.93
80 | 95 | 1059 | 67 | MBh | 30
80 | 95 | 1059 | 67 | S/T | 0.743
80 | 95 | 1059 | 67 | ∆T | 19.5
80 | 95 | 1059 | 67 | LDB | 60.5
80 | 95 | 1059 | 67 | LWB | 58.1
80 | 95 | 1059 | 67 | kW | 2.28
84 | 95 | 1059 | 70 | MBh | 31.8
84 | 95 | 1059 | 70 | S/T | 0.726
84 | 95 | 1059 | 70 | ∆T | 20.2
84 | 95 | 1059 | 70 | LDB | 63.8
84 | 95 | 1059 | 70 | LWB | 61.2
84 | 95 | 1059 | 70 | kW | 2.47
86 | 95 | 1059 | 72 | MBh | 32.2
86 | 95 | 1059 | 72 | S/T | 0.689
86 | 95 | 1059 | 72 | ∆T | 19.4
86 | 95 | 1059 | 72 | LDB | 66.6
86 | 95 | 1059 | 72 | LWB | 63.5
86 | 95 | 1059 | 72 | kW | 2.48
90 | 95 | 1059 | 75 | MBh | 32.9
90 | 95 | 1059 | 75 | S/T | 0.65
90 | 95 | 1059 | 75 | ∆T | 18.7
90 | 95 | 1059 | 75 | LDB | 71.3
90 | 95 | 1059 | 75 | LWB | 66.9
90 | 95 | 1059 | 75 | kW | 2.5
68 | 99 | 1059 | 57 | MBh | 19.5
68 | 99 | 1059 | 57 | S/T | 0.856
68 | 99 | 1059 | 57 | ∆T | 14.6
68 | 99 | 1059 | 57 | LDB | 53.4
68 | 99 | 1059 | 57 | LWB | 50
68 | 99 | 1059 | 57 | kW | 1.38
72 | 99 | 1059 | 61 | MBh | 23.7
72 | 99 | 1059 | 61 | S/T | 0.819
72 | 99 | 1059 | 61 | ∆T | 17
72 | 99 | 1059 | 61 | LDB | 55
72 | 99 | 1059 | 61 | LWB | 53.1
72 | 99 | 1059 | 61 | kW | 1.81
77 | 99 | 1059 | 64 | MBh | 26.8
77 | 99 | 1059 | 64 | S/T | 0.787
77 | 99 | 1059 | 64 | ∆T | 18.4
77 | 99 | 1059 | 64 | LDB | 58.6
77 | 99 | 1059 | 64 | LWB | 55.6
77 | 99 | 1059 | 64 | kW | 2.17
80 | 99 | 1059 | 67 | MBh | 30
80 | 99 | 1059 | 67 | S/T | 0.743
80 | 99 | 1059 | 67 | ∆T | 19.5
80 | 99 | 1059 | 67 | LDB | 60.5
80 | 99 | 1059 | 67 | LWB | 58.1
80 | 99 | 1059 | 67 | kW | 2.56
84 | 99 | 1059 | 70 | MBh | 31.3
84 | 99 | 1059 | 70 | S/T | 0.725
84 | 99 | 1059 | 70 | ∆T | 19.8
84 | 99 | 1059 | 70 | LDB | 64.2
84 | 99 | 1059 | 70 | LWB | 61.4
84 | 99 | 1059 | 70 | kW | 2.68
86 | 99 | 1059 | 72 | MBh | 31.7
86 | 99 | 1059 | 72 | S/T | 0.688
86 | 99 | 1059 | 72 | ∆T | 19.1
86 | 99 | 1059 | 72 | LDB | 66.9
86 | 99 | 1059 | 72 | LWB | 63.7
86 | 99 | 1059 | 72 | kW | 2.7
90 | 99 | 1059 | 75 | MBh | 32.3
90 | 99 | 1059 | 75 | S/T | 0.653
90 | 99 | 1059 | 75 | ∆T | 18.4
90 | 99 | 1059 | 75 | LDB | 71.6
90 | 99 | 1059 | 75 | LWB | 67.1
90 | 99 | 1059 | 75 | kW | 2.72
68 | 103 | 1059 | 57 | MBh | 19.5
68 | 103 | 1059 | 57 | S/T | 0.856
68 | 103 | 1059 | 57 | ∆T | 14.6
68 | 103 | 1059 | 57 | LDB | 53.4
68 | 103 | 1059 | 57 | LWB | 50
68 | 103 | 1059 | 57 | kW | 1.53
72 | 103 | 1059 | 61 | MBh | 23.7
72 | 103 | 1059 | 61 | S/T | 0.819
72 | 103 | 1059 | 61 | ∆T | 17
72 | 103 | 1059 | 61 | LDB | 55
72 | 103 | 1059 | 61 | LWB | 53.1
72 | 103 | 1059 | 61 | kW | 2.02
77 | 103 | 1059 | 64 | MBh | 26.8
77 | 103 | 1059 | 64 | S/T | 0.787
77 | 103 | 1059 | 64 | ∆T | 18.4
77 | 103 | 1059 | 64 | LDB | 58.6
77 | 103 | 1059 | 64 | LWB | 55.6
77 | 103 | 1059 | 64 | kW | 2.42
80 | 103 | 1059 | 67 | MBh | 30
80 | 103 | 1059 | 67 | S/T | 0.743
80 | 103 | 1059 | 67 | ∆T | 19.5
80 | 103 | 1059 | 67 | LDB | 60.5
80 | 103 | 1059 | 67 | LWB | 58.1
80 | 103 | 1059 | 67 | kW | 2.87
84 | 103 | 1059 | 70 | MBh | 30.7
84 | 103 | 1059 | 70 | S/T | 0.726
84 | 103 | 1059 | 70 | ∆T | 19.5
84 | 103 | 1059 | 70 | LDB | 64.5
84 | 103 | 1059 | 70 | LWB | 61.5
84 | 103 | 1059 | 70 | kW | 2.9
86 | 103 | 1059 | 72 | MBh | 31.1
86 | 103 | 1059 | 72 | S/T | 0.688
86 | 103 | 1059 | 72 | ∆T | 18.7
86 | 103 | 1059 | 72 | LDB | 67.3
86 | 103 | 1059 | 72 | LWB | 63.8
86 | 103 | 1059 | 72 | kW | 2.91
90 | 103 | 1059 | 75 | MBh | 31.7
90 | 103 | 1059 | 75 | S/T | 0.653
90 | 103 | 1059 | 75 | ∆T | 18.1
90 | 103 | 1059 | 75 | LDB | 71.9
90 | 103 | 1059 | 75 | LWB | 67.3
90 | 103 | 1059 | 75 | kW | 2.94
68 | 106 | 1059 | 57 | MBh | 19.5
68 | 106 | 1059 | 57 | S/T | 0.856
68 | 106 | 1059 | 57 | ∆T | 14.6
68 | 106 | 1059 | 57 | LDB | 53.4
68 | 106 | 1059 | 57 | LWB | 50
68 | 106 | 1059 | 57 | kW | 1.66
72 | 106 | 1059 | 61 | MBh | 23.7
72 | 106 | 1059 | 61 | S/T | 0.819
72 | 106 | 1059 | 61 | ∆T | 17
72 | 106 | 1059 | 61 | LDB | 55
72 | 106 | 1059 | 61 | LWB | 53.1
72 | 106 | 1059 | 61 | kW | 2.18
77 | 106 | 1059 | 64 | MBh | 26.8
77 | 106 | 1059 | 64 | S/T | 0.787
77 | 106 | 1059 | 64 | ∆T | 18.4
77 | 106 | 1059 | 64 | LDB | 58.6
77 | 106 | 1059 | 64 | LWB | 55.6
77 | 106 | 1059 | 64 | kW | 2.62
80 | 106 | 1059 | 67 | MBh | 29.7
80 | 106 | 1059 | 67 | S/T | 0.741
80 | 106 | 1059 | 67 | ∆T | 19.2
80 | 106 | 1059 | 67 | LDB | 60.8
80 | 106 | 1059 | 67 | LWB | 58.2
80 | 106 | 1059 | 67 | kW | 3.04
84 | 106 | 1059 | 70 | MBh | 30.3
84 | 106 | 1059 | 70 | S/T | 0.726
84 | 106 | 1059 | 70 | ∆T | 19.2
84 | 106 | 1059 | 70 | LDB | 64.8
84 | 106 | 1059 | 70 | LWB | 61.7
84 | 106 | 1059 | 70 | kW | 3.06
86 | 106 | 1059 | 72 | MBh | 30.7
86 | 106 | 1059 | 72 | S/T | 0.687
86 | 106 | 1059 | 72 | ∆T | 18.4
86 | 106 | 1059 | 72 | LDB | 67.6
86 | 106 | 1059 | 72 | LWB | 63.9
86 | 106 | 1059 | 72 | kW | 3.08
90 | 106 | 1059 | 75 | MBh | 31.3
90 | 106 | 1059 | 75 | S/T | 0.652
90 | 106 | 1059 | 75 | ∆T | 17.8
90 | 106 | 1059 | 75 | LDB | 72.2
90 | 106 | 1059 | 75 | LWB | 67.4
90 | 106 | 1059 | 75 | kW | 3.1
68 | 110 | 1059 | 57 | MBh | 19.5
68 | 110 | 1059 | 57 | S/T | 0.856
68 | 110 | 1059 | 57 | ∆T | 14.6
68 | 110 | 1059 | 57 | LDB | 53.4
68 | 110 | 1059 | 57 | LWB | 50
68 | 110 | 1059 | 57 | kW | 1.83
72 | 110 | 1059 | 61 | MBh | 23.7
72 | 110 | 1059 | 61 | S/T | 0.819
72 | 110 | 1059 | 61 | ∆T | 17
72 | 110 | 1059 | 61 | LDB | 55
72 | 110 | 1059 | 61 | LWB | 53.1
72 | 110 | 1059 | 61 | kW | 2.41
77 | 110 | 1059 | 64 | MBh | 26.8
77 | 110 | 1059 | 64 | S/T | 0.787
77 | 110 | 1059 | 64 | ∆T | 18.4
77 | 110 | 1059 | 64 | LDB | 58.6
77 | 110 | 1059 | 64 | LWB | 55.6
77 | 110 | 1059 | 64 | kW | 2.91
80 | 110 | 1059 | 67 | MBh | 29.1
80 | 110 | 1059 | 67 | S/T | 0.742
80 | 110 | 1059 | 67 | ∆T | 18.9
80 | 110 | 1059 | 67 | LDB | 61.1
80 | 110 | 1059 | 67 | LWB | 58.4
80 | 110 | 1059 | 67 | kW | 3.26
84 | 110 | 1059 | 70 | MBh | 29.7
84 | 110 | 1059 | 70 | S/T | 0.727
84 | 110 | 1059 | 70 | ∆T | 18.9
84 | 110 | 1059 | 70 | LDB | 65.1
84 | 110 | 1059 | 70 | LWB | 61.8
84 | 110 | 1059 | 70 | kW | 3.28
86 | 110 | 1059 | 72 | MBh | 30.1
86 | 110 | 1059 | 72 | S/T | 0.688
86 | 110 | 1059 | 72 | ∆T | 18.1
86 | 110 | 1059 | 72 | LDB | 67.9
86 | 110 | 1059 | 72 | LWB | 64.1
86 | 110 | 1059 | 72 | kW | 3.3
90 | 110 | 1059 | 75 | MBh | 30.1
90 | 110 | 1059 | 75 | S/T | 0.651
90 | 110 | 1059 | 75 | ∆T | 17.1
90 | 110 | 1059 | 75 | LDB | 72.9
90 | 110 | 1059 | 75 | LWB | 67.7
90 | 110 | 1059 | 75 | kW | 3.3
68 | 115 | 1059 | 57 | MBh | 19.5
68 | 115 | 1059 | 57 | S/T | 0.856
68 | 115 | 1059 | 57 | ∆T | 14.6
68 | 115 | 1059 | 57 | LDB | 53.4
68 | 115 | 1059 | 57 | LWB | 50
68 | 115 | 1059 | 57 | kW | 2.07
72 | 115 | 1059 | 61 | MBh | 23.7
72 | 115 | 1059 | 61 | S/T | 0.819
72 | 115 | 1059 | 61 | ∆T | 17
72 | 115 | 1059 | 61 | LDB | 55
72 | 115 | 1059 | 61 | LWB | 53.1
72 | 115 | 1059 | 61 | kW | 2.73
77 | 115 | 1059 | 64 | MBh | 26.8
77 | 115 | 1059 | 64 | S/T | 0.787
77 | 115 | 1059 | 64 | ∆T | 18.4
77 | 115 | 1059 | 64 | LDB | 58.6
77 | 115 | 1059 | 64 | LWB | 55.6
77 | 115 | 1059 | 64 | kW | 3.29
80 | 115 | 1059 | 67 | MBh | 28.1
80 | 115 | 1059 | 67 | S/T | 0.744
80 | 115 | 1059 | 67 | ∆T | 18.3
80 | 115 | 1059 | 67 | LDB | 61.7
80 | 115 | 1059 | 67 | LWB | 58.7
80 | 115 | 1059 | 67 | kW | 3.52
84 | 115 | 1059 | 70 | MBh | 28.1
84 | 115 | 1059 | 70 | S/T | 0.726
84 | 115 | 1059 | 70 | ∆T | 17.8
84 | 115 | 1059 | 70 | LDB | 66.2
84 | 115 | 1059 | 70 | LWB | 62.3
84 | 115 | 1059 | 70 | kW | 3.52
86 | 115 | 1059 | 72 | MBh | 28.1
86 | 115 | 1059 | 72 | S/T | 0.687
86 | 115 | 1059 | 72 | ∆T | 16.9
86 | 115 | 1059 | 72 | LDB | 69.1
86 | 115 | 1059 | 72 | LWB | 64.7
86 | 115 | 1059 | 72 | kW | 3.52
90 | 115 | 1059 | 75 | MBh | 28.1
90 | 115 | 1059 | 75 | S/T | 0.651
90 | 115 | 1059 | 75 | ∆T | 16
90 | 115 | 1059 | 75 | LDB | 74
90 | 115 | 1059 | 75 | LWB | 68.2
90 | 115 | 1059 | 75 | kW | 3.52
68 | 118 | 1059 | 57 | MBh | 19.5
68 | 118 | 1059 | 57 | S/T | 0.856
68 | 118 | 1059 | 57 | ∆T | 14.6
68 | 118 | 1059 | 57 | LDB | 53.4
68 | 118 | 1059 | 57 | LWB | 50
68 | 118 | 1059 | 57 | kW | 2.22
72 | 118 | 1059 | 61 | MBh | 23.7
72 | 118 | 1059 | 61 | S/T | 0.819
72 | 118 | 1059 | 61 | ∆T | 17
72 | 118 | 1059 | 61 | LDB | 55
72 | 118 | 1059 | 61 | LWB | 53.1
72 | 118 | 1059 | 61 | kW | 2.93
77 | 118 | 1059 | 64 | MBh | 24.7
77 | 118 | 1059 | 64 | S/T | 0.789
77 | 118 | 1059 | 64 | ∆T | 17
77 | 118 | 1059 | 64 | LDB | 60
77 | 118 | 1059 | 64 | LWB | 56.3
77 | 118 | 1059 | 64 | kW | 3.13
80 | 118 | 1059 | 67 | MBh | 24.7
80 | 118 | 1059 | 67 | S/T | 0.745
80 | 118 | 1059 | 67 | ∆T | 16.1
80 | 118 | 1059 | 67 | LDB | 63.9
80 | 118 | 1059 | 67 | LWB | 59.8
80 | 118 | 1059 | 67 | kW | 3.13
84 | 118 | 1059 | 70 | MBh | 24.7
84 | 118 | 1059 | 70 | S/T | 0.725
84 | 118 | 1059 | 70 | ∆T | 15.7
84 | 118 | 1059 | 70 | LDB | 68.3
84 | 118 | 1059 | 70 | LWB | 63.3
84 | 118 | 1059 | 70 | kW | 3.13
86 | 118 | 1059 | 72 | MBh | 24.7
86 | 118 | 1059 | 72 | S/T | 0.688
86 | 118 | 1059 | 72 | ∆T | 14.9
86 | 118 | 1059 | 72 | LDB | 71.1
86 | 118 | 1059 | 72 | LWB | 65.6
86 | 118 | 1059 | 72 | kW | 3.13
90 | 118 | 1059 | 75 | MBh | 24.7
90 | 118 | 1059 | 75 | S/T | 0.652
90 | 118 | 1059 | 75 | ∆T | 14.1
90 | 118 | 1059 | 75 | LDB | 75.9
90 | 118 | 1059 | 75 | LWB | 69.1
90 | 118 | 1059 | 75 | kW | 3.13
68 | 122 | 1059 | 57 | MBh | 19.5
68 | 122 | 1059 | 57 | S/T | 0.856
68 | 122 | 1059 | 57 | ∆T | 14.6
68 | 122 | 1059 | 57 | LDB | 53.4
68 | 122 | 1059 | 57 | LWB | 50
68 | 122 | 1059 | 57 | kW | 2.43
72 | 122 | 1059 | 61 | MBh | 19.6
72 | 122 | 1059 | 61 | S/T | 0.821
72 | 122 | 1059 | 61 | ∆T | 14.1
72 | 122 | 1059 | 61 | LDB | 57.9
72 | 122 | 1059 | 61 | LWB | 54.6
72 | 122 | 1059 | 61 | kW | 2.46
77 | 122 | 1059 | 64 | MBh | 19.6
77 | 122 | 1059 | 64 | S/T | 0.791
77 | 122 | 1059 | 64 | ∆T | 13.6
77 | 122 | 1059 | 64 | LDB | 63.4
77 | 122 | 1059 | 64 | LWB | 58
77 | 122 | 1059 | 64 | kW | 2.46
80 | 122 | 1059 | 67 | MBh | 19.6
80 | 122 | 1059 | 67 | S/T | 0.745
80 | 122 | 1059 | 67 | ∆T | 12.8
80 | 122 | 1059 | 67 | LDB | 67.2
80 | 122 | 1059 | 67 | LWB | 61.4
80 | 122 | 1059 | 67 | kW | 2.46
84 | 122 | 1059 | 70 | MBh | 19.6
84 | 122 | 1059 | 70 | S/T | 0.724
84 | 122 | 1059 | 70 | ∆T | 12.4
84 | 122 | 1059 | 70 | LDB | 71.6
84 | 122 | 1059 | 70 | LWB | 64.8
84 | 122 | 1059 | 70 | kW | 2.46
86 | 122 | 1059 | 72 | MBh | 19.6
86 | 122 | 1059 | 72 | S/T | 0.689
86 | 122 | 1059 | 72 | ∆T | 11.8
86 | 122 | 1059 | 72 | LDB | 74.2
86 | 122 | 1059 | 72 | LWB | 67
86 | 122 | 1059 | 72 | kW | 2.46
90 | 122 | 1059 | 75 | MBh | 19.6
90 | 122 | 1059 | 75 | S/T | 0.653
90 | 122 | 1059 | 75 | ∆T | 11.2
90 | 122 | 1059 | 75 | LDB | 78.8
90 | 122 | 1059 | 75 | LWB | 70.4
90 | 122 | 1059 | 75 | kW | 2.46

## RZA36AAVJU - FCA36AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1253 | 57 | MBh | 23.4 | 64 | 60 | 61 | 48 | 2.93
68 | 23 | 1253 | 57 | S/T | 0.889 | 64 | 60 | 65 | 44.5 | 2.65
68 | 23 | 1253 | 57 | ∆T | 15.4 | 64 | 60 | 68 | 41.8 | 2.48
68 | 23 | 1253 | 57 | LDB | 52.6 | 64 | 60 | 70 | 40 | 2.37
68 | 23 | 1253 | 57 | LWB | 49.9 | 64 | 60 | 72 | 38.2 | 2.27
68 | 23 | 1253 | 57 | kW | 0.87 | 64 | 60 | 75 | 35.5 | 2.14
72 | 23 | 1253 | 61 | MBh | 28.4 | 60 | 56 | 61 | 48 | 3.07
72 | 23 | 1253 | 61 | S/T | 0.856 | 60 | 56 | 65 | 44.5 | 2.76
72 | 23 | 1253 | 61 | ∆T | 18 | 60 | 56 | 68 | 41.8 | 2.57
72 | 23 | 1253 | 61 | LDB | 54 | 60 | 56 | 70 | 40 | 2.45
72 | 23 | 1253 | 61 | LWB | 53 | 60 | 56 | 72 | 38.2 | 2.34
72 | 23 | 1253 | 61 | kW | 1.07 | 60 | 56 | 75 | 35.5 | 2.2
77 | 23 | 1253 | 64 | MBh | 32.2 | 57 | 53 | 61 | 48 | 3.18
77 | 23 | 1253 | 64 | S/T | 0.829 | 57 | 53 | 65 | 44.5 | 2.86
77 | 23 | 1253 | 64 | ∆T | 19.7 | 57 | 53 | 68 | 41.8 | 2.64
77 | 23 | 1253 | 64 | LDB | 57.3 | 57 | 53 | 70 | 40 | 2.51
77 | 23 | 1253 | 64 | LWB | 55.4 | 57 | 53 | 72 | 38.2 | 2.4
77 | 23 | 1253 | 64 | kW | 1.22 | 57 | 53 | 75 | 35.5 | 2.24
80 | 23 | 1253 | 67 | MBh | 36 | 54 | 50 | 61 | 48 | 3.31
80 | 23 | 1253 | 67 | S/T | 0.786 | 54 | 50 | 65 | 44.5 | 2.96
80 | 23 | 1253 | 67 | ∆T | 20.9 | 54 | 50 | 68 | 41.8 | 2.73
80 | 23 | 1253 | 67 | LDB | 59.1 | 54 | 50 | 70 | 40 | 2.59
80 | 23 | 1253 | 67 | LWB | 58 | 54 | 50 | 72 | 38.2 | 2.46
80 | 23 | 1253 | 67 | kW | 1.39 | 54 | 50 | 75 | 35.5 | 2.29
84 | 23 | 1253 | 70 | MBh | 39.8 | 51 | 47 | 61 | 48 | 3.45
84 | 23 | 1253 | 70 | S/T | 0.761 | 51 | 47 | 65 | 44.5 | 3.07
84 | 23 | 1253 | 70 | ∆T | 22.4 | 51 | 47 | 68 | 41.8 | 2.82
84 | 23 | 1253 | 70 | LDB | 61.6 | 51 | 47 | 70 | 40 | 2.67
84 | 23 | 1253 | 70 | LWB | 60.6 | 51 | 47 | 72 | 38.2 | 2.53
84 | 23 | 1253 | 70 | kW | 1.55 | 51 | 47 | 75 | 35.5 | 2.35
86 | 23 | 1253 | 72 | MBh | 42.3 | 47 | 43 | 61 | 48 | 3.66
86 | 23 | 1253 | 72 | S/T | 0.723 | 47 | 43 | 65 | 44.5 | 3.24
86 | 23 | 1253 | 72 | ∆T | 22.6 | 47 | 43 | 68 | 41.8 | 2.97
86 | 23 | 1253 | 72 | LDB | 63.4 | 47 | 43 | 70 | 40 | 2.8
86 | 23 | 1253 | 72 | LWB | 62.5 | 47 | 43 | 72 | 38.2 | 2.65
86 | 23 | 1253 | 72 | kW | 1.67 | 47 | 43 | 75 | 35.5 | 2.44
90 | 23 | 1253 | 75 | MBh | 46.1 | 44 | 40 | 61 | 48 | 3.84
90 | 23 | 1253 | 75 | S/T | 0.69 | 44 | 40 | 65 | 44.5 | 3.39
90 | 23 | 1253 | 75 | ∆T | 23.5 | 44 | 40 | 68 | 41.8 | 3.09
90 | 23 | 1253 | 75 | LDB | 66.5 | 44 | 40 | 70 | 40 | 2.91
90 | 23 | 1253 | 75 | LWB | 65.3 | 44 | 40 | 72 | 38.2 | 2.74
90 | 23 | 1253 | 75 | kW | 1.84 | 44 | 40 | 75 | 35.5 | 2.52
68 | 30 | 1253 | 57 | MBh | 23.4 | 39 | 36 | 61 | 48 | 4.11
68 | 30 | 1253 | 57 | S/T | 0.889 | 39 | 36 | 65 | 44.5 | 3.61
68 | 30 | 1253 | 57 | ∆T | 15.4 | 39 | 36 | 68 | 41.8 | 3.28
68 | 30 | 1253 | 57 | LDB | 52.6 | 39 | 36 | 70 | 40 | 3.07
68 | 30 | 1253 | 57 | LWB | 49.9 | 39 | 36 | 72 | 38.2 | 2.89
68 | 30 | 1253 | 57 | kW | 0.89 | 39 | 36 | 75 | 35.5 | 2.63
72 | 30 | 1253 | 61 | MBh | 28.4 | 35 | 32 | 61 | 48 | 4.42
72 | 30 | 1253 | 61 | S/T | 0.856 | 35 | 32 | 65 | 44.5 | 3.87
72 | 30 | 1253 | 61 | ∆T | 18 | 35 | 32 | 68 | 41.8 | 3.49
72 | 30 | 1253 | 61 | LDB | 54 | 35 | 32 | 70 | 40 | 3.27
72 | 30 | 1253 | 61 | LWB | 53 | 35 | 32 | 72 | 38.2 | 3.05
72 | 30 | 1253 | 61 | kW | 1.1 | 35 | 32 | 75 | 35.5 | 2.77
77 | 30 | 1253 | 64 | MBh | 32.2 | 30 | 28 | 61 | 48 | 4.79
77 | 30 | 1253 | 64 | S/T | 0.829 | 30 | 28 | 65 | 44.5 | 4.17
77 | 30 | 1253 | 64 | ∆T | 19.7 | 30 | 28 | 68 | 41.8 | 3.75
77 | 30 | 1253 | 64 | LDB | 57.3 | 30 | 28 | 70 | 40 | 3.49
77 | 30 | 1253 | 64 | LWB | 55.4 | 30 | 28 | 72 | 38.2 | 3.25
77 | 30 | 1253 | 64 | kW | 1.26 | 30 | 28 | 75 | 35.5 | 2.93
80 | 30 | 1253 | 67 | MBh | 36 | 26 | 24 | 61 | 48 | 5.21
80 | 30 | 1253 | 67 | S/T | 0.786 | 26 | 24 | 65 | 44.5 | 4.52
80 | 30 | 1253 | 67 | ∆T | 20.9 | 26 | 24 | 68 | 41.8 | 4.05
80 | 30 | 1253 | 67 | LDB | 59.1 | 26 | 24 | 70 | 40 | 3.76
80 | 30 | 1253 | 67 | LWB | 58 | 26 | 24 | 72 | 38.2 | 3.49
80 | 30 | 1253 | 67 | kW | 1.43 | 26 | 24 | 75 | 35.5 | 3.13
84 | 30 | 1253 | 70 | MBh | 39.8 | 22 | 20 | 61 | 48 | 5.59
84 | 30 | 1253 | 70 | S/T | 0.761 | 22 | 20 | 65 | 44.5 | 4.93
84 | 30 | 1253 | 70 | ∆T | 22.4 | 22 | 20 | 68 | 41.8 | 4.4
84 | 30 | 1253 | 70 | LDB | 61.6 | 22 | 20 | 70 | 40 | 4.08
84 | 30 | 1253 | 70 | LWB | 60.6 | 22 | 20 | 72 | 38.2 | 3.77
84 | 30 | 1253 | 70 | kW | 1.61 | 22 | 20 | 75 | 35.5 | 3.36
86 | 30 | 1253 | 72 | MBh | 42.3 | 19 | 18 | 61 | 47.1 | 5.55
86 | 30 | 1253 | 72 | S/T | 0.723 | 19 | 18 | 65 | 44.5 | 5.17
86 | 30 | 1253 | 72 | ∆T | 22.6 | 19 | 18 | 68 | 41.8 | 4.6
86 | 30 | 1253 | 72 | LDB | 63.4 | 19 | 18 | 70 | 40 | 4.26
86 | 30 | 1253 | 72 | LWB | 62.5 | 19 | 18 | 72 | 38.2 | 3.93
86 | 30 | 1253 | 72 | kW | 1.72 | 19 | 18 | 75 | 35.5 | 3.49
90 | 30 | 1253 | 75 | MBh | 46.1 | 17 | 16 | 61 | 45.7 | 5.49
90 | 30 | 1253 | 75 | S/T | 0.69 | 17 | 16 | 65 | 44.5 | 5.49
90 | 30 | 1253 | 75 | ∆T | 23.5 | 17 | 16 | 68 | 41.8 | 4.88
90 | 30 | 1253 | 75 | LDB | 66.5 | 17 | 16 | 70 | 40 | 4.51
90 | 30 | 1253 | 75 | LWB | 65.3 | 17 | 16 | 72 | 38.2 | 4.15
90 | 30 | 1253 | 75 | kW | 1.9 | 17 | 16 | 75 | 35.5 | 3.67
68 | 40 | 1253 | 57 | MBh | 23.4 | 15 | 14 | 61 | 44.8 | 5.45
68 | 40 | 1253 | 57 | S/T | 0.889 | 15 | 14 | 65 | 44.5 | 5.58
68 | 40 | 1253 | 57 | ∆T | 15.4 | 15 | 14 | 68 | 41.8 | 5.07
68 | 40 | 1253 | 57 | LDB | 52.6 | 15 | 14 | 70 | 40 | 4.67
68 | 40 | 1253 | 57 | LWB | 49.9 | 15 | 14 | 72 | 38.2 | 4.3
68 | 40 | 1253 | 57 | kW | 0.93 | 15 | 14 | 75 | 35.5 | 3.8
72 | 40 | 1253 | 61 | MBh | 28.4 | 13 | 12 | 61 | 43.4 | 5.4
72 | 40 | 1253 | 61 | S/T | 0.856 | 13 | 12 | 65 | 43.4 | 5.54
72 | 40 | 1253 | 61 | ∆T | 18 | 13 | 12 | 68 | 41.8 | 5.33
72 | 40 | 1253 | 61 | LDB | 54 | 13 | 12 | 70 | 40 | 4.91
72 | 40 | 1253 | 61 | LWB | 53 | 13 | 12 | 72 | 38.2 | 4.51
72 | 40 | 1253 | 61 | kW | 1.15 | 13 | 12 | 75 | 35.5 | 3.97
77 | 40 | 1253 | 64 | MBh | 32.2 | 10 | 9 | 61 | 40.5 | 5.3
77 | 40 | 1253 | 64 | S/T | 0.829 | 10 | 9 | 65 | 40.5 | 5.44
77 | 40 | 1253 | 64 | ∆T | 19.7 | 10 | 9 | 68 | 40.5 | 5.55
77 | 40 | 1253 | 64 | LDB | 57.3 | 10 | 9 | 70 | 40 | 5.38
77 | 40 | 1253 | 64 | LWB | 55.4 | 10 | 9 | 72 | 38.2 | 4.94
77 | 40 | 1253 | 64 | kW | 1.32 | 10 | 9 | 75 | 35.5 | 4.32
80 | 40 | 1253 | 67 | MBh | 36 | 6 | 5 | 61 | 37.6 | 5.19
80 | 40 | 1253 | 67 | S/T | 0.786 | 6 | 5 | 65 | 37.6 | 5.35
80 | 40 | 1253 | 67 | ∆T | 20.9 | 6 | 5 | 68 | 37.6 | 5.46
80 | 40 | 1253 | 67 | LDB | 59.1 | 6 | 5 | 70 | 37.6 | 5.53
80 | 40 | 1253 | 67 | LWB | 58 | 6 | 5 | 72 | 37.6 | 5.44
80 | 40 | 1253 | 67 | kW | 1.5 | 6 | 5 | 75 | 35.5 | 4.75
84 | 40 | 1253 | 70 | MBh | 39.8 | -2 | -2 | 61 | 31.6 | 4.94
84 | 40 | 1253 | 70 | S/T | 0.761 | -2 | -2 | 65 | 31.6 | 5.11
84 | 40 | 1253 | 70 | ∆T | 22.4 | -2 | -2 | 68 | 31.6 | 5.23
84 | 40 | 1253 | 70 | LDB | 61.6 | -2 | -2 | 70 | 31.6 | 5.32
84 | 40 | 1253 | 70 | LWB | 60.6 | -2 | -2 | 72 | 31.6 | 5.4
84 | 40 | 1253 | 70 | kW | 1.69 | -2 | -2 | 75 | 31.6 | 5.53
86 | 40 | 1253 | 72 | MBh | 42.3 | -4 | -4 | 61 | 30.1 | 4.86
86 | 40 | 1253 | 72 | S/T | 0.723 | -4 | -4 | 65 | 30.1 | 5.04
86 | 40 | 1253 | 72 | ∆T | 22.6 | -4 | -4 | 68 | 30.1 | 5.17
86 | 40 | 1253 | 72 | LDB | 63.4 | -4 | -4 | 70 | 30.1 | 5.26
86 | 40 | 1253 | 72 | LWB | 62.5 | -4 | -4 | 72 | 30.1 | 5.34
86 | 40 | 1253 | 72 | kW | 1.81 | -4 | -4 | 75 | 30.1 | 5.47
90 | 40 | 1253 | 75 | MBh | 46.1
90 | 40 | 1253 | 75 | S/T | 0.69
90 | 40 | 1253 | 75 | ∆T | 23.5
90 | 40 | 1253 | 75 | LDB | 66.5
90 | 40 | 1253 | 75 | LWB | 65.3
90 | 40 | 1253 | 75 | kW | 2
68 | 50 | 1253 | 57 | MBh | 23.4
68 | 50 | 1253 | 57 | S/T | 0.889
68 | 50 | 1253 | 57 | ∆T | 15.4
68 | 50 | 1253 | 57 | LDB | 52.6
68 | 50 | 1253 | 57 | LWB | 49.9
68 | 50 | 1253 | 57 | kW | 0.98
72 | 50 | 1253 | 61 | MBh | 28.4
72 | 50 | 1253 | 61 | S/T | 0.856
72 | 50 | 1253 | 61 | ∆T | 18
72 | 50 | 1253 | 61 | LDB | 54
72 | 50 | 1253 | 61 | LWB | 53
72 | 50 | 1253 | 61 | kW | 1.21
77 | 50 | 1253 | 64 | MBh | 32.2
77 | 50 | 1253 | 64 | S/T | 0.829
77 | 50 | 1253 | 64 | ∆T | 19.7
77 | 50 | 1253 | 64 | LDB | 57.3
77 | 50 | 1253 | 64 | LWB | 55.4
77 | 50 | 1253 | 64 | kW | 1.39
80 | 50 | 1253 | 67 | MBh | 36
80 | 50 | 1253 | 67 | S/T | 0.786
80 | 50 | 1253 | 67 | ∆T | 20.9
80 | 50 | 1253 | 67 | LDB | 59.1
80 | 50 | 1253 | 67 | LWB | 58
80 | 50 | 1253 | 67 | kW | 1.58
84 | 50 | 1253 | 70 | MBh | 39.8
84 | 50 | 1253 | 70 | S/T | 0.761
84 | 50 | 1253 | 70 | ∆T | 22.4
84 | 50 | 1253 | 70 | LDB | 61.6
84 | 50 | 1253 | 70 | LWB | 60.6
84 | 50 | 1253 | 70 | kW | 1.77
86 | 50 | 1253 | 72 | MBh | 42.3
86 | 50 | 1253 | 72 | S/T | 0.723
86 | 50 | 1253 | 72 | ∆T | 22.6
86 | 50 | 1253 | 72 | LDB | 63.4
86 | 50 | 1253 | 72 | LWB | 62.5
86 | 50 | 1253 | 72 | kW | 1.9
90 | 50 | 1253 | 75 | MBh | 46.1
90 | 50 | 1253 | 75 | S/T | 0.69
90 | 50 | 1253 | 75 | ∆T | 23.5
90 | 50 | 1253 | 75 | LDB | 66.5
90 | 50 | 1253 | 75 | LWB | 65.3
90 | 50 | 1253 | 75 | kW | 2.1
68 | 54 | 1253 | 57 | MBh | 23.4
68 | 54 | 1253 | 57 | S/T | 0.889
68 | 54 | 1253 | 57 | ∆T | 15.4
68 | 54 | 1253 | 57 | LDB | 52.6
68 | 54 | 1253 | 57 | LWB | 49.9
68 | 54 | 1253 | 57 | kW | 0.99
72 | 54 | 1253 | 61 | MBh | 28.4
72 | 54 | 1253 | 61 | S/T | 0.856
72 | 54 | 1253 | 61 | ∆T | 18
72 | 54 | 1253 | 61 | LDB | 54
72 | 54 | 1253 | 61 | LWB | 53
72 | 54 | 1253 | 61 | kW | 1.23
77 | 54 | 1253 | 64 | MBh | 32.2
77 | 54 | 1253 | 64 | S/T | 0.829
77 | 54 | 1253 | 64 | ∆T | 19.7
77 | 54 | 1253 | 64 | LDB | 57.3
77 | 54 | 1253 | 64 | LWB | 55.4
77 | 54 | 1253 | 64 | kW | 1.42
80 | 54 | 1253 | 67 | MBh | 36
80 | 54 | 1253 | 67 | S/T | 0.786
80 | 54 | 1253 | 67 | ∆T | 20.9
80 | 54 | 1253 | 67 | LDB | 59.1
80 | 54 | 1253 | 67 | LWB | 58
80 | 54 | 1253 | 67 | kW | 1.61
84 | 54 | 1253 | 70 | MBh | 39.8
84 | 54 | 1253 | 70 | S/T | 0.761
84 | 54 | 1253 | 70 | ∆T | 22.4
84 | 54 | 1253 | 70 | LDB | 61.6
84 | 54 | 1253 | 70 | LWB | 60.6
84 | 54 | 1253 | 70 | kW | 1.81
86 | 54 | 1253 | 72 | MBh | 42.3
86 | 54 | 1253 | 72 | S/T | 0.723
86 | 54 | 1253 | 72 | ∆T | 22.6
86 | 54 | 1253 | 72 | LDB | 63.4
86 | 54 | 1253 | 72 | LWB | 62.5
86 | 54 | 1253 | 72 | kW | 1.94
90 | 54 | 1253 | 75 | MBh | 46.1
90 | 54 | 1253 | 75 | S/T | 0.69
90 | 54 | 1253 | 75 | ∆T | 23.5
90 | 54 | 1253 | 75 | LDB | 66.5
90 | 54 | 1253 | 75 | LWB | 65.3
90 | 54 | 1253 | 75 | kW | 2.15
68 | 58 | 1253 | 57 | MBh | 23.4
68 | 58 | 1253 | 57 | S/T | 0.889
68 | 58 | 1253 | 57 | ∆T | 15.4
68 | 58 | 1253 | 57 | LDB | 52.6
68 | 58 | 1253 | 57 | LWB | 49.9
68 | 58 | 1253 | 57 | kW | 1.01
72 | 58 | 1253 | 61 | MBh | 28.4
72 | 58 | 1253 | 61 | S/T | 0.856
72 | 58 | 1253 | 61 | ∆T | 18
72 | 58 | 1253 | 61 | LDB | 54
72 | 58 | 1253 | 61 | LWB | 53
72 | 58 | 1253 | 61 | kW | 1.26
77 | 58 | 1253 | 64 | MBh | 32.2
77 | 58 | 1253 | 64 | S/T | 0.829
77 | 58 | 1253 | 64 | ∆T | 19.7
77 | 58 | 1253 | 64 | LDB | 57.3
77 | 58 | 1253 | 64 | LWB | 55.4
77 | 58 | 1253 | 64 | kW | 1.45
80 | 58 | 1253 | 67 | MBh | 36
80 | 58 | 1253 | 67 | S/T | 0.786
80 | 58 | 1253 | 67 | ∆T | 20.9
80 | 58 | 1253 | 67 | LDB | 59.1
80 | 58 | 1253 | 67 | LWB | 58
80 | 58 | 1253 | 67 | kW | 1.65
84 | 58 | 1253 | 70 | MBh | 39.8
84 | 58 | 1253 | 70 | S/T | 0.761
84 | 58 | 1253 | 70 | ∆T | 22.4
84 | 58 | 1253 | 70 | LDB | 61.6
84 | 58 | 1253 | 70 | LWB | 60.6
84 | 58 | 1253 | 70 | kW | 1.85
86 | 58 | 1253 | 72 | MBh | 42.3
86 | 58 | 1253 | 72 | S/T | 0.723
86 | 58 | 1253 | 72 | ∆T | 22.6
86 | 58 | 1253 | 72 | LDB | 63.4
86 | 58 | 1253 | 72 | LWB | 62.5
86 | 58 | 1253 | 72 | kW | 1.98
90 | 58 | 1253 | 75 | MBh | 45.7
90 | 58 | 1253 | 75 | S/T | 0.689
90 | 58 | 1253 | 75 | ∆T | 23.3
90 | 58 | 1253 | 75 | LDB | 66.7
90 | 58 | 1253 | 75 | LWB | 65.4
90 | 58 | 1253 | 75 | kW | 2.15
68 | 62 | 1253 | 57 | MBh | 23.4
68 | 62 | 1253 | 57 | S/T | 0.889
68 | 62 | 1253 | 57 | ∆T | 15.4
68 | 62 | 1253 | 57 | LDB | 52.6
68 | 62 | 1253 | 57 | LWB | 49.9
68 | 62 | 1253 | 57 | kW | 1.03
72 | 62 | 1253 | 61 | MBh | 28.4
72 | 62 | 1253 | 61 | S/T | 0.856
72 | 62 | 1253 | 61 | ∆T | 18
72 | 62 | 1253 | 61 | LDB | 54
72 | 62 | 1253 | 61 | LWB | 53
72 | 62 | 1253 | 61 | kW | 1.28
77 | 62 | 1253 | 64 | MBh | 32.2
77 | 62 | 1253 | 64 | S/T | 0.829
77 | 62 | 1253 | 64 | ∆T | 19.7
77 | 62 | 1253 | 64 | LDB | 57.3
77 | 62 | 1253 | 64 | LWB | 55.4
77 | 62 | 1253 | 64 | kW | 1.48
80 | 62 | 1253 | 67 | MBh | 36
80 | 62 | 1253 | 67 | S/T | 0.786
80 | 62 | 1253 | 67 | ∆T | 20.9
80 | 62 | 1253 | 67 | LDB | 59.1
80 | 62 | 1253 | 67 | LWB | 58
80 | 62 | 1253 | 67 | kW | 1.68
84 | 62 | 1253 | 70 | MBh | 39.8
84 | 62 | 1253 | 70 | S/T | 0.761
84 | 62 | 1253 | 70 | ∆T | 22.4
84 | 62 | 1253 | 70 | LDB | 61.6
84 | 62 | 1253 | 70 | LWB | 60.6
84 | 62 | 1253 | 70 | kW | 1.89
86 | 62 | 1253 | 72 | MBh | 42.3
86 | 62 | 1253 | 72 | S/T | 0.723
86 | 62 | 1253 | 72 | ∆T | 22.6
86 | 62 | 1253 | 72 | LDB | 63.4
86 | 62 | 1253 | 72 | LWB | 62.5
86 | 62 | 1253 | 72 | kW | 2.03
90 | 62 | 1253 | 75 | MBh | 45
90 | 62 | 1253 | 75 | S/T | 0.689
90 | 62 | 1253 | 75 | ∆T | 22.9
90 | 62 | 1253 | 75 | LDB | 67.1
90 | 62 | 1253 | 75 | LWB | 65.5
90 | 62 | 1253 | 75 | kW | 2.14
68 | 66 | 1253 | 57 | MBh | 23.4
68 | 66 | 1253 | 57 | S/T | 0.889
68 | 66 | 1253 | 57 | ∆T | 15.4
68 | 66 | 1253 | 57 | LDB | 52.6
68 | 66 | 1253 | 57 | LWB | 49.9
68 | 66 | 1253 | 57 | kW | 1.06
72 | 66 | 1253 | 61 | MBh | 28.4
72 | 66 | 1253 | 61 | S/T | 0.856
72 | 66 | 1253 | 61 | ∆T | 18
72 | 66 | 1253 | 61 | LDB | 54
72 | 66 | 1253 | 61 | LWB | 53
72 | 66 | 1253 | 61 | kW | 1.31
77 | 66 | 1253 | 64 | MBh | 32.2
77 | 66 | 1253 | 64 | S/T | 0.829
77 | 66 | 1253 | 64 | ∆T | 19.7
77 | 66 | 1253 | 64 | LDB | 57.3
77 | 66 | 1253 | 64 | LWB | 55.4
77 | 66 | 1253 | 64 | kW | 1.51
80 | 66 | 1253 | 67 | MBh | 36
80 | 66 | 1253 | 67 | S/T | 0.786
80 | 66 | 1253 | 67 | ∆T | 20.9
80 | 66 | 1253 | 67 | LDB | 59.1
80 | 66 | 1253 | 67 | LWB | 58
80 | 66 | 1253 | 67 | kW | 1.72
84 | 66 | 1253 | 70 | MBh | 39.8
84 | 66 | 1253 | 70 | S/T | 0.761
84 | 66 | 1253 | 70 | ∆T | 22.4
84 | 66 | 1253 | 70 | LDB | 61.6
84 | 66 | 1253 | 70 | LWB | 60.6
84 | 66 | 1253 | 70 | kW | 1.93
86 | 66 | 1253 | 72 | MBh | 42.3
86 | 66 | 1253 | 72 | S/T | 0.723
86 | 66 | 1253 | 72 | ∆T | 22.6
86 | 66 | 1253 | 72 | LDB | 63.4
86 | 66 | 1253 | 72 | LWB | 62.5
86 | 66 | 1253 | 72 | kW | 2.07
90 | 66 | 1253 | 75 | MBh | 44.3
90 | 66 | 1253 | 75 | S/T | 0.688
90 | 66 | 1253 | 75 | ∆T | 22.5
90 | 66 | 1253 | 75 | LDB | 67.5
90 | 66 | 1253 | 75 | LWB | 65.7
90 | 66 | 1253 | 75 | kW | 2.13
68 | 70 | 1253 | 57 | MBh | 23.4
68 | 70 | 1253 | 57 | S/T | 0.889
68 | 70 | 1253 | 57 | ∆T | 15.4
68 | 70 | 1253 | 57 | LDB | 52.6
68 | 70 | 1253 | 57 | LWB | 49.9
68 | 70 | 1253 | 57 | kW | 1.08
72 | 70 | 1253 | 61 | MBh | 28.4
72 | 70 | 1253 | 61 | S/T | 0.856
72 | 70 | 1253 | 61 | ∆T | 18
72 | 70 | 1253 | 61 | LDB | 54
72 | 70 | 1253 | 61 | LWB | 53
72 | 70 | 1253 | 61 | kW | 1.34
77 | 70 | 1253 | 64 | MBh | 32.2
77 | 70 | 1253 | 64 | S/T | 0.829
77 | 70 | 1253 | 64 | ∆T | 19.7
77 | 70 | 1253 | 64 | LDB | 57.3
77 | 70 | 1253 | 64 | LWB | 55.4
77 | 70 | 1253 | 64 | kW | 1.55
80 | 70 | 1253 | 67 | MBh | 36
80 | 70 | 1253 | 67 | S/T | 0.786
80 | 70 | 1253 | 67 | ∆T | 20.9
80 | 70 | 1253 | 67 | LDB | 59.1
80 | 70 | 1253 | 67 | LWB | 58
80 | 70 | 1253 | 67 | kW | 1.76
84 | 70 | 1253 | 70 | MBh | 39.8
84 | 70 | 1253 | 70 | S/T | 0.761
84 | 70 | 1253 | 70 | ∆T | 22.4
84 | 70 | 1253 | 70 | LDB | 61.6
84 | 70 | 1253 | 70 | LWB | 60.6
84 | 70 | 1253 | 70 | kW | 1.97
86 | 70 | 1253 | 72 | MBh | 42.3
86 | 70 | 1253 | 72 | S/T | 0.723
86 | 70 | 1253 | 72 | ∆T | 22.6
86 | 70 | 1253 | 72 | LDB | 63.4
86 | 70 | 1253 | 72 | LWB | 62.5
86 | 70 | 1253 | 72 | kW | 2.12
90 | 70 | 1253 | 75 | MBh | 43.7
90 | 70 | 1253 | 75 | S/T | 0.689
90 | 70 | 1253 | 75 | ∆T | 22.2
90 | 70 | 1253 | 75 | LDB | 67.8
90 | 70 | 1253 | 75 | LWB | 65.8
90 | 70 | 1253 | 75 | kW | 2.11
68 | 72 | 1253 | 57 | MBh | 23.4
68 | 72 | 1253 | 57 | S/T | 0.889
68 | 72 | 1253 | 57 | ∆T | 15.4
68 | 72 | 1253 | 57 | LDB | 52.6
68 | 72 | 1253 | 57 | LWB | 49.9
68 | 72 | 1253 | 57 | kW | 1.09
72 | 72 | 1253 | 61 | MBh | 28.4
72 | 72 | 1253 | 61 | S/T | 0.856
72 | 72 | 1253 | 61 | ∆T | 18
72 | 72 | 1253 | 61 | LDB | 54
72 | 72 | 1253 | 61 | LWB | 53
72 | 72 | 1253 | 61 | kW | 1.35
77 | 72 | 1253 | 64 | MBh | 32.2
77 | 72 | 1253 | 64 | S/T | 0.829
77 | 72 | 1253 | 64 | ∆T | 19.7
77 | 72 | 1253 | 64 | LDB | 57.3
77 | 72 | 1253 | 64 | LWB | 55.4
77 | 72 | 1253 | 64 | kW | 1.56
80 | 72 | 1253 | 67 | MBh | 36
80 | 72 | 1253 | 67 | S/T | 0.786
80 | 72 | 1253 | 67 | ∆T | 20.9
80 | 72 | 1253 | 67 | LDB | 59.1
80 | 72 | 1253 | 67 | LWB | 58
80 | 72 | 1253 | 67 | kW | 1.78
84 | 72 | 1253 | 70 | MBh | 39.8
84 | 72 | 1253 | 70 | S/T | 0.761
84 | 72 | 1253 | 70 | ∆T | 22.4
84 | 72 | 1253 | 70 | LDB | 61.6
84 | 72 | 1253 | 70 | LWB | 60.6
84 | 72 | 1253 | 70 | kW | 2
86 | 72 | 1253 | 72 | MBh | 42.3
86 | 72 | 1253 | 72 | S/T | 0.723
86 | 72 | 1253 | 72 | ∆T | 22.6
86 | 72 | 1253 | 72 | LDB | 63.4
86 | 72 | 1253 | 72 | LWB | 62.5
86 | 72 | 1253 | 72 | kW | 2.14
90 | 72 | 1253 | 75 | MBh | 43.3
90 | 72 | 1253 | 75 | S/T | 0.688
90 | 72 | 1253 | 75 | ∆T | 22
90 | 72 | 1253 | 75 | LDB | 68
90 | 72 | 1253 | 75 | LWB | 65.9
90 | 72 | 1253 | 75 | kW | 2.11
68 | 75 | 1253 | 57 | MBh | 23.4
68 | 75 | 1253 | 57 | S/T | 0.889
68 | 75 | 1253 | 57 | ∆T | 15.4
68 | 75 | 1253 | 57 | LDB | 52.6
68 | 75 | 1253 | 57 | LWB | 49.9
68 | 75 | 1253 | 57 | kW | 1.11
72 | 75 | 1253 | 61 | MBh | 28.4
72 | 75 | 1253 | 61 | S/T | 0.856
72 | 75 | 1253 | 61 | ∆T | 18
72 | 75 | 1253 | 61 | LDB | 54
72 | 75 | 1253 | 61 | LWB | 53
72 | 75 | 1253 | 61 | kW | 1.38
77 | 75 | 1253 | 64 | MBh | 32.2
77 | 75 | 1253 | 64 | S/T | 0.829
77 | 75 | 1253 | 64 | ∆T | 19.7
77 | 75 | 1253 | 64 | LDB | 57.3
77 | 75 | 1253 | 64 | LWB | 55.4
77 | 75 | 1253 | 64 | kW | 1.59
80 | 75 | 1253 | 67 | MBh | 36
80 | 75 | 1253 | 67 | S/T | 0.786
80 | 75 | 1253 | 67 | ∆T | 20.9
80 | 75 | 1253 | 67 | LDB | 59.1
80 | 75 | 1253 | 67 | LWB | 58
80 | 75 | 1253 | 67 | kW | 1.81
84 | 75 | 1253 | 70 | MBh | 39.8
84 | 75 | 1253 | 70 | S/T | 0.761
84 | 75 | 1253 | 70 | ∆T | 22.4
84 | 75 | 1253 | 70 | LDB | 61.6
84 | 75 | 1253 | 70 | LWB | 60.6
84 | 75 | 1253 | 70 | kW | 2.03
86 | 75 | 1253 | 72 | MBh | 42.1
86 | 75 | 1253 | 72 | S/T | 0.722
86 | 75 | 1253 | 72 | ∆T | 22.5
86 | 75 | 1253 | 72 | LDB | 63.5
86 | 75 | 1253 | 72 | LWB | 62.5
86 | 75 | 1253 | 72 | kW | 2.18
90 | 75 | 1253 | 75 | MBh | 42.8
90 | 75 | 1253 | 75 | S/T | 0.689
90 | 75 | 1253 | 75 | ∆T | 21.8
90 | 75 | 1253 | 75 | LDB | 68.2
90 | 75 | 1253 | 75 | LWB | 66
90 | 75 | 1253 | 75 | kW | 2.19
68 | 79 | 1253 | 57 | MBh | 23.4
68 | 79 | 1253 | 57 | S/T | 0.889
68 | 79 | 1253 | 57 | ∆T | 15.4
68 | 79 | 1253 | 57 | LDB | 52.6
68 | 79 | 1253 | 57 | LWB | 49.9
68 | 79 | 1253 | 57 | kW | 1.13
72 | 79 | 1253 | 61 | MBh | 28.4
72 | 79 | 1253 | 61 | S/T | 0.856
72 | 79 | 1253 | 61 | ∆T | 18
72 | 79 | 1253 | 61 | LDB | 54
72 | 79 | 1253 | 61 | LWB | 53
72 | 79 | 1253 | 61 | kW | 1.41
77 | 79 | 1253 | 64 | MBh | 32.2
77 | 79 | 1253 | 64 | S/T | 0.829
77 | 79 | 1253 | 64 | ∆T | 19.7
77 | 79 | 1253 | 64 | LDB | 57.3
77 | 79 | 1253 | 64 | LWB | 55.4
77 | 79 | 1253 | 64 | kW | 1.65
80 | 79 | 1253 | 67 | MBh | 36
80 | 79 | 1253 | 67 | S/T | 0.786
80 | 79 | 1253 | 67 | ∆T | 20.9
80 | 79 | 1253 | 67 | LDB | 59.1
80 | 79 | 1253 | 67 | LWB | 58
80 | 79 | 1253 | 67 | kW | 1.95
84 | 79 | 1253 | 70 | MBh | 39.8
84 | 79 | 1253 | 70 | S/T | 0.761
84 | 79 | 1253 | 70 | ∆T | 22.4
84 | 79 | 1253 | 70 | LDB | 61.6
84 | 79 | 1253 | 70 | LWB | 60.6
84 | 79 | 1253 | 70 | kW | 2.26
86 | 79 | 1253 | 72 | MBh | 41.4
86 | 79 | 1253 | 72 | S/T | 0.722
86 | 79 | 1253 | 72 | ∆T | 22.1
86 | 79 | 1253 | 72 | LDB | 63.9
86 | 79 | 1253 | 72 | LWB | 62.7
86 | 79 | 1253 | 72 | kW | 2.39
90 | 79 | 1253 | 75 | MBh | 42.1
90 | 79 | 1253 | 75 | S/T | 0.689
90 | 79 | 1253 | 75 | ∆T | 21.4
90 | 79 | 1253 | 75 | LDB | 68.6
90 | 79 | 1253 | 75 | LWB | 66.2
90 | 79 | 1253 | 75 | kW | 2.4
68 | 83 | 1253 | 57 | MBh | 23.4
68 | 83 | 1253 | 57 | S/T | 0.889
68 | 83 | 1253 | 57 | ∆T | 15.4
68 | 83 | 1253 | 57 | LDB | 52.6
68 | 83 | 1253 | 57 | LWB | 49.9
68 | 83 | 1253 | 57 | kW | 1.19
72 | 83 | 1253 | 61 | MBh | 28.4
72 | 83 | 1253 | 61 | S/T | 0.856
72 | 83 | 1253 | 61 | ∆T | 18
72 | 83 | 1253 | 61 | LDB | 54
72 | 83 | 1253 | 61 | LWB | 53
72 | 83 | 1253 | 61 | kW | 1.55
77 | 83 | 1253 | 64 | MBh | 32.2
77 | 83 | 1253 | 64 | S/T | 0.829
77 | 83 | 1253 | 64 | ∆T | 19.7
77 | 83 | 1253 | 64 | LDB | 57.3
77 | 83 | 1253 | 64 | LWB | 55.4
77 | 83 | 1253 | 64 | kW | 1.85
80 | 83 | 1253 | 67 | MBh | 36
80 | 83 | 1253 | 67 | S/T | 0.786
80 | 83 | 1253 | 67 | ∆T | 20.9
80 | 83 | 1253 | 67 | LDB | 59.1
80 | 83 | 1253 | 67 | LWB | 58
80 | 83 | 1253 | 67 | kW | 2.18
84 | 83 | 1253 | 70 | MBh | 39.8
84 | 83 | 1253 | 70 | S/T | 0.761
84 | 83 | 1253 | 70 | ∆T | 22.4
84 | 83 | 1253 | 70 | LDB | 61.6
84 | 83 | 1253 | 70 | LWB | 60.6
84 | 83 | 1253 | 70 | kW | 2.53
86 | 83 | 1253 | 72 | MBh | 40.7
86 | 83 | 1253 | 72 | S/T | 0.722
86 | 83 | 1253 | 72 | ∆T | 21.7
86 | 83 | 1253 | 72 | LDB | 64.3
86 | 83 | 1253 | 72 | LWB | 62.9
86 | 83 | 1253 | 72 | kW | 2.59
90 | 83 | 1253 | 75 | MBh | 41.5
90 | 83 | 1253 | 75 | S/T | 0.689
90 | 83 | 1253 | 75 | ∆T | 21.1
90 | 83 | 1253 | 75 | LDB | 68.9
90 | 83 | 1253 | 75 | LWB | 66.3
90 | 83 | 1253 | 75 | kW | 2.61
68 | 87 | 1253 | 57 | MBh | 23.4
68 | 87 | 1253 | 57 | S/T | 0.889
68 | 87 | 1253 | 57 | ∆T | 15.4
68 | 87 | 1253 | 57 | LDB | 52.6
68 | 87 | 1253 | 57 | LWB | 49.9
68 | 87 | 1253 | 57 | kW | 1.32
72 | 87 | 1253 | 61 | MBh | 28.4
72 | 87 | 1253 | 61 | S/T | 0.856
72 | 87 | 1253 | 61 | ∆T | 18
72 | 87 | 1253 | 61 | LDB | 54
72 | 87 | 1253 | 61 | LWB | 53
72 | 87 | 1253 | 61 | kW | 1.72
77 | 87 | 1253 | 64 | MBh | 32.2
77 | 87 | 1253 | 64 | S/T | 0.829
77 | 87 | 1253 | 64 | ∆T | 19.7
77 | 87 | 1253 | 64 | LDB | 57.3
77 | 87 | 1253 | 64 | LWB | 55.4
77 | 87 | 1253 | 64 | kW | 2.06
80 | 87 | 1253 | 67 | MBh | 36
80 | 87 | 1253 | 67 | S/T | 0.786
80 | 87 | 1253 | 67 | ∆T | 20.9
80 | 87 | 1253 | 67 | LDB | 59.1
80 | 87 | 1253 | 67 | LWB | 58
80 | 87 | 1253 | 67 | kW | 2.42
84 | 87 | 1253 | 70 | MBh | 39.5
84 | 87 | 1253 | 70 | S/T | 0.762
84 | 87 | 1253 | 70 | ∆T | 22.2
84 | 87 | 1253 | 70 | LDB | 61.8
84 | 87 | 1253 | 70 | LWB | 60.7
84 | 87 | 1253 | 70 | kW | 2.79
86 | 87 | 1253 | 72 | MBh | 40
86 | 87 | 1253 | 72 | S/T | 0.725
86 | 87 | 1253 | 72 | ∆T | 21.4
86 | 87 | 1253 | 72 | LDB | 64.6
86 | 87 | 1253 | 72 | LWB | 63
86 | 87 | 1253 | 72 | kW | 2.8
90 | 87 | 1253 | 75 | MBh | 40.8
90 | 87 | 1253 | 75 | S/T | 0.689
90 | 87 | 1253 | 75 | ∆T | 20.8
90 | 87 | 1253 | 75 | LDB | 69.2
90 | 87 | 1253 | 75 | LWB | 66.5
90 | 87 | 1253 | 75 | kW | 2.82
68 | 91 | 1253 | 57 | MBh | 23.4
68 | 91 | 1253 | 57 | S/T | 0.889
68 | 91 | 1253 | 57 | ∆T | 15.4
68 | 91 | 1253 | 57 | LDB | 52.6
68 | 91 | 1253 | 57 | LWB | 49.9
68 | 91 | 1253 | 57 | kW | 1.46
72 | 91 | 1253 | 61 | MBh | 28.4
72 | 91 | 1253 | 61 | S/T | 0.856
72 | 91 | 1253 | 61 | ∆T | 18
72 | 91 | 1253 | 61 | LDB | 54
72 | 91 | 1253 | 61 | LWB | 53
72 | 91 | 1253 | 61 | kW | 1.9
77 | 91 | 1253 | 64 | MBh | 32.2
77 | 91 | 1253 | 64 | S/T | 0.829
77 | 91 | 1253 | 64 | ∆T | 19.7
77 | 91 | 1253 | 64 | LDB | 57.3
77 | 91 | 1253 | 64 | LWB | 55.4
77 | 91 | 1253 | 64 | kW | 2.28
80 | 91 | 1253 | 67 | MBh | 36
80 | 91 | 1253 | 67 | S/T | 0.786
80 | 91 | 1253 | 67 | ∆T | 20.9
80 | 91 | 1253 | 67 | LDB | 59.1
80 | 91 | 1253 | 67 | LWB | 58
80 | 91 | 1253 | 67 | kW | 2.69
84 | 91 | 1253 | 70 | MBh | 38.9
84 | 91 | 1253 | 70 | S/T | 0.758
84 | 91 | 1253 | 70 | ∆T | 21.8
84 | 91 | 1253 | 70 | LDB | 62.2
84 | 91 | 1253 | 70 | LWB | 60.9
84 | 91 | 1253 | 70 | kW | 3
86 | 91 | 1253 | 72 | MBh | 39.4
86 | 91 | 1253 | 72 | S/T | 0.723
86 | 91 | 1253 | 72 | ∆T | 21.1
86 | 91 | 1253 | 72 | LDB | 64.9
86 | 91 | 1253 | 72 | LWB | 63.2
86 | 91 | 1253 | 72 | kW | 3.01
90 | 91 | 1253 | 75 | MBh | 40.1
90 | 91 | 1253 | 75 | S/T | 0.688
90 | 91 | 1253 | 75 | ∆T | 20.4
90 | 91 | 1253 | 75 | LDB | 69.6
90 | 91 | 1253 | 75 | LWB | 66.7
90 | 91 | 1253 | 75 | kW | 3.03
68 | 93 | 1253 | 57 | MBh | 23.4
68 | 93 | 1253 | 57 | S/T | 0.889
68 | 93 | 1253 | 57 | ∆T | 15.4
68 | 93 | 1253 | 57 | LDB | 52.6
68 | 93 | 1253 | 57 | LWB | 49.9
68 | 93 | 1253 | 57 | kW | 1.53
72 | 93 | 1253 | 61 | MBh | 28.4
72 | 93 | 1253 | 61 | S/T | 0.856
72 | 93 | 1253 | 61 | ∆T | 18
72 | 93 | 1253 | 61 | LDB | 54
72 | 93 | 1253 | 61 | LWB | 53
72 | 93 | 1253 | 61 | kW | 2
77 | 93 | 1253 | 64 | MBh | 32.2
77 | 93 | 1253 | 64 | S/T | 0.829
77 | 93 | 1253 | 64 | ∆T | 19.7
77 | 93 | 1253 | 64 | LDB | 57.3
77 | 93 | 1253 | 64 | LWB | 55.4
77 | 93 | 1253 | 64 | kW | 2.39
80 | 93 | 1253 | 67 | MBh | 36
80 | 93 | 1253 | 67 | S/T | 0.786
80 | 93 | 1253 | 67 | ∆T | 20.9
80 | 93 | 1253 | 67 | LDB | 59.1
80 | 93 | 1253 | 67 | LWB | 58
80 | 93 | 1253 | 67 | kW | 2.82
84 | 93 | 1253 | 70 | MBh | 38.5
84 | 93 | 1253 | 70 | S/T | 0.761
84 | 93 | 1253 | 70 | ∆T | 21.7
84 | 93 | 1253 | 70 | LDB | 62.3
84 | 93 | 1253 | 70 | LWB | 61
84 | 93 | 1253 | 70 | kW | 3.1
86 | 93 | 1253 | 72 | MBh | 39
86 | 93 | 1253 | 72 | S/T | 0.723
86 | 93 | 1253 | 72 | ∆T | 20.8
86 | 93 | 1253 | 72 | LDB | 65.2
86 | 93 | 1253 | 72 | LWB | 63.3
86 | 93 | 1253 | 72 | kW | 3.12
90 | 93 | 1253 | 75 | MBh | 39.8
90 | 93 | 1253 | 75 | S/T | 0.688
90 | 93 | 1253 | 75 | ∆T | 20.2
90 | 93 | 1253 | 75 | LDB | 69.8
90 | 93 | 1253 | 75 | LWB | 66.7
90 | 93 | 1253 | 75 | kW | 3.14
68 | 95 | 1253 | 57 | MBh | 23.4
68 | 95 | 1253 | 57 | S/T | 0.889
68 | 95 | 1253 | 57 | ∆T | 15.4
68 | 95 | 1253 | 57 | LDB | 52.6
68 | 95 | 1253 | 57 | LWB | 49.9
68 | 95 | 1253 | 57 | kW | 1.6
72 | 95 | 1253 | 61 | MBh | 28.4
72 | 95 | 1253 | 61 | S/T | 0.856
72 | 95 | 1253 | 61 | ∆T | 18
72 | 95 | 1253 | 61 | LDB | 54
72 | 95 | 1253 | 61 | LWB | 53
72 | 95 | 1253 | 61 | kW | 2.1
77 | 95 | 1253 | 64 | MBh | 32.2
77 | 95 | 1253 | 64 | S/T | 0.829
77 | 95 | 1253 | 64 | ∆T | 19.7
77 | 95 | 1253 | 64 | LDB | 57.3
77 | 95 | 1253 | 64 | LWB | 55.4
77 | 95 | 1253 | 64 | kW | 2.51
80 | 95 | 1253 | 67 | MBh | 36
80 | 95 | 1253 | 67 | S/T | 0.786
80 | 95 | 1253 | 67 | ∆T | 20.9
80 | 95 | 1253 | 67 | LDB | 59.1
80 | 95 | 1253 | 67 | LWB | 58
80 | 95 | 1253 | 67 | kW | 2.97
84 | 95 | 1253 | 70 | MBh | 38.2
84 | 95 | 1253 | 70 | S/T | 0.759
84 | 95 | 1253 | 70 | ∆T | 21.4
84 | 95 | 1253 | 70 | LDB | 62.6
84 | 95 | 1253 | 70 | LWB | 61
84 | 95 | 1253 | 70 | kW | 3.21
86 | 95 | 1253 | 72 | MBh | 38.7
86 | 95 | 1253 | 72 | S/T | 0.724
86 | 95 | 1253 | 72 | ∆T | 20.7
86 | 95 | 1253 | 72 | LDB | 65.3
86 | 95 | 1253 | 72 | LWB | 63.4
86 | 95 | 1253 | 72 | kW | 3.22
90 | 95 | 1253 | 75 | MBh | 39.4
90 | 95 | 1253 | 75 | S/T | 0.69
90 | 95 | 1253 | 75 | ∆T | 20.1
90 | 95 | 1253 | 75 | LDB | 69.9
90 | 95 | 1253 | 75 | LWB | 66.8
90 | 95 | 1253 | 75 | kW | 3.24
68 | 99 | 1253 | 57 | MBh | 23.4
68 | 99 | 1253 | 57 | S/T | 0.889
68 | 99 | 1253 | 57 | ∆T | 15.4
68 | 99 | 1253 | 57 | LDB | 52.6
68 | 99 | 1253 | 57 | LWB | 49.9
68 | 99 | 1253 | 57 | kW | 1.76
72 | 99 | 1253 | 61 | MBh | 28.4
72 | 99 | 1253 | 61 | S/T | 0.856
72 | 99 | 1253 | 61 | ∆T | 18
72 | 99 | 1253 | 61 | LDB | 54
72 | 99 | 1253 | 61 | LWB | 53
72 | 99 | 1253 | 61 | kW | 2.3
77 | 99 | 1253 | 64 | MBh | 32.2
77 | 99 | 1253 | 64 | S/T | 0.829
77 | 99 | 1253 | 64 | ∆T | 19.7
77 | 99 | 1253 | 64 | LDB | 57.3
77 | 99 | 1253 | 64 | LWB | 55.4
77 | 99 | 1253 | 64 | kW | 2.76
80 | 99 | 1253 | 67 | MBh | 36
80 | 99 | 1253 | 67 | S/T | 0.786
80 | 99 | 1253 | 67 | ∆T | 20.9
80 | 99 | 1253 | 67 | LDB | 59.1
80 | 99 | 1253 | 67 | LWB | 58
80 | 99 | 1253 | 67 | kW | 3.26
84 | 99 | 1253 | 70 | MBh | 37.5
84 | 99 | 1253 | 70 | S/T | 0.76
84 | 99 | 1253 | 70 | ∆T | 21.1
84 | 99 | 1253 | 70 | LDB | 62.9
84 | 99 | 1253 | 70 | LWB | 61.2
84 | 99 | 1253 | 70 | kW | 3.42
86 | 99 | 1253 | 72 | MBh | 38
86 | 99 | 1253 | 72 | S/T | 0.724
86 | 99 | 1253 | 72 | ∆T | 20.3
86 | 99 | 1253 | 72 | LDB | 65.7
86 | 99 | 1253 | 72 | LWB | 63.5
86 | 99 | 1253 | 72 | kW | 3.43
90 | 99 | 1253 | 75 | MBh | 38.8
90 | 99 | 1253 | 75 | S/T | 0.688
90 | 99 | 1253 | 75 | ∆T | 19.7
90 | 99 | 1253 | 75 | LDB | 70.3
90 | 99 | 1253 | 75 | LWB | 66.9
90 | 99 | 1253 | 75 | kW | 3.46
68 | 103 | 1253 | 57 | MBh | 23.4
68 | 103 | 1253 | 57 | S/T | 0.889
68 | 103 | 1253 | 57 | ∆T | 15.4
68 | 103 | 1253 | 57 | LDB | 52.6
68 | 103 | 1253 | 57 | LWB | 49.9
68 | 103 | 1253 | 57 | kW | 1.92
72 | 103 | 1253 | 61 | MBh | 28.4
72 | 103 | 1253 | 61 | S/T | 0.856
72 | 103 | 1253 | 61 | ∆T | 18
72 | 103 | 1253 | 61 | LDB | 54
72 | 103 | 1253 | 61 | LWB | 53
72 | 103 | 1253 | 61 | kW | 2.52
77 | 103 | 1253 | 64 | MBh | 32.2
77 | 103 | 1253 | 64 | S/T | 0.829
77 | 103 | 1253 | 64 | ∆T | 19.7
77 | 103 | 1253 | 64 | LDB | 57.3
77 | 103 | 1253 | 64 | LWB | 55.4
77 | 103 | 1253 | 64 | kW | 3.03
80 | 103 | 1253 | 67 | MBh | 36
80 | 103 | 1253 | 67 | S/T | 0.786
80 | 103 | 1253 | 67 | ∆T | 20.9
80 | 103 | 1253 | 67 | LDB | 59.1
80 | 103 | 1253 | 67 | LWB | 58
80 | 103 | 1253 | 67 | kW | 3.58
84 | 103 | 1253 | 70 | MBh | 36.8
84 | 103 | 1253 | 70 | S/T | 0.761
84 | 103 | 1253 | 70 | ∆T | 20.7
84 | 103 | 1253 | 70 | LDB | 63.3
84 | 103 | 1253 | 70 | LWB | 61.4
84 | 103 | 1253 | 70 | kW | 3.63
86 | 103 | 1253 | 72 | MBh | 37.3
86 | 103 | 1253 | 72 | S/T | 0.724
86 | 103 | 1253 | 72 | ∆T | 20
86 | 103 | 1253 | 72 | LDB | 66
86 | 103 | 1253 | 72 | LWB | 63.7
86 | 103 | 1253 | 72 | kW | 3.64
90 | 103 | 1253 | 75 | MBh | 38.1
90 | 103 | 1253 | 75 | S/T | 0.688
90 | 103 | 1253 | 75 | ∆T | 19.4
90 | 103 | 1253 | 75 | LDB | 70.6
90 | 103 | 1253 | 75 | LWB | 67.1
90 | 103 | 1253 | 75 | kW | 3.67
68 | 106 | 1253 | 57 | MBh | 23.4
68 | 106 | 1253 | 57 | S/T | 0.889
68 | 106 | 1253 | 57 | ∆T | 15.4
68 | 106 | 1253 | 57 | LDB | 52.6
68 | 106 | 1253 | 57 | LWB | 49.9
68 | 106 | 1253 | 57 | kW | 2.05
72 | 106 | 1253 | 61 | MBh | 28.4
72 | 106 | 1253 | 61 | S/T | 0.856
72 | 106 | 1253 | 61 | ∆T | 18
72 | 106 | 1253 | 61 | LDB | 54
72 | 106 | 1253 | 61 | LWB | 53
72 | 106 | 1253 | 61 | kW | 2.69
77 | 106 | 1253 | 64 | MBh | 32.2
77 | 106 | 1253 | 64 | S/T | 0.829
77 | 106 | 1253 | 64 | ∆T | 19.7
77 | 106 | 1253 | 64 | LDB | 57.3
77 | 106 | 1253 | 64 | LWB | 55.4
77 | 106 | 1253 | 64 | kW | 3.24
80 | 106 | 1253 | 67 | MBh | 35.6
80 | 106 | 1253 | 67 | S/T | 0.787
80 | 106 | 1253 | 67 | ∆T | 20.7
80 | 106 | 1253 | 67 | LDB | 59.3
80 | 106 | 1253 | 67 | LWB | 58.1
80 | 106 | 1253 | 67 | kW | 3.76
84 | 106 | 1253 | 70 | MBh | 36.3
84 | 106 | 1253 | 70 | S/T | 0.76
84 | 106 | 1253 | 70 | ∆T | 20.4
84 | 106 | 1253 | 70 | LDB | 63.6
84 | 106 | 1253 | 70 | LWB | 61.5
84 | 106 | 1253 | 70 | kW | 3.78
86 | 106 | 1253 | 72 | MBh | 36.8
86 | 106 | 1253 | 72 | S/T | 0.723
86 | 106 | 1253 | 72 | ∆T | 19.7
86 | 106 | 1253 | 72 | LDB | 66.3
86 | 106 | 1253 | 72 | LWB | 63.8
86 | 106 | 1253 | 72 | kW | 3.8
90 | 106 | 1253 | 75 | MBh | 37.4
90 | 106 | 1253 | 75 | S/T | 0.69
90 | 106 | 1253 | 75 | ∆T | 19.1
90 | 106 | 1253 | 75 | LDB | 70.9
90 | 106 | 1253 | 75 | LWB | 67.3
90 | 106 | 1253 | 75 | kW | 3.82
68 | 110 | 1253 | 57 | MBh | 23.4
68 | 110 | 1253 | 57 | S/T | 0.889
68 | 110 | 1253 | 57 | ∆T | 15.4
68 | 110 | 1253 | 57 | LDB | 52.6
68 | 110 | 1253 | 57 | LWB | 49.9
68 | 110 | 1253 | 57 | kW | 2.23
72 | 110 | 1253 | 61 | MBh | 28.4
72 | 110 | 1253 | 61 | S/T | 0.856
72 | 110 | 1253 | 61 | ∆T | 18
72 | 110 | 1253 | 61 | LDB | 54
72 | 110 | 1253 | 61 | LWB | 53
72 | 110 | 1253 | 61 | kW | 2.94
77 | 110 | 1253 | 64 | MBh | 32.2
77 | 110 | 1253 | 64 | S/T | 0.829
77 | 110 | 1253 | 64 | ∆T | 19.7
77 | 110 | 1253 | 64 | LDB | 57.3
77 | 110 | 1253 | 64 | LWB | 55.4
77 | 110 | 1253 | 64 | kW | 3.54
80 | 110 | 1253 | 67 | MBh | 34.9
80 | 110 | 1253 | 67 | S/T | 0.785
80 | 110 | 1253 | 67 | ∆T | 20.2
80 | 110 | 1253 | 67 | LDB | 59.8
80 | 110 | 1253 | 67 | LWB | 58.3
80 | 110 | 1253 | 67 | kW | 3.97
84 | 110 | 1253 | 70 | MBh | 35.6
84 | 110 | 1253 | 70 | S/T | 0.758
84 | 110 | 1253 | 70 | ∆T | 20
84 | 110 | 1253 | 70 | LDB | 64
84 | 110 | 1253 | 70 | LWB | 61.7
84 | 110 | 1253 | 70 | kW | 3.99
86 | 110 | 1253 | 72 | MBh | 35.6
86 | 110 | 1253 | 72 | S/T | 0.722
86 | 110 | 1253 | 72 | ∆T | 19
86 | 110 | 1253 | 72 | LDB | 67
86 | 110 | 1253 | 72 | LWB | 64.1
86 | 110 | 1253 | 72 | kW | 3.99
90 | 110 | 1253 | 75 | MBh | 35.6
90 | 110 | 1253 | 75 | S/T | 0.688
90 | 110 | 1253 | 75 | ∆T | 18.1
90 | 110 | 1253 | 75 | LDB | 71.9
90 | 110 | 1253 | 75 | LWB | 67.7
90 | 110 | 1253 | 75 | kW | 3.99
68 | 115 | 1253 | 57 | MBh | 23.4
68 | 115 | 1253 | 57 | S/T | 0.889
68 | 115 | 1253 | 57 | ∆T | 15.4
68 | 115 | 1253 | 57 | LDB | 52.6
68 | 115 | 1253 | 57 | LWB | 49.9
68 | 115 | 1253 | 57 | kW | 2.48
72 | 115 | 1253 | 61 | MBh | 28.4
72 | 115 | 1253 | 61 | S/T | 0.856
72 | 115 | 1253 | 61 | ∆T | 18
72 | 115 | 1253 | 61 | LDB | 54
72 | 115 | 1253 | 61 | LWB | 53
72 | 115 | 1253 | 61 | kW | 3.27
77 | 115 | 1253 | 64 | MBh | 32.1
77 | 115 | 1253 | 64 | S/T | 0.829
77 | 115 | 1253 | 64 | ∆T | 19.7
77 | 115 | 1253 | 64 | LDB | 57.3
77 | 115 | 1253 | 64 | LWB | 55.5
77 | 115 | 1253 | 64 | kW | 3.92
80 | 115 | 1253 | 67 | MBh | 32.1
80 | 115 | 1253 | 67 | S/T | 0.785
80 | 115 | 1253 | 67 | ∆T | 18.6
80 | 115 | 1253 | 67 | LDB | 61.4
80 | 115 | 1253 | 67 | LWB | 59
80 | 115 | 1253 | 67 | kW | 3.92
84 | 115 | 1253 | 70 | MBh | 32.1
84 | 115 | 1253 | 70 | S/T | 0.76
84 | 115 | 1253 | 70 | ∆T | 18
84 | 115 | 1253 | 70 | LDB | 66
84 | 115 | 1253 | 70 | LWB | 62.6
84 | 115 | 1253 | 70 | kW | 3.92
86 | 115 | 1253 | 72 | MBh | 32.1
86 | 115 | 1253 | 72 | S/T | 0.723
86 | 115 | 1253 | 72 | ∆T | 17.1
86 | 115 | 1253 | 72 | LDB | 68.9
86 | 115 | 1253 | 72 | LWB | 64.9
86 | 115 | 1253 | 72 | kW | 3.92
90 | 115 | 1253 | 75 | MBh | 32.1
90 | 115 | 1253 | 75 | S/T | 0.688
90 | 115 | 1253 | 75 | ∆T | 16.3
90 | 115 | 1253 | 75 | LDB | 73.7
90 | 115 | 1253 | 75 | LWB | 68.4
90 | 115 | 1253 | 75 | kW | 3.92
68 | 118 | 1253 | 57 | MBh | 23.4
68 | 118 | 1253 | 57 | S/T | 0.889
68 | 118 | 1253 | 57 | ∆T | 15.4
68 | 118 | 1253 | 57 | LDB | 52.6
68 | 118 | 1253 | 57 | LWB | 49.9
68 | 118 | 1253 | 57 | kW | 2.67
72 | 118 | 1253 | 61 | MBh | 27.7
72 | 118 | 1253 | 61 | S/T | 0.856
72 | 118 | 1253 | 61 | ∆T | 17.5
72 | 118 | 1253 | 61 | LDB | 54.5
72 | 118 | 1253 | 61 | LWB | 53.2
72 | 118 | 1253 | 61 | kW | 3.4
77 | 118 | 1253 | 64 | MBh | 27.7
77 | 118 | 1253 | 64 | S/T | 0.83
77 | 118 | 1253 | 64 | ∆T | 17
77 | 118 | 1253 | 64 | LDB | 60
77 | 118 | 1253 | 64 | LWB | 56.7
77 | 118 | 1253 | 64 | kW | 3.4
80 | 118 | 1253 | 67 | MBh | 27.7
80 | 118 | 1253 | 67 | S/T | 0.787
80 | 118 | 1253 | 67 | ∆T | 16.1
80 | 118 | 1253 | 67 | LDB | 63.9
80 | 118 | 1253 | 67 | LWB | 60.2
80 | 118 | 1253 | 67 | kW | 3.4
84 | 118 | 1253 | 70 | MBh | 27.7
84 | 118 | 1253 | 70 | S/T | 0.758
84 | 118 | 1253 | 70 | ∆T | 15.5
84 | 118 | 1253 | 70 | LDB | 68.5
84 | 118 | 1253 | 70 | LWB | 63.7
84 | 118 | 1253 | 70 | kW | 3.4
86 | 118 | 1253 | 72 | MBh | 27.7
86 | 118 | 1253 | 72 | S/T | 0.722
86 | 118 | 1253 | 72 | ∆T | 14.8
86 | 118 | 1253 | 72 | LDB | 71.2
86 | 118 | 1253 | 72 | LWB | 66
86 | 118 | 1253 | 72 | kW | 3.4
90 | 118 | 1253 | 75 | MBh | 27.7
90 | 118 | 1253 | 75 | S/T | 0.69
90 | 118 | 1253 | 75 | ∆T | 14.1
90 | 118 | 1253 | 75 | LDB | 75.9
90 | 118 | 1253 | 75 | LWB | 69.4
90 | 118 | 1253 | 75 | kW | 3.4
68 | 122 | 1253 | 57 | MBh | 21.8
68 | 122 | 1253 | 57 | S/T | 0.894
68 | 122 | 1253 | 57 | ∆T | 14.4
68 | 122 | 1253 | 57 | LDB | 53.6
68 | 122 | 1253 | 57 | LWB | 50.4
68 | 122 | 1253 | 57 | kW | 2.78
72 | 122 | 1253 | 61 | MBh | 21.8
72 | 122 | 1253 | 61 | S/T | 0.858
72 | 122 | 1253 | 61 | ∆T | 13.8
72 | 122 | 1253 | 61 | LDB | 58.2
72 | 122 | 1253 | 61 | LWB | 55
72 | 122 | 1253 | 61 | kW | 2.78
77 | 122 | 1253 | 64 | MBh | 21.8
77 | 122 | 1253 | 64 | S/T | 0.83
77 | 122 | 1253 | 64 | ∆T | 13.4
77 | 122 | 1253 | 64 | LDB | 63.6
77 | 122 | 1253 | 64 | LWB | 58.4
77 | 122 | 1253 | 64 | kW | 2.78
80 | 122 | 1253 | 67 | MBh | 21.8
80 | 122 | 1253 | 67 | S/T | 0.789
80 | 122 | 1253 | 67 | ∆T | 12.7
80 | 122 | 1253 | 67 | LDB | 67.3
80 | 122 | 1253 | 67 | LWB | 61.7
80 | 122 | 1253 | 67 | kW | 2.78
84 | 122 | 1253 | 70 | MBh | 21.8
84 | 122 | 1253 | 70 | S/T | 0.761
84 | 122 | 1253 | 70 | ∆T | 12.3
84 | 122 | 1253 | 70 | LDB | 71.7
84 | 122 | 1253 | 70 | LWB | 65.1
84 | 122 | 1253 | 70 | kW | 2.78
86 | 122 | 1253 | 72 | MBh | 21.8
86 | 122 | 1253 | 72 | S/T | 0.725
86 | 122 | 1253 | 72 | ∆T | 11.7
86 | 122 | 1253 | 72 | LDB | 74.3
86 | 122 | 1253 | 72 | LWB | 67.3
86 | 122 | 1253 | 72 | kW | 2.78
90 | 122 | 1253 | 75 | MBh | 21.8
90 | 122 | 1253 | 75 | S/T | 0.688
90 | 122 | 1253 | 75 | ∆T | 11.1
90 | 122 | 1253 | 75 | LDB | 78.9
90 | 122 | 1253 | 75 | LWB | 70.7
90 | 122 | 1253 | 75 | kW | 2.78

## RZA42AAVJU - FCA42AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1253 | 57 | MBh | 27.3 | 64 | 60 | 61 | 56.4 | 3.77
68 | 23 | 1253 | 57 | S/T | 0.832 | 64 | 60 | 65 | 52.2 | 3.21
68 | 23 | 1253 | 57 | ∆T | 16.8 | 64 | 60 | 68 | 49.1 | 2.8
68 | 23 | 1253 | 57 | LDB | 51.2 | 64 | 60 | 70 | 47 | 2.52
68 | 23 | 1253 | 57 | LWB | 48.7 | 64 | 60 | 72 | 44.9 | 2.25
68 | 23 | 1253 | 57 | kW | 1.18 | 64 | 60 | 75 | 41.8 | 1.86
72 | 23 | 1253 | 61 | MBh | 33.2 | 60 | 56 | 61 | 56.4 | 4.04
72 | 23 | 1253 | 61 | S/T | 0.795 | 60 | 56 | 65 | 52.2 | 3.45
72 | 23 | 1253 | 61 | ∆T | 19.5 | 60 | 56 | 68 | 49.1 | 3.01
72 | 23 | 1253 | 61 | LDB | 52.5 | 60 | 56 | 70 | 47 | 2.73
72 | 23 | 1253 | 61 | LWB | 51.6 | 60 | 56 | 72 | 44.9 | 2.45
72 | 23 | 1253 | 61 | kW | 1.44 | 60 | 56 | 75 | 41.8 | 2.04
77 | 23 | 1253 | 64 | MBh | 37.6 | 57 | 53 | 61 | 56.4 | 4.24
77 | 23 | 1253 | 64 | S/T | 0.769 | 57 | 53 | 65 | 52.2 | 3.64
77 | 23 | 1253 | 64 | ∆T | 21.4 | 57 | 53 | 68 | 49.1 | 3.19
77 | 23 | 1253 | 64 | LDB | 55.6 | 57 | 53 | 70 | 47 | 2.89
77 | 23 | 1253 | 64 | LWB | 53.9 | 57 | 53 | 72 | 44.9 | 2.61
77 | 23 | 1253 | 64 | kW | 1.66 | 57 | 53 | 75 | 41.8 | 2.18
80 | 23 | 1253 | 67 | MBh | 42 | 54 | 50 | 61 | 56.4 | 4.47
80 | 23 | 1253 | 67 | S/T | 0.729 | 54 | 50 | 65 | 52.2 | 3.84
80 | 23 | 1253 | 67 | ∆T | 22.6 | 54 | 50 | 68 | 49.1 | 3.37
80 | 23 | 1253 | 67 | LDB | 57.4 | 54 | 50 | 70 | 47 | 3.07
80 | 23 | 1253 | 67 | LWB | 56.3 | 54 | 50 | 72 | 44.9 | 2.77
80 | 23 | 1253 | 67 | kW | 1.88 | 54 | 50 | 75 | 41.8 | 2.33
84 | 23 | 1253 | 70 | MBh | 46.4 | 51 | 47 | 61 | 56.4 | 4.7
84 | 23 | 1253 | 70 | S/T | 0.711 | 51 | 47 | 65 | 52.2 | 4.05
84 | 23 | 1253 | 70 | ∆T | 24.4 | 51 | 47 | 68 | 49.1 | 3.57
84 | 23 | 1253 | 70 | LDB | 59.6 | 51 | 47 | 70 | 47 | 3.26
84 | 23 | 1253 | 70 | LWB | 58.9 | 51 | 47 | 72 | 44.9 | 2.95
84 | 23 | 1253 | 70 | kW | 2.11 | 51 | 47 | 75 | 41.8 | 2.49
86 | 23 | 1253 | 72 | MBh | 49.4 | 47 | 43 | 61 | 56.4 | 5.05
86 | 23 | 1253 | 72 | S/T | 0.668 | 47 | 43 | 65 | 52.2 | 4.36
86 | 23 | 1253 | 72 | ∆T | 24.4 | 47 | 43 | 68 | 49.1 | 3.85
86 | 23 | 1253 | 72 | LDB | 61.6 | 47 | 43 | 70 | 47 | 3.52
86 | 23 | 1253 | 72 | LWB | 60.7 | 47 | 43 | 72 | 44.9 | 3.2
86 | 23 | 1253 | 72 | kW | 2.26 | 47 | 43 | 75 | 41.8 | 2.72
90 | 23 | 1253 | 75 | MBh | 53.8 | 44 | 40 | 61 | 56.4 | 5.32
90 | 23 | 1253 | 75 | S/T | 0.632 | 44 | 40 | 65 | 52.2 | 4.61
90 | 23 | 1253 | 75 | ∆T | 25.1 | 44 | 40 | 68 | 49.1 | 4.08
90 | 23 | 1253 | 75 | LDB | 64.9 | 44 | 40 | 70 | 47 | 3.74
90 | 23 | 1253 | 75 | LWB | 63.4 | 44 | 40 | 72 | 44.9 | 3.4
90 | 23 | 1253 | 75 | kW | 2.5 | 44 | 40 | 75 | 41.8 | 2.91
68 | 30 | 1253 | 57 | MBh | 27.3 | 39 | 36 | 61 | 56.4 | 5.64
68 | 30 | 1253 | 57 | S/T | 0.832 | 39 | 36 | 65 | 52.2 | 4.97
68 | 30 | 1253 | 57 | ∆T | 16.8 | 39 | 36 | 68 | 49.1 | 4.42
68 | 30 | 1253 | 57 | LDB | 51.2 | 39 | 36 | 70 | 47 | 4.06
68 | 30 | 1253 | 57 | LWB | 48.7 | 39 | 36 | 72 | 44.9 | 3.7
68 | 30 | 1253 | 57 | kW | 1.21 | 39 | 36 | 75 | 41.8 | 3.17
72 | 30 | 1253 | 61 | MBh | 33.2 | 35 | 32 | 61 | 56 | 5.62
72 | 30 | 1253 | 61 | S/T | 0.795 | 35 | 32 | 65 | 52.2 | 5.37
72 | 30 | 1253 | 61 | ∆T | 19.5 | 35 | 32 | 68 | 49.1 | 4.78
72 | 30 | 1253 | 61 | LDB | 52.5 | 35 | 32 | 70 | 47 | 4.4
72 | 30 | 1253 | 61 | LWB | 51.6 | 35 | 32 | 72 | 44.9 | 4.02
72 | 30 | 1253 | 61 | kW | 1.49 | 35 | 32 | 75 | 41.8 | 3.47
77 | 30 | 1253 | 64 | MBh | 37.6 | 30 | 28 | 61 | 53.6 | 5.6
77 | 30 | 1253 | 64 | S/T | 0.769 | 30 | 28 | 65 | 52.2 | 5.63
77 | 30 | 1253 | 64 | ∆T | 21.4 | 30 | 28 | 68 | 49.1 | 5.19
77 | 30 | 1253 | 64 | LDB | 55.6 | 30 | 28 | 70 | 47 | 4.78
77 | 30 | 1253 | 64 | LWB | 53.9 | 30 | 28 | 72 | 44.9 | 4.38
77 | 30 | 1253 | 64 | kW | 1.71 | 30 | 28 | 75 | 41.8 | 3.8
80 | 30 | 1253 | 67 | MBh | 42 | 26 | 24 | 61 | 51.3 | 5.57
80 | 30 | 1253 | 67 | S/T | 0.729 | 26 | 24 | 65 | 51.3 | 5.61
80 | 30 | 1253 | 67 | ∆T | 22.6 | 26 | 24 | 68 | 49.1 | 5.63
80 | 30 | 1253 | 67 | LDB | 57.4 | 26 | 24 | 70 | 47 | 5.2
80 | 30 | 1253 | 67 | LWB | 56.3 | 26 | 24 | 72 | 44.9 | 4.78
80 | 30 | 1253 | 67 | kW | 1.94 | 26 | 24 | 75 | 41.8 | 4.16
84 | 30 | 1253 | 70 | MBh | 46.4 | 22 | 20 | 61 | 49 | 5.55
84 | 30 | 1253 | 70 | S/T | 0.711 | 22 | 20 | 65 | 49 | 5.58
84 | 30 | 1253 | 70 | ∆T | 24.4 | 22 | 20 | 68 | 49 | 5.61
84 | 30 | 1253 | 70 | LDB | 59.6 | 22 | 20 | 70 | 47 | 5.63
84 | 30 | 1253 | 70 | LWB | 58.9 | 22 | 20 | 72 | 44.9 | 5.23
84 | 30 | 1253 | 70 | kW | 2.18 | 22 | 20 | 75 | 41.8 | 4.56
86 | 30 | 1253 | 72 | MBh | 49.4 | 19 | 18 | 61 | 47.8 | 5.53
86 | 30 | 1253 | 72 | S/T | 0.668 | 19 | 18 | 65 | 47.8 | 5.57
86 | 30 | 1253 | 72 | ∆T | 24.4 | 19 | 18 | 68 | 47.8 | 5.6
86 | 30 | 1253 | 72 | LDB | 61.6 | 19 | 18 | 70 | 47 | 5.61
86 | 30 | 1253 | 72 | LWB | 60.7 | 19 | 18 | 72 | 44.9 | 5.47
86 | 30 | 1253 | 72 | kW | 2.34 | 19 | 18 | 75 | 41.8 | 4.78
90 | 30 | 1253 | 75 | MBh | 53.8 | 17 | 16 | 61 | 46.3 | 5.52
90 | 30 | 1253 | 75 | S/T | 0.632 | 17 | 16 | 65 | 46.3 | 5.55
90 | 30 | 1253 | 75 | ∆T | 25.1 | 17 | 16 | 68 | 46.3 | 5.58
90 | 30 | 1253 | 75 | LDB | 64.9 | 17 | 16 | 70 | 46.3 | 5.6
90 | 30 | 1253 | 75 | LWB | 63.4 | 17 | 16 | 72 | 44.9 | 5.62
90 | 30 | 1253 | 75 | kW | 2.58 | 17 | 16 | 75 | 41.8 | 5.07
68 | 40 | 1253 | 57 | MBh | 27.3 | 15 | 14 | 61 | 45.4 | 5.5
68 | 40 | 1253 | 57 | S/T | 0.832 | 15 | 14 | 65 | 45.4 | 5.54
68 | 40 | 1253 | 57 | ∆T | 16.8 | 15 | 14 | 68 | 45.4 | 5.57
68 | 40 | 1253 | 57 | LDB | 51.2 | 15 | 14 | 70 | 45.4 | 5.59
68 | 40 | 1253 | 57 | LWB | 48.7 | 15 | 14 | 72 | 44.9 | 5.61
68 | 40 | 1253 | 57 | kW | 1.26 | 15 | 14 | 75 | 41.8 | 5.26
72 | 40 | 1253 | 61 | MBh | 33.2 | 13 | 12 | 61 | 43.8 | 5.49
72 | 40 | 1253 | 61 | S/T | 0.795 | 13 | 12 | 65 | 43.8 | 5.53
72 | 40 | 1253 | 61 | ∆T | 19.5 | 13 | 12 | 68 | 43.8 | 5.55
72 | 40 | 1253 | 61 | LDB | 52.5 | 13 | 12 | 70 | 43.8 | 5.57
72 | 40 | 1253 | 61 | LWB | 51.6 | 13 | 12 | 72 | 43.8 | 5.59
72 | 40 | 1253 | 61 | kW | 1.56 | 13 | 12 | 75 | 41.8 | 5.52
77 | 40 | 1253 | 64 | MBh | 37.6 | 10 | 9 | 61 | 40.8 | 5.46
77 | 40 | 1253 | 64 | S/T | 0.769 | 10 | 9 | 65 | 40.8 | 5.5
77 | 40 | 1253 | 64 | ∆T | 21.4 | 10 | 9 | 68 | 40.8 | 5.53
77 | 40 | 1253 | 64 | LDB | 55.6 | 10 | 9 | 70 | 40.8 | 5.55
77 | 40 | 1253 | 64 | LWB | 53.9 | 10 | 9 | 72 | 40.8 | 5.57
77 | 40 | 1253 | 64 | kW | 1.79 | 10 | 9 | 75 | 40.8 | 5.6
80 | 40 | 1253 | 67 | MBh | 42 | 6 | 5 | 61 | 37.8 | 5.42
80 | 40 | 1253 | 67 | S/T | 0.729 | 6 | 5 | 65 | 37.8 | 5.47
80 | 40 | 1253 | 67 | ∆T | 22.6 | 6 | 5 | 68 | 37.8 | 5.5
80 | 40 | 1253 | 67 | LDB | 57.4 | 6 | 5 | 70 | 37.8 | 5.52
80 | 40 | 1253 | 67 | LWB | 56.3 | 6 | 5 | 72 | 37.8 | 5.54
80 | 40 | 1253 | 67 | kW | 2.03 | 6 | 5 | 75 | 37.8 | 5.57
84 | 40 | 1253 | 70 | MBh | 46.4 | -2 | -2 | 61 | 31.6 | 5.35
84 | 40 | 1253 | 70 | S/T | 0.711 | -2 | -2 | 65 | 31.6 | 5.39
84 | 40 | 1253 | 70 | ∆T | 24.4 | -2 | -2 | 68 | 31.6 | 5.43
84 | 40 | 1253 | 70 | LDB | 59.6 | -2 | -2 | 70 | 31.6 | 5.45
84 | 40 | 1253 | 70 | LWB | 58.9 | -2 | -2 | 72 | 31.6 | 5.48
84 | 40 | 1253 | 70 | kW | 2.28 | -2 | -2 | 75 | 31.6 | 5.51
86 | 40 | 1253 | 72 | MBh | 49.4 | -4 | -4 | 61 | 30.1 | 5.32
86 | 40 | 1253 | 72 | S/T | 0.668 | -4 | -4 | 65 | 30.1 | 5.37
86 | 40 | 1253 | 72 | ∆T | 24.4 | -4 | -4 | 68 | 30.1 | 5.41
86 | 40 | 1253 | 72 | LDB | 61.6 | -4 | -4 | 70 | 30.1 | 5.43
86 | 40 | 1253 | 72 | LWB | 60.7 | -4 | -4 | 72 | 30.1 | 5.46
86 | 40 | 1253 | 72 | kW | 2.45 | -4 | -4 | 75 | 30.1 | 5.49
90 | 40 | 1253 | 75 | MBh | 53.8
90 | 40 | 1253 | 75 | S/T | 0.632
90 | 40 | 1253 | 75 | ∆T | 25.1
90 | 40 | 1253 | 75 | LDB | 64.9
90 | 40 | 1253 | 75 | LWB | 63.4
90 | 40 | 1253 | 75 | kW | 2.71
68 | 50 | 1253 | 57 | MBh | 27.3
68 | 50 | 1253 | 57 | S/T | 0.832
68 | 50 | 1253 | 57 | ∆T | 16.8
68 | 50 | 1253 | 57 | LDB | 51.2
68 | 50 | 1253 | 57 | LWB | 48.7
68 | 50 | 1253 | 57 | kW | 1.32
72 | 50 | 1253 | 61 | MBh | 33.2
72 | 50 | 1253 | 61 | S/T | 0.795
72 | 50 | 1253 | 61 | ∆T | 19.5
72 | 50 | 1253 | 61 | LDB | 52.5
72 | 50 | 1253 | 61 | LWB | 51.6
72 | 50 | 1253 | 61 | kW | 1.64
77 | 50 | 1253 | 64 | MBh | 37.6
77 | 50 | 1253 | 64 | S/T | 0.769
77 | 50 | 1253 | 64 | ∆T | 21.4
77 | 50 | 1253 | 64 | LDB | 55.6
77 | 50 | 1253 | 64 | LWB | 53.9
77 | 50 | 1253 | 64 | kW | 1.88
80 | 50 | 1253 | 67 | MBh | 42
80 | 50 | 1253 | 67 | S/T | 0.729
80 | 50 | 1253 | 67 | ∆T | 22.6
80 | 50 | 1253 | 67 | LDB | 57.4
80 | 50 | 1253 | 67 | LWB | 56.3
80 | 50 | 1253 | 67 | kW | 2.14
84 | 50 | 1253 | 70 | MBh | 46.4
84 | 50 | 1253 | 70 | S/T | 0.711
84 | 50 | 1253 | 70 | ∆T | 24.4
84 | 50 | 1253 | 70 | LDB | 59.6
84 | 50 | 1253 | 70 | LWB | 58.9
84 | 50 | 1253 | 70 | kW | 2.4
86 | 50 | 1253 | 72 | MBh | 49.4
86 | 50 | 1253 | 72 | S/T | 0.668
86 | 50 | 1253 | 72 | ∆T | 24.4
86 | 50 | 1253 | 72 | LDB | 61.6
86 | 50 | 1253 | 72 | LWB | 60.7
86 | 50 | 1253 | 72 | kW | 2.58
90 | 50 | 1253 | 75 | MBh | 53.8
90 | 50 | 1253 | 75 | S/T | 0.632
90 | 50 | 1253 | 75 | ∆T | 25.1
90 | 50 | 1253 | 75 | LDB | 64.9
90 | 50 | 1253 | 75 | LWB | 63.4
90 | 50 | 1253 | 75 | kW | 2.85
68 | 54 | 1253 | 57 | MBh | 27.3
68 | 54 | 1253 | 57 | S/T | 0.832
68 | 54 | 1253 | 57 | ∆T | 16.8
68 | 54 | 1253 | 57 | LDB | 51.2
68 | 54 | 1253 | 57 | LWB | 48.7
68 | 54 | 1253 | 57 | kW | 1.35
72 | 54 | 1253 | 61 | MBh | 33.2
72 | 54 | 1253 | 61 | S/T | 0.795
72 | 54 | 1253 | 61 | ∆T | 19.5
72 | 54 | 1253 | 61 | LDB | 52.5
72 | 54 | 1253 | 61 | LWB | 51.6
72 | 54 | 1253 | 61 | kW | 1.67
77 | 54 | 1253 | 64 | MBh | 37.6
77 | 54 | 1253 | 64 | S/T | 0.769
77 | 54 | 1253 | 64 | ∆T | 21.4
77 | 54 | 1253 | 64 | LDB | 55.6
77 | 54 | 1253 | 64 | LWB | 53.9
77 | 54 | 1253 | 64 | kW | 1.92
80 | 54 | 1253 | 67 | MBh | 42
80 | 54 | 1253 | 67 | S/T | 0.729
80 | 54 | 1253 | 67 | ∆T | 22.6
80 | 54 | 1253 | 67 | LDB | 57.4
80 | 54 | 1253 | 67 | LWB | 56.3
80 | 54 | 1253 | 67 | kW | 2.18
84 | 54 | 1253 | 70 | MBh | 46.4
84 | 54 | 1253 | 70 | S/T | 0.711
84 | 54 | 1253 | 70 | ∆T | 24.4
84 | 54 | 1253 | 70 | LDB | 59.6
84 | 54 | 1253 | 70 | LWB | 58.9
84 | 54 | 1253 | 70 | kW | 2.45
86 | 54 | 1253 | 72 | MBh | 49.4
86 | 54 | 1253 | 72 | S/T | 0.668
86 | 54 | 1253 | 72 | ∆T | 24.4
86 | 54 | 1253 | 72 | LDB | 61.6
86 | 54 | 1253 | 72 | LWB | 60.7
86 | 54 | 1253 | 72 | kW | 2.63
90 | 54 | 1253 | 75 | MBh | 53.8
90 | 54 | 1253 | 75 | S/T | 0.632
90 | 54 | 1253 | 75 | ∆T | 25.1
90 | 54 | 1253 | 75 | LDB | 64.9
90 | 54 | 1253 | 75 | LWB | 63.4
90 | 54 | 1253 | 75 | kW | 2.91
68 | 58 | 1253 | 57 | MBh | 27.3
68 | 58 | 1253 | 57 | S/T | 0.832
68 | 58 | 1253 | 57 | ∆T | 16.8
68 | 58 | 1253 | 57 | LDB | 51.2
68 | 58 | 1253 | 57 | LWB | 48.7
68 | 58 | 1253 | 57 | kW | 1.37
72 | 58 | 1253 | 61 | MBh | 33.2
72 | 58 | 1253 | 61 | S/T | 0.795
72 | 58 | 1253 | 61 | ∆T | 19.5
72 | 58 | 1253 | 61 | LDB | 52.5
72 | 58 | 1253 | 61 | LWB | 51.6
72 | 58 | 1253 | 61 | kW | 1.7
77 | 58 | 1253 | 64 | MBh | 37.6
77 | 58 | 1253 | 64 | S/T | 0.769
77 | 58 | 1253 | 64 | ∆T | 21.4
77 | 58 | 1253 | 64 | LDB | 55.6
77 | 58 | 1253 | 64 | LWB | 53.9
77 | 58 | 1253 | 64 | kW | 1.96
80 | 58 | 1253 | 67 | MBh | 42
80 | 58 | 1253 | 67 | S/T | 0.729
80 | 58 | 1253 | 67 | ∆T | 22.6
80 | 58 | 1253 | 67 | LDB | 57.4
80 | 58 | 1253 | 67 | LWB | 56.3
80 | 58 | 1253 | 67 | kW | 2.23
84 | 58 | 1253 | 70 | MBh | 46.4
84 | 58 | 1253 | 70 | S/T | 0.711
84 | 58 | 1253 | 70 | ∆T | 24.4
84 | 58 | 1253 | 70 | LDB | 59.6
84 | 58 | 1253 | 70 | LWB | 58.9
84 | 58 | 1253 | 70 | kW | 2.51
86 | 58 | 1253 | 72 | MBh | 49.4
86 | 58 | 1253 | 72 | S/T | 0.668
86 | 58 | 1253 | 72 | ∆T | 24.4
86 | 58 | 1253 | 72 | LDB | 61.6
86 | 58 | 1253 | 72 | LWB | 60.7
86 | 58 | 1253 | 72 | kW | 2.69
90 | 58 | 1253 | 75 | MBh | 53.3
90 | 58 | 1253 | 75 | S/T | 0.632
90 | 58 | 1253 | 75 | ∆T | 24.9
90 | 58 | 1253 | 75 | LDB | 65.1
90 | 58 | 1253 | 75 | LWB | 63.6
90 | 58 | 1253 | 75 | kW | 2.92
68 | 62 | 1253 | 57 | MBh | 27.3
68 | 62 | 1253 | 57 | S/T | 0.832
68 | 62 | 1253 | 57 | ∆T | 16.8
68 | 62 | 1253 | 57 | LDB | 51.2
68 | 62 | 1253 | 57 | LWB | 48.7
68 | 62 | 1253 | 57 | kW | 1.4
72 | 62 | 1253 | 61 | MBh | 33.2
72 | 62 | 1253 | 61 | S/T | 0.795
72 | 62 | 1253 | 61 | ∆T | 19.5
72 | 62 | 1253 | 61 | LDB | 52.5
72 | 62 | 1253 | 61 | LWB | 51.6
72 | 62 | 1253 | 61 | kW | 1.74
77 | 62 | 1253 | 64 | MBh | 37.6
77 | 62 | 1253 | 64 | S/T | 0.769
77 | 62 | 1253 | 64 | ∆T | 21.4
77 | 62 | 1253 | 64 | LDB | 55.6
77 | 62 | 1253 | 64 | LWB | 53.9
77 | 62 | 1253 | 64 | kW | 2
80 | 62 | 1253 | 67 | MBh | 42
80 | 62 | 1253 | 67 | S/T | 0.729
80 | 62 | 1253 | 67 | ∆T | 22.6
80 | 62 | 1253 | 67 | LDB | 57.4
80 | 62 | 1253 | 67 | LWB | 56.3
80 | 62 | 1253 | 67 | kW | 2.28
84 | 62 | 1253 | 70 | MBh | 46.4
84 | 62 | 1253 | 70 | S/T | 0.711
84 | 62 | 1253 | 70 | ∆T | 24.4
84 | 62 | 1253 | 70 | LDB | 59.6
84 | 62 | 1253 | 70 | LWB | 58.9
84 | 62 | 1253 | 70 | kW | 2.56
86 | 62 | 1253 | 72 | MBh | 49.4
86 | 62 | 1253 | 72 | S/T | 0.668
86 | 62 | 1253 | 72 | ∆T | 24.4
86 | 62 | 1253 | 72 | LDB | 61.6
86 | 62 | 1253 | 72 | LWB | 60.7
86 | 62 | 1253 | 72 | kW | 2.75
90 | 62 | 1253 | 75 | MBh | 52.5
90 | 62 | 1253 | 75 | S/T | 0.632
90 | 62 | 1253 | 75 | ∆T | 24.5
90 | 62 | 1253 | 75 | LDB | 65.5
90 | 62 | 1253 | 75 | LWB | 63.8
90 | 62 | 1253 | 75 | kW | 2.98
68 | 66 | 1253 | 57 | MBh | 27.3
68 | 66 | 1253 | 57 | S/T | 0.832
68 | 66 | 1253 | 57 | ∆T | 16.8
68 | 66 | 1253 | 57 | LDB | 51.2
68 | 66 | 1253 | 57 | LWB | 48.7
68 | 66 | 1253 | 57 | kW | 1.43
72 | 66 | 1253 | 61 | MBh | 33.2
72 | 66 | 1253 | 61 | S/T | 0.795
72 | 66 | 1253 | 61 | ∆T | 19.5
72 | 66 | 1253 | 61 | LDB | 52.5
72 | 66 | 1253 | 61 | LWB | 51.6
72 | 66 | 1253 | 61 | kW | 1.78
77 | 66 | 1253 | 64 | MBh | 37.6
77 | 66 | 1253 | 64 | S/T | 0.769
77 | 66 | 1253 | 64 | ∆T | 21.4
77 | 66 | 1253 | 64 | LDB | 55.6
77 | 66 | 1253 | 64 | LWB | 53.9
77 | 66 | 1253 | 64 | kW | 2.05
80 | 66 | 1253 | 67 | MBh | 42
80 | 66 | 1253 | 67 | S/T | 0.729
80 | 66 | 1253 | 67 | ∆T | 22.6
80 | 66 | 1253 | 67 | LDB | 57.4
80 | 66 | 1253 | 67 | LWB | 56.3
80 | 66 | 1253 | 67 | kW | 2.33
84 | 66 | 1253 | 70 | MBh | 46.4
84 | 66 | 1253 | 70 | S/T | 0.711
84 | 66 | 1253 | 70 | ∆T | 24.4
84 | 66 | 1253 | 70 | LDB | 59.6
84 | 66 | 1253 | 70 | LWB | 58.9
84 | 66 | 1253 | 70 | kW | 2.7
86 | 66 | 1253 | 72 | MBh | 49.4
86 | 66 | 1253 | 72 | S/T | 0.668
86 | 66 | 1253 | 72 | ∆T | 24.4
86 | 66 | 1253 | 72 | LDB | 61.6
86 | 66 | 1253 | 72 | LWB | 60.7
86 | 66 | 1253 | 72 | kW | 2.97
90 | 66 | 1253 | 75 | MBh | 51.7
90 | 66 | 1253 | 75 | S/T | 0.632
90 | 66 | 1253 | 75 | ∆T | 24.2
90 | 66 | 1253 | 75 | LDB | 65.8
90 | 66 | 1253 | 75 | LWB | 63.9
90 | 66 | 1253 | 75 | kW | 3.15
68 | 70 | 1253 | 57 | MBh | 27.3
68 | 70 | 1253 | 57 | S/T | 0.832
68 | 70 | 1253 | 57 | ∆T | 16.8
68 | 70 | 1253 | 57 | LDB | 51.2
68 | 70 | 1253 | 57 | LWB | 48.7
68 | 70 | 1253 | 57 | kW | 1.46
72 | 70 | 1253 | 61 | MBh | 33.2
72 | 70 | 1253 | 61 | S/T | 0.795
72 | 70 | 1253 | 61 | ∆T | 19.5
72 | 70 | 1253 | 61 | LDB | 52.5
72 | 70 | 1253 | 61 | LWB | 51.6
72 | 70 | 1253 | 61 | kW | 1.82
77 | 70 | 1253 | 64 | MBh | 37.6
77 | 70 | 1253 | 64 | S/T | 0.769
77 | 70 | 1253 | 64 | ∆T | 21.4
77 | 70 | 1253 | 64 | LDB | 55.6
77 | 70 | 1253 | 64 | LWB | 53.9
77 | 70 | 1253 | 64 | kW | 2.15
80 | 70 | 1253 | 67 | MBh | 42
80 | 70 | 1253 | 67 | S/T | 0.729
80 | 70 | 1253 | 67 | ∆T | 22.6
80 | 70 | 1253 | 67 | LDB | 57.4
80 | 70 | 1253 | 67 | LWB | 56.3
80 | 70 | 1253 | 67 | kW | 2.52
84 | 70 | 1253 | 70 | MBh | 46.4
84 | 70 | 1253 | 70 | S/T | 0.711
84 | 70 | 1253 | 70 | ∆T | 24.4
84 | 70 | 1253 | 70 | LDB | 59.6
84 | 70 | 1253 | 70 | LWB | 58.9
84 | 70 | 1253 | 70 | kW | 2.93
86 | 70 | 1253 | 72 | MBh | 49.4
86 | 70 | 1253 | 72 | S/T | 0.668
86 | 70 | 1253 | 72 | ∆T | 24.4
86 | 70 | 1253 | 72 | LDB | 61.6
86 | 70 | 1253 | 72 | LWB | 60.7
86 | 70 | 1253 | 72 | kW | 3.21
90 | 70 | 1253 | 75 | MBh | 50.9
90 | 70 | 1253 | 75 | S/T | 0.633
90 | 70 | 1253 | 75 | ∆T | 23.8
90 | 70 | 1253 | 75 | LDB | 66.2
90 | 70 | 1253 | 75 | LWB | 64.1
90 | 70 | 1253 | 75 | kW | 3.31
68 | 72 | 1253 | 57 | MBh | 27.3
68 | 72 | 1253 | 57 | S/T | 0.832
68 | 72 | 1253 | 57 | ∆T | 16.8
68 | 72 | 1253 | 57 | LDB | 51.2
68 | 72 | 1253 | 57 | LWB | 48.7
68 | 72 | 1253 | 57 | kW | 1.48
72 | 72 | 1253 | 61 | MBh | 33.2
72 | 72 | 1253 | 61 | S/T | 0.795
72 | 72 | 1253 | 61 | ∆T | 19.5
72 | 72 | 1253 | 61 | LDB | 52.5
72 | 72 | 1253 | 61 | LWB | 51.6
72 | 72 | 1253 | 61 | kW | 1.88
77 | 72 | 1253 | 64 | MBh | 37.6
77 | 72 | 1253 | 64 | S/T | 0.769
77 | 72 | 1253 | 64 | ∆T | 21.4
77 | 72 | 1253 | 64 | LDB | 55.6
77 | 72 | 1253 | 64 | LWB | 53.9
77 | 72 | 1253 | 64 | kW | 2.23
80 | 72 | 1253 | 67 | MBh | 42
80 | 72 | 1253 | 67 | S/T | 0.729
80 | 72 | 1253 | 67 | ∆T | 22.6
80 | 72 | 1253 | 67 | LDB | 57.4
80 | 72 | 1253 | 67 | LWB | 56.3
80 | 72 | 1253 | 67 | kW | 2.62
84 | 72 | 1253 | 70 | MBh | 46.4
84 | 72 | 1253 | 70 | S/T | 0.711
84 | 72 | 1253 | 70 | ∆T | 24.4
84 | 72 | 1253 | 70 | LDB | 59.6
84 | 72 | 1253 | 70 | LWB | 58.9
84 | 72 | 1253 | 70 | kW | 3.04
86 | 72 | 1253 | 72 | MBh | 49.4
86 | 72 | 1253 | 72 | S/T | 0.668
86 | 72 | 1253 | 72 | ∆T | 24.4
86 | 72 | 1253 | 72 | LDB | 61.6
86 | 72 | 1253 | 72 | LWB | 60.7
86 | 72 | 1253 | 72 | kW | 3.34
90 | 72 | 1253 | 75 | MBh | 50.5
90 | 72 | 1253 | 75 | S/T | 0.632
90 | 72 | 1253 | 75 | ∆T | 23.6
90 | 72 | 1253 | 75 | LDB | 66.4
90 | 72 | 1253 | 75 | LWB | 64.2
90 | 72 | 1253 | 75 | kW | 3.4
68 | 75 | 1253 | 57 | MBh | 27.3
68 | 75 | 1253 | 57 | S/T | 0.832
68 | 75 | 1253 | 57 | ∆T | 16.8
68 | 75 | 1253 | 57 | LDB | 51.2
68 | 75 | 1253 | 57 | LWB | 48.7
68 | 75 | 1253 | 57 | kW | 1.53
72 | 75 | 1253 | 61 | MBh | 33.2
72 | 75 | 1253 | 61 | S/T | 0.795
72 | 75 | 1253 | 61 | ∆T | 19.5
72 | 75 | 1253 | 61 | LDB | 52.5
72 | 75 | 1253 | 61 | LWB | 51.6
72 | 75 | 1253 | 61 | kW | 1.98
77 | 75 | 1253 | 64 | MBh | 37.6
77 | 75 | 1253 | 64 | S/T | 0.769
77 | 75 | 1253 | 64 | ∆T | 21.4
77 | 75 | 1253 | 64 | LDB | 55.6
77 | 75 | 1253 | 64 | LWB | 53.9
77 | 75 | 1253 | 64 | kW | 2.36
80 | 75 | 1253 | 67 | MBh | 42
80 | 75 | 1253 | 67 | S/T | 0.729
80 | 75 | 1253 | 67 | ∆T | 22.6
80 | 75 | 1253 | 67 | LDB | 57.4
80 | 75 | 1253 | 67 | LWB | 56.3
80 | 75 | 1253 | 67 | kW | 2.78
84 | 75 | 1253 | 70 | MBh | 46.4
84 | 75 | 1253 | 70 | S/T | 0.711
84 | 75 | 1253 | 70 | ∆T | 24.4
84 | 75 | 1253 | 70 | LDB | 59.6
84 | 75 | 1253 | 70 | LWB | 58.9
84 | 75 | 1253 | 70 | kW | 3.22
86 | 75 | 1253 | 72 | MBh | 49.1
86 | 75 | 1253 | 72 | S/T | 0.668
86 | 75 | 1253 | 72 | ∆T | 24.2
86 | 75 | 1253 | 72 | LDB | 61.8
86 | 75 | 1253 | 72 | LWB | 60.7
86 | 75 | 1253 | 72 | kW | 3.5
90 | 75 | 1253 | 75 | MBh | 49.9
90 | 75 | 1253 | 75 | S/T | 0.631
90 | 75 | 1253 | 75 | ∆T | 23.3
90 | 75 | 1253 | 75 | LDB | 66.7
90 | 75 | 1253 | 75 | LWB | 64.4
90 | 75 | 1253 | 75 | kW | 3.52
68 | 79 | 1253 | 57 | MBh | 27.3
68 | 79 | 1253 | 57 | S/T | 0.832
68 | 79 | 1253 | 57 | ∆T | 16.8
68 | 79 | 1253 | 57 | LDB | 51.2
68 | 79 | 1253 | 57 | LWB | 48.7
68 | 79 | 1253 | 57 | kW | 1.64
72 | 79 | 1253 | 61 | MBh | 33.2
72 | 79 | 1253 | 61 | S/T | 0.795
72 | 79 | 1253 | 61 | ∆T | 19.5
72 | 79 | 1253 | 61 | LDB | 52.5
72 | 79 | 1253 | 61 | LWB | 51.6
72 | 79 | 1253 | 61 | kW | 2.13
77 | 79 | 1253 | 64 | MBh | 37.6
77 | 79 | 1253 | 64 | S/T | 0.769
77 | 79 | 1253 | 64 | ∆T | 21.4
77 | 79 | 1253 | 64 | LDB | 55.6
77 | 79 | 1253 | 64 | LWB | 53.9
77 | 79 | 1253 | 64 | kW | 2.54
80 | 79 | 1253 | 67 | MBh | 42
80 | 79 | 1253 | 67 | S/T | 0.729
80 | 79 | 1253 | 67 | ∆T | 22.6
80 | 79 | 1253 | 67 | LDB | 57.4
80 | 79 | 1253 | 67 | LWB | 56.3
80 | 79 | 1253 | 67 | kW | 2.99
84 | 79 | 1253 | 70 | MBh | 46.4
84 | 79 | 1253 | 70 | S/T | 0.711
84 | 79 | 1253 | 70 | ∆T | 24.4
84 | 79 | 1253 | 70 | LDB | 59.6
84 | 79 | 1253 | 70 | LWB | 58.9
84 | 79 | 1253 | 70 | kW | 3.48
86 | 79 | 1253 | 72 | MBh | 48.3
86 | 79 | 1253 | 72 | S/T | 0.669
86 | 79 | 1253 | 72 | ∆T | 23.9
86 | 79 | 1253 | 72 | LDB | 62.1
86 | 79 | 1253 | 72 | LWB | 61
86 | 79 | 1253 | 72 | kW | 3.67
90 | 79 | 1253 | 75 | MBh | 49.2
90 | 79 | 1253 | 75 | S/T | 0.632
90 | 79 | 1253 | 75 | ∆T | 23
90 | 79 | 1253 | 75 | LDB | 67
90 | 79 | 1253 | 75 | LWB | 64.5
90 | 79 | 1253 | 75 | kW | 3.69
68 | 83 | 1253 | 57 | MBh | 27.3
68 | 83 | 1253 | 57 | S/T | 0.832
68 | 83 | 1253 | 57 | ∆T | 16.8
68 | 83 | 1253 | 57 | LDB | 51.2
68 | 83 | 1253 | 57 | LWB | 48.7
68 | 83 | 1253 | 57 | kW | 1.76
72 | 83 | 1253 | 61 | MBh | 33.2
72 | 83 | 1253 | 61 | S/T | 0.795
72 | 83 | 1253 | 61 | ∆T | 19.5
72 | 83 | 1253 | 61 | LDB | 52.5
72 | 83 | 1253 | 61 | LWB | 51.6
72 | 83 | 1253 | 61 | kW | 2.29
77 | 83 | 1253 | 64 | MBh | 37.6
77 | 83 | 1253 | 64 | S/T | 0.769
77 | 83 | 1253 | 64 | ∆T | 21.4
77 | 83 | 1253 | 64 | LDB | 55.6
77 | 83 | 1253 | 64 | LWB | 53.9
77 | 83 | 1253 | 64 | kW | 2.74
80 | 83 | 1253 | 67 | MBh | 42
80 | 83 | 1253 | 67 | S/T | 0.729
80 | 83 | 1253 | 67 | ∆T | 22.6
80 | 83 | 1253 | 67 | LDB | 57.4
80 | 83 | 1253 | 67 | LWB | 56.3
80 | 83 | 1253 | 67 | kW | 3.22
84 | 83 | 1253 | 70 | MBh | 46.4
84 | 83 | 1253 | 70 | S/T | 0.711
84 | 83 | 1253 | 70 | ∆T | 24.4
84 | 83 | 1253 | 70 | LDB | 59.6
84 | 83 | 1253 | 70 | LWB | 58.9
84 | 83 | 1253 | 70 | kW | 3.75
86 | 83 | 1253 | 72 | MBh | 47.5
86 | 83 | 1253 | 72 | S/T | 0.669
86 | 83 | 1253 | 72 | ∆T | 23.5
86 | 83 | 1253 | 72 | LDB | 62.5
86 | 83 | 1253 | 72 | LWB | 61.2
86 | 83 | 1253 | 72 | kW | 3.84
90 | 83 | 1253 | 75 | MBh | 48.4
90 | 83 | 1253 | 75 | S/T | 0.632
90 | 83 | 1253 | 75 | ∆T | 22.6
90 | 83 | 1253 | 75 | LDB | 67.4
90 | 83 | 1253 | 75 | LWB | 64.7
90 | 83 | 1253 | 75 | kW | 3.86
68 | 87 | 1253 | 57 | MBh | 27.3
68 | 87 | 1253 | 57 | S/T | 0.832
68 | 87 | 1253 | 57 | ∆T | 16.8
68 | 87 | 1253 | 57 | LDB | 51.2
68 | 87 | 1253 | 57 | LWB | 48.7
68 | 87 | 1253 | 57 | kW | 1.89
72 | 87 | 1253 | 61 | MBh | 33.2
72 | 87 | 1253 | 61 | S/T | 0.795
72 | 87 | 1253 | 61 | ∆T | 19.5
72 | 87 | 1253 | 61 | LDB | 52.5
72 | 87 | 1253 | 61 | LWB | 51.6
72 | 87 | 1253 | 61 | kW | 2.46
77 | 87 | 1253 | 64 | MBh | 37.6
77 | 87 | 1253 | 64 | S/T | 0.769
77 | 87 | 1253 | 64 | ∆T | 21.4
77 | 87 | 1253 | 64 | LDB | 55.6
77 | 87 | 1253 | 64 | LWB | 53.9
77 | 87 | 1253 | 64 | kW | 2.94
80 | 87 | 1253 | 67 | MBh | 42
80 | 87 | 1253 | 67 | S/T | 0.729
80 | 87 | 1253 | 67 | ∆T | 22.6
80 | 87 | 1253 | 67 | LDB | 57.4
80 | 87 | 1253 | 67 | LWB | 56.3
80 | 87 | 1253 | 67 | kW | 3.46
84 | 87 | 1253 | 70 | MBh | 46.1
84 | 87 | 1253 | 70 | S/T | 0.711
84 | 87 | 1253 | 70 | ∆T | 24.2
84 | 87 | 1253 | 70 | LDB | 59.8
84 | 87 | 1253 | 70 | LWB | 59
84 | 87 | 1253 | 70 | kW | 3.99
86 | 87 | 1253 | 72 | MBh | 46.7
86 | 87 | 1253 | 72 | S/T | 0.67
86 | 87 | 1253 | 72 | ∆T | 23.1
86 | 87 | 1253 | 72 | LDB | 62.9
86 | 87 | 1253 | 72 | LWB | 61.4
86 | 87 | 1253 | 72 | kW | 4.01
90 | 87 | 1253 | 75 | MBh | 47.6
90 | 87 | 1253 | 75 | S/T | 0.632
90 | 87 | 1253 | 75 | ∆T | 22.2
90 | 87 | 1253 | 75 | LDB | 67.8
90 | 87 | 1253 | 75 | LWB | 64.9
90 | 87 | 1253 | 75 | kW | 4.03
68 | 91 | 1253 | 57 | MBh | 27.3
68 | 91 | 1253 | 57 | S/T | 0.832
68 | 91 | 1253 | 57 | ∆T | 16.8
68 | 91 | 1253 | 57 | LDB | 51.2
68 | 91 | 1253 | 57 | LWB | 48.7
68 | 91 | 1253 | 57 | kW | 2.02
72 | 91 | 1253 | 61 | MBh | 33.2
72 | 91 | 1253 | 61 | S/T | 0.795
72 | 91 | 1253 | 61 | ∆T | 19.5
72 | 91 | 1253 | 61 | LDB | 52.5
72 | 91 | 1253 | 61 | LWB | 51.6
72 | 91 | 1253 | 61 | kW | 2.64
77 | 91 | 1253 | 64 | MBh | 37.6
77 | 91 | 1253 | 64 | S/T | 0.769
77 | 91 | 1253 | 64 | ∆T | 21.4
77 | 91 | 1253 | 64 | LDB | 55.6
77 | 91 | 1253 | 64 | LWB | 53.9
77 | 91 | 1253 | 64 | kW | 3.16
80 | 91 | 1253 | 67 | MBh | 42
80 | 91 | 1253 | 67 | S/T | 0.729
80 | 91 | 1253 | 67 | ∆T | 22.6
80 | 91 | 1253 | 67 | LDB | 57.4
80 | 91 | 1253 | 67 | LWB | 56.3
80 | 91 | 1253 | 67 | kW | 3.72
84 | 91 | 1253 | 70 | MBh | 45.3
84 | 91 | 1253 | 70 | S/T | 0.711
84 | 91 | 1253 | 70 | ∆T | 23.8
84 | 91 | 1253 | 70 | LDB | 60.2
84 | 91 | 1253 | 70 | LWB | 59.2
84 | 91 | 1253 | 70 | kW | 4.16
86 | 91 | 1253 | 72 | MBh | 45.9
86 | 91 | 1253 | 72 | S/T | 0.669
86 | 91 | 1253 | 72 | ∆T | 22.7
86 | 91 | 1253 | 72 | LDB | 63.3
86 | 91 | 1253 | 72 | LWB | 61.6
86 | 91 | 1253 | 72 | kW | 4.17
90 | 91 | 1253 | 75 | MBh | 46.8
90 | 91 | 1253 | 75 | S/T | 0.632
90 | 91 | 1253 | 75 | ∆T | 21.9
90 | 91 | 1253 | 75 | LDB | 68.1
90 | 91 | 1253 | 75 | LWB | 65.1
90 | 91 | 1253 | 75 | kW | 4.2
68 | 93 | 1253 | 57 | MBh | 27.3
68 | 93 | 1253 | 57 | S/T | 0.832
68 | 93 | 1253 | 57 | ∆T | 16.8
68 | 93 | 1253 | 57 | LDB | 51.2
68 | 93 | 1253 | 57 | LWB | 48.7
68 | 93 | 1253 | 57 | kW | 2.09
72 | 93 | 1253 | 61 | MBh | 33.2
72 | 93 | 1253 | 61 | S/T | 0.795
72 | 93 | 1253 | 61 | ∆T | 19.5
72 | 93 | 1253 | 61 | LDB | 52.5
72 | 93 | 1253 | 61 | LWB | 51.6
72 | 93 | 1253 | 61 | kW | 2.73
77 | 93 | 1253 | 64 | MBh | 37.6
77 | 93 | 1253 | 64 | S/T | 0.769
77 | 93 | 1253 | 64 | ∆T | 21.4
77 | 93 | 1253 | 64 | LDB | 55.6
77 | 93 | 1253 | 64 | LWB | 53.9
77 | 93 | 1253 | 64 | kW | 3.27
80 | 93 | 1253 | 67 | MBh | 42
80 | 93 | 1253 | 67 | S/T | 0.729
80 | 93 | 1253 | 67 | ∆T | 22.6
80 | 93 | 1253 | 67 | LDB | 57.4
80 | 93 | 1253 | 67 | LWB | 56.3
80 | 93 | 1253 | 67 | kW | 3.86
84 | 93 | 1253 | 70 | MBh | 45
84 | 93 | 1253 | 70 | S/T | 0.709
84 | 93 | 1253 | 70 | ∆T | 23.6
84 | 93 | 1253 | 70 | LDB | 60.4
84 | 93 | 1253 | 70 | LWB | 59.3
84 | 93 | 1253 | 70 | kW | 4.24
86 | 93 | 1253 | 72 | MBh | 45.5
86 | 93 | 1253 | 72 | S/T | 0.67
86 | 93 | 1253 | 72 | ∆T | 22.5
86 | 93 | 1253 | 72 | LDB | 63.5
86 | 93 | 1253 | 72 | LWB | 61.7
86 | 93 | 1253 | 72 | kW | 4.26
90 | 93 | 1253 | 75 | MBh | 46.4
90 | 93 | 1253 | 75 | S/T | 0.631
90 | 93 | 1253 | 75 | ∆T | 21.7
90 | 93 | 1253 | 75 | LDB | 68.3
90 | 93 | 1253 | 75 | LWB | 65.2
90 | 93 | 1253 | 75 | kW | 4.29
68 | 95 | 1253 | 57 | MBh | 27.3
68 | 95 | 1253 | 57 | S/T | 0.832
68 | 95 | 1253 | 57 | ∆T | 16.8
68 | 95 | 1253 | 57 | LDB | 51.2
68 | 95 | 1253 | 57 | LWB | 48.7
68 | 95 | 1253 | 57 | kW | 2.16
72 | 95 | 1253 | 61 | MBh | 33.2
72 | 95 | 1253 | 61 | S/T | 0.795
72 | 95 | 1253 | 61 | ∆T | 19.5
72 | 95 | 1253 | 61 | LDB | 52.5
72 | 95 | 1253 | 61 | LWB | 51.6
72 | 95 | 1253 | 61 | kW | 2.83
77 | 95 | 1253 | 64 | MBh | 37.6
77 | 95 | 1253 | 64 | S/T | 0.769
77 | 95 | 1253 | 64 | ∆T | 21.4
77 | 95 | 1253 | 64 | LDB | 55.6
77 | 95 | 1253 | 64 | LWB | 53.9
77 | 95 | 1253 | 64 | kW | 3.39
80 | 95 | 1253 | 67 | MBh | 42
80 | 95 | 1253 | 67 | S/T | 0.729
80 | 95 | 1253 | 67 | ∆T | 22.6
80 | 95 | 1253 | 67 | LDB | 57.4
80 | 95 | 1253 | 67 | LWB | 56.3
80 | 95 | 1253 | 67 | kW | 4
84 | 95 | 1253 | 70 | MBh | 44.6
84 | 95 | 1253 | 70 | S/T | 0.709
84 | 95 | 1253 | 70 | ∆T | 23.4
84 | 95 | 1253 | 70 | LDB | 60.6
84 | 95 | 1253 | 70 | LWB | 59.4
84 | 95 | 1253 | 70 | kW | 4.32
86 | 95 | 1253 | 72 | MBh | 45.1
86 | 95 | 1253 | 72 | S/T | 0.67
86 | 95 | 1253 | 72 | ∆T | 22.3
86 | 95 | 1253 | 72 | LDB | 63.7
86 | 95 | 1253 | 72 | LWB | 61.8
86 | 95 | 1253 | 72 | kW | 4.34
90 | 95 | 1253 | 75 | MBh | 46
90 | 95 | 1253 | 75 | S/T | 0.633
90 | 95 | 1253 | 75 | ∆T | 21.5
90 | 95 | 1253 | 75 | LDB | 68.5
90 | 95 | 1253 | 75 | LWB | 65.3
90 | 95 | 1253 | 75 | kW | 4.37
68 | 99 | 1253 | 57 | MBh | 27.3
68 | 99 | 1253 | 57 | S/T | 0.832
68 | 99 | 1253 | 57 | ∆T | 16.8
68 | 99 | 1253 | 57 | LDB | 51.2
68 | 99 | 1253 | 57 | LWB | 48.7
68 | 99 | 1253 | 57 | kW | 2.31
72 | 99 | 1253 | 61 | MBh | 33.2
72 | 99 | 1253 | 61 | S/T | 0.795
72 | 99 | 1253 | 61 | ∆T | 19.5
72 | 99 | 1253 | 61 | LDB | 52.5
72 | 99 | 1253 | 61 | LWB | 51.6
72 | 99 | 1253 | 61 | kW | 3.03
77 | 99 | 1253 | 64 | MBh | 37.6
77 | 99 | 1253 | 64 | S/T | 0.769
77 | 99 | 1253 | 64 | ∆T | 21.4
77 | 99 | 1253 | 64 | LDB | 55.6
77 | 99 | 1253 | 64 | LWB | 53.9
77 | 99 | 1253 | 64 | kW | 3.63
80 | 99 | 1253 | 67 | MBh | 42
80 | 99 | 1253 | 67 | S/T | 0.729
80 | 99 | 1253 | 67 | ∆T | 22.6
80 | 99 | 1253 | 67 | LDB | 57.4
80 | 99 | 1253 | 67 | LWB | 56.3
80 | 99 | 1253 | 67 | kW | 4.29
84 | 99 | 1253 | 70 | MBh | 43.8
84 | 99 | 1253 | 70 | S/T | 0.71
84 | 99 | 1253 | 70 | ∆T | 23
84 | 99 | 1253 | 70 | LDB | 61
84 | 99 | 1253 | 70 | LWB | 59.6
84 | 99 | 1253 | 70 | kW | 4.49
86 | 99 | 1253 | 72 | MBh | 44.3
86 | 99 | 1253 | 72 | S/T | 0.67
86 | 99 | 1253 | 72 | ∆T | 21.9
86 | 99 | 1253 | 72 | LDB | 64.1
86 | 99 | 1253 | 72 | LWB | 62
86 | 99 | 1253 | 72 | kW | 4.52
90 | 99 | 1253 | 75 | MBh | 45.2
90 | 99 | 1253 | 75 | S/T | 0.633
90 | 99 | 1253 | 75 | ∆T | 21.1
90 | 99 | 1253 | 75 | LDB | 68.9
90 | 99 | 1253 | 75 | LWB | 65.5
90 | 99 | 1253 | 75 | kW | 4.55
68 | 103 | 1253 | 57 | MBh | 27.3
68 | 103 | 1253 | 57 | S/T | 0.832
68 | 103 | 1253 | 57 | ∆T | 16.8
68 | 103 | 1253 | 57 | LDB | 51.2
68 | 103 | 1253 | 57 | LWB | 48.7
68 | 103 | 1253 | 57 | kW | 2.47
72 | 103 | 1253 | 61 | MBh | 33.2
72 | 103 | 1253 | 61 | S/T | 0.795
72 | 103 | 1253 | 61 | ∆T | 19.5
72 | 103 | 1253 | 61 | LDB | 52.5
72 | 103 | 1253 | 61 | LWB | 51.6
72 | 103 | 1253 | 61 | kW | 3.24
77 | 103 | 1253 | 64 | MBh | 37.6
77 | 103 | 1253 | 64 | S/T | 0.769
77 | 103 | 1253 | 64 | ∆T | 21.4
77 | 103 | 1253 | 64 | LDB | 55.6
77 | 103 | 1253 | 64 | LWB | 53.9
77 | 103 | 1253 | 64 | kW | 3.9
80 | 103 | 1253 | 67 | MBh | 42
80 | 103 | 1253 | 67 | S/T | 0.729
80 | 103 | 1253 | 67 | ∆T | 22.6
80 | 103 | 1253 | 67 | LDB | 57.4
80 | 103 | 1253 | 67 | LWB | 56.3
80 | 103 | 1253 | 67 | kW | 4.61
84 | 103 | 1253 | 70 | MBh | 43
84 | 103 | 1253 | 70 | S/T | 0.709
84 | 103 | 1253 | 70 | ∆T | 22.5
84 | 103 | 1253 | 70 | LDB | 61.5
84 | 103 | 1253 | 70 | LWB | 59.8
84 | 103 | 1253 | 70 | kW | 4.67
86 | 103 | 1253 | 72 | MBh | 43.6
86 | 103 | 1253 | 72 | S/T | 0.67
86 | 103 | 1253 | 72 | ∆T | 21.6
86 | 103 | 1253 | 72 | LDB | 64.4
86 | 103 | 1253 | 72 | LWB | 62.2
86 | 103 | 1253 | 72 | kW | 4.69
90 | 103 | 1253 | 75 | MBh | 43.6
90 | 103 | 1253 | 75 | S/T | 0.631
90 | 103 | 1253 | 75 | ∆T | 20.3
90 | 103 | 1253 | 75 | LDB | 69.7
90 | 103 | 1253 | 75 | LWB | 65.9
90 | 103 | 1253 | 75 | kW | 4.69
68 | 106 | 1253 | 57 | MBh | 27.3
68 | 106 | 1253 | 57 | S/T | 0.832
68 | 106 | 1253 | 57 | ∆T | 16.8
68 | 106 | 1253 | 57 | LDB | 51.2
68 | 106 | 1253 | 57 | LWB | 48.7
68 | 106 | 1253 | 57 | kW | 2.59
72 | 106 | 1253 | 61 | MBh | 33.2
72 | 106 | 1253 | 61 | S/T | 0.795
72 | 106 | 1253 | 61 | ∆T | 19.5
72 | 106 | 1253 | 61 | LDB | 52.5
72 | 106 | 1253 | 61 | LWB | 51.6
72 | 106 | 1253 | 61 | kW | 3.41
77 | 106 | 1253 | 64 | MBh | 37.6
77 | 106 | 1253 | 64 | S/T | 0.769
77 | 106 | 1253 | 64 | ∆T | 21.4
77 | 106 | 1253 | 64 | LDB | 55.6
77 | 106 | 1253 | 64 | LWB | 53.9
77 | 106 | 1253 | 64 | kW | 4.1
80 | 106 | 1253 | 67 | MBh | 41.5
80 | 106 | 1253 | 67 | S/T | 0.73
80 | 106 | 1253 | 67 | ∆T | 22.4
80 | 106 | 1253 | 67 | LDB | 57.6
80 | 106 | 1253 | 67 | LWB | 56.5
80 | 106 | 1253 | 67 | kW | 4.76
84 | 106 | 1253 | 70 | MBh | 42.2
84 | 106 | 1253 | 70 | S/T | 0.709
84 | 106 | 1253 | 70 | ∆T | 22.1
84 | 106 | 1253 | 70 | LDB | 61.9
84 | 106 | 1253 | 70 | LWB | 60
84 | 106 | 1253 | 70 | kW | 4.78
86 | 106 | 1253 | 72 | MBh | 42.2
86 | 106 | 1253 | 72 | S/T | 0.668
86 | 106 | 1253 | 72 | ∆T | 20.8
86 | 106 | 1253 | 72 | LDB | 65.2
86 | 106 | 1253 | 72 | LWB | 62.5
86 | 106 | 1253 | 72 | kW | 4.78
90 | 106 | 1253 | 75 | MBh | 42.2
90 | 106 | 1253 | 75 | S/T | 0.63
90 | 106 | 1253 | 75 | ∆T | 19.7
90 | 106 | 1253 | 75 | LDB | 70.3
90 | 106 | 1253 | 75 | LWB | 66.2
90 | 106 | 1253 | 75 | kW | 4.78
68 | 110 | 1253 | 57 | MBh | 27.3
68 | 110 | 1253 | 57 | S/T | 0.832
68 | 110 | 1253 | 57 | ∆T | 16.8
68 | 110 | 1253 | 57 | LDB | 51.2
68 | 110 | 1253 | 57 | LWB | 48.7
68 | 110 | 1253 | 57 | kW | 2.77
72 | 110 | 1253 | 61 | MBh | 33.2
72 | 110 | 1253 | 61 | S/T | 0.795
72 | 110 | 1253 | 61 | ∆T | 19.5
72 | 110 | 1253 | 61 | LDB | 52.5
72 | 110 | 1253 | 61 | LWB | 51.6
72 | 110 | 1253 | 61 | kW | 3.65
77 | 110 | 1253 | 64 | MBh | 37.6
77 | 110 | 1253 | 64 | S/T | 0.769
77 | 110 | 1253 | 64 | ∆T | 21.4
77 | 110 | 1253 | 64 | LDB | 55.6
77 | 110 | 1253 | 64 | LWB | 53.9
77 | 110 | 1253 | 64 | kW | 4.4
80 | 110 | 1253 | 67 | MBh | 39.4
80 | 110 | 1253 | 67 | S/T | 0.731
80 | 110 | 1253 | 67 | ∆T | 21.3
80 | 110 | 1253 | 67 | LDB | 58.7
80 | 110 | 1253 | 67 | LWB | 57.1
80 | 110 | 1253 | 67 | kW | 4.73
84 | 110 | 1253 | 70 | MBh | 39.4
84 | 110 | 1253 | 70 | S/T | 0.711
84 | 110 | 1253 | 70 | ∆T | 20.7
84 | 110 | 1253 | 70 | LDB | 63.3
84 | 110 | 1253 | 70 | LWB | 60.7
84 | 110 | 1253 | 70 | kW | 4.73
86 | 110 | 1253 | 72 | MBh | 39.4
86 | 110 | 1253 | 72 | S/T | 0.67
86 | 110 | 1253 | 72 | ∆T | 19.5
86 | 110 | 1253 | 72 | LDB | 66.5
86 | 110 | 1253 | 72 | LWB | 63.2
86 | 110 | 1253 | 72 | kW | 4.73
90 | 110 | 1253 | 75 | MBh | 39.4
90 | 110 | 1253 | 75 | S/T | 0.632
90 | 110 | 1253 | 75 | ∆T | 18.4
90 | 110 | 1253 | 75 | LDB | 71.6
90 | 110 | 1253 | 75 | LWB | 66.8
90 | 110 | 1253 | 75 | kW | 4.73
68 | 115 | 1253 | 57 | MBh | 27.3
68 | 115 | 1253 | 57 | S/T | 0.832
68 | 115 | 1253 | 57 | ∆T | 16.8
68 | 115 | 1253 | 57 | LDB | 51.2
68 | 115 | 1253 | 57 | LWB | 48.7
68 | 115 | 1253 | 57 | kW | 3.07
72 | 115 | 1253 | 61 | MBh | 32.2
72 | 115 | 1253 | 61 | S/T | 0.795
72 | 115 | 1253 | 61 | ∆T | 18.9
72 | 115 | 1253 | 61 | LDB | 53.1
72 | 115 | 1253 | 61 | LWB | 51.9
72 | 115 | 1253 | 61 | kW | 3.88
77 | 115 | 1253 | 64 | MBh | 32.2
77 | 115 | 1253 | 64 | S/T | 0.77
77 | 115 | 1253 | 64 | ∆T | 18.3
77 | 115 | 1253 | 64 | LDB | 58.7
77 | 115 | 1253 | 64 | LWB | 55.5
77 | 115 | 1253 | 64 | kW | 3.88
80 | 115 | 1253 | 67 | MBh | 32.2
80 | 115 | 1253 | 67 | S/T | 0.73
80 | 115 | 1253 | 67 | ∆T | 17.4
80 | 115 | 1253 | 67 | LDB | 62.6
80 | 115 | 1253 | 67 | LWB | 59
80 | 115 | 1253 | 67 | kW | 3.88
84 | 115 | 1253 | 70 | MBh | 32.2
84 | 115 | 1253 | 70 | S/T | 0.708
84 | 115 | 1253 | 70 | ∆T | 16.8
84 | 115 | 1253 | 70 | LDB | 67.2
84 | 115 | 1253 | 70 | LWB | 62.6
84 | 115 | 1253 | 70 | kW | 3.88
86 | 115 | 1253 | 72 | MBh | 32.2
86 | 115 | 1253 | 72 | S/T | 0.668
86 | 115 | 1253 | 72 | ∆T | 15.9
86 | 115 | 1253 | 72 | LDB | 70.1
86 | 115 | 1253 | 72 | LWB | 64.9
86 | 115 | 1253 | 72 | kW | 3.88
90 | 115 | 1253 | 75 | MBh | 32.2
90 | 115 | 1253 | 75 | S/T | 0.63
90 | 115 | 1253 | 75 | ∆T | 15
90 | 115 | 1253 | 75 | LDB | 75
90 | 115 | 1253 | 75 | LWB | 68.4
90 | 115 | 1253 | 75 | kW | 3.88
68 | 118 | 1253 | 57 | MBh | 27.3
68 | 118 | 1253 | 57 | S/T | 0.832
68 | 118 | 1253 | 57 | ∆T | 16.8
68 | 118 | 1253 | 57 | LDB | 51.2
68 | 118 | 1253 | 57 | LWB | 48.7
68 | 118 | 1253 | 57 | kW | 3.3
72 | 118 | 1253 | 61 | MBh | 27.8
72 | 118 | 1253 | 61 | S/T | 0.799
72 | 118 | 1253 | 61 | ∆T | 16.4
72 | 118 | 1253 | 61 | LDB | 55.6
72 | 118 | 1253 | 61 | LWB | 53.2
72 | 118 | 1253 | 61 | kW | 3.4
77 | 118 | 1253 | 64 | MBh | 27.8
77 | 118 | 1253 | 64 | S/T | 0.77
77 | 118 | 1253 | 64 | ∆T | 15.8
77 | 118 | 1253 | 64 | LDB | 61.2
77 | 118 | 1253 | 64 | LWB | 56.7
77 | 118 | 1253 | 64 | kW | 3.4
80 | 118 | 1253 | 67 | MBh | 27.8
80 | 118 | 1253 | 67 | S/T | 0.73
80 | 118 | 1253 | 67 | ∆T | 15
80 | 118 | 1253 | 67 | LDB | 65
80 | 118 | 1253 | 67 | LWB | 60.2
80 | 118 | 1253 | 67 | kW | 3.4
84 | 118 | 1253 | 70 | MBh | 27.8
84 | 118 | 1253 | 70 | S/T | 0.712
84 | 118 | 1253 | 70 | ∆T | 14.6
84 | 118 | 1253 | 70 | LDB | 69.4
84 | 118 | 1253 | 70 | LWB | 63.7
84 | 118 | 1253 | 70 | kW | 3.4
86 | 118 | 1253 | 72 | MBh | 27.8
86 | 118 | 1253 | 72 | S/T | 0.669
86 | 118 | 1253 | 72 | ∆T | 13.7
86 | 118 | 1253 | 72 | LDB | 72.3
86 | 118 | 1253 | 72 | LWB | 66
86 | 118 | 1253 | 72 | kW | 3.4
90 | 118 | 1253 | 75 | MBh | 27.8
90 | 118 | 1253 | 75 | S/T | 0.633
90 | 118 | 1253 | 75 | ∆T | 13
90 | 118 | 1253 | 75 | LDB | 77
90 | 118 | 1253 | 75 | LWB | 69.4
90 | 118 | 1253 | 75 | kW | 3.4
68 | 122 | 1253 | 57 | MBh | 22
68 | 122 | 1253 | 57 | S/T | 0.832
68 | 122 | 1253 | 57 | ∆T | 13.5
68 | 122 | 1253 | 57 | LDB | 54.5
68 | 122 | 1253 | 57 | LWB | 50.4
68 | 122 | 1253 | 57 | kW | 2.72
72 | 122 | 1253 | 61 | MBh | 22
72 | 122 | 1253 | 61 | S/T | 0.795
72 | 122 | 1253 | 61 | ∆T | 12.9
72 | 122 | 1253 | 61 | LDB | 59.1
72 | 122 | 1253 | 61 | LWB | 54.9
72 | 122 | 1253 | 61 | kW | 2.72
77 | 122 | 1253 | 64 | MBh | 22
77 | 122 | 1253 | 64 | S/T | 0.768
77 | 122 | 1253 | 64 | ∆T | 12.5
77 | 122 | 1253 | 64 | LDB | 64.5
77 | 122 | 1253 | 64 | LWB | 58.3
77 | 122 | 1253 | 64 | kW | 2.72
80 | 122 | 1253 | 67 | MBh | 22
80 | 122 | 1253 | 67 | S/T | 0.727
80 | 122 | 1253 | 67 | ∆T | 11.8
80 | 122 | 1253 | 67 | LDB | 68.2
80 | 122 | 1253 | 67 | LWB | 61.7
80 | 122 | 1253 | 67 | kW | 2.72
84 | 122 | 1253 | 70 | MBh | 22
84 | 122 | 1253 | 70 | S/T | 0.709
84 | 122 | 1253 | 70 | ∆T | 11.5
84 | 122 | 1253 | 70 | LDB | 72.5
84 | 122 | 1253 | 70 | LWB | 65.1
84 | 122 | 1253 | 70 | kW | 2.72
86 | 122 | 1253 | 72 | MBh | 22
86 | 122 | 1253 | 72 | S/T | 0.668
86 | 122 | 1253 | 72 | ∆T | 10.9
86 | 122 | 1253 | 72 | LDB | 75.1
86 | 122 | 1253 | 72 | LWB | 67.3
86 | 122 | 1253 | 72 | kW | 2.72
90 | 122 | 1253 | 75 | MBh | 22
90 | 122 | 1253 | 75 | S/T | 0.632
90 | 122 | 1253 | 75 | ∆T | 10.3
90 | 122 | 1253 | 75 | LDB | 79.7
90 | 122 | 1253 | 75 | LWB | 70.6
90 | 122 | 1253 | 75 | kW | 2.72

## RZA48AAVJU - FCA48AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1253 | 57 | MBh | 31.1 | 64 | 60 | 61 | 64.8 | 4.56
68 | 23 | 1253 | 57 | S/T | 0.833 | 64 | 60 | 65 | 60 | 3.79
68 | 23 | 1253 | 57 | ∆T | 19.1 | 64 | 60 | 68 | 56.4 | 3.33
68 | 23 | 1253 | 57 | LDB | 48.9 | 64 | 60 | 70 | 54 | 3.08
68 | 23 | 1253 | 57 | LWB | 47.4 | 64 | 60 | 72 | 51.6 | 2.88
68 | 23 | 1253 | 57 | kW | 1.6 | 64 | 60 | 75 | 48 | 2.65
72 | 23 | 1253 | 61 | MBh | 37.9 | 60 | 56 | 61 | 64.8 | 4.96
72 | 23 | 1253 | 61 | S/T | 0.797 | 60 | 56 | 65 | 60 | 4.09
72 | 23 | 1253 | 61 | ∆T | 22.3 | 60 | 56 | 68 | 56.4 | 3.56
72 | 23 | 1253 | 61 | LDB | 49.7 | 60 | 56 | 70 | 54 | 3.27
72 | 23 | 1253 | 61 | LWB | 49.7 | 60 | 56 | 72 | 51.6 | 3.02
72 | 23 | 1253 | 61 | kW | 1.97 | 60 | 56 | 75 | 48 | 2.74
77 | 23 | 1253 | 64 | MBh | 42.9 | 57 | 53 | 61 | 64.8 | 5.31
77 | 23 | 1253 | 64 | S/T | 0.772 | 57 | 53 | 65 | 60 | 4.36
77 | 23 | 1253 | 64 | ∆T | 24.5 | 57 | 53 | 68 | 56.4 | 3.77
77 | 23 | 1253 | 64 | LDB | 52.5 | 57 | 53 | 70 | 54 | 3.44
77 | 23 | 1253 | 64 | LWB | 52.3 | 57 | 53 | 72 | 51.6 | 3.15
77 | 23 | 1253 | 64 | kW | 2.26 | 57 | 53 | 75 | 48 | 2.82
80 | 23 | 1253 | 67 | MBh | 48 | 54 | 50 | 61 | 64.8 | 5.71
80 | 23 | 1253 | 67 | S/T | 0.729 | 54 | 50 | 65 | 60 | 4.65
80 | 23 | 1253 | 67 | ∆T | 25.9 | 54 | 50 | 68 | 56.4 | 4
80 | 23 | 1253 | 67 | LDB | 54.1 | 54 | 50 | 70 | 54 | 3.63
80 | 23 | 1253 | 67 | LWB | 54.1 | 54 | 50 | 72 | 51.6 | 3.31
80 | 23 | 1253 | 67 | kW | 2.56 | 54 | 50 | 75 | 48 | 2.93
84 | 23 | 1253 | 70 | MBh | 53.1 | 51 | 47 | 61 | 64.8 | 5.77
84 | 23 | 1253 | 70 | S/T | 0.71 | 51 | 47 | 65 | 60 | 4.99
84 | 23 | 1253 | 70 | ∆T | 27.9 | 51 | 47 | 68 | 56.4 | 4.27
84 | 23 | 1253 | 70 | LDB | 56.1 | 51 | 47 | 70 | 54 | 3.85
84 | 23 | 1253 | 70 | LWB | 56.1 | 51 | 47 | 72 | 51.6 | 3.49
84 | 23 | 1253 | 70 | kW | 2.87 | 51 | 47 | 75 | 48 | 3.05
86 | 23 | 1253 | 72 | MBh | 56.4 | 47 | 43 | 61 | 64.8 | 5.75
86 | 23 | 1253 | 72 | S/T | 0.67 | 47 | 43 | 65 | 60 | 5.52
86 | 23 | 1253 | 72 | ∆T | 27.9 | 47 | 43 | 68 | 56.4 | 4.68
86 | 23 | 1253 | 72 | LDB | 58.1 | 47 | 43 | 70 | 54 | 4.2
86 | 23 | 1253 | 72 | LWB | 58.1 | 47 | 43 | 72 | 51.6 | 3.78
86 | 23 | 1253 | 72 | kW | 3.09 | 47 | 43 | 75 | 48 | 3.26
90 | 23 | 1253 | 75 | MBh | 61.5 | 44 | 40 | 61 | 64.8 | 5.73
90 | 23 | 1253 | 75 | S/T | 0.631 | 44 | 40 | 65 | 60 | 5.77
90 | 23 | 1253 | 75 | ∆T | 28.7 | 44 | 40 | 68 | 56.4 | 5.05
90 | 23 | 1253 | 75 | LDB | 61.3 | 44 | 40 | 70 | 54 | 4.51
90 | 23 | 1253 | 75 | LWB | 61.3 | 44 | 40 | 72 | 51.6 | 4.04
90 | 23 | 1253 | 75 | kW | 3.41 | 44 | 40 | 75 | 48 | 3.45
68 | 30 | 1253 | 57 | MBh | 31.1 | 39 | 36 | 61 | 64.3 | 5.7
68 | 30 | 1253 | 57 | S/T | 0.833 | 39 | 36 | 65 | 60 | 5.74
68 | 30 | 1253 | 57 | ∆T | 19.1 | 39 | 36 | 68 | 56.4 | 5.62
68 | 30 | 1253 | 57 | LDB | 48.9 | 39 | 36 | 70 | 54 | 5
68 | 30 | 1253 | 57 | LWB | 47.4 | 39 | 36 | 72 | 51.6 | 4.45
68 | 30 | 1253 | 57 | kW | 1.65 | 39 | 36 | 75 | 48 | 3.75
72 | 30 | 1253 | 61 | MBh | 37.9 | 35 | 32 | 61 | 60.9 | 5.67
72 | 30 | 1253 | 61 | S/T | 0.797 | 35 | 32 | 65 | 60 | 5.72
72 | 30 | 1253 | 61 | ∆T | 22.3 | 35 | 32 | 68 | 56.4 | 5.75
72 | 30 | 1253 | 61 | LDB | 49.7 | 35 | 32 | 70 | 54 | 5.6
72 | 30 | 1253 | 61 | LWB | 49.7 | 35 | 32 | 72 | 51.6 | 4.95
72 | 30 | 1253 | 61 | kW | 2.03 | 35 | 32 | 75 | 48 | 4.13
77 | 30 | 1253 | 64 | MBh | 42.9 | 30 | 28 | 61 | 57.5 | 5.64
77 | 30 | 1253 | 64 | S/T | 0.772 | 30 | 28 | 65 | 57.5 | 5.69
77 | 30 | 1253 | 64 | ∆T | 24.5 | 30 | 28 | 68 | 56.4 | 5.72
77 | 30 | 1253 | 64 | LDB | 52.5 | 30 | 28 | 70 | 54 | 5.74
77 | 30 | 1253 | 64 | LWB | 52.3 | 30 | 28 | 72 | 51.6 | 5.57
77 | 30 | 1253 | 64 | kW | 2.33 | 30 | 28 | 75 | 48 | 4.6
80 | 30 | 1253 | 67 | MBh | 48 | 26 | 24 | 61 | 54.1 | 5.61
80 | 30 | 1253 | 67 | S/T | 0.729 | 26 | 24 | 65 | 54.1 | 5.66
80 | 30 | 1253 | 67 | ∆T | 25.9 | 26 | 24 | 68 | 54.1 | 5.69
80 | 30 | 1253 | 67 | LDB | 54.1 | 26 | 24 | 70 | 54 | 5.71
80 | 30 | 1253 | 67 | LWB | 54.1 | 26 | 24 | 72 | 51.6 | 5.74
80 | 30 | 1253 | 67 | kW | 2.65 | 26 | 24 | 75 | 48 | 5.18
84 | 30 | 1253 | 70 | MBh | 53.1 | 22 | 20 | 61 | 50.6 | 5.57
84 | 30 | 1253 | 70 | S/T | 0.71 | 22 | 20 | 65 | 50.6 | 5.62
84 | 30 | 1253 | 70 | ∆T | 27.9 | 22 | 20 | 68 | 50.6 | 5.66
84 | 30 | 1253 | 70 | LDB | 56.1 | 22 | 20 | 70 | 50.6 | 5.68
84 | 30 | 1253 | 70 | LWB | 56.1 | 22 | 20 | 72 | 50.6 | 5.71
84 | 30 | 1253 | 70 | kW | 2.97 | 22 | 20 | 75 | 48 | 5.74
86 | 30 | 1253 | 72 | MBh | 56.4 | 19 | 18 | 61 | 48.9 | 5.55
86 | 30 | 1253 | 72 | S/T | 0.67 | 19 | 18 | 65 | 48.9 | 5.6
86 | 30 | 1253 | 72 | ∆T | 27.9 | 19 | 18 | 68 | 48.9 | 5.64
86 | 30 | 1253 | 72 | LDB | 58.1 | 19 | 18 | 70 | 48.9 | 5.67
86 | 30 | 1253 | 72 | LWB | 58.1 | 19 | 18 | 72 | 48.9 | 5.69
86 | 30 | 1253 | 72 | kW | 3.19 | 19 | 18 | 75 | 48 | 5.73
90 | 30 | 1253 | 75 | MBh | 61.5 | 17 | 16 | 61 | 46.8 | 5.53
90 | 30 | 1253 | 75 | S/T | 0.631 | 17 | 16 | 65 | 46.8 | 5.58
90 | 30 | 1253 | 75 | ∆T | 28.7 | 17 | 16 | 68 | 46.8 | 5.62
90 | 30 | 1253 | 75 | LDB | 61.3 | 17 | 16 | 70 | 46.8 | 5.65
90 | 30 | 1253 | 75 | LWB | 61.3 | 17 | 16 | 72 | 46.8 | 5.67
90 | 30 | 1253 | 75 | kW | 3.52 | 17 | 16 | 75 | 46.8 | 5.71
68 | 40 | 1253 | 57 | MBh | 31.1 | 15 | 14 | 61 | 45.5 | 5.51
68 | 40 | 1253 | 57 | S/T | 0.833 | 15 | 14 | 65 | 45.5 | 5.57
68 | 40 | 1253 | 57 | ∆T | 19.1 | 15 | 14 | 68 | 45.5 | 5.61
68 | 40 | 1253 | 57 | LDB | 48.9 | 15 | 14 | 70 | 45.5 | 5.63
68 | 40 | 1253 | 57 | LWB | 47.4 | 15 | 14 | 72 | 45.5 | 5.66
68 | 40 | 1253 | 57 | kW | 1.72 | 15 | 14 | 75 | 45.5 | 5.7
72 | 40 | 1253 | 61 | MBh | 37.9 | 13 | 12 | 61 | 43.8 | 5.49
72 | 40 | 1253 | 61 | S/T | 0.797 | 13 | 12 | 65 | 43.8 | 5.55
72 | 40 | 1253 | 61 | ∆T | 22.3 | 13 | 12 | 68 | 43.8 | 5.59
72 | 40 | 1253 | 61 | LDB | 49.7 | 13 | 12 | 70 | 43.8 | 5.61
72 | 40 | 1253 | 61 | LWB | 49.7 | 13 | 12 | 72 | 43.8 | 5.64
72 | 40 | 1253 | 61 | kW | 2.13 | 13 | 12 | 75 | 43.8 | 5.68
77 | 40 | 1253 | 64 | MBh | 42.9 | 10 | 9 | 61 | 40.8 | 5.45
77 | 40 | 1253 | 64 | S/T | 0.772 | 10 | 9 | 65 | 40.8 | 5.51
77 | 40 | 1253 | 64 | ∆T | 24.5 | 10 | 9 | 68 | 40.8 | 5.55
77 | 40 | 1253 | 64 | LDB | 52.5 | 10 | 9 | 70 | 40.8 | 5.58
77 | 40 | 1253 | 64 | LWB | 52.3 | 10 | 9 | 72 | 40.8 | 5.61
77 | 40 | 1253 | 64 | kW | 2.44 | 10 | 9 | 75 | 40.8 | 5.65
80 | 40 | 1253 | 67 | MBh | 48 | 6 | 5 | 61 | 37.8 | 5.41
80 | 40 | 1253 | 67 | S/T | 0.729 | 6 | 5 | 65 | 37.8 | 5.47
80 | 40 | 1253 | 67 | ∆T | 25.9 | 6 | 5 | 68 | 37.8 | 5.51
80 | 40 | 1253 | 67 | LDB | 54.1 | 6 | 5 | 70 | 37.8 | 5.54
80 | 40 | 1253 | 67 | LWB | 54.1 | 6 | 5 | 72 | 37.8 | 5.57
80 | 40 | 1253 | 67 | kW | 2.77 | 6 | 5 | 75 | 37.8 | 5.61
84 | 40 | 1253 | 70 | MBh | 53.1 | -2 | -2 | 61 | 31.6 | 5.3
84 | 40 | 1253 | 70 | S/T | 0.71 | -2 | -2 | 65 | 31.6 | 5.37
84 | 40 | 1253 | 70 | ∆T | 27.9 | -2 | -2 | 68 | 31.6 | 5.42
84 | 40 | 1253 | 70 | LDB | 56.1 | -2 | -2 | 70 | 31.6 | 5.45
84 | 40 | 1253 | 70 | LWB | 56.1 | -2 | -2 | 72 | 31.6 | 5.48
84 | 40 | 1253 | 70 | kW | 3.11 | -2 | -2 | 75 | 31.6 | 5.53
86 | 40 | 1253 | 72 | MBh | 56.4 | -4 | -4 | 61 | 30.1 | 5.27
86 | 40 | 1253 | 72 | S/T | 0.67 | -4 | -4 | 65 | 30.1 | 5.34
86 | 40 | 1253 | 72 | ∆T | 27.9 | -4 | -4 | 68 | 30.1 | 5.39
86 | 40 | 1253 | 72 | LDB | 58.1 | -4 | -4 | 70 | 30.1 | 5.42
86 | 40 | 1253 | 72 | LWB | 58.1 | -4 | -4 | 72 | 30.1 | 5.46
86 | 40 | 1253 | 72 | kW | 3.35 | -4 | -4 | 75 | 30.1 | 5.51
90 | 40 | 1253 | 75 | MBh | 61.5
90 | 40 | 1253 | 75 | S/T | 0.631
90 | 40 | 1253 | 75 | ∆T | 28.7
90 | 40 | 1253 | 75 | LDB | 61.3
90 | 40 | 1253 | 75 | LWB | 61.3
90 | 40 | 1253 | 75 | kW | 3.69
68 | 50 | 1253 | 57 | MBh | 31.1
68 | 50 | 1253 | 57 | S/T | 0.833
68 | 50 | 1253 | 57 | ∆T | 19.1
68 | 50 | 1253 | 57 | LDB | 48.9
68 | 50 | 1253 | 57 | LWB | 47.4
68 | 50 | 1253 | 57 | kW | 1.8
72 | 50 | 1253 | 61 | MBh | 37.9
72 | 50 | 1253 | 61 | S/T | 0.797
72 | 50 | 1253 | 61 | ∆T | 22.3
72 | 50 | 1253 | 61 | LDB | 49.7
72 | 50 | 1253 | 61 | LWB | 49.7
72 | 50 | 1253 | 61 | kW | 2.23
77 | 50 | 1253 | 64 | MBh | 42.9
77 | 50 | 1253 | 64 | S/T | 0.772
77 | 50 | 1253 | 64 | ∆T | 24.5
77 | 50 | 1253 | 64 | LDB | 52.5
77 | 50 | 1253 | 64 | LWB | 52.3
77 | 50 | 1253 | 64 | kW | 2.57
80 | 50 | 1253 | 67 | MBh | 48
80 | 50 | 1253 | 67 | S/T | 0.729
80 | 50 | 1253 | 67 | ∆T | 25.9
80 | 50 | 1253 | 67 | LDB | 54.1
80 | 50 | 1253 | 67 | LWB | 54.1
80 | 50 | 1253 | 67 | kW | 2.92
84 | 50 | 1253 | 70 | MBh | 53.1
84 | 50 | 1253 | 70 | S/T | 0.71
84 | 50 | 1253 | 70 | ∆T | 27.9
84 | 50 | 1253 | 70 | LDB | 56.1
84 | 50 | 1253 | 70 | LWB | 56.1
84 | 50 | 1253 | 70 | kW | 3.28
86 | 50 | 1253 | 72 | MBh | 56.4
86 | 50 | 1253 | 72 | S/T | 0.67
86 | 50 | 1253 | 72 | ∆T | 27.9
86 | 50 | 1253 | 72 | LDB | 58.1
86 | 50 | 1253 | 72 | LWB | 58.1
86 | 50 | 1253 | 72 | kW | 3.52
90 | 50 | 1253 | 75 | MBh | 61.5
90 | 50 | 1253 | 75 | S/T | 0.631
90 | 50 | 1253 | 75 | ∆T | 28.7
90 | 50 | 1253 | 75 | LDB | 61.3
90 | 50 | 1253 | 75 | LWB | 61.3
90 | 50 | 1253 | 75 | kW | 3.88
68 | 54 | 1253 | 57 | MBh | 31.1
68 | 54 | 1253 | 57 | S/T | 0.833
68 | 54 | 1253 | 57 | ∆T | 19.1
68 | 54 | 1253 | 57 | LDB | 48.9
68 | 54 | 1253 | 57 | LWB | 47.4
68 | 54 | 1253 | 57 | kW | 1.84
72 | 54 | 1253 | 61 | MBh | 37.9
72 | 54 | 1253 | 61 | S/T | 0.797
72 | 54 | 1253 | 61 | ∆T | 22.3
72 | 54 | 1253 | 61 | LDB | 49.7
72 | 54 | 1253 | 61 | LWB | 49.7
72 | 54 | 1253 | 61 | kW | 2.28
77 | 54 | 1253 | 64 | MBh | 42.9
77 | 54 | 1253 | 64 | S/T | 0.772
77 | 54 | 1253 | 64 | ∆T | 24.5
77 | 54 | 1253 | 64 | LDB | 52.5
77 | 54 | 1253 | 64 | LWB | 52.3
77 | 54 | 1253 | 64 | kW | 2.62
80 | 54 | 1253 | 67 | MBh | 48
80 | 54 | 1253 | 67 | S/T | 0.729
80 | 54 | 1253 | 67 | ∆T | 25.9
80 | 54 | 1253 | 67 | LDB | 54.1
80 | 54 | 1253 | 67 | LWB | 54.1
80 | 54 | 1253 | 67 | kW | 2.98
84 | 54 | 1253 | 70 | MBh | 53.1
84 | 54 | 1253 | 70 | S/T | 0.71
84 | 54 | 1253 | 70 | ∆T | 27.9
84 | 54 | 1253 | 70 | LDB | 56.1
84 | 54 | 1253 | 70 | LWB | 56.1
84 | 54 | 1253 | 70 | kW | 3.34
86 | 54 | 1253 | 72 | MBh | 56.4
86 | 54 | 1253 | 72 | S/T | 0.67
86 | 54 | 1253 | 72 | ∆T | 27.9
86 | 54 | 1253 | 72 | LDB | 58.1
86 | 54 | 1253 | 72 | LWB | 58.1
86 | 54 | 1253 | 72 | kW | 3.59
90 | 54 | 1253 | 75 | MBh | 61.5
90 | 54 | 1253 | 75 | S/T | 0.631
90 | 54 | 1253 | 75 | ∆T | 28.7
90 | 54 | 1253 | 75 | LDB | 61.3
90 | 54 | 1253 | 75 | LWB | 61.3
90 | 54 | 1253 | 75 | kW | 3.97
68 | 58 | 1253 | 57 | MBh | 31.1
68 | 58 | 1253 | 57 | S/T | 0.833
68 | 58 | 1253 | 57 | ∆T | 19.1
68 | 58 | 1253 | 57 | LDB | 48.9
68 | 58 | 1253 | 57 | LWB | 47.4
68 | 58 | 1253 | 57 | kW | 1.87
72 | 58 | 1253 | 61 | MBh | 37.9
72 | 58 | 1253 | 61 | S/T | 0.797
72 | 58 | 1253 | 61 | ∆T | 22.3
72 | 58 | 1253 | 61 | LDB | 49.7
72 | 58 | 1253 | 61 | LWB | 49.7
72 | 58 | 1253 | 61 | kW | 2.32
77 | 58 | 1253 | 64 | MBh | 42.9
77 | 58 | 1253 | 64 | S/T | 0.772
77 | 58 | 1253 | 64 | ∆T | 24.5
77 | 58 | 1253 | 64 | LDB | 52.5
77 | 58 | 1253 | 64 | LWB | 52.3
77 | 58 | 1253 | 64 | kW | 2.68
80 | 58 | 1253 | 67 | MBh | 48
80 | 58 | 1253 | 67 | S/T | 0.729
80 | 58 | 1253 | 67 | ∆T | 25.9
80 | 58 | 1253 | 67 | LDB | 54.1
80 | 58 | 1253 | 67 | LWB | 54.1
80 | 58 | 1253 | 67 | kW | 3.04
84 | 58 | 1253 | 70 | MBh | 53.1
84 | 58 | 1253 | 70 | S/T | 0.71
84 | 58 | 1253 | 70 | ∆T | 27.9
84 | 58 | 1253 | 70 | LDB | 56.1
84 | 58 | 1253 | 70 | LWB | 56.1
84 | 58 | 1253 | 70 | kW | 3.42
86 | 58 | 1253 | 72 | MBh | 56.4
86 | 58 | 1253 | 72 | S/T | 0.67
86 | 58 | 1253 | 72 | ∆T | 27.9
86 | 58 | 1253 | 72 | LDB | 58.1
86 | 58 | 1253 | 72 | LWB | 58.1
86 | 58 | 1253 | 72 | kW | 3.67
90 | 58 | 1253 | 75 | MBh | 60.9
90 | 58 | 1253 | 75 | S/T | 0.632
90 | 58 | 1253 | 75 | ∆T | 28.5
90 | 58 | 1253 | 75 | LDB | 61.5
90 | 58 | 1253 | 75 | LWB | 61.5
90 | 58 | 1253 | 75 | kW | 3.98
68 | 62 | 1253 | 57 | MBh | 31.1
68 | 62 | 1253 | 57 | S/T | 0.833
68 | 62 | 1253 | 57 | ∆T | 19.1
68 | 62 | 1253 | 57 | LDB | 48.9
68 | 62 | 1253 | 57 | LWB | 47.4
68 | 62 | 1253 | 57 | kW | 1.91
72 | 62 | 1253 | 61 | MBh | 37.9
72 | 62 | 1253 | 61 | S/T | 0.797
72 | 62 | 1253 | 61 | ∆T | 22.3
72 | 62 | 1253 | 61 | LDB | 49.7
72 | 62 | 1253 | 61 | LWB | 49.7
72 | 62 | 1253 | 61 | kW | 2.37
77 | 62 | 1253 | 64 | MBh | 42.9
77 | 62 | 1253 | 64 | S/T | 0.772
77 | 62 | 1253 | 64 | ∆T | 24.5
77 | 62 | 1253 | 64 | LDB | 52.5
77 | 62 | 1253 | 64 | LWB | 52.3
77 | 62 | 1253 | 64 | kW | 2.73
80 | 62 | 1253 | 67 | MBh | 48
80 | 62 | 1253 | 67 | S/T | 0.729
80 | 62 | 1253 | 67 | ∆T | 25.9
80 | 62 | 1253 | 67 | LDB | 54.1
80 | 62 | 1253 | 67 | LWB | 54.1
80 | 62 | 1253 | 67 | kW | 3.11
84 | 62 | 1253 | 70 | MBh | 53.1
84 | 62 | 1253 | 70 | S/T | 0.71
84 | 62 | 1253 | 70 | ∆T | 27.9
84 | 62 | 1253 | 70 | LDB | 56.1
84 | 62 | 1253 | 70 | LWB | 56.1
84 | 62 | 1253 | 70 | kW | 3.49
86 | 62 | 1253 | 72 | MBh | 56.4
86 | 62 | 1253 | 72 | S/T | 0.67
86 | 62 | 1253 | 72 | ∆T | 27.9
86 | 62 | 1253 | 72 | LDB | 58.1
86 | 62 | 1253 | 72 | LWB | 58.1
86 | 62 | 1253 | 72 | kW | 3.75
90 | 62 | 1253 | 75 | MBh | 60
90 | 62 | 1253 | 75 | S/T | 0.632
90 | 62 | 1253 | 75 | ∆T | 28
90 | 62 | 1253 | 75 | LDB | 62
90 | 62 | 1253 | 75 | LWB | 61.9
90 | 62 | 1253 | 75 | kW | 4.06
68 | 66 | 1253 | 57 | MBh | 31.1
68 | 66 | 1253 | 57 | S/T | 0.833
68 | 66 | 1253 | 57 | ∆T | 19.1
68 | 66 | 1253 | 57 | LDB | 48.9
68 | 66 | 1253 | 57 | LWB | 47.4
68 | 66 | 1253 | 57 | kW | 1.95
72 | 66 | 1253 | 61 | MBh | 37.9
72 | 66 | 1253 | 61 | S/T | 0.797
72 | 66 | 1253 | 61 | ∆T | 22.3
72 | 66 | 1253 | 61 | LDB | 49.7
72 | 66 | 1253 | 61 | LWB | 49.7
72 | 66 | 1253 | 61 | kW | 2.42
77 | 66 | 1253 | 64 | MBh | 42.9
77 | 66 | 1253 | 64 | S/T | 0.772
77 | 66 | 1253 | 64 | ∆T | 24.5
77 | 66 | 1253 | 64 | LDB | 52.5
77 | 66 | 1253 | 64 | LWB | 52.3
77 | 66 | 1253 | 64 | kW | 2.79
80 | 66 | 1253 | 67 | MBh | 48
80 | 66 | 1253 | 67 | S/T | 0.729
80 | 66 | 1253 | 67 | ∆T | 25.9
80 | 66 | 1253 | 67 | LDB | 54.1
80 | 66 | 1253 | 67 | LWB | 54.1
80 | 66 | 1253 | 67 | kW | 3.18
84 | 66 | 1253 | 70 | MBh | 53.1
84 | 66 | 1253 | 70 | S/T | 0.71
84 | 66 | 1253 | 70 | ∆T | 27.9
84 | 66 | 1253 | 70 | LDB | 56.1
84 | 66 | 1253 | 70 | LWB | 56.1
84 | 66 | 1253 | 70 | kW | 3.69
86 | 66 | 1253 | 72 | MBh | 56.4
86 | 66 | 1253 | 72 | S/T | 0.67
86 | 66 | 1253 | 72 | ∆T | 27.9
86 | 66 | 1253 | 72 | LDB | 58.1
86 | 66 | 1253 | 72 | LWB | 58.1
86 | 66 | 1253 | 72 | kW | 4.04
90 | 66 | 1253 | 75 | MBh | 59.1
90 | 66 | 1253 | 75 | S/T | 0.631
90 | 66 | 1253 | 75 | ∆T | 27.6
90 | 66 | 1253 | 75 | LDB | 62.4
90 | 66 | 1253 | 75 | LWB | 62.1
90 | 66 | 1253 | 75 | kW | 4.29
68 | 70 | 1253 | 57 | MBh | 31.1
68 | 70 | 1253 | 57 | S/T | 0.833
68 | 70 | 1253 | 57 | ∆T | 19.1
68 | 70 | 1253 | 57 | LDB | 48.9
68 | 70 | 1253 | 57 | LWB | 47.4
68 | 70 | 1253 | 57 | kW | 1.99
72 | 70 | 1253 | 61 | MBh | 37.9
72 | 70 | 1253 | 61 | S/T | 0.797
72 | 70 | 1253 | 61 | ∆T | 22.3
72 | 70 | 1253 | 61 | LDB | 49.7
72 | 70 | 1253 | 61 | LWB | 49.7
72 | 70 | 1253 | 61 | kW | 2.48
77 | 70 | 1253 | 64 | MBh | 42.9
77 | 70 | 1253 | 64 | S/T | 0.772
77 | 70 | 1253 | 64 | ∆T | 24.5
77 | 70 | 1253 | 64 | LDB | 52.5
77 | 70 | 1253 | 64 | LWB | 52.3
77 | 70 | 1253 | 64 | kW | 2.93
80 | 70 | 1253 | 67 | MBh | 48
80 | 70 | 1253 | 67 | S/T | 0.729
80 | 70 | 1253 | 67 | ∆T | 25.9
80 | 70 | 1253 | 67 | LDB | 54.1
80 | 70 | 1253 | 67 | LWB | 54.1
80 | 70 | 1253 | 67 | kW | 3.44
84 | 70 | 1253 | 70 | MBh | 53.1
84 | 70 | 1253 | 70 | S/T | 0.71
84 | 70 | 1253 | 70 | ∆T | 27.9
84 | 70 | 1253 | 70 | LDB | 56.1
84 | 70 | 1253 | 70 | LWB | 56.1
84 | 70 | 1253 | 70 | kW | 3.99
86 | 70 | 1253 | 72 | MBh | 56.4
86 | 70 | 1253 | 72 | S/T | 0.67
86 | 70 | 1253 | 72 | ∆T | 27.9
86 | 70 | 1253 | 72 | LDB | 58.1
86 | 70 | 1253 | 72 | LWB | 58.1
86 | 70 | 1253 | 72 | kW | 4.38
90 | 70 | 1253 | 75 | MBh | 58.2
90 | 70 | 1253 | 75 | S/T | 0.632
90 | 70 | 1253 | 75 | ∆T | 27.2
90 | 70 | 1253 | 75 | LDB | 62.8
90 | 70 | 1253 | 75 | LWB | 62.3
90 | 70 | 1253 | 75 | kW | 4.52
68 | 72 | 1253 | 57 | MBh | 31.1
68 | 72 | 1253 | 57 | S/T | 0.833
68 | 72 | 1253 | 57 | ∆T | 19.1
68 | 72 | 1253 | 57 | LDB | 48.9
68 | 72 | 1253 | 57 | LWB | 47.4
68 | 72 | 1253 | 57 | kW | 2.01
72 | 72 | 1253 | 61 | MBh | 37.9
72 | 72 | 1253 | 61 | S/T | 0.797
72 | 72 | 1253 | 61 | ∆T | 22.3
72 | 72 | 1253 | 61 | LDB | 49.7
72 | 72 | 1253 | 61 | LWB | 49.7
72 | 72 | 1253 | 61 | kW | 2.56
77 | 72 | 1253 | 64 | MBh | 42.9
77 | 72 | 1253 | 64 | S/T | 0.772
77 | 72 | 1253 | 64 | ∆T | 24.5
77 | 72 | 1253 | 64 | LDB | 52.5
77 | 72 | 1253 | 64 | LWB | 52.3
77 | 72 | 1253 | 64 | kW | 3.04
80 | 72 | 1253 | 67 | MBh | 48
80 | 72 | 1253 | 67 | S/T | 0.729
80 | 72 | 1253 | 67 | ∆T | 25.9
80 | 72 | 1253 | 67 | LDB | 54.1
80 | 72 | 1253 | 67 | LWB | 54.1
80 | 72 | 1253 | 67 | kW | 3.57
84 | 72 | 1253 | 70 | MBh | 53.1
84 | 72 | 1253 | 70 | S/T | 0.71
84 | 72 | 1253 | 70 | ∆T | 27.9
84 | 72 | 1253 | 70 | LDB | 56.1
84 | 72 | 1253 | 70 | LWB | 56.1
84 | 72 | 1253 | 70 | kW | 4.15
86 | 72 | 1253 | 72 | MBh | 56.4
86 | 72 | 1253 | 72 | S/T | 0.67
86 | 72 | 1253 | 72 | ∆T | 27.9
86 | 72 | 1253 | 72 | LDB | 58.1
86 | 72 | 1253 | 72 | LWB | 58.1
86 | 72 | 1253 | 72 | kW | 4.56
90 | 72 | 1253 | 75 | MBh | 57.8
90 | 72 | 1253 | 75 | S/T | 0.631
90 | 72 | 1253 | 75 | ∆T | 27
90 | 72 | 1253 | 75 | LDB | 63
90 | 72 | 1253 | 75 | LWB | 62.4
90 | 72 | 1253 | 75 | kW | 4.63
68 | 75 | 1253 | 57 | MBh | 31.1
68 | 75 | 1253 | 57 | S/T | 0.833
68 | 75 | 1253 | 57 | ∆T | 19.1
68 | 75 | 1253 | 57 | LDB | 48.9
68 | 75 | 1253 | 57 | LWB | 47.4
68 | 75 | 1253 | 57 | kW | 2.09
72 | 75 | 1253 | 61 | MBh | 37.9
72 | 75 | 1253 | 61 | S/T | 0.797
72 | 75 | 1253 | 61 | ∆T | 22.3
72 | 75 | 1253 | 61 | LDB | 49.7
72 | 75 | 1253 | 61 | LWB | 49.7
72 | 75 | 1253 | 61 | kW | 2.7
77 | 75 | 1253 | 64 | MBh | 42.9
77 | 75 | 1253 | 64 | S/T | 0.772
77 | 75 | 1253 | 64 | ∆T | 24.5
77 | 75 | 1253 | 64 | LDB | 52.5
77 | 75 | 1253 | 64 | LWB | 52.3
77 | 75 | 1253 | 64 | kW | 3.22
80 | 75 | 1253 | 67 | MBh | 48
80 | 75 | 1253 | 67 | S/T | 0.729
80 | 75 | 1253 | 67 | ∆T | 25.9
80 | 75 | 1253 | 67 | LDB | 54.1
80 | 75 | 1253 | 67 | LWB | 54.1
80 | 75 | 1253 | 67 | kW | 3.79
84 | 75 | 1253 | 70 | MBh | 53.1
84 | 75 | 1253 | 70 | S/T | 0.71
84 | 75 | 1253 | 70 | ∆T | 27.9
84 | 75 | 1253 | 70 | LDB | 56.1
84 | 75 | 1253 | 70 | LWB | 56.1
84 | 75 | 1253 | 70 | kW | 4.4
86 | 75 | 1253 | 72 | MBh | 56.1
86 | 75 | 1253 | 72 | S/T | 0.668
86 | 75 | 1253 | 72 | ∆T | 27.7
86 | 75 | 1253 | 72 | LDB | 58.3
86 | 75 | 1253 | 72 | LWB | 58.3
86 | 75 | 1253 | 72 | kW | 4.78
90 | 75 | 1253 | 75 | MBh | 57.1
90 | 75 | 1253 | 75 | S/T | 0.632
90 | 75 | 1253 | 75 | ∆T | 26.7
90 | 75 | 1253 | 75 | LDB | 63.3
90 | 75 | 1253 | 75 | LWB | 62.6
90 | 75 | 1253 | 75 | kW | 4.81
68 | 79 | 1253 | 57 | MBh | 31.1
68 | 79 | 1253 | 57 | S/T | 0.833
68 | 79 | 1253 | 57 | ∆T | 19.1
68 | 79 | 1253 | 57 | LDB | 48.9
68 | 79 | 1253 | 57 | LWB | 47.4
68 | 79 | 1253 | 57 | kW | 2.24
72 | 79 | 1253 | 61 | MBh | 37.9
72 | 79 | 1253 | 61 | S/T | 0.797
72 | 79 | 1253 | 61 | ∆T | 22.3
72 | 79 | 1253 | 61 | LDB | 49.7
72 | 79 | 1253 | 61 | LWB | 49.7
72 | 79 | 1253 | 61 | kW | 2.91
77 | 79 | 1253 | 64 | MBh | 42.9
77 | 79 | 1253 | 64 | S/T | 0.772
77 | 79 | 1253 | 64 | ∆T | 24.5
77 | 79 | 1253 | 64 | LDB | 52.5
77 | 79 | 1253 | 64 | LWB | 52.3
77 | 79 | 1253 | 64 | kW | 3.47
80 | 79 | 1253 | 67 | MBh | 48
80 | 79 | 1253 | 67 | S/T | 0.729
80 | 79 | 1253 | 67 | ∆T | 25.9
80 | 79 | 1253 | 67 | LDB | 54.1
80 | 79 | 1253 | 67 | LWB | 54.1
80 | 79 | 1253 | 67 | kW | 4.08
84 | 79 | 1253 | 70 | MBh | 53.1
84 | 79 | 1253 | 70 | S/T | 0.71
84 | 79 | 1253 | 70 | ∆T | 27.9
84 | 79 | 1253 | 70 | LDB | 56.1
84 | 79 | 1253 | 70 | LWB | 56.1
84 | 79 | 1253 | 70 | kW | 4.74
86 | 79 | 1253 | 72 | MBh | 55.2
86 | 79 | 1253 | 72 | S/T | 0.668
86 | 79 | 1253 | 72 | ∆T | 27.3
86 | 79 | 1253 | 72 | LDB | 58.7
86 | 79 | 1253 | 72 | LWB | 58.7
86 | 79 | 1253 | 72 | kW | 5
90 | 79 | 1253 | 75 | MBh | 56.2
90 | 79 | 1253 | 75 | S/T | 0.632
90 | 79 | 1253 | 75 | ∆T | 26.2
90 | 79 | 1253 | 75 | LDB | 63.8
90 | 79 | 1253 | 75 | LWB | 62.8
90 | 79 | 1253 | 75 | kW | 5.04
68 | 83 | 1253 | 57 | MBh | 31.1
68 | 83 | 1253 | 57 | S/T | 0.833
68 | 83 | 1253 | 57 | ∆T | 19.1
68 | 83 | 1253 | 57 | LDB | 48.9
68 | 83 | 1253 | 57 | LWB | 47.4
68 | 83 | 1253 | 57 | kW | 2.4
72 | 83 | 1253 | 61 | MBh | 37.9
72 | 83 | 1253 | 61 | S/T | 0.797
72 | 83 | 1253 | 61 | ∆T | 22.3
72 | 83 | 1253 | 61 | LDB | 49.7
72 | 83 | 1253 | 61 | LWB | 49.7
72 | 83 | 1253 | 61 | kW | 3.12
77 | 83 | 1253 | 64 | MBh | 42.9
77 | 83 | 1253 | 64 | S/T | 0.772
77 | 83 | 1253 | 64 | ∆T | 24.5
77 | 83 | 1253 | 64 | LDB | 52.5
77 | 83 | 1253 | 64 | LWB | 52.3
77 | 83 | 1253 | 64 | kW | 3.73
80 | 83 | 1253 | 67 | MBh | 48
80 | 83 | 1253 | 67 | S/T | 0.729
80 | 83 | 1253 | 67 | ∆T | 25.9
80 | 83 | 1253 | 67 | LDB | 54.1
80 | 83 | 1253 | 67 | LWB | 54.1
80 | 83 | 1253 | 67 | kW | 4.39
84 | 83 | 1253 | 70 | MBh | 53.1
84 | 83 | 1253 | 70 | S/T | 0.71
84 | 83 | 1253 | 70 | ∆T | 27.9
84 | 83 | 1253 | 70 | LDB | 56.1
84 | 83 | 1253 | 70 | LWB | 56.1
84 | 83 | 1253 | 70 | kW | 5.11
86 | 83 | 1253 | 72 | MBh | 54.3
86 | 83 | 1253 | 72 | S/T | 0.669
86 | 83 | 1253 | 72 | ∆T | 26.8
86 | 83 | 1253 | 72 | LDB | 59.2
86 | 83 | 1253 | 72 | LWB | 59.2
86 | 83 | 1253 | 72 | kW | 5.23
90 | 83 | 1253 | 75 | MBh | 55.3
90 | 83 | 1253 | 75 | S/T | 0.631
90 | 83 | 1253 | 75 | ∆T | 25.8
90 | 83 | 1253 | 75 | LDB | 64.2
90 | 83 | 1253 | 75 | LWB | 63.1
90 | 83 | 1253 | 75 | kW | 5.27
68 | 87 | 1253 | 57 | MBh | 31.1
68 | 87 | 1253 | 57 | S/T | 0.833
68 | 87 | 1253 | 57 | ∆T | 19.1
68 | 87 | 1253 | 57 | LDB | 48.9
68 | 87 | 1253 | 57 | LWB | 47.4
68 | 87 | 1253 | 57 | kW | 2.57
72 | 87 | 1253 | 61 | MBh | 37.9
72 | 87 | 1253 | 61 | S/T | 0.797
72 | 87 | 1253 | 61 | ∆T | 22.3
72 | 87 | 1253 | 61 | LDB | 49.7
72 | 87 | 1253 | 61 | LWB | 49.7
72 | 87 | 1253 | 61 | kW | 3.35
77 | 87 | 1253 | 64 | MBh | 42.9
77 | 87 | 1253 | 64 | S/T | 0.772
77 | 87 | 1253 | 64 | ∆T | 24.5
77 | 87 | 1253 | 64 | LDB | 52.5
77 | 87 | 1253 | 64 | LWB | 52.3
77 | 87 | 1253 | 64 | kW | 4.01
80 | 87 | 1253 | 67 | MBh | 48
80 | 87 | 1253 | 67 | S/T | 0.729
80 | 87 | 1253 | 67 | ∆T | 25.9
80 | 87 | 1253 | 67 | LDB | 54.1
80 | 87 | 1253 | 67 | LWB | 54.1
80 | 87 | 1253 | 67 | kW | 4.72
84 | 87 | 1253 | 70 | MBh | 52.7
84 | 87 | 1253 | 70 | S/T | 0.71
84 | 87 | 1253 | 70 | ∆T | 27.6
84 | 87 | 1253 | 70 | LDB | 56.4
84 | 87 | 1253 | 70 | LWB | 56.4
84 | 87 | 1253 | 70 | kW | 5.44
86 | 87 | 1253 | 72 | MBh | 53.4
86 | 87 | 1253 | 72 | S/T | 0.669
86 | 87 | 1253 | 72 | ∆T | 26.4
86 | 87 | 1253 | 72 | LDB | 59.6
86 | 87 | 1253 | 72 | LWB | 59.6
86 | 87 | 1253 | 72 | kW | 5.46
90 | 87 | 1253 | 75 | MBh | 54.4
90 | 87 | 1253 | 75 | S/T | 0.631
90 | 87 | 1253 | 75 | ∆T | 25.3
90 | 87 | 1253 | 75 | LDB | 64.7
90 | 87 | 1253 | 75 | LWB | 63.3
90 | 87 | 1253 | 75 | kW | 5.5
68 | 91 | 1253 | 57 | MBh | 31.1
68 | 91 | 1253 | 57 | S/T | 0.833
68 | 91 | 1253 | 57 | ∆T | 19.1
68 | 91 | 1253 | 57 | LDB | 48.9
68 | 91 | 1253 | 57 | LWB | 47.4
68 | 91 | 1253 | 57 | kW | 2.75
72 | 91 | 1253 | 61 | MBh | 37.9
72 | 91 | 1253 | 61 | S/T | 0.797
72 | 91 | 1253 | 61 | ∆T | 22.3
72 | 91 | 1253 | 61 | LDB | 49.7
72 | 91 | 1253 | 61 | LWB | 49.7
72 | 91 | 1253 | 61 | kW | 3.6
77 | 91 | 1253 | 64 | MBh | 42.9
77 | 91 | 1253 | 64 | S/T | 0.772
77 | 91 | 1253 | 64 | ∆T | 24.5
77 | 91 | 1253 | 64 | LDB | 52.5
77 | 91 | 1253 | 64 | LWB | 52.3
77 | 91 | 1253 | 64 | kW | 4.3
80 | 91 | 1253 | 67 | MBh | 48
80 | 91 | 1253 | 67 | S/T | 0.729
80 | 91 | 1253 | 67 | ∆T | 25.9
80 | 91 | 1253 | 67 | LDB | 54.1
80 | 91 | 1253 | 67 | LWB | 54.1
80 | 91 | 1253 | 67 | kW | 5.08
84 | 91 | 1253 | 70 | MBh | 51.8
84 | 91 | 1253 | 70 | S/T | 0.71
84 | 91 | 1253 | 70 | ∆T | 27.2
84 | 91 | 1253 | 70 | LDB | 56.8
84 | 91 | 1253 | 70 | LWB | 56.8
84 | 91 | 1253 | 70 | kW | 5.67
86 | 91 | 1253 | 72 | MBh | 52.5
86 | 91 | 1253 | 72 | S/T | 0.669
86 | 91 | 1253 | 72 | ∆T | 25.9
86 | 91 | 1253 | 72 | LDB | 60.1
86 | 91 | 1253 | 72 | LWB | 59.9
86 | 91 | 1253 | 72 | kW | 5.69
90 | 91 | 1253 | 75 | MBh | 53.5
90 | 91 | 1253 | 75 | S/T | 0.632
90 | 91 | 1253 | 75 | ∆T | 25
90 | 91 | 1253 | 75 | LDB | 65
90 | 91 | 1253 | 75 | LWB | 63.5
90 | 91 | 1253 | 75 | kW | 5.73
68 | 93 | 1253 | 57 | MBh | 31.1
68 | 93 | 1253 | 57 | S/T | 0.833
68 | 93 | 1253 | 57 | ∆T | 19.1
68 | 93 | 1253 | 57 | LDB | 48.9
68 | 93 | 1253 | 57 | LWB | 47.4
68 | 93 | 1253 | 57 | kW | 2.85
72 | 93 | 1253 | 61 | MBh | 37.9
72 | 93 | 1253 | 61 | S/T | 0.797
72 | 93 | 1253 | 61 | ∆T | 22.3
72 | 93 | 1253 | 61 | LDB | 49.7
72 | 93 | 1253 | 61 | LWB | 49.7
72 | 93 | 1253 | 61 | kW | 3.72
77 | 93 | 1253 | 64 | MBh | 42.9
77 | 93 | 1253 | 64 | S/T | 0.772
77 | 93 | 1253 | 64 | ∆T | 24.5
77 | 93 | 1253 | 64 | LDB | 52.5
77 | 93 | 1253 | 64 | LWB | 52.3
77 | 93 | 1253 | 64 | kW | 4.46
80 | 93 | 1253 | 67 | MBh | 48
80 | 93 | 1253 | 67 | S/T | 0.729
80 | 93 | 1253 | 67 | ∆T | 25.9
80 | 93 | 1253 | 67 | LDB | 54.1
80 | 93 | 1253 | 67 | LWB | 54.1
80 | 93 | 1253 | 67 | kW | 5.26
84 | 93 | 1253 | 70 | MBh | 51.4
84 | 93 | 1253 | 70 | S/T | 0.71
84 | 93 | 1253 | 70 | ∆T | 27
84 | 93 | 1253 | 70 | LDB | 57
84 | 93 | 1253 | 70 | LWB | 57
84 | 93 | 1253 | 70 | kW | 5.78
86 | 93 | 1253 | 72 | MBh | 52
86 | 93 | 1253 | 72 | S/T | 0.669
86 | 93 | 1253 | 72 | ∆T | 25.7
86 | 93 | 1253 | 72 | LDB | 60.3
86 | 93 | 1253 | 72 | LWB | 60
86 | 93 | 1253 | 72 | kW | 5.81
90 | 93 | 1253 | 75 | MBh | 53
90 | 93 | 1253 | 75 | S/T | 0.632
90 | 93 | 1253 | 75 | ∆T | 24.8
90 | 93 | 1253 | 75 | LDB | 65.2
90 | 93 | 1253 | 75 | LWB | 63.6
90 | 93 | 1253 | 75 | kW | 5.85
68 | 95 | 1253 | 57 | MBh | 31.1
68 | 95 | 1253 | 57 | S/T | 0.833
68 | 95 | 1253 | 57 | ∆T | 19.1
68 | 95 | 1253 | 57 | LDB | 48.9
68 | 95 | 1253 | 57 | LWB | 47.4
68 | 95 | 1253 | 57 | kW | 2.95
72 | 95 | 1253 | 61 | MBh | 37.9
72 | 95 | 1253 | 61 | S/T | 0.797
72 | 95 | 1253 | 61 | ∆T | 22.3
72 | 95 | 1253 | 61 | LDB | 49.7
72 | 95 | 1253 | 61 | LWB | 49.7
72 | 95 | 1253 | 61 | kW | 3.86
77 | 95 | 1253 | 64 | MBh | 42.9
77 | 95 | 1253 | 64 | S/T | 0.772
77 | 95 | 1253 | 64 | ∆T | 24.5
77 | 95 | 1253 | 64 | LDB | 52.5
77 | 95 | 1253 | 64 | LWB | 52.3
77 | 95 | 1253 | 64 | kW | 4.62
80 | 95 | 1253 | 67 | MBh | 48
80 | 95 | 1253 | 67 | S/T | 0.729
80 | 95 | 1253 | 67 | ∆T | 25.9
80 | 95 | 1253 | 67 | LDB | 54.1
80 | 95 | 1253 | 67 | LWB | 54.1
80 | 95 | 1253 | 67 | kW | 5.45
84 | 95 | 1253 | 70 | MBh | 50.9
84 | 95 | 1253 | 70 | S/T | 0.711
84 | 95 | 1253 | 70 | ∆T | 26.8
84 | 95 | 1253 | 70 | LDB | 57.2
84 | 95 | 1253 | 70 | LWB | 57.2
84 | 95 | 1253 | 70 | kW | 5.9
86 | 95 | 1253 | 72 | MBh | 51.6
86 | 95 | 1253 | 72 | S/T | 0.669
86 | 95 | 1253 | 72 | ∆T | 25.5
86 | 95 | 1253 | 72 | LDB | 60.5
86 | 95 | 1253 | 72 | LWB | 60.1
86 | 95 | 1253 | 72 | kW | 5.92
90 | 95 | 1253 | 75 | MBh | 52.6
90 | 95 | 1253 | 75 | S/T | 0.631
90 | 95 | 1253 | 75 | ∆T | 24.5
90 | 95 | 1253 | 75 | LDB | 65.5
90 | 95 | 1253 | 75 | LWB | 63.7
90 | 95 | 1253 | 75 | kW | 5.97
68 | 99 | 1253 | 57 | MBh | 31.1
68 | 99 | 1253 | 57 | S/T | 0.833
68 | 99 | 1253 | 57 | ∆T | 19.1
68 | 99 | 1253 | 57 | LDB | 48.9
68 | 99 | 1253 | 57 | LWB | 47.4
68 | 99 | 1253 | 57 | kW | 3.15
72 | 99 | 1253 | 61 | MBh | 37.9
72 | 99 | 1253 | 61 | S/T | 0.797
72 | 99 | 1253 | 61 | ∆T | 22.3
72 | 99 | 1253 | 61 | LDB | 49.7
72 | 99 | 1253 | 61 | LWB | 49.7
72 | 99 | 1253 | 61 | kW | 4.13
77 | 99 | 1253 | 64 | MBh | 42.9
77 | 99 | 1253 | 64 | S/T | 0.772
77 | 99 | 1253 | 64 | ∆T | 24.5
77 | 99 | 1253 | 64 | LDB | 52.5
77 | 99 | 1253 | 64 | LWB | 52.3
77 | 99 | 1253 | 64 | kW | 4.95
80 | 99 | 1253 | 67 | MBh | 48
80 | 99 | 1253 | 67 | S/T | 0.729
80 | 99 | 1253 | 67 | ∆T | 25.9
80 | 99 | 1253 | 67 | LDB | 54.1
80 | 99 | 1253 | 67 | LWB | 54.1
80 | 99 | 1253 | 67 | kW | 5.86
84 | 99 | 1253 | 70 | MBh | 50
84 | 99 | 1253 | 70 | S/T | 0.71
84 | 99 | 1253 | 70 | ∆T | 26.2
84 | 99 | 1253 | 70 | LDB | 57.8
84 | 99 | 1253 | 70 | LWB | 57.8
84 | 99 | 1253 | 70 | kW | 6.13
86 | 99 | 1253 | 72 | MBh | 50.7
86 | 99 | 1253 | 72 | S/T | 0.669
86 | 99 | 1253 | 72 | ∆T | 25.1
86 | 99 | 1253 | 72 | LDB | 60.9
86 | 99 | 1253 | 72 | LWB | 60.3
86 | 99 | 1253 | 72 | kW | 6.16
90 | 99 | 1253 | 75 | MBh | 51.1
90 | 99 | 1253 | 75 | S/T | 0.63
90 | 99 | 1253 | 75 | ∆T | 23.8
90 | 99 | 1253 | 75 | LDB | 66.2
90 | 99 | 1253 | 75 | LWB | 64.1
90 | 99 | 1253 | 75 | kW | 6.17
68 | 103 | 1253 | 57 | MBh | 31.1
68 | 103 | 1253 | 57 | S/T | 0.833
68 | 103 | 1253 | 57 | ∆T | 19.1
68 | 103 | 1253 | 57 | LDB | 48.9
68 | 103 | 1253 | 57 | LWB | 47.4
68 | 103 | 1253 | 57 | kW | 3.37
72 | 103 | 1253 | 61 | MBh | 37.9
72 | 103 | 1253 | 61 | S/T | 0.797
72 | 103 | 1253 | 61 | ∆T | 22.3
72 | 103 | 1253 | 61 | LDB | 49.7
72 | 103 | 1253 | 61 | LWB | 49.7
72 | 103 | 1253 | 61 | kW | 4.42
77 | 103 | 1253 | 64 | MBh | 42.9
77 | 103 | 1253 | 64 | S/T | 0.772
77 | 103 | 1253 | 64 | ∆T | 24.5
77 | 103 | 1253 | 64 | LDB | 52.5
77 | 103 | 1253 | 64 | LWB | 52.3
77 | 103 | 1253 | 64 | kW | 5.31
80 | 103 | 1253 | 67 | MBh | 48
80 | 103 | 1253 | 67 | S/T | 0.729
80 | 103 | 1253 | 67 | ∆T | 25.9
80 | 103 | 1253 | 67 | LDB | 54.1
80 | 103 | 1253 | 67 | LWB | 54.1
80 | 103 | 1253 | 67 | kW | 6.29
84 | 103 | 1253 | 70 | MBh | 48.9
84 | 103 | 1253 | 70 | S/T | 0.71
84 | 103 | 1253 | 70 | ∆T | 25.6
84 | 103 | 1253 | 70 | LDB | 58.4
84 | 103 | 1253 | 70 | LWB | 58.2
84 | 103 | 1253 | 70 | kW | 6.35
86 | 103 | 1253 | 72 | MBh | 48.9
86 | 103 | 1253 | 72 | S/T | 0.669
86 | 103 | 1253 | 72 | ∆T | 24.2
86 | 103 | 1253 | 72 | LDB | 61.8
86 | 103 | 1253 | 72 | LWB | 60.8
86 | 103 | 1253 | 72 | kW | 6.35
90 | 103 | 1253 | 75 | MBh | 48.9
90 | 103 | 1253 | 75 | S/T | 0.632
90 | 103 | 1253 | 75 | ∆T | 22.8
90 | 103 | 1253 | 75 | LDB | 67.2
90 | 103 | 1253 | 75 | LWB | 64.6
90 | 103 | 1253 | 75 | kW | 6.35
68 | 106 | 1253 | 57 | MBh | 31.1
68 | 106 | 1253 | 57 | S/T | 0.833
68 | 106 | 1253 | 57 | ∆T | 19.1
68 | 106 | 1253 | 57 | LDB | 48.9
68 | 106 | 1253 | 57 | LWB | 47.4
68 | 106 | 1253 | 57 | kW | 3.54
72 | 106 | 1253 | 61 | MBh | 37.9
72 | 106 | 1253 | 61 | S/T | 0.797
72 | 106 | 1253 | 61 | ∆T | 22.3
72 | 106 | 1253 | 61 | LDB | 49.7
72 | 106 | 1253 | 61 | LWB | 49.7
72 | 106 | 1253 | 61 | kW | 4.65
77 | 106 | 1253 | 64 | MBh | 42.9
77 | 106 | 1253 | 64 | S/T | 0.772
77 | 106 | 1253 | 64 | ∆T | 24.5
77 | 106 | 1253 | 64 | LDB | 52.5
77 | 106 | 1253 | 64 | LWB | 52.3
77 | 106 | 1253 | 64 | kW | 5.6
80 | 106 | 1253 | 67 | MBh | 47.3
80 | 106 | 1253 | 67 | S/T | 0.729
80 | 106 | 1253 | 67 | ∆T | 25.5
80 | 106 | 1253 | 67 | LDB | 54.5
80 | 106 | 1253 | 67 | LWB | 54.5
80 | 106 | 1253 | 67 | kW | 6.47
84 | 106 | 1253 | 70 | MBh | 47.3
84 | 106 | 1253 | 70 | S/T | 0.71
84 | 106 | 1253 | 70 | ∆T | 24.8
84 | 106 | 1253 | 70 | LDB | 59.2
84 | 106 | 1253 | 70 | LWB | 58.7
84 | 106 | 1253 | 70 | kW | 6.47
86 | 106 | 1253 | 72 | MBh | 47.3
86 | 106 | 1253 | 72 | S/T | 0.668
86 | 106 | 1253 | 72 | ∆T | 23.4
86 | 106 | 1253 | 72 | LDB | 62.6
86 | 106 | 1253 | 72 | LWB | 61.2
86 | 106 | 1253 | 72 | kW | 6.47
90 | 106 | 1253 | 75 | MBh | 47.3
90 | 106 | 1253 | 75 | S/T | 0.63
90 | 106 | 1253 | 75 | ∆T | 22
90 | 106 | 1253 | 75 | LDB | 68
90 | 106 | 1253 | 75 | LWB | 65
90 | 106 | 1253 | 75 | kW | 6.47
68 | 110 | 1253 | 57 | MBh | 31.1
68 | 110 | 1253 | 57 | S/T | 0.833
68 | 110 | 1253 | 57 | ∆T | 19.1
68 | 110 | 1253 | 57 | LDB | 48.9
68 | 110 | 1253 | 57 | LWB | 47.4
68 | 110 | 1253 | 57 | kW | 3.78
72 | 110 | 1253 | 61 | MBh | 37.9
72 | 110 | 1253 | 61 | S/T | 0.797
72 | 110 | 1253 | 61 | ∆T | 22.3
72 | 110 | 1253 | 61 | LDB | 49.7
72 | 110 | 1253 | 61 | LWB | 49.7
72 | 110 | 1253 | 61 | kW | 4.98
77 | 110 | 1253 | 64 | MBh | 40.9
77 | 110 | 1253 | 64 | S/T | 0.77
77 | 110 | 1253 | 64 | ∆T | 23.3
77 | 110 | 1253 | 64 | LDB | 53.7
77 | 110 | 1253 | 64 | LWB | 52.9
77 | 110 | 1253 | 64 | kW | 5.58
80 | 110 | 1253 | 67 | MBh | 40.9
80 | 110 | 1253 | 67 | S/T | 0.731
80 | 110 | 1253 | 67 | ∆T | 22.1
80 | 110 | 1253 | 67 | LDB | 57.9
80 | 110 | 1253 | 67 | LWB | 56.6
80 | 110 | 1253 | 67 | kW | 5.58
84 | 110 | 1253 | 70 | MBh | 40.9
84 | 110 | 1253 | 70 | S/T | 0.711
84 | 110 | 1253 | 70 | ∆T | 21.5
84 | 110 | 1253 | 70 | LDB | 62.5
84 | 110 | 1253 | 70 | LWB | 60.4
84 | 110 | 1253 | 70 | kW | 5.58
86 | 110 | 1253 | 72 | MBh | 40.9
86 | 110 | 1253 | 72 | S/T | 0.67
86 | 110 | 1253 | 72 | ∆T | 20.2
86 | 110 | 1253 | 72 | LDB | 65.8
86 | 110 | 1253 | 72 | LWB | 62.8
86 | 110 | 1253 | 72 | kW | 5.58
90 | 110 | 1253 | 75 | MBh | 40.9
90 | 110 | 1253 | 75 | S/T | 0.633
90 | 110 | 1253 | 75 | ∆T | 19.1
90 | 110 | 1253 | 75 | LDB | 70.9
90 | 110 | 1253 | 75 | LWB | 66.5
90 | 110 | 1253 | 75 | kW | 5.58
68 | 115 | 1253 | 57 | MBh | 31.1
68 | 115 | 1253 | 57 | S/T | 0.833
68 | 115 | 1253 | 57 | ∆T | 19.1
68 | 115 | 1253 | 57 | LDB | 48.9
68 | 115 | 1253 | 57 | LWB | 47.4
68 | 115 | 1253 | 57 | kW | 4.1
72 | 115 | 1253 | 61 | MBh | 33.1
72 | 115 | 1253 | 61 | S/T | 0.795
72 | 115 | 1253 | 61 | ∆T | 19.4
72 | 115 | 1253 | 61 | LDB | 52.6
72 | 115 | 1253 | 61 | LWB | 51.6
72 | 115 | 1253 | 61 | kW | 4.46
77 | 115 | 1253 | 64 | MBh | 33.1
77 | 115 | 1253 | 64 | S/T | 0.767
77 | 115 | 1253 | 64 | ∆T | 18.8
77 | 115 | 1253 | 64 | LDB | 58.2
77 | 115 | 1253 | 64 | LWB | 55.2
77 | 115 | 1253 | 64 | kW | 4.46
80 | 115 | 1253 | 67 | MBh | 33.1
80 | 115 | 1253 | 67 | S/T | 0.728
80 | 115 | 1253 | 67 | ∆T | 17.8
80 | 115 | 1253 | 67 | LDB | 62.2
80 | 115 | 1253 | 67 | LWB | 58.8
80 | 115 | 1253 | 67 | kW | 4.46
84 | 115 | 1253 | 70 | MBh | 33.1
84 | 115 | 1253 | 70 | S/T | 0.71
84 | 115 | 1253 | 70 | ∆T | 17.4
84 | 115 | 1253 | 70 | LDB | 66.6
84 | 115 | 1253 | 70 | LWB | 62.4
84 | 115 | 1253 | 70 | kW | 4.46
86 | 115 | 1253 | 72 | MBh | 33.1
86 | 115 | 1253 | 72 | S/T | 0.668
86 | 115 | 1253 | 72 | ∆T | 16.3
86 | 115 | 1253 | 72 | LDB | 69.7
86 | 115 | 1253 | 72 | LWB | 64.7
86 | 115 | 1253 | 72 | kW | 4.46
90 | 115 | 1253 | 75 | MBh | 33.1
90 | 115 | 1253 | 75 | S/T | 0.631
90 | 115 | 1253 | 75 | ∆T | 15.4
90 | 115 | 1253 | 75 | LDB | 74.6
90 | 115 | 1253 | 75 | LWB | 68.2
90 | 115 | 1253 | 75 | kW | 4.46
68 | 118 | 1253 | 57 | MBh | 28.3
68 | 118 | 1253 | 57 | S/T | 0.834
68 | 118 | 1253 | 57 | ∆T | 17.4
68 | 118 | 1253 | 57 | LDB | 50.6
68 | 118 | 1253 | 57 | LWB | 48.3
68 | 118 | 1253 | 57 | kW | 3.79
72 | 118 | 1253 | 61 | MBh | 28.3
72 | 118 | 1253 | 61 | S/T | 0.799
72 | 118 | 1253 | 61 | ∆T | 16.7
72 | 118 | 1253 | 61 | LDB | 55.3
72 | 118 | 1253 | 61 | LWB | 53.1
72 | 118 | 1253 | 61 | kW | 3.79
77 | 118 | 1253 | 64 | MBh | 28.3
77 | 118 | 1253 | 64 | S/T | 0.77
77 | 118 | 1253 | 64 | ∆T | 16.1
77 | 118 | 1253 | 64 | LDB | 60.9
77 | 118 | 1253 | 64 | LWB | 56.6
77 | 118 | 1253 | 64 | kW | 3.79
80 | 118 | 1253 | 67 | MBh | 28.3
80 | 118 | 1253 | 67 | S/T | 0.728
80 | 118 | 1253 | 67 | ∆T | 15.2
80 | 118 | 1253 | 67 | LDB | 64.8
80 | 118 | 1253 | 67 | LWB | 60.1
80 | 118 | 1253 | 67 | kW | 3.79
84 | 118 | 1253 | 70 | MBh | 28.3
84 | 118 | 1253 | 70 | S/T | 0.71
84 | 118 | 1253 | 70 | ∆T | 14.9
84 | 118 | 1253 | 70 | LDB | 69.1
84 | 118 | 1253 | 70 | LWB | 63.5
84 | 118 | 1253 | 70 | kW | 3.79
86 | 118 | 1253 | 72 | MBh | 28.3
86 | 118 | 1253 | 72 | S/T | 0.671
86 | 118 | 1253 | 72 | ∆T | 14
86 | 118 | 1253 | 72 | LDB | 72
86 | 118 | 1253 | 72 | LWB | 65.8
86 | 118 | 1253 | 72 | kW | 3.79
90 | 118 | 1253 | 75 | MBh | 28.3
90 | 118 | 1253 | 75 | S/T | 0.633
90 | 118 | 1253 | 75 | ∆T | 13.2
90 | 118 | 1253 | 75 | LDB | 76.8
90 | 118 | 1253 | 75 | LWB | 69.3
90 | 118 | 1253 | 75 | kW | 3.79
68 | 122 | 1253 | 57 | MBh | 22
68 | 122 | 1253 | 57 | S/T | 0.832
68 | 122 | 1253 | 57 | ∆T | 13.5
68 | 122 | 1253 | 57 | LDB | 54.5
68 | 122 | 1253 | 57 | LWB | 50.4
68 | 122 | 1253 | 57 | kW | 2.91
72 | 122 | 1253 | 61 | MBh | 22
72 | 122 | 1253 | 61 | S/T | 0.795
72 | 122 | 1253 | 61 | ∆T | 12.9
72 | 122 | 1253 | 61 | LDB | 59.1
72 | 122 | 1253 | 61 | LWB | 54.9
72 | 122 | 1253 | 61 | kW | 2.91
77 | 122 | 1253 | 64 | MBh | 22
77 | 122 | 1253 | 64 | S/T | 0.768
77 | 122 | 1253 | 64 | ∆T | 12.5
77 | 122 | 1253 | 64 | LDB | 64.5
77 | 122 | 1253 | 64 | LWB | 58.3
77 | 122 | 1253 | 64 | kW | 2.91
80 | 122 | 1253 | 67 | MBh | 22
80 | 122 | 1253 | 67 | S/T | 0.727
80 | 122 | 1253 | 67 | ∆T | 11.8
80 | 122 | 1253 | 67 | LDB | 68.2
80 | 122 | 1253 | 67 | LWB | 61.7
80 | 122 | 1253 | 67 | kW | 2.91
84 | 122 | 1253 | 70 | MBh | 22
84 | 122 | 1253 | 70 | S/T | 0.709
84 | 122 | 1253 | 70 | ∆T | 11.5
84 | 122 | 1253 | 70 | LDB | 72.5
84 | 122 | 1253 | 70 | LWB | 65.1
84 | 122 | 1253 | 70 | kW | 2.91
86 | 122 | 1253 | 72 | MBh | 22
86 | 122 | 1253 | 72 | S/T | 0.668
86 | 122 | 1253 | 72 | ∆T | 10.9
86 | 122 | 1253 | 72 | LDB | 75.1
86 | 122 | 1253 | 72 | LWB | 67.3
86 | 122 | 1253 | 72 | kW | 2.91
90 | 122 | 1253 | 75 | MBh | 22
90 | 122 | 1253 | 75 | S/T | 0.632
90 | 122 | 1253 | 75 | ∆T | 10.3
90 | 122 | 1253 | 75 | LDB | 79.7
90 | 122 | 1253 | 75 | LWB | 70.6
90 | 122 | 1253 | 75 | kW | 2.91

## RZA18AAVJU - FBA18AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 635 | 57 | MBh | 11.7 | 64 | 60 | 61 | 24 | 2.12
68 | 23 | 635 | 57 | S/T | 0.957 | 64 | 60 | 65 | 22.2 | 1.94
68 | 23 | 635 | 57 | ∆T | 16.3 | 64 | 60 | 68 | 20.9 | 1.81
68 | 23 | 635 | 57 | LDB | 51.7 | 64 | 60 | 70 | 20 | 1.72
68 | 23 | 635 | 57 | LWB | 50 | 64 | 60 | 72 | 19.1 | 1.62
68 | 23 | 635 | 57 | kW | 0.39 | 64 | 60 | 75 | 17.8 | 1.49
72 | 23 | 635 | 61 | MBh | 14.2 | 60 | 56 | 61 | 24 | 2.2
72 | 23 | 635 | 61 | S/T | 0.908 | 60 | 56 | 65 | 22.2 | 2.02
72 | 23 | 635 | 61 | ∆T | 18.8 | 60 | 56 | 68 | 20.9 | 1.88
72 | 23 | 635 | 61 | LDB | 53.2 | 60 | 56 | 70 | 20 | 1.78
72 | 23 | 635 | 61 | LWB | 53.1 | 60 | 56 | 72 | 19.1 | 1.69
72 | 23 | 635 | 61 | kW | 0.48 | 60 | 56 | 75 | 17.8 | 1.55
77 | 23 | 635 | 64 | MBh | 16.1 | 57 | 53 | 61 | 24 | 2.26
77 | 23 | 635 | 64 | S/T | 0.87 | 57 | 53 | 65 | 22.2 | 2.08
77 | 23 | 635 | 64 | ∆T | 20.4 | 57 | 53 | 68 | 20.9 | 1.93
77 | 23 | 635 | 64 | LDB | 56.6 | 57 | 53 | 70 | 20 | 1.84
77 | 23 | 635 | 64 | LWB | 55.6 | 57 | 53 | 72 | 19.1 | 1.74
77 | 23 | 635 | 64 | kW | 0.55 | 57 | 53 | 75 | 17.8 | 1.6
80 | 23 | 635 | 67 | MBh | 18 | 54 | 50 | 61 | 24 | 2.33
80 | 23 | 635 | 67 | S/T | 0.822 | 54 | 50 | 65 | 22.2 | 2.14
80 | 23 | 635 | 67 | ∆T | 21.6 | 54 | 50 | 68 | 20.9 | 1.99
80 | 23 | 635 | 67 | LDB | 58.4 | 54 | 50 | 70 | 20 | 1.89
80 | 23 | 635 | 67 | LWB | 58.1 | 54 | 50 | 72 | 19.1 | 1.8
80 | 23 | 635 | 67 | kW | 0.63 | 54 | 50 | 75 | 17.8 | 1.65
84 | 23 | 635 | 70 | MBh | 19.9 | 51 | 47 | 61 | 24 | 2.4
84 | 23 | 635 | 70 | S/T | 0.779 | 51 | 47 | 65 | 22.2 | 2.2
84 | 23 | 635 | 70 | ∆T | 22.6 | 51 | 47 | 68 | 20.9 | 2.05
84 | 23 | 635 | 70 | LDB | 61.4 | 51 | 47 | 70 | 20 | 1.95
84 | 23 | 635 | 70 | LWB | 60.8 | 51 | 47 | 72 | 19.1 | 1.85
84 | 23 | 635 | 70 | kW | 0.7 | 51 | 47 | 75 | 17.8 | 1.7
86 | 23 | 635 | 72 | MBh | 21.2 | 47 | 43 | 61 | 24 | 2.49
86 | 23 | 635 | 72 | S/T | 0.736 | 47 | 43 | 65 | 22.2 | 2.29
86 | 23 | 635 | 72 | ∆T | 22.7 | 47 | 43 | 68 | 20.9 | 2.14
86 | 23 | 635 | 72 | LDB | 63.3 | 47 | 43 | 70 | 20 | 2.04
86 | 23 | 635 | 72 | LWB | 62.6 | 47 | 43 | 72 | 19.1 | 1.93
86 | 23 | 635 | 72 | kW | 0.76 | 47 | 43 | 75 | 17.8 | 1.78
90 | 23 | 635 | 75 | MBh | 23.1 | 44 | 40 | 61 | 24 | 2.57
90 | 23 | 635 | 75 | S/T | 0.606 | 44 | 40 | 65 | 22.2 | 2.37
90 | 23 | 635 | 75 | ∆T | 20.4 | 44 | 40 | 68 | 20.9 | 2.21
90 | 23 | 635 | 75 | LDB | 69.6 | 44 | 40 | 70 | 20 | 2.11
90 | 23 | 635 | 75 | LWB | 65.4 | 44 | 40 | 72 | 19.1 | 2
90 | 23 | 635 | 75 | kW | 0.84 | 44 | 40 | 75 | 17.8 | 1.84
68 | 30 | 635 | 57 | MBh | 11.7 | 39 | 36 | 61 | 24 | 2.68
68 | 30 | 635 | 57 | S/T | 0.957 | 39 | 36 | 65 | 22.2 | 2.47
68 | 30 | 635 | 57 | ∆T | 16.3 | 39 | 36 | 68 | 20.9 | 2.31
68 | 30 | 635 | 57 | LDB | 51.7 | 39 | 36 | 70 | 20 | 2.2
68 | 30 | 635 | 57 | LWB | 50 | 39 | 36 | 72 | 19.1 | 2.09
68 | 30 | 635 | 57 | kW | 0.4 | 39 | 36 | 75 | 17.8 | 1.93
72 | 30 | 635 | 61 | MBh | 14.2 | 35 | 32 | 61 | 24 | 2.8
72 | 30 | 635 | 61 | S/T | 0.908 | 35 | 32 | 65 | 22.2 | 2.58
72 | 30 | 635 | 61 | ∆T | 18.8 | 35 | 32 | 68 | 20.9 | 2.41
72 | 30 | 635 | 61 | LDB | 53.2 | 35 | 32 | 70 | 20 | 2.3
72 | 30 | 635 | 61 | LWB | 53.1 | 35 | 32 | 72 | 19.1 | 2.19
72 | 30 | 635 | 61 | kW | 0.5 | 35 | 32 | 75 | 17.8 | 2.02
77 | 30 | 635 | 64 | MBh | 16.1 | 30 | 28 | 61 | 24 | 2.92
77 | 30 | 635 | 64 | S/T | 0.87 | 30 | 28 | 65 | 22.2 | 2.7
77 | 30 | 635 | 64 | ∆T | 20.4 | 30 | 28 | 68 | 20.9 | 2.53
77 | 30 | 635 | 64 | LDB | 56.6 | 30 | 28 | 70 | 20 | 2.41
77 | 30 | 635 | 64 | LWB | 55.6 | 30 | 28 | 72 | 19.1 | 2.3
77 | 30 | 635 | 64 | kW | 0.57 | 30 | 28 | 75 | 17.8 | 2.12
80 | 30 | 635 | 67 | MBh | 18 | 26 | 24 | 61 | 24 | 3.06
80 | 30 | 635 | 67 | S/T | 0.822 | 26 | 24 | 65 | 22.2 | 2.83
80 | 30 | 635 | 67 | ∆T | 21.6 | 26 | 24 | 68 | 20.9 | 2.65
80 | 30 | 635 | 67 | LDB | 58.4 | 26 | 24 | 70 | 20 | 2.53
80 | 30 | 635 | 67 | LWB | 58.1 | 26 | 24 | 72 | 19.1 | 2.41
80 | 30 | 635 | 67 | kW | 0.65 | 26 | 24 | 75 | 17.8 | 2.23
84 | 30 | 635 | 70 | MBh | 19.9 | 22 | 20 | 61 | 24 | 3.08
84 | 30 | 635 | 70 | S/T | 0.779 | 22 | 20 | 65 | 22.2 | 2.97
84 | 30 | 635 | 70 | ∆T | 22.6 | 22 | 20 | 68 | 20.9 | 2.79
84 | 30 | 635 | 70 | LDB | 61.4 | 22 | 20 | 70 | 20 | 2.66
84 | 30 | 635 | 70 | LWB | 60.8 | 22 | 20 | 72 | 19.1 | 2.54
84 | 30 | 635 | 70 | kW | 0.73 | 22 | 20 | 75 | 17.8 | 2.35
86 | 30 | 635 | 72 | MBh | 21.2 | 19 | 18 | 61 | 24 | 3.06
86 | 30 | 635 | 72 | S/T | 0.736 | 19 | 18 | 65 | 22.2 | 3.04
86 | 30 | 635 | 72 | ∆T | 22.7 | 19 | 18 | 68 | 20.9 | 2.86
86 | 30 | 635 | 72 | LDB | 63.3 | 19 | 18 | 70 | 20 | 2.73
86 | 30 | 635 | 72 | LWB | 62.6 | 19 | 18 | 72 | 19.1 | 2.6
86 | 30 | 635 | 72 | kW | 0.78 | 19 | 18 | 75 | 17.8 | 2.41
90 | 30 | 635 | 75 | MBh | 23.1 | 17 | 16 | 61 | 24 | 3.03
90 | 30 | 635 | 75 | S/T | 0.606 | 17 | 16 | 65 | 22.2 | 3.09
90 | 30 | 635 | 75 | ∆T | 20.4 | 17 | 16 | 68 | 20.9 | 2.95
90 | 30 | 635 | 75 | LDB | 69.6 | 17 | 16 | 70 | 20 | 2.82
90 | 30 | 635 | 75 | LWB | 65.4 | 17 | 16 | 72 | 19.1 | 2.69
90 | 30 | 635 | 75 | kW | 0.86 | 17 | 16 | 75 | 17.8 | 2.49
68 | 40 | 635 | 57 | MBh | 11.7 | 15 | 14 | 61 | 24 | 3.02
68 | 40 | 635 | 57 | S/T | 0.957 | 15 | 14 | 65 | 22.2 | 3.07
68 | 40 | 635 | 57 | ∆T | 16.3 | 15 | 14 | 68 | 20.9 | 3.01
68 | 40 | 635 | 57 | LDB | 51.7 | 15 | 14 | 70 | 20 | 2.88
68 | 40 | 635 | 57 | LWB | 50 | 15 | 14 | 72 | 19.1 | 2.75
68 | 40 | 635 | 57 | kW | 0.42 | 15 | 14 | 75 | 17.8 | 2.55
72 | 40 | 635 | 61 | MBh | 14.2 | 13 | 12 | 61 | 24 | 3
72 | 40 | 635 | 61 | S/T | 0.908 | 13 | 12 | 65 | 22.2 | 3.05
72 | 40 | 635 | 61 | ∆T | 18.8 | 13 | 12 | 68 | 20.9 | 3.09
72 | 40 | 635 | 61 | LDB | 53.2 | 13 | 12 | 70 | 20 | 2.96
72 | 40 | 635 | 61 | LWB | 53.1 | 13 | 12 | 72 | 19.1 | 2.82
72 | 40 | 635 | 61 | kW | 0.52 | 13 | 12 | 75 | 17.8 | 2.62
77 | 40 | 635 | 64 | MBh | 16.1 | 10 | 9 | 61 | 22.5 | 2.96
77 | 40 | 635 | 64 | S/T | 0.87 | 10 | 9 | 65 | 22.2 | 3.02
77 | 40 | 635 | 64 | ∆T | 20.4 | 10 | 9 | 68 | 20.9 | 3.06
77 | 40 | 635 | 64 | LDB | 56.6 | 10 | 9 | 70 | 20 | 3.09
77 | 40 | 635 | 64 | LWB | 55.6 | 10 | 9 | 72 | 19.1 | 2.97
77 | 40 | 635 | 64 | kW | 0.6 | 10 | 9 | 75 | 17.8 | 2.75
80 | 40 | 635 | 67 | MBh | 18 | 6 | 5 | 61 | 21.1 | 2.91
80 | 40 | 635 | 67 | S/T | 0.822 | 6 | 5 | 65 | 21.1 | 2.98
80 | 40 | 635 | 67 | ∆T | 21.6 | 6 | 5 | 68 | 20.9 | 3.02
80 | 40 | 635 | 67 | LDB | 58.4 | 6 | 5 | 70 | 20 | 3.05
80 | 40 | 635 | 67 | LWB | 58.1 | 6 | 5 | 72 | 19.1 | 3.08
80 | 40 | 635 | 67 | kW | 0.68 | 6 | 5 | 75 | 17.8 | 2.9
84 | 40 | 635 | 70 | MBh | 19.9 | -2 | -2 | 61 | 18.1 | 2.81
84 | 40 | 635 | 70 | S/T | 0.779 | -2 | -2 | 65 | 18.1 | 2.88
84 | 40 | 635 | 70 | ∆T | 22.6 | -2 | -2 | 68 | 18.1 | 2.93
84 | 40 | 635 | 70 | LDB | 61.4 | -2 | -2 | 70 | 18.1 | 2.96
84 | 40 | 635 | 70 | LWB | 60.8 | -2 | -2 | 72 | 18.1 | 3
84 | 40 | 635 | 70 | kW | 0.76 | -2 | -2 | 75 | 17.8 | 3.05
86 | 40 | 635 | 72 | MBh | 21.2 | -4 | -4 | 61 | 17.3 | 2.78
86 | 40 | 635 | 72 | S/T | 0.736 | -4 | -4 | 65 | 17.3 | 2.85
86 | 40 | 635 | 72 | ∆T | 22.7 | -4 | -4 | 68 | 17.3 | 2.9
86 | 40 | 635 | 72 | LDB | 63.3 | -4 | -4 | 70 | 17.3 | 2.94
86 | 40 | 635 | 72 | LWB | 62.6 | -4 | -4 | 72 | 17.3 | 2.97
86 | 40 | 635 | 72 | kW | 0.82 | -4 | -4 | 75 | 17.3 | 3.03
90 | 40 | 635 | 75 | MBh | 23.1
90 | 40 | 635 | 75 | S/T | 0.606
90 | 40 | 635 | 75 | ∆T | 20.4
90 | 40 | 635 | 75 | LDB | 69.6
90 | 40 | 635 | 75 | LWB | 65.4
90 | 40 | 635 | 75 | kW | 0.91
68 | 50 | 635 | 57 | MBh | 11.7
68 | 50 | 635 | 57 | S/T | 0.957
68 | 50 | 635 | 57 | ∆T | 16.3
68 | 50 | 635 | 57 | LDB | 51.7
68 | 50 | 635 | 57 | LWB | 50
68 | 50 | 635 | 57 | kW | 0.44
72 | 50 | 635 | 61 | MBh | 14.2
72 | 50 | 635 | 61 | S/T | 0.908
72 | 50 | 635 | 61 | ∆T | 18.8
72 | 50 | 635 | 61 | LDB | 53.2
72 | 50 | 635 | 61 | LWB | 53.1
72 | 50 | 635 | 61 | kW | 0.55
77 | 50 | 635 | 64 | MBh | 16.1
77 | 50 | 635 | 64 | S/T | 0.87
77 | 50 | 635 | 64 | ∆T | 20.4
77 | 50 | 635 | 64 | LDB | 56.6
77 | 50 | 635 | 64 | LWB | 55.6
77 | 50 | 635 | 64 | kW | 0.63
80 | 50 | 635 | 67 | MBh | 18
80 | 50 | 635 | 67 | S/T | 0.822
80 | 50 | 635 | 67 | ∆T | 21.6
80 | 50 | 635 | 67 | LDB | 58.4
80 | 50 | 635 | 67 | LWB | 58.1
80 | 50 | 635 | 67 | kW | 0.72
84 | 50 | 635 | 70 | MBh | 19.9
84 | 50 | 635 | 70 | S/T | 0.779
84 | 50 | 635 | 70 | ∆T | 22.6
84 | 50 | 635 | 70 | LDB | 61.4
84 | 50 | 635 | 70 | LWB | 60.8
84 | 50 | 635 | 70 | kW | 0.8
86 | 50 | 635 | 72 | MBh | 21.2
86 | 50 | 635 | 72 | S/T | 0.736
86 | 50 | 635 | 72 | ∆T | 22.7
86 | 50 | 635 | 72 | LDB | 63.3
86 | 50 | 635 | 72 | LWB | 62.6
86 | 50 | 635 | 72 | kW | 0.86
90 | 50 | 635 | 75 | MBh | 23.1
90 | 50 | 635 | 75 | S/T | 0.606
90 | 50 | 635 | 75 | ∆T | 20.4
90 | 50 | 635 | 75 | LDB | 69.6
90 | 50 | 635 | 75 | LWB | 65.4
90 | 50 | 635 | 75 | kW | 0.95
68 | 54 | 635 | 57 | MBh | 11.7
68 | 54 | 635 | 57 | S/T | 0.957
68 | 54 | 635 | 57 | ∆T | 16.3
68 | 54 | 635 | 57 | LDB | 51.7
68 | 54 | 635 | 57 | LWB | 50
68 | 54 | 635 | 57 | kW | 0.45
72 | 54 | 635 | 61 | MBh | 14.2
72 | 54 | 635 | 61 | S/T | 0.908
72 | 54 | 635 | 61 | ∆T | 18.8
72 | 54 | 635 | 61 | LDB | 53.2
72 | 54 | 635 | 61 | LWB | 53.1
72 | 54 | 635 | 61 | kW | 0.56
77 | 54 | 635 | 64 | MBh | 16.1
77 | 54 | 635 | 64 | S/T | 0.87
77 | 54 | 635 | 64 | ∆T | 20.4
77 | 54 | 635 | 64 | LDB | 56.6
77 | 54 | 635 | 64 | LWB | 55.6
77 | 54 | 635 | 64 | kW | 0.64
80 | 54 | 635 | 67 | MBh | 18
80 | 54 | 635 | 67 | S/T | 0.822
80 | 54 | 635 | 67 | ∆T | 21.6
80 | 54 | 635 | 67 | LDB | 58.4
80 | 54 | 635 | 67 | LWB | 58.1
80 | 54 | 635 | 67 | kW | 0.73
84 | 54 | 635 | 70 | MBh | 19.9
84 | 54 | 635 | 70 | S/T | 0.779
84 | 54 | 635 | 70 | ∆T | 22.6
84 | 54 | 635 | 70 | LDB | 61.4
84 | 54 | 635 | 70 | LWB | 60.8
84 | 54 | 635 | 70 | kW | 0.82
86 | 54 | 635 | 72 | MBh | 21.2
86 | 54 | 635 | 72 | S/T | 0.736
86 | 54 | 635 | 72 | ∆T | 22.7
86 | 54 | 635 | 72 | LDB | 63.3
86 | 54 | 635 | 72 | LWB | 62.6
86 | 54 | 635 | 72 | kW | 0.88
90 | 54 | 635 | 75 | MBh | 23.1
90 | 54 | 635 | 75 | S/T | 0.606
90 | 54 | 635 | 75 | ∆T | 20.4
90 | 54 | 635 | 75 | LDB | 69.6
90 | 54 | 635 | 75 | LWB | 65.4
90 | 54 | 635 | 75 | kW | 0.97
68 | 58 | 635 | 57 | MBh | 11.7
68 | 58 | 635 | 57 | S/T | 0.957
68 | 58 | 635 | 57 | ∆T | 16.3
68 | 58 | 635 | 57 | LDB | 51.7
68 | 58 | 635 | 57 | LWB | 50
68 | 58 | 635 | 57 | kW | 0.46
72 | 58 | 635 | 61 | MBh | 14.2
72 | 58 | 635 | 61 | S/T | 0.908
72 | 58 | 635 | 61 | ∆T | 18.8
72 | 58 | 635 | 61 | LDB | 53.2
72 | 58 | 635 | 61 | LWB | 53.1
72 | 58 | 635 | 61 | kW | 0.57
77 | 58 | 635 | 64 | MBh | 16.1
77 | 58 | 635 | 64 | S/T | 0.87
77 | 58 | 635 | 64 | ∆T | 20.4
77 | 58 | 635 | 64 | LDB | 56.6
77 | 58 | 635 | 64 | LWB | 55.6
77 | 58 | 635 | 64 | kW | 0.66
80 | 58 | 635 | 67 | MBh | 18
80 | 58 | 635 | 67 | S/T | 0.822
80 | 58 | 635 | 67 | ∆T | 21.6
80 | 58 | 635 | 67 | LDB | 58.4
80 | 58 | 635 | 67 | LWB | 58.1
80 | 58 | 635 | 67 | kW | 0.75
84 | 58 | 635 | 70 | MBh | 19.9
84 | 58 | 635 | 70 | S/T | 0.779
84 | 58 | 635 | 70 | ∆T | 22.6
84 | 58 | 635 | 70 | LDB | 61.4
84 | 58 | 635 | 70 | LWB | 60.8
84 | 58 | 635 | 70 | kW | 0.84
86 | 58 | 635 | 72 | MBh | 21.2
86 | 58 | 635 | 72 | S/T | 0.736
86 | 58 | 635 | 72 | ∆T | 22.7
86 | 58 | 635 | 72 | LDB | 63.3
86 | 58 | 635 | 72 | LWB | 62.6
86 | 58 | 635 | 72 | kW | 0.9
90 | 58 | 635 | 75 | MBh | 22.8
90 | 58 | 635 | 75 | S/T | 0.61
90 | 58 | 635 | 75 | ∆T | 20.3
90 | 58 | 635 | 75 | LDB | 69.7
90 | 58 | 635 | 75 | LWB | 65.5
90 | 58 | 635 | 75 | kW | 0.98
68 | 62 | 635 | 57 | MBh | 11.7
68 | 62 | 635 | 57 | S/T | 0.957
68 | 62 | 635 | 57 | ∆T | 16.3
68 | 62 | 635 | 57 | LDB | 51.7
68 | 62 | 635 | 57 | LWB | 50
68 | 62 | 635 | 57 | kW | 0.47
72 | 62 | 635 | 61 | MBh | 14.2
72 | 62 | 635 | 61 | S/T | 0.908
72 | 62 | 635 | 61 | ∆T | 18.8
72 | 62 | 635 | 61 | LDB | 53.2
72 | 62 | 635 | 61 | LWB | 53.1
72 | 62 | 635 | 61 | kW | 0.58
77 | 62 | 635 | 64 | MBh | 16.1
77 | 62 | 635 | 64 | S/T | 0.87
77 | 62 | 635 | 64 | ∆T | 20.4
77 | 62 | 635 | 64 | LDB | 56.6
77 | 62 | 635 | 64 | LWB | 55.6
77 | 62 | 635 | 64 | kW | 0.67
80 | 62 | 635 | 67 | MBh | 18
80 | 62 | 635 | 67 | S/T | 0.822
80 | 62 | 635 | 67 | ∆T | 21.6
80 | 62 | 635 | 67 | LDB | 58.4
80 | 62 | 635 | 67 | LWB | 58.1
80 | 62 | 635 | 67 | kW | 0.76
84 | 62 | 635 | 70 | MBh | 19.9
84 | 62 | 635 | 70 | S/T | 0.779
84 | 62 | 635 | 70 | ∆T | 22.6
84 | 62 | 635 | 70 | LDB | 61.4
84 | 62 | 635 | 70 | LWB | 60.8
84 | 62 | 635 | 70 | kW | 0.86
86 | 62 | 635 | 72 | MBh | 21.2
86 | 62 | 635 | 72 | S/T | 0.736
86 | 62 | 635 | 72 | ∆T | 22.7
86 | 62 | 635 | 72 | LDB | 63.3
86 | 62 | 635 | 72 | LWB | 62.6
86 | 62 | 635 | 72 | kW | 0.92
90 | 62 | 635 | 75 | MBh | 22.5
90 | 62 | 635 | 75 | S/T | 0.609
90 | 62 | 635 | 75 | ∆T | 20
90 | 62 | 635 | 75 | LDB | 70
90 | 62 | 635 | 75 | LWB | 65.7
90 | 62 | 635 | 75 | kW | 0.97
68 | 66 | 635 | 57 | MBh | 11.7
68 | 66 | 635 | 57 | S/T | 0.957
68 | 66 | 635 | 57 | ∆T | 16.3
68 | 66 | 635 | 57 | LDB | 51.7
68 | 66 | 635 | 57 | LWB | 50
68 | 66 | 635 | 57 | kW | 0.48
72 | 66 | 635 | 61 | MBh | 14.2
72 | 66 | 635 | 61 | S/T | 0.908
72 | 66 | 635 | 61 | ∆T | 18.8
72 | 66 | 635 | 61 | LDB | 53.2
72 | 66 | 635 | 61 | LWB | 53.1
72 | 66 | 635 | 61 | kW | 0.59
77 | 66 | 635 | 64 | MBh | 16.1
77 | 66 | 635 | 64 | S/T | 0.87
77 | 66 | 635 | 64 | ∆T | 20.4
77 | 66 | 635 | 64 | LDB | 56.6
77 | 66 | 635 | 64 | LWB | 55.6
77 | 66 | 635 | 64 | kW | 0.68
80 | 66 | 635 | 67 | MBh | 18
80 | 66 | 635 | 67 | S/T | 0.822
80 | 66 | 635 | 67 | ∆T | 21.6
80 | 66 | 635 | 67 | LDB | 58.4
80 | 66 | 635 | 67 | LWB | 58.1
80 | 66 | 635 | 67 | kW | 0.78
84 | 66 | 635 | 70 | MBh | 19.9
84 | 66 | 635 | 70 | S/T | 0.779
84 | 66 | 635 | 70 | ∆T | 22.6
84 | 66 | 635 | 70 | LDB | 61.4
84 | 66 | 635 | 70 | LWB | 60.8
84 | 66 | 635 | 70 | kW | 0.87
86 | 66 | 635 | 72 | MBh | 21.2
86 | 66 | 635 | 72 | S/T | 0.736
86 | 66 | 635 | 72 | ∆T | 22.7
86 | 66 | 635 | 72 | LDB | 63.3
86 | 66 | 635 | 72 | LWB | 62.6
86 | 66 | 635 | 72 | kW | 0.94
90 | 66 | 635 | 75 | MBh | 22.2
90 | 66 | 635 | 75 | S/T | 0.608
90 | 66 | 635 | 75 | ∆T | 19.7
90 | 66 | 635 | 75 | LDB | 70.3
90 | 66 | 635 | 75 | LWB | 65.8
90 | 66 | 635 | 75 | kW | 0.96
68 | 70 | 635 | 57 | MBh | 11.7
68 | 70 | 635 | 57 | S/T | 0.957
68 | 70 | 635 | 57 | ∆T | 16.3
68 | 70 | 635 | 57 | LDB | 51.7
68 | 70 | 635 | 57 | LWB | 50
68 | 70 | 635 | 57 | kW | 0.49
72 | 70 | 635 | 61 | MBh | 14.2
72 | 70 | 635 | 61 | S/T | 0.908
72 | 70 | 635 | 61 | ∆T | 18.8
72 | 70 | 635 | 61 | LDB | 53.2
72 | 70 | 635 | 61 | LWB | 53.1
72 | 70 | 635 | 61 | kW | 0.61
77 | 70 | 635 | 64 | MBh | 16.1
77 | 70 | 635 | 64 | S/T | 0.87
77 | 70 | 635 | 64 | ∆T | 20.4
77 | 70 | 635 | 64 | LDB | 56.6
77 | 70 | 635 | 64 | LWB | 55.6
77 | 70 | 635 | 64 | kW | 0.7
80 | 70 | 635 | 67 | MBh | 18
80 | 70 | 635 | 67 | S/T | 0.822
80 | 70 | 635 | 67 | ∆T | 21.6
80 | 70 | 635 | 67 | LDB | 58.4
80 | 70 | 635 | 67 | LWB | 58.1
80 | 70 | 635 | 67 | kW | 0.8
84 | 70 | 635 | 70 | MBh | 19.9
84 | 70 | 635 | 70 | S/T | 0.779
84 | 70 | 635 | 70 | ∆T | 22.6
84 | 70 | 635 | 70 | LDB | 61.4
84 | 70 | 635 | 70 | LWB | 60.8
84 | 70 | 635 | 70 | kW | 0.89
86 | 70 | 635 | 72 | MBh | 21.2
86 | 70 | 635 | 72 | S/T | 0.736
86 | 70 | 635 | 72 | ∆T | 22.7
86 | 70 | 635 | 72 | LDB | 63.3
86 | 70 | 635 | 72 | LWB | 62.6
86 | 70 | 635 | 72 | kW | 0.96
90 | 70 | 635 | 75 | MBh | 21.8
90 | 70 | 635 | 75 | S/T | 0.606
90 | 70 | 635 | 75 | ∆T | 19.2
90 | 70 | 635 | 75 | LDB | 70.8
90 | 70 | 635 | 75 | LWB | 66
90 | 70 | 635 | 75 | kW | 0.96
68 | 72 | 635 | 57 | MBh | 11.7
68 | 72 | 635 | 57 | S/T | 0.957
68 | 72 | 635 | 57 | ∆T | 16.3
68 | 72 | 635 | 57 | LDB | 51.7
68 | 72 | 635 | 57 | LWB | 50
68 | 72 | 635 | 57 | kW | 0.49
72 | 72 | 635 | 61 | MBh | 14.2
72 | 72 | 635 | 61 | S/T | 0.908
72 | 72 | 635 | 61 | ∆T | 18.8
72 | 72 | 635 | 61 | LDB | 53.2
72 | 72 | 635 | 61 | LWB | 53.1
72 | 72 | 635 | 61 | kW | 0.61
77 | 72 | 635 | 64 | MBh | 16.1
77 | 72 | 635 | 64 | S/T | 0.87
77 | 72 | 635 | 64 | ∆T | 20.4
77 | 72 | 635 | 64 | LDB | 56.6
77 | 72 | 635 | 64 | LWB | 55.6
77 | 72 | 635 | 64 | kW | 0.71
80 | 72 | 635 | 67 | MBh | 18
80 | 72 | 635 | 67 | S/T | 0.822
80 | 72 | 635 | 67 | ∆T | 21.6
80 | 72 | 635 | 67 | LDB | 58.4
80 | 72 | 635 | 67 | LWB | 58.1
80 | 72 | 635 | 67 | kW | 0.81
84 | 72 | 635 | 70 | MBh | 19.9
84 | 72 | 635 | 70 | S/T | 0.779
84 | 72 | 635 | 70 | ∆T | 22.6
84 | 72 | 635 | 70 | LDB | 61.4
84 | 72 | 635 | 70 | LWB | 60.8
84 | 72 | 635 | 70 | kW | 0.9
86 | 72 | 635 | 72 | MBh | 21.2
86 | 72 | 635 | 72 | S/T | 0.736
86 | 72 | 635 | 72 | ∆T | 22.7
86 | 72 | 635 | 72 | LDB | 63.3
86 | 72 | 635 | 72 | LWB | 62.6
86 | 72 | 635 | 72 | kW | 0.98
90 | 72 | 635 | 75 | MBh | 21.7
90 | 72 | 635 | 75 | S/T | 0.604
90 | 72 | 635 | 75 | ∆T | 19.1
90 | 72 | 635 | 75 | LDB | 70.9
90 | 72 | 635 | 75 | LWB | 66.1
90 | 72 | 635 | 75 | kW | 0.99
68 | 75 | 635 | 57 | MBh | 11.7
68 | 75 | 635 | 57 | S/T | 0.957
68 | 75 | 635 | 57 | ∆T | 16.3
68 | 75 | 635 | 57 | LDB | 51.7
68 | 75 | 635 | 57 | LWB | 50
68 | 75 | 635 | 57 | kW | 0.5
72 | 75 | 635 | 61 | MBh | 14.2
72 | 75 | 635 | 61 | S/T | 0.908
72 | 75 | 635 | 61 | ∆T | 18.8
72 | 75 | 635 | 61 | LDB | 53.2
72 | 75 | 635 | 61 | LWB | 53.1
72 | 75 | 635 | 61 | kW | 0.62
77 | 75 | 635 | 64 | MBh | 16.1
77 | 75 | 635 | 64 | S/T | 0.87
77 | 75 | 635 | 64 | ∆T | 20.4
77 | 75 | 635 | 64 | LDB | 56.6
77 | 75 | 635 | 64 | LWB | 55.6
77 | 75 | 635 | 64 | kW | 0.72
80 | 75 | 635 | 67 | MBh | 18
80 | 75 | 635 | 67 | S/T | 0.822
80 | 75 | 635 | 67 | ∆T | 21.6
80 | 75 | 635 | 67 | LDB | 58.4
80 | 75 | 635 | 67 | LWB | 58.1
80 | 75 | 635 | 67 | kW | 0.83
84 | 75 | 635 | 70 | MBh | 19.9
84 | 75 | 635 | 70 | S/T | 0.779
84 | 75 | 635 | 70 | ∆T | 22.6
84 | 75 | 635 | 70 | LDB | 61.4
84 | 75 | 635 | 70 | LWB | 60.8
84 | 75 | 635 | 70 | kW | 0.96
86 | 75 | 635 | 72 | MBh | 21
86 | 75 | 635 | 72 | S/T | 0.738
86 | 75 | 635 | 72 | ∆T | 22.6
86 | 75 | 635 | 72 | LDB | 63.4
86 | 75 | 635 | 72 | LWB | 62.7
86 | 75 | 635 | 72 | kW | 1.05
90 | 75 | 635 | 75 | MBh | 21.4
90 | 75 | 635 | 75 | S/T | 0.607
90 | 75 | 635 | 75 | ∆T | 19
90 | 75 | 635 | 75 | LDB | 71
90 | 75 | 635 | 75 | LWB | 66.2
90 | 75 | 635 | 75 | kW | 1.05
68 | 79 | 635 | 57 | MBh | 11.7
68 | 79 | 635 | 57 | S/T | 0.957
68 | 79 | 635 | 57 | ∆T | 16.3
68 | 79 | 635 | 57 | LDB | 51.7
68 | 79 | 635 | 57 | LWB | 50
68 | 79 | 635 | 57 | kW | 0.51
72 | 79 | 635 | 61 | MBh | 14.2
72 | 79 | 635 | 61 | S/T | 0.908
72 | 79 | 635 | 61 | ∆T | 18.8
72 | 79 | 635 | 61 | LDB | 53.2
72 | 79 | 635 | 61 | LWB | 53.1
72 | 79 | 635 | 61 | kW | 0.66
77 | 79 | 635 | 64 | MBh | 16.1
77 | 79 | 635 | 64 | S/T | 0.87
77 | 79 | 635 | 64 | ∆T | 20.4
77 | 79 | 635 | 64 | LDB | 56.6
77 | 79 | 635 | 64 | LWB | 55.6
77 | 79 | 635 | 64 | kW | 0.78
80 | 79 | 635 | 67 | MBh | 18
80 | 79 | 635 | 67 | S/T | 0.822
80 | 79 | 635 | 67 | ∆T | 21.6
80 | 79 | 635 | 67 | LDB | 58.4
80 | 79 | 635 | 67 | LWB | 58.1
80 | 79 | 635 | 67 | kW | 0.92
84 | 79 | 635 | 70 | MBh | 19.9
84 | 79 | 635 | 70 | S/T | 0.779
84 | 79 | 635 | 70 | ∆T | 22.6
84 | 79 | 635 | 70 | LDB | 61.4
84 | 79 | 635 | 70 | LWB | 60.8
84 | 79 | 635 | 70 | kW | 1.07
86 | 79 | 635 | 72 | MBh | 20.7
86 | 79 | 635 | 72 | S/T | 0.739
86 | 79 | 635 | 72 | ∆T | 22.3
86 | 79 | 635 | 72 | LDB | 63.7
86 | 79 | 635 | 72 | LWB | 62.8
86 | 79 | 635 | 72 | kW | 1.13
90 | 79 | 635 | 75 | MBh | 21.1
90 | 79 | 635 | 75 | S/T | 0.607
90 | 79 | 635 | 75 | ∆T | 18.7
90 | 79 | 635 | 75 | LDB | 71.3
90 | 79 | 635 | 75 | LWB | 66.3
90 | 79 | 635 | 75 | kW | 1.14
68 | 83 | 635 | 57 | MBh | 11.7
68 | 83 | 635 | 57 | S/T | 0.957
68 | 83 | 635 | 57 | ∆T | 16.3
68 | 83 | 635 | 57 | LDB | 51.7
68 | 83 | 635 | 57 | LWB | 50
68 | 83 | 635 | 57 | kW | 0.56
72 | 83 | 635 | 61 | MBh | 14.2
72 | 83 | 635 | 61 | S/T | 0.908
72 | 83 | 635 | 61 | ∆T | 18.8
72 | 83 | 635 | 61 | LDB | 53.2
72 | 83 | 635 | 61 | LWB | 53.1
72 | 83 | 635 | 61 | kW | 0.72
77 | 83 | 635 | 64 | MBh | 16.1
77 | 83 | 635 | 64 | S/T | 0.87
77 | 83 | 635 | 64 | ∆T | 20.4
77 | 83 | 635 | 64 | LDB | 56.6
77 | 83 | 635 | 64 | LWB | 55.6
77 | 83 | 635 | 64 | kW | 0.86
80 | 83 | 635 | 67 | MBh | 18
80 | 83 | 635 | 67 | S/T | 0.822
80 | 83 | 635 | 67 | ∆T | 21.6
80 | 83 | 635 | 67 | LDB | 58.4
80 | 83 | 635 | 67 | LWB | 58.1
80 | 83 | 635 | 67 | kW | 1.02
84 | 83 | 635 | 70 | MBh | 19.9
84 | 83 | 635 | 70 | S/T | 0.779
84 | 83 | 635 | 70 | ∆T | 22.6
84 | 83 | 635 | 70 | LDB | 61.4
84 | 83 | 635 | 70 | LWB | 60.8
84 | 83 | 635 | 70 | kW | 1.18
86 | 83 | 635 | 72 | MBh | 20.4
86 | 83 | 635 | 72 | S/T | 0.735
86 | 83 | 635 | 72 | ∆T | 21.9
86 | 83 | 635 | 72 | LDB | 64.1
86 | 83 | 635 | 72 | LWB | 63
86 | 83 | 635 | 72 | kW | 1.21
90 | 83 | 635 | 75 | MBh | 20.7
90 | 83 | 635 | 75 | S/T | 0.609
90 | 83 | 635 | 75 | ∆T | 18.4
90 | 83 | 635 | 75 | LDB | 71.6
90 | 83 | 635 | 75 | LWB | 66.5
90 | 83 | 635 | 75 | kW | 1.22
68 | 87 | 635 | 57 | MBh | 11.7
68 | 87 | 635 | 57 | S/T | 0.957
68 | 87 | 635 | 57 | ∆T | 16.3
68 | 87 | 635 | 57 | LDB | 51.7
68 | 87 | 635 | 57 | LWB | 50
68 | 87 | 635 | 57 | kW | 0.61
72 | 87 | 635 | 61 | MBh | 14.2
72 | 87 | 635 | 61 | S/T | 0.908
72 | 87 | 635 | 61 | ∆T | 18.8
72 | 87 | 635 | 61 | LDB | 53.2
72 | 87 | 635 | 61 | LWB | 53.1
72 | 87 | 635 | 61 | kW | 0.8
77 | 87 | 635 | 64 | MBh | 16.1
77 | 87 | 635 | 64 | S/T | 0.87
77 | 87 | 635 | 64 | ∆T | 20.4
77 | 87 | 635 | 64 | LDB | 56.6
77 | 87 | 635 | 64 | LWB | 55.6
77 | 87 | 635 | 64 | kW | 0.95
80 | 87 | 635 | 67 | MBh | 18
80 | 87 | 635 | 67 | S/T | 0.822
80 | 87 | 635 | 67 | ∆T | 21.6
80 | 87 | 635 | 67 | LDB | 58.4
80 | 87 | 635 | 67 | LWB | 58.1
80 | 87 | 635 | 67 | kW | 1.12
84 | 87 | 635 | 70 | MBh | 19.8
84 | 87 | 635 | 70 | S/T | 0.778
84 | 87 | 635 | 70 | ∆T | 22.5
84 | 87 | 635 | 70 | LDB | 61.5
84 | 87 | 635 | 70 | LWB | 60.8
84 | 87 | 635 | 70 | kW | 1.29
86 | 87 | 635 | 72 | MBh | 20
86 | 87 | 635 | 72 | S/T | 0.74
86 | 87 | 635 | 72 | ∆T | 21.6
86 | 87 | 635 | 72 | LDB | 64.4
86 | 87 | 635 | 72 | LWB | 63.2
86 | 87 | 635 | 72 | kW | 1.29
90 | 87 | 635 | 75 | MBh | 20.4
90 | 87 | 635 | 75 | S/T | 0.608
90 | 87 | 635 | 75 | ∆T | 18.1
90 | 87 | 635 | 75 | LDB | 71.9
90 | 87 | 635 | 75 | LWB | 66.6
90 | 87 | 635 | 75 | kW | 1.3
68 | 91 | 635 | 57 | MBh | 11.7
68 | 91 | 635 | 57 | S/T | 0.957
68 | 91 | 635 | 57 | ∆T | 16.3
68 | 91 | 635 | 57 | LDB | 51.7
68 | 91 | 635 | 57 | LWB | 50
68 | 91 | 635 | 57 | kW | 0.67
72 | 91 | 635 | 61 | MBh | 14.2
72 | 91 | 635 | 61 | S/T | 0.908
72 | 91 | 635 | 61 | ∆T | 18.8
72 | 91 | 635 | 61 | LDB | 53.2
72 | 91 | 635 | 61 | LWB | 53.1
72 | 91 | 635 | 61 | kW | 0.87
77 | 91 | 635 | 64 | MBh | 16.1
77 | 91 | 635 | 64 | S/T | 0.87
77 | 91 | 635 | 64 | ∆T | 20.4
77 | 91 | 635 | 64 | LDB | 56.6
77 | 91 | 635 | 64 | LWB | 55.6
77 | 91 | 635 | 64 | kW | 1.04
80 | 91 | 635 | 67 | MBh | 18
80 | 91 | 635 | 67 | S/T | 0.822
80 | 91 | 635 | 67 | ∆T | 21.6
80 | 91 | 635 | 67 | LDB | 58.4
80 | 91 | 635 | 67 | LWB | 58.1
80 | 91 | 635 | 67 | kW | 1.23
84 | 91 | 635 | 70 | MBh | 19.4
84 | 91 | 635 | 70 | S/T | 0.778
84 | 91 | 635 | 70 | ∆T | 22
84 | 91 | 635 | 70 | LDB | 62
84 | 91 | 635 | 70 | LWB | 61
84 | 91 | 635 | 70 | kW | 1.37
86 | 91 | 635 | 72 | MBh | 19.7
86 | 91 | 635 | 72 | S/T | 0.736
86 | 91 | 635 | 72 | ∆T | 21.1
86 | 91 | 635 | 72 | LDB | 64.9
86 | 91 | 635 | 72 | LWB | 63.3
86 | 91 | 635 | 72 | kW | 1.38
90 | 91 | 635 | 75 | MBh | 20.1
90 | 91 | 635 | 75 | S/T | 0.607
90 | 91 | 635 | 75 | ∆T | 17.8
90 | 91 | 635 | 75 | LDB | 72.2
90 | 91 | 635 | 75 | LWB | 66.8
90 | 91 | 635 | 75 | kW | 1.39
68 | 93 | 635 | 57 | MBh | 11.7
68 | 93 | 635 | 57 | S/T | 0.957
68 | 93 | 635 | 57 | ∆T | 16.3
68 | 93 | 635 | 57 | LDB | 51.7
68 | 93 | 635 | 57 | LWB | 50
68 | 93 | 635 | 57 | kW | 0.7
72 | 93 | 635 | 61 | MBh | 14.2
72 | 93 | 635 | 61 | S/T | 0.908
72 | 93 | 635 | 61 | ∆T | 18.8
72 | 93 | 635 | 61 | LDB | 53.2
72 | 93 | 635 | 61 | LWB | 53.1
72 | 93 | 635 | 61 | kW | 0.91
77 | 93 | 635 | 64 | MBh | 16.1
77 | 93 | 635 | 64 | S/T | 0.87
77 | 93 | 635 | 64 | ∆T | 20.4
77 | 93 | 635 | 64 | LDB | 56.6
77 | 93 | 635 | 64 | LWB | 55.6
77 | 93 | 635 | 64 | kW | 1.09
80 | 93 | 635 | 67 | MBh | 18
80 | 93 | 635 | 67 | S/T | 0.822
80 | 93 | 635 | 67 | ∆T | 21.6
80 | 93 | 635 | 67 | LDB | 58.4
80 | 93 | 635 | 67 | LWB | 58.1
80 | 93 | 635 | 67 | kW | 1.29
84 | 93 | 635 | 70 | MBh | 19.3
84 | 93 | 635 | 70 | S/T | 0.777
84 | 93 | 635 | 70 | ∆T | 21.9
84 | 93 | 635 | 70 | LDB | 62.1
84 | 93 | 635 | 70 | LWB | 61.1
84 | 93 | 635 | 70 | kW | 1.41
86 | 93 | 635 | 72 | MBh | 19.5
86 | 93 | 635 | 72 | S/T | 0.738
86 | 93 | 635 | 72 | ∆T | 21
86 | 93 | 635 | 72 | LDB | 65
86 | 93 | 635 | 72 | LWB | 63.4
86 | 93 | 635 | 72 | kW | 1.42
90 | 93 | 635 | 75 | MBh | 19.9
90 | 93 | 635 | 75 | S/T | 0.608
90 | 93 | 635 | 75 | ∆T | 17.6
90 | 93 | 635 | 75 | LDB | 72.4
90 | 93 | 635 | 75 | LWB | 66.9
90 | 93 | 635 | 75 | kW | 1.43
68 | 95 | 635 | 57 | MBh | 11.7
68 | 95 | 635 | 57 | S/T | 0.957
68 | 95 | 635 | 57 | ∆T | 16.3
68 | 95 | 635 | 57 | LDB | 51.7
68 | 95 | 635 | 57 | LWB | 50
68 | 95 | 635 | 57 | kW | 0.73
72 | 95 | 635 | 61 | MBh | 14.2
72 | 95 | 635 | 61 | S/T | 0.908
72 | 95 | 635 | 61 | ∆T | 18.8
72 | 95 | 635 | 61 | LDB | 53.2
72 | 95 | 635 | 61 | LWB | 53.1
72 | 95 | 635 | 61 | kW | 0.95
77 | 95 | 635 | 64 | MBh | 16.1
77 | 95 | 635 | 64 | S/T | 0.87
77 | 95 | 635 | 64 | ∆T | 20.4
77 | 95 | 635 | 64 | LDB | 56.6
77 | 95 | 635 | 64 | LWB | 55.6
77 | 95 | 635 | 64 | kW | 1.14
80 | 95 | 635 | 67 | MBh | 18
80 | 95 | 635 | 67 | S/T | 0.822
80 | 95 | 635 | 67 | ∆T | 21.6
80 | 95 | 635 | 67 | LDB | 58.4
80 | 95 | 635 | 67 | LWB | 58.1
80 | 95 | 635 | 67 | kW | 1.35
84 | 95 | 635 | 70 | MBh | 19.1
84 | 95 | 635 | 70 | S/T | 0.78
84 | 95 | 635 | 70 | ∆T | 21.7
84 | 95 | 635 | 70 | LDB | 62.3
84 | 95 | 635 | 70 | LWB | 61.2
84 | 95 | 635 | 70 | kW | 1.45
86 | 95 | 635 | 72 | MBh | 19.3
86 | 95 | 635 | 72 | S/T | 0.741
86 | 95 | 635 | 72 | ∆T | 20.9
86 | 95 | 635 | 72 | LDB | 65.1
86 | 95 | 635 | 72 | LWB | 63.5
86 | 95 | 635 | 72 | kW | 1.46
90 | 95 | 635 | 75 | MBh | 19.7
90 | 95 | 635 | 75 | S/T | 0.609
90 | 95 | 635 | 75 | ∆T | 17.5
90 | 95 | 635 | 75 | LDB | 72.5
90 | 95 | 635 | 75 | LWB | 67
90 | 95 | 635 | 75 | kW | 1.47
68 | 99 | 635 | 57 | MBh | 11.7
68 | 99 | 635 | 57 | S/T | 0.957
68 | 99 | 635 | 57 | ∆T | 16.3
68 | 99 | 635 | 57 | LDB | 51.7
68 | 99 | 635 | 57 | LWB | 50
68 | 99 | 635 | 57 | kW | 0.79
72 | 99 | 635 | 61 | MBh | 14.2
72 | 99 | 635 | 61 | S/T | 0.908
72 | 99 | 635 | 61 | ∆T | 18.8
72 | 99 | 635 | 61 | LDB | 53.2
72 | 99 | 635 | 61 | LWB | 53.1
72 | 99 | 635 | 61 | kW | 1.04
77 | 99 | 635 | 64 | MBh | 16.1
77 | 99 | 635 | 64 | S/T | 0.87
77 | 99 | 635 | 64 | ∆T | 20.4
77 | 99 | 635 | 64 | LDB | 56.6
77 | 99 | 635 | 64 | LWB | 55.6
77 | 99 | 635 | 64 | kW | 1.24
80 | 99 | 635 | 67 | MBh | 18
80 | 99 | 635 | 67 | S/T | 0.822
80 | 99 | 635 | 67 | ∆T | 21.6
80 | 99 | 635 | 67 | LDB | 58.4
80 | 99 | 635 | 67 | LWB | 58.1
80 | 99 | 635 | 67 | kW | 1.47
84 | 99 | 635 | 70 | MBh | 18.8
84 | 99 | 635 | 70 | S/T | 0.777
84 | 99 | 635 | 70 | ∆T | 21.3
84 | 99 | 635 | 70 | LDB | 62.7
84 | 99 | 635 | 70 | LWB | 61.3
84 | 99 | 635 | 70 | kW | 1.54
86 | 99 | 635 | 72 | MBh | 19
86 | 99 | 635 | 72 | S/T | 0.737
86 | 99 | 635 | 72 | ∆T | 20.4
86 | 99 | 635 | 72 | LDB | 65.6
86 | 99 | 635 | 72 | LWB | 63.6
86 | 99 | 635 | 72 | kW | 1.54
90 | 99 | 635 | 75 | MBh | 19.4
90 | 99 | 635 | 75 | S/T | 0.608
90 | 99 | 635 | 75 | ∆T | 17.2
90 | 99 | 635 | 75 | LDB | 72.8
90 | 99 | 635 | 75 | LWB | 67.1
90 | 99 | 635 | 75 | kW | 1.56
68 | 103 | 635 | 57 | MBh | 11.7
68 | 103 | 635 | 57 | S/T | 0.957
68 | 103 | 635 | 57 | ∆T | 16.3
68 | 103 | 635 | 57 | LDB | 51.7
68 | 103 | 635 | 57 | LWB | 50
68 | 103 | 635 | 57 | kW | 0.86
72 | 103 | 635 | 61 | MBh | 14.2
72 | 103 | 635 | 61 | S/T | 0.908
72 | 103 | 635 | 61 | ∆T | 18.8
72 | 103 | 635 | 61 | LDB | 53.2
72 | 103 | 635 | 61 | LWB | 53.1
72 | 103 | 635 | 61 | kW | 1.13
77 | 103 | 635 | 64 | MBh | 16.1
77 | 103 | 635 | 64 | S/T | 0.87
77 | 103 | 635 | 64 | ∆T | 20.4
77 | 103 | 635 | 64 | LDB | 56.6
77 | 103 | 635 | 64 | LWB | 55.6
77 | 103 | 635 | 64 | kW | 1.35
80 | 103 | 635 | 67 | MBh | 18
80 | 103 | 635 | 67 | S/T | 0.822
80 | 103 | 635 | 67 | ∆T | 21.6
80 | 103 | 635 | 67 | LDB | 58.4
80 | 103 | 635 | 67 | LWB | 58.1
80 | 103 | 635 | 67 | kW | 1.6
84 | 103 | 635 | 70 | MBh | 18.4
84 | 103 | 635 | 70 | S/T | 0.777
84 | 103 | 635 | 70 | ∆T | 20.9
84 | 103 | 635 | 70 | LDB | 63.1
84 | 103 | 635 | 70 | LWB | 61.5
84 | 103 | 635 | 70 | kW | 1.62
86 | 103 | 635 | 72 | MBh | 18.7
86 | 103 | 635 | 72 | S/T | 0.738
86 | 103 | 635 | 72 | ∆T | 20.1
86 | 103 | 635 | 72 | LDB | 65.9
86 | 103 | 635 | 72 | LWB | 63.8
86 | 103 | 635 | 72 | kW | 1.63
90 | 103 | 635 | 75 | MBh | 19
90 | 103 | 635 | 75 | S/T | 0.611
90 | 103 | 635 | 75 | ∆T | 16.9
90 | 103 | 635 | 75 | LDB | 73.1
90 | 103 | 635 | 75 | LWB | 67.3
90 | 103 | 635 | 75 | kW | 1.64
68 | 106 | 635 | 57 | MBh | 11.7
68 | 106 | 635 | 57 | S/T | 0.957
68 | 106 | 635 | 57 | ∆T | 16.3
68 | 106 | 635 | 57 | LDB | 51.7
68 | 106 | 635 | 57 | LWB | 50
68 | 106 | 635 | 57 | kW | 0.91
72 | 106 | 635 | 61 | MBh | 14.2
72 | 106 | 635 | 61 | S/T | 0.908
72 | 106 | 635 | 61 | ∆T | 18.8
72 | 106 | 635 | 61 | LDB | 53.2
72 | 106 | 635 | 61 | LWB | 53.1
72 | 106 | 635 | 61 | kW | 1.2
77 | 106 | 635 | 64 | MBh | 16.1
77 | 106 | 635 | 64 | S/T | 0.87
77 | 106 | 635 | 64 | ∆T | 20.4
77 | 106 | 635 | 64 | LDB | 56.6
77 | 106 | 635 | 64 | LWB | 55.6
77 | 106 | 635 | 64 | kW | 1.44
80 | 106 | 635 | 67 | MBh | 17.8
80 | 106 | 635 | 67 | S/T | 0.82
80 | 106 | 635 | 67 | ∆T | 21.3
80 | 106 | 635 | 67 | LDB | 58.7
80 | 106 | 635 | 67 | LWB | 58.2
80 | 106 | 635 | 67 | kW | 1.67
84 | 106 | 635 | 70 | MBh | 18.2
84 | 106 | 635 | 70 | S/T | 0.78
84 | 106 | 635 | 70 | ∆T | 20.7
84 | 106 | 635 | 70 | LDB | 63.3
84 | 106 | 635 | 70 | LWB | 61.6
84 | 106 | 635 | 70 | kW | 1.68
86 | 106 | 635 | 72 | MBh | 18.4
86 | 106 | 635 | 72 | S/T | 0.739
86 | 106 | 635 | 72 | ∆T | 19.8
86 | 106 | 635 | 72 | LDB | 66.2
86 | 106 | 635 | 72 | LWB | 63.9
86 | 106 | 635 | 72 | kW | 1.69
90 | 106 | 635 | 75 | MBh | 18.8
90 | 106 | 635 | 75 | S/T | 0.606
90 | 106 | 635 | 75 | ∆T | 16.6
90 | 106 | 635 | 75 | LDB | 73.4
90 | 106 | 635 | 75 | LWB | 67.4
90 | 106 | 635 | 75 | kW | 1.71
68 | 110 | 635 | 57 | MBh | 11.7
68 | 110 | 635 | 57 | S/T | 0.957
68 | 110 | 635 | 57 | ∆T | 16.3
68 | 110 | 635 | 57 | LDB | 51.7
68 | 110 | 635 | 57 | LWB | 50
68 | 110 | 635 | 57 | kW | 0.99
72 | 110 | 635 | 61 | MBh | 14.2
72 | 110 | 635 | 61 | S/T | 0.908
72 | 110 | 635 | 61 | ∆T | 18.8
72 | 110 | 635 | 61 | LDB | 53.2
72 | 110 | 635 | 61 | LWB | 53.1
72 | 110 | 635 | 61 | kW | 1.3
77 | 110 | 635 | 64 | MBh | 16.1
77 | 110 | 635 | 64 | S/T | 0.87
77 | 110 | 635 | 64 | ∆T | 20.4
77 | 110 | 635 | 64 | LDB | 56.6
77 | 110 | 635 | 64 | LWB | 55.6
77 | 110 | 635 | 64 | kW | 1.57
80 | 110 | 635 | 67 | MBh | 17.5
80 | 110 | 635 | 67 | S/T | 0.823
80 | 110 | 635 | 67 | ∆T | 21
80 | 110 | 635 | 67 | LDB | 59
80 | 110 | 635 | 67 | LWB | 58.4
80 | 110 | 635 | 67 | kW | 1.76
84 | 110 | 635 | 70 | MBh | 17.8
84 | 110 | 635 | 70 | S/T | 0.781
84 | 110 | 635 | 70 | ∆T | 20.3
84 | 110 | 635 | 70 | LDB | 63.7
84 | 110 | 635 | 70 | LWB | 61.8
84 | 110 | 635 | 70 | kW | 1.77
86 | 110 | 635 | 72 | MBh | 18.1
86 | 110 | 635 | 72 | S/T | 0.735
86 | 110 | 635 | 72 | ∆T | 19.4
86 | 110 | 635 | 72 | LDB | 66.6
86 | 110 | 635 | 72 | LWB | 64.1
86 | 110 | 635 | 72 | kW | 1.78
90 | 110 | 635 | 75 | MBh | 18.3
90 | 110 | 635 | 75 | S/T | 0.607
90 | 110 | 635 | 75 | ∆T | 16.2
90 | 110 | 635 | 75 | LDB | 73.8
90 | 110 | 635 | 75 | LWB | 67.6
90 | 110 | 635 | 75 | kW | 1.78
68 | 115 | 635 | 57 | MBh | 11.7
68 | 115 | 635 | 57 | S/T | 0.957
68 | 115 | 635 | 57 | ∆T | 16.3
68 | 115 | 635 | 57 | LDB | 51.7
68 | 115 | 635 | 57 | LWB | 50
68 | 115 | 635 | 57 | kW | 1.09
72 | 115 | 635 | 61 | MBh | 14.2
72 | 115 | 635 | 61 | S/T | 0.908
72 | 115 | 635 | 61 | ∆T | 18.8
72 | 115 | 635 | 61 | LDB | 53.2
72 | 115 | 635 | 61 | LWB | 53.1
72 | 115 | 635 | 61 | kW | 1.44
77 | 115 | 635 | 64 | MBh | 16.1
77 | 115 | 635 | 64 | S/T | 0.87
77 | 115 | 635 | 64 | ∆T | 20.4
77 | 115 | 635 | 64 | LDB | 56.6
77 | 115 | 635 | 64 | LWB | 55.6
77 | 115 | 635 | 64 | kW | 1.74
80 | 115 | 635 | 67 | MBh | 16.9
80 | 115 | 635 | 67 | S/T | 0.822
80 | 115 | 635 | 67 | ∆T | 20.3
80 | 115 | 635 | 67 | LDB | 59.7
80 | 115 | 635 | 67 | LWB | 58.7
80 | 115 | 635 | 67 | kW | 1.85
84 | 115 | 635 | 70 | MBh | 16.9
84 | 115 | 635 | 70 | S/T | 0.775
84 | 115 | 635 | 70 | ∆T | 19.1
84 | 115 | 635 | 70 | LDB | 64.9
84 | 115 | 635 | 70 | LWB | 62.3
84 | 115 | 635 | 70 | kW | 1.85
86 | 115 | 635 | 72 | MBh | 16.9
86 | 115 | 635 | 72 | S/T | 0.734
86 | 115 | 635 | 72 | ∆T | 18.1
86 | 115 | 635 | 72 | LDB | 67.9
86 | 115 | 635 | 72 | LWB | 64.6
86 | 115 | 635 | 72 | kW | 1.85
90 | 115 | 635 | 75 | MBh | 16.9
90 | 115 | 635 | 75 | S/T | 0.604
90 | 115 | 635 | 75 | ∆T | 14.9
90 | 115 | 635 | 75 | LDB | 75.1
90 | 115 | 635 | 75 | LWB | 68.2
90 | 115 | 635 | 75 | kW | 1.85
68 | 118 | 635 | 57 | MBh | 11.7
68 | 118 | 635 | 57 | S/T | 0.957
68 | 118 | 635 | 57 | ∆T | 16.3
68 | 118 | 635 | 57 | LDB | 51.7
68 | 118 | 635 | 57 | LWB | 50
68 | 118 | 635 | 57 | kW | 1.16
72 | 118 | 635 | 61 | MBh | 14.2
72 | 118 | 635 | 61 | S/T | 0.908
72 | 118 | 635 | 61 | ∆T | 18.8
72 | 118 | 635 | 61 | LDB | 53.2
72 | 118 | 635 | 61 | LWB | 53.1
72 | 118 | 635 | 61 | kW | 1.53
77 | 118 | 635 | 64 | MBh | 14.2
77 | 118 | 635 | 64 | S/T | 0.873
77 | 118 | 635 | 64 | ∆T | 18.1
77 | 118 | 635 | 64 | LDB | 58.9
77 | 118 | 635 | 64 | LWB | 56.6
77 | 118 | 635 | 64 | kW | 1.53
80 | 118 | 635 | 67 | MBh | 14.2
80 | 118 | 635 | 67 | S/T | 0.824
80 | 118 | 635 | 67 | ∆T | 17.1
80 | 118 | 635 | 67 | LDB | 62.9
80 | 118 | 635 | 67 | LWB | 60.1
80 | 118 | 635 | 67 | kW | 1.53
84 | 118 | 635 | 70 | MBh | 14.2
84 | 118 | 635 | 70 | S/T | 0.782
84 | 118 | 635 | 70 | ∆T | 16.2
84 | 118 | 635 | 70 | LDB | 67.8
84 | 118 | 635 | 70 | LWB | 63.6
84 | 118 | 635 | 70 | kW | 1.53
86 | 118 | 635 | 72 | MBh | 14.2
86 | 118 | 635 | 72 | S/T | 0.739
86 | 118 | 635 | 72 | ∆T | 15.3
86 | 118 | 635 | 72 | LDB | 70.7
86 | 118 | 635 | 72 | LWB | 65.9
86 | 118 | 635 | 72 | kW | 1.53
90 | 118 | 635 | 75 | MBh | 14.2
90 | 118 | 635 | 75 | S/T | 0.607
90 | 118 | 635 | 75 | ∆T | 12.6
90 | 118 | 635 | 75 | LDB | 77.4
90 | 118 | 635 | 75 | LWB | 69.4
90 | 118 | 635 | 75 | kW | 1.53
68 | 122 | 635 | 57 | MBh | 10.3
68 | 122 | 635 | 57 | S/T | 0.958
68 | 122 | 635 | 57 | ∆T | 14.4
68 | 122 | 635 | 57 | LDB | 53.6
68 | 122 | 635 | 57 | LWB | 50.9
68 | 122 | 635 | 57 | kW | 1.07
72 | 122 | 635 | 61 | MBh | 10.3
72 | 122 | 635 | 61 | S/T | 0.908
72 | 122 | 635 | 61 | ∆T | 13.6
72 | 122 | 635 | 61 | LDB | 58.4
72 | 122 | 635 | 61 | LWB | 55.4
72 | 122 | 635 | 61 | kW | 1.07
77 | 122 | 635 | 64 | MBh | 10.3
77 | 122 | 635 | 64 | S/T | 0.87
77 | 122 | 635 | 64 | ∆T | 13.1
77 | 122 | 635 | 64 | LDB | 63.9
77 | 122 | 635 | 64 | LWB | 58.8
77 | 122 | 635 | 64 | kW | 1.07
80 | 122 | 635 | 67 | MBh | 10.3
80 | 122 | 635 | 67 | S/T | 0.822
80 | 122 | 635 | 67 | ∆T | 12.4
80 | 122 | 635 | 67 | LDB | 67.6
80 | 122 | 635 | 67 | LWB | 62.1
80 | 122 | 635 | 67 | kW | 1.07
84 | 122 | 635 | 70 | MBh | 10.3
84 | 122 | 635 | 70 | S/T | 0.779
84 | 122 | 635 | 70 | ∆T | 11.7
84 | 122 | 635 | 70 | LDB | 72.3
84 | 122 | 635 | 70 | LWB | 65.4
84 | 122 | 635 | 70 | kW | 1.07
86 | 122 | 635 | 72 | MBh | 10.3
86 | 122 | 635 | 72 | S/T | 0.737
86 | 122 | 635 | 72 | ∆T | 11.1
86 | 122 | 635 | 72 | LDB | 74.9
86 | 122 | 635 | 72 | LWB | 67.7
86 | 122 | 635 | 72 | kW | 1.07
90 | 122 | 635 | 75 | MBh | 10.3
90 | 122 | 635 | 75 | S/T | 0.607
90 | 122 | 635 | 75 | ∆T | 9.1
90 | 122 | 635 | 75 | LDB | 80.9
90 | 122 | 635 | 75 | LWB | 71
90 | 122 | 635 | 75 | kW | 1.07

## RZA24AAVJU - FBA24AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 742 | 57 | MBh | 15.6 | 64 | 60 | 61 | 32.4 | 2.44
68 | 23 | 742 | 57 | S/T | 0.904 | 64 | 60 | 65 | 30 | 2.21
68 | 23 | 742 | 57 | ∆T | 17.6 | 64 | 60 | 68 | 28.2 | 2.06
68 | 23 | 742 | 57 | LDB | 50.4 | 64 | 60 | 70 | 27 | 1.96
68 | 23 | 742 | 57 | LWB | 49 | 64 | 60 | 72 | 25.8 | 1.88
68 | 23 | 742 | 57 | kW | 0.6 | 64 | 60 | 75 | 24 | 1.76
72 | 23 | 742 | 61 | MBh | 18.9 | 60 | 56 | 61 | 32.4 | 2.55
72 | 23 | 742 | 61 | S/T | 0.857 | 60 | 56 | 65 | 30 | 2.3
72 | 23 | 742 | 61 | ∆T | 20.2 | 60 | 56 | 68 | 28.2 | 2.13
72 | 23 | 742 | 61 | LDB | 51.8 | 60 | 56 | 70 | 27 | 2.03
72 | 23 | 742 | 61 | LWB | 51.8 | 60 | 56 | 72 | 25.8 | 1.94
72 | 23 | 742 | 61 | kW | 0.74 | 60 | 56 | 75 | 24 | 1.81
77 | 23 | 742 | 64 | MBh | 21.5 | 57 | 53 | 61 | 32.4 | 2.65
77 | 23 | 742 | 64 | S/T | 0.819 | 57 | 53 | 65 | 30 | 2.38
77 | 23 | 742 | 64 | ∆T | 22 | 57 | 53 | 68 | 28.2 | 2.2
77 | 23 | 742 | 64 | LDB | 55 | 57 | 53 | 70 | 27 | 2.09
77 | 23 | 742 | 64 | LWB | 54.2 | 57 | 53 | 72 | 25.8 | 1.99
77 | 23 | 742 | 64 | kW | 0.85 | 57 | 53 | 75 | 24 | 1.85
80 | 23 | 742 | 67 | MBh | 24 | 54 | 50 | 61 | 32.4 | 2.75
80 | 23 | 742 | 67 | S/T | 0.779 | 54 | 50 | 65 | 30 | 2.46
80 | 23 | 742 | 67 | ∆T | 23.3 | 54 | 50 | 68 | 28.2 | 2.27
80 | 23 | 742 | 67 | LDB | 56.7 | 54 | 50 | 70 | 27 | 2.15
80 | 23 | 742 | 67 | LWB | 56.7 | 54 | 50 | 72 | 25.8 | 2.05
80 | 23 | 742 | 67 | kW | 0.96 | 54 | 50 | 75 | 24 | 1.9
84 | 23 | 742 | 70 | MBh | 26.5 | 51 | 47 | 61 | 32.4 | 2.86
84 | 23 | 742 | 70 | S/T | 0.747 | 51 | 47 | 65 | 30 | 2.56
84 | 23 | 742 | 70 | ∆T | 24.7 | 51 | 47 | 68 | 28.2 | 2.35
84 | 23 | 742 | 70 | LDB | 59.3 | 51 | 47 | 70 | 27 | 2.23
84 | 23 | 742 | 70 | LWB | 59.3 | 51 | 47 | 72 | 25.8 | 2.11
84 | 23 | 742 | 70 | kW | 1.08 | 51 | 47 | 75 | 24 | 1.95
86 | 23 | 742 | 72 | MBh | 28.2 | 47 | 43 | 61 | 32.4 | 3.03
86 | 23 | 742 | 72 | S/T | 0.713 | 47 | 43 | 65 | 30 | 2.7
86 | 23 | 742 | 72 | ∆T | 25.1 | 47 | 43 | 68 | 28.2 | 2.47
86 | 23 | 742 | 72 | LDB | 60.9 | 47 | 43 | 70 | 27 | 2.33
86 | 23 | 742 | 72 | LWB | 60.9 | 47 | 43 | 72 | 25.8 | 2.2
86 | 23 | 742 | 72 | kW | 1.16 | 47 | 43 | 75 | 24 | 2.03
90 | 23 | 742 | 75 | MBh | 30.7 | 44 | 40 | 61 | 32.4 | 3.18
90 | 23 | 742 | 75 | S/T | 0.785 | 44 | 40 | 65 | 30 | 2.82
90 | 23 | 742 | 75 | ∆T | 30.1 | 44 | 40 | 68 | 28.2 | 2.57
90 | 23 | 742 | 75 | LDB | 59.9 | 44 | 40 | 70 | 27 | 2.42
90 | 23 | 742 | 75 | LWB | 59.9 | 44 | 40 | 72 | 25.8 | 2.28
90 | 23 | 742 | 75 | kW | 1.28 | 44 | 40 | 75 | 24 | 2.09
68 | 30 | 742 | 57 | MBh | 15.6 | 39 | 36 | 61 | 31.7 | 3.25
68 | 30 | 742 | 57 | S/T | 0.904 | 39 | 36 | 65 | 30 | 2.99
68 | 30 | 742 | 57 | ∆T | 17.6 | 39 | 36 | 68 | 28.2 | 2.72
68 | 30 | 742 | 57 | LDB | 50.4 | 39 | 36 | 70 | 27 | 2.56
68 | 30 | 742 | 57 | LWB | 49 | 39 | 36 | 72 | 25.8 | 2.4
68 | 30 | 742 | 57 | kW | 0.62 | 39 | 36 | 75 | 24 | 2.19
72 | 30 | 742 | 61 | MBh | 18.9 | 35 | 32 | 61 | 30.3 | 3.21
72 | 30 | 742 | 61 | S/T | 0.857 | 35 | 32 | 65 | 30 | 3.2
72 | 30 | 742 | 61 | ∆T | 20.2 | 35 | 32 | 68 | 28.2 | 2.9
72 | 30 | 742 | 61 | LDB | 51.8 | 35 | 32 | 70 | 27 | 2.72
72 | 30 | 742 | 61 | LWB | 51.8 | 35 | 32 | 72 | 25.8 | 2.54
72 | 30 | 742 | 61 | kW | 0.76 | 35 | 32 | 75 | 24 | 2.31
77 | 30 | 742 | 64 | MBh | 21.5 | 30 | 28 | 61 | 28.9 | 3.18
77 | 30 | 742 | 64 | S/T | 0.819 | 30 | 28 | 65 | 28.9 | 3.23
77 | 30 | 742 | 64 | ∆T | 22 | 30 | 28 | 68 | 28.2 | 3.11
77 | 30 | 742 | 64 | LDB | 55 | 30 | 28 | 70 | 27 | 2.9
77 | 30 | 742 | 64 | LWB | 54.2 | 30 | 28 | 72 | 25.8 | 2.71
77 | 30 | 742 | 64 | kW | 0.88 | 30 | 28 | 75 | 24 | 2.44
80 | 30 | 742 | 67 | MBh | 24 | 26 | 24 | 61 | 27.5 | 3.14
80 | 30 | 742 | 67 | S/T | 0.779 | 26 | 24 | 65 | 27.5 | 3.2
80 | 30 | 742 | 67 | ∆T | 23.3 | 26 | 24 | 68 | 27.5 | 3.24
80 | 30 | 742 | 67 | LDB | 56.7 | 26 | 24 | 70 | 27 | 3.11
80 | 30 | 742 | 67 | LWB | 56.7 | 26 | 24 | 72 | 25.8 | 2.9
80 | 30 | 742 | 67 | kW | 0.99 | 26 | 24 | 75 | 24 | 2.6
84 | 30 | 742 | 70 | MBh | 26.5 | 22 | 20 | 61 | 26.2 | 3.1
84 | 30 | 742 | 70 | S/T | 0.747 | 22 | 20 | 65 | 26.2 | 3.16
84 | 30 | 742 | 70 | ∆T | 24.7 | 22 | 20 | 68 | 26.2 | 3.21
84 | 30 | 742 | 70 | LDB | 59.3 | 22 | 20 | 70 | 26.2 | 3.24
84 | 30 | 742 | 70 | LWB | 59.3 | 22 | 20 | 72 | 25.8 | 3.13
84 | 30 | 742 | 70 | kW | 1.11 | 22 | 20 | 75 | 24 | 2.79
86 | 30 | 742 | 72 | MBh | 28.2 | 19 | 18 | 61 | 25.5 | 3.08
86 | 30 | 742 | 72 | S/T | 0.713 | 19 | 18 | 65 | 25.5 | 3.14
86 | 30 | 742 | 72 | ∆T | 25.1 | 19 | 18 | 68 | 25.5 | 3.19
86 | 30 | 742 | 72 | LDB | 60.9 | 19 | 18 | 70 | 25.5 | 3.22
86 | 30 | 742 | 72 | LWB | 60.9 | 19 | 18 | 72 | 25.5 | 3.25
86 | 30 | 742 | 72 | kW | 1.2 | 19 | 18 | 75 | 24 | 2.9
90 | 30 | 742 | 75 | MBh | 30.7 | 17 | 16 | 61 | 24.6 | 3.05
90 | 30 | 742 | 75 | S/T | 0.785 | 17 | 16 | 65 | 24.6 | 3.11
90 | 30 | 742 | 75 | ∆T | 30.1 | 17 | 16 | 68 | 24.6 | 3.16
90 | 30 | 742 | 75 | LDB | 59.9 | 17 | 16 | 70 | 24.6 | 3.19
90 | 30 | 742 | 75 | LWB | 59.9 | 17 | 16 | 72 | 24.6 | 3.23
90 | 30 | 742 | 75 | kW | 1.32 | 17 | 16 | 75 | 24 | 3.05
68 | 40 | 742 | 57 | MBh | 15.6 | 15 | 14 | 61 | 24.1 | 3.03
68 | 40 | 742 | 57 | S/T | 0.904 | 15 | 14 | 65 | 24.1 | 3.1
68 | 40 | 742 | 57 | ∆T | 17.6 | 15 | 14 | 68 | 24.1 | 3.15
68 | 40 | 742 | 57 | LDB | 50.4 | 15 | 14 | 70 | 24.1 | 3.18
68 | 40 | 742 | 57 | LWB | 49 | 15 | 14 | 72 | 24.1 | 3.21
68 | 40 | 742 | 57 | kW | 0.65 | 15 | 14 | 75 | 24 | 3.14
72 | 40 | 742 | 61 | MBh | 18.9 | 13 | 12 | 61 | 23.4 | 3.01
72 | 40 | 742 | 61 | S/T | 0.857 | 13 | 12 | 65 | 23.4 | 3.07
72 | 40 | 742 | 61 | ∆T | 20.2 | 13 | 12 | 68 | 23.4 | 3.12
72 | 40 | 742 | 61 | LDB | 51.8 | 13 | 12 | 70 | 23.4 | 3.16
72 | 40 | 742 | 61 | LWB | 51.8 | 13 | 12 | 72 | 23.4 | 3.19
72 | 40 | 742 | 61 | kW | 0.8 | 13 | 12 | 75 | 23.4 | 3.24
77 | 40 | 742 | 64 | MBh | 21.5 | 10 | 9 | 61 | 22.2 | 2.96
77 | 40 | 742 | 64 | S/T | 0.819 | 10 | 9 | 65 | 22.2 | 3.03
77 | 40 | 742 | 64 | ∆T | 22 | 10 | 9 | 68 | 22.2 | 3.08
77 | 40 | 742 | 64 | LDB | 55 | 10 | 9 | 70 | 22.2 | 3.12
77 | 40 | 742 | 64 | LWB | 54.2 | 10 | 9 | 72 | 22.2 | 3.15
77 | 40 | 742 | 64 | kW | 0.92 | 10 | 9 | 75 | 22.2 | 3.2
80 | 40 | 742 | 67 | MBh | 24 | 6 | 5 | 61 | 21 | 2.91
80 | 40 | 742 | 67 | S/T | 0.779 | 6 | 5 | 65 | 21 | 2.98
80 | 40 | 742 | 67 | ∆T | 23.3 | 6 | 5 | 68 | 21 | 3.04
80 | 40 | 742 | 67 | LDB | 56.7 | 6 | 5 | 70 | 21 | 3.07
80 | 40 | 742 | 67 | LWB | 56.7 | 6 | 5 | 72 | 21 | 3.11
80 | 40 | 742 | 67 | kW | 1.04 | 6 | 5 | 75 | 21 | 3.17
84 | 40 | 742 | 70 | MBh | 26.5 | -2 | -2 | 61 | 18.5 | 2.78
84 | 40 | 742 | 70 | S/T | 0.747 | -2 | -2 | 65 | 18.5 | 2.87
84 | 40 | 742 | 70 | ∆T | 24.7 | -2 | -2 | 68 | 18.5 | 2.93
84 | 40 | 742 | 70 | LDB | 59.3 | -2 | -2 | 70 | 18.5 | 2.97
84 | 40 | 742 | 70 | LWB | 59.3 | -2 | -2 | 72 | 18.5 | 3.01
84 | 40 | 742 | 70 | kW | 1.17 | -2 | -2 | 75 | 18.5 | 3.07
86 | 40 | 742 | 72 | MBh | 28.2 | -4 | -4 | 61 | 17.9 | 2.75
86 | 40 | 742 | 72 | S/T | 0.713 | -4 | -4 | 65 | 17.9 | 2.83
86 | 40 | 742 | 72 | ∆T | 25.1 | -4 | -4 | 68 | 17.9 | 2.9
86 | 40 | 742 | 72 | LDB | 60.9 | -4 | -4 | 70 | 17.9 | 2.94
86 | 40 | 742 | 72 | LWB | 60.9 | -4 | -4 | 72 | 17.9 | 2.98
86 | 40 | 742 | 72 | kW | 1.26 | -4 | -4 | 75 | 17.9 | 3.04
90 | 40 | 742 | 75 | MBh | 30.7
90 | 40 | 742 | 75 | S/T | 0.785
90 | 40 | 742 | 75 | ∆T | 30.1
90 | 40 | 742 | 75 | LDB | 59.9
90 | 40 | 742 | 75 | LWB | 59.9
90 | 40 | 742 | 75 | kW | 1.39
68 | 50 | 742 | 57 | MBh | 15.6
68 | 50 | 742 | 57 | S/T | 0.904
68 | 50 | 742 | 57 | ∆T | 17.6
68 | 50 | 742 | 57 | LDB | 50.4
68 | 50 | 742 | 57 | LWB | 49
68 | 50 | 742 | 57 | kW | 0.68
72 | 50 | 742 | 61 | MBh | 18.9
72 | 50 | 742 | 61 | S/T | 0.857
72 | 50 | 742 | 61 | ∆T | 20.2
72 | 50 | 742 | 61 | LDB | 51.8
72 | 50 | 742 | 61 | LWB | 51.8
72 | 50 | 742 | 61 | kW | 0.84
77 | 50 | 742 | 64 | MBh | 21.5
77 | 50 | 742 | 64 | S/T | 0.819
77 | 50 | 742 | 64 | ∆T | 22
77 | 50 | 742 | 64 | LDB | 55
77 | 50 | 742 | 64 | LWB | 54.2
77 | 50 | 742 | 64 | kW | 0.96
80 | 50 | 742 | 67 | MBh | 24
80 | 50 | 742 | 67 | S/T | 0.779
80 | 50 | 742 | 67 | ∆T | 23.3
80 | 50 | 742 | 67 | LDB | 56.7
80 | 50 | 742 | 67 | LWB | 56.7
80 | 50 | 742 | 67 | kW | 1.09
84 | 50 | 742 | 70 | MBh | 26.5
84 | 50 | 742 | 70 | S/T | 0.747
84 | 50 | 742 | 70 | ∆T | 24.7
84 | 50 | 742 | 70 | LDB | 59.3
84 | 50 | 742 | 70 | LWB | 59.3
84 | 50 | 742 | 70 | kW | 1.23
86 | 50 | 742 | 72 | MBh | 28.2
86 | 50 | 742 | 72 | S/T | 0.713
86 | 50 | 742 | 72 | ∆T | 25.1
86 | 50 | 742 | 72 | LDB | 60.9
86 | 50 | 742 | 72 | LWB | 60.9
86 | 50 | 742 | 72 | kW | 1.32
90 | 50 | 742 | 75 | MBh | 30.7
90 | 50 | 742 | 75 | S/T | 0.785
90 | 50 | 742 | 75 | ∆T | 30.1
90 | 50 | 742 | 75 | LDB | 59.9
90 | 50 | 742 | 75 | LWB | 59.9
90 | 50 | 742 | 75 | kW | 1.46
68 | 54 | 742 | 57 | MBh | 15.6
68 | 54 | 742 | 57 | S/T | 0.904
68 | 54 | 742 | 57 | ∆T | 17.6
68 | 54 | 742 | 57 | LDB | 50.4
68 | 54 | 742 | 57 | LWB | 49
68 | 54 | 742 | 57 | kW | 0.69
72 | 54 | 742 | 61 | MBh | 18.9
72 | 54 | 742 | 61 | S/T | 0.857
72 | 54 | 742 | 61 | ∆T | 20.2
72 | 54 | 742 | 61 | LDB | 51.8
72 | 54 | 742 | 61 | LWB | 51.8
72 | 54 | 742 | 61 | kW | 0.85
77 | 54 | 742 | 64 | MBh | 21.5
77 | 54 | 742 | 64 | S/T | 0.819
77 | 54 | 742 | 64 | ∆T | 22
77 | 54 | 742 | 64 | LDB | 55
77 | 54 | 742 | 64 | LWB | 54.2
77 | 54 | 742 | 64 | kW | 0.98
80 | 54 | 742 | 67 | MBh | 24
80 | 54 | 742 | 67 | S/T | 0.779
80 | 54 | 742 | 67 | ∆T | 23.3
80 | 54 | 742 | 67 | LDB | 56.7
80 | 54 | 742 | 67 | LWB | 56.7
80 | 54 | 742 | 67 | kW | 1.12
84 | 54 | 742 | 70 | MBh | 26.5
84 | 54 | 742 | 70 | S/T | 0.747
84 | 54 | 742 | 70 | ∆T | 24.7
84 | 54 | 742 | 70 | LDB | 59.3
84 | 54 | 742 | 70 | LWB | 59.3
84 | 54 | 742 | 70 | kW | 1.26
86 | 54 | 742 | 72 | MBh | 28.2
86 | 54 | 742 | 72 | S/T | 0.713
86 | 54 | 742 | 72 | ∆T | 25.1
86 | 54 | 742 | 72 | LDB | 60.9
86 | 54 | 742 | 72 | LWB | 60.9
86 | 54 | 742 | 72 | kW | 1.35
90 | 54 | 742 | 75 | MBh | 30.7
90 | 54 | 742 | 75 | S/T | 0.785
90 | 54 | 742 | 75 | ∆T | 30.1
90 | 54 | 742 | 75 | LDB | 59.9
90 | 54 | 742 | 75 | LWB | 59.9
90 | 54 | 742 | 75 | kW | 1.49
68 | 58 | 742 | 57 | MBh | 15.6
68 | 58 | 742 | 57 | S/T | 0.904
68 | 58 | 742 | 57 | ∆T | 17.6
68 | 58 | 742 | 57 | LDB | 50.4
68 | 58 | 742 | 57 | LWB | 49
68 | 58 | 742 | 57 | kW | 0.7
72 | 58 | 742 | 61 | MBh | 18.9
72 | 58 | 742 | 61 | S/T | 0.857
72 | 58 | 742 | 61 | ∆T | 20.2
72 | 58 | 742 | 61 | LDB | 51.8
72 | 58 | 742 | 61 | LWB | 51.8
72 | 58 | 742 | 61 | kW | 0.87
77 | 58 | 742 | 64 | MBh | 21.5
77 | 58 | 742 | 64 | S/T | 0.819
77 | 58 | 742 | 64 | ∆T | 22
77 | 58 | 742 | 64 | LDB | 55
77 | 58 | 742 | 64 | LWB | 54.2
77 | 58 | 742 | 64 | kW | 1
80 | 58 | 742 | 67 | MBh | 24
80 | 58 | 742 | 67 | S/T | 0.779
80 | 58 | 742 | 67 | ∆T | 23.3
80 | 58 | 742 | 67 | LDB | 56.7
80 | 58 | 742 | 67 | LWB | 56.7
80 | 58 | 742 | 67 | kW | 1.14
84 | 58 | 742 | 70 | MBh | 26.5
84 | 58 | 742 | 70 | S/T | 0.747
84 | 58 | 742 | 70 | ∆T | 24.7
84 | 58 | 742 | 70 | LDB | 59.3
84 | 58 | 742 | 70 | LWB | 59.3
84 | 58 | 742 | 70 | kW | 1.28
86 | 58 | 742 | 72 | MBh | 28.2
86 | 58 | 742 | 72 | S/T | 0.713
86 | 58 | 742 | 72 | ∆T | 25.1
86 | 58 | 742 | 72 | LDB | 60.9
86 | 58 | 742 | 72 | LWB | 60.9
86 | 58 | 742 | 72 | kW | 1.38
90 | 58 | 742 | 75 | MBh | 30.5
90 | 58 | 742 | 75 | S/T | 0.784
90 | 58 | 742 | 75 | ∆T | 29.8
90 | 58 | 742 | 75 | LDB | 60.2
90 | 58 | 742 | 75 | LWB | 60.2
90 | 58 | 742 | 75 | kW | 1.49
68 | 62 | 742 | 57 | MBh | 15.6
68 | 62 | 742 | 57 | S/T | 0.904
68 | 62 | 742 | 57 | ∆T | 17.6
68 | 62 | 742 | 57 | LDB | 50.4
68 | 62 | 742 | 57 | LWB | 49
68 | 62 | 742 | 57 | kW | 0.72
72 | 62 | 742 | 61 | MBh | 18.9
72 | 62 | 742 | 61 | S/T | 0.857
72 | 62 | 742 | 61 | ∆T | 20.2
72 | 62 | 742 | 61 | LDB | 51.8
72 | 62 | 742 | 61 | LWB | 51.8
72 | 62 | 742 | 61 | kW | 0.89
77 | 62 | 742 | 64 | MBh | 21.5
77 | 62 | 742 | 64 | S/T | 0.819
77 | 62 | 742 | 64 | ∆T | 22
77 | 62 | 742 | 64 | LDB | 55
77 | 62 | 742 | 64 | LWB | 54.2
77 | 62 | 742 | 64 | kW | 1.03
80 | 62 | 742 | 67 | MBh | 24
80 | 62 | 742 | 67 | S/T | 0.779
80 | 62 | 742 | 67 | ∆T | 23.3
80 | 62 | 742 | 67 | LDB | 56.7
80 | 62 | 742 | 67 | LWB | 56.7
80 | 62 | 742 | 67 | kW | 1.17
84 | 62 | 742 | 70 | MBh | 26.5
84 | 62 | 742 | 70 | S/T | 0.747
84 | 62 | 742 | 70 | ∆T | 24.7
84 | 62 | 742 | 70 | LDB | 59.3
84 | 62 | 742 | 70 | LWB | 59.3
84 | 62 | 742 | 70 | kW | 1.31
86 | 62 | 742 | 72 | MBh | 28.2
86 | 62 | 742 | 72 | S/T | 0.713
86 | 62 | 742 | 72 | ∆T | 25.1
86 | 62 | 742 | 72 | LDB | 60.9
86 | 62 | 742 | 72 | LWB | 60.9
86 | 62 | 742 | 72 | kW | 1.41
90 | 62 | 742 | 75 | MBh | 30
90 | 62 | 742 | 75 | S/T | 0.783
90 | 62 | 742 | 75 | ∆T | 29.3
90 | 62 | 742 | 75 | LDB | 60.7
90 | 62 | 742 | 75 | LWB | 60.7
90 | 62 | 742 | 75 | kW | 1.48
68 | 66 | 742 | 57 | MBh | 15.6
68 | 66 | 742 | 57 | S/T | 0.904
68 | 66 | 742 | 57 | ∆T | 17.6
68 | 66 | 742 | 57 | LDB | 50.4
68 | 66 | 742 | 57 | LWB | 49
68 | 66 | 742 | 57 | kW | 0.73
72 | 66 | 742 | 61 | MBh | 18.9
72 | 66 | 742 | 61 | S/T | 0.857
72 | 66 | 742 | 61 | ∆T | 20.2
72 | 66 | 742 | 61 | LDB | 51.8
72 | 66 | 742 | 61 | LWB | 51.8
72 | 66 | 742 | 61 | kW | 0.91
77 | 66 | 742 | 64 | MBh | 21.5
77 | 66 | 742 | 64 | S/T | 0.819
77 | 66 | 742 | 64 | ∆T | 22
77 | 66 | 742 | 64 | LDB | 55
77 | 66 | 742 | 64 | LWB | 54.2
77 | 66 | 742 | 64 | kW | 1.05
80 | 66 | 742 | 67 | MBh | 24
80 | 66 | 742 | 67 | S/T | 0.779
80 | 66 | 742 | 67 | ∆T | 23.3
80 | 66 | 742 | 67 | LDB | 56.7
80 | 66 | 742 | 67 | LWB | 56.7
80 | 66 | 742 | 67 | kW | 1.19
84 | 66 | 742 | 70 | MBh | 26.5
84 | 66 | 742 | 70 | S/T | 0.747
84 | 66 | 742 | 70 | ∆T | 24.7
84 | 66 | 742 | 70 | LDB | 59.3
84 | 66 | 742 | 70 | LWB | 59.3
84 | 66 | 742 | 70 | kW | 1.34
86 | 66 | 742 | 72 | MBh | 28.2
86 | 66 | 742 | 72 | S/T | 0.713
86 | 66 | 742 | 72 | ∆T | 25.1
86 | 66 | 742 | 72 | LDB | 60.9
86 | 66 | 742 | 72 | LWB | 60.9
86 | 66 | 742 | 72 | kW | 1.44
90 | 66 | 742 | 75 | MBh | 29.6
90 | 66 | 742 | 75 | S/T | 0.784
90 | 66 | 742 | 75 | ∆T | 29
90 | 66 | 742 | 75 | LDB | 61
90 | 66 | 742 | 75 | LWB | 61
90 | 66 | 742 | 75 | kW | 1.48
68 | 70 | 742 | 57 | MBh | 15.6
68 | 70 | 742 | 57 | S/T | 0.904
68 | 70 | 742 | 57 | ∆T | 17.6
68 | 70 | 742 | 57 | LDB | 50.4
68 | 70 | 742 | 57 | LWB | 49
68 | 70 | 742 | 57 | kW | 0.75
72 | 70 | 742 | 61 | MBh | 18.9
72 | 70 | 742 | 61 | S/T | 0.857
72 | 70 | 742 | 61 | ∆T | 20.2
72 | 70 | 742 | 61 | LDB | 51.8
72 | 70 | 742 | 61 | LWB | 51.8
72 | 70 | 742 | 61 | kW | 0.93
77 | 70 | 742 | 64 | MBh | 21.5
77 | 70 | 742 | 64 | S/T | 0.819
77 | 70 | 742 | 64 | ∆T | 22
77 | 70 | 742 | 64 | LDB | 55
77 | 70 | 742 | 64 | LWB | 54.2
77 | 70 | 742 | 64 | kW | 1.07
80 | 70 | 742 | 67 | MBh | 24
80 | 70 | 742 | 67 | S/T | 0.779
80 | 70 | 742 | 67 | ∆T | 23.3
80 | 70 | 742 | 67 | LDB | 56.7
80 | 70 | 742 | 67 | LWB | 56.7
80 | 70 | 742 | 67 | kW | 1.22
84 | 70 | 742 | 70 | MBh | 26.5
84 | 70 | 742 | 70 | S/T | 0.747
84 | 70 | 742 | 70 | ∆T | 24.7
84 | 70 | 742 | 70 | LDB | 59.3
84 | 70 | 742 | 70 | LWB | 59.3
84 | 70 | 742 | 70 | kW | 1.37
86 | 70 | 742 | 72 | MBh | 28.2
86 | 70 | 742 | 72 | S/T | 0.713
86 | 70 | 742 | 72 | ∆T | 25.1
86 | 70 | 742 | 72 | LDB | 60.9
86 | 70 | 742 | 72 | LWB | 60.9
86 | 70 | 742 | 72 | kW | 1.47
90 | 70 | 742 | 75 | MBh | 29.1
90 | 70 | 742 | 75 | S/T | 0.784
90 | 70 | 742 | 75 | ∆T | 28.5
90 | 70 | 742 | 75 | LDB | 61.5
90 | 70 | 742 | 75 | LWB | 61.5
90 | 70 | 742 | 75 | kW | 1.51
68 | 72 | 742 | 57 | MBh | 15.6
68 | 72 | 742 | 57 | S/T | 0.904
68 | 72 | 742 | 57 | ∆T | 17.6
68 | 72 | 742 | 57 | LDB | 50.4
68 | 72 | 742 | 57 | LWB | 49
68 | 72 | 742 | 57 | kW | 0.76
72 | 72 | 742 | 61 | MBh | 18.9
72 | 72 | 742 | 61 | S/T | 0.857
72 | 72 | 742 | 61 | ∆T | 20.2
72 | 72 | 742 | 61 | LDB | 51.8
72 | 72 | 742 | 61 | LWB | 51.8
72 | 72 | 742 | 61 | kW | 0.94
77 | 72 | 742 | 64 | MBh | 21.5
77 | 72 | 742 | 64 | S/T | 0.819
77 | 72 | 742 | 64 | ∆T | 22
77 | 72 | 742 | 64 | LDB | 55
77 | 72 | 742 | 64 | LWB | 54.2
77 | 72 | 742 | 64 | kW | 1.08
80 | 72 | 742 | 67 | MBh | 24
80 | 72 | 742 | 67 | S/T | 0.779
80 | 72 | 742 | 67 | ∆T | 23.3
80 | 72 | 742 | 67 | LDB | 56.7
80 | 72 | 742 | 67 | LWB | 56.7
80 | 72 | 742 | 67 | kW | 1.23
84 | 72 | 742 | 70 | MBh | 26.5
84 | 72 | 742 | 70 | S/T | 0.747
84 | 72 | 742 | 70 | ∆T | 24.7
84 | 72 | 742 | 70 | LDB | 59.3
84 | 72 | 742 | 70 | LWB | 59.3
84 | 72 | 742 | 70 | kW | 1.41
86 | 72 | 742 | 72 | MBh | 28.2
86 | 72 | 742 | 72 | S/T | 0.713
86 | 72 | 742 | 72 | ∆T | 25.1
86 | 72 | 742 | 72 | LDB | 60.9
86 | 72 | 742 | 72 | LWB | 60.9
86 | 72 | 742 | 72 | kW | 1.54
90 | 72 | 742 | 75 | MBh | 28.9
90 | 72 | 742 | 75 | S/T | 0.782
90 | 72 | 742 | 75 | ∆T | 28.2
90 | 72 | 742 | 75 | LDB | 61.8
90 | 72 | 742 | 75 | LWB | 61.8
90 | 72 | 742 | 75 | kW | 1.57
68 | 75 | 742 | 57 | MBh | 15.6
68 | 75 | 742 | 57 | S/T | 0.904
68 | 75 | 742 | 57 | ∆T | 17.6
68 | 75 | 742 | 57 | LDB | 50.4
68 | 75 | 742 | 57 | LWB | 49
68 | 75 | 742 | 57 | kW | 0.77
72 | 75 | 742 | 61 | MBh | 18.9
72 | 75 | 742 | 61 | S/T | 0.857
72 | 75 | 742 | 61 | ∆T | 20.2
72 | 75 | 742 | 61 | LDB | 51.8
72 | 75 | 742 | 61 | LWB | 51.8
72 | 75 | 742 | 61 | kW | 0.96
77 | 75 | 742 | 64 | MBh | 21.5
77 | 75 | 742 | 64 | S/T | 0.819
77 | 75 | 742 | 64 | ∆T | 22
77 | 75 | 742 | 64 | LDB | 55
77 | 75 | 742 | 64 | LWB | 54.2
77 | 75 | 742 | 64 | kW | 1.11
80 | 75 | 742 | 67 | MBh | 24
80 | 75 | 742 | 67 | S/T | 0.779
80 | 75 | 742 | 67 | ∆T | 23.3
80 | 75 | 742 | 67 | LDB | 56.7
80 | 75 | 742 | 67 | LWB | 56.7
80 | 75 | 742 | 67 | kW | 1.3
84 | 75 | 742 | 70 | MBh | 26.5
84 | 75 | 742 | 70 | S/T | 0.747
84 | 75 | 742 | 70 | ∆T | 24.7
84 | 75 | 742 | 70 | LDB | 59.3
84 | 75 | 742 | 70 | LWB | 59.3
84 | 75 | 742 | 70 | kW | 1.51
86 | 75 | 742 | 72 | MBh | 28
86 | 75 | 742 | 72 | S/T | 0.714
86 | 75 | 742 | 72 | ∆T | 25
86 | 75 | 742 | 72 | LDB | 61
86 | 75 | 742 | 72 | LWB | 61
86 | 75 | 742 | 72 | kW | 1.64
90 | 75 | 742 | 75 | MBh | 28.5
90 | 75 | 742 | 75 | S/T | 0.786
90 | 75 | 742 | 75 | ∆T | 28
90 | 75 | 742 | 75 | LDB | 62
90 | 75 | 742 | 75 | LWB | 62
90 | 75 | 742 | 75 | kW | 1.65
68 | 79 | 742 | 57 | MBh | 15.6
68 | 79 | 742 | 57 | S/T | 0.904
68 | 79 | 742 | 57 | ∆T | 17.6
68 | 79 | 742 | 57 | LDB | 50.4
68 | 79 | 742 | 57 | LWB | 49
68 | 79 | 742 | 57 | kW | 0.79
72 | 79 | 742 | 61 | MBh | 18.9
72 | 79 | 742 | 61 | S/T | 0.857
72 | 79 | 742 | 61 | ∆T | 20.2
72 | 79 | 742 | 61 | LDB | 51.8
72 | 79 | 742 | 61 | LWB | 51.8
72 | 79 | 742 | 61 | kW | 1.02
77 | 79 | 742 | 64 | MBh | 21.5
77 | 79 | 742 | 64 | S/T | 0.819
77 | 79 | 742 | 64 | ∆T | 22
77 | 79 | 742 | 64 | LDB | 55
77 | 79 | 742 | 64 | LWB | 54.2
77 | 79 | 742 | 64 | kW | 1.22
80 | 79 | 742 | 67 | MBh | 24
80 | 79 | 742 | 67 | S/T | 0.779
80 | 79 | 742 | 67 | ∆T | 23.3
80 | 79 | 742 | 67 | LDB | 56.7
80 | 79 | 742 | 67 | LWB | 56.7
80 | 79 | 742 | 67 | kW | 1.43
84 | 79 | 742 | 70 | MBh | 26.5
84 | 79 | 742 | 70 | S/T | 0.747
84 | 79 | 742 | 70 | ∆T | 24.7
84 | 79 | 742 | 70 | LDB | 59.3
84 | 79 | 742 | 70 | LWB | 59.3
84 | 79 | 742 | 70 | kW | 1.66
86 | 79 | 742 | 72 | MBh | 27.6
86 | 79 | 742 | 72 | S/T | 0.714
86 | 79 | 742 | 72 | ∆T | 24.6
86 | 79 | 742 | 72 | LDB | 61.4
86 | 79 | 742 | 72 | LWB | 61.4
86 | 79 | 742 | 72 | kW | 1.75
90 | 79 | 742 | 75 | MBh | 28.1
90 | 79 | 742 | 75 | S/T | 0.783
90 | 79 | 742 | 75 | ∆T | 27.5
90 | 79 | 742 | 75 | LDB | 62.5
90 | 79 | 742 | 75 | LWB | 62.5
90 | 79 | 742 | 75 | kW | 1.76
68 | 83 | 742 | 57 | MBh | 15.6
68 | 83 | 742 | 57 | S/T | 0.904
68 | 83 | 742 | 57 | ∆T | 17.6
68 | 83 | 742 | 57 | LDB | 50.4
68 | 83 | 742 | 57 | LWB | 49
68 | 83 | 742 | 57 | kW | 0.86
72 | 83 | 742 | 61 | MBh | 18.9
72 | 83 | 742 | 61 | S/T | 0.857
72 | 83 | 742 | 61 | ∆T | 20.2
72 | 83 | 742 | 61 | LDB | 51.8
72 | 83 | 742 | 61 | LWB | 51.8
72 | 83 | 742 | 61 | kW | 1.11
77 | 83 | 742 | 64 | MBh | 21.5
77 | 83 | 742 | 64 | S/T | 0.819
77 | 83 | 742 | 64 | ∆T | 22
77 | 83 | 742 | 64 | LDB | 55
77 | 83 | 742 | 64 | LWB | 54.2
77 | 83 | 742 | 64 | kW | 1.33
80 | 83 | 742 | 67 | MBh | 24
80 | 83 | 742 | 67 | S/T | 0.779
80 | 83 | 742 | 67 | ∆T | 23.3
80 | 83 | 742 | 67 | LDB | 56.7
80 | 83 | 742 | 67 | LWB | 56.7
80 | 83 | 742 | 67 | kW | 1.56
84 | 83 | 742 | 70 | MBh | 26.5
84 | 83 | 742 | 70 | S/T | 0.747
84 | 83 | 742 | 70 | ∆T | 24.7
84 | 83 | 742 | 70 | LDB | 59.3
84 | 83 | 742 | 70 | LWB | 59.3
84 | 83 | 742 | 70 | kW | 1.82
86 | 83 | 742 | 72 | MBh | 27.1
86 | 83 | 742 | 72 | S/T | 0.716
86 | 83 | 742 | 72 | ∆T | 24.2
86 | 83 | 742 | 72 | LDB | 61.8
86 | 83 | 742 | 72 | LWB | 61.6
86 | 83 | 742 | 72 | kW | 1.86
90 | 83 | 742 | 75 | MBh | 27.6
90 | 83 | 742 | 75 | S/T | 0.786
90 | 83 | 742 | 75 | ∆T | 27.1
90 | 83 | 742 | 75 | LDB | 62.9
90 | 83 | 742 | 75 | LWB | 62.9
90 | 83 | 742 | 75 | kW | 1.88
68 | 87 | 742 | 57 | MBh | 15.6
68 | 87 | 742 | 57 | S/T | 0.904
68 | 87 | 742 | 57 | ∆T | 17.6
68 | 87 | 742 | 57 | LDB | 50.4
68 | 87 | 742 | 57 | LWB | 49
68 | 87 | 742 | 57 | kW | 0.93
72 | 87 | 742 | 61 | MBh | 18.9
72 | 87 | 742 | 61 | S/T | 0.857
72 | 87 | 742 | 61 | ∆T | 20.2
72 | 87 | 742 | 61 | LDB | 51.8
72 | 87 | 742 | 61 | LWB | 51.8
72 | 87 | 742 | 61 | kW | 1.21
77 | 87 | 742 | 64 | MBh | 21.5
77 | 87 | 742 | 64 | S/T | 0.819
77 | 87 | 742 | 64 | ∆T | 22
77 | 87 | 742 | 64 | LDB | 55
77 | 87 | 742 | 64 | LWB | 54.2
77 | 87 | 742 | 64 | kW | 1.45
80 | 87 | 742 | 67 | MBh | 24
80 | 87 | 742 | 67 | S/T | 0.779
80 | 87 | 742 | 67 | ∆T | 23.3
80 | 87 | 742 | 67 | LDB | 56.7
80 | 87 | 742 | 67 | LWB | 56.7
80 | 87 | 742 | 67 | kW | 1.71
84 | 87 | 742 | 70 | MBh | 26.4
84 | 87 | 742 | 70 | S/T | 0.746
84 | 87 | 742 | 70 | ∆T | 24.6
84 | 87 | 742 | 70 | LDB | 59.4
84 | 87 | 742 | 70 | LWB | 59.4
84 | 87 | 742 | 70 | kW | 1.97
86 | 87 | 742 | 72 | MBh | 26.7
86 | 87 | 742 | 72 | S/T | 0.715
86 | 87 | 742 | 72 | ∆T | 23.8
86 | 87 | 742 | 72 | LDB | 62.2
86 | 87 | 742 | 72 | LWB | 61.8
86 | 87 | 742 | 72 | kW | 1.97
90 | 87 | 742 | 75 | MBh | 27.2
90 | 87 | 742 | 75 | S/T | 0.783
90 | 87 | 742 | 75 | ∆T | 26.6
90 | 87 | 742 | 75 | LDB | 63.4
90 | 87 | 742 | 75 | LWB | 63.4
90 | 87 | 742 | 75 | kW | 1.99
68 | 91 | 742 | 57 | MBh | 15.6
68 | 91 | 742 | 57 | S/T | 0.904
68 | 91 | 742 | 57 | ∆T | 17.6
68 | 91 | 742 | 57 | LDB | 50.4
68 | 91 | 742 | 57 | LWB | 49
68 | 91 | 742 | 57 | kW | 1.03
72 | 91 | 742 | 61 | MBh | 18.9
72 | 91 | 742 | 61 | S/T | 0.857
72 | 91 | 742 | 61 | ∆T | 20.2
72 | 91 | 742 | 61 | LDB | 51.8
72 | 91 | 742 | 61 | LWB | 51.8
72 | 91 | 742 | 61 | kW | 1.35
77 | 91 | 742 | 64 | MBh | 21.5
77 | 91 | 742 | 64 | S/T | 0.819
77 | 91 | 742 | 64 | ∆T | 22
77 | 91 | 742 | 64 | LDB | 55
77 | 91 | 742 | 64 | LWB | 54.2
77 | 91 | 742 | 64 | kW | 1.62
80 | 91 | 742 | 67 | MBh | 24
80 | 91 | 742 | 67 | S/T | 0.779
80 | 91 | 742 | 67 | ∆T | 23.3
80 | 91 | 742 | 67 | LDB | 56.7
80 | 91 | 742 | 67 | LWB | 56.7
80 | 91 | 742 | 67 | kW | 1.91
84 | 91 | 742 | 70 | MBh | 25.9
84 | 91 | 742 | 70 | S/T | 0.745
84 | 91 | 742 | 70 | ∆T | 24.1
84 | 91 | 742 | 70 | LDB | 59.9
84 | 91 | 742 | 70 | LWB | 59.6
84 | 91 | 742 | 70 | kW | 2.13
86 | 91 | 742 | 72 | MBh | 26.2
86 | 91 | 742 | 72 | S/T | 0.714
86 | 91 | 742 | 72 | ∆T | 23.3
86 | 91 | 742 | 72 | LDB | 62.7
86 | 91 | 742 | 72 | LWB | 62
86 | 91 | 742 | 72 | kW | 2.14
90 | 91 | 742 | 75 | MBh | 26.7
90 | 91 | 742 | 75 | S/T | 0.787
90 | 91 | 742 | 75 | ∆T | 26.2
90 | 91 | 742 | 75 | LDB | 63.8
90 | 91 | 742 | 75 | LWB | 63.8
90 | 91 | 742 | 75 | kW | 2.15
68 | 93 | 742 | 57 | MBh | 15.6
68 | 93 | 742 | 57 | S/T | 0.904
68 | 93 | 742 | 57 | ∆T | 17.6
68 | 93 | 742 | 57 | LDB | 50.4
68 | 93 | 742 | 57 | LWB | 49
68 | 93 | 742 | 57 | kW | 1.09
72 | 93 | 742 | 61 | MBh | 18.9
72 | 93 | 742 | 61 | S/T | 0.857
72 | 93 | 742 | 61 | ∆T | 20.2
72 | 93 | 742 | 61 | LDB | 51.8
72 | 93 | 742 | 61 | LWB | 51.8
72 | 93 | 742 | 61 | kW | 1.42
77 | 93 | 742 | 64 | MBh | 21.5
77 | 93 | 742 | 64 | S/T | 0.819
77 | 93 | 742 | 64 | ∆T | 22
77 | 93 | 742 | 64 | LDB | 55
77 | 93 | 742 | 64 | LWB | 54.2
77 | 93 | 742 | 64 | kW | 1.7
80 | 93 | 742 | 67 | MBh | 24
80 | 93 | 742 | 67 | S/T | 0.779
80 | 93 | 742 | 67 | ∆T | 23.3
80 | 93 | 742 | 67 | LDB | 56.7
80 | 93 | 742 | 67 | LWB | 56.7
80 | 93 | 742 | 67 | kW | 2.01
84 | 93 | 742 | 70 | MBh | 25.7
84 | 93 | 742 | 70 | S/T | 0.747
84 | 93 | 742 | 70 | ∆T | 24
84 | 93 | 742 | 70 | LDB | 60
84 | 93 | 742 | 70 | LWB | 59.7
84 | 93 | 742 | 70 | kW | 2.21
86 | 93 | 742 | 72 | MBh | 26
86 | 93 | 742 | 72 | S/T | 0.715
86 | 93 | 742 | 72 | ∆T | 23.2
86 | 93 | 742 | 72 | LDB | 62.8
86 | 93 | 742 | 72 | LWB | 62.1
86 | 93 | 742 | 72 | kW | 2.22
90 | 93 | 742 | 75 | MBh | 26.5
90 | 93 | 742 | 75 | S/T | 0.785
90 | 93 | 742 | 75 | ∆T | 26
90 | 93 | 742 | 75 | LDB | 64
90 | 93 | 742 | 75 | LWB | 64
90 | 93 | 742 | 75 | kW | 2.23
68 | 95 | 742 | 57 | MBh | 15.6
68 | 95 | 742 | 57 | S/T | 0.904
68 | 95 | 742 | 57 | ∆T | 17.6
68 | 95 | 742 | 57 | LDB | 50.4
68 | 95 | 742 | 57 | LWB | 49
68 | 95 | 742 | 57 | kW | 1.14
72 | 95 | 742 | 61 | MBh | 18.9
72 | 95 | 742 | 61 | S/T | 0.857
72 | 95 | 742 | 61 | ∆T | 20.2
72 | 95 | 742 | 61 | LDB | 51.8
72 | 95 | 742 | 61 | LWB | 51.8
72 | 95 | 742 | 61 | kW | 1.5
77 | 95 | 742 | 64 | MBh | 21.5
77 | 95 | 742 | 64 | S/T | 0.819
77 | 95 | 742 | 64 | ∆T | 22
77 | 95 | 742 | 64 | LDB | 55
77 | 95 | 742 | 64 | LWB | 54.2
77 | 95 | 742 | 64 | kW | 1.79
80 | 95 | 742 | 67 | MBh | 24
80 | 95 | 742 | 67 | S/T | 0.779
80 | 95 | 742 | 67 | ∆T | 23.3
80 | 95 | 742 | 67 | LDB | 56.7
80 | 95 | 742 | 67 | LWB | 56.7
80 | 95 | 742 | 67 | kW | 2.12
84 | 95 | 742 | 70 | MBh | 25.5
84 | 95 | 742 | 70 | S/T | 0.745
84 | 95 | 742 | 70 | ∆T | 23.7
84 | 95 | 742 | 70 | LDB | 60.3
84 | 95 | 742 | 70 | LWB | 59.8
84 | 95 | 742 | 70 | kW | 2.29
86 | 95 | 742 | 72 | MBh | 25.8
86 | 95 | 742 | 72 | S/T | 0.713
86 | 95 | 742 | 72 | ∆T | 23
86 | 95 | 742 | 72 | LDB | 63
86 | 95 | 742 | 72 | LWB | 62.1
86 | 95 | 742 | 72 | kW | 2.3
90 | 95 | 742 | 75 | MBh | 26.3
90 | 95 | 742 | 75 | S/T | 0.783
90 | 95 | 742 | 75 | ∆T | 25.7
90 | 95 | 742 | 75 | LDB | 64.3
90 | 95 | 742 | 75 | LWB | 64.3
90 | 95 | 742 | 75 | kW | 2.32
68 | 99 | 742 | 57 | MBh | 15.6
68 | 99 | 742 | 57 | S/T | 0.904
68 | 99 | 742 | 57 | ∆T | 17.6
68 | 99 | 742 | 57 | LDB | 50.4
68 | 99 | 742 | 57 | LWB | 49
68 | 99 | 742 | 57 | kW | 1.26
72 | 99 | 742 | 61 | MBh | 18.9
72 | 99 | 742 | 61 | S/T | 0.857
72 | 99 | 742 | 61 | ∆T | 20.2
72 | 99 | 742 | 61 | LDB | 51.8
72 | 99 | 742 | 61 | LWB | 51.8
72 | 99 | 742 | 61 | kW | 1.65
77 | 99 | 742 | 64 | MBh | 21.5
77 | 99 | 742 | 64 | S/T | 0.819
77 | 99 | 742 | 64 | ∆T | 22
77 | 99 | 742 | 64 | LDB | 55
77 | 99 | 742 | 64 | LWB | 54.2
77 | 99 | 742 | 64 | kW | 1.98
80 | 99 | 742 | 67 | MBh | 24
80 | 99 | 742 | 67 | S/T | 0.779
80 | 99 | 742 | 67 | ∆T | 23.3
80 | 99 | 742 | 67 | LDB | 56.7
80 | 99 | 742 | 67 | LWB | 56.7
80 | 99 | 742 | 67 | kW | 2.34
84 | 99 | 742 | 70 | MBh | 25
84 | 99 | 742 | 70 | S/T | 0.748
84 | 99 | 742 | 70 | ∆T | 23.3
84 | 99 | 742 | 70 | LDB | 60.7
84 | 99 | 742 | 70 | LWB | 60
84 | 99 | 742 | 70 | kW | 2.45
86 | 99 | 742 | 72 | MBh | 25.3
86 | 99 | 742 | 72 | S/T | 0.715
86 | 99 | 742 | 72 | ∆T | 22.6
86 | 99 | 742 | 72 | LDB | 63.4
86 | 99 | 742 | 72 | LWB | 62.4
86 | 99 | 742 | 72 | kW | 2.46
90 | 99 | 742 | 75 | MBh | 25.8
90 | 99 | 742 | 75 | S/T | 0.787
90 | 99 | 742 | 75 | ∆T | 25.3
90 | 99 | 742 | 75 | LDB | 64.7
90 | 99 | 742 | 75 | LWB | 64.7
90 | 99 | 742 | 75 | kW | 2.48
68 | 103 | 742 | 57 | MBh | 15.6
68 | 103 | 742 | 57 | S/T | 0.904
68 | 103 | 742 | 57 | ∆T | 17.6
68 | 103 | 742 | 57 | LDB | 50.4
68 | 103 | 742 | 57 | LWB | 49
68 | 103 | 742 | 57 | kW | 1.38
72 | 103 | 742 | 61 | MBh | 18.9
72 | 103 | 742 | 61 | S/T | 0.857
72 | 103 | 742 | 61 | ∆T | 20.2
72 | 103 | 742 | 61 | LDB | 51.8
72 | 103 | 742 | 61 | LWB | 51.8
72 | 103 | 742 | 61 | kW | 1.82
77 | 103 | 742 | 64 | MBh | 21.5
77 | 103 | 742 | 64 | S/T | 0.819
77 | 103 | 742 | 64 | ∆T | 22
77 | 103 | 742 | 64 | LDB | 55
77 | 103 | 742 | 64 | LWB | 54.2
77 | 103 | 742 | 64 | kW | 2.19
80 | 103 | 742 | 67 | MBh | 24
80 | 103 | 742 | 67 | S/T | 0.779
80 | 103 | 742 | 67 | ∆T | 23.3
80 | 103 | 742 | 67 | LDB | 56.7
80 | 103 | 742 | 67 | LWB | 56.7
80 | 103 | 742 | 67 | kW | 2.59
84 | 103 | 742 | 70 | MBh | 24.6
84 | 103 | 742 | 70 | S/T | 0.744
84 | 103 | 742 | 70 | ∆T | 22.8
84 | 103 | 742 | 70 | LDB | 61.2
84 | 103 | 742 | 70 | LWB | 60.2
84 | 103 | 742 | 70 | kW | 2.62
86 | 103 | 742 | 72 | MBh | 24.9
86 | 103 | 742 | 72 | S/T | 0.715
86 | 103 | 742 | 72 | ∆T | 22.2
86 | 103 | 742 | 72 | LDB | 63.8
86 | 103 | 742 | 72 | LWB | 62.5
86 | 103 | 742 | 72 | kW | 2.63
90 | 103 | 742 | 75 | MBh | 25.4
90 | 103 | 742 | 75 | S/T | 0.783
90 | 103 | 742 | 75 | ∆T | 24.8
90 | 103 | 742 | 75 | LDB | 65.2
90 | 103 | 742 | 75 | LWB | 65.2
90 | 103 | 742 | 75 | kW | 2.65
68 | 106 | 742 | 57 | MBh | 15.6
68 | 106 | 742 | 57 | S/T | 0.904
68 | 106 | 742 | 57 | ∆T | 17.6
68 | 106 | 742 | 57 | LDB | 50.4
68 | 106 | 742 | 57 | LWB | 49
68 | 106 | 742 | 57 | kW | 1.48
72 | 106 | 742 | 61 | MBh | 18.9
72 | 106 | 742 | 61 | S/T | 0.857
72 | 106 | 742 | 61 | ∆T | 20.2
72 | 106 | 742 | 61 | LDB | 51.8
72 | 106 | 742 | 61 | LWB | 51.8
72 | 106 | 742 | 61 | kW | 1.95
77 | 106 | 742 | 64 | MBh | 21.5
77 | 106 | 742 | 64 | S/T | 0.819
77 | 106 | 742 | 64 | ∆T | 22
77 | 106 | 742 | 64 | LDB | 55
77 | 106 | 742 | 64 | LWB | 54.2
77 | 106 | 742 | 64 | kW | 2.35
80 | 106 | 742 | 67 | MBh | 23.7
80 | 106 | 742 | 67 | S/T | 0.781
80 | 106 | 742 | 67 | ∆T | 23.1
80 | 106 | 742 | 67 | LDB | 56.9
80 | 106 | 742 | 67 | LWB | 56.9
80 | 106 | 742 | 67 | kW | 2.72
84 | 106 | 742 | 70 | MBh | 24.2
84 | 106 | 742 | 70 | S/T | 0.748
84 | 106 | 742 | 70 | ∆T | 22.6
84 | 106 | 742 | 70 | LDB | 61.4
84 | 106 | 742 | 70 | LWB | 60.4
84 | 106 | 742 | 70 | kW | 2.74
86 | 106 | 742 | 72 | MBh | 24.6
86 | 106 | 742 | 72 | S/T | 0.711
86 | 106 | 742 | 72 | ∆T | 21.8
86 | 106 | 742 | 72 | LDB | 64.2
86 | 106 | 742 | 72 | LWB | 62.7
86 | 106 | 742 | 72 | kW | 2.75
90 | 106 | 742 | 75 | MBh | 25.1
90 | 106 | 742 | 75 | S/T | 0.781
90 | 106 | 742 | 75 | ∆T | 24.5
90 | 106 | 742 | 75 | LDB | 65.5
90 | 106 | 742 | 75 | LWB | 65.5
90 | 106 | 742 | 75 | kW | 2.77
68 | 110 | 742 | 57 | MBh | 15.6
68 | 110 | 742 | 57 | S/T | 0.904
68 | 110 | 742 | 57 | ∆T | 17.6
68 | 110 | 742 | 57 | LDB | 50.4
68 | 110 | 742 | 57 | LWB | 49
68 | 110 | 742 | 57 | kW | 1.62
72 | 110 | 742 | 61 | MBh | 18.9
72 | 110 | 742 | 61 | S/T | 0.857
72 | 110 | 742 | 61 | ∆T | 20.2
72 | 110 | 742 | 61 | LDB | 51.8
72 | 110 | 742 | 61 | LWB | 51.8
72 | 110 | 742 | 61 | kW | 2.14
77 | 110 | 742 | 64 | MBh | 21.5
77 | 110 | 742 | 64 | S/T | 0.819
77 | 110 | 742 | 64 | ∆T | 22
77 | 110 | 742 | 64 | LDB | 55
77 | 110 | 742 | 64 | LWB | 54.2
77 | 110 | 742 | 64 | kW | 2.57
80 | 110 | 742 | 67 | MBh | 23.3
80 | 110 | 742 | 67 | S/T | 0.777
80 | 110 | 742 | 67 | ∆T | 22.6
80 | 110 | 742 | 67 | LDB | 57.4
80 | 110 | 742 | 67 | LWB | 57.1
80 | 110 | 742 | 67 | kW | 2.88
84 | 110 | 742 | 70 | MBh | 23.8
84 | 110 | 742 | 70 | S/T | 0.744
84 | 110 | 742 | 70 | ∆T | 22.1
84 | 110 | 742 | 70 | LDB | 61.9
84 | 110 | 742 | 70 | LWB | 60.5
84 | 110 | 742 | 70 | kW | 2.91
86 | 110 | 742 | 72 | MBh | 24.1
86 | 110 | 742 | 72 | S/T | 0.714
86 | 110 | 742 | 72 | ∆T | 21.5
86 | 110 | 742 | 72 | LDB | 64.5
86 | 110 | 742 | 72 | LWB | 62.9
86 | 110 | 742 | 72 | kW | 2.92
90 | 110 | 742 | 75 | MBh | 24.1
90 | 110 | 742 | 75 | S/T | 0.784
90 | 110 | 742 | 75 | ∆T | 23.6
90 | 110 | 742 | 75 | LDB | 66.4
90 | 110 | 742 | 75 | LWB | 66.4
90 | 110 | 742 | 75 | kW | 2.92
68 | 115 | 742 | 57 | MBh | 15.6
68 | 115 | 742 | 57 | S/T | 0.904
68 | 115 | 742 | 57 | ∆T | 17.6
68 | 115 | 742 | 57 | LDB | 50.4
68 | 115 | 742 | 57 | LWB | 49
68 | 115 | 742 | 57 | kW | 1.81
72 | 115 | 742 | 61 | MBh | 18.9
72 | 115 | 742 | 61 | S/T | 0.857
72 | 115 | 742 | 61 | ∆T | 20.2
72 | 115 | 742 | 61 | LDB | 51.8
72 | 115 | 742 | 61 | LWB | 51.8
72 | 115 | 742 | 61 | kW | 2.39
77 | 115 | 742 | 64 | MBh | 21.5
77 | 115 | 742 | 64 | S/T | 0.819
77 | 115 | 742 | 64 | ∆T | 22
77 | 115 | 742 | 64 | LDB | 55
77 | 115 | 742 | 64 | LWB | 54.2
77 | 115 | 742 | 64 | kW | 2.88
80 | 115 | 742 | 67 | MBh | 22.4
80 | 115 | 742 | 67 | S/T | 0.781
80 | 115 | 742 | 67 | ∆T | 21.8
80 | 115 | 742 | 67 | LDB | 58.2
80 | 115 | 742 | 67 | LWB | 57.5
80 | 115 | 742 | 67 | kW | 3.08
84 | 115 | 742 | 70 | MBh | 22.4
84 | 115 | 742 | 70 | S/T | 0.746
84 | 115 | 742 | 70 | ∆T | 20.8
84 | 115 | 742 | 70 | LDB | 63.2
84 | 115 | 742 | 70 | LWB | 61.1
84 | 115 | 742 | 70 | kW | 3.08
86 | 115 | 742 | 72 | MBh | 22.4
86 | 115 | 742 | 72 | S/T | 0.714
86 | 115 | 742 | 72 | ∆T | 20
86 | 115 | 742 | 72 | LDB | 66
86 | 115 | 742 | 72 | LWB | 63.6
86 | 115 | 742 | 72 | kW | 3.08
90 | 115 | 742 | 75 | MBh | 22.4
90 | 115 | 742 | 75 | S/T | 0.786
90 | 115 | 742 | 75 | ∆T | 22
90 | 115 | 742 | 75 | LDB | 68
90 | 115 | 742 | 75 | LWB | 67.1
90 | 115 | 742 | 75 | kW | 3.08
68 | 118 | 742 | 57 | MBh | 15.6
68 | 118 | 742 | 57 | S/T | 0.904
68 | 118 | 742 | 57 | ∆T | 17.6
68 | 118 | 742 | 57 | LDB | 50.4
68 | 118 | 742 | 57 | LWB | 49
68 | 118 | 742 | 57 | kW | 1.93
72 | 118 | 742 | 61 | MBh | 18.9
72 | 118 | 742 | 61 | S/T | 0.857
72 | 118 | 742 | 61 | ∆T | 20.2
72 | 118 | 742 | 61 | LDB | 51.8
72 | 118 | 742 | 61 | LWB | 51.8
72 | 118 | 742 | 61 | kW | 2.55
77 | 118 | 742 | 64 | MBh | 19.2
77 | 118 | 742 | 64 | S/T | 0.818
77 | 118 | 742 | 64 | ∆T | 19.6
77 | 118 | 742 | 64 | LDB | 57.4
77 | 118 | 742 | 64 | LWB | 55.4
77 | 118 | 742 | 64 | kW | 2.6
80 | 118 | 742 | 67 | MBh | 19.2
80 | 118 | 742 | 67 | S/T | 0.776
80 | 118 | 742 | 67 | ∆T | 18.6
80 | 118 | 742 | 67 | LDB | 61.4
80 | 118 | 742 | 67 | LWB | 59
80 | 118 | 742 | 67 | kW | 2.6
84 | 118 | 742 | 70 | MBh | 19.2
84 | 118 | 742 | 70 | S/T | 0.745
84 | 118 | 742 | 70 | ∆T | 17.8
84 | 118 | 742 | 70 | LDB | 66.2
84 | 118 | 742 | 70 | LWB | 62.5
84 | 118 | 742 | 70 | kW | 2.6
86 | 118 | 742 | 72 | MBh | 19.2
86 | 118 | 742 | 72 | S/T | 0.714
86 | 118 | 742 | 72 | ∆T | 17.1
86 | 118 | 742 | 72 | LDB | 68.9
86 | 118 | 742 | 72 | LWB | 64.9
86 | 118 | 742 | 72 | kW | 2.6
90 | 118 | 742 | 75 | MBh | 19.2
90 | 118 | 742 | 75 | S/T | 0.781
90 | 118 | 742 | 75 | ∆T | 18.7
90 | 118 | 742 | 75 | LDB | 71.3
90 | 118 | 742 | 75 | LWB | 68.4
90 | 118 | 742 | 75 | kW | 2.6
68 | 122 | 742 | 57 | MBh | 14.7
68 | 122 | 742 | 57 | S/T | 0.898
68 | 122 | 742 | 57 | ∆T | 16.5
68 | 122 | 742 | 57 | LDB | 51.5
68 | 122 | 742 | 57 | LWB | 49.5
68 | 122 | 742 | 57 | kW | 1.93
72 | 122 | 742 | 61 | MBh | 14.7
72 | 122 | 742 | 61 | S/T | 0.85
72 | 122 | 742 | 61 | ∆T | 15.6
72 | 122 | 742 | 61 | LDB | 56.4
72 | 122 | 742 | 61 | LWB | 54.1
72 | 122 | 742 | 61 | kW | 1.93
77 | 122 | 742 | 64 | MBh | 14.7
77 | 122 | 742 | 64 | S/T | 0.816
77 | 122 | 742 | 64 | ∆T | 15
77 | 122 | 742 | 64 | LDB | 62
77 | 122 | 742 | 64 | LWB | 57.5
77 | 122 | 742 | 64 | kW | 1.93
80 | 122 | 742 | 67 | MBh | 14.7
80 | 122 | 742 | 67 | S/T | 0.776
80 | 122 | 742 | 67 | ∆T | 14.2
80 | 122 | 742 | 67 | LDB | 65.8
80 | 122 | 742 | 67 | LWB | 61
80 | 122 | 742 | 67 | kW | 1.93
84 | 122 | 742 | 70 | MBh | 14.7
84 | 122 | 742 | 70 | S/T | 0.741
84 | 122 | 742 | 70 | ∆T | 13.6
84 | 122 | 742 | 70 | LDB | 70.4
84 | 122 | 742 | 70 | LWB | 64.4
84 | 122 | 742 | 70 | kW | 1.93
86 | 122 | 742 | 72 | MBh | 14.7
86 | 122 | 742 | 72 | S/T | 0.714
86 | 122 | 742 | 72 | ∆T | 13.1
86 | 122 | 742 | 72 | LDB | 72.9
86 | 122 | 742 | 72 | LWB | 66.6
86 | 122 | 742 | 72 | kW | 1.93
90 | 122 | 742 | 75 | MBh | 14.7
90 | 122 | 742 | 75 | S/T | 0.782
90 | 122 | 742 | 75 | ∆T | 14.4
90 | 122 | 742 | 75 | LDB | 75.6
90 | 122 | 742 | 75 | LWB | 70
90 | 122 | 742 | 75 | kW | 1.93

## RZA30AAVJU - FBA30AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1094 | 57 | MBh | 19.5 | 64 | 60 | 61 | 40.8 | 3.16
68 | 23 | 1094 | 57 | S/T | 0.882 | 64 | 60 | 65 | 37.8 | 2.88
68 | 23 | 1094 | 57 | ∆T | 14.6 | 64 | 60 | 68 | 35.5 | 2.68
68 | 23 | 1094 | 57 | LDB | 53.4 | 64 | 60 | 70 | 34 | 2.55
68 | 23 | 1094 | 57 | LWB | 50.3 | 64 | 60 | 72 | 32.5 | 2.42
68 | 23 | 1094 | 57 | kW | 0.71 | 64 | 60 | 75 | 30.2 | 2.22
72 | 23 | 1094 | 61 | MBh | 23.7 | 60 | 56 | 61 | 40.8 | 3.28
72 | 23 | 1094 | 61 | S/T | 0.844 | 60 | 56 | 65 | 37.8 | 3
72 | 23 | 1094 | 61 | ∆T | 16.9 | 60 | 56 | 68 | 35.5 | 2.79
72 | 23 | 1094 | 61 | LDB | 55.1 | 60 | 56 | 70 | 34 | 2.65
72 | 23 | 1094 | 61 | LWB | 53.4 | 60 | 56 | 72 | 32.5 | 2.51
72 | 23 | 1094 | 61 | kW | 0.87 | 60 | 56 | 75 | 30.2 | 2.31
77 | 23 | 1094 | 64 | MBh | 26.8 | 57 | 53 | 61 | 40.8 | 3.38
77 | 23 | 1094 | 64 | S/T | 0.817 | 57 | 53 | 65 | 37.8 | 3.09
77 | 23 | 1094 | 64 | ∆T | 18.5 | 57 | 53 | 68 | 35.5 | 2.87
77 | 23 | 1094 | 64 | LDB | 58.5 | 57 | 53 | 70 | 34 | 2.73
77 | 23 | 1094 | 64 | LWB | 55.9 | 57 | 53 | 72 | 32.5 | 2.59
77 | 23 | 1094 | 64 | kW | 1 | 57 | 53 | 75 | 30.2 | 2.38
80 | 23 | 1094 | 67 | MBh | 30 | 54 | 50 | 61 | 40.8 | 3.48
80 | 23 | 1094 | 67 | S/T | 0.78 | 54 | 50 | 65 | 37.8 | 3.18
80 | 23 | 1094 | 67 | ∆T | 19.8 | 54 | 50 | 68 | 35.5 | 2.96
80 | 23 | 1094 | 67 | LDB | 60.2 | 54 | 50 | 70 | 34 | 2.81
80 | 23 | 1094 | 67 | LWB | 58.4 | 54 | 50 | 72 | 32.5 | 2.67
80 | 23 | 1094 | 67 | kW | 1.14 | 54 | 50 | 75 | 30.2 | 2.45
84 | 23 | 1094 | 70 | MBh | 33.2 | 51 | 47 | 61 | 40.8 | 3.59
84 | 23 | 1094 | 70 | S/T | 0.744 | 51 | 47 | 65 | 37.8 | 3.28
84 | 23 | 1094 | 70 | ∆T | 20.9 | 51 | 47 | 68 | 35.5 | 3.05
84 | 23 | 1094 | 70 | LDB | 63.1 | 51 | 47 | 70 | 34 | 2.9
84 | 23 | 1094 | 70 | LWB | 61.1 | 51 | 47 | 72 | 32.5 | 2.75
84 | 23 | 1094 | 70 | kW | 1.28 | 51 | 47 | 75 | 30.2 | 2.53
86 | 23 | 1094 | 72 | MBh | 35.3 | 47 | 43 | 61 | 40.8 | 3.75
86 | 23 | 1094 | 72 | S/T | 0.711 | 47 | 43 | 65 | 37.8 | 3.43
86 | 23 | 1094 | 72 | ∆T | 21.2 | 47 | 43 | 68 | 35.5 | 3.19
86 | 23 | 1094 | 72 | LDB | 64.8 | 47 | 43 | 70 | 34 | 3.03
86 | 23 | 1094 | 72 | LWB | 62.9 | 47 | 43 | 72 | 32.5 | 2.87
86 | 23 | 1094 | 72 | kW | 1.37 | 47 | 43 | 75 | 30.2 | 2.64
90 | 23 | 1094 | 75 | MBh | 38.4 | 44 | 40 | 61 | 40.8 | 3.88
90 | 23 | 1094 | 75 | S/T | 0.693 | 44 | 40 | 65 | 37.8 | 3.55
90 | 23 | 1094 | 75 | ∆T | 22.5 | 44 | 40 | 68 | 35.5 | 3.3
90 | 23 | 1094 | 75 | LDB | 67.5 | 44 | 40 | 70 | 34 | 3.13
90 | 23 | 1094 | 75 | LWB | 65.8 | 44 | 40 | 72 | 32.5 | 2.97
90 | 23 | 1094 | 75 | kW | 1.51 | 44 | 40 | 75 | 30.2 | 2.73
68 | 30 | 1094 | 57 | MBh | 19.5 | 39 | 36 | 61 | 40.8 | 4.07
68 | 30 | 1094 | 57 | S/T | 0.882 | 39 | 36 | 65 | 37.8 | 3.72
68 | 30 | 1094 | 57 | ∆T | 14.6 | 39 | 36 | 68 | 35.5 | 3.45
68 | 30 | 1094 | 57 | LDB | 53.4 | 39 | 36 | 70 | 34 | 3.28
68 | 30 | 1094 | 57 | LWB | 50.3 | 39 | 36 | 72 | 32.5 | 3.11
68 | 30 | 1094 | 57 | kW | 0.73 | 39 | 36 | 75 | 30.2 | 2.86
72 | 30 | 1094 | 61 | MBh | 23.7 | 35 | 32 | 61 | 40.8 | 4.27
72 | 30 | 1094 | 61 | S/T | 0.844 | 35 | 32 | 65 | 37.8 | 3.9
72 | 30 | 1094 | 61 | ∆T | 16.9 | 35 | 32 | 68 | 35.5 | 3.63
72 | 30 | 1094 | 61 | LDB | 55.1 | 35 | 32 | 70 | 34 | 3.45
72 | 30 | 1094 | 61 | LWB | 53.4 | 35 | 32 | 72 | 32.5 | 3.27
72 | 30 | 1094 | 61 | kW | 0.9 | 35 | 32 | 75 | 30.2 | 3
77 | 30 | 1094 | 64 | MBh | 26.8 | 30 | 28 | 61 | 40.8 | 4.49
77 | 30 | 1094 | 64 | S/T | 0.817 | 30 | 28 | 65 | 37.8 | 4.1
77 | 30 | 1094 | 64 | ∆T | 18.5 | 30 | 28 | 68 | 35.5 | 3.82
77 | 30 | 1094 | 64 | LDB | 58.5 | 30 | 28 | 70 | 34 | 3.62
77 | 30 | 1094 | 64 | LWB | 55.9 | 30 | 28 | 72 | 32.5 | 3.44
77 | 30 | 1094 | 64 | kW | 1.04 | 30 | 28 | 75 | 30.2 | 3.16
80 | 30 | 1094 | 67 | MBh | 30 | 26 | 24 | 61 | 40.8 | 4.74
80 | 30 | 1094 | 67 | S/T | 0.78 | 26 | 24 | 65 | 37.8 | 4.33
80 | 30 | 1094 | 67 | ∆T | 19.8 | 26 | 24 | 68 | 35.5 | 4.02
80 | 30 | 1094 | 67 | LDB | 60.2 | 26 | 24 | 70 | 34 | 3.82
80 | 30 | 1094 | 67 | LWB | 58.4 | 26 | 24 | 72 | 32.5 | 3.62
80 | 30 | 1094 | 67 | kW | 1.17 | 26 | 24 | 75 | 30.2 | 3.33
84 | 30 | 1094 | 70 | MBh | 33.2 | 22 | 20 | 61 | 40.8 | 4.96
84 | 30 | 1094 | 70 | S/T | 0.744 | 22 | 20 | 65 | 37.8 | 4.58
84 | 30 | 1094 | 70 | ∆T | 20.9 | 22 | 20 | 68 | 35.5 | 4.26
84 | 30 | 1094 | 70 | LDB | 63.1 | 22 | 20 | 70 | 34 | 4.04
84 | 30 | 1094 | 70 | LWB | 61.1 | 22 | 20 | 72 | 32.5 | 3.83
84 | 30 | 1094 | 70 | kW | 1.32 | 22 | 20 | 75 | 30.2 | 3.52
86 | 30 | 1094 | 72 | MBh | 35.3 | 19 | 18 | 61 | 40.8 | 4.83
86 | 30 | 1094 | 72 | S/T | 0.711 | 19 | 18 | 65 | 37.8 | 4.71
86 | 30 | 1094 | 72 | ∆T | 21.2 | 19 | 18 | 68 | 35.5 | 4.38
86 | 30 | 1094 | 72 | LDB | 64.8 | 19 | 18 | 70 | 34 | 4.16
86 | 30 | 1094 | 72 | LWB | 62.9 | 19 | 18 | 72 | 32.5 | 3.94
86 | 30 | 1094 | 72 | kW | 1.42 | 19 | 18 | 75 | 30.2 | 3.62
90 | 30 | 1094 | 75 | MBh | 38.4 | 17 | 16 | 61 | 40.2 | 4.65
90 | 30 | 1094 | 75 | S/T | 0.693 | 17 | 16 | 65 | 37.8 | 4.89
90 | 30 | 1094 | 75 | ∆T | 22.5 | 17 | 16 | 68 | 35.5 | 4.55
90 | 30 | 1094 | 75 | LDB | 67.5 | 17 | 16 | 70 | 34 | 4.32
90 | 30 | 1094 | 75 | LWB | 65.8 | 17 | 16 | 72 | 32.5 | 4.09
90 | 30 | 1094 | 75 | kW | 1.56 | 17 | 16 | 75 | 30.2 | 3.76
68 | 40 | 1094 | 57 | MBh | 19.5 | 15 | 14 | 61 | 39.4 | 4.54
68 | 40 | 1094 | 57 | S/T | 0.882 | 15 | 14 | 65 | 37.8 | 4.95
68 | 40 | 1094 | 57 | ∆T | 14.6 | 15 | 14 | 68 | 35.5 | 4.65
68 | 40 | 1094 | 57 | LDB | 53.4 | 15 | 14 | 70 | 34 | 4.42
68 | 40 | 1094 | 57 | LWB | 50.3 | 15 | 14 | 72 | 32.5 | 4.19
68 | 40 | 1094 | 57 | kW | 0.76 | 15 | 14 | 75 | 30.2 | 3.85
72 | 40 | 1094 | 61 | MBh | 23.7 | 13 | 12 | 61 | 38.4 | 4.39
72 | 40 | 1094 | 61 | S/T | 0.844 | 13 | 12 | 65 | 37.8 | 4.81
72 | 40 | 1094 | 61 | ∆T | 16.9 | 13 | 12 | 68 | 35.5 | 4.8
72 | 40 | 1094 | 61 | LDB | 55.1 | 13 | 12 | 70 | 34 | 4.56
72 | 40 | 1094 | 61 | LWB | 53.4 | 13 | 12 | 72 | 32.5 | 4.32
72 | 40 | 1094 | 61 | kW | 0.94 | 13 | 12 | 75 | 30.2 | 3.97
77 | 40 | 1094 | 64 | MBh | 26.8 | 10 | 9 | 61 | 36.6 | 4.1
77 | 40 | 1094 | 64 | S/T | 0.817 | 10 | 9 | 65 | 36.6 | 4.54
77 | 40 | 1094 | 64 | ∆T | 18.5 | 10 | 9 | 68 | 35.5 | 4.87
77 | 40 | 1094 | 64 | LDB | 58.5 | 10 | 9 | 70 | 34 | 4.83
77 | 40 | 1094 | 64 | LWB | 55.9 | 10 | 9 | 72 | 32.5 | 4.58
77 | 40 | 1094 | 64 | kW | 1.09 | 10 | 9 | 75 | 30.2 | 4.2
80 | 40 | 1094 | 67 | MBh | 30 | 6 | 5 | 61 | 34.8 | 3.79
80 | 40 | 1094 | 67 | S/T | 0.78 | 6 | 5 | 65 | 34.8 | 4.25
80 | 40 | 1094 | 67 | ∆T | 19.8 | 6 | 5 | 68 | 34.8 | 4.6
80 | 40 | 1094 | 67 | LDB | 60.2 | 6 | 5 | 70 | 34 | 4.83
80 | 40 | 1094 | 67 | LWB | 58.4 | 6 | 5 | 72 | 32.5 | 4.86
80 | 40 | 1094 | 67 | kW | 1.23 | 6 | 5 | 75 | 30.2 | 4.46
84 | 40 | 1094 | 70 | MBh | 33.2 | -2 | -2 | 61 | 31.2 | 3.02
84 | 40 | 1094 | 70 | S/T | 0.744 | -2 | -2 | 65 | 31.2 | 3.54
84 | 40 | 1094 | 70 | ∆T | 20.9 | -2 | -2 | 68 | 31.2 | 3.93
84 | 40 | 1094 | 70 | LDB | 63.1 | -2 | -2 | 70 | 31.2 | 4.18
84 | 40 | 1094 | 70 | LWB | 61.1 | -2 | -2 | 72 | 31.2 | 4.44
84 | 40 | 1094 | 70 | kW | 1.38 | -2 | -2 | 75 | 30.2 | 4.83
86 | 40 | 1094 | 72 | MBh | 35.3 | -4 | -4 | 61 | 30.3 | 2.8
86 | 40 | 1094 | 72 | S/T | 0.711 | -4 | -4 | 65 | 30.3 | 3.33
86 | 40 | 1094 | 72 | ∆T | 21.2 | -4 | -4 | 68 | 30.3 | 3.73
86 | 40 | 1094 | 72 | LDB | 64.8 | -4 | -4 | 70 | 30.3 | 4
86 | 40 | 1094 | 72 | LWB | 62.9 | -4 | -4 | 72 | 30.3 | 4.27
86 | 40 | 1094 | 72 | kW | 1.49 | -4 | -4 | 75 | 30.2 | 4.67
90 | 40 | 1094 | 75 | MBh | 38.4
90 | 40 | 1094 | 75 | S/T | 0.693
90 | 40 | 1094 | 75 | ∆T | 22.5
90 | 40 | 1094 | 75 | LDB | 67.5
90 | 40 | 1094 | 75 | LWB | 65.8
90 | 40 | 1094 | 75 | kW | 1.64
68 | 50 | 1094 | 57 | MBh | 19.5
68 | 50 | 1094 | 57 | S/T | 0.882
68 | 50 | 1094 | 57 | ∆T | 14.6
68 | 50 | 1094 | 57 | LDB | 53.4
68 | 50 | 1094 | 57 | LWB | 50.3
68 | 50 | 1094 | 57 | kW | 0.8
72 | 50 | 1094 | 61 | MBh | 23.7
72 | 50 | 1094 | 61 | S/T | 0.844
72 | 50 | 1094 | 61 | ∆T | 16.9
72 | 50 | 1094 | 61 | LDB | 55.1
72 | 50 | 1094 | 61 | LWB | 53.4
72 | 50 | 1094 | 61 | kW | 0.99
77 | 50 | 1094 | 64 | MBh | 26.8
77 | 50 | 1094 | 64 | S/T | 0.817
77 | 50 | 1094 | 64 | ∆T | 18.5
77 | 50 | 1094 | 64 | LDB | 58.5
77 | 50 | 1094 | 64 | LWB | 55.9
77 | 50 | 1094 | 64 | kW | 1.14
80 | 50 | 1094 | 67 | MBh | 30
80 | 50 | 1094 | 67 | S/T | 0.78
80 | 50 | 1094 | 67 | ∆T | 19.8
80 | 50 | 1094 | 67 | LDB | 60.2
80 | 50 | 1094 | 67 | LWB | 58.4
80 | 50 | 1094 | 67 | kW | 1.3
84 | 50 | 1094 | 70 | MBh | 33.2
84 | 50 | 1094 | 70 | S/T | 0.744
84 | 50 | 1094 | 70 | ∆T | 20.9
84 | 50 | 1094 | 70 | LDB | 63.1
84 | 50 | 1094 | 70 | LWB | 61.1
84 | 50 | 1094 | 70 | kW | 1.45
86 | 50 | 1094 | 72 | MBh | 35.3
86 | 50 | 1094 | 72 | S/T | 0.711
86 | 50 | 1094 | 72 | ∆T | 21.2
86 | 50 | 1094 | 72 | LDB | 64.8
86 | 50 | 1094 | 72 | LWB | 62.9
86 | 50 | 1094 | 72 | kW | 1.56
90 | 50 | 1094 | 75 | MBh | 38.4
90 | 50 | 1094 | 75 | S/T | 0.693
90 | 50 | 1094 | 75 | ∆T | 22.5
90 | 50 | 1094 | 75 | LDB | 67.5
90 | 50 | 1094 | 75 | LWB | 65.8
90 | 50 | 1094 | 75 | kW | 1.72
68 | 54 | 1094 | 57 | MBh | 19.5
68 | 54 | 1094 | 57 | S/T | 0.882
68 | 54 | 1094 | 57 | ∆T | 14.6
68 | 54 | 1094 | 57 | LDB | 53.4
68 | 54 | 1094 | 57 | LWB | 50.3
68 | 54 | 1094 | 57 | kW | 0.82
72 | 54 | 1094 | 61 | MBh | 23.7
72 | 54 | 1094 | 61 | S/T | 0.844
72 | 54 | 1094 | 61 | ∆T | 16.9
72 | 54 | 1094 | 61 | LDB | 55.1
72 | 54 | 1094 | 61 | LWB | 53.4
72 | 54 | 1094 | 61 | kW | 1.01
77 | 54 | 1094 | 64 | MBh | 26.8
77 | 54 | 1094 | 64 | S/T | 0.817
77 | 54 | 1094 | 64 | ∆T | 18.5
77 | 54 | 1094 | 64 | LDB | 58.5
77 | 54 | 1094 | 64 | LWB | 55.9
77 | 54 | 1094 | 64 | kW | 1.16
80 | 54 | 1094 | 67 | MBh | 30
80 | 54 | 1094 | 67 | S/T | 0.78
80 | 54 | 1094 | 67 | ∆T | 19.8
80 | 54 | 1094 | 67 | LDB | 60.2
80 | 54 | 1094 | 67 | LWB | 58.4
80 | 54 | 1094 | 67 | kW | 1.32
84 | 54 | 1094 | 70 | MBh | 33.2
84 | 54 | 1094 | 70 | S/T | 0.744
84 | 54 | 1094 | 70 | ∆T | 20.9
84 | 54 | 1094 | 70 | LDB | 63.1
84 | 54 | 1094 | 70 | LWB | 61.1
84 | 54 | 1094 | 70 | kW | 1.48
86 | 54 | 1094 | 72 | MBh | 35.3
86 | 54 | 1094 | 72 | S/T | 0.711
86 | 54 | 1094 | 72 | ∆T | 21.2
86 | 54 | 1094 | 72 | LDB | 64.8
86 | 54 | 1094 | 72 | LWB | 62.9
86 | 54 | 1094 | 72 | kW | 1.59
90 | 54 | 1094 | 75 | MBh | 38.4
90 | 54 | 1094 | 75 | S/T | 0.693
90 | 54 | 1094 | 75 | ∆T | 22.5
90 | 54 | 1094 | 75 | LDB | 67.5
90 | 54 | 1094 | 75 | LWB | 65.8
90 | 54 | 1094 | 75 | kW | 1.76
68 | 58 | 1094 | 57 | MBh | 19.5
68 | 58 | 1094 | 57 | S/T | 0.882
68 | 58 | 1094 | 57 | ∆T | 14.6
68 | 58 | 1094 | 57 | LDB | 53.4
68 | 58 | 1094 | 57 | LWB | 50.3
68 | 58 | 1094 | 57 | kW | 0.83
72 | 58 | 1094 | 61 | MBh | 23.7
72 | 58 | 1094 | 61 | S/T | 0.844
72 | 58 | 1094 | 61 | ∆T | 16.9
72 | 58 | 1094 | 61 | LDB | 55.1
72 | 58 | 1094 | 61 | LWB | 53.4
72 | 58 | 1094 | 61 | kW | 1.03
77 | 58 | 1094 | 64 | MBh | 26.8
77 | 58 | 1094 | 64 | S/T | 0.817
77 | 58 | 1094 | 64 | ∆T | 18.5
77 | 58 | 1094 | 64 | LDB | 58.5
77 | 58 | 1094 | 64 | LWB | 55.9
77 | 58 | 1094 | 64 | kW | 1.19
80 | 58 | 1094 | 67 | MBh | 30
80 | 58 | 1094 | 67 | S/T | 0.78
80 | 58 | 1094 | 67 | ∆T | 19.8
80 | 58 | 1094 | 67 | LDB | 60.2
80 | 58 | 1094 | 67 | LWB | 58.4
80 | 58 | 1094 | 67 | kW | 1.35
84 | 58 | 1094 | 70 | MBh | 33.2
84 | 58 | 1094 | 70 | S/T | 0.744
84 | 58 | 1094 | 70 | ∆T | 20.9
84 | 58 | 1094 | 70 | LDB | 63.1
84 | 58 | 1094 | 70 | LWB | 61.1
84 | 58 | 1094 | 70 | kW | 1.52
86 | 58 | 1094 | 72 | MBh | 35.3
86 | 58 | 1094 | 72 | S/T | 0.711
86 | 58 | 1094 | 72 | ∆T | 21.2
86 | 58 | 1094 | 72 | LDB | 64.8
86 | 58 | 1094 | 72 | LWB | 62.9
86 | 58 | 1094 | 72 | kW | 1.63
90 | 58 | 1094 | 75 | MBh | 38.1
90 | 58 | 1094 | 75 | S/T | 0.693
90 | 58 | 1094 | 75 | ∆T | 22.3
90 | 58 | 1094 | 75 | LDB | 67.7
90 | 58 | 1094 | 75 | LWB | 65.8
90 | 58 | 1094 | 75 | kW | 1.77
68 | 62 | 1094 | 57 | MBh | 19.5
68 | 62 | 1094 | 57 | S/T | 0.882
68 | 62 | 1094 | 57 | ∆T | 14.6
68 | 62 | 1094 | 57 | LDB | 53.4
68 | 62 | 1094 | 57 | LWB | 50.3
68 | 62 | 1094 | 57 | kW | 0.85
72 | 62 | 1094 | 61 | MBh | 23.7
72 | 62 | 1094 | 61 | S/T | 0.844
72 | 62 | 1094 | 61 | ∆T | 16.9
72 | 62 | 1094 | 61 | LDB | 55.1
72 | 62 | 1094 | 61 | LWB | 53.4
72 | 62 | 1094 | 61 | kW | 1.05
77 | 62 | 1094 | 64 | MBh | 26.8
77 | 62 | 1094 | 64 | S/T | 0.817
77 | 62 | 1094 | 64 | ∆T | 18.5
77 | 62 | 1094 | 64 | LDB | 58.5
77 | 62 | 1094 | 64 | LWB | 55.9
77 | 62 | 1094 | 64 | kW | 1.21
80 | 62 | 1094 | 67 | MBh | 30
80 | 62 | 1094 | 67 | S/T | 0.78
80 | 62 | 1094 | 67 | ∆T | 19.8
80 | 62 | 1094 | 67 | LDB | 60.2
80 | 62 | 1094 | 67 | LWB | 58.4
80 | 62 | 1094 | 67 | kW | 1.38
84 | 62 | 1094 | 70 | MBh | 33.2
84 | 62 | 1094 | 70 | S/T | 0.744
84 | 62 | 1094 | 70 | ∆T | 20.9
84 | 62 | 1094 | 70 | LDB | 63.1
84 | 62 | 1094 | 70 | LWB | 61.1
84 | 62 | 1094 | 70 | kW | 1.55
86 | 62 | 1094 | 72 | MBh | 35.3
86 | 62 | 1094 | 72 | S/T | 0.711
86 | 62 | 1094 | 72 | ∆T | 21.2
86 | 62 | 1094 | 72 | LDB | 64.8
86 | 62 | 1094 | 72 | LWB | 62.9
86 | 62 | 1094 | 72 | kW | 1.66
90 | 62 | 1094 | 75 | MBh | 37.5
90 | 62 | 1094 | 75 | S/T | 0.693
90 | 62 | 1094 | 75 | ∆T | 22
90 | 62 | 1094 | 75 | LDB | 68
90 | 62 | 1094 | 75 | LWB | 66
90 | 62 | 1094 | 75 | kW | 1.76
68 | 66 | 1094 | 57 | MBh | 19.5
68 | 66 | 1094 | 57 | S/T | 0.882
68 | 66 | 1094 | 57 | ∆T | 14.6
68 | 66 | 1094 | 57 | LDB | 53.4
68 | 66 | 1094 | 57 | LWB | 50.3
68 | 66 | 1094 | 57 | kW | 0.87
72 | 66 | 1094 | 61 | MBh | 23.7
72 | 66 | 1094 | 61 | S/T | 0.844
72 | 66 | 1094 | 61 | ∆T | 16.9
72 | 66 | 1094 | 61 | LDB | 55.1
72 | 66 | 1094 | 61 | LWB | 53.4
72 | 66 | 1094 | 61 | kW | 1.08
77 | 66 | 1094 | 64 | MBh | 26.8
77 | 66 | 1094 | 64 | S/T | 0.817
77 | 66 | 1094 | 64 | ∆T | 18.5
77 | 66 | 1094 | 64 | LDB | 58.5
77 | 66 | 1094 | 64 | LWB | 55.9
77 | 66 | 1094 | 64 | kW | 1.24
80 | 66 | 1094 | 67 | MBh | 30
80 | 66 | 1094 | 67 | S/T | 0.78
80 | 66 | 1094 | 67 | ∆T | 19.8
80 | 66 | 1094 | 67 | LDB | 60.2
80 | 66 | 1094 | 67 | LWB | 58.4
80 | 66 | 1094 | 67 | kW | 1.41
84 | 66 | 1094 | 70 | MBh | 33.2
84 | 66 | 1094 | 70 | S/T | 0.744
84 | 66 | 1094 | 70 | ∆T | 20.9
84 | 66 | 1094 | 70 | LDB | 63.1
84 | 66 | 1094 | 70 | LWB | 61.1
84 | 66 | 1094 | 70 | kW | 1.58
86 | 66 | 1094 | 72 | MBh | 35.3
86 | 66 | 1094 | 72 | S/T | 0.711
86 | 66 | 1094 | 72 | ∆T | 21.2
86 | 66 | 1094 | 72 | LDB | 64.8
86 | 66 | 1094 | 72 | LWB | 62.9
86 | 66 | 1094 | 72 | kW | 1.7
90 | 66 | 1094 | 75 | MBh | 36.9
90 | 66 | 1094 | 75 | S/T | 0.694
90 | 66 | 1094 | 75 | ∆T | 21.7
90 | 66 | 1094 | 75 | LDB | 68.3
90 | 66 | 1094 | 75 | LWB | 66.2
90 | 66 | 1094 | 75 | kW | 1.75
68 | 70 | 1094 | 57 | MBh | 19.5
68 | 70 | 1094 | 57 | S/T | 0.882
68 | 70 | 1094 | 57 | ∆T | 14.6
68 | 70 | 1094 | 57 | LDB | 53.4
68 | 70 | 1094 | 57 | LWB | 50.3
68 | 70 | 1094 | 57 | kW | 0.88
72 | 70 | 1094 | 61 | MBh | 23.7
72 | 70 | 1094 | 61 | S/T | 0.844
72 | 70 | 1094 | 61 | ∆T | 16.9
72 | 70 | 1094 | 61 | LDB | 55.1
72 | 70 | 1094 | 61 | LWB | 53.4
72 | 70 | 1094 | 61 | kW | 1.1
77 | 70 | 1094 | 64 | MBh | 26.8
77 | 70 | 1094 | 64 | S/T | 0.817
77 | 70 | 1094 | 64 | ∆T | 18.5
77 | 70 | 1094 | 64 | LDB | 58.5
77 | 70 | 1094 | 64 | LWB | 55.9
77 | 70 | 1094 | 64 | kW | 1.27
80 | 70 | 1094 | 67 | MBh | 30
80 | 70 | 1094 | 67 | S/T | 0.78
80 | 70 | 1094 | 67 | ∆T | 19.8
80 | 70 | 1094 | 67 | LDB | 60.2
80 | 70 | 1094 | 67 | LWB | 58.4
80 | 70 | 1094 | 67 | kW | 1.44
84 | 70 | 1094 | 70 | MBh | 33.2
84 | 70 | 1094 | 70 | S/T | 0.744
84 | 70 | 1094 | 70 | ∆T | 20.9
84 | 70 | 1094 | 70 | LDB | 63.1
84 | 70 | 1094 | 70 | LWB | 61.1
84 | 70 | 1094 | 70 | kW | 1.62
86 | 70 | 1094 | 72 | MBh | 35.3
86 | 70 | 1094 | 72 | S/T | 0.711
86 | 70 | 1094 | 72 | ∆T | 21.2
86 | 70 | 1094 | 72 | LDB | 64.8
86 | 70 | 1094 | 72 | LWB | 62.9
86 | 70 | 1094 | 72 | kW | 1.74
90 | 70 | 1094 | 75 | MBh | 36.4
90 | 70 | 1094 | 75 | S/T | 0.692
90 | 70 | 1094 | 75 | ∆T | 21.3
90 | 70 | 1094 | 75 | LDB | 68.7
90 | 70 | 1094 | 75 | LWB | 66.3
90 | 70 | 1094 | 75 | kW | 1.73
68 | 72 | 1094 | 57 | MBh | 19.5
68 | 72 | 1094 | 57 | S/T | 0.882
68 | 72 | 1094 | 57 | ∆T | 14.6
68 | 72 | 1094 | 57 | LDB | 53.4
68 | 72 | 1094 | 57 | LWB | 50.3
68 | 72 | 1094 | 57 | kW | 0.89
72 | 72 | 1094 | 61 | MBh | 23.7
72 | 72 | 1094 | 61 | S/T | 0.844
72 | 72 | 1094 | 61 | ∆T | 16.9
72 | 72 | 1094 | 61 | LDB | 55.1
72 | 72 | 1094 | 61 | LWB | 53.4
72 | 72 | 1094 | 61 | kW | 1.11
77 | 72 | 1094 | 64 | MBh | 26.8
77 | 72 | 1094 | 64 | S/T | 0.817
77 | 72 | 1094 | 64 | ∆T | 18.5
77 | 72 | 1094 | 64 | LDB | 58.5
77 | 72 | 1094 | 64 | LWB | 55.9
77 | 72 | 1094 | 64 | kW | 1.28
80 | 72 | 1094 | 67 | MBh | 30
80 | 72 | 1094 | 67 | S/T | 0.78
80 | 72 | 1094 | 67 | ∆T | 19.8
80 | 72 | 1094 | 67 | LDB | 60.2
80 | 72 | 1094 | 67 | LWB | 58.4
80 | 72 | 1094 | 67 | kW | 1.46
84 | 72 | 1094 | 70 | MBh | 33.2
84 | 72 | 1094 | 70 | S/T | 0.744
84 | 72 | 1094 | 70 | ∆T | 20.9
84 | 72 | 1094 | 70 | LDB | 63.1
84 | 72 | 1094 | 70 | LWB | 61.1
84 | 72 | 1094 | 70 | kW | 1.64
86 | 72 | 1094 | 72 | MBh | 35.3
86 | 72 | 1094 | 72 | S/T | 0.711
86 | 72 | 1094 | 72 | ∆T | 21.2
86 | 72 | 1094 | 72 | LDB | 64.8
86 | 72 | 1094 | 72 | LWB | 62.9
86 | 72 | 1094 | 72 | kW | 1.76
90 | 72 | 1094 | 75 | MBh | 36.1
90 | 72 | 1094 | 75 | S/T | 0.693
90 | 72 | 1094 | 75 | ∆T | 21.2
90 | 72 | 1094 | 75 | LDB | 68.8
90 | 72 | 1094 | 75 | LWB | 66.4
90 | 72 | 1094 | 75 | kW | 1.73
68 | 75 | 1094 | 57 | MBh | 19.5
68 | 75 | 1094 | 57 | S/T | 0.882
68 | 75 | 1094 | 57 | ∆T | 14.6
68 | 75 | 1094 | 57 | LDB | 53.4
68 | 75 | 1094 | 57 | LWB | 50.3
68 | 75 | 1094 | 57 | kW | 0.91
72 | 75 | 1094 | 61 | MBh | 23.7
72 | 75 | 1094 | 61 | S/T | 0.844
72 | 75 | 1094 | 61 | ∆T | 16.9
72 | 75 | 1094 | 61 | LDB | 55.1
72 | 75 | 1094 | 61 | LWB | 53.4
72 | 75 | 1094 | 61 | kW | 1.13
77 | 75 | 1094 | 64 | MBh | 26.8
77 | 75 | 1094 | 64 | S/T | 0.817
77 | 75 | 1094 | 64 | ∆T | 18.5
77 | 75 | 1094 | 64 | LDB | 58.5
77 | 75 | 1094 | 64 | LWB | 55.9
77 | 75 | 1094 | 64 | kW | 1.31
80 | 75 | 1094 | 67 | MBh | 30
80 | 75 | 1094 | 67 | S/T | 0.78
80 | 75 | 1094 | 67 | ∆T | 19.8
80 | 75 | 1094 | 67 | LDB | 60.2
80 | 75 | 1094 | 67 | LWB | 58.4
80 | 75 | 1094 | 67 | kW | 1.48
84 | 75 | 1094 | 70 | MBh | 33.2
84 | 75 | 1094 | 70 | S/T | 0.744
84 | 75 | 1094 | 70 | ∆T | 20.9
84 | 75 | 1094 | 70 | LDB | 63.1
84 | 75 | 1094 | 70 | LWB | 61.1
84 | 75 | 1094 | 70 | kW | 1.68
86 | 75 | 1094 | 72 | MBh | 35.1
86 | 75 | 1094 | 72 | S/T | 0.712
86 | 75 | 1094 | 72 | ∆T | 21.2
86 | 75 | 1094 | 72 | LDB | 64.8
86 | 75 | 1094 | 72 | LWB | 63
86 | 75 | 1094 | 72 | kW | 1.82
90 | 75 | 1094 | 75 | MBh | 35.7
90 | 75 | 1094 | 75 | S/T | 0.692
90 | 75 | 1094 | 75 | ∆T | 20.9
90 | 75 | 1094 | 75 | LDB | 69.1
90 | 75 | 1094 | 75 | LWB | 66.5
90 | 75 | 1094 | 75 | kW | 1.83
68 | 79 | 1094 | 57 | MBh | 19.5
68 | 79 | 1094 | 57 | S/T | 0.882
68 | 79 | 1094 | 57 | ∆T | 14.6
68 | 79 | 1094 | 57 | LDB | 53.4
68 | 79 | 1094 | 57 | LWB | 50.3
68 | 79 | 1094 | 57 | kW | 0.93
72 | 79 | 1094 | 61 | MBh | 23.7
72 | 79 | 1094 | 61 | S/T | 0.844
72 | 79 | 1094 | 61 | ∆T | 16.9
72 | 79 | 1094 | 61 | LDB | 55.1
72 | 79 | 1094 | 61 | LWB | 53.4
72 | 79 | 1094 | 61 | kW | 1.16
77 | 79 | 1094 | 64 | MBh | 26.8
77 | 79 | 1094 | 64 | S/T | 0.817
77 | 79 | 1094 | 64 | ∆T | 18.5
77 | 79 | 1094 | 64 | LDB | 58.5
77 | 79 | 1094 | 64 | LWB | 55.9
77 | 79 | 1094 | 64 | kW | 1.36
80 | 79 | 1094 | 67 | MBh | 30
80 | 79 | 1094 | 67 | S/T | 0.78
80 | 79 | 1094 | 67 | ∆T | 19.8
80 | 79 | 1094 | 67 | LDB | 60.2
80 | 79 | 1094 | 67 | LWB | 58.4
80 | 79 | 1094 | 67 | kW | 1.6
84 | 79 | 1094 | 70 | MBh | 33.2
84 | 79 | 1094 | 70 | S/T | 0.744
84 | 79 | 1094 | 70 | ∆T | 20.9
84 | 79 | 1094 | 70 | LDB | 63.1
84 | 79 | 1094 | 70 | LWB | 61.1
84 | 79 | 1094 | 70 | kW | 1.86
86 | 79 | 1094 | 72 | MBh | 34.5
86 | 79 | 1094 | 72 | S/T | 0.713
86 | 79 | 1094 | 72 | ∆T | 20.8
86 | 79 | 1094 | 72 | LDB | 65.2
86 | 79 | 1094 | 72 | LWB | 63.2
86 | 79 | 1094 | 72 | kW | 1.96
90 | 79 | 1094 | 75 | MBh | 35.1
90 | 79 | 1094 | 75 | S/T | 0.692
90 | 79 | 1094 | 75 | ∆T | 20.6
90 | 79 | 1094 | 75 | LDB | 69.4
90 | 79 | 1094 | 75 | LWB | 66.6
90 | 79 | 1094 | 75 | kW | 1.97
68 | 83 | 1094 | 57 | MBh | 19.5
68 | 83 | 1094 | 57 | S/T | 0.882
68 | 83 | 1094 | 57 | ∆T | 14.6
68 | 83 | 1094 | 57 | LDB | 53.4
68 | 83 | 1094 | 57 | LWB | 50.3
68 | 83 | 1094 | 57 | kW | 0.96
72 | 83 | 1094 | 61 | MBh | 23.7
72 | 83 | 1094 | 61 | S/T | 0.844
72 | 83 | 1094 | 61 | ∆T | 16.9
72 | 83 | 1094 | 61 | LDB | 55.1
72 | 83 | 1094 | 61 | LWB | 53.4
72 | 83 | 1094 | 61 | kW | 1.25
77 | 83 | 1094 | 64 | MBh | 26.8
77 | 83 | 1094 | 64 | S/T | 0.817
77 | 83 | 1094 | 64 | ∆T | 18.5
77 | 83 | 1094 | 64 | LDB | 58.5
77 | 83 | 1094 | 64 | LWB | 55.9
77 | 83 | 1094 | 64 | kW | 1.49
80 | 83 | 1094 | 67 | MBh | 30
80 | 83 | 1094 | 67 | S/T | 0.78
80 | 83 | 1094 | 67 | ∆T | 19.8
80 | 83 | 1094 | 67 | LDB | 60.2
80 | 83 | 1094 | 67 | LWB | 58.4
80 | 83 | 1094 | 67 | kW | 1.76
84 | 83 | 1094 | 70 | MBh | 33.2
84 | 83 | 1094 | 70 | S/T | 0.744
84 | 83 | 1094 | 70 | ∆T | 20.9
84 | 83 | 1094 | 70 | LDB | 63.1
84 | 83 | 1094 | 70 | LWB | 61.1
84 | 83 | 1094 | 70 | kW | 2.05
86 | 83 | 1094 | 72 | MBh | 33.9
86 | 83 | 1094 | 72 | S/T | 0.714
86 | 83 | 1094 | 72 | ∆T | 20.5
86 | 83 | 1094 | 72 | LDB | 65.5
86 | 83 | 1094 | 72 | LWB | 63.3
86 | 83 | 1094 | 72 | kW | 2.09
90 | 83 | 1094 | 75 | MBh | 34.5
90 | 83 | 1094 | 75 | S/T | 0.696
90 | 83 | 1094 | 75 | ∆T | 20.3
90 | 83 | 1094 | 75 | LDB | 69.7
90 | 83 | 1094 | 75 | LWB | 66.8
90 | 83 | 1094 | 75 | kW | 2.11
68 | 87 | 1094 | 57 | MBh | 19.5
68 | 87 | 1094 | 57 | S/T | 0.882
68 | 87 | 1094 | 57 | ∆T | 14.6
68 | 87 | 1094 | 57 | LDB | 53.4
68 | 87 | 1094 | 57 | LWB | 50.3
68 | 87 | 1094 | 57 | kW | 1.05
72 | 87 | 1094 | 61 | MBh | 23.7
72 | 87 | 1094 | 61 | S/T | 0.844
72 | 87 | 1094 | 61 | ∆T | 16.9
72 | 87 | 1094 | 61 | LDB | 55.1
72 | 87 | 1094 | 61 | LWB | 53.4
72 | 87 | 1094 | 61 | kW | 1.37
77 | 87 | 1094 | 64 | MBh | 26.8
77 | 87 | 1094 | 64 | S/T | 0.817
77 | 87 | 1094 | 64 | ∆T | 18.5
77 | 87 | 1094 | 64 | LDB | 58.5
77 | 87 | 1094 | 64 | LWB | 55.9
77 | 87 | 1094 | 64 | kW | 1.64
80 | 87 | 1094 | 67 | MBh | 30
80 | 87 | 1094 | 67 | S/T | 0.78
80 | 87 | 1094 | 67 | ∆T | 19.8
80 | 87 | 1094 | 67 | LDB | 60.2
80 | 87 | 1094 | 67 | LWB | 58.4
80 | 87 | 1094 | 67 | kW | 1.93
84 | 87 | 1094 | 70 | MBh | 33
84 | 87 | 1094 | 70 | S/T | 0.745
84 | 87 | 1094 | 70 | ∆T | 20.8
84 | 87 | 1094 | 70 | LDB | 63.2
84 | 87 | 1094 | 70 | LWB | 61.2
84 | 87 | 1094 | 70 | kW | 2.22
86 | 87 | 1094 | 72 | MBh | 33.4
86 | 87 | 1094 | 72 | S/T | 0.713
86 | 87 | 1094 | 72 | ∆T | 20.1
86 | 87 | 1094 | 72 | LDB | 65.9
86 | 87 | 1094 | 72 | LWB | 63.5
86 | 87 | 1094 | 72 | kW | 2.23
90 | 87 | 1094 | 75 | MBh | 34
90 | 87 | 1094 | 75 | S/T | 0.694
90 | 87 | 1094 | 75 | ∆T | 20
90 | 87 | 1094 | 75 | LDB | 70
90 | 87 | 1094 | 75 | LWB | 66.9
90 | 87 | 1094 | 75 | kW | 2.25
68 | 91 | 1094 | 57 | MBh | 19.5
68 | 91 | 1094 | 57 | S/T | 0.882
68 | 91 | 1094 | 57 | ∆T | 14.6
68 | 91 | 1094 | 57 | LDB | 53.4
68 | 91 | 1094 | 57 | LWB | 50.3
68 | 91 | 1094 | 57 | kW | 1.15
72 | 91 | 1094 | 61 | MBh | 23.7
72 | 91 | 1094 | 61 | S/T | 0.844
72 | 91 | 1094 | 61 | ∆T | 16.9
72 | 91 | 1094 | 61 | LDB | 55.1
72 | 91 | 1094 | 61 | LWB | 53.4
72 | 91 | 1094 | 61 | kW | 1.5
77 | 91 | 1094 | 64 | MBh | 26.8
77 | 91 | 1094 | 64 | S/T | 0.817
77 | 91 | 1094 | 64 | ∆T | 18.5
77 | 91 | 1094 | 64 | LDB | 58.5
77 | 91 | 1094 | 64 | LWB | 55.9
77 | 91 | 1094 | 64 | kW | 1.79
80 | 91 | 1094 | 67 | MBh | 30
80 | 91 | 1094 | 67 | S/T | 0.78
80 | 91 | 1094 | 67 | ∆T | 19.8
80 | 91 | 1094 | 67 | LDB | 60.2
80 | 91 | 1094 | 67 | LWB | 58.4
80 | 91 | 1094 | 67 | kW | 2.11
84 | 91 | 1094 | 70 | MBh | 32.4
84 | 91 | 1094 | 70 | S/T | 0.747
84 | 91 | 1094 | 70 | ∆T | 20.5
84 | 91 | 1094 | 70 | LDB | 63.5
84 | 91 | 1094 | 70 | LWB | 61.3
84 | 91 | 1094 | 70 | kW | 2.36
86 | 91 | 1094 | 72 | MBh | 32.8
86 | 91 | 1094 | 72 | S/T | 0.713
86 | 91 | 1094 | 72 | ∆T | 19.8
86 | 91 | 1094 | 72 | LDB | 66.2
86 | 91 | 1094 | 72 | LWB | 63.6
86 | 91 | 1094 | 72 | kW | 2.37
90 | 91 | 1094 | 75 | MBh | 33.4
90 | 91 | 1094 | 75 | S/T | 0.695
90 | 91 | 1094 | 75 | ∆T | 19.6
90 | 91 | 1094 | 75 | LDB | 70.4
90 | 91 | 1094 | 75 | LWB | 67.1
90 | 91 | 1094 | 75 | kW | 2.38
68 | 93 | 1094 | 57 | MBh | 19.5
68 | 93 | 1094 | 57 | S/T | 0.882
68 | 93 | 1094 | 57 | ∆T | 14.6
68 | 93 | 1094 | 57 | LDB | 53.4
68 | 93 | 1094 | 57 | LWB | 50.3
68 | 93 | 1094 | 57 | kW | 1.19
72 | 93 | 1094 | 61 | MBh | 23.7
72 | 93 | 1094 | 61 | S/T | 0.844
72 | 93 | 1094 | 61 | ∆T | 16.9
72 | 93 | 1094 | 61 | LDB | 55.1
72 | 93 | 1094 | 61 | LWB | 53.4
72 | 93 | 1094 | 61 | kW | 1.56
77 | 93 | 1094 | 64 | MBh | 26.8
77 | 93 | 1094 | 64 | S/T | 0.817
77 | 93 | 1094 | 64 | ∆T | 18.5
77 | 93 | 1094 | 64 | LDB | 58.5
77 | 93 | 1094 | 64 | LWB | 55.9
77 | 93 | 1094 | 64 | kW | 1.87
80 | 93 | 1094 | 67 | MBh | 30
80 | 93 | 1094 | 67 | S/T | 0.78
80 | 93 | 1094 | 67 | ∆T | 19.8
80 | 93 | 1094 | 67 | LDB | 60.2
80 | 93 | 1094 | 67 | LWB | 58.4
80 | 93 | 1094 | 67 | kW | 2.21
84 | 93 | 1094 | 70 | MBh | 32.1
84 | 93 | 1094 | 70 | S/T | 0.748
84 | 93 | 1094 | 70 | ∆T | 20.3
84 | 93 | 1094 | 70 | LDB | 63.7
84 | 93 | 1094 | 70 | LWB | 61.4
84 | 93 | 1094 | 70 | kW | 2.42
86 | 93 | 1094 | 72 | MBh | 32.5
86 | 93 | 1094 | 72 | S/T | 0.714
86 | 93 | 1094 | 72 | ∆T | 19.6
86 | 93 | 1094 | 72 | LDB | 66.4
86 | 93 | 1094 | 72 | LWB | 63.7
86 | 93 | 1094 | 72 | kW | 2.44
90 | 93 | 1094 | 75 | MBh | 33.1
90 | 93 | 1094 | 75 | S/T | 0.695
90 | 93 | 1094 | 75 | ∆T | 19.5
90 | 93 | 1094 | 75 | LDB | 70.5
90 | 93 | 1094 | 75 | LWB | 67.1
90 | 93 | 1094 | 75 | kW | 2.45
68 | 95 | 1094 | 57 | MBh | 19.5
68 | 95 | 1094 | 57 | S/T | 0.882
68 | 95 | 1094 | 57 | ∆T | 14.6
68 | 95 | 1094 | 57 | LDB | 53.4
68 | 95 | 1094 | 57 | LWB | 50.3
68 | 95 | 1094 | 57 | kW | 1.25
72 | 95 | 1094 | 61 | MBh | 23.7
72 | 95 | 1094 | 61 | S/T | 0.844
72 | 95 | 1094 | 61 | ∆T | 16.9
72 | 95 | 1094 | 61 | LDB | 55.1
72 | 95 | 1094 | 61 | LWB | 53.4
72 | 95 | 1094 | 61 | kW | 1.63
77 | 95 | 1094 | 64 | MBh | 26.8
77 | 95 | 1094 | 64 | S/T | 0.817
77 | 95 | 1094 | 64 | ∆T | 18.5
77 | 95 | 1094 | 64 | LDB | 58.5
77 | 95 | 1094 | 64 | LWB | 55.9
77 | 95 | 1094 | 64 | kW | 1.95
80 | 95 | 1094 | 67 | MBh | 30
80 | 95 | 1094 | 67 | S/T | 0.78
80 | 95 | 1094 | 67 | ∆T | 19.8
80 | 95 | 1094 | 67 | LDB | 60.2
80 | 95 | 1094 | 67 | LWB | 58.4
80 | 95 | 1094 | 67 | kW | 2.31
84 | 95 | 1094 | 70 | MBh | 31.8
84 | 95 | 1094 | 70 | S/T | 0.745
84 | 95 | 1094 | 70 | ∆T | 20.1
84 | 95 | 1094 | 70 | LDB | 63.9
84 | 95 | 1094 | 70 | LWB | 61.5
84 | 95 | 1094 | 70 | kW | 2.49
86 | 95 | 1094 | 72 | MBh | 32.2
86 | 95 | 1094 | 72 | S/T | 0.714
86 | 95 | 1094 | 72 | ∆T | 19.5
86 | 95 | 1094 | 72 | LDB | 66.5
86 | 95 | 1094 | 72 | LWB | 63.8
86 | 95 | 1094 | 72 | kW | 2.5
90 | 95 | 1094 | 75 | MBh | 32.9
90 | 95 | 1094 | 75 | S/T | 0.693
90 | 95 | 1094 | 75 | ∆T | 19.3
90 | 95 | 1094 | 75 | LDB | 70.7
90 | 95 | 1094 | 75 | LWB | 67.2
90 | 95 | 1094 | 75 | kW | 2.52
68 | 99 | 1094 | 57 | MBh | 19.5
68 | 99 | 1094 | 57 | S/T | 0.882
68 | 99 | 1094 | 57 | ∆T | 14.6
68 | 99 | 1094 | 57 | LDB | 53.4
68 | 99 | 1094 | 57 | LWB | 50.3
68 | 99 | 1094 | 57 | kW | 1.35
72 | 99 | 1094 | 61 | MBh | 23.7
72 | 99 | 1094 | 61 | S/T | 0.844
72 | 99 | 1094 | 61 | ∆T | 16.9
72 | 99 | 1094 | 61 | LDB | 55.1
72 | 99 | 1094 | 61 | LWB | 53.4
72 | 99 | 1094 | 61 | kW | 1.77
77 | 99 | 1094 | 64 | MBh | 26.8
77 | 99 | 1094 | 64 | S/T | 0.817
77 | 99 | 1094 | 64 | ∆T | 18.5
77 | 99 | 1094 | 64 | LDB | 58.5
77 | 99 | 1094 | 64 | LWB | 55.9
77 | 99 | 1094 | 64 | kW | 2.13
80 | 99 | 1094 | 67 | MBh | 30
80 | 99 | 1094 | 67 | S/T | 0.78
80 | 99 | 1094 | 67 | ∆T | 19.8
80 | 99 | 1094 | 67 | LDB | 60.2
80 | 99 | 1094 | 67 | LWB | 58.4
80 | 99 | 1094 | 67 | kW | 2.51
84 | 99 | 1094 | 70 | MBh | 31.3
84 | 99 | 1094 | 70 | S/T | 0.744
84 | 99 | 1094 | 70 | ∆T | 19.7
84 | 99 | 1094 | 70 | LDB | 64.3
84 | 99 | 1094 | 70 | LWB | 61.7
84 | 99 | 1094 | 70 | kW | 2.63
86 | 99 | 1094 | 72 | MBh | 31.7
86 | 99 | 1094 | 72 | S/T | 0.713
86 | 99 | 1094 | 72 | ∆T | 19.1
86 | 99 | 1094 | 72 | LDB | 66.9
86 | 99 | 1094 | 72 | LWB | 63.9
86 | 99 | 1094 | 72 | kW | 2.64
90 | 99 | 1094 | 75 | MBh | 32.3
90 | 99 | 1094 | 75 | S/T | 0.693
90 | 99 | 1094 | 75 | ∆T | 19
90 | 99 | 1094 | 75 | LDB | 71
90 | 99 | 1094 | 75 | LWB | 67.4
90 | 99 | 1094 | 75 | kW | 2.66
68 | 103 | 1094 | 57 | MBh | 19.5
68 | 103 | 1094 | 57 | S/T | 0.882
68 | 103 | 1094 | 57 | ∆T | 14.6
68 | 103 | 1094 | 57 | LDB | 53.4
68 | 103 | 1094 | 57 | LWB | 50.3
68 | 103 | 1094 | 57 | kW | 1.46
72 | 103 | 1094 | 61 | MBh | 23.7
72 | 103 | 1094 | 61 | S/T | 0.844
72 | 103 | 1094 | 61 | ∆T | 16.9
72 | 103 | 1094 | 61 | LDB | 55.1
72 | 103 | 1094 | 61 | LWB | 53.4
72 | 103 | 1094 | 61 | kW | 1.92
77 | 103 | 1094 | 64 | MBh | 26.8
77 | 103 | 1094 | 64 | S/T | 0.817
77 | 103 | 1094 | 64 | ∆T | 18.5
77 | 103 | 1094 | 64 | LDB | 58.5
77 | 103 | 1094 | 64 | LWB | 55.9
77 | 103 | 1094 | 64 | kW | 2.31
80 | 103 | 1094 | 67 | MBh | 30
80 | 103 | 1094 | 67 | S/T | 0.78
80 | 103 | 1094 | 67 | ∆T | 19.8
80 | 103 | 1094 | 67 | LDB | 60.2
80 | 103 | 1094 | 67 | LWB | 58.4
80 | 103 | 1094 | 67 | kW | 2.73
84 | 103 | 1094 | 70 | MBh | 30.7
84 | 103 | 1094 | 70 | S/T | 0.746
84 | 103 | 1094 | 70 | ∆T | 19.4
84 | 103 | 1094 | 70 | LDB | 64.6
84 | 103 | 1094 | 70 | LWB | 61.8
84 | 103 | 1094 | 70 | kW | 2.77
86 | 103 | 1094 | 72 | MBh | 31.1
86 | 103 | 1094 | 72 | S/T | 0.714
86 | 103 | 1094 | 72 | ∆T | 18.8
86 | 103 | 1094 | 72 | LDB | 67.2
86 | 103 | 1094 | 72 | LWB | 64.1
86 | 103 | 1094 | 72 | kW | 2.78
90 | 103 | 1094 | 75 | MBh | 31.7
90 | 103 | 1094 | 75 | S/T | 0.694
90 | 103 | 1094 | 75 | ∆T | 18.6
90 | 103 | 1094 | 75 | LDB | 71.4
90 | 103 | 1094 | 75 | LWB | 67.5
90 | 103 | 1094 | 75 | kW | 2.8
68 | 106 | 1094 | 57 | MBh | 19.5
68 | 106 | 1094 | 57 | S/T | 0.882
68 | 106 | 1094 | 57 | ∆T | 14.6
68 | 106 | 1094 | 57 | LDB | 53.4
68 | 106 | 1094 | 57 | LWB | 50.3
68 | 106 | 1094 | 57 | kW | 1.55
72 | 106 | 1094 | 61 | MBh | 23.7
72 | 106 | 1094 | 61 | S/T | 0.844
72 | 106 | 1094 | 61 | ∆T | 16.9
72 | 106 | 1094 | 61 | LDB | 55.1
72 | 106 | 1094 | 61 | LWB | 53.4
72 | 106 | 1094 | 61 | kW | 2.04
77 | 106 | 1094 | 64 | MBh | 26.8
77 | 106 | 1094 | 64 | S/T | 0.817
77 | 106 | 1094 | 64 | ∆T | 18.5
77 | 106 | 1094 | 64 | LDB | 58.5
77 | 106 | 1094 | 64 | LWB | 55.9
77 | 106 | 1094 | 64 | kW | 2.46
80 | 106 | 1094 | 67 | MBh | 29.7
80 | 106 | 1094 | 67 | S/T | 0.778
80 | 106 | 1094 | 67 | ∆T | 19.6
80 | 106 | 1094 | 67 | LDB | 60.4
80 | 106 | 1094 | 67 | LWB | 58.5
80 | 106 | 1094 | 67 | kW | 2.85
84 | 106 | 1094 | 70 | MBh | 30.3
84 | 106 | 1094 | 70 | S/T | 0.746
84 | 106 | 1094 | 70 | ∆T | 19.1
84 | 106 | 1094 | 70 | LDB | 64.9
84 | 106 | 1094 | 70 | LWB | 61.9
84 | 106 | 1094 | 70 | kW | 2.87
86 | 106 | 1094 | 72 | MBh | 30.7
86 | 106 | 1094 | 72 | S/T | 0.713
86 | 106 | 1094 | 72 | ∆T | 18.5
86 | 106 | 1094 | 72 | LDB | 67.5
86 | 106 | 1094 | 72 | LWB | 64.2
86 | 106 | 1094 | 72 | kW | 2.89
90 | 106 | 1094 | 75 | MBh | 31.2
90 | 106 | 1094 | 75 | S/T | 0.696
90 | 106 | 1094 | 75 | ∆T | 18.4
90 | 106 | 1094 | 75 | LDB | 71.6
90 | 106 | 1094 | 75 | LWB | 67.6
90 | 106 | 1094 | 75 | kW | 2.9
68 | 110 | 1094 | 57 | MBh | 19.5
68 | 110 | 1094 | 57 | S/T | 0.882
68 | 110 | 1094 | 57 | ∆T | 14.6
68 | 110 | 1094 | 57 | LDB | 53.4
68 | 110 | 1094 | 57 | LWB | 50.3
68 | 110 | 1094 | 57 | kW | 1.7
72 | 110 | 1094 | 61 | MBh | 23.7
72 | 110 | 1094 | 61 | S/T | 0.844
72 | 110 | 1094 | 61 | ∆T | 16.9
72 | 110 | 1094 | 61 | LDB | 55.1
72 | 110 | 1094 | 61 | LWB | 53.4
72 | 110 | 1094 | 61 | kW | 2.25
77 | 110 | 1094 | 64 | MBh | 26.8
77 | 110 | 1094 | 64 | S/T | 0.817
77 | 110 | 1094 | 64 | ∆T | 18.5
77 | 110 | 1094 | 64 | LDB | 58.5
77 | 110 | 1094 | 64 | LWB | 55.9
77 | 110 | 1094 | 64 | kW | 2.7
80 | 110 | 1094 | 67 | MBh | 29.1
80 | 110 | 1094 | 67 | S/T | 0.78
80 | 110 | 1094 | 67 | ∆T | 19.2
80 | 110 | 1094 | 67 | LDB | 60.8
80 | 110 | 1094 | 67 | LWB | 58.7
80 | 110 | 1094 | 67 | kW | 3.03
84 | 110 | 1094 | 70 | MBh | 29.7
84 | 110 | 1094 | 70 | S/T | 0.747
84 | 110 | 1094 | 70 | ∆T | 18.8
84 | 110 | 1094 | 70 | LDB | 65.2
84 | 110 | 1094 | 70 | LWB | 62.1
84 | 110 | 1094 | 70 | kW | 3.05
86 | 110 | 1094 | 72 | MBh | 29.8
86 | 110 | 1094 | 72 | S/T | 0.715
86 | 110 | 1094 | 72 | ∆T | 18
86 | 110 | 1094 | 72 | LDB | 68
86 | 110 | 1094 | 72 | LWB | 64.5
86 | 110 | 1094 | 72 | kW | 3.06
90 | 110 | 1094 | 75 | MBh | 29.8
90 | 110 | 1094 | 75 | S/T | 0.695
90 | 110 | 1094 | 75 | ∆T | 17.5
90 | 110 | 1094 | 75 | LDB | 72.5
90 | 110 | 1094 | 75 | LWB | 68
90 | 110 | 1094 | 75 | kW | 3.06
68 | 115 | 1094 | 57 | MBh | 19.5
68 | 115 | 1094 | 57 | S/T | 0.882
68 | 115 | 1094 | 57 | ∆T | 14.6
68 | 115 | 1094 | 57 | LDB | 53.4
68 | 115 | 1094 | 57 | LWB | 50.3
68 | 115 | 1094 | 57 | kW | 1.92
72 | 115 | 1094 | 61 | MBh | 23.7
72 | 115 | 1094 | 61 | S/T | 0.844
72 | 115 | 1094 | 61 | ∆T | 16.9
72 | 115 | 1094 | 61 | LDB | 55.1
72 | 115 | 1094 | 61 | LWB | 53.4
72 | 115 | 1094 | 61 | kW | 2.54
77 | 115 | 1094 | 64 | MBh | 26.8
77 | 115 | 1094 | 64 | S/T | 0.817
77 | 115 | 1094 | 64 | ∆T | 18.5
77 | 115 | 1094 | 64 | LDB | 58.5
77 | 115 | 1094 | 64 | LWB | 55.9
77 | 115 | 1094 | 64 | kW | 3.07
80 | 115 | 1094 | 67 | MBh | 28.1
80 | 115 | 1094 | 67 | S/T | 0.779
80 | 115 | 1094 | 67 | ∆T | 18.5
80 | 115 | 1094 | 67 | LDB | 61.5
80 | 115 | 1094 | 67 | LWB | 59
80 | 115 | 1094 | 67 | kW | 3.28
84 | 115 | 1094 | 70 | MBh | 28.1
84 | 115 | 1094 | 70 | S/T | 0.747
84 | 115 | 1094 | 70 | ∆T | 17.8
84 | 115 | 1094 | 70 | LDB | 66.2
84 | 115 | 1094 | 70 | LWB | 62.6
84 | 115 | 1094 | 70 | kW | 3.28
86 | 115 | 1094 | 72 | MBh | 28.1
86 | 115 | 1094 | 72 | S/T | 0.712
86 | 115 | 1094 | 72 | ∆T | 16.9
86 | 115 | 1094 | 72 | LDB | 69.1
86 | 115 | 1094 | 72 | LWB | 64.9
86 | 115 | 1094 | 72 | kW | 3.28
90 | 115 | 1094 | 75 | MBh | 28.1
90 | 115 | 1094 | 75 | S/T | 0.694
90 | 115 | 1094 | 75 | ∆T | 16.5
90 | 115 | 1094 | 75 | LDB | 73.5
90 | 115 | 1094 | 75 | LWB | 68.4
90 | 115 | 1094 | 75 | kW | 3.28
68 | 118 | 1094 | 57 | MBh | 19.5
68 | 118 | 1094 | 57 | S/T | 0.882
68 | 118 | 1094 | 57 | ∆T | 14.6
68 | 118 | 1094 | 57 | LDB | 53.4
68 | 118 | 1094 | 57 | LWB | 50.3
68 | 118 | 1094 | 57 | kW | 2.07
72 | 118 | 1094 | 61 | MBh | 23.7
72 | 118 | 1094 | 61 | S/T | 0.844
72 | 118 | 1094 | 61 | ∆T | 16.9
72 | 118 | 1094 | 61 | LDB | 55.1
72 | 118 | 1094 | 61 | LWB | 53.4
72 | 118 | 1094 | 61 | kW | 2.73
77 | 118 | 1094 | 64 | MBh | 25.4
77 | 118 | 1094 | 64 | S/T | 0.815
77 | 118 | 1094 | 64 | ∆T | 17.5
77 | 118 | 1094 | 64 | LDB | 59.5
77 | 118 | 1094 | 64 | LWB | 56.3
77 | 118 | 1094 | 64 | kW | 3.04
80 | 118 | 1094 | 67 | MBh | 25.4
80 | 118 | 1094 | 67 | S/T | 0.78
80 | 118 | 1094 | 67 | ∆T | 16.8
80 | 118 | 1094 | 67 | LDB | 63.2
80 | 118 | 1094 | 67 | LWB | 59.9
80 | 118 | 1094 | 67 | kW | 3.04
84 | 118 | 1094 | 70 | MBh | 25.4
84 | 118 | 1094 | 70 | S/T | 0.748
84 | 118 | 1094 | 70 | ∆T | 16.1
84 | 118 | 1094 | 70 | LDB | 67.9
84 | 118 | 1094 | 70 | LWB | 63.3
84 | 118 | 1094 | 70 | kW | 3.04
86 | 118 | 1094 | 72 | MBh | 25.4
86 | 118 | 1094 | 72 | S/T | 0.713
86 | 118 | 1094 | 72 | ∆T | 15.3
86 | 118 | 1094 | 72 | LDB | 70.7
86 | 118 | 1094 | 72 | LWB | 65.7
86 | 118 | 1094 | 72 | kW | 3.04
90 | 118 | 1094 | 75 | MBh | 25.4
90 | 118 | 1094 | 75 | S/T | 0.693
90 | 118 | 1094 | 75 | ∆T | 14.9
90 | 118 | 1094 | 75 | LDB | 75.1
90 | 118 | 1094 | 75 | LWB | 69.1
90 | 118 | 1094 | 75 | kW | 3.04
68 | 122 | 1094 | 57 | MBh | 19.5
68 | 122 | 1094 | 57 | S/T | 0.882
68 | 122 | 1094 | 57 | ∆T | 14.6
68 | 122 | 1094 | 57 | LDB | 53.4
68 | 122 | 1094 | 57 | LWB | 50.3
68 | 122 | 1094 | 57 | kW | 2.27
72 | 122 | 1094 | 61 | MBh | 21.2
72 | 122 | 1094 | 61 | S/T | 0.844
72 | 122 | 1094 | 61 | ∆T | 15.1
72 | 122 | 1094 | 61 | LDB | 56.9
72 | 122 | 1094 | 61 | LWB | 54.3
72 | 122 | 1094 | 61 | kW | 2.56
77 | 122 | 1094 | 64 | MBh | 21.2
77 | 122 | 1094 | 64 | S/T | 0.816
77 | 122 | 1094 | 64 | ∆T | 14.6
77 | 122 | 1094 | 64 | LDB | 62.4
77 | 122 | 1094 | 64 | LWB | 57.7
77 | 122 | 1094 | 64 | kW | 2.56
80 | 122 | 1094 | 67 | MBh | 21.2
80 | 122 | 1094 | 67 | S/T | 0.783
80 | 122 | 1094 | 67 | ∆T | 14
80 | 122 | 1094 | 67 | LDB | 66
80 | 122 | 1094 | 67 | LWB | 61.1
80 | 122 | 1094 | 67 | kW | 2.56
84 | 122 | 1094 | 70 | MBh | 21.2
84 | 122 | 1094 | 70 | S/T | 0.745
84 | 122 | 1094 | 70 | ∆T | 13.4
84 | 122 | 1094 | 70 | LDB | 70.6
84 | 122 | 1094 | 70 | LWB | 64.5
84 | 122 | 1094 | 70 | kW | 2.56
86 | 122 | 1094 | 72 | MBh | 21.2
86 | 122 | 1094 | 72 | S/T | 0.712
86 | 122 | 1094 | 72 | ∆T | 12.8
86 | 122 | 1094 | 72 | LDB | 73.2
86 | 122 | 1094 | 72 | LWB | 66.8
86 | 122 | 1094 | 72 | kW | 2.56
90 | 122 | 1094 | 75 | MBh | 21.2
90 | 122 | 1094 | 75 | S/T | 0.693
90 | 122 | 1094 | 75 | ∆T | 12.4
90 | 122 | 1094 | 75 | LDB | 77.6
90 | 122 | 1094 | 75 | LWB | 70.1
90 | 122 | 1094 | 75 | kW | 2.56

## RZA36AAVJU - FBA36AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1130 | 57 | MBh | 23.4 | 64 | 60 | 61 | 48 | 3.66
68 | 23 | 1130 | 57 | S/T | 0.846 | 64 | 60 | 65 | 44.5 | 3.35
68 | 23 | 1130 | 57 | ∆T | 16.2 | 64 | 60 | 68 | 41.8 | 3.11
68 | 23 | 1130 | 57 | LDB | 51.8 | 64 | 60 | 70 | 40 | 2.96
68 | 23 | 1130 | 57 | LWB | 49.1 | 64 | 60 | 72 | 38.2 | 2.8
68 | 23 | 1130 | 57 | kW | 0.9 | 64 | 60 | 75 | 35.5 | 2.58
72 | 23 | 1130 | 61 | MBh | 28.4 | 60 | 56 | 61 | 48 | 3.81
72 | 23 | 1130 | 61 | S/T | 0.813 | 60 | 56 | 65 | 44.5 | 3.48
72 | 23 | 1130 | 61 | ∆T | 18.9 | 60 | 56 | 68 | 41.8 | 3.23
72 | 23 | 1130 | 61 | LDB | 53.1 | 60 | 56 | 70 | 40 | 3.07
72 | 23 | 1130 | 61 | LWB | 52.1 | 60 | 56 | 72 | 38.2 | 2.91
72 | 23 | 1130 | 61 | kW | 1.1 | 60 | 56 | 75 | 35.5 | 2.68
77 | 23 | 1130 | 64 | MBh | 32.2 | 57 | 53 | 61 | 48 | 3.92
77 | 23 | 1130 | 64 | S/T | 0.789 | 57 | 53 | 65 | 44.5 | 3.58
77 | 23 | 1130 | 64 | ∆T | 20.8 | 57 | 53 | 68 | 41.8 | 3.33
77 | 23 | 1130 | 64 | LDB | 56.2 | 57 | 53 | 70 | 40 | 3.17
77 | 23 | 1130 | 64 | LWB | 54.4 | 57 | 53 | 72 | 38.2 | 3
77 | 23 | 1130 | 64 | kW | 1.26 | 57 | 53 | 75 | 35.5 | 2.76
80 | 23 | 1130 | 67 | MBh | 36 | 54 | 50 | 61 | 48 | 4.04
80 | 23 | 1130 | 67 | S/T | 0.756 | 54 | 50 | 65 | 44.5 | 3.69
80 | 23 | 1130 | 67 | ∆T | 22.3 | 54 | 50 | 68 | 41.8 | 3.44
80 | 23 | 1130 | 67 | LDB | 57.7 | 54 | 50 | 70 | 40 | 3.26
80 | 23 | 1130 | 67 | LWB | 56.9 | 54 | 50 | 72 | 38.2 | 3.1
80 | 23 | 1130 | 67 | kW | 1.43 | 54 | 50 | 75 | 35.5 | 2.84
84 | 23 | 1130 | 70 | MBh | 39.8 | 51 | 47 | 61 | 48 | 4.17
84 | 23 | 1130 | 70 | S/T | 0.726 | 51 | 47 | 65 | 44.5 | 3.81
84 | 23 | 1130 | 70 | ∆T | 23.7 | 51 | 47 | 68 | 41.8 | 3.54
84 | 23 | 1130 | 70 | LDB | 60.3 | 51 | 47 | 70 | 40 | 3.37
84 | 23 | 1130 | 70 | LWB | 59.5 | 51 | 47 | 72 | 38.2 | 3.19
84 | 23 | 1130 | 70 | kW | 1.61 | 51 | 47 | 75 | 35.5 | 2.93
86 | 23 | 1130 | 72 | MBh | 42.3 | 47 | 43 | 61 | 48 | 4.36
86 | 23 | 1130 | 72 | S/T | 0.7 | 47 | 43 | 65 | 44.5 | 3.98
86 | 23 | 1130 | 72 | ∆T | 24.3 | 47 | 43 | 68 | 41.8 | 3.7
86 | 23 | 1130 | 72 | LDB | 61.7 | 47 | 43 | 70 | 40 | 3.52
86 | 23 | 1130 | 72 | LWB | 61.3 | 47 | 43 | 72 | 38.2 | 3.33
86 | 23 | 1130 | 72 | kW | 1.73 | 47 | 43 | 75 | 35.5 | 3.06
90 | 23 | 1130 | 75 | MBh | 46.1 | 44 | 40 | 61 | 48 | 4.51
90 | 23 | 1130 | 75 | S/T | 0.657 | 44 | 40 | 65 | 44.5 | 4.12
90 | 23 | 1130 | 75 | ∆T | 24.8 | 44 | 40 | 68 | 41.8 | 3.83
90 | 23 | 1130 | 75 | LDB | 65.2 | 44 | 40 | 70 | 40 | 3.64
90 | 23 | 1130 | 75 | LWB | 64.1 | 44 | 40 | 72 | 38.2 | 3.45
90 | 23 | 1130 | 75 | kW | 1.91 | 44 | 40 | 75 | 35.5 | 3.17
68 | 30 | 1130 | 57 | MBh | 23.4 | 39 | 36 | 61 | 48 | 4.72
68 | 30 | 1130 | 57 | S/T | 0.846 | 39 | 36 | 65 | 44.5 | 4.31
68 | 30 | 1130 | 57 | ∆T | 16.2 | 39 | 36 | 68 | 41.8 | 4.01
68 | 30 | 1130 | 57 | LDB | 51.8 | 39 | 36 | 70 | 40 | 3.81
68 | 30 | 1130 | 57 | LWB | 49.1 | 39 | 36 | 72 | 38.2 | 3.61
68 | 30 | 1130 | 57 | kW | 0.92 | 39 | 36 | 75 | 35.5 | 3.32
72 | 30 | 1130 | 61 | MBh | 28.4 | 35 | 32 | 61 | 48 | 4.96
72 | 30 | 1130 | 61 | S/T | 0.813 | 35 | 32 | 65 | 44.5 | 4.53
72 | 30 | 1130 | 61 | ∆T | 18.9 | 35 | 32 | 68 | 41.8 | 4.21
72 | 30 | 1130 | 61 | LDB | 53.1 | 35 | 32 | 70 | 40 | 4
72 | 30 | 1130 | 61 | LWB | 52.1 | 35 | 32 | 72 | 38.2 | 3.79
72 | 30 | 1130 | 61 | kW | 1.14 | 35 | 32 | 75 | 35.5 | 3.48
77 | 30 | 1130 | 64 | MBh | 32.2 | 30 | 28 | 61 | 48 | 5.22
77 | 30 | 1130 | 64 | S/T | 0.789 | 30 | 28 | 65 | 44.5 | 4.76
77 | 30 | 1130 | 64 | ∆T | 20.8 | 30 | 28 | 68 | 41.8 | 4.43
77 | 30 | 1130 | 64 | LDB | 56.2 | 30 | 28 | 70 | 40 | 4.21
77 | 30 | 1130 | 64 | LWB | 54.4 | 30 | 28 | 72 | 38.2 | 3.99
77 | 30 | 1130 | 64 | kW | 1.3 | 30 | 28 | 75 | 35.5 | 3.66
80 | 30 | 1130 | 67 | MBh | 36 | 26 | 24 | 61 | 48 | 5.5
80 | 30 | 1130 | 67 | S/T | 0.756 | 26 | 24 | 65 | 44.5 | 5.02
80 | 30 | 1130 | 67 | ∆T | 22.3 | 26 | 24 | 68 | 41.8 | 4.67
80 | 30 | 1130 | 67 | LDB | 57.7 | 26 | 24 | 70 | 40 | 4.44
80 | 30 | 1130 | 67 | LWB | 56.9 | 26 | 24 | 72 | 38.2 | 4.21
80 | 30 | 1130 | 67 | kW | 1.48 | 26 | 24 | 75 | 35.5 | 3.86
84 | 30 | 1130 | 70 | MBh | 39.8 | 22 | 20 | 61 | 48 | 5.82
84 | 30 | 1130 | 70 | S/T | 0.726 | 22 | 20 | 65 | 44.5 | 5.31
84 | 30 | 1130 | 70 | ∆T | 23.7 | 22 | 20 | 68 | 41.8 | 4.94
84 | 30 | 1130 | 70 | LDB | 60.3 | 22 | 20 | 70 | 40 | 4.69
84 | 30 | 1130 | 70 | LWB | 59.5 | 22 | 20 | 72 | 38.2 | 4.45
84 | 30 | 1130 | 70 | kW | 1.66 | 22 | 20 | 75 | 35.5 | 4.08
86 | 30 | 1130 | 72 | MBh | 42.3 | 19 | 18 | 61 | 47.1 | 5.71
86 | 30 | 1130 | 72 | S/T | 0.7 | 19 | 18 | 65 | 44.5 | 5.47
86 | 30 | 1130 | 72 | ∆T | 24.3 | 19 | 18 | 68 | 41.8 | 5.08
86 | 30 | 1130 | 72 | LDB | 61.7 | 19 | 18 | 70 | 40 | 4.83
86 | 30 | 1130 | 72 | LWB | 61.3 | 19 | 18 | 72 | 38.2 | 4.58
86 | 30 | 1130 | 72 | kW | 1.78 | 19 | 18 | 75 | 35.5 | 4.2
90 | 30 | 1130 | 75 | MBh | 46.1 | 17 | 16 | 61 | 45.7 | 5.51
90 | 30 | 1130 | 75 | S/T | 0.657 | 17 | 16 | 65 | 44.5 | 5.68
90 | 30 | 1130 | 75 | ∆T | 24.8 | 17 | 16 | 68 | 41.8 | 5.28
90 | 30 | 1130 | 75 | LDB | 65.2 | 17 | 16 | 70 | 40 | 5.01
90 | 30 | 1130 | 75 | LWB | 64.1 | 17 | 16 | 72 | 38.2 | 4.75
90 | 30 | 1130 | 75 | kW | 1.97 | 17 | 16 | 75 | 35.5 | 4.36
68 | 40 | 1130 | 57 | MBh | 23.4 | 15 | 14 | 61 | 44.8 | 5.38
68 | 40 | 1130 | 57 | S/T | 0.846 | 15 | 14 | 65 | 44.5 | 5.81
68 | 40 | 1130 | 57 | ∆T | 16.2 | 15 | 14 | 68 | 41.8 | 5.4
68 | 40 | 1130 | 57 | LDB | 51.8 | 15 | 14 | 70 | 40 | 5.13
68 | 40 | 1130 | 57 | LWB | 49.1 | 15 | 14 | 72 | 38.2 | 4.86
68 | 40 | 1130 | 57 | kW | 0.96 | 15 | 14 | 75 | 35.5 | 4.46
72 | 40 | 1130 | 61 | MBh | 28.4 | 13 | 12 | 61 | 43.4 | 5.2
72 | 40 | 1130 | 61 | S/T | 0.813 | 13 | 12 | 65 | 43.4 | 5.7
72 | 40 | 1130 | 61 | ∆T | 18.9 | 13 | 12 | 68 | 41.8 | 5.58
72 | 40 | 1130 | 61 | LDB | 53.1 | 13 | 12 | 70 | 40 | 5.29
72 | 40 | 1130 | 61 | LWB | 52.1 | 13 | 12 | 72 | 38.2 | 5.02
72 | 40 | 1130 | 61 | kW | 1.19 | 13 | 12 | 75 | 35.5 | 4.61
77 | 40 | 1130 | 64 | MBh | 32.2 | 10 | 9 | 61 | 40.5 | 4.86
77 | 40 | 1130 | 64 | S/T | 0.789 | 10 | 9 | 65 | 40.5 | 5.38
77 | 40 | 1130 | 64 | ∆T | 20.8 | 10 | 9 | 68 | 40.5 | 5.77
77 | 40 | 1130 | 64 | LDB | 56.2 | 10 | 9 | 70 | 40 | 5.61
77 | 40 | 1130 | 64 | LWB | 54.4 | 10 | 9 | 72 | 38.2 | 5.31
77 | 40 | 1130 | 64 | kW | 1.37 | 10 | 9 | 75 | 35.5 | 4.88
80 | 40 | 1130 | 67 | MBh | 36 | 6 | 5 | 61 | 37.6 | 4.48
80 | 40 | 1130 | 67 | S/T | 0.756 | 6 | 5 | 65 | 37.6 | 5.03
80 | 40 | 1130 | 67 | ∆T | 22.3 | 6 | 5 | 68 | 37.6 | 5.44
80 | 40 | 1130 | 67 | LDB | 57.7 | 6 | 5 | 70 | 37.6 | 5.72
80 | 40 | 1130 | 67 | LWB | 56.9 | 6 | 5 | 72 | 37.6 | 5.64
80 | 40 | 1130 | 67 | kW | 1.55 | 6 | 5 | 75 | 35.5 | 5.18
84 | 40 | 1130 | 70 | MBh | 39.8 | -2 | -2 | 61 | 31.6 | 3.57
84 | 40 | 1130 | 70 | S/T | 0.726 | -2 | -2 | 65 | 31.6 | 4.19
84 | 40 | 1130 | 70 | ∆T | 23.7 | -2 | -2 | 68 | 31.6 | 4.65
84 | 40 | 1130 | 70 | LDB | 60.3 | -2 | -2 | 70 | 31.6 | 4.95
84 | 40 | 1130 | 70 | LWB | 59.5 | -2 | -2 | 72 | 31.6 | 5.26
84 | 40 | 1130 | 70 | kW | 1.74 | -2 | -2 | 75 | 31.6 | 5.72
86 | 40 | 1130 | 72 | MBh | 42.3 | -4 | -4 | 61 | 30.1 | 3.31
86 | 40 | 1130 | 72 | S/T | 0.7 | -4 | -4 | 65 | 30.1 | 3.94
86 | 40 | 1130 | 72 | ∆T | 24.3 | -4 | -4 | 68 | 30.1 | 4.42
86 | 40 | 1130 | 72 | LDB | 61.7 | -4 | -4 | 70 | 30.1 | 4.73
86 | 40 | 1130 | 72 | LWB | 61.3 | -4 | -4 | 72 | 30.1 | 5.05
86 | 40 | 1130 | 72 | kW | 1.87 | -4 | -4 | 75 | 30.1 | 5.53
90 | 40 | 1130 | 75 | MBh | 46.1
90 | 40 | 1130 | 75 | S/T | 0.657
90 | 40 | 1130 | 75 | ∆T | 24.8
90 | 40 | 1130 | 75 | LDB | 65.2
90 | 40 | 1130 | 75 | LWB | 64.1
90 | 40 | 1130 | 75 | kW | 2.07
68 | 50 | 1130 | 57 | MBh | 23.4
68 | 50 | 1130 | 57 | S/T | 0.846
68 | 50 | 1130 | 57 | ∆T | 16.2
68 | 50 | 1130 | 57 | LDB | 51.8
68 | 50 | 1130 | 57 | LWB | 49.1
68 | 50 | 1130 | 57 | kW | 1.01
72 | 50 | 1130 | 61 | MBh | 28.4
72 | 50 | 1130 | 61 | S/T | 0.813
72 | 50 | 1130 | 61 | ∆T | 18.9
72 | 50 | 1130 | 61 | LDB | 53.1
72 | 50 | 1130 | 61 | LWB | 52.1
72 | 50 | 1130 | 61 | kW | 1.25
77 | 50 | 1130 | 64 | MBh | 32.2
77 | 50 | 1130 | 64 | S/T | 0.789
77 | 50 | 1130 | 64 | ∆T | 20.8
77 | 50 | 1130 | 64 | LDB | 56.2
77 | 50 | 1130 | 64 | LWB | 54.4
77 | 50 | 1130 | 64 | kW | 1.44
80 | 50 | 1130 | 67 | MBh | 36
80 | 50 | 1130 | 67 | S/T | 0.756
80 | 50 | 1130 | 67 | ∆T | 22.3
80 | 50 | 1130 | 67 | LDB | 57.7
80 | 50 | 1130 | 67 | LWB | 56.9
80 | 50 | 1130 | 67 | kW | 1.63
84 | 50 | 1130 | 70 | MBh | 39.8
84 | 50 | 1130 | 70 | S/T | 0.726
84 | 50 | 1130 | 70 | ∆T | 23.7
84 | 50 | 1130 | 70 | LDB | 60.3
84 | 50 | 1130 | 70 | LWB | 59.5
84 | 50 | 1130 | 70 | kW | 1.83
86 | 50 | 1130 | 72 | MBh | 42.3
86 | 50 | 1130 | 72 | S/T | 0.7
86 | 50 | 1130 | 72 | ∆T | 24.3
86 | 50 | 1130 | 72 | LDB | 61.7
86 | 50 | 1130 | 72 | LWB | 61.3
86 | 50 | 1130 | 72 | kW | 1.97
90 | 50 | 1130 | 75 | MBh | 46.1
90 | 50 | 1130 | 75 | S/T | 0.657
90 | 50 | 1130 | 75 | ∆T | 24.8
90 | 50 | 1130 | 75 | LDB | 65.2
90 | 50 | 1130 | 75 | LWB | 64.1
90 | 50 | 1130 | 75 | kW | 2.17
68 | 54 | 1130 | 57 | MBh | 23.4
68 | 54 | 1130 | 57 | S/T | 0.846
68 | 54 | 1130 | 57 | ∆T | 16.2
68 | 54 | 1130 | 57 | LDB | 51.8
68 | 54 | 1130 | 57 | LWB | 49.1
68 | 54 | 1130 | 57 | kW | 1.03
72 | 54 | 1130 | 61 | MBh | 28.4
72 | 54 | 1130 | 61 | S/T | 0.813
72 | 54 | 1130 | 61 | ∆T | 18.9
72 | 54 | 1130 | 61 | LDB | 53.1
72 | 54 | 1130 | 61 | LWB | 52.1
72 | 54 | 1130 | 61 | kW | 1.27
77 | 54 | 1130 | 64 | MBh | 32.2
77 | 54 | 1130 | 64 | S/T | 0.789
77 | 54 | 1130 | 64 | ∆T | 20.8
77 | 54 | 1130 | 64 | LDB | 56.2
77 | 54 | 1130 | 64 | LWB | 54.4
77 | 54 | 1130 | 64 | kW | 1.47
80 | 54 | 1130 | 67 | MBh | 36
80 | 54 | 1130 | 67 | S/T | 0.756
80 | 54 | 1130 | 67 | ∆T | 22.3
80 | 54 | 1130 | 67 | LDB | 57.7
80 | 54 | 1130 | 67 | LWB | 56.9
80 | 54 | 1130 | 67 | kW | 1.67
84 | 54 | 1130 | 70 | MBh | 39.8
84 | 54 | 1130 | 70 | S/T | 0.726
84 | 54 | 1130 | 70 | ∆T | 23.7
84 | 54 | 1130 | 70 | LDB | 60.3
84 | 54 | 1130 | 70 | LWB | 59.5
84 | 54 | 1130 | 70 | kW | 1.87
86 | 54 | 1130 | 72 | MBh | 42.3
86 | 54 | 1130 | 72 | S/T | 0.7
86 | 54 | 1130 | 72 | ∆T | 24.3
86 | 54 | 1130 | 72 | LDB | 61.7
86 | 54 | 1130 | 72 | LWB | 61.3
86 | 54 | 1130 | 72 | kW | 2.01
90 | 54 | 1130 | 75 | MBh | 46.1
90 | 54 | 1130 | 75 | S/T | 0.657
90 | 54 | 1130 | 75 | ∆T | 24.8
90 | 54 | 1130 | 75 | LDB | 65.2
90 | 54 | 1130 | 75 | LWB | 64.1
90 | 54 | 1130 | 75 | kW | 2.22
68 | 58 | 1130 | 57 | MBh | 23.4
68 | 58 | 1130 | 57 | S/T | 0.846
68 | 58 | 1130 | 57 | ∆T | 16.2
68 | 58 | 1130 | 57 | LDB | 51.8
68 | 58 | 1130 | 57 | LWB | 49.1
68 | 58 | 1130 | 57 | kW | 1.05
72 | 58 | 1130 | 61 | MBh | 28.4
72 | 58 | 1130 | 61 | S/T | 0.813
72 | 58 | 1130 | 61 | ∆T | 18.9
72 | 58 | 1130 | 61 | LDB | 53.1
72 | 58 | 1130 | 61 | LWB | 52.1
72 | 58 | 1130 | 61 | kW | 1.3
77 | 58 | 1130 | 64 | MBh | 32.2
77 | 58 | 1130 | 64 | S/T | 0.789
77 | 58 | 1130 | 64 | ∆T | 20.8
77 | 58 | 1130 | 64 | LDB | 56.2
77 | 58 | 1130 | 64 | LWB | 54.4
77 | 58 | 1130 | 64 | kW | 1.5
80 | 58 | 1130 | 67 | MBh | 36
80 | 58 | 1130 | 67 | S/T | 0.756
80 | 58 | 1130 | 67 | ∆T | 22.3
80 | 58 | 1130 | 67 | LDB | 57.7
80 | 58 | 1130 | 67 | LWB | 56.9
80 | 58 | 1130 | 67 | kW | 1.7
84 | 58 | 1130 | 70 | MBh | 39.8
84 | 58 | 1130 | 70 | S/T | 0.726
84 | 58 | 1130 | 70 | ∆T | 23.7
84 | 58 | 1130 | 70 | LDB | 60.3
84 | 58 | 1130 | 70 | LWB | 59.5
84 | 58 | 1130 | 70 | kW | 1.91
86 | 58 | 1130 | 72 | MBh | 42.3
86 | 58 | 1130 | 72 | S/T | 0.7
86 | 58 | 1130 | 72 | ∆T | 24.3
86 | 58 | 1130 | 72 | LDB | 61.7
86 | 58 | 1130 | 72 | LWB | 61.3
86 | 58 | 1130 | 72 | kW | 2.05
90 | 58 | 1130 | 75 | MBh | 45.7
90 | 58 | 1130 | 75 | S/T | 0.656
90 | 58 | 1130 | 75 | ∆T | 24.6
90 | 58 | 1130 | 75 | LDB | 65.4
90 | 58 | 1130 | 75 | LWB | 64.2
90 | 58 | 1130 | 75 | kW | 2.23
68 | 62 | 1130 | 57 | MBh | 23.4
68 | 62 | 1130 | 57 | S/T | 0.846
68 | 62 | 1130 | 57 | ∆T | 16.2
68 | 62 | 1130 | 57 | LDB | 51.8
68 | 62 | 1130 | 57 | LWB | 49.1
68 | 62 | 1130 | 57 | kW | 1.07
72 | 62 | 1130 | 61 | MBh | 28.4
72 | 62 | 1130 | 61 | S/T | 0.813
72 | 62 | 1130 | 61 | ∆T | 18.9
72 | 62 | 1130 | 61 | LDB | 53.1
72 | 62 | 1130 | 61 | LWB | 52.1
72 | 62 | 1130 | 61 | kW | 1.33
77 | 62 | 1130 | 64 | MBh | 32.2
77 | 62 | 1130 | 64 | S/T | 0.789
77 | 62 | 1130 | 64 | ∆T | 20.8
77 | 62 | 1130 | 64 | LDB | 56.2
77 | 62 | 1130 | 64 | LWB | 54.4
77 | 62 | 1130 | 64 | kW | 1.53
80 | 62 | 1130 | 67 | MBh | 36
80 | 62 | 1130 | 67 | S/T | 0.756
80 | 62 | 1130 | 67 | ∆T | 22.3
80 | 62 | 1130 | 67 | LDB | 57.7
80 | 62 | 1130 | 67 | LWB | 56.9
80 | 62 | 1130 | 67 | kW | 1.74
84 | 62 | 1130 | 70 | MBh | 39.8
84 | 62 | 1130 | 70 | S/T | 0.726
84 | 62 | 1130 | 70 | ∆T | 23.7
84 | 62 | 1130 | 70 | LDB | 60.3
84 | 62 | 1130 | 70 | LWB | 59.5
84 | 62 | 1130 | 70 | kW | 1.95
86 | 62 | 1130 | 72 | MBh | 42.3
86 | 62 | 1130 | 72 | S/T | 0.7
86 | 62 | 1130 | 72 | ∆T | 24.3
86 | 62 | 1130 | 72 | LDB | 61.7
86 | 62 | 1130 | 72 | LWB | 61.3
86 | 62 | 1130 | 72 | kW | 2.1
90 | 62 | 1130 | 75 | MBh | 45
90 | 62 | 1130 | 75 | S/T | 0.658
90 | 62 | 1130 | 75 | ∆T | 24.3
90 | 62 | 1130 | 75 | LDB | 65.7
90 | 62 | 1130 | 75 | LWB | 64.4
90 | 62 | 1130 | 75 | kW | 2.21
68 | 66 | 1130 | 57 | MBh | 23.4
68 | 66 | 1130 | 57 | S/T | 0.846
68 | 66 | 1130 | 57 | ∆T | 16.2
68 | 66 | 1130 | 57 | LDB | 51.8
68 | 66 | 1130 | 57 | LWB | 49.1
68 | 66 | 1130 | 57 | kW | 1.09
72 | 66 | 1130 | 61 | MBh | 28.4
72 | 66 | 1130 | 61 | S/T | 0.813
72 | 66 | 1130 | 61 | ∆T | 18.9
72 | 66 | 1130 | 61 | LDB | 53.1
72 | 66 | 1130 | 61 | LWB | 52.1
72 | 66 | 1130 | 61 | kW | 1.36
77 | 66 | 1130 | 64 | MBh | 32.2
77 | 66 | 1130 | 64 | S/T | 0.789
77 | 66 | 1130 | 64 | ∆T | 20.8
77 | 66 | 1130 | 64 | LDB | 56.2
77 | 66 | 1130 | 64 | LWB | 54.4
77 | 66 | 1130 | 64 | kW | 1.56
80 | 66 | 1130 | 67 | MBh | 36
80 | 66 | 1130 | 67 | S/T | 0.756
80 | 66 | 1130 | 67 | ∆T | 22.3
80 | 66 | 1130 | 67 | LDB | 57.7
80 | 66 | 1130 | 67 | LWB | 56.9
80 | 66 | 1130 | 67 | kW | 1.78
84 | 66 | 1130 | 70 | MBh | 39.8
84 | 66 | 1130 | 70 | S/T | 0.726
84 | 66 | 1130 | 70 | ∆T | 23.7
84 | 66 | 1130 | 70 | LDB | 60.3
84 | 66 | 1130 | 70 | LWB | 59.5
84 | 66 | 1130 | 70 | kW | 2
86 | 66 | 1130 | 72 | MBh | 42.3
86 | 66 | 1130 | 72 | S/T | 0.7
86 | 66 | 1130 | 72 | ∆T | 24.3
86 | 66 | 1130 | 72 | LDB | 61.7
86 | 66 | 1130 | 72 | LWB | 61.3
86 | 66 | 1130 | 72 | kW | 2.14
90 | 66 | 1130 | 75 | MBh | 44.3
90 | 66 | 1130 | 75 | S/T | 0.657
90 | 66 | 1130 | 75 | ∆T | 23.8
90 | 66 | 1130 | 75 | LDB | 66.2
90 | 66 | 1130 | 75 | LWB | 64.6
90 | 66 | 1130 | 75 | kW | 2.2
68 | 70 | 1130 | 57 | MBh | 23.4
68 | 70 | 1130 | 57 | S/T | 0.846
68 | 70 | 1130 | 57 | ∆T | 16.2
68 | 70 | 1130 | 57 | LDB | 51.8
68 | 70 | 1130 | 57 | LWB | 49.1
68 | 70 | 1130 | 57 | kW | 1.11
72 | 70 | 1130 | 61 | MBh | 28.4
72 | 70 | 1130 | 61 | S/T | 0.813
72 | 70 | 1130 | 61 | ∆T | 18.9
72 | 70 | 1130 | 61 | LDB | 53.1
72 | 70 | 1130 | 61 | LWB | 52.1
72 | 70 | 1130 | 61 | kW | 1.39
77 | 70 | 1130 | 64 | MBh | 32.2
77 | 70 | 1130 | 64 | S/T | 0.789
77 | 70 | 1130 | 64 | ∆T | 20.8
77 | 70 | 1130 | 64 | LDB | 56.2
77 | 70 | 1130 | 64 | LWB | 54.4
77 | 70 | 1130 | 64 | kW | 1.6
80 | 70 | 1130 | 67 | MBh | 36
80 | 70 | 1130 | 67 | S/T | 0.756
80 | 70 | 1130 | 67 | ∆T | 22.3
80 | 70 | 1130 | 67 | LDB | 57.7
80 | 70 | 1130 | 67 | LWB | 56.9
80 | 70 | 1130 | 67 | kW | 1.82
84 | 70 | 1130 | 70 | MBh | 39.8
84 | 70 | 1130 | 70 | S/T | 0.726
84 | 70 | 1130 | 70 | ∆T | 23.7
84 | 70 | 1130 | 70 | LDB | 60.3
84 | 70 | 1130 | 70 | LWB | 59.5
84 | 70 | 1130 | 70 | kW | 2.04
86 | 70 | 1130 | 72 | MBh | 42.3
86 | 70 | 1130 | 72 | S/T | 0.7
86 | 70 | 1130 | 72 | ∆T | 24.3
86 | 70 | 1130 | 72 | LDB | 61.7
86 | 70 | 1130 | 72 | LWB | 61.3
86 | 70 | 1130 | 72 | kW | 2.19
90 | 70 | 1130 | 75 | MBh | 43.7
90 | 70 | 1130 | 75 | S/T | 0.657
90 | 70 | 1130 | 75 | ∆T | 23.5
90 | 70 | 1130 | 75 | LDB | 66.5
90 | 70 | 1130 | 75 | LWB | 64.7
90 | 70 | 1130 | 75 | kW | 2.19
68 | 72 | 1130 | 57 | MBh | 23.4
68 | 72 | 1130 | 57 | S/T | 0.846
68 | 72 | 1130 | 57 | ∆T | 16.2
68 | 72 | 1130 | 57 | LDB | 51.8
68 | 72 | 1130 | 57 | LWB | 49.1
68 | 72 | 1130 | 57 | kW | 1.13
72 | 72 | 1130 | 61 | MBh | 28.4
72 | 72 | 1130 | 61 | S/T | 0.813
72 | 72 | 1130 | 61 | ∆T | 18.9
72 | 72 | 1130 | 61 | LDB | 53.1
72 | 72 | 1130 | 61 | LWB | 52.1
72 | 72 | 1130 | 61 | kW | 1.4
77 | 72 | 1130 | 64 | MBh | 32.2
77 | 72 | 1130 | 64 | S/T | 0.789
77 | 72 | 1130 | 64 | ∆T | 20.8
77 | 72 | 1130 | 64 | LDB | 56.2
77 | 72 | 1130 | 64 | LWB | 54.4
77 | 72 | 1130 | 64 | kW | 1.62
80 | 72 | 1130 | 67 | MBh | 36
80 | 72 | 1130 | 67 | S/T | 0.756
80 | 72 | 1130 | 67 | ∆T | 22.3
80 | 72 | 1130 | 67 | LDB | 57.7
80 | 72 | 1130 | 67 | LWB | 56.9
80 | 72 | 1130 | 67 | kW | 1.84
84 | 72 | 1130 | 70 | MBh | 39.8
84 | 72 | 1130 | 70 | S/T | 0.726
84 | 72 | 1130 | 70 | ∆T | 23.7
84 | 72 | 1130 | 70 | LDB | 60.3
84 | 72 | 1130 | 70 | LWB | 59.5
84 | 72 | 1130 | 70 | kW | 2.06
86 | 72 | 1130 | 72 | MBh | 42.3
86 | 72 | 1130 | 72 | S/T | 0.7
86 | 72 | 1130 | 72 | ∆T | 24.3
86 | 72 | 1130 | 72 | LDB | 61.7
86 | 72 | 1130 | 72 | LWB | 61.3
86 | 72 | 1130 | 72 | kW | 2.22
90 | 72 | 1130 | 75 | MBh | 43.3
90 | 72 | 1130 | 75 | S/T | 0.658
90 | 72 | 1130 | 75 | ∆T | 23.4
90 | 72 | 1130 | 75 | LDB | 66.6
90 | 72 | 1130 | 75 | LWB | 64.8
90 | 72 | 1130 | 75 | kW | 2.18
68 | 75 | 1130 | 57 | MBh | 23.4
68 | 75 | 1130 | 57 | S/T | 0.846
68 | 75 | 1130 | 57 | ∆T | 16.2
68 | 75 | 1130 | 57 | LDB | 51.8
68 | 75 | 1130 | 57 | LWB | 49.1
68 | 75 | 1130 | 57 | kW | 1.14
72 | 75 | 1130 | 61 | MBh | 28.4
72 | 75 | 1130 | 61 | S/T | 0.813
72 | 75 | 1130 | 61 | ∆T | 18.9
72 | 75 | 1130 | 61 | LDB | 53.1
72 | 75 | 1130 | 61 | LWB | 52.1
72 | 75 | 1130 | 61 | kW | 1.42
77 | 75 | 1130 | 64 | MBh | 32.2
77 | 75 | 1130 | 64 | S/T | 0.789
77 | 75 | 1130 | 64 | ∆T | 20.8
77 | 75 | 1130 | 64 | LDB | 56.2
77 | 75 | 1130 | 64 | LWB | 54.4
77 | 75 | 1130 | 64 | kW | 1.64
80 | 75 | 1130 | 67 | MBh | 36
80 | 75 | 1130 | 67 | S/T | 0.756
80 | 75 | 1130 | 67 | ∆T | 22.3
80 | 75 | 1130 | 67 | LDB | 57.7
80 | 75 | 1130 | 67 | LWB | 56.9
80 | 75 | 1130 | 67 | kW | 1.87
84 | 75 | 1130 | 70 | MBh | 39.8
84 | 75 | 1130 | 70 | S/T | 0.726
84 | 75 | 1130 | 70 | ∆T | 23.7
84 | 75 | 1130 | 70 | LDB | 60.3
84 | 75 | 1130 | 70 | LWB | 59.5
84 | 75 | 1130 | 70 | kW | 2.1
86 | 75 | 1130 | 72 | MBh | 42.1
86 | 75 | 1130 | 72 | S/T | 0.698
86 | 75 | 1130 | 72 | ∆T | 24.1
86 | 75 | 1130 | 72 | LDB | 61.9
86 | 75 | 1130 | 72 | LWB | 61.4
86 | 75 | 1130 | 72 | kW | 2.25
90 | 75 | 1130 | 75 | MBh | 42.8
90 | 75 | 1130 | 75 | S/T | 0.657
90 | 75 | 1130 | 75 | ∆T | 23
90 | 75 | 1130 | 75 | LDB | 67
90 | 75 | 1130 | 75 | LWB | 65
90 | 75 | 1130 | 75 | kW | 2.27
68 | 79 | 1130 | 57 | MBh | 23.4
68 | 79 | 1130 | 57 | S/T | 0.846
68 | 79 | 1130 | 57 | ∆T | 16.2
68 | 79 | 1130 | 57 | LDB | 51.8
68 | 79 | 1130 | 57 | LWB | 49.1
68 | 79 | 1130 | 57 | kW | 1.17
72 | 79 | 1130 | 61 | MBh | 28.4
72 | 79 | 1130 | 61 | S/T | 0.813
72 | 79 | 1130 | 61 | ∆T | 18.9
72 | 79 | 1130 | 61 | LDB | 53.1
72 | 79 | 1130 | 61 | LWB | 52.1
72 | 79 | 1130 | 61 | kW | 1.46
77 | 79 | 1130 | 64 | MBh | 32.2
77 | 79 | 1130 | 64 | S/T | 0.789
77 | 79 | 1130 | 64 | ∆T | 20.8
77 | 79 | 1130 | 64 | LDB | 56.2
77 | 79 | 1130 | 64 | LWB | 54.4
77 | 79 | 1130 | 64 | kW | 1.71
80 | 79 | 1130 | 67 | MBh | 36
80 | 79 | 1130 | 67 | S/T | 0.756
80 | 79 | 1130 | 67 | ∆T | 22.3
80 | 79 | 1130 | 67 | LDB | 57.7
80 | 79 | 1130 | 67 | LWB | 56.9
80 | 79 | 1130 | 67 | kW | 2.01
84 | 79 | 1130 | 70 | MBh | 39.8
84 | 79 | 1130 | 70 | S/T | 0.726
84 | 79 | 1130 | 70 | ∆T | 23.7
84 | 79 | 1130 | 70 | LDB | 60.3
84 | 79 | 1130 | 70 | LWB | 59.5
84 | 79 | 1130 | 70 | kW | 2.34
86 | 79 | 1130 | 72 | MBh | 41.4
86 | 79 | 1130 | 72 | S/T | 0.698
86 | 79 | 1130 | 72 | ∆T | 23.7
86 | 79 | 1130 | 72 | LDB | 62.3
86 | 79 | 1130 | 72 | LWB | 61.6
86 | 79 | 1130 | 72 | kW | 2.47
90 | 79 | 1130 | 75 | MBh | 42.1
90 | 79 | 1130 | 75 | S/T | 0.658
90 | 79 | 1130 | 75 | ∆T | 22.7
90 | 79 | 1130 | 75 | LDB | 67.3
90 | 79 | 1130 | 75 | LWB | 65.1
90 | 79 | 1130 | 75 | kW | 2.48
68 | 83 | 1130 | 57 | MBh | 23.4
68 | 83 | 1130 | 57 | S/T | 0.846
68 | 83 | 1130 | 57 | ∆T | 16.2
68 | 83 | 1130 | 57 | LDB | 51.8
68 | 83 | 1130 | 57 | LWB | 49.1
68 | 83 | 1130 | 57 | kW | 1.23
72 | 83 | 1130 | 61 | MBh | 28.4
72 | 83 | 1130 | 61 | S/T | 0.813
72 | 83 | 1130 | 61 | ∆T | 18.9
72 | 83 | 1130 | 61 | LDB | 53.1
72 | 83 | 1130 | 61 | LWB | 52.1
72 | 83 | 1130 | 61 | kW | 1.6
77 | 83 | 1130 | 64 | MBh | 32.2
77 | 83 | 1130 | 64 | S/T | 0.789
77 | 83 | 1130 | 64 | ∆T | 20.8
77 | 83 | 1130 | 64 | LDB | 56.2
77 | 83 | 1130 | 64 | LWB | 54.4
77 | 83 | 1130 | 64 | kW | 1.91
80 | 83 | 1130 | 67 | MBh | 36
80 | 83 | 1130 | 67 | S/T | 0.756
80 | 83 | 1130 | 67 | ∆T | 22.3
80 | 83 | 1130 | 67 | LDB | 57.7
80 | 83 | 1130 | 67 | LWB | 56.9
80 | 83 | 1130 | 67 | kW | 2.25
84 | 83 | 1130 | 70 | MBh | 39.8
84 | 83 | 1130 | 70 | S/T | 0.726
84 | 83 | 1130 | 70 | ∆T | 23.7
84 | 83 | 1130 | 70 | LDB | 60.3
84 | 83 | 1130 | 70 | LWB | 59.5
84 | 83 | 1130 | 70 | kW | 2.62
86 | 83 | 1130 | 72 | MBh | 40.7
86 | 83 | 1130 | 72 | S/T | 0.7
86 | 83 | 1130 | 72 | ∆T | 23.4
86 | 83 | 1130 | 72 | LDB | 62.6
86 | 83 | 1130 | 72 | LWB | 61.8
86 | 83 | 1130 | 72 | kW | 2.68
90 | 83 | 1130 | 75 | MBh | 41.5
90 | 83 | 1130 | 75 | S/T | 0.655
90 | 83 | 1130 | 75 | ∆T | 22.3
90 | 83 | 1130 | 75 | LDB | 67.7
90 | 83 | 1130 | 75 | LWB | 65.3
90 | 83 | 1130 | 75 | kW | 2.7
68 | 87 | 1130 | 57 | MBh | 23.4
68 | 87 | 1130 | 57 | S/T | 0.846
68 | 87 | 1130 | 57 | ∆T | 16.2
68 | 87 | 1130 | 57 | LDB | 51.8
68 | 87 | 1130 | 57 | LWB | 49.1
68 | 87 | 1130 | 57 | kW | 1.37
72 | 87 | 1130 | 61 | MBh | 28.4
72 | 87 | 1130 | 61 | S/T | 0.813
72 | 87 | 1130 | 61 | ∆T | 18.9
72 | 87 | 1130 | 61 | LDB | 53.1
72 | 87 | 1130 | 61 | LWB | 52.1
72 | 87 | 1130 | 61 | kW | 1.78
77 | 87 | 1130 | 64 | MBh | 32.2
77 | 87 | 1130 | 64 | S/T | 0.789
77 | 87 | 1130 | 64 | ∆T | 20.8
77 | 87 | 1130 | 64 | LDB | 56.2
77 | 87 | 1130 | 64 | LWB | 54.4
77 | 87 | 1130 | 64 | kW | 2.13
80 | 87 | 1130 | 67 | MBh | 36
80 | 87 | 1130 | 67 | S/T | 0.756
80 | 87 | 1130 | 67 | ∆T | 22.3
80 | 87 | 1130 | 67 | LDB | 57.7
80 | 87 | 1130 | 67 | LWB | 56.9
80 | 87 | 1130 | 67 | kW | 2.51
84 | 87 | 1130 | 70 | MBh | 39.5
84 | 87 | 1130 | 70 | S/T | 0.727
84 | 87 | 1130 | 70 | ∆T | 23.5
84 | 87 | 1130 | 70 | LDB | 60.5
84 | 87 | 1130 | 70 | LWB | 59.6
84 | 87 | 1130 | 70 | kW | 2.88
86 | 87 | 1130 | 72 | MBh | 40
86 | 87 | 1130 | 72 | S/T | 0.7
86 | 87 | 1130 | 72 | ∆T | 22.9
86 | 87 | 1130 | 72 | LDB | 63.1
86 | 87 | 1130 | 72 | LWB | 62
86 | 87 | 1130 | 72 | kW | 2.9
90 | 87 | 1130 | 75 | MBh | 40.8
90 | 87 | 1130 | 75 | S/T | 0.657
90 | 87 | 1130 | 75 | ∆T | 22
90 | 87 | 1130 | 75 | LDB | 68
90 | 87 | 1130 | 75 | LWB | 65.5
90 | 87 | 1130 | 75 | kW | 2.92
68 | 91 | 1130 | 57 | MBh | 23.4
68 | 91 | 1130 | 57 | S/T | 0.846
68 | 91 | 1130 | 57 | ∆T | 16.2
68 | 91 | 1130 | 57 | LDB | 51.8
68 | 91 | 1130 | 57 | LWB | 49.1
68 | 91 | 1130 | 57 | kW | 1.51
72 | 91 | 1130 | 61 | MBh | 28.4
72 | 91 | 1130 | 61 | S/T | 0.813
72 | 91 | 1130 | 61 | ∆T | 18.9
72 | 91 | 1130 | 61 | LDB | 53.1
72 | 91 | 1130 | 61 | LWB | 52.1
72 | 91 | 1130 | 61 | kW | 1.97
77 | 91 | 1130 | 64 | MBh | 32.2
77 | 91 | 1130 | 64 | S/T | 0.789
77 | 91 | 1130 | 64 | ∆T | 20.8
77 | 91 | 1130 | 64 | LDB | 56.2
77 | 91 | 1130 | 64 | LWB | 54.4
77 | 91 | 1130 | 64 | kW | 2.35
80 | 91 | 1130 | 67 | MBh | 36
80 | 91 | 1130 | 67 | S/T | 0.756
80 | 91 | 1130 | 67 | ∆T | 22.3
80 | 91 | 1130 | 67 | LDB | 57.7
80 | 91 | 1130 | 67 | LWB | 56.9
80 | 91 | 1130 | 67 | kW | 2.78
84 | 91 | 1130 | 70 | MBh | 38.9
84 | 91 | 1130 | 70 | S/T | 0.725
84 | 91 | 1130 | 70 | ∆T | 23.1
84 | 91 | 1130 | 70 | LDB | 60.9
84 | 91 | 1130 | 70 | LWB | 59.8
84 | 91 | 1130 | 70 | kW | 3.1
86 | 91 | 1130 | 72 | MBh | 39.4
86 | 91 | 1130 | 72 | S/T | 0.698
86 | 91 | 1130 | 72 | ∆T | 22.5
86 | 91 | 1130 | 72 | LDB | 63.5
86 | 91 | 1130 | 72 | LWB | 62.1
86 | 91 | 1130 | 72 | kW | 3.11
90 | 91 | 1130 | 75 | MBh | 40.1
90 | 91 | 1130 | 75 | S/T | 0.658
90 | 91 | 1130 | 75 | ∆T | 21.6
90 | 91 | 1130 | 75 | LDB | 68.4
90 | 91 | 1130 | 75 | LWB | 65.7
90 | 91 | 1130 | 75 | kW | 3.13
68 | 93 | 1130 | 57 | MBh | 23.4
68 | 93 | 1130 | 57 | S/T | 0.846
68 | 93 | 1130 | 57 | ∆T | 16.2
68 | 93 | 1130 | 57 | LDB | 51.8
68 | 93 | 1130 | 57 | LWB | 49.1
68 | 93 | 1130 | 57 | kW | 1.58
72 | 93 | 1130 | 61 | MBh | 28.4
72 | 93 | 1130 | 61 | S/T | 0.813
72 | 93 | 1130 | 61 | ∆T | 18.9
72 | 93 | 1130 | 61 | LDB | 53.1
72 | 93 | 1130 | 61 | LWB | 52.1
72 | 93 | 1130 | 61 | kW | 2.07
77 | 93 | 1130 | 64 | MBh | 32.2
77 | 93 | 1130 | 64 | S/T | 0.789
77 | 93 | 1130 | 64 | ∆T | 20.8
77 | 93 | 1130 | 64 | LDB | 56.2
77 | 93 | 1130 | 64 | LWB | 54.4
77 | 93 | 1130 | 64 | kW | 2.47
80 | 93 | 1130 | 67 | MBh | 36
80 | 93 | 1130 | 67 | S/T | 0.756
80 | 93 | 1130 | 67 | ∆T | 22.3
80 | 93 | 1130 | 67 | LDB | 57.7
80 | 93 | 1130 | 67 | LWB | 56.9
80 | 93 | 1130 | 67 | kW | 2.92
84 | 93 | 1130 | 70 | MBh | 38.5
84 | 93 | 1130 | 70 | S/T | 0.727
84 | 93 | 1130 | 70 | ∆T | 22.9
84 | 93 | 1130 | 70 | LDB | 61.1
84 | 93 | 1130 | 70 | LWB | 59.9
84 | 93 | 1130 | 70 | kW | 3.21
86 | 93 | 1130 | 72 | MBh | 39
86 | 93 | 1130 | 72 | S/T | 0.7
86 | 93 | 1130 | 72 | ∆T | 22.4
86 | 93 | 1130 | 72 | LDB | 63.6
86 | 93 | 1130 | 72 | LWB | 62.2
86 | 93 | 1130 | 72 | kW | 3.22
90 | 93 | 1130 | 75 | MBh | 39.8
90 | 93 | 1130 | 75 | S/T | 0.656
90 | 93 | 1130 | 75 | ∆T | 21.4
90 | 93 | 1130 | 75 | LDB | 68.6
90 | 93 | 1130 | 75 | LWB | 65.7
90 | 93 | 1130 | 75 | kW | 3.24
68 | 95 | 1130 | 57 | MBh | 23.4
68 | 95 | 1130 | 57 | S/T | 0.846
68 | 95 | 1130 | 57 | ∆T | 16.2
68 | 95 | 1130 | 57 | LDB | 51.8
68 | 95 | 1130 | 57 | LWB | 49.1
68 | 95 | 1130 | 57 | kW | 1.66
72 | 95 | 1130 | 61 | MBh | 28.4
72 | 95 | 1130 | 61 | S/T | 0.813
72 | 95 | 1130 | 61 | ∆T | 18.9
72 | 95 | 1130 | 61 | LDB | 53.1
72 | 95 | 1130 | 61 | LWB | 52.1
72 | 95 | 1130 | 61 | kW | 2.17
77 | 95 | 1130 | 64 | MBh | 32.2
77 | 95 | 1130 | 64 | S/T | 0.789
77 | 95 | 1130 | 64 | ∆T | 20.8
77 | 95 | 1130 | 64 | LDB | 56.2
77 | 95 | 1130 | 64 | LWB | 54.4
77 | 95 | 1130 | 64 | kW | 2.6
80 | 95 | 1130 | 67 | MBh | 36
80 | 95 | 1130 | 67 | S/T | 0.756
80 | 95 | 1130 | 67 | ∆T | 22.3
80 | 95 | 1130 | 67 | LDB | 57.7
80 | 95 | 1130 | 67 | LWB | 56.9
80 | 95 | 1130 | 67 | kW | 3.07
84 | 95 | 1130 | 70 | MBh | 38.2
84 | 95 | 1130 | 70 | S/T | 0.728
84 | 95 | 1130 | 70 | ∆T | 22.8
84 | 95 | 1130 | 70 | LDB | 61.2
84 | 95 | 1130 | 70 | LWB | 60
84 | 95 | 1130 | 70 | kW | 3.32
86 | 95 | 1130 | 72 | MBh | 38.7
86 | 95 | 1130 | 72 | S/T | 0.698
86 | 95 | 1130 | 72 | ∆T | 22.1
86 | 95 | 1130 | 72 | LDB | 63.9
86 | 95 | 1130 | 72 | LWB | 62.3
86 | 95 | 1130 | 72 | kW | 3.33
90 | 95 | 1130 | 75 | MBh | 39.4
90 | 95 | 1130 | 75 | S/T | 0.657
90 | 95 | 1130 | 75 | ∆T | 21.2
90 | 95 | 1130 | 75 | LDB | 68.8
90 | 95 | 1130 | 75 | LWB | 65.8
90 | 95 | 1130 | 75 | kW | 3.35
68 | 99 | 1130 | 57 | MBh | 23.4
68 | 99 | 1130 | 57 | S/T | 0.846
68 | 99 | 1130 | 57 | ∆T | 16.2
68 | 99 | 1130 | 57 | LDB | 51.8
68 | 99 | 1130 | 57 | LWB | 49.1
68 | 99 | 1130 | 57 | kW | 1.82
72 | 99 | 1130 | 61 | MBh | 28.4
72 | 99 | 1130 | 61 | S/T | 0.813
72 | 99 | 1130 | 61 | ∆T | 18.9
72 | 99 | 1130 | 61 | LDB | 53.1
72 | 99 | 1130 | 61 | LWB | 52.1
72 | 99 | 1130 | 61 | kW | 2.38
77 | 99 | 1130 | 64 | MBh | 32.2
77 | 99 | 1130 | 64 | S/T | 0.789
77 | 99 | 1130 | 64 | ∆T | 20.8
77 | 99 | 1130 | 64 | LDB | 56.2
77 | 99 | 1130 | 64 | LWB | 54.4
77 | 99 | 1130 | 64 | kW | 2.86
80 | 99 | 1130 | 67 | MBh | 36
80 | 99 | 1130 | 67 | S/T | 0.756
80 | 99 | 1130 | 67 | ∆T | 22.3
80 | 99 | 1130 | 67 | LDB | 57.7
80 | 99 | 1130 | 67 | LWB | 56.9
80 | 99 | 1130 | 67 | kW | 3.37
84 | 99 | 1130 | 70 | MBh | 37.5
84 | 99 | 1130 | 70 | S/T | 0.728
84 | 99 | 1130 | 70 | ∆T | 22.4
84 | 99 | 1130 | 70 | LDB | 61.6
84 | 99 | 1130 | 70 | LWB | 60.2
84 | 99 | 1130 | 70 | kW | 3.53
86 | 99 | 1130 | 72 | MBh | 38
86 | 99 | 1130 | 72 | S/T | 0.7
86 | 99 | 1130 | 72 | ∆T | 21.8
86 | 99 | 1130 | 72 | LDB | 64.2
86 | 99 | 1130 | 72 | LWB | 62.5
86 | 99 | 1130 | 72 | kW | 3.55
90 | 99 | 1130 | 75 | MBh | 38.8
90 | 99 | 1130 | 75 | S/T | 0.657
90 | 99 | 1130 | 75 | ∆T | 20.9
90 | 99 | 1130 | 75 | LDB | 69.1
90 | 99 | 1130 | 75 | LWB | 66
90 | 99 | 1130 | 75 | kW | 3.57
68 | 103 | 1130 | 57 | MBh | 23.4
68 | 103 | 1130 | 57 | S/T | 0.846
68 | 103 | 1130 | 57 | ∆T | 16.2
68 | 103 | 1130 | 57 | LDB | 51.8
68 | 103 | 1130 | 57 | LWB | 49.1
68 | 103 | 1130 | 57 | kW | 1.98
72 | 103 | 1130 | 61 | MBh | 28.4
72 | 103 | 1130 | 61 | S/T | 0.813
72 | 103 | 1130 | 61 | ∆T | 18.9
72 | 103 | 1130 | 61 | LDB | 53.1
72 | 103 | 1130 | 61 | LWB | 52.1
72 | 103 | 1130 | 61 | kW | 2.61
77 | 103 | 1130 | 64 | MBh | 32.2
77 | 103 | 1130 | 64 | S/T | 0.789
77 | 103 | 1130 | 64 | ∆T | 20.8
77 | 103 | 1130 | 64 | LDB | 56.2
77 | 103 | 1130 | 64 | LWB | 54.4
77 | 103 | 1130 | 64 | kW | 3.13
80 | 103 | 1130 | 67 | MBh | 36
80 | 103 | 1130 | 67 | S/T | 0.756
80 | 103 | 1130 | 67 | ∆T | 22.3
80 | 103 | 1130 | 67 | LDB | 57.7
80 | 103 | 1130 | 67 | LWB | 56.9
80 | 103 | 1130 | 67 | kW | 3.7
84 | 103 | 1130 | 70 | MBh | 36.8
84 | 103 | 1130 | 70 | S/T | 0.728
84 | 103 | 1130 | 70 | ∆T | 22
84 | 103 | 1130 | 70 | LDB | 62
84 | 103 | 1130 | 70 | LWB | 60.4
84 | 103 | 1130 | 70 | kW | 3.75
86 | 103 | 1130 | 72 | MBh | 37.3
86 | 103 | 1130 | 72 | S/T | 0.7
86 | 103 | 1130 | 72 | ∆T | 21.4
86 | 103 | 1130 | 72 | LDB | 64.6
86 | 103 | 1130 | 72 | LWB | 62.7
86 | 103 | 1130 | 72 | kW | 3.77
90 | 103 | 1130 | 75 | MBh | 37.9
90 | 103 | 1130 | 75 | S/T | 0.657
90 | 103 | 1130 | 75 | ∆T | 20.4
90 | 103 | 1130 | 75 | LDB | 69.6
90 | 103 | 1130 | 75 | LWB | 66.2
90 | 103 | 1130 | 75 | kW | 3.79
68 | 106 | 1130 | 57 | MBh | 23.4
68 | 106 | 1130 | 57 | S/T | 0.846
68 | 106 | 1130 | 57 | ∆T | 16.2
68 | 106 | 1130 | 57 | LDB | 51.8
68 | 106 | 1130 | 57 | LWB | 49.1
68 | 106 | 1130 | 57 | kW | 2.12
72 | 106 | 1130 | 61 | MBh | 28.4
72 | 106 | 1130 | 61 | S/T | 0.813
72 | 106 | 1130 | 61 | ∆T | 18.9
72 | 106 | 1130 | 61 | LDB | 53.1
72 | 106 | 1130 | 61 | LWB | 52.1
72 | 106 | 1130 | 61 | kW | 2.79
77 | 106 | 1130 | 64 | MBh | 32.2
77 | 106 | 1130 | 64 | S/T | 0.789
77 | 106 | 1130 | 64 | ∆T | 20.8
77 | 106 | 1130 | 64 | LDB | 56.2
77 | 106 | 1130 | 64 | LWB | 54.4
77 | 106 | 1130 | 64 | kW | 3.35
80 | 106 | 1130 | 67 | MBh | 35.6
80 | 106 | 1130 | 67 | S/T | 0.756
80 | 106 | 1130 | 67 | ∆T | 22
80 | 106 | 1130 | 67 | LDB | 58
80 | 106 | 1130 | 67 | LWB | 57
80 | 106 | 1130 | 67 | kW | 3.88
84 | 106 | 1130 | 70 | MBh | 36.3
84 | 106 | 1130 | 70 | S/T | 0.727
84 | 106 | 1130 | 70 | ∆T | 21.6
84 | 106 | 1130 | 70 | LDB | 62.4
84 | 106 | 1130 | 70 | LWB | 60.5
84 | 106 | 1130 | 70 | kW | 3.91
86 | 106 | 1130 | 72 | MBh | 36.6
86 | 106 | 1130 | 72 | S/T | 0.699
86 | 106 | 1130 | 72 | ∆T | 21
86 | 106 | 1130 | 72 | LDB | 65
86 | 106 | 1130 | 72 | LWB | 62.9
86 | 106 | 1130 | 72 | kW | 3.93
90 | 106 | 1130 | 75 | MBh | 36.6
90 | 106 | 1130 | 75 | S/T | 0.658
90 | 106 | 1130 | 75 | ∆T | 19.7
90 | 106 | 1130 | 75 | LDB | 70.3
90 | 106 | 1130 | 75 | LWB | 66.6
90 | 106 | 1130 | 75 | kW | 3.93
68 | 110 | 1130 | 57 | MBh | 23.4
68 | 110 | 1130 | 57 | S/T | 0.846
68 | 110 | 1130 | 57 | ∆T | 16.2
68 | 110 | 1130 | 57 | LDB | 51.8
68 | 110 | 1130 | 57 | LWB | 49.1
68 | 110 | 1130 | 57 | kW | 2.31
72 | 110 | 1130 | 61 | MBh | 28.4
72 | 110 | 1130 | 61 | S/T | 0.813
72 | 110 | 1130 | 61 | ∆T | 18.9
72 | 110 | 1130 | 61 | LDB | 53.1
72 | 110 | 1130 | 61 | LWB | 52.1
72 | 110 | 1130 | 61 | kW | 3.04
77 | 110 | 1130 | 64 | MBh | 32.2
77 | 110 | 1130 | 64 | S/T | 0.789
77 | 110 | 1130 | 64 | ∆T | 20.8
77 | 110 | 1130 | 64 | LDB | 56.2
77 | 110 | 1130 | 64 | LWB | 54.4
77 | 110 | 1130 | 64 | kW | 3.66
80 | 110 | 1130 | 67 | MBh | 34.9
80 | 110 | 1130 | 67 | S/T | 0.756
80 | 110 | 1130 | 67 | ∆T | 21.6
80 | 110 | 1130 | 67 | LDB | 58.4
80 | 110 | 1130 | 67 | LWB | 57.2
80 | 110 | 1130 | 67 | kW | 4.1
84 | 110 | 1130 | 70 | MBh | 35
84 | 110 | 1130 | 70 | S/T | 0.726
84 | 110 | 1130 | 70 | ∆T | 20.8
84 | 110 | 1130 | 70 | LDB | 63.2
84 | 110 | 1130 | 70 | LWB | 60.9
84 | 110 | 1130 | 70 | kW | 4.11
86 | 110 | 1130 | 72 | MBh | 35
86 | 110 | 1130 | 72 | S/T | 0.7
86 | 110 | 1130 | 72 | ∆T | 20.1
86 | 110 | 1130 | 72 | LDB | 65.9
86 | 110 | 1130 | 72 | LWB | 63.3
86 | 110 | 1130 | 72 | kW | 4.11
90 | 110 | 1130 | 75 | MBh | 35
90 | 110 | 1130 | 75 | S/T | 0.657
90 | 110 | 1130 | 75 | ∆T | 18.8
90 | 110 | 1130 | 75 | LDB | 71.2
90 | 110 | 1130 | 75 | LWB | 67
90 | 110 | 1130 | 75 | kW | 4.11
68 | 115 | 1130 | 57 | MBh | 23.4
68 | 115 | 1130 | 57 | S/T | 0.846
68 | 115 | 1130 | 57 | ∆T | 16.2
68 | 115 | 1130 | 57 | LDB | 51.8
68 | 115 | 1130 | 57 | LWB | 49.1
68 | 115 | 1130 | 57 | kW | 2.56
72 | 115 | 1130 | 61 | MBh | 28.4
72 | 115 | 1130 | 61 | S/T | 0.813
72 | 115 | 1130 | 61 | ∆T | 18.9
72 | 115 | 1130 | 61 | LDB | 53.1
72 | 115 | 1130 | 61 | LWB | 52.1
72 | 115 | 1130 | 61 | kW | 3.39
77 | 115 | 1130 | 64 | MBh | 30.4
77 | 115 | 1130 | 64 | S/T | 0.789
77 | 115 | 1130 | 64 | ∆T | 19.7
77 | 115 | 1130 | 64 | LDB | 57.3
77 | 115 | 1130 | 64 | LWB | 55
77 | 115 | 1130 | 64 | kW | 3.74
80 | 115 | 1130 | 67 | MBh | 30.4
80 | 115 | 1130 | 67 | S/T | 0.753
80 | 115 | 1130 | 67 | ∆T | 18.8
80 | 115 | 1130 | 67 | LDB | 61.2
80 | 115 | 1130 | 67 | LWB | 58.6
80 | 115 | 1130 | 67 | kW | 3.74
84 | 115 | 1130 | 70 | MBh | 30.4
84 | 115 | 1130 | 70 | S/T | 0.727
84 | 115 | 1130 | 70 | ∆T | 18.1
84 | 115 | 1130 | 70 | LDB | 65.9
84 | 115 | 1130 | 70 | LWB | 62.2
84 | 115 | 1130 | 70 | kW | 3.74
86 | 115 | 1130 | 72 | MBh | 30.4
86 | 115 | 1130 | 72 | S/T | 0.697
86 | 115 | 1130 | 72 | ∆T | 17.4
86 | 115 | 1130 | 72 | LDB | 68.6
86 | 115 | 1130 | 72 | LWB | 64.6
86 | 115 | 1130 | 72 | kW | 3.74
90 | 115 | 1130 | 75 | MBh | 30.4
90 | 115 | 1130 | 75 | S/T | 0.658
90 | 115 | 1130 | 75 | ∆T | 16.4
90 | 115 | 1130 | 75 | LDB | 73.6
90 | 115 | 1130 | 75 | LWB | 68.1
90 | 115 | 1130 | 75 | kW | 3.74
68 | 118 | 1130 | 57 | MBh | 23.4
68 | 118 | 1130 | 57 | S/T | 0.846
68 | 118 | 1130 | 57 | ∆T | 16.2
68 | 118 | 1130 | 57 | LDB | 51.8
68 | 118 | 1130 | 57 | LWB | 49.1
68 | 118 | 1130 | 57 | kW | 2.72
72 | 118 | 1130 | 61 | MBh | 26.7
72 | 118 | 1130 | 61 | S/T | 0.813
72 | 118 | 1130 | 61 | ∆T | 17.8
72 | 118 | 1130 | 61 | LDB | 54.2
72 | 118 | 1130 | 61 | LWB | 52.7
72 | 118 | 1130 | 61 | kW | 3.3
77 | 118 | 1130 | 64 | MBh | 26.7
77 | 118 | 1130 | 64 | S/T | 0.79
77 | 118 | 1130 | 64 | ∆T | 17.3
77 | 118 | 1130 | 64 | LDB | 59.7
77 | 118 | 1130 | 64 | LWB | 56.2
77 | 118 | 1130 | 64 | kW | 3.3
80 | 118 | 1130 | 67 | MBh | 26.7
80 | 118 | 1130 | 67 | S/T | 0.757
80 | 118 | 1130 | 67 | ∆T | 16.6
80 | 118 | 1130 | 67 | LDB | 63.4
80 | 118 | 1130 | 67 | LWB | 59.7
80 | 118 | 1130 | 67 | kW | 3.3
84 | 118 | 1130 | 70 | MBh | 26.7
84 | 118 | 1130 | 70 | S/T | 0.727
84 | 118 | 1130 | 70 | ∆T | 15.9
84 | 118 | 1130 | 70 | LDB | 68.1
84 | 118 | 1130 | 70 | LWB | 63.2
84 | 118 | 1130 | 70 | kW | 3.3
86 | 118 | 1130 | 72 | MBh | 26.7
86 | 118 | 1130 | 72 | S/T | 0.7
86 | 118 | 1130 | 72 | ∆T | 15.3
86 | 118 | 1130 | 72 | LDB | 70.7
86 | 118 | 1130 | 72 | LWB | 65.5
86 | 118 | 1130 | 72 | kW | 3.3
90 | 118 | 1130 | 75 | MBh | 26.7
90 | 118 | 1130 | 75 | S/T | 0.655
90 | 118 | 1130 | 75 | ∆T | 14.3
90 | 118 | 1130 | 75 | LDB | 75.7
90 | 118 | 1130 | 75 | LWB | 69
90 | 118 | 1130 | 75 | kW | 3.3
68 | 122 | 1130 | 57 | MBh | 21.8
68 | 122 | 1130 | 57 | S/T | 0.849
68 | 122 | 1130 | 57 | ∆T | 15.2
68 | 122 | 1130 | 57 | LDB | 52.8
68 | 122 | 1130 | 57 | LWB | 49.7
68 | 122 | 1130 | 57 | kW | 2.69
72 | 122 | 1130 | 61 | MBh | 21.8
72 | 122 | 1130 | 61 | S/T | 0.817
72 | 122 | 1130 | 61 | ∆T | 14.6
72 | 122 | 1130 | 61 | LDB | 57.4
72 | 122 | 1130 | 61 | LWB | 54.3
72 | 122 | 1130 | 61 | kW | 2.69
77 | 122 | 1130 | 64 | MBh | 21.8
77 | 122 | 1130 | 64 | S/T | 0.789
77 | 122 | 1130 | 64 | ∆T | 14.1
77 | 122 | 1130 | 64 | LDB | 62.9
77 | 122 | 1130 | 64 | LWB | 57.7
77 | 122 | 1130 | 64 | kW | 2.69
80 | 122 | 1130 | 67 | MBh | 21.8
80 | 122 | 1130 | 67 | S/T | 0.757
80 | 122 | 1130 | 67 | ∆T | 13.5
80 | 122 | 1130 | 67 | LDB | 66.5
80 | 122 | 1130 | 67 | LWB | 61.1
80 | 122 | 1130 | 67 | kW | 2.69
84 | 122 | 1130 | 70 | MBh | 21.8
84 | 122 | 1130 | 70 | S/T | 0.729
84 | 122 | 1130 | 70 | ∆T | 13
84 | 122 | 1130 | 70 | LDB | 71
84 | 122 | 1130 | 70 | LWB | 64.5
84 | 122 | 1130 | 70 | kW | 2.69
86 | 122 | 1130 | 72 | MBh | 21.8
86 | 122 | 1130 | 72 | S/T | 0.702
86 | 122 | 1130 | 72 | ∆T | 12.5
86 | 122 | 1130 | 72 | LDB | 73.5
86 | 122 | 1130 | 72 | LWB | 66.8
86 | 122 | 1130 | 72 | kW | 2.69
90 | 122 | 1130 | 75 | MBh | 21.8
90 | 122 | 1130 | 75 | S/T | 0.656
90 | 122 | 1130 | 75 | ∆T | 11.7
90 | 122 | 1130 | 75 | LDB | 78.3
90 | 122 | 1130 | 75 | LWB | 70.2
90 | 122 | 1130 | 75 | kW | 2.69

## RZA42AAVJU - FBA42AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1377 | 57 | MBh | 26.3 | 64 | 60 | 61 | 56.4 | 3.99
68 | 23 | 1377 | 57 | S/T | 0.852 | 64 | 60 | 65 | 52.2 | 3.48
68 | 23 | 1377 | 57 | ∆T | 15.1 | 64 | 60 | 68 | 49.1 | 3.1
68 | 23 | 1377 | 57 | LDB | 52.9 | 64 | 60 | 70 | 47 | 2.85
68 | 23 | 1377 | 57 | LWB | 49.8 | 64 | 60 | 72 | 44.9 | 2.6
68 | 23 | 1377 | 57 | kW | 1.13 | 64 | 60 | 75 | 41.8 | 2.24
72 | 23 | 1377 | 61 | MBh | 32 | 60 | 56 | 61 | 56.4 | 4.23
72 | 23 | 1377 | 61 | S/T | 0.816 | 60 | 56 | 65 | 52.2 | 3.69
72 | 23 | 1377 | 61 | ∆T | 17.6 | 60 | 56 | 68 | 49.1 | 3.29
72 | 23 | 1377 | 61 | LDB | 54.4 | 60 | 56 | 70 | 47 | 3.03
72 | 23 | 1377 | 61 | LWB | 52.8 | 60 | 56 | 72 | 44.9 | 2.78
72 | 23 | 1377 | 61 | kW | 1.39 | 60 | 56 | 75 | 41.8 | 2.4
77 | 23 | 1377 | 64 | MBh | 36.2 | 57 | 53 | 61 | 56.4 | 4.43
77 | 23 | 1377 | 64 | S/T | 0.79 | 57 | 53 | 65 | 52.2 | 3.87
77 | 23 | 1377 | 64 | ∆T | 19.2 | 57 | 53 | 68 | 49.1 | 3.45
77 | 23 | 1377 | 64 | LDB | 57.8 | 57 | 53 | 70 | 47 | 3.19
77 | 23 | 1377 | 64 | LWB | 55.2 | 57 | 53 | 72 | 44.9 | 2.92
77 | 23 | 1377 | 64 | kW | 1.6 | 57 | 53 | 75 | 41.8 | 2.53
80 | 23 | 1377 | 67 | MBh | 40.5 | 54 | 50 | 61 | 56.4 | 4.63
80 | 23 | 1377 | 67 | S/T | 0.753 | 54 | 50 | 65 | 52.2 | 4.05
80 | 23 | 1377 | 67 | ∆T | 20.5 | 54 | 50 | 68 | 49.1 | 3.62
80 | 23 | 1377 | 67 | LDB | 59.5 | 54 | 50 | 70 | 47 | 3.35
80 | 23 | 1377 | 67 | LWB | 57.8 | 54 | 50 | 72 | 44.9 | 3.07
80 | 23 | 1377 | 67 | kW | 1.81 | 54 | 50 | 75 | 41.8 | 2.67
84 | 23 | 1377 | 70 | MBh | 44.8 | 51 | 47 | 61 | 56.4 | 4.85
84 | 23 | 1377 | 70 | S/T | 0.725 | 51 | 47 | 65 | 52.2 | 4.25
84 | 23 | 1377 | 70 | ∆T | 21.9 | 51 | 47 | 68 | 49.1 | 3.81
84 | 23 | 1377 | 70 | LDB | 62.1 | 51 | 47 | 70 | 47 | 3.52
84 | 23 | 1377 | 70 | LWB | 60.4 | 51 | 47 | 72 | 44.9 | 3.23
84 | 23 | 1377 | 70 | kW | 2.03 | 51 | 47 | 75 | 41.8 | 2.81
86 | 23 | 1377 | 72 | MBh | 47.6 | 47 | 43 | 61 | 56.4 | 5.17
86 | 23 | 1377 | 72 | S/T | 0.7 | 47 | 43 | 65 | 52.2 | 4.53
86 | 23 | 1377 | 72 | ∆T | 22.4 | 47 | 43 | 68 | 49.1 | 4.07
86 | 23 | 1377 | 72 | LDB | 63.6 | 47 | 43 | 70 | 47 | 3.76
86 | 23 | 1377 | 72 | LWB | 62.2 | 47 | 43 | 72 | 44.9 | 3.46
86 | 23 | 1377 | 72 | kW | 2.18 | 47 | 43 | 75 | 41.8 | 3.02
90 | 23 | 1377 | 75 | MBh | 51.9 | 44 | 40 | 61 | 56.4 | 5.42
90 | 23 | 1377 | 75 | S/T | 0.657 | 44 | 40 | 65 | 52.2 | 4.76
90 | 23 | 1377 | 75 | ∆T | 22.9 | 44 | 40 | 68 | 49.1 | 4.28
90 | 23 | 1377 | 75 | LDB | 67.1 | 44 | 40 | 70 | 47 | 3.96
90 | 23 | 1377 | 75 | LWB | 65 | 44 | 40 | 72 | 44.9 | 3.65
90 | 23 | 1377 | 75 | kW | 2.41 | 44 | 40 | 75 | 41.8 | 3.19
68 | 30 | 1377 | 57 | MBh | 26.3 | 39 | 36 | 61 | 56.4 | 5.79
68 | 30 | 1377 | 57 | S/T | 0.852 | 39 | 36 | 65 | 52.2 | 5.09
68 | 30 | 1377 | 57 | ∆T | 15.1 | 39 | 36 | 68 | 49.1 | 4.58
68 | 30 | 1377 | 57 | LDB | 52.9 | 39 | 36 | 70 | 47 | 4.25
68 | 30 | 1377 | 57 | LWB | 49.8 | 39 | 36 | 72 | 44.9 | 3.92
68 | 30 | 1377 | 57 | kW | 1.17 | 39 | 36 | 75 | 41.8 | 3.44
72 | 30 | 1377 | 61 | MBh | 32 | 35 | 32 | 61 | 56.4 | 6.2
72 | 30 | 1377 | 61 | S/T | 0.816 | 35 | 32 | 65 | 52.2 | 5.46
72 | 30 | 1377 | 61 | ∆T | 17.6 | 35 | 32 | 68 | 49.1 | 4.92
72 | 30 | 1377 | 61 | LDB | 54.4 | 35 | 32 | 70 | 47 | 4.57
72 | 30 | 1377 | 61 | LWB | 52.8 | 35 | 32 | 72 | 44.9 | 4.22
72 | 30 | 1377 | 61 | kW | 1.44 | 35 | 32 | 75 | 41.8 | 3.71
77 | 30 | 1377 | 64 | MBh | 36.2 | 30 | 28 | 61 | 56.1 | 6.2
77 | 30 | 1377 | 64 | S/T | 0.79 | 30 | 28 | 65 | 52.2 | 5.87
77 | 30 | 1377 | 64 | ∆T | 19.2 | 30 | 28 | 68 | 49.1 | 5.29
77 | 30 | 1377 | 64 | LDB | 57.8 | 30 | 28 | 70 | 47 | 4.92
77 | 30 | 1377 | 64 | LWB | 55.2 | 30 | 28 | 72 | 44.9 | 4.55
77 | 30 | 1377 | 64 | kW | 1.65 | 30 | 28 | 75 | 41.8 | 4.01
80 | 30 | 1377 | 67 | MBh | 40.5 | 26 | 24 | 61 | 53.7 | 5.95
80 | 30 | 1377 | 67 | S/T | 0.753 | 26 | 24 | 65 | 52.2 | 6.32
80 | 30 | 1377 | 67 | ∆T | 20.5 | 26 | 24 | 68 | 49.1 | 5.71
80 | 30 | 1377 | 67 | LDB | 59.5 | 26 | 24 | 70 | 47 | 5.31
80 | 30 | 1377 | 67 | LWB | 57.8 | 26 | 24 | 72 | 44.9 | 4.92
80 | 30 | 1377 | 67 | kW | 1.87 | 26 | 24 | 75 | 41.8 | 4.34
84 | 30 | 1377 | 70 | MBh | 44.8 | 22 | 20 | 61 | 51.2 | 5.67
84 | 30 | 1377 | 70 | S/T | 0.725 | 22 | 20 | 65 | 51.2 | 6.1
84 | 30 | 1377 | 70 | ∆T | 21.9 | 22 | 20 | 68 | 49.1 | 6.17
84 | 30 | 1377 | 70 | LDB | 62.1 | 22 | 20 | 70 | 47 | 5.75
84 | 30 | 1377 | 70 | LWB | 60.4 | 22 | 20 | 72 | 44.9 | 5.33
84 | 30 | 1377 | 70 | kW | 2.1 | 22 | 20 | 75 | 41.8 | 4.71
86 | 30 | 1377 | 72 | MBh | 47.6 | 19 | 18 | 61 | 50 | 5.51
86 | 30 | 1377 | 72 | S/T | 0.7 | 19 | 18 | 65 | 50 | 5.96
86 | 30 | 1377 | 72 | ∆T | 22.4 | 19 | 18 | 68 | 49.1 | 6.29
86 | 30 | 1377 | 72 | LDB | 63.6 | 19 | 18 | 70 | 47 | 5.99
86 | 30 | 1377 | 72 | LWB | 62.2 | 19 | 18 | 72 | 44.9 | 5.55
86 | 30 | 1377 | 72 | kW | 2.25 | 19 | 18 | 75 | 41.8 | 4.92
90 | 30 | 1377 | 75 | MBh | 51.9 | 17 | 16 | 61 | 48.3 | 5.32
90 | 30 | 1377 | 75 | S/T | 0.657 | 17 | 16 | 65 | 48.3 | 5.78
90 | 30 | 1377 | 75 | ∆T | 22.9 | 17 | 16 | 68 | 48.3 | 6.12
90 | 30 | 1377 | 75 | LDB | 67.1 | 17 | 16 | 70 | 47 | 6.31
90 | 30 | 1377 | 75 | LWB | 65 | 17 | 16 | 72 | 44.9 | 5.85
90 | 30 | 1377 | 75 | kW | 2.49 | 17 | 16 | 75 | 41.8 | 5.19
68 | 40 | 1377 | 57 | MBh | 26.3 | 15 | 14 | 61 | 46.9 | 5.19
68 | 40 | 1377 | 57 | S/T | 0.852 | 15 | 14 | 65 | 46.9 | 5.66
68 | 40 | 1377 | 57 | ∆T | 15.1 | 15 | 14 | 68 | 46.9 | 6.01
68 | 40 | 1377 | 57 | LDB | 52.9 | 15 | 14 | 70 | 46.9 | 6.24
68 | 40 | 1377 | 57 | LWB | 49.8 | 15 | 14 | 72 | 44.9 | 6.04
68 | 40 | 1377 | 57 | kW | 1.22 | 15 | 14 | 75 | 41.8 | 5.36
72 | 40 | 1377 | 61 | MBh | 32 | 13 | 12 | 61 | 45 | 5.02
72 | 40 | 1377 | 61 | S/T | 0.816 | 13 | 12 | 65 | 45 | 5.5
72 | 40 | 1377 | 61 | ∆T | 17.6 | 13 | 12 | 68 | 45 | 5.86
72 | 40 | 1377 | 61 | LDB | 54.4 | 13 | 12 | 70 | 45 | 6.1
72 | 40 | 1377 | 61 | LWB | 52.8 | 13 | 12 | 72 | 44.9 | 6.31
72 | 40 | 1377 | 61 | kW | 1.5 | 13 | 12 | 75 | 41.8 | 5.61
77 | 40 | 1377 | 64 | MBh | 36.2 | 10 | 9 | 61 | 41.8 | 4.69
77 | 40 | 1377 | 64 | S/T | 0.79 | 10 | 9 | 65 | 41.8 | 5.19
77 | 40 | 1377 | 64 | ∆T | 19.2 | 10 | 9 | 68 | 41.8 | 5.57
77 | 40 | 1377 | 64 | LDB | 57.8 | 10 | 9 | 70 | 41.8 | 5.82
77 | 40 | 1377 | 64 | LWB | 55.2 | 10 | 9 | 72 | 41.8 | 6.07
77 | 40 | 1377 | 64 | kW | 1.73 | 10 | 9 | 75 | 41.8 | 6.07
80 | 40 | 1377 | 67 | MBh | 40.5 | 6 | 5 | 61 | 38.5 | 4.32
80 | 40 | 1377 | 67 | S/T | 0.753 | 6 | 5 | 65 | 38.5 | 4.85
80 | 40 | 1377 | 67 | ∆T | 20.5 | 6 | 5 | 68 | 38.5 | 5.25
80 | 40 | 1377 | 67 | LDB | 59.5 | 6 | 5 | 70 | 38.5 | 5.52
80 | 40 | 1377 | 67 | LWB | 57.8 | 6 | 5 | 72 | 38.5 | 5.78
80 | 40 | 1377 | 67 | kW | 1.96 | 6 | 5 | 75 | 38.5 | 6.18
84 | 40 | 1377 | 70 | MBh | 44.8 | -2 | -2 | 61 | 31.8 | 3.44
84 | 40 | 1377 | 70 | S/T | 0.725 | -2 | -2 | 65 | 31.8 | 4.03
84 | 40 | 1377 | 70 | ∆T | 21.9 | -2 | -2 | 68 | 31.8 | 4.48
84 | 40 | 1377 | 70 | LDB | 62.1 | -2 | -2 | 70 | 31.8 | 4.78
84 | 40 | 1377 | 70 | LWB | 60.4 | -2 | -2 | 72 | 31.8 | 5.08
84 | 40 | 1377 | 70 | kW | 2.2 | -2 | -2 | 75 | 31.8 | 5.52
86 | 40 | 1377 | 72 | MBh | 47.6 | -4 | -4 | 61 | 30.1 | 3.18
86 | 40 | 1377 | 72 | S/T | 0.7 | -4 | -4 | 65 | 30.1 | 3.8
86 | 40 | 1377 | 72 | ∆T | 22.4 | -4 | -4 | 68 | 30.1 | 4.26
86 | 40 | 1377 | 72 | LDB | 63.6 | -4 | -4 | 70 | 30.1 | 4.57
86 | 40 | 1377 | 72 | LWB | 62.2 | -4 | -4 | 72 | 30.1 | 4.87
86 | 40 | 1377 | 72 | kW | 2.37 | -4 | -4 | 75 | 30.1 | 5.33
90 | 40 | 1377 | 75 | MBh | 51.9
90 | 40 | 1377 | 75 | S/T | 0.657
90 | 40 | 1377 | 75 | ∆T | 22.9
90 | 40 | 1377 | 75 | LDB | 67.1
90 | 40 | 1377 | 75 | LWB | 65
90 | 40 | 1377 | 75 | kW | 2.61
68 | 50 | 1377 | 57 | MBh | 26.3
68 | 50 | 1377 | 57 | S/T | 0.852
68 | 50 | 1377 | 57 | ∆T | 15.1
68 | 50 | 1377 | 57 | LDB | 52.9
68 | 50 | 1377 | 57 | LWB | 49.8
68 | 50 | 1377 | 57 | kW | 1.27
72 | 50 | 1377 | 61 | MBh | 32
72 | 50 | 1377 | 61 | S/T | 0.816
72 | 50 | 1377 | 61 | ∆T | 17.6
72 | 50 | 1377 | 61 | LDB | 54.4
72 | 50 | 1377 | 61 | LWB | 52.8
72 | 50 | 1377 | 61 | kW | 1.58
77 | 50 | 1377 | 64 | MBh | 36.2
77 | 50 | 1377 | 64 | S/T | 0.79
77 | 50 | 1377 | 64 | ∆T | 19.2
77 | 50 | 1377 | 64 | LDB | 57.8
77 | 50 | 1377 | 64 | LWB | 55.2
77 | 50 | 1377 | 64 | kW | 1.82
80 | 50 | 1377 | 67 | MBh | 40.5
80 | 50 | 1377 | 67 | S/T | 0.753
80 | 50 | 1377 | 67 | ∆T | 20.5
80 | 50 | 1377 | 67 | LDB | 59.5
80 | 50 | 1377 | 67 | LWB | 57.8
80 | 50 | 1377 | 67 | kW | 2.06
84 | 50 | 1377 | 70 | MBh | 44.8
84 | 50 | 1377 | 70 | S/T | 0.725
84 | 50 | 1377 | 70 | ∆T | 21.9
84 | 50 | 1377 | 70 | LDB | 62.1
84 | 50 | 1377 | 70 | LWB | 60.4
84 | 50 | 1377 | 70 | kW | 2.32
86 | 50 | 1377 | 72 | MBh | 47.6
86 | 50 | 1377 | 72 | S/T | 0.7
86 | 50 | 1377 | 72 | ∆T | 22.4
86 | 50 | 1377 | 72 | LDB | 63.6
86 | 50 | 1377 | 72 | LWB | 62.2
86 | 50 | 1377 | 72 | kW | 2.49
90 | 50 | 1377 | 75 | MBh | 51.9
90 | 50 | 1377 | 75 | S/T | 0.657
90 | 50 | 1377 | 75 | ∆T | 22.9
90 | 50 | 1377 | 75 | LDB | 67.1
90 | 50 | 1377 | 75 | LWB | 65
90 | 50 | 1377 | 75 | kW | 2.75
68 | 54 | 1377 | 57 | MBh | 26.3
68 | 54 | 1377 | 57 | S/T | 0.852
68 | 54 | 1377 | 57 | ∆T | 15.1
68 | 54 | 1377 | 57 | LDB | 52.9
68 | 54 | 1377 | 57 | LWB | 49.8
68 | 54 | 1377 | 57 | kW | 1.3
72 | 54 | 1377 | 61 | MBh | 32
72 | 54 | 1377 | 61 | S/T | 0.816
72 | 54 | 1377 | 61 | ∆T | 17.6
72 | 54 | 1377 | 61 | LDB | 54.4
72 | 54 | 1377 | 61 | LWB | 52.8
72 | 54 | 1377 | 61 | kW | 1.61
77 | 54 | 1377 | 64 | MBh | 36.2
77 | 54 | 1377 | 64 | S/T | 0.79
77 | 54 | 1377 | 64 | ∆T | 19.2
77 | 54 | 1377 | 64 | LDB | 57.8
77 | 54 | 1377 | 64 | LWB | 55.2
77 | 54 | 1377 | 64 | kW | 1.85
80 | 54 | 1377 | 67 | MBh | 40.5
80 | 54 | 1377 | 67 | S/T | 0.753
80 | 54 | 1377 | 67 | ∆T | 20.5
80 | 54 | 1377 | 67 | LDB | 59.5
80 | 54 | 1377 | 67 | LWB | 57.8
80 | 54 | 1377 | 67 | kW | 2.11
84 | 54 | 1377 | 70 | MBh | 44.8
84 | 54 | 1377 | 70 | S/T | 0.725
84 | 54 | 1377 | 70 | ∆T | 21.9
84 | 54 | 1377 | 70 | LDB | 62.1
84 | 54 | 1377 | 70 | LWB | 60.4
84 | 54 | 1377 | 70 | kW | 2.37
86 | 54 | 1377 | 72 | MBh | 47.6
86 | 54 | 1377 | 72 | S/T | 0.7
86 | 54 | 1377 | 72 | ∆T | 22.4
86 | 54 | 1377 | 72 | LDB | 63.6
86 | 54 | 1377 | 72 | LWB | 62.2
86 | 54 | 1377 | 72 | kW | 2.54
90 | 54 | 1377 | 75 | MBh | 51.9
90 | 54 | 1377 | 75 | S/T | 0.657
90 | 54 | 1377 | 75 | ∆T | 22.9
90 | 54 | 1377 | 75 | LDB | 67.1
90 | 54 | 1377 | 75 | LWB | 65
90 | 54 | 1377 | 75 | kW | 2.8
68 | 58 | 1377 | 57 | MBh | 26.3
68 | 58 | 1377 | 57 | S/T | 0.852
68 | 58 | 1377 | 57 | ∆T | 15.1
68 | 58 | 1377 | 57 | LDB | 52.9
68 | 58 | 1377 | 57 | LWB | 49.8
68 | 58 | 1377 | 57 | kW | 1.32
72 | 58 | 1377 | 61 | MBh | 32
72 | 58 | 1377 | 61 | S/T | 0.816
72 | 58 | 1377 | 61 | ∆T | 17.6
72 | 58 | 1377 | 61 | LDB | 54.4
72 | 58 | 1377 | 61 | LWB | 52.8
72 | 58 | 1377 | 61 | kW | 1.64
77 | 58 | 1377 | 64 | MBh | 36.2
77 | 58 | 1377 | 64 | S/T | 0.79
77 | 58 | 1377 | 64 | ∆T | 19.2
77 | 58 | 1377 | 64 | LDB | 57.8
77 | 58 | 1377 | 64 | LWB | 55.2
77 | 58 | 1377 | 64 | kW | 1.89
80 | 58 | 1377 | 67 | MBh | 40.5
80 | 58 | 1377 | 67 | S/T | 0.753
80 | 58 | 1377 | 67 | ∆T | 20.5
80 | 58 | 1377 | 67 | LDB | 59.5
80 | 58 | 1377 | 67 | LWB | 57.8
80 | 58 | 1377 | 67 | kW | 2.15
84 | 58 | 1377 | 70 | MBh | 44.8
84 | 58 | 1377 | 70 | S/T | 0.725
84 | 58 | 1377 | 70 | ∆T | 21.9
84 | 58 | 1377 | 70 | LDB | 62.1
84 | 58 | 1377 | 70 | LWB | 60.4
84 | 58 | 1377 | 70 | kW | 2.42
86 | 58 | 1377 | 72 | MBh | 47.6
86 | 58 | 1377 | 72 | S/T | 0.7
86 | 58 | 1377 | 72 | ∆T | 22.4
86 | 58 | 1377 | 72 | LDB | 63.6
86 | 58 | 1377 | 72 | LWB | 62.2
86 | 58 | 1377 | 72 | kW | 2.59
90 | 58 | 1377 | 75 | MBh | 51.4
90 | 58 | 1377 | 75 | S/T | 0.656
90 | 58 | 1377 | 75 | ∆T | 22.7
90 | 58 | 1377 | 75 | LDB | 67.3
90 | 58 | 1377 | 75 | LWB | 65.1
90 | 58 | 1377 | 75 | kW | 2.82
68 | 62 | 1377 | 57 | MBh | 26.3
68 | 62 | 1377 | 57 | S/T | 0.852
68 | 62 | 1377 | 57 | ∆T | 15.1
68 | 62 | 1377 | 57 | LDB | 52.9
68 | 62 | 1377 | 57 | LWB | 49.8
68 | 62 | 1377 | 57 | kW | 1.35
72 | 62 | 1377 | 61 | MBh | 32
72 | 62 | 1377 | 61 | S/T | 0.816
72 | 62 | 1377 | 61 | ∆T | 17.6
72 | 62 | 1377 | 61 | LDB | 54.4
72 | 62 | 1377 | 61 | LWB | 52.8
72 | 62 | 1377 | 61 | kW | 1.68
77 | 62 | 1377 | 64 | MBh | 36.2
77 | 62 | 1377 | 64 | S/T | 0.79
77 | 62 | 1377 | 64 | ∆T | 19.2
77 | 62 | 1377 | 64 | LDB | 57.8
77 | 62 | 1377 | 64 | LWB | 55.2
77 | 62 | 1377 | 64 | kW | 1.93
80 | 62 | 1377 | 67 | MBh | 40.5
80 | 62 | 1377 | 67 | S/T | 0.753
80 | 62 | 1377 | 67 | ∆T | 20.5
80 | 62 | 1377 | 67 | LDB | 59.5
80 | 62 | 1377 | 67 | LWB | 57.8
80 | 62 | 1377 | 67 | kW | 2.2
84 | 62 | 1377 | 70 | MBh | 44.8
84 | 62 | 1377 | 70 | S/T | 0.725
84 | 62 | 1377 | 70 | ∆T | 21.9
84 | 62 | 1377 | 70 | LDB | 62.1
84 | 62 | 1377 | 70 | LWB | 60.4
84 | 62 | 1377 | 70 | kW | 2.47
86 | 62 | 1377 | 72 | MBh | 47.6
86 | 62 | 1377 | 72 | S/T | 0.7
86 | 62 | 1377 | 72 | ∆T | 22.4
86 | 62 | 1377 | 72 | LDB | 63.6
86 | 62 | 1377 | 72 | LWB | 62.2
86 | 62 | 1377 | 72 | kW | 2.65
90 | 62 | 1377 | 75 | MBh | 50.6
90 | 62 | 1377 | 75 | S/T | 0.656
90 | 62 | 1377 | 75 | ∆T | 22.3
90 | 62 | 1377 | 75 | LDB | 67.7
90 | 62 | 1377 | 75 | LWB | 65.3
90 | 62 | 1377 | 75 | kW | 2.87
68 | 66 | 1377 | 57 | MBh | 26.3
68 | 66 | 1377 | 57 | S/T | 0.852
68 | 66 | 1377 | 57 | ∆T | 15.1
68 | 66 | 1377 | 57 | LDB | 52.9
68 | 66 | 1377 | 57 | LWB | 49.8
68 | 66 | 1377 | 57 | kW | 1.38
72 | 66 | 1377 | 61 | MBh | 32
72 | 66 | 1377 | 61 | S/T | 0.816
72 | 66 | 1377 | 61 | ∆T | 17.6
72 | 66 | 1377 | 61 | LDB | 54.4
72 | 66 | 1377 | 61 | LWB | 52.8
72 | 66 | 1377 | 61 | kW | 1.71
77 | 66 | 1377 | 64 | MBh | 36.2
77 | 66 | 1377 | 64 | S/T | 0.79
77 | 66 | 1377 | 64 | ∆T | 19.2
77 | 66 | 1377 | 64 | LDB | 57.8
77 | 66 | 1377 | 64 | LWB | 55.2
77 | 66 | 1377 | 64 | kW | 1.98
80 | 66 | 1377 | 67 | MBh | 40.5
80 | 66 | 1377 | 67 | S/T | 0.753
80 | 66 | 1377 | 67 | ∆T | 20.5
80 | 66 | 1377 | 67 | LDB | 59.5
80 | 66 | 1377 | 67 | LWB | 57.8
80 | 66 | 1377 | 67 | kW | 2.25
84 | 66 | 1377 | 70 | MBh | 44.8
84 | 66 | 1377 | 70 | S/T | 0.725
84 | 66 | 1377 | 70 | ∆T | 21.9
84 | 66 | 1377 | 70 | LDB | 62.1
84 | 66 | 1377 | 70 | LWB | 60.4
84 | 66 | 1377 | 70 | kW | 2.61
86 | 66 | 1377 | 72 | MBh | 47.6
86 | 66 | 1377 | 72 | S/T | 0.7
86 | 66 | 1377 | 72 | ∆T | 22.4
86 | 66 | 1377 | 72 | LDB | 63.6
86 | 66 | 1377 | 72 | LWB | 62.2
86 | 66 | 1377 | 72 | kW | 2.86
90 | 66 | 1377 | 75 | MBh | 49.9
90 | 66 | 1377 | 75 | S/T | 0.655
90 | 66 | 1377 | 75 | ∆T | 22
90 | 66 | 1377 | 75 | LDB | 68
90 | 66 | 1377 | 75 | LWB | 65.4
90 | 66 | 1377 | 75 | kW | 3.03
68 | 70 | 1377 | 57 | MBh | 26.3
68 | 70 | 1377 | 57 | S/T | 0.852
68 | 70 | 1377 | 57 | ∆T | 15.1
68 | 70 | 1377 | 57 | LDB | 52.9
68 | 70 | 1377 | 57 | LWB | 49.8
68 | 70 | 1377 | 57 | kW | 1.41
72 | 70 | 1377 | 61 | MBh | 32
72 | 70 | 1377 | 61 | S/T | 0.816
72 | 70 | 1377 | 61 | ∆T | 17.6
72 | 70 | 1377 | 61 | LDB | 54.4
72 | 70 | 1377 | 61 | LWB | 52.8
72 | 70 | 1377 | 61 | kW | 1.75
77 | 70 | 1377 | 64 | MBh | 36.2
77 | 70 | 1377 | 64 | S/T | 0.79
77 | 70 | 1377 | 64 | ∆T | 19.2
77 | 70 | 1377 | 64 | LDB | 57.8
77 | 70 | 1377 | 64 | LWB | 55.2
77 | 70 | 1377 | 64 | kW | 2.07
80 | 70 | 1377 | 67 | MBh | 40.5
80 | 70 | 1377 | 67 | S/T | 0.753
80 | 70 | 1377 | 67 | ∆T | 20.5
80 | 70 | 1377 | 67 | LDB | 59.5
80 | 70 | 1377 | 67 | LWB | 57.8
80 | 70 | 1377 | 67 | kW | 2.43
84 | 70 | 1377 | 70 | MBh | 44.8
84 | 70 | 1377 | 70 | S/T | 0.725
84 | 70 | 1377 | 70 | ∆T | 21.9
84 | 70 | 1377 | 70 | LDB | 62.1
84 | 70 | 1377 | 70 | LWB | 60.4
84 | 70 | 1377 | 70 | kW | 2.82
86 | 70 | 1377 | 72 | MBh | 47.6
86 | 70 | 1377 | 72 | S/T | 0.7
86 | 70 | 1377 | 72 | ∆T | 22.4
86 | 70 | 1377 | 72 | LDB | 63.6
86 | 70 | 1377 | 72 | LWB | 62.2
86 | 70 | 1377 | 72 | kW | 3.1
90 | 70 | 1377 | 75 | MBh | 49.1
90 | 70 | 1377 | 75 | S/T | 0.656
90 | 70 | 1377 | 75 | ∆T | 21.7
90 | 70 | 1377 | 75 | LDB | 68.3
90 | 70 | 1377 | 75 | LWB | 65.6
90 | 70 | 1377 | 75 | kW | 3.2
68 | 72 | 1377 | 57 | MBh | 26.3
68 | 72 | 1377 | 57 | S/T | 0.852
68 | 72 | 1377 | 57 | ∆T | 15.1
68 | 72 | 1377 | 57 | LDB | 52.9
68 | 72 | 1377 | 57 | LWB | 49.8
68 | 72 | 1377 | 57 | kW | 1.42
72 | 72 | 1377 | 61 | MBh | 32
72 | 72 | 1377 | 61 | S/T | 0.816
72 | 72 | 1377 | 61 | ∆T | 17.6
72 | 72 | 1377 | 61 | LDB | 54.4
72 | 72 | 1377 | 61 | LWB | 52.8
72 | 72 | 1377 | 61 | kW | 1.81
77 | 72 | 1377 | 64 | MBh | 36.2
77 | 72 | 1377 | 64 | S/T | 0.79
77 | 72 | 1377 | 64 | ∆T | 19.2
77 | 72 | 1377 | 64 | LDB | 57.8
77 | 72 | 1377 | 64 | LWB | 55.2
77 | 72 | 1377 | 64 | kW | 2.15
80 | 72 | 1377 | 67 | MBh | 40.5
80 | 72 | 1377 | 67 | S/T | 0.753
80 | 72 | 1377 | 67 | ∆T | 20.5
80 | 72 | 1377 | 67 | LDB | 59.5
80 | 72 | 1377 | 67 | LWB | 57.8
80 | 72 | 1377 | 67 | kW | 2.53
84 | 72 | 1377 | 70 | MBh | 44.8
84 | 72 | 1377 | 70 | S/T | 0.725
84 | 72 | 1377 | 70 | ∆T | 21.9
84 | 72 | 1377 | 70 | LDB | 62.1
84 | 72 | 1377 | 70 | LWB | 60.4
84 | 72 | 1377 | 70 | kW | 2.93
86 | 72 | 1377 | 72 | MBh | 47.6
86 | 72 | 1377 | 72 | S/T | 0.7
86 | 72 | 1377 | 72 | ∆T | 22.4
86 | 72 | 1377 | 72 | LDB | 63.6
86 | 72 | 1377 | 72 | LWB | 62.2
86 | 72 | 1377 | 72 | kW | 3.22
90 | 72 | 1377 | 75 | MBh | 48.7
90 | 72 | 1377 | 75 | S/T | 0.657
90 | 72 | 1377 | 75 | ∆T | 21.5
90 | 72 | 1377 | 75 | LDB | 68.5
90 | 72 | 1377 | 75 | LWB | 65.7
90 | 72 | 1377 | 75 | kW | 3.28
68 | 75 | 1377 | 57 | MBh | 26.3
68 | 75 | 1377 | 57 | S/T | 0.852
68 | 75 | 1377 | 57 | ∆T | 15.1
68 | 75 | 1377 | 57 | LDB | 52.9
68 | 75 | 1377 | 57 | LWB | 49.8
68 | 75 | 1377 | 57 | kW | 1.48
72 | 75 | 1377 | 61 | MBh | 32
72 | 75 | 1377 | 61 | S/T | 0.816
72 | 75 | 1377 | 61 | ∆T | 17.6
72 | 75 | 1377 | 61 | LDB | 54.4
72 | 75 | 1377 | 61 | LWB | 52.8
72 | 75 | 1377 | 61 | kW | 1.91
77 | 75 | 1377 | 64 | MBh | 36.2
77 | 75 | 1377 | 64 | S/T | 0.79
77 | 75 | 1377 | 64 | ∆T | 19.2
77 | 75 | 1377 | 64 | LDB | 57.8
77 | 75 | 1377 | 64 | LWB | 55.2
77 | 75 | 1377 | 64 | kW | 2.28
80 | 75 | 1377 | 67 | MBh | 40.5
80 | 75 | 1377 | 67 | S/T | 0.753
80 | 75 | 1377 | 67 | ∆T | 20.5
80 | 75 | 1377 | 67 | LDB | 59.5
80 | 75 | 1377 | 67 | LWB | 57.8
80 | 75 | 1377 | 67 | kW | 2.68
84 | 75 | 1377 | 70 | MBh | 44.8
84 | 75 | 1377 | 70 | S/T | 0.725
84 | 75 | 1377 | 70 | ∆T | 21.9
84 | 75 | 1377 | 70 | LDB | 62.1
84 | 75 | 1377 | 70 | LWB | 60.4
84 | 75 | 1377 | 70 | kW | 3.11
86 | 75 | 1377 | 72 | MBh | 47.3
86 | 75 | 1377 | 72 | S/T | 0.7
86 | 75 | 1377 | 72 | ∆T | 22.3
86 | 75 | 1377 | 72 | LDB | 63.7
86 | 75 | 1377 | 72 | LWB | 62.3
86 | 75 | 1377 | 72 | kW | 3.38
90 | 75 | 1377 | 75 | MBh | 48.2
90 | 75 | 1377 | 75 | S/T | 0.656
90 | 75 | 1377 | 75 | ∆T | 21.2
90 | 75 | 1377 | 75 | LDB | 68.8
90 | 75 | 1377 | 75 | LWB | 65.8
90 | 75 | 1377 | 75 | kW | 3.4
68 | 79 | 1377 | 57 | MBh | 26.3
68 | 79 | 1377 | 57 | S/T | 0.852
68 | 79 | 1377 | 57 | ∆T | 15.1
68 | 79 | 1377 | 57 | LDB | 52.9
68 | 79 | 1377 | 57 | LWB | 49.8
68 | 79 | 1377 | 57 | kW | 1.58
72 | 79 | 1377 | 61 | MBh | 32
72 | 79 | 1377 | 61 | S/T | 0.816
72 | 79 | 1377 | 61 | ∆T | 17.6
72 | 79 | 1377 | 61 | LDB | 54.4
72 | 79 | 1377 | 61 | LWB | 52.8
72 | 79 | 1377 | 61 | kW | 2.06
77 | 79 | 1377 | 64 | MBh | 36.2
77 | 79 | 1377 | 64 | S/T | 0.79
77 | 79 | 1377 | 64 | ∆T | 19.2
77 | 79 | 1377 | 64 | LDB | 57.8
77 | 79 | 1377 | 64 | LWB | 55.2
77 | 79 | 1377 | 64 | kW | 2.45
80 | 79 | 1377 | 67 | MBh | 40.5
80 | 79 | 1377 | 67 | S/T | 0.753
80 | 79 | 1377 | 67 | ∆T | 20.5
80 | 79 | 1377 | 67 | LDB | 59.5
80 | 79 | 1377 | 67 | LWB | 57.8
80 | 79 | 1377 | 67 | kW | 2.89
84 | 79 | 1377 | 70 | MBh | 44.8
84 | 79 | 1377 | 70 | S/T | 0.725
84 | 79 | 1377 | 70 | ∆T | 21.9
84 | 79 | 1377 | 70 | LDB | 62.1
84 | 79 | 1377 | 70 | LWB | 60.4
84 | 79 | 1377 | 70 | kW | 3.35
86 | 79 | 1377 | 72 | MBh | 46.6
86 | 79 | 1377 | 72 | S/T | 0.697
86 | 79 | 1377 | 72 | ∆T | 21.9
86 | 79 | 1377 | 72 | LDB | 64.1
86 | 79 | 1377 | 72 | LWB | 62.4
86 | 79 | 1377 | 72 | kW | 3.54
90 | 79 | 1377 | 75 | MBh | 47.4
90 | 79 | 1377 | 75 | S/T | 0.656
90 | 79 | 1377 | 75 | ∆T | 20.9
90 | 79 | 1377 | 75 | LDB | 69.1
90 | 79 | 1377 | 75 | LWB | 66
90 | 79 | 1377 | 75 | kW | 3.56
68 | 83 | 1377 | 57 | MBh | 26.3
68 | 83 | 1377 | 57 | S/T | 0.852
68 | 83 | 1377 | 57 | ∆T | 15.1
68 | 83 | 1377 | 57 | LDB | 52.9
68 | 83 | 1377 | 57 | LWB | 49.8
68 | 83 | 1377 | 57 | kW | 1.7
72 | 83 | 1377 | 61 | MBh | 32
72 | 83 | 1377 | 61 | S/T | 0.816
72 | 83 | 1377 | 61 | ∆T | 17.6
72 | 83 | 1377 | 61 | LDB | 54.4
72 | 83 | 1377 | 61 | LWB | 52.8
72 | 83 | 1377 | 61 | kW | 2.21
77 | 83 | 1377 | 64 | MBh | 36.2
77 | 83 | 1377 | 64 | S/T | 0.79
77 | 83 | 1377 | 64 | ∆T | 19.2
77 | 83 | 1377 | 64 | LDB | 57.8
77 | 83 | 1377 | 64 | LWB | 55.2
77 | 83 | 1377 | 64 | kW | 2.64
80 | 83 | 1377 | 67 | MBh | 40.5
80 | 83 | 1377 | 67 | S/T | 0.753
80 | 83 | 1377 | 67 | ∆T | 20.5
80 | 83 | 1377 | 67 | LDB | 59.5
80 | 83 | 1377 | 67 | LWB | 57.8
80 | 83 | 1377 | 67 | kW | 3.11
84 | 83 | 1377 | 70 | MBh | 44.8
84 | 83 | 1377 | 70 | S/T | 0.725
84 | 83 | 1377 | 70 | ∆T | 21.9
84 | 83 | 1377 | 70 | LDB | 62.1
84 | 83 | 1377 | 70 | LWB | 60.4
84 | 83 | 1377 | 70 | kW | 3.61
86 | 83 | 1377 | 72 | MBh | 45.8
86 | 83 | 1377 | 72 | S/T | 0.699
86 | 83 | 1377 | 72 | ∆T | 21.5
86 | 83 | 1377 | 72 | LDB | 64.5
86 | 83 | 1377 | 72 | LWB | 62.6
86 | 83 | 1377 | 72 | kW | 3.7
90 | 83 | 1377 | 75 | MBh | 46.6
90 | 83 | 1377 | 75 | S/T | 0.657
90 | 83 | 1377 | 75 | ∆T | 20.6
90 | 83 | 1377 | 75 | LDB | 69.4
90 | 83 | 1377 | 75 | LWB | 66.1
90 | 83 | 1377 | 75 | kW | 3.72
68 | 87 | 1377 | 57 | MBh | 26.3
68 | 87 | 1377 | 57 | S/T | 0.852
68 | 87 | 1377 | 57 | ∆T | 15.1
68 | 87 | 1377 | 57 | LDB | 52.9
68 | 87 | 1377 | 57 | LWB | 49.8
68 | 87 | 1377 | 57 | kW | 1.82
72 | 87 | 1377 | 61 | MBh | 32
72 | 87 | 1377 | 61 | S/T | 0.816
72 | 87 | 1377 | 61 | ∆T | 17.6
72 | 87 | 1377 | 61 | LDB | 54.4
72 | 87 | 1377 | 61 | LWB | 52.8
72 | 87 | 1377 | 61 | kW | 2.37
77 | 87 | 1377 | 64 | MBh | 36.2
77 | 87 | 1377 | 64 | S/T | 0.79
77 | 87 | 1377 | 64 | ∆T | 19.2
77 | 87 | 1377 | 64 | LDB | 57.8
77 | 87 | 1377 | 64 | LWB | 55.2
77 | 87 | 1377 | 64 | kW | 2.84
80 | 87 | 1377 | 67 | MBh | 40.5
80 | 87 | 1377 | 67 | S/T | 0.753
80 | 87 | 1377 | 67 | ∆T | 20.5
80 | 87 | 1377 | 67 | LDB | 59.5
80 | 87 | 1377 | 67 | LWB | 57.8
80 | 87 | 1377 | 67 | kW | 3.34
84 | 87 | 1377 | 70 | MBh | 44.5
84 | 87 | 1377 | 70 | S/T | 0.726
84 | 87 | 1377 | 70 | ∆T | 21.7
84 | 87 | 1377 | 70 | LDB | 62.3
84 | 87 | 1377 | 70 | LWB | 60.5
84 | 87 | 1377 | 70 | kW | 3.85
86 | 87 | 1377 | 72 | MBh | 45
86 | 87 | 1377 | 72 | S/T | 0.7
86 | 87 | 1377 | 72 | ∆T | 21.2
86 | 87 | 1377 | 72 | LDB | 64.8
86 | 87 | 1377 | 72 | LWB | 62.8
86 | 87 | 1377 | 72 | kW | 3.86
90 | 87 | 1377 | 75 | MBh | 45.9
90 | 87 | 1377 | 75 | S/T | 0.656
90 | 87 | 1377 | 75 | ∆T | 20.2
90 | 87 | 1377 | 75 | LDB | 69.8
90 | 87 | 1377 | 75 | LWB | 66.3
90 | 87 | 1377 | 75 | kW | 3.89
68 | 91 | 1377 | 57 | MBh | 26.3
68 | 91 | 1377 | 57 | S/T | 0.852
68 | 91 | 1377 | 57 | ∆T | 15.1
68 | 91 | 1377 | 57 | LDB | 52.9
68 | 91 | 1377 | 57 | LWB | 49.8
68 | 91 | 1377 | 57 | kW | 1.95
72 | 91 | 1377 | 61 | MBh | 32
72 | 91 | 1377 | 61 | S/T | 0.816
72 | 91 | 1377 | 61 | ∆T | 17.6
72 | 91 | 1377 | 61 | LDB | 54.4
72 | 91 | 1377 | 61 | LWB | 52.8
72 | 91 | 1377 | 61 | kW | 2.54
77 | 91 | 1377 | 64 | MBh | 36.2
77 | 91 | 1377 | 64 | S/T | 0.79
77 | 91 | 1377 | 64 | ∆T | 19.2
77 | 91 | 1377 | 64 | LDB | 57.8
77 | 91 | 1377 | 64 | LWB | 55.2
77 | 91 | 1377 | 64 | kW | 3.04
80 | 91 | 1377 | 67 | MBh | 40.5
80 | 91 | 1377 | 67 | S/T | 0.753
80 | 91 | 1377 | 67 | ∆T | 20.5
80 | 91 | 1377 | 67 | LDB | 59.5
80 | 91 | 1377 | 67 | LWB | 57.8
80 | 91 | 1377 | 67 | kW | 3.59
84 | 91 | 1377 | 70 | MBh | 43.7
84 | 91 | 1377 | 70 | S/T | 0.725
84 | 91 | 1377 | 70 | ∆T | 21.3
84 | 91 | 1377 | 70 | LDB | 62.7
84 | 91 | 1377 | 70 | LWB | 60.6
84 | 91 | 1377 | 70 | kW | 4.01
86 | 91 | 1377 | 72 | MBh | 44.3
86 | 91 | 1377 | 72 | S/T | 0.7
86 | 91 | 1377 | 72 | ∆T | 20.8
86 | 91 | 1377 | 72 | LDB | 65.2
86 | 91 | 1377 | 72 | LWB | 63
86 | 91 | 1377 | 72 | kW | 4.03
90 | 91 | 1377 | 75 | MBh | 45.1
90 | 91 | 1377 | 75 | S/T | 0.656
90 | 91 | 1377 | 75 | ∆T | 19.9
90 | 91 | 1377 | 75 | LDB | 70.1
90 | 91 | 1377 | 75 | LWB | 66.4
90 | 91 | 1377 | 75 | kW | 4.05
68 | 93 | 1377 | 57 | MBh | 26.3
68 | 93 | 1377 | 57 | S/T | 0.852
68 | 93 | 1377 | 57 | ∆T | 15.1
68 | 93 | 1377 | 57 | LDB | 52.9
68 | 93 | 1377 | 57 | LWB | 49.8
68 | 93 | 1377 | 57 | kW | 2.01
72 | 93 | 1377 | 61 | MBh | 32
72 | 93 | 1377 | 61 | S/T | 0.816
72 | 93 | 1377 | 61 | ∆T | 17.6
72 | 93 | 1377 | 61 | LDB | 54.4
72 | 93 | 1377 | 61 | LWB | 52.8
72 | 93 | 1377 | 61 | kW | 2.63
77 | 93 | 1377 | 64 | MBh | 36.2
77 | 93 | 1377 | 64 | S/T | 0.79
77 | 93 | 1377 | 64 | ∆T | 19.2
77 | 93 | 1377 | 64 | LDB | 57.8
77 | 93 | 1377 | 64 | LWB | 55.2
77 | 93 | 1377 | 64 | kW | 3.15
80 | 93 | 1377 | 67 | MBh | 40.5
80 | 93 | 1377 | 67 | S/T | 0.753
80 | 93 | 1377 | 67 | ∆T | 20.5
80 | 93 | 1377 | 67 | LDB | 59.5
80 | 93 | 1377 | 67 | LWB | 57.8
80 | 93 | 1377 | 67 | kW | 3.72
84 | 93 | 1377 | 70 | MBh | 43.3
84 | 93 | 1377 | 70 | S/T | 0.725
84 | 93 | 1377 | 70 | ∆T | 21.1
84 | 93 | 1377 | 70 | LDB | 62.9
84 | 93 | 1377 | 70 | LWB | 60.7
84 | 93 | 1377 | 70 | kW | 4.09
86 | 93 | 1377 | 72 | MBh | 43.9
86 | 93 | 1377 | 72 | S/T | 0.699
86 | 93 | 1377 | 72 | ∆T | 20.6
86 | 93 | 1377 | 72 | LDB | 65.4
86 | 93 | 1377 | 72 | LWB | 63.1
86 | 93 | 1377 | 72 | kW | 4.11
90 | 93 | 1377 | 75 | MBh | 44.7
90 | 93 | 1377 | 75 | S/T | 0.658
90 | 93 | 1377 | 75 | ∆T | 19.8
90 | 93 | 1377 | 75 | LDB | 70.2
90 | 93 | 1377 | 75 | LWB | 66.5
90 | 93 | 1377 | 75 | kW | 4.14
68 | 95 | 1377 | 57 | MBh | 26.3
68 | 95 | 1377 | 57 | S/T | 0.852
68 | 95 | 1377 | 57 | ∆T | 15.1
68 | 95 | 1377 | 57 | LDB | 52.9
68 | 95 | 1377 | 57 | LWB | 49.8
68 | 95 | 1377 | 57 | kW | 2.08
72 | 95 | 1377 | 61 | MBh | 32
72 | 95 | 1377 | 61 | S/T | 0.816
72 | 95 | 1377 | 61 | ∆T | 17.6
72 | 95 | 1377 | 61 | LDB | 54.4
72 | 95 | 1377 | 61 | LWB | 52.8
72 | 95 | 1377 | 61 | kW | 2.73
77 | 95 | 1377 | 64 | MBh | 36.2
77 | 95 | 1377 | 64 | S/T | 0.79
77 | 95 | 1377 | 64 | ∆T | 19.2
77 | 95 | 1377 | 64 | LDB | 57.8
77 | 95 | 1377 | 64 | LWB | 55.2
77 | 95 | 1377 | 64 | kW | 3.27
80 | 95 | 1377 | 67 | MBh | 40.5
80 | 95 | 1377 | 67 | S/T | 0.753
80 | 95 | 1377 | 67 | ∆T | 20.5
80 | 95 | 1377 | 67 | LDB | 59.5
80 | 95 | 1377 | 67 | LWB | 57.8
80 | 95 | 1377 | 67 | kW | 3.86
84 | 95 | 1377 | 70 | MBh | 43
84 | 95 | 1377 | 70 | S/T | 0.726
84 | 95 | 1377 | 70 | ∆T | 21
84 | 95 | 1377 | 70 | LDB | 63
84 | 95 | 1377 | 70 | LWB | 60.8
84 | 95 | 1377 | 70 | kW | 4.17
86 | 95 | 1377 | 72 | MBh | 43.5
86 | 95 | 1377 | 72 | S/T | 0.699
86 | 95 | 1377 | 72 | ∆T | 20.4
86 | 95 | 1377 | 72 | LDB | 65.6
86 | 95 | 1377 | 72 | LWB | 63.1
86 | 95 | 1377 | 72 | kW | 4.19
90 | 95 | 1377 | 75 | MBh | 44.4
90 | 95 | 1377 | 75 | S/T | 0.655
90 | 95 | 1377 | 75 | ∆T | 19.6
90 | 95 | 1377 | 75 | LDB | 70.4
90 | 95 | 1377 | 75 | LWB | 66.6
90 | 95 | 1377 | 75 | kW | 4.22
68 | 99 | 1377 | 57 | MBh | 26.3
68 | 99 | 1377 | 57 | S/T | 0.852
68 | 99 | 1377 | 57 | ∆T | 15.1
68 | 99 | 1377 | 57 | LDB | 52.9
68 | 99 | 1377 | 57 | LWB | 49.8
68 | 99 | 1377 | 57 | kW | 2.23
72 | 99 | 1377 | 61 | MBh | 32
72 | 99 | 1377 | 61 | S/T | 0.816
72 | 99 | 1377 | 61 | ∆T | 17.6
72 | 99 | 1377 | 61 | LDB | 54.4
72 | 99 | 1377 | 61 | LWB | 52.8
72 | 99 | 1377 | 61 | kW | 2.92
77 | 99 | 1377 | 64 | MBh | 36.2
77 | 99 | 1377 | 64 | S/T | 0.79
77 | 99 | 1377 | 64 | ∆T | 19.2
77 | 99 | 1377 | 64 | LDB | 57.8
77 | 99 | 1377 | 64 | LWB | 55.2
77 | 99 | 1377 | 64 | kW | 3.5
80 | 99 | 1377 | 67 | MBh | 40.5
80 | 99 | 1377 | 67 | S/T | 0.753
80 | 99 | 1377 | 67 | ∆T | 20.5
80 | 99 | 1377 | 67 | LDB | 59.5
80 | 99 | 1377 | 67 | LWB | 57.8
80 | 99 | 1377 | 67 | kW | 4.14
84 | 99 | 1377 | 70 | MBh | 42.2
84 | 99 | 1377 | 70 | S/T | 0.725
84 | 99 | 1377 | 70 | ∆T | 20.6
84 | 99 | 1377 | 70 | LDB | 63.4
84 | 99 | 1377 | 70 | LWB | 61
84 | 99 | 1377 | 70 | kW | 4.33
86 | 99 | 1377 | 72 | MBh | 42.8
86 | 99 | 1377 | 72 | S/T | 0.699
86 | 99 | 1377 | 72 | ∆T | 20.1
86 | 99 | 1377 | 72 | LDB | 65.9
86 | 99 | 1377 | 72 | LWB | 63.3
86 | 99 | 1377 | 72 | kW | 4.35
90 | 99 | 1377 | 75 | MBh | 43.1
90 | 99 | 1377 | 75 | S/T | 0.657
90 | 99 | 1377 | 75 | ∆T | 19
90 | 99 | 1377 | 75 | LDB | 71
90 | 99 | 1377 | 75 | LWB | 66.9
90 | 99 | 1377 | 75 | kW | 4.37
68 | 103 | 1377 | 57 | MBh | 26.3
68 | 103 | 1377 | 57 | S/T | 0.852
68 | 103 | 1377 | 57 | ∆T | 15.1
68 | 103 | 1377 | 57 | LDB | 52.9
68 | 103 | 1377 | 57 | LWB | 49.8
68 | 103 | 1377 | 57 | kW | 2.38
72 | 103 | 1377 | 61 | MBh | 32
72 | 103 | 1377 | 61 | S/T | 0.816
72 | 103 | 1377 | 61 | ∆T | 17.6
72 | 103 | 1377 | 61 | LDB | 54.4
72 | 103 | 1377 | 61 | LWB | 52.8
72 | 103 | 1377 | 61 | kW | 3.13
77 | 103 | 1377 | 64 | MBh | 36.2
77 | 103 | 1377 | 64 | S/T | 0.79
77 | 103 | 1377 | 64 | ∆T | 19.2
77 | 103 | 1377 | 64 | LDB | 57.8
77 | 103 | 1377 | 64 | LWB | 55.2
77 | 103 | 1377 | 64 | kW | 3.76
80 | 103 | 1377 | 67 | MBh | 40.5
80 | 103 | 1377 | 67 | S/T | 0.753
80 | 103 | 1377 | 67 | ∆T | 20.5
80 | 103 | 1377 | 67 | LDB | 59.5
80 | 103 | 1377 | 67 | LWB | 57.8
80 | 103 | 1377 | 67 | kW | 4.44
84 | 103 | 1377 | 70 | MBh | 41.4
84 | 103 | 1377 | 70 | S/T | 0.727
84 | 103 | 1377 | 70 | ∆T | 20.2
84 | 103 | 1377 | 70 | LDB | 63.8
84 | 103 | 1377 | 70 | LWB | 61.2
84 | 103 | 1377 | 70 | kW | 4.5
86 | 103 | 1377 | 72 | MBh | 41.4
86 | 103 | 1377 | 72 | S/T | 0.7
86 | 103 | 1377 | 72 | ∆T | 19.5
86 | 103 | 1377 | 72 | LDB | 66.5
86 | 103 | 1377 | 72 | LWB | 63.6
86 | 103 | 1377 | 72 | kW | 4.5
90 | 103 | 1377 | 75 | MBh | 41.4
90 | 103 | 1377 | 75 | S/T | 0.657
90 | 103 | 1377 | 75 | ∆T | 18.3
90 | 103 | 1377 | 75 | LDB | 71.7
90 | 103 | 1377 | 75 | LWB | 67.2
90 | 103 | 1377 | 75 | kW | 4.5
68 | 106 | 1377 | 57 | MBh | 26.3
68 | 106 | 1377 | 57 | S/T | 0.852
68 | 106 | 1377 | 57 | ∆T | 15.1
68 | 106 | 1377 | 57 | LDB | 52.9
68 | 106 | 1377 | 57 | LWB | 49.8
68 | 106 | 1377 | 57 | kW | 2.5
72 | 106 | 1377 | 61 | MBh | 32
72 | 106 | 1377 | 61 | S/T | 0.816
72 | 106 | 1377 | 61 | ∆T | 17.6
72 | 106 | 1377 | 61 | LDB | 54.4
72 | 106 | 1377 | 61 | LWB | 52.8
72 | 106 | 1377 | 61 | kW | 3.29
77 | 106 | 1377 | 64 | MBh | 36.2
77 | 106 | 1377 | 64 | S/T | 0.79
77 | 106 | 1377 | 64 | ∆T | 19.2
77 | 106 | 1377 | 64 | LDB | 57.8
77 | 106 | 1377 | 64 | LWB | 55.2
77 | 106 | 1377 | 64 | kW | 3.96
80 | 106 | 1377 | 67 | MBh | 40
80 | 106 | 1377 | 67 | S/T | 0.753
80 | 106 | 1377 | 67 | ∆T | 20.2
80 | 106 | 1377 | 67 | LDB | 59.8
80 | 106 | 1377 | 67 | LWB | 57.9
80 | 106 | 1377 | 67 | kW | 4.59
84 | 106 | 1377 | 70 | MBh | 40.2
84 | 106 | 1377 | 70 | S/T | 0.724
84 | 106 | 1377 | 70 | ∆T | 19.6
84 | 106 | 1377 | 70 | LDB | 64.4
84 | 106 | 1377 | 70 | LWB | 61.5
84 | 106 | 1377 | 70 | kW | 4.59
86 | 106 | 1377 | 72 | MBh | 40.2
86 | 106 | 1377 | 72 | S/T | 0.699
86 | 106 | 1377 | 72 | ∆T | 18.9
86 | 106 | 1377 | 72 | LDB | 67.1
86 | 106 | 1377 | 72 | LWB | 63.9
86 | 106 | 1377 | 72 | kW | 4.59
90 | 106 | 1377 | 75 | MBh | 40.2
90 | 106 | 1377 | 75 | S/T | 0.657
90 | 106 | 1377 | 75 | ∆T | 17.8
90 | 106 | 1377 | 75 | LDB | 72.2
90 | 106 | 1377 | 75 | LWB | 67.5
90 | 106 | 1377 | 75 | kW | 4.59
68 | 110 | 1377 | 57 | MBh | 26.3
68 | 110 | 1377 | 57 | S/T | 0.852
68 | 110 | 1377 | 57 | ∆T | 15.1
68 | 110 | 1377 | 57 | LDB | 52.9
68 | 110 | 1377 | 57 | LWB | 49.8
68 | 110 | 1377 | 57 | kW | 2.67
72 | 110 | 1377 | 61 | MBh | 32
72 | 110 | 1377 | 61 | S/T | 0.816
72 | 110 | 1377 | 61 | ∆T | 17.6
72 | 110 | 1377 | 61 | LDB | 54.4
72 | 110 | 1377 | 61 | LWB | 52.8
72 | 110 | 1377 | 61 | kW | 3.52
77 | 110 | 1377 | 64 | MBh | 36.2
77 | 110 | 1377 | 64 | S/T | 0.79
77 | 110 | 1377 | 64 | ∆T | 19.2
77 | 110 | 1377 | 64 | LDB | 57.8
77 | 110 | 1377 | 64 | LWB | 55.2
77 | 110 | 1377 | 64 | kW | 4.24
80 | 110 | 1377 | 67 | MBh | 36.4
80 | 110 | 1377 | 67 | S/T | 0.753
80 | 110 | 1377 | 67 | ∆T | 18.4
80 | 110 | 1377 | 67 | LDB | 61.6
80 | 110 | 1377 | 67 | LWB | 58.8
80 | 110 | 1377 | 67 | kW | 4.26
84 | 110 | 1377 | 70 | MBh | 36.4
84 | 110 | 1377 | 70 | S/T | 0.725
84 | 110 | 1377 | 70 | ∆T | 17.8
84 | 110 | 1377 | 70 | LDB | 66.2
84 | 110 | 1377 | 70 | LWB | 62.3
84 | 110 | 1377 | 70 | kW | 4.26
86 | 110 | 1377 | 72 | MBh | 36.4
86 | 110 | 1377 | 72 | S/T | 0.698
86 | 110 | 1377 | 72 | ∆T | 17.1
86 | 110 | 1377 | 72 | LDB | 68.9
86 | 110 | 1377 | 72 | LWB | 64.7
86 | 110 | 1377 | 72 | kW | 4.26
90 | 110 | 1377 | 75 | MBh | 36.4
90 | 110 | 1377 | 75 | S/T | 0.657
90 | 110 | 1377 | 75 | ∆T | 16.1
90 | 110 | 1377 | 75 | LDB | 73.9
90 | 110 | 1377 | 75 | LWB | 68.2
90 | 110 | 1377 | 75 | kW | 4.26
68 | 115 | 1377 | 57 | MBh | 26.3
68 | 115 | 1377 | 57 | S/T | 0.852
68 | 115 | 1377 | 57 | ∆T | 15.1
68 | 115 | 1377 | 57 | LDB | 52.9
68 | 115 | 1377 | 57 | LWB | 49.8
68 | 115 | 1377 | 57 | kW | 3.01
72 | 115 | 1377 | 61 | MBh | 30.4
72 | 115 | 1377 | 61 | S/T | 0.816
72 | 115 | 1377 | 61 | ∆T | 16.7
72 | 115 | 1377 | 61 | LDB | 55.3
72 | 115 | 1377 | 61 | LWB | 53.3
72 | 115 | 1377 | 61 | kW | 3.69
77 | 115 | 1377 | 64 | MBh | 30.4
77 | 115 | 1377 | 64 | S/T | 0.789
77 | 115 | 1377 | 64 | ∆T | 16.1
77 | 115 | 1377 | 64 | LDB | 60.9
77 | 115 | 1377 | 64 | LWB | 56.8
77 | 115 | 1377 | 64 | kW | 3.69
80 | 115 | 1377 | 67 | MBh | 30.4
80 | 115 | 1377 | 67 | S/T | 0.753
80 | 115 | 1377 | 67 | ∆T | 15.4
80 | 115 | 1377 | 67 | LDB | 64.6
80 | 115 | 1377 | 67 | LWB | 60.2
80 | 115 | 1377 | 67 | kW | 3.69
84 | 115 | 1377 | 70 | MBh | 30.4
84 | 115 | 1377 | 70 | S/T | 0.724
84 | 115 | 1377 | 70 | ∆T | 14.8
84 | 115 | 1377 | 70 | LDB | 69.2
84 | 115 | 1377 | 70 | LWB | 63.7
84 | 115 | 1377 | 70 | kW | 3.69
86 | 115 | 1377 | 72 | MBh | 30.4
86 | 115 | 1377 | 72 | S/T | 0.697
86 | 115 | 1377 | 72 | ∆T | 14.3
86 | 115 | 1377 | 72 | LDB | 71.7
86 | 115 | 1377 | 72 | LWB | 66
86 | 115 | 1377 | 72 | kW | 3.69
90 | 115 | 1377 | 75 | MBh | 30.4
90 | 115 | 1377 | 75 | S/T | 0.655
90 | 115 | 1377 | 75 | ∆T | 13.4
90 | 115 | 1377 | 75 | LDB | 76.6
90 | 115 | 1377 | 75 | LWB | 69.4
90 | 115 | 1377 | 75 | kW | 3.69
68 | 118 | 1377 | 57 | MBh | 26.3
68 | 118 | 1377 | 57 | S/T | 0.852
68 | 118 | 1377 | 57 | ∆T | 15.1
68 | 118 | 1377 | 57 | LDB | 52.9
68 | 118 | 1377 | 57 | LWB | 49.8
68 | 118 | 1377 | 57 | kW | 3.26
72 | 118 | 1377 | 61 | MBh | 26.8
72 | 118 | 1377 | 61 | S/T | 0.817
72 | 118 | 1377 | 61 | ∆T | 14.7
72 | 118 | 1377 | 61 | LDB | 57.3
72 | 118 | 1377 | 61 | LWB | 54.2
72 | 118 | 1377 | 61 | kW | 3.35
77 | 118 | 1377 | 64 | MBh | 26.8
77 | 118 | 1377 | 64 | S/T | 0.787
77 | 118 | 1377 | 64 | ∆T | 14.2
77 | 118 | 1377 | 64 | LDB | 62.8
77 | 118 | 1377 | 64 | LWB | 57.7
77 | 118 | 1377 | 64 | kW | 3.35
80 | 118 | 1377 | 67 | MBh | 26.8
80 | 118 | 1377 | 67 | S/T | 0.754
80 | 118 | 1377 | 67 | ∆T | 13.6
80 | 118 | 1377 | 67 | LDB | 66.4
80 | 118 | 1377 | 67 | LWB | 61.1
80 | 118 | 1377 | 67 | kW | 3.35
84 | 118 | 1377 | 70 | MBh | 26.8
84 | 118 | 1377 | 70 | S/T | 0.724
84 | 118 | 1377 | 70 | ∆T | 13
84 | 118 | 1377 | 70 | LDB | 71
84 | 118 | 1377 | 70 | LWB | 64.5
84 | 118 | 1377 | 70 | kW | 3.35
86 | 118 | 1377 | 72 | MBh | 26.8
86 | 118 | 1377 | 72 | S/T | 0.698
86 | 118 | 1377 | 72 | ∆T | 12.6
86 | 118 | 1377 | 72 | LDB | 73.4
86 | 118 | 1377 | 72 | LWB | 66.7
86 | 118 | 1377 | 72 | kW | 3.35
90 | 118 | 1377 | 75 | MBh | 26.8
90 | 118 | 1377 | 75 | S/T | 0.657
90 | 118 | 1377 | 75 | ∆T | 11.8
90 | 118 | 1377 | 75 | LDB | 78.2
90 | 118 | 1377 | 75 | LWB | 70.1
90 | 118 | 1377 | 75 | kW | 3.35
68 | 122 | 1377 | 57 | MBh | 22
68 | 122 | 1377 | 57 | S/T | 0.855
68 | 122 | 1377 | 57 | ∆T | 12.6
68 | 122 | 1377 | 57 | LDB | 55.4
68 | 122 | 1377 | 57 | LWB | 51
68 | 122 | 1377 | 57 | kW | 2.84
72 | 122 | 1377 | 61 | MBh | 22
72 | 122 | 1377 | 61 | S/T | 0.818
72 | 122 | 1377 | 61 | ∆T | 12.1
72 | 122 | 1377 | 61 | LDB | 59.9
72 | 122 | 1377 | 61 | LWB | 55.5
72 | 122 | 1377 | 61 | kW | 2.84
77 | 122 | 1377 | 64 | MBh | 22
77 | 122 | 1377 | 64 | S/T | 0.791
77 | 122 | 1377 | 64 | ∆T | 11.7
77 | 122 | 1377 | 64 | LDB | 65.3
77 | 122 | 1377 | 64 | LWB | 58.9
77 | 122 | 1377 | 64 | kW | 2.84
80 | 122 | 1377 | 67 | MBh | 22
80 | 122 | 1377 | 67 | S/T | 0.755
80 | 122 | 1377 | 67 | ∆T | 11.2
80 | 122 | 1377 | 67 | LDB | 68.8
80 | 122 | 1377 | 67 | LWB | 62.2
80 | 122 | 1377 | 67 | kW | 2.84
84 | 122 | 1377 | 70 | MBh | 22
84 | 122 | 1377 | 70 | S/T | 0.727
84 | 122 | 1377 | 70 | ∆T | 10.8
84 | 122 | 1377 | 70 | LDB | 73.2
84 | 122 | 1377 | 70 | LWB | 65.5
84 | 122 | 1377 | 70 | kW | 2.84
86 | 122 | 1377 | 72 | MBh | 22
86 | 122 | 1377 | 72 | S/T | 0.7
86 | 122 | 1377 | 72 | ∆T | 10.4
86 | 122 | 1377 | 72 | LDB | 75.6
86 | 122 | 1377 | 72 | LWB | 67.7
86 | 122 | 1377 | 72 | kW | 2.84
90 | 122 | 1377 | 75 | MBh | 22
90 | 122 | 1377 | 75 | S/T | 0.655
90 | 122 | 1377 | 75 | ∆T | 9.7
90 | 122 | 1377 | 75 | LDB | 80.3
90 | 122 | 1377 | 75 | LWB | 71
90 | 122 | 1377 | 75 | kW | 2.84

## RZA48AAVJU - FBA48AAVJU
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1377 | 57 | MBh | 31.1 | 64 | 60 | 61 | 64.8 | 4.51
68 | 23 | 1377 | 57 | S/T | 0.855 | 64 | 60 | 65 | 60 | 3.87
68 | 23 | 1377 | 57 | ∆T | 17.9 | 64 | 60 | 68 | 56.4 | 3.39
68 | 23 | 1377 | 57 | LDB | 50.1 | 64 | 60 | 70 | 54 | 3.09
68 | 23 | 1377 | 57 | LWB | 48.3 | 64 | 60 | 72 | 51.6 | 2.78
68 | 23 | 1377 | 57 | kW | 1.58 | 64 | 60 | 75 | 48 | 2.33
72 | 23 | 1377 | 61 | MBh | 37.9 | 60 | 56 | 61 | 64.8 | 4.81
72 | 23 | 1377 | 61 | S/T | 0.815 | 60 | 56 | 65 | 60 | 4.13
72 | 23 | 1377 | 61 | ∆T | 20.8 | 60 | 56 | 68 | 56.4 | 3.64
72 | 23 | 1377 | 61 | LDB | 51.2 | 60 | 56 | 70 | 54 | 3.32
72 | 23 | 1377 | 61 | LWB | 51.1 | 60 | 56 | 72 | 51.6 | 3
72 | 23 | 1377 | 61 | kW | 1.95 | 60 | 56 | 75 | 48 | 2.53
77 | 23 | 1377 | 64 | MBh | 42.9 | 57 | 53 | 61 | 64.8 | 5.05
77 | 23 | 1377 | 64 | S/T | 0.79 | 57 | 53 | 65 | 60 | 4.35
77 | 23 | 1377 | 64 | ∆T | 22.8 | 57 | 53 | 68 | 56.4 | 3.84
77 | 23 | 1377 | 64 | LDB | 54.2 | 57 | 53 | 70 | 54 | 3.51
77 | 23 | 1377 | 64 | LWB | 53.4 | 57 | 53 | 72 | 51.6 | 3.18
77 | 23 | 1377 | 64 | kW | 2.23 | 57 | 53 | 75 | 48 | 2.69
80 | 23 | 1377 | 67 | MBh | 48 | 54 | 50 | 61 | 64.8 | 5.3
80 | 23 | 1377 | 67 | S/T | 0.752 | 54 | 50 | 65 | 60 | 4.58
80 | 23 | 1377 | 67 | ∆T | 24.3 | 54 | 50 | 68 | 56.4 | 4.05
80 | 23 | 1377 | 67 | LDB | 55.7 | 54 | 50 | 70 | 54 | 3.71
80 | 23 | 1377 | 67 | LWB | 55.7 | 54 | 50 | 72 | 51.6 | 3.37
80 | 23 | 1377 | 67 | kW | 2.53 | 54 | 50 | 75 | 48 | 2.86
84 | 23 | 1377 | 70 | MBh | 53.1 | 51 | 47 | 61 | 64.8 | 5.57
84 | 23 | 1377 | 70 | S/T | 0.725 | 51 | 47 | 65 | 60 | 4.82
84 | 23 | 1377 | 70 | ∆T | 25.9 | 51 | 47 | 68 | 56.4 | 4.28
84 | 23 | 1377 | 70 | LDB | 58.1 | 51 | 47 | 70 | 54 | 3.92
84 | 23 | 1377 | 70 | LWB | 58.1 | 51 | 47 | 72 | 51.6 | 3.57
84 | 23 | 1377 | 70 | kW | 2.84 | 51 | 47 | 75 | 48 | 3.05
86 | 23 | 1377 | 72 | MBh | 56.4 | 47 | 43 | 61 | 64.8 | 5.96
86 | 23 | 1377 | 72 | S/T | 0.699 | 47 | 43 | 65 | 60 | 5.18
86 | 23 | 1377 | 72 | ∆T | 26.5 | 47 | 43 | 68 | 56.4 | 4.6
86 | 23 | 1377 | 72 | LDB | 59.5 | 47 | 43 | 70 | 54 | 4.22
86 | 23 | 1377 | 72 | LWB | 59.5 | 47 | 43 | 72 | 51.6 | 3.85
86 | 23 | 1377 | 72 | kW | 3.05 | 47 | 43 | 75 | 48 | 3.31
90 | 23 | 1377 | 75 | MBh | 61.5 | 44 | 40 | 61 | 64.8 | 6.28
90 | 23 | 1377 | 75 | S/T | 0.657 | 44 | 40 | 65 | 60 | 5.46
90 | 23 | 1377 | 75 | ∆T | 27.2 | 44 | 40 | 68 | 56.4 | 4.86
90 | 23 | 1377 | 75 | LDB | 62.8 | 44 | 40 | 70 | 54 | 4.47
90 | 23 | 1377 | 75 | LWB | 62.8 | 44 | 40 | 72 | 51.6 | 4.09
90 | 23 | 1377 | 75 | kW | 3.37 | 44 | 40 | 75 | 48 | 3.52
68 | 30 | 1377 | 57 | MBh | 31.1 | 39 | 36 | 61 | 64.8 | 6.74
68 | 30 | 1377 | 57 | S/T | 0.855 | 39 | 36 | 65 | 60 | 5.87
68 | 30 | 1377 | 57 | ∆T | 17.9 | 39 | 36 | 68 | 56.4 | 5.24
68 | 30 | 1377 | 57 | LDB | 50.1 | 39 | 36 | 70 | 54 | 4.83
68 | 30 | 1377 | 57 | LWB | 48.3 | 39 | 36 | 72 | 51.6 | 4.42
68 | 30 | 1377 | 57 | kW | 1.63 | 39 | 36 | 75 | 48 | 3.82
72 | 30 | 1377 | 61 | MBh | 37.9 | 35 | 32 | 61 | 62.2 | 6.94
72 | 30 | 1377 | 61 | S/T | 0.815 | 35 | 32 | 65 | 60 | 6.33
72 | 30 | 1377 | 61 | ∆T | 20.8 | 35 | 32 | 68 | 56.4 | 5.66
72 | 30 | 1377 | 61 | LDB | 51.2 | 35 | 32 | 70 | 54 | 5.22
72 | 30 | 1377 | 61 | LWB | 51.1 | 35 | 32 | 72 | 51.6 | 4.79
72 | 30 | 1377 | 61 | kW | 2.01 | 35 | 32 | 75 | 48 | 4.16
77 | 30 | 1377 | 64 | MBh | 42.9 | 30 | 28 | 61 | 59.5 | 6.65
77 | 30 | 1377 | 64 | S/T | 0.79 | 30 | 28 | 65 | 59.5 | 6.84
77 | 30 | 1377 | 64 | ∆T | 22.8 | 30 | 28 | 68 | 56.4 | 6.12
77 | 30 | 1377 | 64 | LDB | 54.2 | 30 | 28 | 70 | 54 | 5.66
77 | 30 | 1377 | 64 | LWB | 53.4 | 30 | 28 | 72 | 51.6 | 5.2
77 | 30 | 1377 | 64 | kW | 2.3 | 30 | 28 | 75 | 48 | 4.53
80 | 30 | 1377 | 67 | MBh | 48 | 26 | 24 | 61 | 56.2 | 6.34
80 | 30 | 1377 | 67 | S/T | 0.752 | 26 | 24 | 65 | 56.2 | 6.85
80 | 30 | 1377 | 67 | ∆T | 24.3 | 26 | 24 | 68 | 56.2 | 6.64
80 | 30 | 1377 | 67 | LDB | 55.7 | 26 | 24 | 70 | 54 | 6.15
80 | 30 | 1377 | 67 | LWB | 55.7 | 26 | 24 | 72 | 51.6 | 5.66
80 | 30 | 1377 | 67 | kW | 2.61 | 26 | 24 | 75 | 48 | 4.95
84 | 30 | 1377 | 70 | MBh | 53.1 | 22 | 20 | 61 | 52.5 | 5.99
84 | 30 | 1377 | 70 | S/T | 0.725 | 22 | 20 | 65 | 52.5 | 6.53
84 | 30 | 1377 | 70 | ∆T | 25.9 | 22 | 20 | 68 | 52.5 | 6.93
84 | 30 | 1377 | 70 | LDB | 58.1 | 22 | 20 | 70 | 52.5 | 6.69
84 | 30 | 1377 | 70 | LWB | 58.1 | 22 | 20 | 72 | 51.6 | 6.17
84 | 30 | 1377 | 70 | kW | 2.93 | 22 | 20 | 75 | 48 | 5.41
86 | 30 | 1377 | 72 | MBh | 56.4 | 19 | 18 | 61 | 50.6 | 5.8
86 | 30 | 1377 | 72 | S/T | 0.699 | 19 | 18 | 65 | 50.6 | 6.36
86 | 30 | 1377 | 72 | ∆T | 26.5 | 19 | 18 | 68 | 50.6 | 6.77
86 | 30 | 1377 | 72 | LDB | 59.5 | 19 | 18 | 70 | 50.6 | 6.98
86 | 30 | 1377 | 72 | LWB | 59.5 | 19 | 18 | 72 | 50.6 | 6.45
86 | 30 | 1377 | 72 | kW | 3.15 | 19 | 18 | 75 | 48 | 5.66
90 | 30 | 1377 | 75 | MBh | 61.5 | 17 | 16 | 61 | 48.3 | 5.56
90 | 30 | 1377 | 75 | S/T | 0.657 | 17 | 16 | 65 | 48.3 | 6.13
90 | 30 | 1377 | 75 | ∆T | 27.2 | 17 | 16 | 68 | 48.3 | 6.55
90 | 30 | 1377 | 75 | LDB | 62.8 | 17 | 16 | 70 | 48.3 | 6.84
90 | 30 | 1377 | 75 | LWB | 62.8 | 17 | 16 | 72 | 48.3 | 6.82
90 | 30 | 1377 | 75 | kW | 3.48 | 17 | 16 | 75 | 48 | 5.99
68 | 40 | 1377 | 57 | MBh | 31.1 | 15 | 14 | 61 | 46.9 | 5.4
68 | 40 | 1377 | 57 | S/T | 0.855 | 15 | 14 | 65 | 46.9 | 5.98
68 | 40 | 1377 | 57 | ∆T | 17.9 | 15 | 14 | 68 | 46.9 | 6.42
68 | 40 | 1377 | 57 | LDB | 50.1 | 15 | 14 | 70 | 46.9 | 6.71
68 | 40 | 1377 | 57 | LWB | 48.3 | 15 | 14 | 72 | 46.9 | 7
68 | 40 | 1377 | 57 | kW | 1.7 | 15 | 14 | 75 | 46.9 | 6.21
72 | 40 | 1377 | 61 | MBh | 37.9 | 13 | 12 | 61 | 45 | 5.18
72 | 40 | 1377 | 61 | S/T | 0.815 | 13 | 12 | 65 | 45 | 5.78
72 | 40 | 1377 | 61 | ∆T | 20.8 | 13 | 12 | 68 | 45 | 6.23
72 | 40 | 1377 | 61 | LDB | 51.2 | 13 | 12 | 70 | 45 | 6.53
72 | 40 | 1377 | 61 | LWB | 51.1 | 13 | 12 | 72 | 45 | 6.83
72 | 40 | 1377 | 61 | kW | 2.1 | 13 | 12 | 75 | 45 | 6.51
77 | 40 | 1377 | 64 | MBh | 42.9 | 10 | 9 | 61 | 41.8 | 4.78
77 | 40 | 1377 | 64 | S/T | 0.79 | 10 | 9 | 65 | 41.8 | 5.4
77 | 40 | 1377 | 64 | ∆T | 22.8 | 10 | 9 | 68 | 41.8 | 5.87
77 | 40 | 1377 | 64 | LDB | 54.2 | 10 | 9 | 70 | 41.8 | 6.19
77 | 40 | 1377 | 64 | LWB | 53.4 | 10 | 9 | 72 | 41.8 | 6.5
77 | 40 | 1377 | 64 | kW | 2.41 | 10 | 9 | 75 | 41.8 | 6.97
80 | 40 | 1377 | 67 | MBh | 48 | 6 | 5 | 61 | 38.5 | 4.32
80 | 40 | 1377 | 67 | S/T | 0.752 | 6 | 5 | 65 | 38.5 | 4.98
80 | 40 | 1377 | 67 | ∆T | 24.3 | 6 | 5 | 68 | 38.5 | 5.48
80 | 40 | 1377 | 67 | LDB | 55.7 | 6 | 5 | 70 | 38.5 | 5.81
80 | 40 | 1377 | 67 | LWB | 55.7 | 6 | 5 | 72 | 38.5 | 6.14
80 | 40 | 1377 | 67 | kW | 2.74 | 6 | 5 | 75 | 38.5 | 6.63
84 | 40 | 1377 | 70 | MBh | 53.1 | -2 | -2 | 61 | 31.8 | 3.23
84 | 40 | 1377 | 70 | S/T | 0.725 | -2 | -2 | 65 | 31.8 | 3.97
84 | 40 | 1377 | 70 | ∆T | 25.9 | -2 | -2 | 68 | 31.8 | 4.52
84 | 40 | 1377 | 70 | LDB | 58.1 | -2 | -2 | 70 | 31.8 | 4.89
84 | 40 | 1377 | 70 | LWB | 58.1 | -2 | -2 | 72 | 31.8 | 5.26
84 | 40 | 1377 | 70 | kW | 3.08 | -2 | -2 | 75 | 31.8 | 5.82
86 | 40 | 1377 | 72 | MBh | 56.4 | -4 | -4 | 61 | 30.1 | 2.91
86 | 40 | 1377 | 72 | S/T | 0.699 | -4 | -4 | 65 | 30.1 | 3.68
86 | 40 | 1377 | 72 | ∆T | 26.5 | -4 | -4 | 68 | 30.1 | 4.25
86 | 40 | 1377 | 72 | LDB | 59.5 | -4 | -4 | 70 | 30.1 | 4.63
86 | 40 | 1377 | 72 | LWB | 59.5 | -4 | -4 | 72 | 30.1 | 5.01
86 | 40 | 1377 | 72 | kW | 3.3 | -4 | -4 | 75 | 30.1 | 5.58
90 | 40 | 1377 | 75 | MBh | 61.5
90 | 40 | 1377 | 75 | S/T | 0.657
90 | 40 | 1377 | 75 | ∆T | 27.2
90 | 40 | 1377 | 75 | LDB | 62.8
90 | 40 | 1377 | 75 | LWB | 62.8
90 | 40 | 1377 | 75 | kW | 3.65
68 | 50 | 1377 | 57 | MBh | 31.1
68 | 50 | 1377 | 57 | S/T | 0.855
68 | 50 | 1377 | 57 | ∆T | 17.9
68 | 50 | 1377 | 57 | LDB | 50.1
68 | 50 | 1377 | 57 | LWB | 48.3
68 | 50 | 1377 | 57 | kW | 1.78
72 | 50 | 1377 | 61 | MBh | 37.9
72 | 50 | 1377 | 61 | S/T | 0.815
72 | 50 | 1377 | 61 | ∆T | 20.8
72 | 50 | 1377 | 61 | LDB | 51.2
72 | 50 | 1377 | 61 | LWB | 51.1
72 | 50 | 1377 | 61 | kW | 2.2
77 | 50 | 1377 | 64 | MBh | 42.9
77 | 50 | 1377 | 64 | S/T | 0.79
77 | 50 | 1377 | 64 | ∆T | 22.8
77 | 50 | 1377 | 64 | LDB | 54.2
77 | 50 | 1377 | 64 | LWB | 53.4
77 | 50 | 1377 | 64 | kW | 2.54
80 | 50 | 1377 | 67 | MBh | 48
80 | 50 | 1377 | 67 | S/T | 0.752
80 | 50 | 1377 | 67 | ∆T | 24.3
80 | 50 | 1377 | 67 | LDB | 55.7
80 | 50 | 1377 | 67 | LWB | 55.7
80 | 50 | 1377 | 67 | kW | 2.88
84 | 50 | 1377 | 70 | MBh | 53.1
84 | 50 | 1377 | 70 | S/T | 0.725
84 | 50 | 1377 | 70 | ∆T | 25.9
84 | 50 | 1377 | 70 | LDB | 58.1
84 | 50 | 1377 | 70 | LWB | 58.1
84 | 50 | 1377 | 70 | kW | 3.24
86 | 50 | 1377 | 72 | MBh | 56.4
86 | 50 | 1377 | 72 | S/T | 0.699
86 | 50 | 1377 | 72 | ∆T | 26.5
86 | 50 | 1377 | 72 | LDB | 59.5
86 | 50 | 1377 | 72 | LWB | 59.5
86 | 50 | 1377 | 72 | kW | 3.48
90 | 50 | 1377 | 75 | MBh | 61.5
90 | 50 | 1377 | 75 | S/T | 0.657
90 | 50 | 1377 | 75 | ∆T | 27.2
90 | 50 | 1377 | 75 | LDB | 62.8
90 | 50 | 1377 | 75 | LWB | 62.8
90 | 50 | 1377 | 75 | kW | 3.84
68 | 54 | 1377 | 57 | MBh | 31.1
68 | 54 | 1377 | 57 | S/T | 0.855
68 | 54 | 1377 | 57 | ∆T | 17.9
68 | 54 | 1377 | 57 | LDB | 50.1
68 | 54 | 1377 | 57 | LWB | 48.3
68 | 54 | 1377 | 57 | kW | 1.82
72 | 54 | 1377 | 61 | MBh | 37.9
72 | 54 | 1377 | 61 | S/T | 0.815
72 | 54 | 1377 | 61 | ∆T | 20.8
72 | 54 | 1377 | 61 | LDB | 51.2
72 | 54 | 1377 | 61 | LWB | 51.1
72 | 54 | 1377 | 61 | kW | 2.25
77 | 54 | 1377 | 64 | MBh | 42.9
77 | 54 | 1377 | 64 | S/T | 0.79
77 | 54 | 1377 | 64 | ∆T | 22.8
77 | 54 | 1377 | 64 | LDB | 54.2
77 | 54 | 1377 | 64 | LWB | 53.4
77 | 54 | 1377 | 64 | kW | 2.59
80 | 54 | 1377 | 67 | MBh | 48
80 | 54 | 1377 | 67 | S/T | 0.752
80 | 54 | 1377 | 67 | ∆T | 24.3
80 | 54 | 1377 | 67 | LDB | 55.7
80 | 54 | 1377 | 67 | LWB | 55.7
80 | 54 | 1377 | 67 | kW | 2.94
84 | 54 | 1377 | 70 | MBh | 53.1
84 | 54 | 1377 | 70 | S/T | 0.725
84 | 54 | 1377 | 70 | ∆T | 25.9
84 | 54 | 1377 | 70 | LDB | 58.1
84 | 54 | 1377 | 70 | LWB | 58.1
84 | 54 | 1377 | 70 | kW | 3.3
86 | 54 | 1377 | 72 | MBh | 56.4
86 | 54 | 1377 | 72 | S/T | 0.699
86 | 54 | 1377 | 72 | ∆T | 26.5
86 | 54 | 1377 | 72 | LDB | 59.5
86 | 54 | 1377 | 72 | LWB | 59.5
86 | 54 | 1377 | 72 | kW | 3.55
90 | 54 | 1377 | 75 | MBh | 61.5
90 | 54 | 1377 | 75 | S/T | 0.657
90 | 54 | 1377 | 75 | ∆T | 27.2
90 | 54 | 1377 | 75 | LDB | 62.8
90 | 54 | 1377 | 75 | LWB | 62.8
90 | 54 | 1377 | 75 | kW | 3.92
68 | 58 | 1377 | 57 | MBh | 31.1
68 | 58 | 1377 | 57 | S/T | 0.855
68 | 58 | 1377 | 57 | ∆T | 17.9
68 | 58 | 1377 | 57 | LDB | 50.1
68 | 58 | 1377 | 57 | LWB | 48.3
68 | 58 | 1377 | 57 | kW | 1.85
72 | 58 | 1377 | 61 | MBh | 37.9
72 | 58 | 1377 | 61 | S/T | 0.815
72 | 58 | 1377 | 61 | ∆T | 20.8
72 | 58 | 1377 | 61 | LDB | 51.2
72 | 58 | 1377 | 61 | LWB | 51.1
72 | 58 | 1377 | 61 | kW | 2.29
77 | 58 | 1377 | 64 | MBh | 42.9
77 | 58 | 1377 | 64 | S/T | 0.79
77 | 58 | 1377 | 64 | ∆T | 22.8
77 | 58 | 1377 | 64 | LDB | 54.2
77 | 58 | 1377 | 64 | LWB | 53.4
77 | 58 | 1377 | 64 | kW | 2.64
80 | 58 | 1377 | 67 | MBh | 48
80 | 58 | 1377 | 67 | S/T | 0.752
80 | 58 | 1377 | 67 | ∆T | 24.3
80 | 58 | 1377 | 67 | LDB | 55.7
80 | 58 | 1377 | 67 | LWB | 55.7
80 | 58 | 1377 | 67 | kW | 3.01
84 | 58 | 1377 | 70 | MBh | 53.1
84 | 58 | 1377 | 70 | S/T | 0.725
84 | 58 | 1377 | 70 | ∆T | 25.9
84 | 58 | 1377 | 70 | LDB | 58.1
84 | 58 | 1377 | 70 | LWB | 58.1
84 | 58 | 1377 | 70 | kW | 3.38
86 | 58 | 1377 | 72 | MBh | 56.4
86 | 58 | 1377 | 72 | S/T | 0.699
86 | 58 | 1377 | 72 | ∆T | 26.5
86 | 58 | 1377 | 72 | LDB | 59.5
86 | 58 | 1377 | 72 | LWB | 59.5
86 | 58 | 1377 | 72 | kW | 3.62
90 | 58 | 1377 | 75 | MBh | 60.9
90 | 58 | 1377 | 75 | S/T | 0.657
90 | 58 | 1377 | 75 | ∆T | 26.9
90 | 58 | 1377 | 75 | LDB | 63.1
90 | 58 | 1377 | 75 | LWB | 63
90 | 58 | 1377 | 75 | kW | 3.93
68 | 62 | 1377 | 57 | MBh | 31.1
68 | 62 | 1377 | 57 | S/T | 0.855
68 | 62 | 1377 | 57 | ∆T | 17.9
68 | 62 | 1377 | 57 | LDB | 50.1
68 | 62 | 1377 | 57 | LWB | 48.3
68 | 62 | 1377 | 57 | kW | 1.89
72 | 62 | 1377 | 61 | MBh | 37.9
72 | 62 | 1377 | 61 | S/T | 0.815
72 | 62 | 1377 | 61 | ∆T | 20.8
72 | 62 | 1377 | 61 | LDB | 51.2
72 | 62 | 1377 | 61 | LWB | 51.1
72 | 62 | 1377 | 61 | kW | 2.34
77 | 62 | 1377 | 64 | MBh | 42.9
77 | 62 | 1377 | 64 | S/T | 0.79
77 | 62 | 1377 | 64 | ∆T | 22.8
77 | 62 | 1377 | 64 | LDB | 54.2
77 | 62 | 1377 | 64 | LWB | 53.4
77 | 62 | 1377 | 64 | kW | 2.7
80 | 62 | 1377 | 67 | MBh | 48
80 | 62 | 1377 | 67 | S/T | 0.752
80 | 62 | 1377 | 67 | ∆T | 24.3
80 | 62 | 1377 | 67 | LDB | 55.7
80 | 62 | 1377 | 67 | LWB | 55.7
80 | 62 | 1377 | 67 | kW | 3.07
84 | 62 | 1377 | 70 | MBh | 53.1
84 | 62 | 1377 | 70 | S/T | 0.725
84 | 62 | 1377 | 70 | ∆T | 25.9
84 | 62 | 1377 | 70 | LDB | 58.1
84 | 62 | 1377 | 70 | LWB | 58.1
84 | 62 | 1377 | 70 | kW | 3.45
86 | 62 | 1377 | 72 | MBh | 56.4
86 | 62 | 1377 | 72 | S/T | 0.699
86 | 62 | 1377 | 72 | ∆T | 26.5
86 | 62 | 1377 | 72 | LDB | 59.5
86 | 62 | 1377 | 72 | LWB | 59.5
86 | 62 | 1377 | 72 | kW | 3.7
90 | 62 | 1377 | 75 | MBh | 60
90 | 62 | 1377 | 75 | S/T | 0.657
90 | 62 | 1377 | 75 | ∆T | 26.5
90 | 62 | 1377 | 75 | LDB | 63.5
90 | 62 | 1377 | 75 | LWB | 63.2
90 | 62 | 1377 | 75 | kW | 4.02
68 | 66 | 1377 | 57 | MBh | 31.1
68 | 66 | 1377 | 57 | S/T | 0.855
68 | 66 | 1377 | 57 | ∆T | 17.9
68 | 66 | 1377 | 57 | LDB | 50.1
68 | 66 | 1377 | 57 | LWB | 48.3
68 | 66 | 1377 | 57 | kW | 1.93
72 | 66 | 1377 | 61 | MBh | 37.9
72 | 66 | 1377 | 61 | S/T | 0.815
72 | 66 | 1377 | 61 | ∆T | 20.8
72 | 66 | 1377 | 61 | LDB | 51.2
72 | 66 | 1377 | 61 | LWB | 51.1
72 | 66 | 1377 | 61 | kW | 2.39
77 | 66 | 1377 | 64 | MBh | 42.9
77 | 66 | 1377 | 64 | S/T | 0.79
77 | 66 | 1377 | 64 | ∆T | 22.8
77 | 66 | 1377 | 64 | LDB | 54.2
77 | 66 | 1377 | 64 | LWB | 53.4
77 | 66 | 1377 | 64 | kW | 2.76
80 | 66 | 1377 | 67 | MBh | 48
80 | 66 | 1377 | 67 | S/T | 0.752
80 | 66 | 1377 | 67 | ∆T | 24.3
80 | 66 | 1377 | 67 | LDB | 55.7
80 | 66 | 1377 | 67 | LWB | 55.7
80 | 66 | 1377 | 67 | kW | 3.14
84 | 66 | 1377 | 70 | MBh | 53.1
84 | 66 | 1377 | 70 | S/T | 0.725
84 | 66 | 1377 | 70 | ∆T | 25.9
84 | 66 | 1377 | 70 | LDB | 58.1
84 | 66 | 1377 | 70 | LWB | 58.1
84 | 66 | 1377 | 70 | kW | 3.64
86 | 66 | 1377 | 72 | MBh | 56.4
86 | 66 | 1377 | 72 | S/T | 0.699
86 | 66 | 1377 | 72 | ∆T | 26.5
86 | 66 | 1377 | 72 | LDB | 59.5
86 | 66 | 1377 | 72 | LWB | 59.5
86 | 66 | 1377 | 72 | kW | 4
90 | 66 | 1377 | 75 | MBh | 59.1
90 | 66 | 1377 | 75 | S/T | 0.657
90 | 66 | 1377 | 75 | ∆T | 26.1
90 | 66 | 1377 | 75 | LDB | 63.9
90 | 66 | 1377 | 75 | LWB | 63.4
90 | 66 | 1377 | 75 | kW | 4.24
68 | 70 | 1377 | 57 | MBh | 31.1
68 | 70 | 1377 | 57 | S/T | 0.855
68 | 70 | 1377 | 57 | ∆T | 17.9
68 | 70 | 1377 | 57 | LDB | 50.1
68 | 70 | 1377 | 57 | LWB | 48.3
68 | 70 | 1377 | 57 | kW | 1.97
72 | 70 | 1377 | 61 | MBh | 37.9
72 | 70 | 1377 | 61 | S/T | 0.815
72 | 70 | 1377 | 61 | ∆T | 20.8
72 | 70 | 1377 | 61 | LDB | 51.2
72 | 70 | 1377 | 61 | LWB | 51.1
72 | 70 | 1377 | 61 | kW | 2.45
77 | 70 | 1377 | 64 | MBh | 42.9
77 | 70 | 1377 | 64 | S/T | 0.79
77 | 70 | 1377 | 64 | ∆T | 22.8
77 | 70 | 1377 | 64 | LDB | 54.2
77 | 70 | 1377 | 64 | LWB | 53.4
77 | 70 | 1377 | 64 | kW | 2.9
80 | 70 | 1377 | 67 | MBh | 48
80 | 70 | 1377 | 67 | S/T | 0.752
80 | 70 | 1377 | 67 | ∆T | 24.3
80 | 70 | 1377 | 67 | LDB | 55.7
80 | 70 | 1377 | 67 | LWB | 55.7
80 | 70 | 1377 | 67 | kW | 3.4
84 | 70 | 1377 | 70 | MBh | 53.1
84 | 70 | 1377 | 70 | S/T | 0.725
84 | 70 | 1377 | 70 | ∆T | 25.9
84 | 70 | 1377 | 70 | LDB | 58.1
84 | 70 | 1377 | 70 | LWB | 58.1
84 | 70 | 1377 | 70 | kW | 3.94
86 | 70 | 1377 | 72 | MBh | 56.4
86 | 70 | 1377 | 72 | S/T | 0.699
86 | 70 | 1377 | 72 | ∆T | 26.5
86 | 70 | 1377 | 72 | LDB | 59.5
86 | 70 | 1377 | 72 | LWB | 59.5
86 | 70 | 1377 | 72 | kW | 4.33
90 | 70 | 1377 | 75 | MBh | 58.2
90 | 70 | 1377 | 75 | S/T | 0.656
90 | 70 | 1377 | 75 | ∆T | 25.7
90 | 70 | 1377 | 75 | LDB | 64.3
90 | 70 | 1377 | 75 | LWB | 63.6
90 | 70 | 1377 | 75 | kW | 4.47
68 | 72 | 1377 | 57 | MBh | 31.1
68 | 72 | 1377 | 57 | S/T | 0.855
68 | 72 | 1377 | 57 | ∆T | 17.9
68 | 72 | 1377 | 57 | LDB | 50.1
68 | 72 | 1377 | 57 | LWB | 48.3
68 | 72 | 1377 | 57 | kW | 1.99
72 | 72 | 1377 | 61 | MBh | 37.9
72 | 72 | 1377 | 61 | S/T | 0.815
72 | 72 | 1377 | 61 | ∆T | 20.8
72 | 72 | 1377 | 61 | LDB | 51.2
72 | 72 | 1377 | 61 | LWB | 51.1
72 | 72 | 1377 | 61 | kW | 2.53
77 | 72 | 1377 | 64 | MBh | 42.9
77 | 72 | 1377 | 64 | S/T | 0.79
77 | 72 | 1377 | 64 | ∆T | 22.8
77 | 72 | 1377 | 64 | LDB | 54.2
77 | 72 | 1377 | 64 | LWB | 53.4
77 | 72 | 1377 | 64 | kW | 3.01
80 | 72 | 1377 | 67 | MBh | 48
80 | 72 | 1377 | 67 | S/T | 0.752
80 | 72 | 1377 | 67 | ∆T | 24.3
80 | 72 | 1377 | 67 | LDB | 55.7
80 | 72 | 1377 | 67 | LWB | 55.7
80 | 72 | 1377 | 67 | kW | 3.53
84 | 72 | 1377 | 70 | MBh | 53.1
84 | 72 | 1377 | 70 | S/T | 0.725
84 | 72 | 1377 | 70 | ∆T | 25.9
84 | 72 | 1377 | 70 | LDB | 58.1
84 | 72 | 1377 | 70 | LWB | 58.1
84 | 72 | 1377 | 70 | kW | 4.1
86 | 72 | 1377 | 72 | MBh | 56.4
86 | 72 | 1377 | 72 | S/T | 0.699
86 | 72 | 1377 | 72 | ∆T | 26.5
86 | 72 | 1377 | 72 | LDB | 59.5
86 | 72 | 1377 | 72 | LWB | 59.5
86 | 72 | 1377 | 72 | kW | 4.5
90 | 72 | 1377 | 75 | MBh | 57.8
90 | 72 | 1377 | 75 | S/T | 0.656
90 | 72 | 1377 | 75 | ∆T | 25.5
90 | 72 | 1377 | 75 | LDB | 64.5
90 | 72 | 1377 | 75 | LWB | 63.7
90 | 72 | 1377 | 75 | kW | 4.58
68 | 75 | 1377 | 57 | MBh | 31.1
68 | 75 | 1377 | 57 | S/T | 0.855
68 | 75 | 1377 | 57 | ∆T | 17.9
68 | 75 | 1377 | 57 | LDB | 50.1
68 | 75 | 1377 | 57 | LWB | 48.3
68 | 75 | 1377 | 57 | kW | 2.06
72 | 75 | 1377 | 61 | MBh | 37.9
72 | 75 | 1377 | 61 | S/T | 0.815
72 | 75 | 1377 | 61 | ∆T | 20.8
72 | 75 | 1377 | 61 | LDB | 51.2
72 | 75 | 1377 | 61 | LWB | 51.1
72 | 75 | 1377 | 61 | kW | 2.67
77 | 75 | 1377 | 64 | MBh | 42.9
77 | 75 | 1377 | 64 | S/T | 0.79
77 | 75 | 1377 | 64 | ∆T | 22.8
77 | 75 | 1377 | 64 | LDB | 54.2
77 | 75 | 1377 | 64 | LWB | 53.4
77 | 75 | 1377 | 64 | kW | 3.18
80 | 75 | 1377 | 67 | MBh | 48
80 | 75 | 1377 | 67 | S/T | 0.752
80 | 75 | 1377 | 67 | ∆T | 24.3
80 | 75 | 1377 | 67 | LDB | 55.7
80 | 75 | 1377 | 67 | LWB | 55.7
80 | 75 | 1377 | 67 | kW | 3.74
84 | 75 | 1377 | 70 | MBh | 53.1
84 | 75 | 1377 | 70 | S/T | 0.725
84 | 75 | 1377 | 70 | ∆T | 25.9
84 | 75 | 1377 | 70 | LDB | 58.1
84 | 75 | 1377 | 70 | LWB | 58.1
84 | 75 | 1377 | 70 | kW | 4.34
86 | 75 | 1377 | 72 | MBh | 56.1
86 | 75 | 1377 | 72 | S/T | 0.699
86 | 75 | 1377 | 72 | ∆T | 26.4
86 | 75 | 1377 | 72 | LDB | 59.6
86 | 75 | 1377 | 72 | LWB | 59.6
86 | 75 | 1377 | 72 | kW | 4.72
90 | 75 | 1377 | 75 | MBh | 57.1
90 | 75 | 1377 | 75 | S/T | 0.657
90 | 75 | 1377 | 75 | ∆T | 25.2
90 | 75 | 1377 | 75 | LDB | 64.8
90 | 75 | 1377 | 75 | LWB | 63.9
90 | 75 | 1377 | 75 | kW | 4.75
68 | 79 | 1377 | 57 | MBh | 31.1
68 | 79 | 1377 | 57 | S/T | 0.855
68 | 79 | 1377 | 57 | ∆T | 17.9
68 | 79 | 1377 | 57 | LDB | 50.1
68 | 79 | 1377 | 57 | LWB | 48.3
68 | 79 | 1377 | 57 | kW | 2.21
72 | 79 | 1377 | 61 | MBh | 37.9
72 | 79 | 1377 | 61 | S/T | 0.815
72 | 79 | 1377 | 61 | ∆T | 20.8
72 | 79 | 1377 | 61 | LDB | 51.2
72 | 79 | 1377 | 61 | LWB | 51.1
72 | 79 | 1377 | 61 | kW | 2.87
77 | 79 | 1377 | 64 | MBh | 42.9
77 | 79 | 1377 | 64 | S/T | 0.79
77 | 79 | 1377 | 64 | ∆T | 22.8
77 | 79 | 1377 | 64 | LDB | 54.2
77 | 79 | 1377 | 64 | LWB | 53.4
77 | 79 | 1377 | 64 | kW | 3.43
80 | 79 | 1377 | 67 | MBh | 48
80 | 79 | 1377 | 67 | S/T | 0.752
80 | 79 | 1377 | 67 | ∆T | 24.3
80 | 79 | 1377 | 67 | LDB | 55.7
80 | 79 | 1377 | 67 | LWB | 55.7
80 | 79 | 1377 | 67 | kW | 4.03
84 | 79 | 1377 | 70 | MBh | 53.1
84 | 79 | 1377 | 70 | S/T | 0.725
84 | 79 | 1377 | 70 | ∆T | 25.9
84 | 79 | 1377 | 70 | LDB | 58.1
84 | 79 | 1377 | 70 | LWB | 58.1
84 | 79 | 1377 | 70 | kW | 4.68
86 | 79 | 1377 | 72 | MBh | 55.2
86 | 79 | 1377 | 72 | S/T | 0.699
86 | 79 | 1377 | 72 | ∆T | 26
86 | 79 | 1377 | 72 | LDB | 60
86 | 79 | 1377 | 72 | LWB | 60
86 | 79 | 1377 | 72 | kW | 4.94
90 | 79 | 1377 | 75 | MBh | 56.2
90 | 79 | 1377 | 75 | S/T | 0.657
90 | 79 | 1377 | 75 | ∆T | 24.8
90 | 79 | 1377 | 75 | LDB | 65.2
90 | 79 | 1377 | 75 | LWB | 64.1
90 | 79 | 1377 | 75 | kW | 4.97
68 | 83 | 1377 | 57 | MBh | 31.1
68 | 83 | 1377 | 57 | S/T | 0.855
68 | 83 | 1377 | 57 | ∆T | 17.9
68 | 83 | 1377 | 57 | LDB | 50.1
68 | 83 | 1377 | 57 | LWB | 48.3
68 | 83 | 1377 | 57 | kW | 2.37
72 | 83 | 1377 | 61 | MBh | 37.9
72 | 83 | 1377 | 61 | S/T | 0.815
72 | 83 | 1377 | 61 | ∆T | 20.8
72 | 83 | 1377 | 61 | LDB | 51.2
72 | 83 | 1377 | 61 | LWB | 51.1
72 | 83 | 1377 | 61 | kW | 3.09
77 | 83 | 1377 | 64 | MBh | 42.9
77 | 83 | 1377 | 64 | S/T | 0.79
77 | 83 | 1377 | 64 | ∆T | 22.8
77 | 83 | 1377 | 64 | LDB | 54.2
77 | 83 | 1377 | 64 | LWB | 53.4
77 | 83 | 1377 | 64 | kW | 3.69
80 | 83 | 1377 | 67 | MBh | 48
80 | 83 | 1377 | 67 | S/T | 0.752
80 | 83 | 1377 | 67 | ∆T | 24.3
80 | 83 | 1377 | 67 | LDB | 55.7
80 | 83 | 1377 | 67 | LWB | 55.7
80 | 83 | 1377 | 67 | kW | 4.34
84 | 83 | 1377 | 70 | MBh | 53.1
84 | 83 | 1377 | 70 | S/T | 0.725
84 | 83 | 1377 | 70 | ∆T | 25.9
84 | 83 | 1377 | 70 | LDB | 58.1
84 | 83 | 1377 | 70 | LWB | 58.1
84 | 83 | 1377 | 70 | kW | 5.05
86 | 83 | 1377 | 72 | MBh | 54.3
86 | 83 | 1377 | 72 | S/T | 0.698
86 | 83 | 1377 | 72 | ∆T | 25.5
86 | 83 | 1377 | 72 | LDB | 60.5
86 | 83 | 1377 | 72 | LWB | 60.5
86 | 83 | 1377 | 72 | kW | 5.17
90 | 83 | 1377 | 75 | MBh | 55.3
90 | 83 | 1377 | 75 | S/T | 0.656
90 | 83 | 1377 | 75 | ∆T | 24.4
90 | 83 | 1377 | 75 | LDB | 65.6
90 | 83 | 1377 | 75 | LWB | 64.3
90 | 83 | 1377 | 75 | kW | 5.2
68 | 87 | 1377 | 57 | MBh | 31.1
68 | 87 | 1377 | 57 | S/T | 0.855
68 | 87 | 1377 | 57 | ∆T | 17.9
68 | 87 | 1377 | 57 | LDB | 50.1
68 | 87 | 1377 | 57 | LWB | 48.3
68 | 87 | 1377 | 57 | kW | 2.54
72 | 87 | 1377 | 61 | MBh | 37.9
72 | 87 | 1377 | 61 | S/T | 0.815
72 | 87 | 1377 | 61 | ∆T | 20.8
72 | 87 | 1377 | 61 | LDB | 51.2
72 | 87 | 1377 | 61 | LWB | 51.1
72 | 87 | 1377 | 61 | kW | 3.31
77 | 87 | 1377 | 64 | MBh | 42.9
77 | 87 | 1377 | 64 | S/T | 0.79
77 | 87 | 1377 | 64 | ∆T | 22.8
77 | 87 | 1377 | 64 | LDB | 54.2
77 | 87 | 1377 | 64 | LWB | 53.4
77 | 87 | 1377 | 64 | kW | 3.96
80 | 87 | 1377 | 67 | MBh | 48
80 | 87 | 1377 | 67 | S/T | 0.752
80 | 87 | 1377 | 67 | ∆T | 24.3
80 | 87 | 1377 | 67 | LDB | 55.7
80 | 87 | 1377 | 67 | LWB | 55.7
80 | 87 | 1377 | 67 | kW | 4.67
84 | 87 | 1377 | 70 | MBh | 52.7
84 | 87 | 1377 | 70 | S/T | 0.725
84 | 87 | 1377 | 70 | ∆T | 25.7
84 | 87 | 1377 | 70 | LDB | 58.3
84 | 87 | 1377 | 70 | LWB | 58.3
84 | 87 | 1377 | 70 | kW | 5.37
86 | 87 | 1377 | 72 | MBh | 53.4
86 | 87 | 1377 | 72 | S/T | 0.699
86 | 87 | 1377 | 72 | ∆T | 25.1
86 | 87 | 1377 | 72 | LDB | 60.9
86 | 87 | 1377 | 72 | LWB | 60.9
86 | 87 | 1377 | 72 | kW | 5.4
90 | 87 | 1377 | 75 | MBh | 54.4
90 | 87 | 1377 | 75 | S/T | 0.656
90 | 87 | 1377 | 75 | ∆T | 24
90 | 87 | 1377 | 75 | LDB | 66
90 | 87 | 1377 | 75 | LWB | 64.5
90 | 87 | 1377 | 75 | kW | 5.43
68 | 91 | 1377 | 57 | MBh | 31.1
68 | 91 | 1377 | 57 | S/T | 0.855
68 | 91 | 1377 | 57 | ∆T | 17.9
68 | 91 | 1377 | 57 | LDB | 50.1
68 | 91 | 1377 | 57 | LWB | 48.3
68 | 91 | 1377 | 57 | kW | 2.72
72 | 91 | 1377 | 61 | MBh | 37.9
72 | 91 | 1377 | 61 | S/T | 0.815
72 | 91 | 1377 | 61 | ∆T | 20.8
72 | 91 | 1377 | 61 | LDB | 51.2
72 | 91 | 1377 | 61 | LWB | 51.1
72 | 91 | 1377 | 61 | kW | 3.55
77 | 91 | 1377 | 64 | MBh | 42.9
77 | 91 | 1377 | 64 | S/T | 0.79
77 | 91 | 1377 | 64 | ∆T | 22.8
77 | 91 | 1377 | 64 | LDB | 54.2
77 | 91 | 1377 | 64 | LWB | 53.4
77 | 91 | 1377 | 64 | kW | 4.25
80 | 91 | 1377 | 67 | MBh | 48
80 | 91 | 1377 | 67 | S/T | 0.752
80 | 91 | 1377 | 67 | ∆T | 24.3
80 | 91 | 1377 | 67 | LDB | 55.7
80 | 91 | 1377 | 67 | LWB | 55.7
80 | 91 | 1377 | 67 | kW | 5.02
84 | 91 | 1377 | 70 | MBh | 51.8
84 | 91 | 1377 | 70 | S/T | 0.726
84 | 91 | 1377 | 70 | ∆T | 25.3
84 | 91 | 1377 | 70 | LDB | 58.7
84 | 91 | 1377 | 70 | LWB | 58.7
84 | 91 | 1377 | 70 | kW | 5.6
86 | 91 | 1377 | 72 | MBh | 52.5
86 | 91 | 1377 | 72 | S/T | 0.699
86 | 91 | 1377 | 72 | ∆T | 24.7
86 | 91 | 1377 | 72 | LDB | 61.3
86 | 91 | 1377 | 72 | LWB | 61.1
86 | 91 | 1377 | 72 | kW | 5.62
90 | 91 | 1377 | 75 | MBh | 53.5
90 | 91 | 1377 | 75 | S/T | 0.656
90 | 91 | 1377 | 75 | ∆T | 23.6
90 | 91 | 1377 | 75 | LDB | 66.4
90 | 91 | 1377 | 75 | LWB | 64.7
90 | 91 | 1377 | 75 | kW | 5.66
68 | 93 | 1377 | 57 | MBh | 31.1
68 | 93 | 1377 | 57 | S/T | 0.855
68 | 93 | 1377 | 57 | ∆T | 17.9
68 | 93 | 1377 | 57 | LDB | 50.1
68 | 93 | 1377 | 57 | LWB | 48.3
68 | 93 | 1377 | 57 | kW | 2.81
72 | 93 | 1377 | 61 | MBh | 37.9
72 | 93 | 1377 | 61 | S/T | 0.815
72 | 93 | 1377 | 61 | ∆T | 20.8
72 | 93 | 1377 | 61 | LDB | 51.2
72 | 93 | 1377 | 61 | LWB | 51.1
72 | 93 | 1377 | 61 | kW | 3.68
77 | 93 | 1377 | 64 | MBh | 42.9
77 | 93 | 1377 | 64 | S/T | 0.79
77 | 93 | 1377 | 64 | ∆T | 22.8
77 | 93 | 1377 | 64 | LDB | 54.2
77 | 93 | 1377 | 64 | LWB | 53.4
77 | 93 | 1377 | 64 | kW | 4.41
80 | 93 | 1377 | 67 | MBh | 48
80 | 93 | 1377 | 67 | S/T | 0.752
80 | 93 | 1377 | 67 | ∆T | 24.3
80 | 93 | 1377 | 67 | LDB | 55.7
80 | 93 | 1377 | 67 | LWB | 55.7
80 | 93 | 1377 | 67 | kW | 5.2
84 | 93 | 1377 | 70 | MBh | 51.4
84 | 93 | 1377 | 70 | S/T | 0.726
84 | 93 | 1377 | 70 | ∆T | 25.1
84 | 93 | 1377 | 70 | LDB | 58.9
84 | 93 | 1377 | 70 | LWB | 58.8
84 | 93 | 1377 | 70 | kW | 5.71
86 | 93 | 1377 | 72 | MBh | 52
86 | 93 | 1377 | 72 | S/T | 0.7
86 | 93 | 1377 | 72 | ∆T | 24.5
86 | 93 | 1377 | 72 | LDB | 61.5
86 | 93 | 1377 | 72 | LWB | 61.2
86 | 93 | 1377 | 72 | kW | 5.74
90 | 93 | 1377 | 75 | MBh | 53
90 | 93 | 1377 | 75 | S/T | 0.657
90 | 93 | 1377 | 75 | ∆T | 23.4
90 | 93 | 1377 | 75 | LDB | 66.6
90 | 93 | 1377 | 75 | LWB | 64.8
90 | 93 | 1377 | 75 | kW | 5.78
68 | 95 | 1377 | 57 | MBh | 31.1
68 | 95 | 1377 | 57 | S/T | 0.855
68 | 95 | 1377 | 57 | ∆T | 17.9
68 | 95 | 1377 | 57 | LDB | 50.1
68 | 95 | 1377 | 57 | LWB | 48.3
68 | 95 | 1377 | 57 | kW | 2.91
72 | 95 | 1377 | 61 | MBh | 37.9
72 | 95 | 1377 | 61 | S/T | 0.815
72 | 95 | 1377 | 61 | ∆T | 20.8
72 | 95 | 1377 | 61 | LDB | 51.2
72 | 95 | 1377 | 61 | LWB | 51.1
72 | 95 | 1377 | 61 | kW | 3.81
77 | 95 | 1377 | 64 | MBh | 42.9
77 | 95 | 1377 | 64 | S/T | 0.79
77 | 95 | 1377 | 64 | ∆T | 22.8
77 | 95 | 1377 | 64 | LDB | 54.2
77 | 95 | 1377 | 64 | LWB | 53.4
77 | 95 | 1377 | 64 | kW | 4.56
80 | 95 | 1377 | 67 | MBh | 48
80 | 95 | 1377 | 67 | S/T | 0.752
80 | 95 | 1377 | 67 | ∆T | 24.3
80 | 95 | 1377 | 67 | LDB | 55.7
80 | 95 | 1377 | 67 | LWB | 55.7
80 | 95 | 1377 | 67 | kW | 5.39
84 | 95 | 1377 | 70 | MBh | 50.9
84 | 95 | 1377 | 70 | S/T | 0.725
84 | 95 | 1377 | 70 | ∆T | 24.8
84 | 95 | 1377 | 70 | LDB | 59.2
84 | 95 | 1377 | 70 | LWB | 58.9
84 | 95 | 1377 | 70 | kW | 5.83
86 | 95 | 1377 | 72 | MBh | 51.6
86 | 95 | 1377 | 72 | S/T | 0.7
86 | 95 | 1377 | 72 | ∆T | 24.3
86 | 95 | 1377 | 72 | LDB | 61.7
86 | 95 | 1377 | 72 | LWB | 61.3
86 | 95 | 1377 | 72 | kW | 5.85
90 | 95 | 1377 | 75 | MBh | 52
90 | 95 | 1377 | 75 | S/T | 0.658
90 | 95 | 1377 | 75 | ∆T | 23
90 | 95 | 1377 | 75 | LDB | 67
90 | 95 | 1377 | 75 | LWB | 65
90 | 95 | 1377 | 75 | kW | 5.87
68 | 99 | 1377 | 57 | MBh | 31.1
68 | 99 | 1377 | 57 | S/T | 0.855
68 | 99 | 1377 | 57 | ∆T | 17.9
68 | 99 | 1377 | 57 | LDB | 50.1
68 | 99 | 1377 | 57 | LWB | 48.3
68 | 99 | 1377 | 57 | kW | 3.11
72 | 99 | 1377 | 61 | MBh | 37.9
72 | 99 | 1377 | 61 | S/T | 0.815
72 | 99 | 1377 | 61 | ∆T | 20.8
72 | 99 | 1377 | 61 | LDB | 51.2
72 | 99 | 1377 | 61 | LWB | 51.1
72 | 99 | 1377 | 61 | kW | 4.08
77 | 99 | 1377 | 64 | MBh | 42.9
77 | 99 | 1377 | 64 | S/T | 0.79
77 | 99 | 1377 | 64 | ∆T | 22.8
77 | 99 | 1377 | 64 | LDB | 54.2
77 | 99 | 1377 | 64 | LWB | 53.4
77 | 99 | 1377 | 64 | kW | 4.89
80 | 99 | 1377 | 67 | MBh | 48
80 | 99 | 1377 | 67 | S/T | 0.752
80 | 99 | 1377 | 67 | ∆T | 24.3
80 | 99 | 1377 | 67 | LDB | 55.7
80 | 99 | 1377 | 67 | LWB | 55.7
80 | 99 | 1377 | 67 | kW | 5.79
84 | 99 | 1377 | 70 | MBh | 50
84 | 99 | 1377 | 70 | S/T | 0.726
84 | 99 | 1377 | 70 | ∆T | 24.4
84 | 99 | 1377 | 70 | LDB | 59.6
84 | 99 | 1377 | 70 | LWB | 59.1
84 | 99 | 1377 | 70 | kW | 6.06
86 | 99 | 1377 | 72 | MBh | 50.1
86 | 99 | 1377 | 72 | S/T | 0.699
86 | 99 | 1377 | 72 | ∆T | 23.5
86 | 99 | 1377 | 72 | LDB | 62.5
86 | 99 | 1377 | 72 | LWB | 61.6
86 | 99 | 1377 | 72 | kW | 6.06
90 | 99 | 1377 | 75 | MBh | 50.1
90 | 99 | 1377 | 75 | S/T | 0.657
90 | 99 | 1377 | 75 | ∆T | 22.1
90 | 99 | 1377 | 75 | LDB | 67.9
90 | 99 | 1377 | 75 | LWB | 65.4
90 | 99 | 1377 | 75 | kW | 6.06
68 | 103 | 1377 | 57 | MBh | 31.1
68 | 103 | 1377 | 57 | S/T | 0.855
68 | 103 | 1377 | 57 | ∆T | 17.9
68 | 103 | 1377 | 57 | LDB | 50.1
68 | 103 | 1377 | 57 | LWB | 48.3
68 | 103 | 1377 | 57 | kW | 3.33
72 | 103 | 1377 | 61 | MBh | 37.9
72 | 103 | 1377 | 61 | S/T | 0.815
72 | 103 | 1377 | 61 | ∆T | 20.8
72 | 103 | 1377 | 61 | LDB | 51.2
72 | 103 | 1377 | 61 | LWB | 51.1
72 | 103 | 1377 | 61 | kW | 4.37
77 | 103 | 1377 | 64 | MBh | 42.9
77 | 103 | 1377 | 64 | S/T | 0.79
77 | 103 | 1377 | 64 | ∆T | 22.8
77 | 103 | 1377 | 64 | LDB | 54.2
77 | 103 | 1377 | 64 | LWB | 53.4
77 | 103 | 1377 | 64 | kW | 5.25
80 | 103 | 1377 | 67 | MBh | 47.7
80 | 103 | 1377 | 67 | S/T | 0.753
80 | 103 | 1377 | 67 | ∆T | 24.1
80 | 103 | 1377 | 67 | LDB | 55.9
80 | 103 | 1377 | 67 | LWB | 55.9
80 | 103 | 1377 | 67 | kW | 6.15
84 | 103 | 1377 | 70 | MBh | 47.7
84 | 103 | 1377 | 70 | S/T | 0.725
84 | 103 | 1377 | 70 | ∆T | 23.3
84 | 103 | 1377 | 70 | LDB | 60.7
84 | 103 | 1377 | 70 | LWB | 59.7
84 | 103 | 1377 | 70 | kW | 6.15
86 | 103 | 1377 | 72 | MBh | 47.7
86 | 103 | 1377 | 72 | S/T | 0.698
86 | 103 | 1377 | 72 | ∆T | 22.4
86 | 103 | 1377 | 72 | LDB | 63.6
86 | 103 | 1377 | 72 | LWB | 62.2
86 | 103 | 1377 | 72 | kW | 6.15
90 | 103 | 1377 | 75 | MBh | 47.7
90 | 103 | 1377 | 75 | S/T | 0.656
90 | 103 | 1377 | 75 | ∆T | 21
90 | 103 | 1377 | 75 | LDB | 69
90 | 103 | 1377 | 75 | LWB | 65.9
90 | 103 | 1377 | 75 | kW | 6.15
68 | 106 | 1377 | 57 | MBh | 31.1
68 | 106 | 1377 | 57 | S/T | 0.855
68 | 106 | 1377 | 57 | ∆T | 17.9
68 | 106 | 1377 | 57 | LDB | 50.1
68 | 106 | 1377 | 57 | LWB | 48.3
68 | 106 | 1377 | 57 | kW | 3.49
72 | 106 | 1377 | 61 | MBh | 37.9
72 | 106 | 1377 | 61 | S/T | 0.815
72 | 106 | 1377 | 61 | ∆T | 20.8
72 | 106 | 1377 | 61 | LDB | 51.2
72 | 106 | 1377 | 61 | LWB | 51.1
72 | 106 | 1377 | 61 | kW | 4.6
77 | 106 | 1377 | 64 | MBh | 42.9
77 | 106 | 1377 | 64 | S/T | 0.79
77 | 106 | 1377 | 64 | ∆T | 22.8
77 | 106 | 1377 | 64 | LDB | 54.2
77 | 106 | 1377 | 64 | LWB | 53.4
77 | 106 | 1377 | 64 | kW | 5.53
80 | 106 | 1377 | 67 | MBh | 43.6
80 | 106 | 1377 | 67 | S/T | 0.752
80 | 106 | 1377 | 67 | ∆T | 22.1
80 | 106 | 1377 | 67 | LDB | 57.9
80 | 106 | 1377 | 67 | LWB | 57
80 | 106 | 1377 | 67 | kW | 5.65
84 | 106 | 1377 | 70 | MBh | 43.6
84 | 106 | 1377 | 70 | S/T | 0.725
84 | 106 | 1377 | 70 | ∆T | 21.2
84 | 106 | 1377 | 70 | LDB | 62.8
84 | 106 | 1377 | 70 | LWB | 60.7
84 | 106 | 1377 | 70 | kW | 5.65
86 | 106 | 1377 | 72 | MBh | 43.6
86 | 106 | 1377 | 72 | S/T | 0.7
86 | 106 | 1377 | 72 | ∆T | 20.5
86 | 106 | 1377 | 72 | LDB | 65.5
86 | 106 | 1377 | 72 | LWB | 63.1
86 | 106 | 1377 | 72 | kW | 5.65
90 | 106 | 1377 | 75 | MBh | 43.6
90 | 106 | 1377 | 75 | S/T | 0.656
90 | 106 | 1377 | 75 | ∆T | 19.2
90 | 106 | 1377 | 75 | LDB | 70.8
90 | 106 | 1377 | 75 | LWB | 66.8
90 | 106 | 1377 | 75 | kW | 5.65
68 | 110 | 1377 | 57 | MBh | 31.1
68 | 110 | 1377 | 57 | S/T | 0.855
68 | 110 | 1377 | 57 | ∆T | 17.9
68 | 110 | 1377 | 57 | LDB | 50.1
68 | 110 | 1377 | 57 | LWB | 48.3
68 | 110 | 1377 | 57 | kW | 3.73
72 | 110 | 1377 | 61 | MBh | 37.9
72 | 110 | 1377 | 61 | S/T | 0.815
72 | 110 | 1377 | 61 | ∆T | 20.8
72 | 110 | 1377 | 61 | LDB | 51.2
72 | 110 | 1377 | 61 | LWB | 51.1
72 | 110 | 1377 | 61 | kW | 4.92
77 | 110 | 1377 | 64 | MBh | 38.1
77 | 110 | 1377 | 64 | S/T | 0.787
77 | 110 | 1377 | 64 | ∆T | 20.2
77 | 110 | 1377 | 64 | LDB | 56.8
77 | 110 | 1377 | 64 | LWB | 54.7
77 | 110 | 1377 | 64 | kW | 4.96
80 | 110 | 1377 | 67 | MBh | 38.1
80 | 110 | 1377 | 67 | S/T | 0.751
80 | 110 | 1377 | 67 | ∆T | 19.2
80 | 110 | 1377 | 67 | LDB | 60.8
80 | 110 | 1377 | 67 | LWB | 58.4
80 | 110 | 1377 | 67 | kW | 4.96
84 | 110 | 1377 | 70 | MBh | 38.1
84 | 110 | 1377 | 70 | S/T | 0.724
84 | 110 | 1377 | 70 | ∆T | 18.6
84 | 110 | 1377 | 70 | LDB | 65.4
84 | 110 | 1377 | 70 | LWB | 62
84 | 110 | 1377 | 70 | kW | 4.96
86 | 110 | 1377 | 72 | MBh | 38.1
86 | 110 | 1377 | 72 | S/T | 0.698
86 | 110 | 1377 | 72 | ∆T | 17.9
86 | 110 | 1377 | 72 | LDB | 68.1
86 | 110 | 1377 | 72 | LWB | 64.3
86 | 110 | 1377 | 72 | kW | 4.96
90 | 110 | 1377 | 75 | MBh | 38.1
90 | 110 | 1377 | 75 | S/T | 0.656
90 | 110 | 1377 | 75 | ∆T | 16.8
90 | 110 | 1377 | 75 | LDB | 73.2
90 | 110 | 1377 | 75 | LWB | 67.9
90 | 110 | 1377 | 75 | kW | 4.96
68 | 115 | 1377 | 57 | MBh | 31.1
68 | 115 | 1377 | 57 | S/T | 0.855
68 | 115 | 1377 | 57 | ∆T | 17.9
68 | 115 | 1377 | 57 | LDB | 50.1
68 | 115 | 1377 | 57 | LWB | 48.3
68 | 115 | 1377 | 57 | kW | 4.11
72 | 115 | 1377 | 61 | MBh | 31.2
72 | 115 | 1377 | 61 | S/T | 0.814
72 | 115 | 1377 | 61 | ∆T | 17.1
72 | 115 | 1377 | 61 | LDB | 54.9
72 | 115 | 1377 | 61 | LWB | 53
72 | 115 | 1377 | 61 | kW | 4.12
77 | 115 | 1377 | 64 | MBh | 31.2
77 | 115 | 1377 | 64 | S/T | 0.788
77 | 115 | 1377 | 64 | ∆T | 16.5
77 | 115 | 1377 | 64 | LDB | 60.5
77 | 115 | 1377 | 64 | LWB | 56.5
77 | 115 | 1377 | 64 | kW | 4.12
80 | 115 | 1377 | 67 | MBh | 31.2
80 | 115 | 1377 | 67 | S/T | 0.75
80 | 115 | 1377 | 67 | ∆T | 15.7
80 | 115 | 1377 | 67 | LDB | 64.3
80 | 115 | 1377 | 67 | LWB | 60
80 | 115 | 1377 | 67 | kW | 4.12
84 | 115 | 1377 | 70 | MBh | 31.2
84 | 115 | 1377 | 70 | S/T | 0.724
84 | 115 | 1377 | 70 | ∆T | 15.2
84 | 115 | 1377 | 70 | LDB | 68.8
84 | 115 | 1377 | 70 | LWB | 63.5
84 | 115 | 1377 | 70 | kW | 4.12
86 | 115 | 1377 | 72 | MBh | 31.2
86 | 115 | 1377 | 72 | S/T | 0.699
86 | 115 | 1377 | 72 | ∆T | 14.7
86 | 115 | 1377 | 72 | LDB | 71.3
86 | 115 | 1377 | 72 | LWB | 65.8
86 | 115 | 1377 | 72 | kW | 4.12
90 | 115 | 1377 | 75 | MBh | 31.2
90 | 115 | 1377 | 75 | S/T | 0.657
90 | 115 | 1377 | 75 | ∆T | 13.8
90 | 115 | 1377 | 75 | LDB | 76.2
90 | 115 | 1377 | 75 | LWB | 69.3
90 | 115 | 1377 | 75 | kW | 4.12
68 | 118 | 1377 | 57 | MBh | 27
68 | 118 | 1377 | 57 | S/T | 0.856
68 | 118 | 1377 | 57 | ∆T | 15.5
68 | 118 | 1377 | 57 | LDB | 52.5
68 | 118 | 1377 | 57 | LWB | 49.6
68 | 118 | 1377 | 57 | kW | 3.69
72 | 118 | 1377 | 61 | MBh | 27
72 | 118 | 1377 | 61 | S/T | 0.819
72 | 118 | 1377 | 61 | ∆T | 14.9
72 | 118 | 1377 | 61 | LDB | 57.1
72 | 118 | 1377 | 61 | LWB | 54.2
72 | 118 | 1377 | 61 | kW | 3.69
77 | 118 | 1377 | 64 | MBh | 27
77 | 118 | 1377 | 64 | S/T | 0.789
77 | 118 | 1377 | 64 | ∆T | 14.3
77 | 118 | 1377 | 64 | LDB | 62.7
77 | 118 | 1377 | 64 | LWB | 57.6
77 | 118 | 1377 | 64 | kW | 3.69
80 | 118 | 1377 | 67 | MBh | 27
80 | 118 | 1377 | 67 | S/T | 0.752
80 | 118 | 1377 | 67 | ∆T | 13.7
80 | 118 | 1377 | 67 | LDB | 66.3
80 | 118 | 1377 | 67 | LWB | 61
80 | 118 | 1377 | 67 | kW | 3.69
84 | 118 | 1377 | 70 | MBh | 27
84 | 118 | 1377 | 70 | S/T | 0.726
84 | 118 | 1377 | 70 | ∆T | 13.2
84 | 118 | 1377 | 70 | LDB | 70.8
84 | 118 | 1377 | 70 | LWB | 64.4
84 | 118 | 1377 | 70 | kW | 3.69
86 | 118 | 1377 | 72 | MBh | 27
86 | 118 | 1377 | 72 | S/T | 0.7
86 | 118 | 1377 | 72 | ∆T | 12.7
86 | 118 | 1377 | 72 | LDB | 73.3
86 | 118 | 1377 | 72 | LWB | 66.7
86 | 118 | 1377 | 72 | kW | 3.69
90 | 118 | 1377 | 75 | MBh | 27
90 | 118 | 1377 | 75 | S/T | 0.656
90 | 118 | 1377 | 75 | ∆T | 11.9
90 | 118 | 1377 | 75 | LDB | 78.1
90 | 118 | 1377 | 75 | LWB | 70.1
90 | 118 | 1377 | 75 | kW | 3.69
68 | 122 | 1377 | 57 | MBh | 21.5
68 | 122 | 1377 | 57 | S/T | 0.856
68 | 122 | 1377 | 57 | ∆T | 12.4
68 | 122 | 1377 | 57 | LDB | 55.6
68 | 122 | 1377 | 57 | LWB | 51.2
68 | 122 | 1377 | 57 | kW | 3.06
72 | 122 | 1377 | 61 | MBh | 21.5
72 | 122 | 1377 | 61 | S/T | 0.819
72 | 122 | 1377 | 61 | ∆T | 11.8
72 | 122 | 1377 | 61 | LDB | 60.2
72 | 122 | 1377 | 61 | LWB | 55.6
72 | 122 | 1377 | 61 | kW | 3.06
77 | 122 | 1377 | 64 | MBh | 21.5
77 | 122 | 1377 | 64 | S/T | 0.791
77 | 122 | 1377 | 64 | ∆T | 11.4
77 | 122 | 1377 | 64 | LDB | 65.6
77 | 122 | 1377 | 64 | LWB | 59
77 | 122 | 1377 | 64 | kW | 3.06
80 | 122 | 1377 | 67 | MBh | 21.5
80 | 122 | 1377 | 67 | S/T | 0.753
80 | 122 | 1377 | 67 | ∆T | 10.9
80 | 122 | 1377 | 67 | LDB | 69.1
80 | 122 | 1377 | 67 | LWB | 62.3
80 | 122 | 1377 | 67 | kW | 3.06
84 | 122 | 1377 | 70 | MBh | 21.5
84 | 122 | 1377 | 70 | S/T | 0.726
84 | 122 | 1377 | 70 | ∆T | 10.5
84 | 122 | 1377 | 70 | LDB | 73.5
84 | 122 | 1377 | 70 | LWB | 65.6
84 | 122 | 1377 | 70 | kW | 3.06
86 | 122 | 1377 | 72 | MBh | 21.5
86 | 122 | 1377 | 72 | S/T | 0.698
86 | 122 | 1377 | 72 | ∆T | 10.1
86 | 122 | 1377 | 72 | LDB | 75.9
86 | 122 | 1377 | 72 | LWB | 67.8
86 | 122 | 1377 | 72 | kW | 3.06
90 | 122 | 1377 | 75 | MBh | 21.5
90 | 122 | 1377 | 75 | S/T | 0.656
90 | 122 | 1377 | 75 | ∆T | 9.5
90 | 122 | 1377 | 75 | LDB | 80.5
90 | 122 | 1377 | 75 | LWB | 71.1
90 | 122 | 1377 | 75 | kW | 3.06

## RZA18AAVJU - FTA18AAVJUD
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 600 | 57 | MBh | 11.2 | 64 | 60 | 61 | 25.2 | 2.24
68 | 23 | 600 | 57 | S/T | 0.871 | 64 | 60 | 65 | 23.3 | 2.02
68 | 23 | 600 | 57 | ∆T | 15.1 | 64 | 60 | 68 | 21.9 | 1.87
68 | 23 | 600 | 57 | LDB | 52.9 | 64 | 60 | 70 | 21 | 1.77
68 | 23 | 600 | 57 | LWB | 49.9 | 64 | 60 | 72 | 20.1 | 1.69
68 | 23 | 600 | 57 | kW | 0.43 | 64 | 60 | 75 | 18.7 | 1.57
72 | 23 | 600 | 61 | MBh | 13.6 | 60 | 56 | 61 | 25.2 | 2.35
72 | 23 | 600 | 61 | S/T | 0.809 | 60 | 56 | 65 | 23.3 | 2.11
72 | 23 | 600 | 61 | ∆T | 17 | 60 | 56 | 68 | 21.9 | 1.94
72 | 23 | 600 | 61 | LDB | 55 | 60 | 56 | 70 | 21 | 1.84
72 | 23 | 600 | 61 | LWB | 53 | 60 | 56 | 72 | 20.1 | 1.75
72 | 23 | 600 | 61 | kW | 0.53 | 60 | 56 | 75 | 18.7 | 1.62
77 | 23 | 600 | 64 | MBh | 15.4 | 57 | 53 | 61 | 25.2 | 2.45
77 | 23 | 600 | 64 | S/T | 0.76 | 57 | 53 | 65 | 23.3 | 2.19
77 | 23 | 600 | 64 | ∆T | 18.1 | 57 | 53 | 68 | 21.9 | 2.01
77 | 23 | 600 | 64 | LDB | 58.9 | 57 | 53 | 70 | 21 | 1.9
77 | 23 | 600 | 64 | LWB | 55.5 | 57 | 53 | 72 | 20.1 | 1.8
77 | 23 | 600 | 64 | kW | 0.61 | 57 | 53 | 75 | 18.7 | 1.66
80 | 23 | 600 | 67 | MBh | 17.2 | 54 | 50 | 61 | 25.2 | 2.55
80 | 23 | 600 | 67 | S/T | 0.703 | 54 | 50 | 65 | 23.3 | 2.27
80 | 23 | 600 | 67 | ∆T | 18.7 | 54 | 50 | 68 | 21.9 | 2.08
80 | 23 | 600 | 67 | LDB | 61.3 | 54 | 50 | 70 | 21 | 1.96
80 | 23 | 600 | 67 | LWB | 58 | 54 | 50 | 72 | 20.1 | 1.86
80 | 23 | 600 | 67 | kW | 0.69 | 54 | 50 | 75 | 18.7 | 1.71
84 | 23 | 600 | 70 | MBh | 19 | 51 | 47 | 61 | 25.2 | 2.66
84 | 23 | 600 | 70 | S/T | 0.668 | 51 | 47 | 65 | 23.3 | 2.36
84 | 23 | 600 | 70 | ∆T | 19.6 | 51 | 47 | 68 | 21.9 | 2.16
84 | 23 | 600 | 70 | LDB | 64.4 | 51 | 47 | 70 | 21 | 2.03
84 | 23 | 600 | 70 | LWB | 60.7 | 51 | 47 | 72 | 20.1 | 1.92
84 | 23 | 600 | 70 | kW | 0.77 | 51 | 47 | 75 | 18.7 | 1.76
86 | 23 | 600 | 72 | MBh | 20.2 | 47 | 43 | 61 | 25.2 | 2.83
86 | 23 | 600 | 72 | S/T | 0.658 | 47 | 43 | 65 | 23.3 | 2.5
86 | 23 | 600 | 72 | ∆T | 20.5 | 47 | 43 | 68 | 21.9 | 2.28
86 | 23 | 600 | 72 | LDB | 65.5 | 47 | 43 | 70 | 21 | 2.14
86 | 23 | 600 | 72 | LWB | 62.5 | 47 | 43 | 72 | 20.1 | 2.01
86 | 23 | 600 | 72 | kW | 0.83 | 47 | 43 | 75 | 18.7 | 1.84
90 | 23 | 600 | 75 | MBh | 22 | 44 | 40 | 61 | 25.2 | 2.97
90 | 23 | 600 | 75 | S/T | 0.632 | 44 | 40 | 65 | 23.3 | 2.61
90 | 23 | 600 | 75 | ∆T | 21.5 | 44 | 40 | 68 | 21.9 | 2.37
90 | 23 | 600 | 75 | LDB | 68.5 | 44 | 40 | 70 | 21 | 2.23
90 | 23 | 600 | 75 | LWB | 65.3 | 44 | 40 | 72 | 20.1 | 2.09
90 | 23 | 600 | 75 | kW | 0.92 | 44 | 40 | 75 | 18.7 | 1.9
68 | 30 | 600 | 57 | MBh | 11.2 | 39 | 36 | 61 | 25.2 | 3.18
68 | 30 | 600 | 57 | S/T | 0.871 | 39 | 36 | 65 | 23.3 | 2.79
68 | 30 | 600 | 57 | ∆T | 15.1 | 39 | 36 | 68 | 21.9 | 2.52
68 | 30 | 600 | 57 | LDB | 52.9 | 39 | 36 | 70 | 21 | 2.36
68 | 30 | 600 | 57 | LWB | 49.9 | 39 | 36 | 72 | 20.1 | 2.21
68 | 30 | 600 | 57 | kW | 0.44 | 39 | 36 | 75 | 18.7 | 2
72 | 30 | 600 | 61 | MBh | 13.6 | 35 | 32 | 61 | 25.2 | 3.39
72 | 30 | 600 | 61 | S/T | 0.809 | 35 | 32 | 65 | 23.3 | 2.99
72 | 30 | 600 | 61 | ∆T | 17 | 35 | 32 | 68 | 21.9 | 2.7
72 | 30 | 600 | 61 | LDB | 55 | 35 | 32 | 70 | 21 | 2.52
72 | 30 | 600 | 61 | LWB | 53 | 35 | 32 | 72 | 20.1 | 2.35
72 | 30 | 600 | 61 | kW | 0.55 | 35 | 32 | 75 | 18.7 | 2.11
77 | 30 | 600 | 64 | MBh | 15.4 | 30 | 28 | 61 | 25.2 | 3.36
77 | 30 | 600 | 64 | S/T | 0.76 | 30 | 28 | 65 | 23.3 | 3.22
77 | 30 | 600 | 64 | ∆T | 18.1 | 30 | 28 | 68 | 21.9 | 2.9
77 | 30 | 600 | 64 | LDB | 58.9 | 30 | 28 | 70 | 21 | 2.7
77 | 30 | 600 | 64 | LWB | 55.5 | 30 | 28 | 72 | 20.1 | 2.51
77 | 30 | 600 | 64 | kW | 0.63 | 30 | 28 | 75 | 18.7 | 2.25
80 | 30 | 600 | 67 | MBh | 17.2 | 26 | 24 | 61 | 25.2 | 3.33
80 | 30 | 600 | 67 | S/T | 0.703 | 26 | 24 | 65 | 23.3 | 3.38
80 | 30 | 600 | 67 | ∆T | 18.7 | 26 | 24 | 68 | 21.9 | 3.13
80 | 30 | 600 | 67 | LDB | 61.3 | 26 | 24 | 70 | 21 | 2.91
80 | 30 | 600 | 67 | LWB | 58 | 26 | 24 | 72 | 20.1 | 2.7
80 | 30 | 600 | 67 | kW | 0.71 | 26 | 24 | 75 | 18.7 | 2.4
84 | 30 | 600 | 70 | MBh | 19 | 22 | 20 | 61 | 25.2 | 3.29
84 | 30 | 600 | 70 | S/T | 0.668 | 22 | 20 | 65 | 23.3 | 3.35
84 | 30 | 600 | 70 | ∆T | 19.6 | 22 | 20 | 68 | 21.9 | 3.39
84 | 30 | 600 | 70 | LDB | 64.4 | 22 | 20 | 70 | 21 | 3.15
84 | 30 | 600 | 70 | LWB | 60.7 | 22 | 20 | 72 | 20.1 | 2.92
84 | 30 | 600 | 70 | kW | 0.8 | 22 | 20 | 75 | 18.7 | 2.59
86 | 30 | 600 | 72 | MBh | 20.2 | 19 | 18 | 61 | 25.2 | 3.27
86 | 30 | 600 | 72 | S/T | 0.658 | 19 | 18 | 65 | 23.3 | 3.33
86 | 30 | 600 | 72 | ∆T | 20.5 | 19 | 18 | 68 | 21.9 | 3.37
86 | 30 | 600 | 72 | LDB | 65.5 | 19 | 18 | 70 | 21 | 3.29
86 | 30 | 600 | 72 | LWB | 62.5 | 19 | 18 | 72 | 20.1 | 3.04
86 | 30 | 600 | 72 | kW | 0.86 | 19 | 18 | 75 | 18.7 | 2.69
90 | 30 | 600 | 75 | MBh | 22 | 17 | 16 | 61 | 24.8 | 3.25
90 | 30 | 600 | 75 | S/T | 0.632 | 17 | 16 | 65 | 23.3 | 3.3
90 | 30 | 600 | 75 | ∆T | 21.5 | 17 | 16 | 68 | 21.9 | 3.35
90 | 30 | 600 | 75 | LDB | 68.5 | 17 | 16 | 70 | 21 | 3.37
90 | 30 | 600 | 75 | LWB | 65.3 | 17 | 16 | 72 | 20.1 | 3.21
90 | 30 | 600 | 75 | kW | 0.95 | 17 | 16 | 75 | 18.7 | 2.84
68 | 40 | 600 | 57 | MBh | 11.2 | 15 | 14 | 61 | 24.3 | 3.23
68 | 40 | 600 | 57 | S/T | 0.871 | 15 | 14 | 65 | 23.3 | 3.29
68 | 40 | 600 | 57 | ∆T | 15.1 | 15 | 14 | 68 | 21.9 | 3.33
68 | 40 | 600 | 57 | LDB | 52.9 | 15 | 14 | 70 | 21 | 3.36
68 | 40 | 600 | 57 | LWB | 49.9 | 15 | 14 | 72 | 20.1 | 3.33
68 | 40 | 600 | 57 | kW | 0.46 | 15 | 14 | 75 | 18.7 | 2.93
72 | 40 | 600 | 61 | MBh | 13.6 | 13 | 12 | 61 | 23.6 | 3.21
72 | 40 | 600 | 61 | S/T | 0.809 | 13 | 12 | 65 | 23.3 | 3.27
72 | 40 | 600 | 61 | ∆T | 17 | 13 | 12 | 68 | 21.9 | 3.31
72 | 40 | 600 | 61 | LDB | 55 | 13 | 12 | 70 | 21 | 3.34
72 | 40 | 600 | 61 | LWB | 53 | 13 | 12 | 72 | 20.1 | 3.37
72 | 40 | 600 | 61 | kW | 0.57 | 13 | 12 | 75 | 18.7 | 3.07
77 | 40 | 600 | 64 | MBh | 15.4 | 10 | 9 | 61 | 22.3 | 3.16
77 | 40 | 600 | 64 | S/T | 0.76 | 10 | 9 | 65 | 22.3 | 3.23
77 | 40 | 600 | 64 | ∆T | 18.1 | 10 | 9 | 68 | 21.9 | 3.27
77 | 40 | 600 | 64 | LDB | 58.9 | 10 | 9 | 70 | 21 | 3.3
77 | 40 | 600 | 64 | LWB | 55.5 | 10 | 9 | 72 | 20.1 | 3.34
77 | 40 | 600 | 64 | kW | 0.66 | 10 | 9 | 75 | 18.7 | 3.34
80 | 40 | 600 | 67 | MBh | 17.2 | 6 | 5 | 61 | 21 | 3.08
80 | 40 | 600 | 67 | S/T | 0.703 | 6 | 5 | 65 | 21 | 3.08
80 | 40 | 600 | 67 | ∆T | 18.7 | 6 | 5 | 68 | 21 | 3.08
80 | 40 | 600 | 67 | LDB | 61.3 | 6 | 5 | 70 | 21 | 3.08
80 | 40 | 600 | 67 | LWB | 58 | 6 | 5 | 72 | 20.1 | 3.08
80 | 40 | 600 | 67 | kW | 0.75 | 6 | 5 | 75 | 18.7 | 3.08
84 | 40 | 600 | 70 | MBh | 19 | -2 | -2 | 61 | 18.4 | 2.82
84 | 40 | 600 | 70 | S/T | 0.668 | -2 | -2 | 65 | 18.4 | 2.82
84 | 40 | 600 | 70 | ∆T | 19.6 | -2 | -2 | 68 | 18.4 | 2.82
84 | 40 | 600 | 70 | LDB | 64.4 | -2 | -2 | 70 | 18.4 | 2.82
84 | 40 | 600 | 70 | LWB | 60.7 | -2 | -2 | 72 | 18.4 | 2.82
84 | 40 | 600 | 70 | kW | 0.84 | -2 | -2 | 75 | 18.4 | 2.82
86 | 40 | 600 | 72 | MBh | 20.2 | -4 | -4 | 61 | 17.7 | 2.75
86 | 40 | 600 | 72 | S/T | 0.658 | -4 | -4 | 65 | 17.7 | 2.75
86 | 40 | 600 | 72 | ∆T | 20.5 | -4 | -4 | 68 | 17.7 | 2.75
86 | 40 | 600 | 72 | LDB | 65.5 | -4 | -4 | 70 | 17.7 | 2.75
86 | 40 | 600 | 72 | LWB | 62.5 | -4 | -4 | 72 | 17.7 | 2.75
86 | 40 | 600 | 72 | kW | 0.9 | -4 | -4 | 75 | 17.7 | 2.75
90 | 40 | 600 | 75 | MBh | 22
90 | 40 | 600 | 75 | S/T | 0.632
90 | 40 | 600 | 75 | ∆T | 21.5
90 | 40 | 600 | 75 | LDB | 68.5
90 | 40 | 600 | 75 | LWB | 65.3
90 | 40 | 600 | 75 | kW | 1
68 | 50 | 600 | 57 | MBh | 11.2
68 | 50 | 600 | 57 | S/T | 0.871
68 | 50 | 600 | 57 | ∆T | 15.1
68 | 50 | 600 | 57 | LDB | 52.9
68 | 50 | 600 | 57 | LWB | 49.9
68 | 50 | 600 | 57 | kW | 0.49
72 | 50 | 600 | 61 | MBh | 13.6
72 | 50 | 600 | 61 | S/T | 0.809
72 | 50 | 600 | 61 | ∆T | 17
72 | 50 | 600 | 61 | LDB | 55
72 | 50 | 600 | 61 | LWB | 53
72 | 50 | 600 | 61 | kW | 0.6
77 | 50 | 600 | 64 | MBh | 15.4
77 | 50 | 600 | 64 | S/T | 0.76
77 | 50 | 600 | 64 | ∆T | 18.1
77 | 50 | 600 | 64 | LDB | 58.9
77 | 50 | 600 | 64 | LWB | 55.5
77 | 50 | 600 | 64 | kW | 0.69
80 | 50 | 600 | 67 | MBh | 17.2
80 | 50 | 600 | 67 | S/T | 0.703
80 | 50 | 600 | 67 | ∆T | 18.7
80 | 50 | 600 | 67 | LDB | 61.3
80 | 50 | 600 | 67 | LWB | 58
80 | 50 | 600 | 67 | kW | 0.79
84 | 50 | 600 | 70 | MBh | 19
84 | 50 | 600 | 70 | S/T | 0.668
84 | 50 | 600 | 70 | ∆T | 19.6
84 | 50 | 600 | 70 | LDB | 64.4
84 | 50 | 600 | 70 | LWB | 60.7
84 | 50 | 600 | 70 | kW | 0.88
86 | 50 | 600 | 72 | MBh | 20.2
86 | 50 | 600 | 72 | S/T | 0.658
86 | 50 | 600 | 72 | ∆T | 20.5
86 | 50 | 600 | 72 | LDB | 65.5
86 | 50 | 600 | 72 | LWB | 62.5
86 | 50 | 600 | 72 | kW | 0.95
90 | 50 | 600 | 75 | MBh | 22
90 | 50 | 600 | 75 | S/T | 0.632
90 | 50 | 600 | 75 | ∆T | 21.5
90 | 50 | 600 | 75 | LDB | 68.5
90 | 50 | 600 | 75 | LWB | 65.3
90 | 50 | 600 | 75 | kW | 1.05
68 | 54 | 600 | 57 | MBh | 11.2
68 | 54 | 600 | 57 | S/T | 0.871
68 | 54 | 600 | 57 | ∆T | 15.1
68 | 54 | 600 | 57 | LDB | 52.9
68 | 54 | 600 | 57 | LWB | 49.9
68 | 54 | 600 | 57 | kW | 0.5
72 | 54 | 600 | 61 | MBh | 13.6
72 | 54 | 600 | 61 | S/T | 0.809
72 | 54 | 600 | 61 | ∆T | 17
72 | 54 | 600 | 61 | LDB | 55
72 | 54 | 600 | 61 | LWB | 53
72 | 54 | 600 | 61 | kW | 0.61
77 | 54 | 600 | 64 | MBh | 15.4
77 | 54 | 600 | 64 | S/T | 0.76
77 | 54 | 600 | 64 | ∆T | 18.1
77 | 54 | 600 | 64 | LDB | 58.9
77 | 54 | 600 | 64 | LWB | 55.5
77 | 54 | 600 | 64 | kW | 0.71
80 | 54 | 600 | 67 | MBh | 17.2
80 | 54 | 600 | 67 | S/T | 0.703
80 | 54 | 600 | 67 | ∆T | 18.7
80 | 54 | 600 | 67 | LDB | 61.3
80 | 54 | 600 | 67 | LWB | 58
80 | 54 | 600 | 67 | kW | 0.8
84 | 54 | 600 | 70 | MBh | 19
84 | 54 | 600 | 70 | S/T | 0.668
84 | 54 | 600 | 70 | ∆T | 19.6
84 | 54 | 600 | 70 | LDB | 64.4
84 | 54 | 600 | 70 | LWB | 60.7
84 | 54 | 600 | 70 | kW | 0.9
86 | 54 | 600 | 72 | MBh | 20.2
86 | 54 | 600 | 72 | S/T | 0.658
86 | 54 | 600 | 72 | ∆T | 20.5
86 | 54 | 600 | 72 | LDB | 65.5
86 | 54 | 600 | 72 | LWB | 62.5
86 | 54 | 600 | 72 | kW | 0.97
90 | 54 | 600 | 75 | MBh | 22
90 | 54 | 600 | 75 | S/T | 0.632
90 | 54 | 600 | 75 | ∆T | 21.5
90 | 54 | 600 | 75 | LDB | 68.5
90 | 54 | 600 | 75 | LWB | 65.3
90 | 54 | 600 | 75 | kW | 1.07
68 | 58 | 600 | 57 | MBh | 11.2
68 | 58 | 600 | 57 | S/T | 0.871
68 | 58 | 600 | 57 | ∆T | 15.1
68 | 58 | 600 | 57 | LDB | 52.9
68 | 58 | 600 | 57 | LWB | 49.9
68 | 58 | 600 | 57 | kW | 0.5
72 | 58 | 600 | 61 | MBh | 13.6
72 | 58 | 600 | 61 | S/T | 0.809
72 | 58 | 600 | 61 | ∆T | 17
72 | 58 | 600 | 61 | LDB | 55
72 | 58 | 600 | 61 | LWB | 53
72 | 58 | 600 | 61 | kW | 0.63
77 | 58 | 600 | 64 | MBh | 15.4
77 | 58 | 600 | 64 | S/T | 0.76
77 | 58 | 600 | 64 | ∆T | 18.1
77 | 58 | 600 | 64 | LDB | 58.9
77 | 58 | 600 | 64 | LWB | 55.5
77 | 58 | 600 | 64 | kW | 0.72
80 | 58 | 600 | 67 | MBh | 17.2
80 | 58 | 600 | 67 | S/T | 0.703
80 | 58 | 600 | 67 | ∆T | 18.7
80 | 58 | 600 | 67 | LDB | 61.3
80 | 58 | 600 | 67 | LWB | 58
80 | 58 | 600 | 67 | kW | 0.82
84 | 58 | 600 | 70 | MBh | 19
84 | 58 | 600 | 70 | S/T | 0.668
84 | 58 | 600 | 70 | ∆T | 19.6
84 | 58 | 600 | 70 | LDB | 64.4
84 | 58 | 600 | 70 | LWB | 60.7
84 | 58 | 600 | 70 | kW | 0.92
86 | 58 | 600 | 72 | MBh | 20.2
86 | 58 | 600 | 72 | S/T | 0.658
86 | 58 | 600 | 72 | ∆T | 20.5
86 | 58 | 600 | 72 | LDB | 65.5
86 | 58 | 600 | 72 | LWB | 62.5
86 | 58 | 600 | 72 | kW | 0.99
90 | 58 | 600 | 75 | MBh | 21.8
90 | 58 | 600 | 75 | S/T | 0.633
90 | 58 | 600 | 75 | ∆T | 21.3
90 | 58 | 600 | 75 | LDB | 68.7
90 | 58 | 600 | 75 | LWB | 65.4
90 | 58 | 600 | 75 | kW | 1.07
68 | 62 | 600 | 57 | MBh | 11.2
68 | 62 | 600 | 57 | S/T | 0.871
68 | 62 | 600 | 57 | ∆T | 15.1
68 | 62 | 600 | 57 | LDB | 52.9
68 | 62 | 600 | 57 | LWB | 49.9
68 | 62 | 600 | 57 | kW | 0.52
72 | 62 | 600 | 61 | MBh | 13.6
72 | 62 | 600 | 61 | S/T | 0.809
72 | 62 | 600 | 61 | ∆T | 17
72 | 62 | 600 | 61 | LDB | 55
72 | 62 | 600 | 61 | LWB | 53
72 | 62 | 600 | 61 | kW | 0.64
77 | 62 | 600 | 64 | MBh | 15.4
77 | 62 | 600 | 64 | S/T | 0.76
77 | 62 | 600 | 64 | ∆T | 18.1
77 | 62 | 600 | 64 | LDB | 58.9
77 | 62 | 600 | 64 | LWB | 55.5
77 | 62 | 600 | 64 | kW | 0.74
80 | 62 | 600 | 67 | MBh | 17.2
80 | 62 | 600 | 67 | S/T | 0.703
80 | 62 | 600 | 67 | ∆T | 18.7
80 | 62 | 600 | 67 | LDB | 61.3
80 | 62 | 600 | 67 | LWB | 58
80 | 62 | 600 | 67 | kW | 0.84
84 | 62 | 600 | 70 | MBh | 19
84 | 62 | 600 | 70 | S/T | 0.668
84 | 62 | 600 | 70 | ∆T | 19.6
84 | 62 | 600 | 70 | LDB | 64.4
84 | 62 | 600 | 70 | LWB | 60.7
84 | 62 | 600 | 70 | kW | 0.94
86 | 62 | 600 | 72 | MBh | 20.2
86 | 62 | 600 | 72 | S/T | 0.658
86 | 62 | 600 | 72 | ∆T | 20.5
86 | 62 | 600 | 72 | LDB | 65.5
86 | 62 | 600 | 72 | LWB | 62.5
86 | 62 | 600 | 72 | kW | 1.01
90 | 62 | 600 | 75 | MBh | 21.5
90 | 62 | 600 | 75 | S/T | 0.633
90 | 62 | 600 | 75 | ∆T | 21
90 | 62 | 600 | 75 | LDB | 69
90 | 62 | 600 | 75 | LWB | 65.6
90 | 62 | 600 | 75 | kW | 1.1
68 | 66 | 600 | 57 | MBh | 11.2
68 | 66 | 600 | 57 | S/T | 0.871
68 | 66 | 600 | 57 | ∆T | 15.1
68 | 66 | 600 | 57 | LDB | 52.9
68 | 66 | 600 | 57 | LWB | 49.9
68 | 66 | 600 | 57 | kW | 0.53
72 | 66 | 600 | 61 | MBh | 13.6
72 | 66 | 600 | 61 | S/T | 0.809
72 | 66 | 600 | 61 | ∆T | 17
72 | 66 | 600 | 61 | LDB | 55
72 | 66 | 600 | 61 | LWB | 53
72 | 66 | 600 | 61 | kW | 0.65
77 | 66 | 600 | 64 | MBh | 15.4
77 | 66 | 600 | 64 | S/T | 0.76
77 | 66 | 600 | 64 | ∆T | 18.1
77 | 66 | 600 | 64 | LDB | 58.9
77 | 66 | 600 | 64 | LWB | 55.5
77 | 66 | 600 | 64 | kW | 0.75
80 | 66 | 600 | 67 | MBh | 17.2
80 | 66 | 600 | 67 | S/T | 0.703
80 | 66 | 600 | 67 | ∆T | 18.7
80 | 66 | 600 | 67 | LDB | 61.3
80 | 66 | 600 | 67 | LWB | 58
80 | 66 | 600 | 67 | kW | 0.86
84 | 66 | 600 | 70 | MBh | 19
84 | 66 | 600 | 70 | S/T | 0.668
84 | 66 | 600 | 70 | ∆T | 19.6
84 | 66 | 600 | 70 | LDB | 64.4
84 | 66 | 600 | 70 | LWB | 60.7
84 | 66 | 600 | 70 | kW | 0.99
86 | 66 | 600 | 72 | MBh | 20.2
86 | 66 | 600 | 72 | S/T | 0.658
86 | 66 | 600 | 72 | ∆T | 20.5
86 | 66 | 600 | 72 | LDB | 65.5
86 | 66 | 600 | 72 | LWB | 62.5
86 | 66 | 600 | 72 | kW | 1.09
90 | 66 | 600 | 75 | MBh | 21.2
90 | 66 | 600 | 75 | S/T | 0.632
90 | 66 | 600 | 75 | ∆T | 20.7
90 | 66 | 600 | 75 | LDB | 69.3
90 | 66 | 600 | 75 | LWB | 65.7
90 | 66 | 600 | 75 | kW | 1.16
68 | 70 | 600 | 57 | MBh | 11.2
68 | 70 | 600 | 57 | S/T | 0.871
68 | 70 | 600 | 57 | ∆T | 15.1
68 | 70 | 600 | 57 | LDB | 52.9
68 | 70 | 600 | 57 | LWB | 49.9
68 | 70 | 600 | 57 | kW | 0.54
72 | 70 | 600 | 61 | MBh | 13.6
72 | 70 | 600 | 61 | S/T | 0.809
72 | 70 | 600 | 61 | ∆T | 17
72 | 70 | 600 | 61 | LDB | 55
72 | 70 | 600 | 61 | LWB | 53
72 | 70 | 600 | 61 | kW | 0.67
77 | 70 | 600 | 64 | MBh | 15.4
77 | 70 | 600 | 64 | S/T | 0.76
77 | 70 | 600 | 64 | ∆T | 18.1
77 | 70 | 600 | 64 | LDB | 58.9
77 | 70 | 600 | 64 | LWB | 55.5
77 | 70 | 600 | 64 | kW | 0.79
80 | 70 | 600 | 67 | MBh | 17.2
80 | 70 | 600 | 67 | S/T | 0.703
80 | 70 | 600 | 67 | ∆T | 18.7
80 | 70 | 600 | 67 | LDB | 61.3
80 | 70 | 600 | 67 | LWB | 58
80 | 70 | 600 | 67 | kW | 0.93
84 | 70 | 600 | 70 | MBh | 19
84 | 70 | 600 | 70 | S/T | 0.668
84 | 70 | 600 | 70 | ∆T | 19.6
84 | 70 | 600 | 70 | LDB | 64.4
84 | 70 | 600 | 70 | LWB | 60.7
84 | 70 | 600 | 70 | kW | 1.08
86 | 70 | 600 | 72 | MBh | 20.2
86 | 70 | 600 | 72 | S/T | 0.658
86 | 70 | 600 | 72 | ∆T | 20.5
86 | 70 | 600 | 72 | LDB | 65.5
86 | 70 | 600 | 72 | LWB | 62.5
86 | 70 | 600 | 72 | kW | 1.18
90 | 70 | 600 | 75 | MBh | 20.9
90 | 70 | 600 | 75 | S/T | 0.632
90 | 70 | 600 | 75 | ∆T | 20.4
90 | 70 | 600 | 75 | LDB | 69.6
90 | 70 | 600 | 75 | LWB | 65.9
90 | 70 | 600 | 75 | kW | 1.22
68 | 72 | 600 | 57 | MBh | 11.2
68 | 72 | 600 | 57 | S/T | 0.871
68 | 72 | 600 | 57 | ∆T | 15.1
68 | 72 | 600 | 57 | LDB | 52.9
68 | 72 | 600 | 57 | LWB | 49.9
68 | 72 | 600 | 57 | kW | 0.54
72 | 72 | 600 | 61 | MBh | 13.6
72 | 72 | 600 | 61 | S/T | 0.809
72 | 72 | 600 | 61 | ∆T | 17
72 | 72 | 600 | 61 | LDB | 55
72 | 72 | 600 | 61 | LWB | 53
72 | 72 | 600 | 61 | kW | 0.69
77 | 72 | 600 | 64 | MBh | 15.4
77 | 72 | 600 | 64 | S/T | 0.76
77 | 72 | 600 | 64 | ∆T | 18.1
77 | 72 | 600 | 64 | LDB | 58.9
77 | 72 | 600 | 64 | LWB | 55.5
77 | 72 | 600 | 64 | kW | 0.82
80 | 72 | 600 | 67 | MBh | 17.2
80 | 72 | 600 | 67 | S/T | 0.703
80 | 72 | 600 | 67 | ∆T | 18.7
80 | 72 | 600 | 67 | LDB | 61.3
80 | 72 | 600 | 67 | LWB | 58
80 | 72 | 600 | 67 | kW | 0.96
84 | 72 | 600 | 70 | MBh | 19
84 | 72 | 600 | 70 | S/T | 0.668
84 | 72 | 600 | 70 | ∆T | 19.6
84 | 72 | 600 | 70 | LDB | 64.4
84 | 72 | 600 | 70 | LWB | 60.7
84 | 72 | 600 | 70 | kW | 1.12
86 | 72 | 600 | 72 | MBh | 20.2
86 | 72 | 600 | 72 | S/T | 0.658
86 | 72 | 600 | 72 | ∆T | 20.5
86 | 72 | 600 | 72 | LDB | 65.5
86 | 72 | 600 | 72 | LWB | 62.5
86 | 72 | 600 | 72 | kW | 1.23
90 | 72 | 600 | 75 | MBh | 20.7
90 | 72 | 600 | 75 | S/T | 0.633
90 | 72 | 600 | 75 | ∆T | 20.2
90 | 72 | 600 | 75 | LDB | 69.8
90 | 72 | 600 | 75 | LWB | 66
90 | 72 | 600 | 75 | kW | 1.25
68 | 75 | 600 | 57 | MBh | 11.2
68 | 75 | 600 | 57 | S/T | 0.871
68 | 75 | 600 | 57 | ∆T | 15.1
68 | 75 | 600 | 57 | LDB | 52.9
68 | 75 | 600 | 57 | LWB | 49.9
68 | 75 | 600 | 57 | kW | 0.56
72 | 75 | 600 | 61 | MBh | 13.6
72 | 75 | 600 | 61 | S/T | 0.809
72 | 75 | 600 | 61 | ∆T | 17
72 | 75 | 600 | 61 | LDB | 55
72 | 75 | 600 | 61 | LWB | 53
72 | 75 | 600 | 61 | kW | 0.73
77 | 75 | 600 | 64 | MBh | 15.4
77 | 75 | 600 | 64 | S/T | 0.76
77 | 75 | 600 | 64 | ∆T | 18.1
77 | 75 | 600 | 64 | LDB | 58.9
77 | 75 | 600 | 64 | LWB | 55.5
77 | 75 | 600 | 64 | kW | 0.87
80 | 75 | 600 | 67 | MBh | 17.2
80 | 75 | 600 | 67 | S/T | 0.703
80 | 75 | 600 | 67 | ∆T | 18.7
80 | 75 | 600 | 67 | LDB | 61.3
80 | 75 | 600 | 67 | LWB | 58
80 | 75 | 600 | 67 | kW | 1.02
84 | 75 | 600 | 70 | MBh | 19
84 | 75 | 600 | 70 | S/T | 0.668
84 | 75 | 600 | 70 | ∆T | 19.6
84 | 75 | 600 | 70 | LDB | 64.4
84 | 75 | 600 | 70 | LWB | 60.7
84 | 75 | 600 | 70 | kW | 1.18
86 | 75 | 600 | 72 | MBh | 20.1
86 | 75 | 600 | 72 | S/T | 0.662
86 | 75 | 600 | 72 | ∆T | 20.5
86 | 75 | 600 | 72 | LDB | 65.5
86 | 75 | 600 | 72 | LWB | 62.6
86 | 75 | 600 | 72 | kW | 1.29
90 | 75 | 600 | 75 | MBh | 20.5
90 | 75 | 600 | 75 | S/T | 0.629
90 | 75 | 600 | 75 | ∆T | 19.9
90 | 75 | 600 | 75 | LDB | 70.1
90 | 75 | 600 | 75 | LWB | 66
90 | 75 | 600 | 75 | kW | 1.3
68 | 79 | 600 | 57 | MBh | 11.2
68 | 79 | 600 | 57 | S/T | 0.871
68 | 79 | 600 | 57 | ∆T | 15.1
68 | 79 | 600 | 57 | LDB | 52.9
68 | 79 | 600 | 57 | LWB | 49.9
68 | 79 | 600 | 57 | kW | 0.6
72 | 79 | 600 | 61 | MBh | 13.6
72 | 79 | 600 | 61 | S/T | 0.809
72 | 79 | 600 | 61 | ∆T | 17
72 | 79 | 600 | 61 | LDB | 55
72 | 79 | 600 | 61 | LWB | 53
72 | 79 | 600 | 61 | kW | 0.78
77 | 79 | 600 | 64 | MBh | 15.4
77 | 79 | 600 | 64 | S/T | 0.76
77 | 79 | 600 | 64 | ∆T | 18.1
77 | 79 | 600 | 64 | LDB | 58.9
77 | 79 | 600 | 64 | LWB | 55.5
77 | 79 | 600 | 64 | kW | 0.93
80 | 79 | 600 | 67 | MBh | 17.2
80 | 79 | 600 | 67 | S/T | 0.703
80 | 79 | 600 | 67 | ∆T | 18.7
80 | 79 | 600 | 67 | LDB | 61.3
80 | 79 | 600 | 67 | LWB | 58
80 | 79 | 600 | 67 | kW | 1.1
84 | 79 | 600 | 70 | MBh | 19
84 | 79 | 600 | 70 | S/T | 0.668
84 | 79 | 600 | 70 | ∆T | 19.6
84 | 79 | 600 | 70 | LDB | 64.4
84 | 79 | 600 | 70 | LWB | 60.7
84 | 79 | 600 | 70 | kW | 1.28
86 | 79 | 600 | 72 | MBh | 19.8
86 | 79 | 600 | 72 | S/T | 0.657
86 | 79 | 600 | 72 | ∆T | 20.1
86 | 79 | 600 | 72 | LDB | 65.9
86 | 79 | 600 | 72 | LWB | 62.7
86 | 79 | 600 | 72 | kW | 1.35
90 | 79 | 600 | 75 | MBh | 20.1
90 | 79 | 600 | 75 | S/T | 0.632
90 | 79 | 600 | 75 | ∆T | 19.6
90 | 79 | 600 | 75 | LDB | 70.4
90 | 79 | 600 | 75 | LWB | 66.2
90 | 79 | 600 | 75 | kW | 1.36
68 | 83 | 600 | 57 | MBh | 11.2
68 | 83 | 600 | 57 | S/T | 0.871
68 | 83 | 600 | 57 | ∆T | 15.1
68 | 83 | 600 | 57 | LDB | 52.9
68 | 83 | 600 | 57 | LWB | 49.9
68 | 83 | 600 | 57 | kW | 0.65
72 | 83 | 600 | 61 | MBh | 13.6
72 | 83 | 600 | 61 | S/T | 0.809
72 | 83 | 600 | 61 | ∆T | 17
72 | 83 | 600 | 61 | LDB | 55
72 | 83 | 600 | 61 | LWB | 53
72 | 83 | 600 | 61 | kW | 0.84
77 | 83 | 600 | 64 | MBh | 15.4
77 | 83 | 600 | 64 | S/T | 0.76
77 | 83 | 600 | 64 | ∆T | 18.1
77 | 83 | 600 | 64 | LDB | 58.9
77 | 83 | 600 | 64 | LWB | 55.5
77 | 83 | 600 | 64 | kW | 1.01
80 | 83 | 600 | 67 | MBh | 17.2
80 | 83 | 600 | 67 | S/T | 0.703
80 | 83 | 600 | 67 | ∆T | 18.7
80 | 83 | 600 | 67 | LDB | 61.3
80 | 83 | 600 | 67 | LWB | 58
80 | 83 | 600 | 67 | kW | 1.18
84 | 83 | 600 | 70 | MBh | 19
84 | 83 | 600 | 70 | S/T | 0.668
84 | 83 | 600 | 70 | ∆T | 19.6
84 | 83 | 600 | 70 | LDB | 64.4
84 | 83 | 600 | 70 | LWB | 60.7
84 | 83 | 600 | 70 | kW | 1.38
86 | 83 | 600 | 72 | MBh | 19.5
86 | 83 | 600 | 72 | S/T | 0.656
86 | 83 | 600 | 72 | ∆T | 19.8
86 | 83 | 600 | 72 | LDB | 66.2
86 | 83 | 600 | 72 | LWB | 62.9
86 | 83 | 600 | 72 | kW | 1.41
90 | 83 | 600 | 75 | MBh | 19.8
90 | 83 | 600 | 75 | S/T | 0.631
90 | 83 | 600 | 75 | ∆T | 19.3
90 | 83 | 600 | 75 | LDB | 70.7
90 | 83 | 600 | 75 | LWB | 66.4
90 | 83 | 600 | 75 | kW | 1.42
68 | 87 | 600 | 57 | MBh | 11.2
68 | 87 | 600 | 57 | S/T | 0.871
68 | 87 | 600 | 57 | ∆T | 15.1
68 | 87 | 600 | 57 | LDB | 52.9
68 | 87 | 600 | 57 | LWB | 49.9
68 | 87 | 600 | 57 | kW | 0.69
72 | 87 | 600 | 61 | MBh | 13.6
72 | 87 | 600 | 61 | S/T | 0.809
72 | 87 | 600 | 61 | ∆T | 17
72 | 87 | 600 | 61 | LDB | 55
72 | 87 | 600 | 61 | LWB | 53
72 | 87 | 600 | 61 | kW | 0.9
77 | 87 | 600 | 64 | MBh | 15.4
77 | 87 | 600 | 64 | S/T | 0.76
77 | 87 | 600 | 64 | ∆T | 18.1
77 | 87 | 600 | 64 | LDB | 58.9
77 | 87 | 600 | 64 | LWB | 55.5
77 | 87 | 600 | 64 | kW | 1.08
80 | 87 | 600 | 67 | MBh | 17.2
80 | 87 | 600 | 67 | S/T | 0.703
80 | 87 | 600 | 67 | ∆T | 18.7
80 | 87 | 600 | 67 | LDB | 61.3
80 | 87 | 600 | 67 | LWB | 58
80 | 87 | 600 | 67 | kW | 1.27
84 | 87 | 600 | 70 | MBh | 18.9
84 | 87 | 600 | 70 | S/T | 0.672
84 | 87 | 600 | 70 | ∆T | 19.6
84 | 87 | 600 | 70 | LDB | 64.4
84 | 87 | 600 | 70 | LWB | 60.7
84 | 87 | 600 | 70 | kW | 1.47
86 | 87 | 600 | 72 | MBh | 19.1
86 | 87 | 600 | 72 | S/T | 0.66
86 | 87 | 600 | 72 | ∆T | 19.4
86 | 87 | 600 | 72 | LDB | 66.6
86 | 87 | 600 | 72 | LWB | 63.1
86 | 87 | 600 | 72 | kW | 1.47
90 | 87 | 600 | 75 | MBh | 19.5
90 | 87 | 600 | 75 | S/T | 0.631
90 | 87 | 600 | 75 | ∆T | 19
90 | 87 | 600 | 75 | LDB | 71
90 | 87 | 600 | 75 | LWB | 66.5
90 | 87 | 600 | 75 | kW | 1.48
68 | 91 | 600 | 57 | MBh | 11.2
68 | 91 | 600 | 57 | S/T | 0.871
68 | 91 | 600 | 57 | ∆T | 15.1
68 | 91 | 600 | 57 | LDB | 52.9
68 | 91 | 600 | 57 | LWB | 49.9
68 | 91 | 600 | 57 | kW | 0.74
72 | 91 | 600 | 61 | MBh | 13.6
72 | 91 | 600 | 61 | S/T | 0.809
72 | 91 | 600 | 61 | ∆T | 17
72 | 91 | 600 | 61 | LDB | 55
72 | 91 | 600 | 61 | LWB | 53
72 | 91 | 600 | 61 | kW | 0.97
77 | 91 | 600 | 64 | MBh | 15.4
77 | 91 | 600 | 64 | S/T | 0.76
77 | 91 | 600 | 64 | ∆T | 18.1
77 | 91 | 600 | 64 | LDB | 58.9
77 | 91 | 600 | 64 | LWB | 55.5
77 | 91 | 600 | 64 | kW | 1.16
80 | 91 | 600 | 67 | MBh | 17.2
80 | 91 | 600 | 67 | S/T | 0.703
80 | 91 | 600 | 67 | ∆T | 18.7
80 | 91 | 600 | 67 | LDB | 61.3
80 | 91 | 600 | 67 | LWB | 58
80 | 91 | 600 | 67 | kW | 1.37
84 | 91 | 600 | 70 | MBh | 18.6
84 | 91 | 600 | 70 | S/T | 0.672
84 | 91 | 600 | 70 | ∆T | 19.3
84 | 91 | 600 | 70 | LDB | 64.7
84 | 91 | 600 | 70 | LWB | 60.9
84 | 91 | 600 | 70 | kW | 1.53
86 | 91 | 600 | 72 | MBh | 18.8
86 | 91 | 600 | 72 | S/T | 0.66
86 | 91 | 600 | 72 | ∆T | 19.1
86 | 91 | 600 | 72 | LDB | 66.9
86 | 91 | 600 | 72 | LWB | 63.2
86 | 91 | 600 | 72 | kW | 1.53
90 | 91 | 600 | 75 | MBh | 19.2
90 | 91 | 600 | 75 | S/T | 0.63
90 | 91 | 600 | 75 | ∆T | 18.7
90 | 91 | 600 | 75 | LDB | 71.3
90 | 91 | 600 | 75 | LWB | 66.7
90 | 91 | 600 | 75 | kW | 1.54
68 | 93 | 600 | 57 | MBh | 11.2
68 | 93 | 600 | 57 | S/T | 0.871
68 | 93 | 600 | 57 | ∆T | 15.1
68 | 93 | 600 | 57 | LDB | 52.9
68 | 93 | 600 | 57 | LWB | 49.9
68 | 93 | 600 | 57 | kW | 0.77
72 | 93 | 600 | 61 | MBh | 13.6
72 | 93 | 600 | 61 | S/T | 0.809
72 | 93 | 600 | 61 | ∆T | 17
72 | 93 | 600 | 61 | LDB | 55
72 | 93 | 600 | 61 | LWB | 53
72 | 93 | 600 | 61 | kW | 1
77 | 93 | 600 | 64 | MBh | 15.4
77 | 93 | 600 | 64 | S/T | 0.76
77 | 93 | 600 | 64 | ∆T | 18.1
77 | 93 | 600 | 64 | LDB | 58.9
77 | 93 | 600 | 64 | LWB | 55.5
77 | 93 | 600 | 64 | kW | 1.2
80 | 93 | 600 | 67 | MBh | 17.2
80 | 93 | 600 | 67 | S/T | 0.703
80 | 93 | 600 | 67 | ∆T | 18.7
80 | 93 | 600 | 67 | LDB | 61.3
80 | 93 | 600 | 67 | LWB | 58
80 | 93 | 600 | 67 | kW | 1.42
84 | 93 | 600 | 70 | MBh | 18.4
84 | 93 | 600 | 70 | S/T | 0.668
84 | 93 | 600 | 70 | ∆T | 19
84 | 93 | 600 | 70 | LDB | 65
84 | 93 | 600 | 70 | LWB | 61
84 | 93 | 600 | 70 | kW | 1.56
86 | 93 | 600 | 72 | MBh | 18.6
86 | 93 | 600 | 72 | S/T | 0.661
86 | 93 | 600 | 72 | ∆T | 19
86 | 93 | 600 | 72 | LDB | 67
86 | 93 | 600 | 72 | LWB | 63.3
86 | 93 | 600 | 72 | kW | 1.57
90 | 93 | 600 | 75 | MBh | 19
90 | 93 | 600 | 75 | S/T | 0.632
90 | 93 | 600 | 75 | ∆T | 18.5
90 | 93 | 600 | 75 | LDB | 71.5
90 | 93 | 600 | 75 | LWB | 66.8
90 | 93 | 600 | 75 | kW | 1.58
68 | 95 | 600 | 57 | MBh | 11.2
68 | 95 | 600 | 57 | S/T | 0.871
68 | 95 | 600 | 57 | ∆T | 15.1
68 | 95 | 600 | 57 | LDB | 52.9
68 | 95 | 600 | 57 | LWB | 49.9
68 | 95 | 600 | 57 | kW | 0.79
72 | 95 | 600 | 61 | MBh | 13.6
72 | 95 | 600 | 61 | S/T | 0.809
72 | 95 | 600 | 61 | ∆T | 17
72 | 95 | 600 | 61 | LDB | 55
72 | 95 | 600 | 61 | LWB | 53
72 | 95 | 600 | 61 | kW | 1.04
77 | 95 | 600 | 64 | MBh | 15.4
77 | 95 | 600 | 64 | S/T | 0.76
77 | 95 | 600 | 64 | ∆T | 18.1
77 | 95 | 600 | 64 | LDB | 58.9
77 | 95 | 600 | 64 | LWB | 55.5
77 | 95 | 600 | 64 | kW | 1.25
80 | 95 | 600 | 67 | MBh | 17.2
80 | 95 | 600 | 67 | S/T | 0.703
80 | 95 | 600 | 67 | ∆T | 18.7
80 | 95 | 600 | 67 | LDB | 61.3
80 | 95 | 600 | 67 | LWB | 58
80 | 95 | 600 | 67 | kW | 1.47
84 | 95 | 600 | 70 | MBh | 18.2
84 | 95 | 600 | 70 | S/T | 0.67
84 | 95 | 600 | 70 | ∆T | 18.8
84 | 95 | 600 | 70 | LDB | 65.2
84 | 95 | 600 | 70 | LWB | 61.1
84 | 95 | 600 | 70 | kW | 1.59
86 | 95 | 600 | 72 | MBh | 18.5
86 | 95 | 600 | 72 | S/T | 0.659
86 | 95 | 600 | 72 | ∆T | 18.8
86 | 95 | 600 | 72 | LDB | 67.2
86 | 95 | 600 | 72 | LWB | 63.4
86 | 95 | 600 | 72 | kW | 1.6
90 | 95 | 600 | 75 | MBh | 18.8
90 | 95 | 600 | 75 | S/T | 0.633
90 | 95 | 600 | 75 | ∆T | 18.4
90 | 95 | 600 | 75 | LDB | 71.6
90 | 95 | 600 | 75 | LWB | 66.9
90 | 95 | 600 | 75 | kW | 1.61
68 | 99 | 600 | 57 | MBh | 11.2
68 | 99 | 600 | 57 | S/T | 0.871
68 | 99 | 600 | 57 | ∆T | 15.1
68 | 99 | 600 | 57 | LDB | 52.9
68 | 99 | 600 | 57 | LWB | 49.9
68 | 99 | 600 | 57 | kW | 0.85
72 | 99 | 600 | 61 | MBh | 13.6
72 | 99 | 600 | 61 | S/T | 0.809
72 | 99 | 600 | 61 | ∆T | 17
72 | 99 | 600 | 61 | LDB | 55
72 | 99 | 600 | 61 | LWB | 53
72 | 99 | 600 | 61 | kW | 1.11
77 | 99 | 600 | 64 | MBh | 15.4
77 | 99 | 600 | 64 | S/T | 0.76
77 | 99 | 600 | 64 | ∆T | 18.1
77 | 99 | 600 | 64 | LDB | 58.9
77 | 99 | 600 | 64 | LWB | 55.5
77 | 99 | 600 | 64 | kW | 1.34
80 | 99 | 600 | 67 | MBh | 17.2
80 | 99 | 600 | 67 | S/T | 0.703
80 | 99 | 600 | 67 | ∆T | 18.7
80 | 99 | 600 | 67 | LDB | 61.3
80 | 99 | 600 | 67 | LWB | 58
80 | 99 | 600 | 67 | kW | 1.58
84 | 99 | 600 | 70 | MBh | 17.9
84 | 99 | 600 | 70 | S/T | 0.676
84 | 99 | 600 | 70 | ∆T | 18.7
84 | 99 | 600 | 70 | LDB | 65.3
84 | 99 | 600 | 70 | LWB | 61.3
84 | 99 | 600 | 70 | kW | 1.65
86 | 99 | 600 | 72 | MBh | 18.2
86 | 99 | 600 | 72 | S/T | 0.659
86 | 99 | 600 | 72 | ∆T | 18.5
86 | 99 | 600 | 72 | LDB | 67.5
86 | 99 | 600 | 72 | LWB | 63.5
86 | 99 | 600 | 72 | kW | 1.66
90 | 99 | 600 | 75 | MBh | 18.5
90 | 99 | 600 | 75 | S/T | 0.638
90 | 99 | 600 | 75 | ∆T | 18.2
90 | 99 | 600 | 75 | LDB | 71.8
90 | 99 | 600 | 75 | LWB | 67
90 | 99 | 600 | 75 | kW | 1.67
68 | 103 | 600 | 57 | MBh | 11.2
68 | 103 | 600 | 57 | S/T | 0.871
68 | 103 | 600 | 57 | ∆T | 15.1
68 | 103 | 600 | 57 | LDB | 52.9
68 | 103 | 600 | 57 | LWB | 49.9
68 | 103 | 600 | 57 | kW | 0.91
72 | 103 | 600 | 61 | MBh | 13.6
72 | 103 | 600 | 61 | S/T | 0.809
72 | 103 | 600 | 61 | ∆T | 17
72 | 103 | 600 | 61 | LDB | 55
72 | 103 | 600 | 61 | LWB | 53
72 | 103 | 600 | 61 | kW | 1.19
77 | 103 | 600 | 64 | MBh | 15.4
77 | 103 | 600 | 64 | S/T | 0.76
77 | 103 | 600 | 64 | ∆T | 18.1
77 | 103 | 600 | 64 | LDB | 58.9
77 | 103 | 600 | 64 | LWB | 55.5
77 | 103 | 600 | 64 | kW | 1.43
80 | 103 | 600 | 67 | MBh | 17.2
80 | 103 | 600 | 67 | S/T | 0.703
80 | 103 | 600 | 67 | ∆T | 18.7
80 | 103 | 600 | 67 | LDB | 61.3
80 | 103 | 600 | 67 | LWB | 58
80 | 103 | 600 | 67 | kW | 1.69
84 | 103 | 600 | 70 | MBh | 17.6
84 | 103 | 600 | 70 | S/T | 0.676
84 | 103 | 600 | 70 | ∆T | 18.4
84 | 103 | 600 | 70 | LDB | 65.6
84 | 103 | 600 | 70 | LWB | 61.4
84 | 103 | 600 | 70 | kW | 1.71
86 | 103 | 600 | 72 | MBh | 17.8
86 | 103 | 600 | 72 | S/T | 0.663
86 | 103 | 600 | 72 | ∆T | 18.2
86 | 103 | 600 | 72 | LDB | 67.8
86 | 103 | 600 | 72 | LWB | 63.7
86 | 103 | 600 | 72 | kW | 1.72
90 | 103 | 600 | 75 | MBh | 18.2
90 | 103 | 600 | 75 | S/T | 0.637
90 | 103 | 600 | 75 | ∆T | 17.9
90 | 103 | 600 | 75 | LDB | 72.1
90 | 103 | 600 | 75 | LWB | 67.1
90 | 103 | 600 | 75 | kW | 1.74
68 | 106 | 600 | 57 | MBh | 11.2
68 | 106 | 600 | 57 | S/T | 0.871
68 | 106 | 600 | 57 | ∆T | 15.1
68 | 106 | 600 | 57 | LDB | 52.9
68 | 106 | 600 | 57 | LWB | 49.9
68 | 106 | 600 | 57 | kW | 1
72 | 106 | 600 | 61 | MBh | 13.6
72 | 106 | 600 | 61 | S/T | 0.809
72 | 106 | 600 | 61 | ∆T | 17
72 | 106 | 600 | 61 | LDB | 55
72 | 106 | 600 | 61 | LWB | 53
72 | 106 | 600 | 61 | kW | 1.31
77 | 106 | 600 | 64 | MBh | 15.4
77 | 106 | 600 | 64 | S/T | 0.76
77 | 106 | 600 | 64 | ∆T | 18.1
77 | 106 | 600 | 64 | LDB | 58.9
77 | 106 | 600 | 64 | LWB | 55.5
77 | 106 | 600 | 64 | kW | 1.58
80 | 106 | 600 | 67 | MBh | 17
80 | 106 | 600 | 67 | S/T | 0.706
80 | 106 | 600 | 67 | ∆T | 18.5
80 | 106 | 600 | 67 | LDB | 61.5
80 | 106 | 600 | 67 | LWB | 58.1
80 | 106 | 600 | 67 | kW | 1.83
84 | 106 | 600 | 70 | MBh | 17.4
84 | 106 | 600 | 70 | S/T | 0.672
84 | 106 | 600 | 70 | ∆T | 18.1
84 | 106 | 600 | 70 | LDB | 65.9
84 | 106 | 600 | 70 | LWB | 61.5
84 | 106 | 600 | 70 | kW | 1.85
86 | 106 | 600 | 72 | MBh | 17.6
86 | 106 | 600 | 72 | S/T | 0.665
86 | 106 | 600 | 72 | ∆T | 18.1
86 | 106 | 600 | 72 | LDB | 67.9
86 | 106 | 600 | 72 | LWB | 63.8
86 | 106 | 600 | 72 | kW | 1.86
90 | 106 | 600 | 75 | MBh | 18
90 | 106 | 600 | 75 | S/T | 0.633
90 | 106 | 600 | 75 | ∆T | 17.6
90 | 106 | 600 | 75 | LDB | 72.4
90 | 106 | 600 | 75 | LWB | 67.2
90 | 106 | 600 | 75 | kW | 1.87
68 | 110 | 600 | 57 | MBh | 11.2
68 | 110 | 600 | 57 | S/T | 0.871
68 | 110 | 600 | 57 | ∆T | 15.1
68 | 110 | 600 | 57 | LDB | 52.9
68 | 110 | 600 | 57 | LWB | 49.9
68 | 110 | 600 | 57 | kW | 1.14
72 | 110 | 600 | 61 | MBh | 13.6
72 | 110 | 600 | 61 | S/T | 0.809
72 | 110 | 600 | 61 | ∆T | 17
72 | 110 | 600 | 61 | LDB | 55
72 | 110 | 600 | 61 | LWB | 53
72 | 110 | 600 | 61 | kW | 1.51
77 | 110 | 600 | 64 | MBh | 15.4
77 | 110 | 600 | 64 | S/T | 0.76
77 | 110 | 600 | 64 | ∆T | 18.1
77 | 110 | 600 | 64 | LDB | 58.9
77 | 110 | 600 | 64 | LWB | 55.5
77 | 110 | 600 | 64 | kW | 1.81
80 | 110 | 600 | 67 | MBh | 16.7
80 | 110 | 600 | 67 | S/T | 0.707
80 | 110 | 600 | 67 | ∆T | 18.2
80 | 110 | 600 | 67 | LDB | 61.8
80 | 110 | 600 | 67 | LWB | 58.3
80 | 110 | 600 | 67 | kW | 2.03
84 | 110 | 600 | 70 | MBh | 17
84 | 110 | 600 | 70 | S/T | 0.676
84 | 110 | 600 | 70 | ∆T | 17.7
84 | 110 | 600 | 70 | LDB | 66.3
84 | 110 | 600 | 70 | LWB | 61.8
84 | 110 | 600 | 70 | kW | 2.05
86 | 110 | 600 | 72 | MBh | 17.3
86 | 110 | 600 | 72 | S/T | 0.659
86 | 110 | 600 | 72 | ∆T | 17.6
86 | 110 | 600 | 72 | LDB | 68.4
86 | 110 | 600 | 72 | LWB | 64
86 | 110 | 600 | 72 | kW | 2.06
90 | 110 | 600 | 75 | MBh | 17.3
90 | 110 | 600 | 75 | S/T | 0.636
90 | 110 | 600 | 75 | ∆T | 17
90 | 110 | 600 | 75 | LDB | 73
90 | 110 | 600 | 75 | LWB | 67.6
90 | 110 | 600 | 75 | kW | 2.06
68 | 115 | 600 | 57 | MBh | 11.2
68 | 115 | 600 | 57 | S/T | 0.871
68 | 115 | 600 | 57 | ∆T | 15.1
68 | 115 | 600 | 57 | LDB | 52.9
68 | 115 | 600 | 57 | LWB | 49.9
68 | 115 | 600 | 57 | kW | 1.34
72 | 115 | 600 | 61 | MBh | 13.6
72 | 115 | 600 | 61 | S/T | 0.809
72 | 115 | 600 | 61 | ∆T | 17
72 | 115 | 600 | 61 | LDB | 55
72 | 115 | 600 | 61 | LWB | 53
72 | 115 | 600 | 61 | kW | 1.77
77 | 115 | 600 | 64 | MBh | 15.4
77 | 115 | 600 | 64 | S/T | 0.76
77 | 115 | 600 | 64 | ∆T | 18.1
77 | 115 | 600 | 64 | LDB | 58.9
77 | 115 | 600 | 64 | LWB | 55.5
77 | 115 | 600 | 64 | kW | 2.13
80 | 115 | 600 | 67 | MBh | 16.1
80 | 115 | 600 | 67 | S/T | 0.708
80 | 115 | 600 | 67 | ∆T | 17.6
80 | 115 | 600 | 67 | LDB | 62.4
80 | 115 | 600 | 67 | LWB | 58.7
80 | 115 | 600 | 67 | kW | 2.27
84 | 115 | 600 | 70 | MBh | 16.1
84 | 115 | 600 | 70 | S/T | 0.671
84 | 115 | 600 | 70 | ∆T | 16.7
84 | 115 | 600 | 70 | LDB | 67.3
84 | 115 | 600 | 70 | LWB | 62.2
84 | 115 | 600 | 70 | kW | 2.27
86 | 115 | 600 | 72 | MBh | 16.1
86 | 115 | 600 | 72 | S/T | 0.665
86 | 115 | 600 | 72 | ∆T | 16.5
86 | 115 | 600 | 72 | LDB | 69.5
86 | 115 | 600 | 72 | LWB | 64.6
86 | 115 | 600 | 72 | kW | 2.27
90 | 115 | 600 | 75 | MBh | 16.1
90 | 115 | 600 | 75 | S/T | 0.634
90 | 115 | 600 | 75 | ∆T | 15.7
90 | 115 | 600 | 75 | LDB | 74.3
90 | 115 | 600 | 75 | LWB | 68.1
90 | 115 | 600 | 75 | kW | 2.27
68 | 118 | 600 | 57 | MBh | 11.2
68 | 118 | 600 | 57 | S/T | 0.871
68 | 118 | 600 | 57 | ∆T | 15.1
68 | 118 | 600 | 57 | LDB | 52.9
68 | 118 | 600 | 57 | LWB | 49.9
68 | 118 | 600 | 57 | kW | 1.46
72 | 118 | 600 | 61 | MBh | 13.6
72 | 118 | 600 | 61 | S/T | 0.809
72 | 118 | 600 | 61 | ∆T | 17
72 | 118 | 600 | 61 | LDB | 55
72 | 118 | 600 | 61 | LWB | 53
72 | 118 | 600 | 61 | kW | 1.93
77 | 118 | 600 | 64 | MBh | 13.7
77 | 118 | 600 | 64 | S/T | 0.766
77 | 118 | 600 | 64 | ∆T | 16.2
77 | 118 | 600 | 64 | LDB | 60.8
77 | 118 | 600 | 64 | LWB | 56.5
77 | 118 | 600 | 64 | kW | 1.96
80 | 118 | 600 | 67 | MBh | 13.7
80 | 118 | 600 | 67 | S/T | 0.707
80 | 118 | 600 | 67 | ∆T | 15
80 | 118 | 600 | 67 | LDB | 65
80 | 118 | 600 | 67 | LWB | 60
80 | 118 | 600 | 67 | kW | 1.96
84 | 118 | 600 | 70 | MBh | 13.7
84 | 118 | 600 | 70 | S/T | 0.674
84 | 118 | 600 | 70 | ∆T | 14.3
84 | 118 | 600 | 70 | LDB | 69.7
84 | 118 | 600 | 70 | LWB | 63.5
84 | 118 | 600 | 70 | kW | 1.96
86 | 118 | 600 | 72 | MBh | 13.7
86 | 118 | 600 | 72 | S/T | 0.664
86 | 118 | 600 | 72 | ∆T | 14
86 | 118 | 600 | 72 | LDB | 72
86 | 118 | 600 | 72 | LWB | 65.8
86 | 118 | 600 | 72 | kW | 1.96
90 | 118 | 600 | 75 | MBh | 13.7
90 | 118 | 600 | 75 | S/T | 0.636
90 | 118 | 600 | 75 | ∆T | 13.4
90 | 118 | 600 | 75 | LDB | 76.6
90 | 118 | 600 | 75 | LWB | 69.2
90 | 118 | 600 | 75 | kW | 1.96
68 | 122 | 600 | 57 | MBh | 10.3
68 | 122 | 600 | 57 | S/T | 0.875
68 | 122 | 600 | 57 | ∆T | 13.9
68 | 122 | 600 | 57 | LDB | 54.1
68 | 122 | 600 | 57 | LWB | 50.5
68 | 122 | 600 | 57 | kW | 1.46
72 | 122 | 600 | 61 | MBh | 10.3
72 | 122 | 600 | 61 | S/T | 0.811
72 | 122 | 600 | 61 | ∆T | 12.9
72 | 122 | 600 | 61 | LDB | 59.1
72 | 122 | 600 | 61 | LWB | 55.1
72 | 122 | 600 | 61 | kW | 1.46
77 | 122 | 600 | 64 | MBh | 10.3
77 | 122 | 600 | 64 | S/T | 0.762
77 | 122 | 600 | 64 | ∆T | 12.1
77 | 122 | 600 | 64 | LDB | 64.9
77 | 122 | 600 | 64 | LWB | 58.5
77 | 122 | 600 | 64 | kW | 1.46
80 | 122 | 600 | 67 | MBh | 10.3
80 | 122 | 600 | 67 | S/T | 0.707
80 | 122 | 600 | 67 | ∆T | 11.2
80 | 122 | 600 | 67 | LDB | 68.8
80 | 122 | 600 | 67 | LWB | 61.8
80 | 122 | 600 | 67 | kW | 1.46
84 | 122 | 600 | 70 | MBh | 10.3
84 | 122 | 600 | 70 | S/T | 0.674
84 | 122 | 600 | 70 | ∆T | 10.7
84 | 122 | 600 | 70 | LDB | 73.3
84 | 122 | 600 | 70 | LWB | 65.2
84 | 122 | 600 | 70 | kW | 1.46
86 | 122 | 600 | 72 | MBh | 10.3
86 | 122 | 600 | 72 | S/T | 0.663
86 | 122 | 600 | 72 | ∆T | 10.5
86 | 122 | 600 | 72 | LDB | 75.5
86 | 122 | 600 | 72 | LWB | 67.4
86 | 122 | 600 | 72 | kW | 1.46
90 | 122 | 600 | 75 | MBh | 10.3
90 | 122 | 600 | 75 | S/T | 0.636
90 | 122 | 600 | 75 | ∆T | 10.1
90 | 122 | 600 | 75 | LDB | 79.9
90 | 122 | 600 | 75 | LWB | 70.7
90 | 122 | 600 | 75 | kW | 1.46

## RZA18AAVJU - FTA18AAVJUA
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 600 | 57 | MBh | 11.2 | 64 | 60 | 61 | 25.2 | 2.24
68 | 23 | 600 | 57 | S/T | 0.871 | 64 | 60 | 65 | 23.3 | 2.02
68 | 23 | 600 | 57 | ∆T | 15.1 | 64 | 60 | 68 | 21.9 | 1.87
68 | 23 | 600 | 57 | LDB | 52.9 | 64 | 60 | 70 | 21 | 1.77
68 | 23 | 600 | 57 | LWB | 49.9 | 64 | 60 | 72 | 20.1 | 1.69
68 | 23 | 600 | 57 | kW | 0.43 | 64 | 60 | 75 | 18.7 | 1.57
72 | 23 | 600 | 61 | MBh | 13.6 | 60 | 56 | 61 | 25.2 | 2.35
72 | 23 | 600 | 61 | S/T | 0.809 | 60 | 56 | 65 | 23.3 | 2.11
72 | 23 | 600 | 61 | ∆T | 17 | 60 | 56 | 68 | 21.9 | 1.94
72 | 23 | 600 | 61 | LDB | 55 | 60 | 56 | 70 | 21 | 1.84
72 | 23 | 600 | 61 | LWB | 53 | 60 | 56 | 72 | 20.1 | 1.75
72 | 23 | 600 | 61 | kW | 0.53 | 60 | 56 | 75 | 18.7 | 1.62
77 | 23 | 600 | 64 | MBh | 15.4 | 57 | 53 | 61 | 25.2 | 2.45
77 | 23 | 600 | 64 | S/T | 0.76 | 57 | 53 | 65 | 23.3 | 2.19
77 | 23 | 600 | 64 | ∆T | 18.1 | 57 | 53 | 68 | 21.9 | 2.01
77 | 23 | 600 | 64 | LDB | 58.9 | 57 | 53 | 70 | 21 | 1.9
77 | 23 | 600 | 64 | LWB | 55.5 | 57 | 53 | 72 | 20.1 | 1.8
77 | 23 | 600 | 64 | kW | 0.61 | 57 | 53 | 75 | 18.7 | 1.66
80 | 23 | 600 | 67 | MBh | 17.2 | 54 | 50 | 61 | 25.2 | 2.55
80 | 23 | 600 | 67 | S/T | 0.703 | 54 | 50 | 65 | 23.3 | 2.27
80 | 23 | 600 | 67 | ∆T | 18.7 | 54 | 50 | 68 | 21.9 | 2.08
80 | 23 | 600 | 67 | LDB | 61.3 | 54 | 50 | 70 | 21 | 1.96
80 | 23 | 600 | 67 | LWB | 58 | 54 | 50 | 72 | 20.1 | 1.86
80 | 23 | 600 | 67 | kW | 0.69 | 54 | 50 | 75 | 18.7 | 1.71
84 | 23 | 600 | 70 | MBh | 19 | 51 | 47 | 61 | 25.2 | 2.66
84 | 23 | 600 | 70 | S/T | 0.668 | 51 | 47 | 65 | 23.3 | 2.36
84 | 23 | 600 | 70 | ∆T | 19.6 | 51 | 47 | 68 | 21.9 | 2.16
84 | 23 | 600 | 70 | LDB | 64.4 | 51 | 47 | 70 | 21 | 2.03
84 | 23 | 600 | 70 | LWB | 60.7 | 51 | 47 | 72 | 20.1 | 1.92
84 | 23 | 600 | 70 | kW | 0.77 | 51 | 47 | 75 | 18.7 | 1.76
86 | 23 | 600 | 72 | MBh | 20.2 | 47 | 43 | 61 | 25.2 | 2.83
86 | 23 | 600 | 72 | S/T | 0.658 | 47 | 43 | 65 | 23.3 | 2.5
86 | 23 | 600 | 72 | ∆T | 20.5 | 47 | 43 | 68 | 21.9 | 2.28
86 | 23 | 600 | 72 | LDB | 65.5 | 47 | 43 | 70 | 21 | 2.14
86 | 23 | 600 | 72 | LWB | 62.5 | 47 | 43 | 72 | 20.1 | 2.01
86 | 23 | 600 | 72 | kW | 0.83 | 47 | 43 | 75 | 18.7 | 1.84
90 | 23 | 600 | 75 | MBh | 22 | 44 | 40 | 61 | 25.2 | 2.97
90 | 23 | 600 | 75 | S/T | 0.632 | 44 | 40 | 65 | 23.3 | 2.61
90 | 23 | 600 | 75 | ∆T | 21.5 | 44 | 40 | 68 | 21.9 | 2.37
90 | 23 | 600 | 75 | LDB | 68.5 | 44 | 40 | 70 | 21 | 2.23
90 | 23 | 600 | 75 | LWB | 65.3 | 44 | 40 | 72 | 20.1 | 2.09
90 | 23 | 600 | 75 | kW | 0.92 | 44 | 40 | 75 | 18.7 | 1.9
68 | 30 | 600 | 57 | MBh | 11.2 | 39 | 36 | 61 | 25.2 | 3.18
68 | 30 | 600 | 57 | S/T | 0.871 | 39 | 36 | 65 | 23.3 | 2.79
68 | 30 | 600 | 57 | ∆T | 15.1 | 39 | 36 | 68 | 21.9 | 2.52
68 | 30 | 600 | 57 | LDB | 52.9 | 39 | 36 | 70 | 21 | 2.36
68 | 30 | 600 | 57 | LWB | 49.9 | 39 | 36 | 72 | 20.1 | 2.21
68 | 30 | 600 | 57 | kW | 0.44 | 39 | 36 | 75 | 18.7 | 2
72 | 30 | 600 | 61 | MBh | 13.6 | 35 | 32 | 61 | 25.2 | 3.39
72 | 30 | 600 | 61 | S/T | 0.809 | 35 | 32 | 65 | 23.3 | 2.99
72 | 30 | 600 | 61 | ∆T | 17 | 35 | 32 | 68 | 21.9 | 2.7
72 | 30 | 600 | 61 | LDB | 55 | 35 | 32 | 70 | 21 | 2.52
72 | 30 | 600 | 61 | LWB | 53 | 35 | 32 | 72 | 20.1 | 2.35
72 | 30 | 600 | 61 | kW | 0.55 | 35 | 32 | 75 | 18.7 | 2.11
77 | 30 | 600 | 64 | MBh | 15.4 | 30 | 28 | 61 | 25.2 | 3.36
77 | 30 | 600 | 64 | S/T | 0.76 | 30 | 28 | 65 | 23.3 | 3.22
77 | 30 | 600 | 64 | ∆T | 18.1 | 30 | 28 | 68 | 21.9 | 2.9
77 | 30 | 600 | 64 | LDB | 58.9 | 30 | 28 | 70 | 21 | 2.7
77 | 30 | 600 | 64 | LWB | 55.5 | 30 | 28 | 72 | 20.1 | 2.51
77 | 30 | 600 | 64 | kW | 0.63 | 30 | 28 | 75 | 18.7 | 2.25
80 | 30 | 600 | 67 | MBh | 17.2 | 26 | 24 | 61 | 25.2 | 3.33
80 | 30 | 600 | 67 | S/T | 0.703 | 26 | 24 | 65 | 23.3 | 3.38
80 | 30 | 600 | 67 | ∆T | 18.7 | 26 | 24 | 68 | 21.9 | 3.13
80 | 30 | 600 | 67 | LDB | 61.3 | 26 | 24 | 70 | 21 | 2.91
80 | 30 | 600 | 67 | LWB | 58 | 26 | 24 | 72 | 20.1 | 2.7
80 | 30 | 600 | 67 | kW | 0.71 | 26 | 24 | 75 | 18.7 | 2.4
84 | 30 | 600 | 70 | MBh | 19 | 22 | 20 | 61 | 25.2 | 3.29
84 | 30 | 600 | 70 | S/T | 0.668 | 22 | 20 | 65 | 23.3 | 3.35
84 | 30 | 600 | 70 | ∆T | 19.6 | 22 | 20 | 68 | 21.9 | 3.39
84 | 30 | 600 | 70 | LDB | 64.4 | 22 | 20 | 70 | 21 | 3.15
84 | 30 | 600 | 70 | LWB | 60.7 | 22 | 20 | 72 | 20.1 | 2.92
84 | 30 | 600 | 70 | kW | 0.8 | 22 | 20 | 75 | 18.7 | 2.59
86 | 30 | 600 | 72 | MBh | 20.2 | 19 | 18 | 61 | 25.2 | 3.27
86 | 30 | 600 | 72 | S/T | 0.658 | 19 | 18 | 65 | 23.3 | 3.33
86 | 30 | 600 | 72 | ∆T | 20.5 | 19 | 18 | 68 | 21.9 | 3.37
86 | 30 | 600 | 72 | LDB | 65.5 | 19 | 18 | 70 | 21 | 3.29
86 | 30 | 600 | 72 | LWB | 62.5 | 19 | 18 | 72 | 20.1 | 3.04
86 | 30 | 600 | 72 | kW | 0.86 | 19 | 18 | 75 | 18.7 | 2.69
90 | 30 | 600 | 75 | MBh | 22 | 17 | 16 | 61 | 24.8 | 3.25
90 | 30 | 600 | 75 | S/T | 0.632 | 17 | 16 | 65 | 23.3 | 3.3
90 | 30 | 600 | 75 | ∆T | 21.5 | 17 | 16 | 68 | 21.9 | 3.35
90 | 30 | 600 | 75 | LDB | 68.5 | 17 | 16 | 70 | 21 | 3.37
90 | 30 | 600 | 75 | LWB | 65.3 | 17 | 16 | 72 | 20.1 | 3.21
90 | 30 | 600 | 75 | kW | 0.95 | 17 | 16 | 75 | 18.7 | 2.84
68 | 40 | 600 | 57 | MBh | 11.2 | 15 | 14 | 61 | 24.3 | 3.23
68 | 40 | 600 | 57 | S/T | 0.871 | 15 | 14 | 65 | 23.3 | 3.29
68 | 40 | 600 | 57 | ∆T | 15.1 | 15 | 14 | 68 | 21.9 | 3.33
68 | 40 | 600 | 57 | LDB | 52.9 | 15 | 14 | 70 | 21 | 3.36
68 | 40 | 600 | 57 | LWB | 49.9 | 15 | 14 | 72 | 20.1 | 3.33
68 | 40 | 600 | 57 | kW | 0.46 | 15 | 14 | 75 | 18.7 | 2.93
72 | 40 | 600 | 61 | MBh | 13.6 | 13 | 12 | 61 | 23.6 | 3.21
72 | 40 | 600 | 61 | S/T | 0.809 | 13 | 12 | 65 | 23.3 | 3.27
72 | 40 | 600 | 61 | ∆T | 17 | 13 | 12 | 68 | 21.9 | 3.31
72 | 40 | 600 | 61 | LDB | 55 | 13 | 12 | 70 | 21 | 3.34
72 | 40 | 600 | 61 | LWB | 53 | 13 | 12 | 72 | 20.1 | 3.37
72 | 40 | 600 | 61 | kW | 0.57 | 13 | 12 | 75 | 18.7 | 3.07
77 | 40 | 600 | 64 | MBh | 15.4 | 10 | 9 | 61 | 22.3 | 3.16
77 | 40 | 600 | 64 | S/T | 0.76 | 10 | 9 | 65 | 22.3 | 3.23
77 | 40 | 600 | 64 | ∆T | 18.1 | 10 | 9 | 68 | 21.9 | 3.27
77 | 40 | 600 | 64 | LDB | 58.9 | 10 | 9 | 70 | 21 | 3.3
77 | 40 | 600 | 64 | LWB | 55.5 | 10 | 9 | 72 | 20.1 | 3.34
77 | 40 | 600 | 64 | kW | 0.66 | 10 | 9 | 75 | 18.7 | 3.34
80 | 40 | 600 | 67 | MBh | 17.2 | 6 | 5 | 61 | 21 | 3.08
80 | 40 | 600 | 67 | S/T | 0.703 | 6 | 5 | 65 | 21 | 3.08
80 | 40 | 600 | 67 | ∆T | 18.7 | 6 | 5 | 68 | 21 | 3.08
80 | 40 | 600 | 67 | LDB | 61.3 | 6 | 5 | 70 | 21 | 3.08
80 | 40 | 600 | 67 | LWB | 58 | 6 | 5 | 72 | 20.1 | 3.08
80 | 40 | 600 | 67 | kW | 0.75 | 6 | 5 | 75 | 18.7 | 3.08
84 | 40 | 600 | 70 | MBh | 19 | -2 | -2 | 61 | 18.4 | 2.82
84 | 40 | 600 | 70 | S/T | 0.668 | -2 | -2 | 65 | 18.4 | 2.82
84 | 40 | 600 | 70 | ∆T | 19.6 | -2 | -2 | 68 | 18.4 | 2.82
84 | 40 | 600 | 70 | LDB | 64.4 | -2 | -2 | 70 | 18.4 | 2.82
84 | 40 | 600 | 70 | LWB | 60.7 | -2 | -2 | 72 | 18.4 | 2.82
84 | 40 | 600 | 70 | kW | 0.84 | -2 | -2 | 75 | 18.4 | 2.82
86 | 40 | 600 | 72 | MBh | 20.2 | -4 | -4 | 61 | 17.7 | 2.75
86 | 40 | 600 | 72 | S/T | 0.658 | -4 | -4 | 65 | 17.7 | 2.75
86 | 40 | 600 | 72 | ∆T | 20.5 | -4 | -4 | 68 | 17.7 | 2.75
86 | 40 | 600 | 72 | LDB | 65.5 | -4 | -4 | 70 | 17.7 | 2.75
86 | 40 | 600 | 72 | LWB | 62.5 | -4 | -4 | 72 | 17.7 | 2.75
86 | 40 | 600 | 72 | kW | 0.9 | -4 | -4 | 75 | 17.7 | 2.75
90 | 40 | 600 | 75 | MBh | 22
90 | 40 | 600 | 75 | S/T | 0.632
90 | 40 | 600 | 75 | ∆T | 21.5
90 | 40 | 600 | 75 | LDB | 68.5
90 | 40 | 600 | 75 | LWB | 65.3
90 | 40 | 600 | 75 | kW | 1
68 | 50 | 600 | 57 | MBh | 11.2
68 | 50 | 600 | 57 | S/T | 0.871
68 | 50 | 600 | 57 | ∆T | 15.1
68 | 50 | 600 | 57 | LDB | 52.9
68 | 50 | 600 | 57 | LWB | 49.9
68 | 50 | 600 | 57 | kW | 0.49
72 | 50 | 600 | 61 | MBh | 13.6
72 | 50 | 600 | 61 | S/T | 0.809
72 | 50 | 600 | 61 | ∆T | 17
72 | 50 | 600 | 61 | LDB | 55
72 | 50 | 600 | 61 | LWB | 53
72 | 50 | 600 | 61 | kW | 0.6
77 | 50 | 600 | 64 | MBh | 15.4
77 | 50 | 600 | 64 | S/T | 0.76
77 | 50 | 600 | 64 | ∆T | 18.1
77 | 50 | 600 | 64 | LDB | 58.9
77 | 50 | 600 | 64 | LWB | 55.5
77 | 50 | 600 | 64 | kW | 0.69
80 | 50 | 600 | 67 | MBh | 17.2
80 | 50 | 600 | 67 | S/T | 0.703
80 | 50 | 600 | 67 | ∆T | 18.7
80 | 50 | 600 | 67 | LDB | 61.3
80 | 50 | 600 | 67 | LWB | 58
80 | 50 | 600 | 67 | kW | 0.79
84 | 50 | 600 | 70 | MBh | 19
84 | 50 | 600 | 70 | S/T | 0.668
84 | 50 | 600 | 70 | ∆T | 19.6
84 | 50 | 600 | 70 | LDB | 64.4
84 | 50 | 600 | 70 | LWB | 60.7
84 | 50 | 600 | 70 | kW | 0.88
86 | 50 | 600 | 72 | MBh | 20.2
86 | 50 | 600 | 72 | S/T | 0.658
86 | 50 | 600 | 72 | ∆T | 20.5
86 | 50 | 600 | 72 | LDB | 65.5
86 | 50 | 600 | 72 | LWB | 62.5
86 | 50 | 600 | 72 | kW | 0.95
90 | 50 | 600 | 75 | MBh | 22
90 | 50 | 600 | 75 | S/T | 0.632
90 | 50 | 600 | 75 | ∆T | 21.5
90 | 50 | 600 | 75 | LDB | 68.5
90 | 50 | 600 | 75 | LWB | 65.3
90 | 50 | 600 | 75 | kW | 1.05
68 | 54 | 600 | 57 | MBh | 11.2
68 | 54 | 600 | 57 | S/T | 0.871
68 | 54 | 600 | 57 | ∆T | 15.1
68 | 54 | 600 | 57 | LDB | 52.9
68 | 54 | 600 | 57 | LWB | 49.9
68 | 54 | 600 | 57 | kW | 0.5
72 | 54 | 600 | 61 | MBh | 13.6
72 | 54 | 600 | 61 | S/T | 0.809
72 | 54 | 600 | 61 | ∆T | 17
72 | 54 | 600 | 61 | LDB | 55
72 | 54 | 600 | 61 | LWB | 53
72 | 54 | 600 | 61 | kW | 0.61
77 | 54 | 600 | 64 | MBh | 15.4
77 | 54 | 600 | 64 | S/T | 0.76
77 | 54 | 600 | 64 | ∆T | 18.1
77 | 54 | 600 | 64 | LDB | 58.9
77 | 54 | 600 | 64 | LWB | 55.5
77 | 54 | 600 | 64 | kW | 0.71
80 | 54 | 600 | 67 | MBh | 17.2
80 | 54 | 600 | 67 | S/T | 0.703
80 | 54 | 600 | 67 | ∆T | 18.7
80 | 54 | 600 | 67 | LDB | 61.3
80 | 54 | 600 | 67 | LWB | 58
80 | 54 | 600 | 67 | kW | 0.8
84 | 54 | 600 | 70 | MBh | 19
84 | 54 | 600 | 70 | S/T | 0.668
84 | 54 | 600 | 70 | ∆T | 19.6
84 | 54 | 600 | 70 | LDB | 64.4
84 | 54 | 600 | 70 | LWB | 60.7
84 | 54 | 600 | 70 | kW | 0.9
86 | 54 | 600 | 72 | MBh | 20.2
86 | 54 | 600 | 72 | S/T | 0.658
86 | 54 | 600 | 72 | ∆T | 20.5
86 | 54 | 600 | 72 | LDB | 65.5
86 | 54 | 600 | 72 | LWB | 62.5
86 | 54 | 600 | 72 | kW | 0.97
90 | 54 | 600 | 75 | MBh | 22
90 | 54 | 600 | 75 | S/T | 0.632
90 | 54 | 600 | 75 | ∆T | 21.5
90 | 54 | 600 | 75 | LDB | 68.5
90 | 54 | 600 | 75 | LWB | 65.3
90 | 54 | 600 | 75 | kW | 1.07
68 | 58 | 600 | 57 | MBh | 11.2
68 | 58 | 600 | 57 | S/T | 0.871
68 | 58 | 600 | 57 | ∆T | 15.1
68 | 58 | 600 | 57 | LDB | 52.9
68 | 58 | 600 | 57 | LWB | 49.9
68 | 58 | 600 | 57 | kW | 0.5
72 | 58 | 600 | 61 | MBh | 13.6
72 | 58 | 600 | 61 | S/T | 0.809
72 | 58 | 600 | 61 | ∆T | 17
72 | 58 | 600 | 61 | LDB | 55
72 | 58 | 600 | 61 | LWB | 53
72 | 58 | 600 | 61 | kW | 0.63
77 | 58 | 600 | 64 | MBh | 15.4
77 | 58 | 600 | 64 | S/T | 0.76
77 | 58 | 600 | 64 | ∆T | 18.1
77 | 58 | 600 | 64 | LDB | 58.9
77 | 58 | 600 | 64 | LWB | 55.5
77 | 58 | 600 | 64 | kW | 0.72
80 | 58 | 600 | 67 | MBh | 17.2
80 | 58 | 600 | 67 | S/T | 0.703
80 | 58 | 600 | 67 | ∆T | 18.7
80 | 58 | 600 | 67 | LDB | 61.3
80 | 58 | 600 | 67 | LWB | 58
80 | 58 | 600 | 67 | kW | 0.82
84 | 58 | 600 | 70 | MBh | 19
84 | 58 | 600 | 70 | S/T | 0.668
84 | 58 | 600 | 70 | ∆T | 19.6
84 | 58 | 600 | 70 | LDB | 64.4
84 | 58 | 600 | 70 | LWB | 60.7
84 | 58 | 600 | 70 | kW | 0.92
86 | 58 | 600 | 72 | MBh | 20.2
86 | 58 | 600 | 72 | S/T | 0.658
86 | 58 | 600 | 72 | ∆T | 20.5
86 | 58 | 600 | 72 | LDB | 65.5
86 | 58 | 600 | 72 | LWB | 62.5
86 | 58 | 600 | 72 | kW | 0.99
90 | 58 | 600 | 75 | MBh | 21.8
90 | 58 | 600 | 75 | S/T | 0.633
90 | 58 | 600 | 75 | ∆T | 21.3
90 | 58 | 600 | 75 | LDB | 68.7
90 | 58 | 600 | 75 | LWB | 65.4
90 | 58 | 600 | 75 | kW | 1.07
68 | 62 | 600 | 57 | MBh | 11.2
68 | 62 | 600 | 57 | S/T | 0.871
68 | 62 | 600 | 57 | ∆T | 15.1
68 | 62 | 600 | 57 | LDB | 52.9
68 | 62 | 600 | 57 | LWB | 49.9
68 | 62 | 600 | 57 | kW | 0.52
72 | 62 | 600 | 61 | MBh | 13.6
72 | 62 | 600 | 61 | S/T | 0.809
72 | 62 | 600 | 61 | ∆T | 17
72 | 62 | 600 | 61 | LDB | 55
72 | 62 | 600 | 61 | LWB | 53
72 | 62 | 600 | 61 | kW | 0.64
77 | 62 | 600 | 64 | MBh | 15.4
77 | 62 | 600 | 64 | S/T | 0.76
77 | 62 | 600 | 64 | ∆T | 18.1
77 | 62 | 600 | 64 | LDB | 58.9
77 | 62 | 600 | 64 | LWB | 55.5
77 | 62 | 600 | 64 | kW | 0.74
80 | 62 | 600 | 67 | MBh | 17.2
80 | 62 | 600 | 67 | S/T | 0.703
80 | 62 | 600 | 67 | ∆T | 18.7
80 | 62 | 600 | 67 | LDB | 61.3
80 | 62 | 600 | 67 | LWB | 58
80 | 62 | 600 | 67 | kW | 0.84
84 | 62 | 600 | 70 | MBh | 19
84 | 62 | 600 | 70 | S/T | 0.668
84 | 62 | 600 | 70 | ∆T | 19.6
84 | 62 | 600 | 70 | LDB | 64.4
84 | 62 | 600 | 70 | LWB | 60.7
84 | 62 | 600 | 70 | kW | 0.94
86 | 62 | 600 | 72 | MBh | 20.2
86 | 62 | 600 | 72 | S/T | 0.658
86 | 62 | 600 | 72 | ∆T | 20.5
86 | 62 | 600 | 72 | LDB | 65.5
86 | 62 | 600 | 72 | LWB | 62.5
86 | 62 | 600 | 72 | kW | 1.01
90 | 62 | 600 | 75 | MBh | 21.5
90 | 62 | 600 | 75 | S/T | 0.633
90 | 62 | 600 | 75 | ∆T | 21
90 | 62 | 600 | 75 | LDB | 69
90 | 62 | 600 | 75 | LWB | 65.6
90 | 62 | 600 | 75 | kW | 1.1
68 | 66 | 600 | 57 | MBh | 11.2
68 | 66 | 600 | 57 | S/T | 0.871
68 | 66 | 600 | 57 | ∆T | 15.1
68 | 66 | 600 | 57 | LDB | 52.9
68 | 66 | 600 | 57 | LWB | 49.9
68 | 66 | 600 | 57 | kW | 0.53
72 | 66 | 600 | 61 | MBh | 13.6
72 | 66 | 600 | 61 | S/T | 0.809
72 | 66 | 600 | 61 | ∆T | 17
72 | 66 | 600 | 61 | LDB | 55
72 | 66 | 600 | 61 | LWB | 53
72 | 66 | 600 | 61 | kW | 0.65
77 | 66 | 600 | 64 | MBh | 15.4
77 | 66 | 600 | 64 | S/T | 0.76
77 | 66 | 600 | 64 | ∆T | 18.1
77 | 66 | 600 | 64 | LDB | 58.9
77 | 66 | 600 | 64 | LWB | 55.5
77 | 66 | 600 | 64 | kW | 0.75
80 | 66 | 600 | 67 | MBh | 17.2
80 | 66 | 600 | 67 | S/T | 0.703
80 | 66 | 600 | 67 | ∆T | 18.7
80 | 66 | 600 | 67 | LDB | 61.3
80 | 66 | 600 | 67 | LWB | 58
80 | 66 | 600 | 67 | kW | 0.86
84 | 66 | 600 | 70 | MBh | 19
84 | 66 | 600 | 70 | S/T | 0.668
84 | 66 | 600 | 70 | ∆T | 19.6
84 | 66 | 600 | 70 | LDB | 64.4
84 | 66 | 600 | 70 | LWB | 60.7
84 | 66 | 600 | 70 | kW | 0.99
86 | 66 | 600 | 72 | MBh | 20.2
86 | 66 | 600 | 72 | S/T | 0.658
86 | 66 | 600 | 72 | ∆T | 20.5
86 | 66 | 600 | 72 | LDB | 65.5
86 | 66 | 600 | 72 | LWB | 62.5
86 | 66 | 600 | 72 | kW | 1.09
90 | 66 | 600 | 75 | MBh | 21.2
90 | 66 | 600 | 75 | S/T | 0.632
90 | 66 | 600 | 75 | ∆T | 20.7
90 | 66 | 600 | 75 | LDB | 69.3
90 | 66 | 600 | 75 | LWB | 65.7
90 | 66 | 600 | 75 | kW | 1.16
68 | 70 | 600 | 57 | MBh | 11.2
68 | 70 | 600 | 57 | S/T | 0.871
68 | 70 | 600 | 57 | ∆T | 15.1
68 | 70 | 600 | 57 | LDB | 52.9
68 | 70 | 600 | 57 | LWB | 49.9
68 | 70 | 600 | 57 | kW | 0.54
72 | 70 | 600 | 61 | MBh | 13.6
72 | 70 | 600 | 61 | S/T | 0.809
72 | 70 | 600 | 61 | ∆T | 17
72 | 70 | 600 | 61 | LDB | 55
72 | 70 | 600 | 61 | LWB | 53
72 | 70 | 600 | 61 | kW | 0.67
77 | 70 | 600 | 64 | MBh | 15.4
77 | 70 | 600 | 64 | S/T | 0.76
77 | 70 | 600 | 64 | ∆T | 18.1
77 | 70 | 600 | 64 | LDB | 58.9
77 | 70 | 600 | 64 | LWB | 55.5
77 | 70 | 600 | 64 | kW | 0.79
80 | 70 | 600 | 67 | MBh | 17.2
80 | 70 | 600 | 67 | S/T | 0.703
80 | 70 | 600 | 67 | ∆T | 18.7
80 | 70 | 600 | 67 | LDB | 61.3
80 | 70 | 600 | 67 | LWB | 58
80 | 70 | 600 | 67 | kW | 0.93
84 | 70 | 600 | 70 | MBh | 19
84 | 70 | 600 | 70 | S/T | 0.668
84 | 70 | 600 | 70 | ∆T | 19.6
84 | 70 | 600 | 70 | LDB | 64.4
84 | 70 | 600 | 70 | LWB | 60.7
84 | 70 | 600 | 70 | kW | 1.08
86 | 70 | 600 | 72 | MBh | 20.2
86 | 70 | 600 | 72 | S/T | 0.658
86 | 70 | 600 | 72 | ∆T | 20.5
86 | 70 | 600 | 72 | LDB | 65.5
86 | 70 | 600 | 72 | LWB | 62.5
86 | 70 | 600 | 72 | kW | 1.18
90 | 70 | 600 | 75 | MBh | 20.9
90 | 70 | 600 | 75 | S/T | 0.632
90 | 70 | 600 | 75 | ∆T | 20.4
90 | 70 | 600 | 75 | LDB | 69.6
90 | 70 | 600 | 75 | LWB | 65.9
90 | 70 | 600 | 75 | kW | 1.22
68 | 72 | 600 | 57 | MBh | 11.2
68 | 72 | 600 | 57 | S/T | 0.871
68 | 72 | 600 | 57 | ∆T | 15.1
68 | 72 | 600 | 57 | LDB | 52.9
68 | 72 | 600 | 57 | LWB | 49.9
68 | 72 | 600 | 57 | kW | 0.54
72 | 72 | 600 | 61 | MBh | 13.6
72 | 72 | 600 | 61 | S/T | 0.809
72 | 72 | 600 | 61 | ∆T | 17
72 | 72 | 600 | 61 | LDB | 55
72 | 72 | 600 | 61 | LWB | 53
72 | 72 | 600 | 61 | kW | 0.69
77 | 72 | 600 | 64 | MBh | 15.4
77 | 72 | 600 | 64 | S/T | 0.76
77 | 72 | 600 | 64 | ∆T | 18.1
77 | 72 | 600 | 64 | LDB | 58.9
77 | 72 | 600 | 64 | LWB | 55.5
77 | 72 | 600 | 64 | kW | 0.82
80 | 72 | 600 | 67 | MBh | 17.2
80 | 72 | 600 | 67 | S/T | 0.703
80 | 72 | 600 | 67 | ∆T | 18.7
80 | 72 | 600 | 67 | LDB | 61.3
80 | 72 | 600 | 67 | LWB | 58
80 | 72 | 600 | 67 | kW | 0.96
84 | 72 | 600 | 70 | MBh | 19
84 | 72 | 600 | 70 | S/T | 0.668
84 | 72 | 600 | 70 | ∆T | 19.6
84 | 72 | 600 | 70 | LDB | 64.4
84 | 72 | 600 | 70 | LWB | 60.7
84 | 72 | 600 | 70 | kW | 1.12
86 | 72 | 600 | 72 | MBh | 20.2
86 | 72 | 600 | 72 | S/T | 0.658
86 | 72 | 600 | 72 | ∆T | 20.5
86 | 72 | 600 | 72 | LDB | 65.5
86 | 72 | 600 | 72 | LWB | 62.5
86 | 72 | 600 | 72 | kW | 1.23
90 | 72 | 600 | 75 | MBh | 20.7
90 | 72 | 600 | 75 | S/T | 0.633
90 | 72 | 600 | 75 | ∆T | 20.2
90 | 72 | 600 | 75 | LDB | 69.8
90 | 72 | 600 | 75 | LWB | 66
90 | 72 | 600 | 75 | kW | 1.25
68 | 75 | 600 | 57 | MBh | 11.2
68 | 75 | 600 | 57 | S/T | 0.871
68 | 75 | 600 | 57 | ∆T | 15.1
68 | 75 | 600 | 57 | LDB | 52.9
68 | 75 | 600 | 57 | LWB | 49.9
68 | 75 | 600 | 57 | kW | 0.56
72 | 75 | 600 | 61 | MBh | 13.6
72 | 75 | 600 | 61 | S/T | 0.809
72 | 75 | 600 | 61 | ∆T | 17
72 | 75 | 600 | 61 | LDB | 55
72 | 75 | 600 | 61 | LWB | 53
72 | 75 | 600 | 61 | kW | 0.73
77 | 75 | 600 | 64 | MBh | 15.4
77 | 75 | 600 | 64 | S/T | 0.76
77 | 75 | 600 | 64 | ∆T | 18.1
77 | 75 | 600 | 64 | LDB | 58.9
77 | 75 | 600 | 64 | LWB | 55.5
77 | 75 | 600 | 64 | kW | 0.87
80 | 75 | 600 | 67 | MBh | 17.2
80 | 75 | 600 | 67 | S/T | 0.703
80 | 75 | 600 | 67 | ∆T | 18.7
80 | 75 | 600 | 67 | LDB | 61.3
80 | 75 | 600 | 67 | LWB | 58
80 | 75 | 600 | 67 | kW | 1.02
84 | 75 | 600 | 70 | MBh | 19
84 | 75 | 600 | 70 | S/T | 0.668
84 | 75 | 600 | 70 | ∆T | 19.6
84 | 75 | 600 | 70 | LDB | 64.4
84 | 75 | 600 | 70 | LWB | 60.7
84 | 75 | 600 | 70 | kW | 1.18
86 | 75 | 600 | 72 | MBh | 20.1
86 | 75 | 600 | 72 | S/T | 0.662
86 | 75 | 600 | 72 | ∆T | 20.5
86 | 75 | 600 | 72 | LDB | 65.5
86 | 75 | 600 | 72 | LWB | 62.6
86 | 75 | 600 | 72 | kW | 1.29
90 | 75 | 600 | 75 | MBh | 20.5
90 | 75 | 600 | 75 | S/T | 0.629
90 | 75 | 600 | 75 | ∆T | 19.9
90 | 75 | 600 | 75 | LDB | 70.1
90 | 75 | 600 | 75 | LWB | 66
90 | 75 | 600 | 75 | kW | 1.3
68 | 79 | 600 | 57 | MBh | 11.2
68 | 79 | 600 | 57 | S/T | 0.871
68 | 79 | 600 | 57 | ∆T | 15.1
68 | 79 | 600 | 57 | LDB | 52.9
68 | 79 | 600 | 57 | LWB | 49.9
68 | 79 | 600 | 57 | kW | 0.6
72 | 79 | 600 | 61 | MBh | 13.6
72 | 79 | 600 | 61 | S/T | 0.809
72 | 79 | 600 | 61 | ∆T | 17
72 | 79 | 600 | 61 | LDB | 55
72 | 79 | 600 | 61 | LWB | 53
72 | 79 | 600 | 61 | kW | 0.78
77 | 79 | 600 | 64 | MBh | 15.4
77 | 79 | 600 | 64 | S/T | 0.76
77 | 79 | 600 | 64 | ∆T | 18.1
77 | 79 | 600 | 64 | LDB | 58.9
77 | 79 | 600 | 64 | LWB | 55.5
77 | 79 | 600 | 64 | kW | 0.93
80 | 79 | 600 | 67 | MBh | 17.2
80 | 79 | 600 | 67 | S/T | 0.703
80 | 79 | 600 | 67 | ∆T | 18.7
80 | 79 | 600 | 67 | LDB | 61.3
80 | 79 | 600 | 67 | LWB | 58
80 | 79 | 600 | 67 | kW | 1.1
84 | 79 | 600 | 70 | MBh | 19
84 | 79 | 600 | 70 | S/T | 0.668
84 | 79 | 600 | 70 | ∆T | 19.6
84 | 79 | 600 | 70 | LDB | 64.4
84 | 79 | 600 | 70 | LWB | 60.7
84 | 79 | 600 | 70 | kW | 1.28
86 | 79 | 600 | 72 | MBh | 19.8
86 | 79 | 600 | 72 | S/T | 0.657
86 | 79 | 600 | 72 | ∆T | 20.1
86 | 79 | 600 | 72 | LDB | 65.9
86 | 79 | 600 | 72 | LWB | 62.7
86 | 79 | 600 | 72 | kW | 1.35
90 | 79 | 600 | 75 | MBh | 20.1
90 | 79 | 600 | 75 | S/T | 0.632
90 | 79 | 600 | 75 | ∆T | 19.6
90 | 79 | 600 | 75 | LDB | 70.4
90 | 79 | 600 | 75 | LWB | 66.2
90 | 79 | 600 | 75 | kW | 1.36
68 | 83 | 600 | 57 | MBh | 11.2
68 | 83 | 600 | 57 | S/T | 0.871
68 | 83 | 600 | 57 | ∆T | 15.1
68 | 83 | 600 | 57 | LDB | 52.9
68 | 83 | 600 | 57 | LWB | 49.9
68 | 83 | 600 | 57 | kW | 0.65
72 | 83 | 600 | 61 | MBh | 13.6
72 | 83 | 600 | 61 | S/T | 0.809
72 | 83 | 600 | 61 | ∆T | 17
72 | 83 | 600 | 61 | LDB | 55
72 | 83 | 600 | 61 | LWB | 53
72 | 83 | 600 | 61 | kW | 0.84
77 | 83 | 600 | 64 | MBh | 15.4
77 | 83 | 600 | 64 | S/T | 0.76
77 | 83 | 600 | 64 | ∆T | 18.1
77 | 83 | 600 | 64 | LDB | 58.9
77 | 83 | 600 | 64 | LWB | 55.5
77 | 83 | 600 | 64 | kW | 1.01
80 | 83 | 600 | 67 | MBh | 17.2
80 | 83 | 600 | 67 | S/T | 0.703
80 | 83 | 600 | 67 | ∆T | 18.7
80 | 83 | 600 | 67 | LDB | 61.3
80 | 83 | 600 | 67 | LWB | 58
80 | 83 | 600 | 67 | kW | 1.18
84 | 83 | 600 | 70 | MBh | 19
84 | 83 | 600 | 70 | S/T | 0.668
84 | 83 | 600 | 70 | ∆T | 19.6
84 | 83 | 600 | 70 | LDB | 64.4
84 | 83 | 600 | 70 | LWB | 60.7
84 | 83 | 600 | 70 | kW | 1.38
86 | 83 | 600 | 72 | MBh | 19.5
86 | 83 | 600 | 72 | S/T | 0.656
86 | 83 | 600 | 72 | ∆T | 19.8
86 | 83 | 600 | 72 | LDB | 66.2
86 | 83 | 600 | 72 | LWB | 62.9
86 | 83 | 600 | 72 | kW | 1.41
90 | 83 | 600 | 75 | MBh | 19.8
90 | 83 | 600 | 75 | S/T | 0.631
90 | 83 | 600 | 75 | ∆T | 19.3
90 | 83 | 600 | 75 | LDB | 70.7
90 | 83 | 600 | 75 | LWB | 66.4
90 | 83 | 600 | 75 | kW | 1.42
68 | 87 | 600 | 57 | MBh | 11.2
68 | 87 | 600 | 57 | S/T | 0.871
68 | 87 | 600 | 57 | ∆T | 15.1
68 | 87 | 600 | 57 | LDB | 52.9
68 | 87 | 600 | 57 | LWB | 49.9
68 | 87 | 600 | 57 | kW | 0.69
72 | 87 | 600 | 61 | MBh | 13.6
72 | 87 | 600 | 61 | S/T | 0.809
72 | 87 | 600 | 61 | ∆T | 17
72 | 87 | 600 | 61 | LDB | 55
72 | 87 | 600 | 61 | LWB | 53
72 | 87 | 600 | 61 | kW | 0.9
77 | 87 | 600 | 64 | MBh | 15.4
77 | 87 | 600 | 64 | S/T | 0.76
77 | 87 | 600 | 64 | ∆T | 18.1
77 | 87 | 600 | 64 | LDB | 58.9
77 | 87 | 600 | 64 | LWB | 55.5
77 | 87 | 600 | 64 | kW | 1.08
80 | 87 | 600 | 67 | MBh | 17.2
80 | 87 | 600 | 67 | S/T | 0.703
80 | 87 | 600 | 67 | ∆T | 18.7
80 | 87 | 600 | 67 | LDB | 61.3
80 | 87 | 600 | 67 | LWB | 58
80 | 87 | 600 | 67 | kW | 1.27
84 | 87 | 600 | 70 | MBh | 18.9
84 | 87 | 600 | 70 | S/T | 0.672
84 | 87 | 600 | 70 | ∆T | 19.6
84 | 87 | 600 | 70 | LDB | 64.4
84 | 87 | 600 | 70 | LWB | 60.7
84 | 87 | 600 | 70 | kW | 1.47
86 | 87 | 600 | 72 | MBh | 19.1
86 | 87 | 600 | 72 | S/T | 0.66
86 | 87 | 600 | 72 | ∆T | 19.4
86 | 87 | 600 | 72 | LDB | 66.6
86 | 87 | 600 | 72 | LWB | 63.1
86 | 87 | 600 | 72 | kW | 1.47
90 | 87 | 600 | 75 | MBh | 19.5
90 | 87 | 600 | 75 | S/T | 0.631
90 | 87 | 600 | 75 | ∆T | 19
90 | 87 | 600 | 75 | LDB | 71
90 | 87 | 600 | 75 | LWB | 66.5
90 | 87 | 600 | 75 | kW | 1.48
68 | 91 | 600 | 57 | MBh | 11.2
68 | 91 | 600 | 57 | S/T | 0.871
68 | 91 | 600 | 57 | ∆T | 15.1
68 | 91 | 600 | 57 | LDB | 52.9
68 | 91 | 600 | 57 | LWB | 49.9
68 | 91 | 600 | 57 | kW | 0.74
72 | 91 | 600 | 61 | MBh | 13.6
72 | 91 | 600 | 61 | S/T | 0.809
72 | 91 | 600 | 61 | ∆T | 17
72 | 91 | 600 | 61 | LDB | 55
72 | 91 | 600 | 61 | LWB | 53
72 | 91 | 600 | 61 | kW | 0.97
77 | 91 | 600 | 64 | MBh | 15.4
77 | 91 | 600 | 64 | S/T | 0.76
77 | 91 | 600 | 64 | ∆T | 18.1
77 | 91 | 600 | 64 | LDB | 58.9
77 | 91 | 600 | 64 | LWB | 55.5
77 | 91 | 600 | 64 | kW | 1.16
80 | 91 | 600 | 67 | MBh | 17.2
80 | 91 | 600 | 67 | S/T | 0.703
80 | 91 | 600 | 67 | ∆T | 18.7
80 | 91 | 600 | 67 | LDB | 61.3
80 | 91 | 600 | 67 | LWB | 58
80 | 91 | 600 | 67 | kW | 1.37
84 | 91 | 600 | 70 | MBh | 18.6
84 | 91 | 600 | 70 | S/T | 0.672
84 | 91 | 600 | 70 | ∆T | 19.3
84 | 91 | 600 | 70 | LDB | 64.7
84 | 91 | 600 | 70 | LWB | 60.9
84 | 91 | 600 | 70 | kW | 1.53
86 | 91 | 600 | 72 | MBh | 18.8
86 | 91 | 600 | 72 | S/T | 0.66
86 | 91 | 600 | 72 | ∆T | 19.1
86 | 91 | 600 | 72 | LDB | 66.9
86 | 91 | 600 | 72 | LWB | 63.2
86 | 91 | 600 | 72 | kW | 1.53
90 | 91 | 600 | 75 | MBh | 19.2
90 | 91 | 600 | 75 | S/T | 0.63
90 | 91 | 600 | 75 | ∆T | 18.7
90 | 91 | 600 | 75 | LDB | 71.3
90 | 91 | 600 | 75 | LWB | 66.7
90 | 91 | 600 | 75 | kW | 1.54
68 | 93 | 600 | 57 | MBh | 11.2
68 | 93 | 600 | 57 | S/T | 0.871
68 | 93 | 600 | 57 | ∆T | 15.1
68 | 93 | 600 | 57 | LDB | 52.9
68 | 93 | 600 | 57 | LWB | 49.9
68 | 93 | 600 | 57 | kW | 0.77
72 | 93 | 600 | 61 | MBh | 13.6
72 | 93 | 600 | 61 | S/T | 0.809
72 | 93 | 600 | 61 | ∆T | 17
72 | 93 | 600 | 61 | LDB | 55
72 | 93 | 600 | 61 | LWB | 53
72 | 93 | 600 | 61 | kW | 1
77 | 93 | 600 | 64 | MBh | 15.4
77 | 93 | 600 | 64 | S/T | 0.76
77 | 93 | 600 | 64 | ∆T | 18.1
77 | 93 | 600 | 64 | LDB | 58.9
77 | 93 | 600 | 64 | LWB | 55.5
77 | 93 | 600 | 64 | kW | 1.2
80 | 93 | 600 | 67 | MBh | 17.2
80 | 93 | 600 | 67 | S/T | 0.703
80 | 93 | 600 | 67 | ∆T | 18.7
80 | 93 | 600 | 67 | LDB | 61.3
80 | 93 | 600 | 67 | LWB | 58
80 | 93 | 600 | 67 | kW | 1.42
84 | 93 | 600 | 70 | MBh | 18.4
84 | 93 | 600 | 70 | S/T | 0.668
84 | 93 | 600 | 70 | ∆T | 19
84 | 93 | 600 | 70 | LDB | 65
84 | 93 | 600 | 70 | LWB | 61
84 | 93 | 600 | 70 | kW | 1.56
86 | 93 | 600 | 72 | MBh | 18.6
86 | 93 | 600 | 72 | S/T | 0.661
86 | 93 | 600 | 72 | ∆T | 19
86 | 93 | 600 | 72 | LDB | 67
86 | 93 | 600 | 72 | LWB | 63.3
86 | 93 | 600 | 72 | kW | 1.57
90 | 93 | 600 | 75 | MBh | 19
90 | 93 | 600 | 75 | S/T | 0.632
90 | 93 | 600 | 75 | ∆T | 18.5
90 | 93 | 600 | 75 | LDB | 71.5
90 | 93 | 600 | 75 | LWB | 66.8
90 | 93 | 600 | 75 | kW | 1.58
68 | 95 | 600 | 57 | MBh | 11.2
68 | 95 | 600 | 57 | S/T | 0.871
68 | 95 | 600 | 57 | ∆T | 15.1
68 | 95 | 600 | 57 | LDB | 52.9
68 | 95 | 600 | 57 | LWB | 49.9
68 | 95 | 600 | 57 | kW | 0.79
72 | 95 | 600 | 61 | MBh | 13.6
72 | 95 | 600 | 61 | S/T | 0.809
72 | 95 | 600 | 61 | ∆T | 17
72 | 95 | 600 | 61 | LDB | 55
72 | 95 | 600 | 61 | LWB | 53
72 | 95 | 600 | 61 | kW | 1.04
77 | 95 | 600 | 64 | MBh | 15.4
77 | 95 | 600 | 64 | S/T | 0.76
77 | 95 | 600 | 64 | ∆T | 18.1
77 | 95 | 600 | 64 | LDB | 58.9
77 | 95 | 600 | 64 | LWB | 55.5
77 | 95 | 600 | 64 | kW | 1.25
80 | 95 | 600 | 67 | MBh | 17.2
80 | 95 | 600 | 67 | S/T | 0.703
80 | 95 | 600 | 67 | ∆T | 18.7
80 | 95 | 600 | 67 | LDB | 61.3
80 | 95 | 600 | 67 | LWB | 58
80 | 95 | 600 | 67 | kW | 1.47
84 | 95 | 600 | 70 | MBh | 18.2
84 | 95 | 600 | 70 | S/T | 0.67
84 | 95 | 600 | 70 | ∆T | 18.8
84 | 95 | 600 | 70 | LDB | 65.2
84 | 95 | 600 | 70 | LWB | 61.1
84 | 95 | 600 | 70 | kW | 1.59
86 | 95 | 600 | 72 | MBh | 18.5
86 | 95 | 600 | 72 | S/T | 0.659
86 | 95 | 600 | 72 | ∆T | 18.8
86 | 95 | 600 | 72 | LDB | 67.2
86 | 95 | 600 | 72 | LWB | 63.4
86 | 95 | 600 | 72 | kW | 1.6
90 | 95 | 600 | 75 | MBh | 18.8
90 | 95 | 600 | 75 | S/T | 0.633
90 | 95 | 600 | 75 | ∆T | 18.4
90 | 95 | 600 | 75 | LDB | 71.6
90 | 95 | 600 | 75 | LWB | 66.9
90 | 95 | 600 | 75 | kW | 1.61
68 | 99 | 600 | 57 | MBh | 11.2
68 | 99 | 600 | 57 | S/T | 0.871
68 | 99 | 600 | 57 | ∆T | 15.1
68 | 99 | 600 | 57 | LDB | 52.9
68 | 99 | 600 | 57 | LWB | 49.9
68 | 99 | 600 | 57 | kW | 0.85
72 | 99 | 600 | 61 | MBh | 13.6
72 | 99 | 600 | 61 | S/T | 0.809
72 | 99 | 600 | 61 | ∆T | 17
72 | 99 | 600 | 61 | LDB | 55
72 | 99 | 600 | 61 | LWB | 53
72 | 99 | 600 | 61 | kW | 1.11
77 | 99 | 600 | 64 | MBh | 15.4
77 | 99 | 600 | 64 | S/T | 0.76
77 | 99 | 600 | 64 | ∆T | 18.1
77 | 99 | 600 | 64 | LDB | 58.9
77 | 99 | 600 | 64 | LWB | 55.5
77 | 99 | 600 | 64 | kW | 1.34
80 | 99 | 600 | 67 | MBh | 17.2
80 | 99 | 600 | 67 | S/T | 0.703
80 | 99 | 600 | 67 | ∆T | 18.7
80 | 99 | 600 | 67 | LDB | 61.3
80 | 99 | 600 | 67 | LWB | 58
80 | 99 | 600 | 67 | kW | 1.58
84 | 99 | 600 | 70 | MBh | 17.9
84 | 99 | 600 | 70 | S/T | 0.676
84 | 99 | 600 | 70 | ∆T | 18.7
84 | 99 | 600 | 70 | LDB | 65.3
84 | 99 | 600 | 70 | LWB | 61.3
84 | 99 | 600 | 70 | kW | 1.65
86 | 99 | 600 | 72 | MBh | 18.2
86 | 99 | 600 | 72 | S/T | 0.659
86 | 99 | 600 | 72 | ∆T | 18.5
86 | 99 | 600 | 72 | LDB | 67.5
86 | 99 | 600 | 72 | LWB | 63.5
86 | 99 | 600 | 72 | kW | 1.66
90 | 99 | 600 | 75 | MBh | 18.5
90 | 99 | 600 | 75 | S/T | 0.638
90 | 99 | 600 | 75 | ∆T | 18.2
90 | 99 | 600 | 75 | LDB | 71.8
90 | 99 | 600 | 75 | LWB | 67
90 | 99 | 600 | 75 | kW | 1.67
68 | 103 | 600 | 57 | MBh | 11.2
68 | 103 | 600 | 57 | S/T | 0.871
68 | 103 | 600 | 57 | ∆T | 15.1
68 | 103 | 600 | 57 | LDB | 52.9
68 | 103 | 600 | 57 | LWB | 49.9
68 | 103 | 600 | 57 | kW | 0.91
72 | 103 | 600 | 61 | MBh | 13.6
72 | 103 | 600 | 61 | S/T | 0.809
72 | 103 | 600 | 61 | ∆T | 17
72 | 103 | 600 | 61 | LDB | 55
72 | 103 | 600 | 61 | LWB | 53
72 | 103 | 600 | 61 | kW | 1.19
77 | 103 | 600 | 64 | MBh | 15.4
77 | 103 | 600 | 64 | S/T | 0.76
77 | 103 | 600 | 64 | ∆T | 18.1
77 | 103 | 600 | 64 | LDB | 58.9
77 | 103 | 600 | 64 | LWB | 55.5
77 | 103 | 600 | 64 | kW | 1.43
80 | 103 | 600 | 67 | MBh | 17.2
80 | 103 | 600 | 67 | S/T | 0.703
80 | 103 | 600 | 67 | ∆T | 18.7
80 | 103 | 600 | 67 | LDB | 61.3
80 | 103 | 600 | 67 | LWB | 58
80 | 103 | 600 | 67 | kW | 1.69
84 | 103 | 600 | 70 | MBh | 17.6
84 | 103 | 600 | 70 | S/T | 0.676
84 | 103 | 600 | 70 | ∆T | 18.4
84 | 103 | 600 | 70 | LDB | 65.6
84 | 103 | 600 | 70 | LWB | 61.4
84 | 103 | 600 | 70 | kW | 1.71
86 | 103 | 600 | 72 | MBh | 17.8
86 | 103 | 600 | 72 | S/T | 0.663
86 | 103 | 600 | 72 | ∆T | 18.2
86 | 103 | 600 | 72 | LDB | 67.8
86 | 103 | 600 | 72 | LWB | 63.7
86 | 103 | 600 | 72 | kW | 1.72
90 | 103 | 600 | 75 | MBh | 18.2
90 | 103 | 600 | 75 | S/T | 0.637
90 | 103 | 600 | 75 | ∆T | 17.9
90 | 103 | 600 | 75 | LDB | 72.1
90 | 103 | 600 | 75 | LWB | 67.1
90 | 103 | 600 | 75 | kW | 1.74
68 | 106 | 600 | 57 | MBh | 11.2
68 | 106 | 600 | 57 | S/T | 0.871
68 | 106 | 600 | 57 | ∆T | 15.1
68 | 106 | 600 | 57 | LDB | 52.9
68 | 106 | 600 | 57 | LWB | 49.9
68 | 106 | 600 | 57 | kW | 1
72 | 106 | 600 | 61 | MBh | 13.6
72 | 106 | 600 | 61 | S/T | 0.809
72 | 106 | 600 | 61 | ∆T | 17
72 | 106 | 600 | 61 | LDB | 55
72 | 106 | 600 | 61 | LWB | 53
72 | 106 | 600 | 61 | kW | 1.31
77 | 106 | 600 | 64 | MBh | 15.4
77 | 106 | 600 | 64 | S/T | 0.76
77 | 106 | 600 | 64 | ∆T | 18.1
77 | 106 | 600 | 64 | LDB | 58.9
77 | 106 | 600 | 64 | LWB | 55.5
77 | 106 | 600 | 64 | kW | 1.58
80 | 106 | 600 | 67 | MBh | 17
80 | 106 | 600 | 67 | S/T | 0.706
80 | 106 | 600 | 67 | ∆T | 18.5
80 | 106 | 600 | 67 | LDB | 61.5
80 | 106 | 600 | 67 | LWB | 58.1
80 | 106 | 600 | 67 | kW | 1.83
84 | 106 | 600 | 70 | MBh | 17.4
84 | 106 | 600 | 70 | S/T | 0.672
84 | 106 | 600 | 70 | ∆T | 18.1
84 | 106 | 600 | 70 | LDB | 65.9
84 | 106 | 600 | 70 | LWB | 61.5
84 | 106 | 600 | 70 | kW | 1.85
86 | 106 | 600 | 72 | MBh | 17.6
86 | 106 | 600 | 72 | S/T | 0.665
86 | 106 | 600 | 72 | ∆T | 18.1
86 | 106 | 600 | 72 | LDB | 67.9
86 | 106 | 600 | 72 | LWB | 63.8
86 | 106 | 600 | 72 | kW | 1.86
90 | 106 | 600 | 75 | MBh | 18
90 | 106 | 600 | 75 | S/T | 0.633
90 | 106 | 600 | 75 | ∆T | 17.6
90 | 106 | 600 | 75 | LDB | 72.4
90 | 106 | 600 | 75 | LWB | 67.2
90 | 106 | 600 | 75 | kW | 1.87
68 | 110 | 600 | 57 | MBh | 11.2
68 | 110 | 600 | 57 | S/T | 0.871
68 | 110 | 600 | 57 | ∆T | 15.1
68 | 110 | 600 | 57 | LDB | 52.9
68 | 110 | 600 | 57 | LWB | 49.9
68 | 110 | 600 | 57 | kW | 1.14
72 | 110 | 600 | 61 | MBh | 13.6
72 | 110 | 600 | 61 | S/T | 0.809
72 | 110 | 600 | 61 | ∆T | 17
72 | 110 | 600 | 61 | LDB | 55
72 | 110 | 600 | 61 | LWB | 53
72 | 110 | 600 | 61 | kW | 1.51
77 | 110 | 600 | 64 | MBh | 15.4
77 | 110 | 600 | 64 | S/T | 0.76
77 | 110 | 600 | 64 | ∆T | 18.1
77 | 110 | 600 | 64 | LDB | 58.9
77 | 110 | 600 | 64 | LWB | 55.5
77 | 110 | 600 | 64 | kW | 1.81
80 | 110 | 600 | 67 | MBh | 16.7
80 | 110 | 600 | 67 | S/T | 0.707
80 | 110 | 600 | 67 | ∆T | 18.2
80 | 110 | 600 | 67 | LDB | 61.8
80 | 110 | 600 | 67 | LWB | 58.3
80 | 110 | 600 | 67 | kW | 2.03
84 | 110 | 600 | 70 | MBh | 17
84 | 110 | 600 | 70 | S/T | 0.676
84 | 110 | 600 | 70 | ∆T | 17.7
84 | 110 | 600 | 70 | LDB | 66.3
84 | 110 | 600 | 70 | LWB | 61.8
84 | 110 | 600 | 70 | kW | 2.05
86 | 110 | 600 | 72 | MBh | 17.3
86 | 110 | 600 | 72 | S/T | 0.659
86 | 110 | 600 | 72 | ∆T | 17.6
86 | 110 | 600 | 72 | LDB | 68.4
86 | 110 | 600 | 72 | LWB | 64
86 | 110 | 600 | 72 | kW | 2.06
90 | 110 | 600 | 75 | MBh | 17.3
90 | 110 | 600 | 75 | S/T | 0.636
90 | 110 | 600 | 75 | ∆T | 17
90 | 110 | 600 | 75 | LDB | 73
90 | 110 | 600 | 75 | LWB | 67.6
90 | 110 | 600 | 75 | kW | 2.06
68 | 115 | 600 | 57 | MBh | 11.2
68 | 115 | 600 | 57 | S/T | 0.871
68 | 115 | 600 | 57 | ∆T | 15.1
68 | 115 | 600 | 57 | LDB | 52.9
68 | 115 | 600 | 57 | LWB | 49.9
68 | 115 | 600 | 57 | kW | 1.34
72 | 115 | 600 | 61 | MBh | 13.6
72 | 115 | 600 | 61 | S/T | 0.809
72 | 115 | 600 | 61 | ∆T | 17
72 | 115 | 600 | 61 | LDB | 55
72 | 115 | 600 | 61 | LWB | 53
72 | 115 | 600 | 61 | kW | 1.77
77 | 115 | 600 | 64 | MBh | 15.4
77 | 115 | 600 | 64 | S/T | 0.76
77 | 115 | 600 | 64 | ∆T | 18.1
77 | 115 | 600 | 64 | LDB | 58.9
77 | 115 | 600 | 64 | LWB | 55.5
77 | 115 | 600 | 64 | kW | 2.13
80 | 115 | 600 | 67 | MBh | 16.1
80 | 115 | 600 | 67 | S/T | 0.708
80 | 115 | 600 | 67 | ∆T | 17.6
80 | 115 | 600 | 67 | LDB | 62.4
80 | 115 | 600 | 67 | LWB | 58.7
80 | 115 | 600 | 67 | kW | 2.27
84 | 115 | 600 | 70 | MBh | 16.1
84 | 115 | 600 | 70 | S/T | 0.671
84 | 115 | 600 | 70 | ∆T | 16.7
84 | 115 | 600 | 70 | LDB | 67.3
84 | 115 | 600 | 70 | LWB | 62.2
84 | 115 | 600 | 70 | kW | 2.27
86 | 115 | 600 | 72 | MBh | 16.1
86 | 115 | 600 | 72 | S/T | 0.665
86 | 115 | 600 | 72 | ∆T | 16.5
86 | 115 | 600 | 72 | LDB | 69.5
86 | 115 | 600 | 72 | LWB | 64.6
86 | 115 | 600 | 72 | kW | 2.27
90 | 115 | 600 | 75 | MBh | 16.1
90 | 115 | 600 | 75 | S/T | 0.634
90 | 115 | 600 | 75 | ∆T | 15.7
90 | 115 | 600 | 75 | LDB | 74.3
90 | 115 | 600 | 75 | LWB | 68.1
90 | 115 | 600 | 75 | kW | 2.27
68 | 118 | 600 | 57 | MBh | 11.2
68 | 118 | 600 | 57 | S/T | 0.871
68 | 118 | 600 | 57 | ∆T | 15.1
68 | 118 | 600 | 57 | LDB | 52.9
68 | 118 | 600 | 57 | LWB | 49.9
68 | 118 | 600 | 57 | kW | 1.46
72 | 118 | 600 | 61 | MBh | 13.6
72 | 118 | 600 | 61 | S/T | 0.809
72 | 118 | 600 | 61 | ∆T | 17
72 | 118 | 600 | 61 | LDB | 55
72 | 118 | 600 | 61 | LWB | 53
72 | 118 | 600 | 61 | kW | 1.93
77 | 118 | 600 | 64 | MBh | 13.7
77 | 118 | 600 | 64 | S/T | 0.766
77 | 118 | 600 | 64 | ∆T | 16.2
77 | 118 | 600 | 64 | LDB | 60.8
77 | 118 | 600 | 64 | LWB | 56.5
77 | 118 | 600 | 64 | kW | 1.96
80 | 118 | 600 | 67 | MBh | 13.7
80 | 118 | 600 | 67 | S/T | 0.707
80 | 118 | 600 | 67 | ∆T | 15
80 | 118 | 600 | 67 | LDB | 65
80 | 118 | 600 | 67 | LWB | 60
80 | 118 | 600 | 67 | kW | 1.96
84 | 118 | 600 | 70 | MBh | 13.7
84 | 118 | 600 | 70 | S/T | 0.674
84 | 118 | 600 | 70 | ∆T | 14.3
84 | 118 | 600 | 70 | LDB | 69.7
84 | 118 | 600 | 70 | LWB | 63.5
84 | 118 | 600 | 70 | kW | 1.96
86 | 118 | 600 | 72 | MBh | 13.7
86 | 118 | 600 | 72 | S/T | 0.664
86 | 118 | 600 | 72 | ∆T | 14
86 | 118 | 600 | 72 | LDB | 72
86 | 118 | 600 | 72 | LWB | 65.8
86 | 118 | 600 | 72 | kW | 1.96
90 | 118 | 600 | 75 | MBh | 13.7
90 | 118 | 600 | 75 | S/T | 0.636
90 | 118 | 600 | 75 | ∆T | 13.4
90 | 118 | 600 | 75 | LDB | 76.6
90 | 118 | 600 | 75 | LWB | 69.2
90 | 118 | 600 | 75 | kW | 1.96
68 | 122 | 600 | 57 | MBh | 10.3
68 | 122 | 600 | 57 | S/T | 0.875
68 | 122 | 600 | 57 | ∆T | 13.9
68 | 122 | 600 | 57 | LDB | 54.1
68 | 122 | 600 | 57 | LWB | 50.5
68 | 122 | 600 | 57 | kW | 1.46
72 | 122 | 600 | 61 | MBh | 10.3
72 | 122 | 600 | 61 | S/T | 0.811
72 | 122 | 600 | 61 | ∆T | 12.9
72 | 122 | 600 | 61 | LDB | 59.1
72 | 122 | 600 | 61 | LWB | 55.1
72 | 122 | 600 | 61 | kW | 1.46
77 | 122 | 600 | 64 | MBh | 10.3
77 | 122 | 600 | 64 | S/T | 0.762
77 | 122 | 600 | 64 | ∆T | 12.1
77 | 122 | 600 | 64 | LDB | 64.9
77 | 122 | 600 | 64 | LWB | 58.5
77 | 122 | 600 | 64 | kW | 1.46
80 | 122 | 600 | 67 | MBh | 10.3
80 | 122 | 600 | 67 | S/T | 0.707
80 | 122 | 600 | 67 | ∆T | 11.2
80 | 122 | 600 | 67 | LDB | 68.8
80 | 122 | 600 | 67 | LWB | 61.8
80 | 122 | 600 | 67 | kW | 1.46
84 | 122 | 600 | 70 | MBh | 10.3
84 | 122 | 600 | 70 | S/T | 0.674
84 | 122 | 600 | 70 | ∆T | 10.7
84 | 122 | 600 | 70 | LDB | 73.3
84 | 122 | 600 | 70 | LWB | 65.2
84 | 122 | 600 | 70 | kW | 1.46
86 | 122 | 600 | 72 | MBh | 10.3
86 | 122 | 600 | 72 | S/T | 0.663
86 | 122 | 600 | 72 | ∆T | 10.5
86 | 122 | 600 | 72 | LDB | 75.5
86 | 122 | 600 | 72 | LWB | 67.4
86 | 122 | 600 | 72 | kW | 1.46
90 | 122 | 600 | 75 | MBh | 10.3
90 | 122 | 600 | 75 | S/T | 0.636
90 | 122 | 600 | 75 | ∆T | 10.1
90 | 122 | 600 | 75 | LDB | 79.9
90 | 122 | 600 | 75 | LWB | 70.7
90 | 122 | 600 | 75 | kW | 1.46

## RZA24AAVJU - FTA24AAVJUD
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 800 | 57 | MBh | 15.6 | 64 | 60 | 61 | 32.4 | 3.14
68 | 23 | 800 | 57 | S/T | 0.878 | 64 | 60 | 65 | 30 | 2.85
68 | 23 | 800 | 57 | ∆T | 15.9 | 64 | 60 | 68 | 28.2 | 2.66
68 | 23 | 800 | 57 | LDB | 52.1 | 64 | 60 | 70 | 27 | 2.54
68 | 23 | 800 | 57 | LWB | 49.6 | 64 | 60 | 72 | 25.8 | 2.43
68 | 23 | 800 | 57 | kW | 0.6 | 64 | 60 | 75 | 24 | 2.28
72 | 23 | 800 | 61 | MBh | 18.9 | 60 | 56 | 61 | 32.4 | 3.29
72 | 23 | 800 | 61 | S/T | 0.815 | 60 | 56 | 65 | 30 | 2.97
72 | 23 | 800 | 61 | ∆T | 17.8 | 60 | 56 | 68 | 28.2 | 2.76
72 | 23 | 800 | 61 | LDB | 54.2 | 60 | 56 | 70 | 27 | 2.63
72 | 23 | 800 | 61 | LWB | 52.7 | 60 | 56 | 72 | 25.8 | 2.51
72 | 23 | 800 | 61 | kW | 0.74 | 60 | 56 | 75 | 24 | 2.34
77 | 23 | 800 | 64 | MBh | 21.5 | 57 | 53 | 61 | 32.4 | 3.4
77 | 23 | 800 | 64 | S/T | 0.758 | 57 | 53 | 65 | 30 | 3.07
77 | 23 | 800 | 64 | ∆T | 18.9 | 57 | 53 | 68 | 28.2 | 2.84
77 | 23 | 800 | 64 | LDB | 58.1 | 57 | 53 | 70 | 27 | 2.7
77 | 23 | 800 | 64 | LWB | 55 | 57 | 53 | 72 | 25.8 | 2.57
77 | 23 | 800 | 64 | kW | 0.85 | 57 | 53 | 75 | 24 | 2.4
80 | 23 | 800 | 67 | MBh | 24 | 54 | 50 | 61 | 32.4 | 3.53
80 | 23 | 800 | 67 | S/T | 0.704 | 54 | 50 | 65 | 30 | 3.18
80 | 23 | 800 | 67 | ∆T | 19.6 | 54 | 50 | 68 | 28.2 | 2.93
80 | 23 | 800 | 67 | LDB | 60.4 | 54 | 50 | 70 | 27 | 2.78
80 | 23 | 800 | 67 | LWB | 57.6 | 54 | 50 | 72 | 25.8 | 2.64
80 | 23 | 800 | 67 | kW | 0.96 | 54 | 50 | 75 | 24 | 2.45
84 | 23 | 800 | 70 | MBh | 26.5 | 51 | 47 | 61 | 32.4 | 3.67
84 | 23 | 800 | 70 | S/T | 0.672 | 51 | 47 | 65 | 30 | 3.29
84 | 23 | 800 | 70 | ∆T | 20.6 | 51 | 47 | 68 | 28.2 | 3.03
84 | 23 | 800 | 70 | LDB | 63.4 | 51 | 47 | 70 | 27 | 2.87
84 | 23 | 800 | 70 | LWB | 60.2 | 51 | 47 | 72 | 25.8 | 2.72
84 | 23 | 800 | 70 | kW | 1.08 | 51 | 47 | 75 | 24 | 2.52
86 | 23 | 800 | 72 | MBh | 28.2 | 47 | 43 | 61 | 32.4 | 3.89
86 | 23 | 800 | 72 | S/T | 0.663 | 47 | 43 | 65 | 30 | 3.47
86 | 23 | 800 | 72 | ∆T | 21.6 | 47 | 43 | 68 | 28.2 | 3.18
86 | 23 | 800 | 72 | LDB | 64.4 | 47 | 43 | 70 | 27 | 3.01
86 | 23 | 800 | 72 | LWB | 62 | 47 | 43 | 72 | 25.8 | 2.84
86 | 23 | 800 | 72 | kW | 1.16 | 47 | 43 | 75 | 24 | 2.62
90 | 23 | 800 | 75 | MBh | 30.7 | 44 | 40 | 61 | 32.4 | 4.06
90 | 23 | 800 | 75 | S/T | 0.619 | 44 | 40 | 65 | 30 | 3.61
90 | 23 | 800 | 75 | ∆T | 22 | 44 | 40 | 68 | 28.2 | 3.31
90 | 23 | 800 | 75 | LDB | 68 | 44 | 40 | 70 | 27 | 3.12
90 | 23 | 800 | 75 | LWB | 64.8 | 44 | 40 | 72 | 25.8 | 2.95
90 | 23 | 800 | 75 | kW | 1.28 | 44 | 40 | 75 | 24 | 2.7
68 | 30 | 800 | 57 | MBh | 15.6 | 39 | 36 | 61 | 32.4 | 4.33
68 | 30 | 800 | 57 | S/T | 0.878 | 39 | 36 | 65 | 30 | 3.84
68 | 30 | 800 | 57 | ∆T | 15.9 | 39 | 36 | 68 | 28.2 | 3.5
68 | 30 | 800 | 57 | LDB | 52.1 | 39 | 36 | 70 | 27 | 3.29
68 | 30 | 800 | 57 | LWB | 49.6 | 39 | 36 | 72 | 25.8 | 3.1
68 | 30 | 800 | 57 | kW | 0.62 | 39 | 36 | 75 | 24 | 2.83
72 | 30 | 800 | 61 | MBh | 18.9 | 35 | 32 | 61 | 31.7 | 4.3
72 | 30 | 800 | 61 | S/T | 0.815 | 35 | 32 | 65 | 30 | 4.09
72 | 30 | 800 | 61 | ∆T | 17.8 | 35 | 32 | 68 | 28.2 | 3.72
72 | 30 | 800 | 61 | LDB | 54.2 | 35 | 32 | 70 | 27 | 3.49
72 | 30 | 800 | 61 | LWB | 52.7 | 35 | 32 | 72 | 25.8 | 3.27
72 | 30 | 800 | 61 | kW | 0.76 | 35 | 32 | 75 | 24 | 2.98
77 | 30 | 800 | 64 | MBh | 21.5 | 30 | 28 | 61 | 30.1 | 3.92
77 | 30 | 800 | 64 | S/T | 0.758 | 30 | 28 | 65 | 30 | 4.38
77 | 30 | 800 | 64 | ∆T | 18.9 | 30 | 28 | 68 | 28.2 | 3.97
77 | 30 | 800 | 64 | LDB | 58.1 | 30 | 28 | 70 | 27 | 3.72
77 | 30 | 800 | 64 | LWB | 55 | 30 | 28 | 72 | 25.8 | 3.48
77 | 30 | 800 | 64 | kW | 0.88 | 30 | 28 | 75 | 24 | 3.15
80 | 30 | 800 | 67 | MBh | 24 | 26 | 24 | 61 | 28.6 | 3.56
80 | 30 | 800 | 67 | S/T | 0.704 | 26 | 24 | 65 | 28.6 | 4.18
80 | 30 | 800 | 67 | ∆T | 19.6 | 26 | 24 | 68 | 28.2 | 4.24
80 | 30 | 800 | 67 | LDB | 60.4 | 26 | 24 | 70 | 27 | 3.98
80 | 30 | 800 | 67 | LWB | 57.6 | 26 | 24 | 72 | 25.8 | 3.72
80 | 30 | 800 | 67 | kW | 0.99 | 26 | 24 | 75 | 24 | 3.35
84 | 30 | 800 | 70 | MBh | 26.5 | 22 | 20 | 61 | 27 | 3.24
84 | 30 | 800 | 70 | S/T | 0.672 | 22 | 20 | 65 | 27 | 3.77
84 | 30 | 800 | 70 | ∆T | 20.6 | 22 | 20 | 68 | 27 | 4.03
84 | 30 | 800 | 70 | LDB | 63.4 | 22 | 20 | 70 | 27 | 4.03
84 | 30 | 800 | 70 | LWB | 60.2 | 22 | 20 | 72 | 25.8 | 4
84 | 30 | 800 | 70 | kW | 1.12 | 22 | 20 | 75 | 24 | 3.58
86 | 30 | 800 | 72 | MBh | 28.2 | 19 | 18 | 61 | 26.3 | 3.1
86 | 30 | 800 | 72 | S/T | 0.663 | 19 | 18 | 65 | 26.3 | 3.58
86 | 30 | 800 | 72 | ∆T | 21.6 | 19 | 18 | 68 | 26.3 | 3.93
86 | 30 | 800 | 72 | LDB | 64.4 | 19 | 18 | 70 | 26.3 | 3.93
86 | 30 | 800 | 72 | LWB | 62 | 19 | 18 | 72 | 25.8 | 3.93
86 | 30 | 800 | 72 | kW | 1.2 | 19 | 18 | 75 | 24 | 3.72
90 | 30 | 800 | 75 | MBh | 30.7 | 17 | 16 | 61 | 25.3 | 2.95
90 | 30 | 800 | 75 | S/T | 0.619 | 17 | 16 | 65 | 25.3 | 3.36
90 | 30 | 800 | 75 | ∆T | 22 | 17 | 16 | 68 | 25.3 | 3.8
90 | 30 | 800 | 75 | LDB | 68 | 17 | 16 | 70 | 25.3 | 3.8
90 | 30 | 800 | 75 | LWB | 64.8 | 17 | 16 | 72 | 25.3 | 3.8
90 | 30 | 800 | 75 | kW | 1.32 | 17 | 16 | 75 | 24 | 3.8
68 | 40 | 800 | 57 | MBh | 15.6 | 15 | 14 | 61 | 24.7 | 2.88
68 | 40 | 800 | 57 | S/T | 0.878 | 15 | 14 | 65 | 24.7 | 3.24
68 | 40 | 800 | 57 | ∆T | 15.9 | 15 | 14 | 68 | 24.7 | 3.65
68 | 40 | 800 | 57 | LDB | 52.1 | 15 | 14 | 70 | 24.7 | 3.72
68 | 40 | 800 | 57 | LWB | 49.6 | 15 | 14 | 72 | 24.7 | 3.72
68 | 40 | 800 | 57 | kW | 0.65 | 15 | 14 | 75 | 24 | 3.72
72 | 40 | 800 | 61 | MBh | 18.9 | 13 | 12 | 61 | 23.9 | 2.81
72 | 40 | 800 | 61 | S/T | 0.815 | 13 | 12 | 65 | 23.9 | 3.09
72 | 40 | 800 | 61 | ∆T | 17.8 | 13 | 12 | 68 | 23.9 | 3.46
72 | 40 | 800 | 61 | LDB | 54.2 | 13 | 12 | 70 | 23.9 | 3.62
72 | 40 | 800 | 61 | LWB | 52.7 | 13 | 12 | 72 | 23.9 | 3.62
72 | 40 | 800 | 61 | kW | 0.8 | 13 | 12 | 75 | 23.9 | 3.62
77 | 40 | 800 | 64 | MBh | 21.5 | 10 | 9 | 61 | 22.6 | 2.75
77 | 40 | 800 | 64 | S/T | 0.758 | 10 | 9 | 65 | 22.6 | 2.88
77 | 40 | 800 | 64 | ∆T | 18.9 | 10 | 9 | 68 | 22.6 | 3.15
77 | 40 | 800 | 64 | LDB | 58.1 | 10 | 9 | 70 | 22.6 | 3.42
77 | 40 | 800 | 64 | LWB | 55 | 10 | 9 | 72 | 22.6 | 3.44
77 | 40 | 800 | 64 | kW | 0.92 | 10 | 9 | 75 | 22.6 | 3.44
80 | 40 | 800 | 67 | MBh | 24 | 6 | 5 | 61 | 21.2 | 2.82
80 | 40 | 800 | 67 | S/T | 0.704 | 6 | 5 | 65 | 21.2 | 2.76
80 | 40 | 800 | 67 | ∆T | 19.6 | 6 | 5 | 68 | 21.2 | 2.91
80 | 40 | 800 | 67 | LDB | 60.4 | 6 | 5 | 70 | 21.2 | 3.11
80 | 40 | 800 | 67 | LWB | 57.6 | 6 | 5 | 72 | 21.2 | 3.26
80 | 40 | 800 | 67 | kW | 1.04 | 6 | 5 | 75 | 21.2 | 3.26
84 | 40 | 800 | 70 | MBh | 26.5 | -2 | -2 | 61 | 18.4 | 2.89
84 | 40 | 800 | 70 | S/T | 0.672 | -2 | -2 | 65 | 18.4 | 2.89
84 | 40 | 800 | 70 | ∆T | 20.6 | -2 | -2 | 68 | 18.4 | 2.77
84 | 40 | 800 | 70 | LDB | 63.4 | -2 | -2 | 70 | 18.4 | 2.75
84 | 40 | 800 | 70 | LWB | 60.2 | -2 | -2 | 72 | 18.4 | 2.83
84 | 40 | 800 | 70 | kW | 1.17 | -2 | -2 | 75 | 18.4 | 2.89
86 | 40 | 800 | 72 | MBh | 28.2 | -4 | -4 | 61 | 17.7 | 2.79
86 | 40 | 800 | 72 | S/T | 0.663 | -4 | -4 | 65 | 17.7 | 2.79
86 | 40 | 800 | 72 | ∆T | 21.6 | -4 | -4 | 68 | 17.7 | 2.79
86 | 40 | 800 | 72 | LDB | 64.4 | -4 | -4 | 70 | 17.7 | 2.75
86 | 40 | 800 | 72 | LWB | 62 | -4 | -4 | 72 | 17.7 | 2.76
86 | 40 | 800 | 72 | kW | 1.26 | -4 | -4 | 75 | 17.7 | 2.79
90 | 40 | 800 | 75 | MBh | 30.7
90 | 40 | 800 | 75 | S/T | 0.619
90 | 40 | 800 | 75 | ∆T | 22
90 | 40 | 800 | 75 | LDB | 68
90 | 40 | 800 | 75 | LWB | 64.8
90 | 40 | 800 | 75 | kW | 1.39
68 | 50 | 800 | 57 | MBh | 15.6
68 | 50 | 800 | 57 | S/T | 0.878
68 | 50 | 800 | 57 | ∆T | 15.9
68 | 50 | 800 | 57 | LDB | 52.1
68 | 50 | 800 | 57 | LWB | 49.6
68 | 50 | 800 | 57 | kW | 0.68
72 | 50 | 800 | 61 | MBh | 18.9
72 | 50 | 800 | 61 | S/T | 0.815
72 | 50 | 800 | 61 | ∆T | 17.8
72 | 50 | 800 | 61 | LDB | 54.2
72 | 50 | 800 | 61 | LWB | 52.7
72 | 50 | 800 | 61 | kW | 0.84
77 | 50 | 800 | 64 | MBh | 21.5
77 | 50 | 800 | 64 | S/T | 0.758
77 | 50 | 800 | 64 | ∆T | 18.9
77 | 50 | 800 | 64 | LDB | 58.1
77 | 50 | 800 | 64 | LWB | 55
77 | 50 | 800 | 64 | kW | 0.97
80 | 50 | 800 | 67 | MBh | 24
80 | 50 | 800 | 67 | S/T | 0.704
80 | 50 | 800 | 67 | ∆T | 19.6
80 | 50 | 800 | 67 | LDB | 60.4
80 | 50 | 800 | 67 | LWB | 57.6
80 | 50 | 800 | 67 | kW | 1.1
84 | 50 | 800 | 70 | MBh | 26.5
84 | 50 | 800 | 70 | S/T | 0.672
84 | 50 | 800 | 70 | ∆T | 20.6
84 | 50 | 800 | 70 | LDB | 63.4
84 | 50 | 800 | 70 | LWB | 60.2
84 | 50 | 800 | 70 | kW | 1.23
86 | 50 | 800 | 72 | MBh | 28.2
86 | 50 | 800 | 72 | S/T | 0.663
86 | 50 | 800 | 72 | ∆T | 21.6
86 | 50 | 800 | 72 | LDB | 64.4
86 | 50 | 800 | 72 | LWB | 62
86 | 50 | 800 | 72 | kW | 1.32
90 | 50 | 800 | 75 | MBh | 30.7
90 | 50 | 800 | 75 | S/T | 0.619
90 | 50 | 800 | 75 | ∆T | 22
90 | 50 | 800 | 75 | LDB | 68
90 | 50 | 800 | 75 | LWB | 64.8
90 | 50 | 800 | 75 | kW | 1.46
68 | 54 | 800 | 57 | MBh | 15.6
68 | 54 | 800 | 57 | S/T | 0.878
68 | 54 | 800 | 57 | ∆T | 15.9
68 | 54 | 800 | 57 | LDB | 52.1
68 | 54 | 800 | 57 | LWB | 49.6
68 | 54 | 800 | 57 | kW | 0.69
72 | 54 | 800 | 61 | MBh | 18.9
72 | 54 | 800 | 61 | S/T | 0.815
72 | 54 | 800 | 61 | ∆T | 17.8
72 | 54 | 800 | 61 | LDB | 54.2
72 | 54 | 800 | 61 | LWB | 52.7
72 | 54 | 800 | 61 | kW | 0.86
77 | 54 | 800 | 64 | MBh | 21.5
77 | 54 | 800 | 64 | S/T | 0.758
77 | 54 | 800 | 64 | ∆T | 18.9
77 | 54 | 800 | 64 | LDB | 58.1
77 | 54 | 800 | 64 | LWB | 55
77 | 54 | 800 | 64 | kW | 0.99
80 | 54 | 800 | 67 | MBh | 24
80 | 54 | 800 | 67 | S/T | 0.704
80 | 54 | 800 | 67 | ∆T | 19.6
80 | 54 | 800 | 67 | LDB | 60.4
80 | 54 | 800 | 67 | LWB | 57.6
80 | 54 | 800 | 67 | kW | 1.12
84 | 54 | 800 | 70 | MBh | 26.5
84 | 54 | 800 | 70 | S/T | 0.672
84 | 54 | 800 | 70 | ∆T | 20.6
84 | 54 | 800 | 70 | LDB | 63.4
84 | 54 | 800 | 70 | LWB | 60.2
84 | 54 | 800 | 70 | kW | 1.26
86 | 54 | 800 | 72 | MBh | 28.2
86 | 54 | 800 | 72 | S/T | 0.663
86 | 54 | 800 | 72 | ∆T | 21.6
86 | 54 | 800 | 72 | LDB | 64.4
86 | 54 | 800 | 72 | LWB | 62
86 | 54 | 800 | 72 | kW | 1.35
90 | 54 | 800 | 75 | MBh | 30.7
90 | 54 | 800 | 75 | S/T | 0.619
90 | 54 | 800 | 75 | ∆T | 22
90 | 54 | 800 | 75 | LDB | 68
90 | 54 | 800 | 75 | LWB | 64.8
90 | 54 | 800 | 75 | kW | 1.49
68 | 58 | 800 | 57 | MBh | 15.6
68 | 58 | 800 | 57 | S/T | 0.878
68 | 58 | 800 | 57 | ∆T | 15.9
68 | 58 | 800 | 57 | LDB | 52.1
68 | 58 | 800 | 57 | LWB | 49.6
68 | 58 | 800 | 57 | kW | 0.7
72 | 58 | 800 | 61 | MBh | 18.9
72 | 58 | 800 | 61 | S/T | 0.815
72 | 58 | 800 | 61 | ∆T | 17.8
72 | 58 | 800 | 61 | LDB | 54.2
72 | 58 | 800 | 61 | LWB | 52.7
72 | 58 | 800 | 61 | kW | 0.87
77 | 58 | 800 | 64 | MBh | 21.5
77 | 58 | 800 | 64 | S/T | 0.758
77 | 58 | 800 | 64 | ∆T | 18.9
77 | 58 | 800 | 64 | LDB | 58.1
77 | 58 | 800 | 64 | LWB | 55
77 | 58 | 800 | 64 | kW | 1.01
80 | 58 | 800 | 67 | MBh | 24
80 | 58 | 800 | 67 | S/T | 0.704
80 | 58 | 800 | 67 | ∆T | 19.6
80 | 58 | 800 | 67 | LDB | 60.4
80 | 58 | 800 | 67 | LWB | 57.6
80 | 58 | 800 | 67 | kW | 1.14
84 | 58 | 800 | 70 | MBh | 26.5
84 | 58 | 800 | 70 | S/T | 0.672
84 | 58 | 800 | 70 | ∆T | 20.6
84 | 58 | 800 | 70 | LDB | 63.4
84 | 58 | 800 | 70 | LWB | 60.2
84 | 58 | 800 | 70 | kW | 1.28
86 | 58 | 800 | 72 | MBh | 28.2
86 | 58 | 800 | 72 | S/T | 0.663
86 | 58 | 800 | 72 | ∆T | 21.6
86 | 58 | 800 | 72 | LDB | 64.4
86 | 58 | 800 | 72 | LWB | 62
86 | 58 | 800 | 72 | kW | 1.38
90 | 58 | 800 | 75 | MBh | 30.5
90 | 58 | 800 | 75 | S/T | 0.616
90 | 58 | 800 | 75 | ∆T | 21.8
90 | 58 | 800 | 75 | LDB | 68.2
90 | 58 | 800 | 75 | LWB | 64.9
90 | 58 | 800 | 75 | kW | 1.5
68 | 62 | 800 | 57 | MBh | 15.6
68 | 62 | 800 | 57 | S/T | 0.878
68 | 62 | 800 | 57 | ∆T | 15.9
68 | 62 | 800 | 57 | LDB | 52.1
68 | 62 | 800 | 57 | LWB | 49.6
68 | 62 | 800 | 57 | kW | 0.72
72 | 62 | 800 | 61 | MBh | 18.9
72 | 62 | 800 | 61 | S/T | 0.815
72 | 62 | 800 | 61 | ∆T | 17.8
72 | 62 | 800 | 61 | LDB | 54.2
72 | 62 | 800 | 61 | LWB | 52.7
72 | 62 | 800 | 61 | kW | 0.89
77 | 62 | 800 | 64 | MBh | 21.5
77 | 62 | 800 | 64 | S/T | 0.758
77 | 62 | 800 | 64 | ∆T | 18.9
77 | 62 | 800 | 64 | LDB | 58.1
77 | 62 | 800 | 64 | LWB | 55
77 | 62 | 800 | 64 | kW | 1.03
80 | 62 | 800 | 67 | MBh | 24
80 | 62 | 800 | 67 | S/T | 0.704
80 | 62 | 800 | 67 | ∆T | 19.6
80 | 62 | 800 | 67 | LDB | 60.4
80 | 62 | 800 | 67 | LWB | 57.6
80 | 62 | 800 | 67 | kW | 1.17
84 | 62 | 800 | 70 | MBh | 26.5
84 | 62 | 800 | 70 | S/T | 0.672
84 | 62 | 800 | 70 | ∆T | 20.6
84 | 62 | 800 | 70 | LDB | 63.4
84 | 62 | 800 | 70 | LWB | 60.2
84 | 62 | 800 | 70 | kW | 1.31
86 | 62 | 800 | 72 | MBh | 28.2
86 | 62 | 800 | 72 | S/T | 0.663
86 | 62 | 800 | 72 | ∆T | 21.6
86 | 62 | 800 | 72 | LDB | 64.4
86 | 62 | 800 | 72 | LWB | 62
86 | 62 | 800 | 72 | kW | 1.41
90 | 62 | 800 | 75 | MBh | 30
90 | 62 | 800 | 75 | S/T | 0.617
90 | 62 | 800 | 75 | ∆T | 21.4
90 | 62 | 800 | 75 | LDB | 68.6
90 | 62 | 800 | 75 | LWB | 65.1
90 | 62 | 800 | 75 | kW | 1.49
68 | 66 | 800 | 57 | MBh | 15.6
68 | 66 | 800 | 57 | S/T | 0.878
68 | 66 | 800 | 57 | ∆T | 15.9
68 | 66 | 800 | 57 | LDB | 52.1
68 | 66 | 800 | 57 | LWB | 49.6
68 | 66 | 800 | 57 | kW | 0.73
72 | 66 | 800 | 61 | MBh | 18.9
72 | 66 | 800 | 61 | S/T | 0.815
72 | 66 | 800 | 61 | ∆T | 17.8
72 | 66 | 800 | 61 | LDB | 54.2
72 | 66 | 800 | 61 | LWB | 52.7
72 | 66 | 800 | 61 | kW | 0.91
77 | 66 | 800 | 64 | MBh | 21.5
77 | 66 | 800 | 64 | S/T | 0.758
77 | 66 | 800 | 64 | ∆T | 18.9
77 | 66 | 800 | 64 | LDB | 58.1
77 | 66 | 800 | 64 | LWB | 55
77 | 66 | 800 | 64 | kW | 1.05
80 | 66 | 800 | 67 | MBh | 24
80 | 66 | 800 | 67 | S/T | 0.704
80 | 66 | 800 | 67 | ∆T | 19.6
80 | 66 | 800 | 67 | LDB | 60.4
80 | 66 | 800 | 67 | LWB | 57.6
80 | 66 | 800 | 67 | kW | 1.19
84 | 66 | 800 | 70 | MBh | 26.5
84 | 66 | 800 | 70 | S/T | 0.672
84 | 66 | 800 | 70 | ∆T | 20.6
84 | 66 | 800 | 70 | LDB | 63.4
84 | 66 | 800 | 70 | LWB | 60.2
84 | 66 | 800 | 70 | kW | 1.34
86 | 66 | 800 | 72 | MBh | 28.2
86 | 66 | 800 | 72 | S/T | 0.663
86 | 66 | 800 | 72 | ∆T | 21.6
86 | 66 | 800 | 72 | LDB | 64.4
86 | 66 | 800 | 72 | LWB | 62
86 | 66 | 800 | 72 | kW | 1.44
90 | 66 | 800 | 75 | MBh | 29.6
90 | 66 | 800 | 75 | S/T | 0.618
90 | 66 | 800 | 75 | ∆T | 21.2
90 | 66 | 800 | 75 | LDB | 68.8
90 | 66 | 800 | 75 | LWB | 65.2
90 | 66 | 800 | 75 | kW | 1.48
68 | 70 | 800 | 57 | MBh | 15.6
68 | 70 | 800 | 57 | S/T | 0.878
68 | 70 | 800 | 57 | ∆T | 15.9
68 | 70 | 800 | 57 | LDB | 52.1
68 | 70 | 800 | 57 | LWB | 49.6
68 | 70 | 800 | 57 | kW | 0.75
72 | 70 | 800 | 61 | MBh | 18.9
72 | 70 | 800 | 61 | S/T | 0.815
72 | 70 | 800 | 61 | ∆T | 17.8
72 | 70 | 800 | 61 | LDB | 54.2
72 | 70 | 800 | 61 | LWB | 52.7
72 | 70 | 800 | 61 | kW | 0.93
77 | 70 | 800 | 64 | MBh | 21.5
77 | 70 | 800 | 64 | S/T | 0.758
77 | 70 | 800 | 64 | ∆T | 18.9
77 | 70 | 800 | 64 | LDB | 58.1
77 | 70 | 800 | 64 | LWB | 55
77 | 70 | 800 | 64 | kW | 1.07
80 | 70 | 800 | 67 | MBh | 24
80 | 70 | 800 | 67 | S/T | 0.704
80 | 70 | 800 | 67 | ∆T | 19.6
80 | 70 | 800 | 67 | LDB | 60.4
80 | 70 | 800 | 67 | LWB | 57.6
80 | 70 | 800 | 67 | kW | 1.22
84 | 70 | 800 | 70 | MBh | 26.5
84 | 70 | 800 | 70 | S/T | 0.672
84 | 70 | 800 | 70 | ∆T | 20.6
84 | 70 | 800 | 70 | LDB | 63.4
84 | 70 | 800 | 70 | LWB | 60.2
84 | 70 | 800 | 70 | kW | 1.37
86 | 70 | 800 | 72 | MBh | 28.2
86 | 70 | 800 | 72 | S/T | 0.663
86 | 70 | 800 | 72 | ∆T | 21.6
86 | 70 | 800 | 72 | LDB | 64.4
86 | 70 | 800 | 72 | LWB | 62
86 | 70 | 800 | 72 | kW | 1.47
90 | 70 | 800 | 75 | MBh | 29.1
90 | 70 | 800 | 75 | S/T | 0.619
90 | 70 | 800 | 75 | ∆T | 20.8
90 | 70 | 800 | 75 | LDB | 69.2
90 | 70 | 800 | 75 | LWB | 65.4
90 | 70 | 800 | 75 | kW | 1.47
68 | 72 | 800 | 57 | MBh | 15.6
68 | 72 | 800 | 57 | S/T | 0.878
68 | 72 | 800 | 57 | ∆T | 15.9
68 | 72 | 800 | 57 | LDB | 52.1
68 | 72 | 800 | 57 | LWB | 49.6
68 | 72 | 800 | 57 | kW | 0.76
72 | 72 | 800 | 61 | MBh | 18.9
72 | 72 | 800 | 61 | S/T | 0.815
72 | 72 | 800 | 61 | ∆T | 17.8
72 | 72 | 800 | 61 | LDB | 54.2
72 | 72 | 800 | 61 | LWB | 52.7
72 | 72 | 800 | 61 | kW | 0.94
77 | 72 | 800 | 64 | MBh | 21.5
77 | 72 | 800 | 64 | S/T | 0.758
77 | 72 | 800 | 64 | ∆T | 18.9
77 | 72 | 800 | 64 | LDB | 58.1
77 | 72 | 800 | 64 | LWB | 55
77 | 72 | 800 | 64 | kW | 1.09
80 | 72 | 800 | 67 | MBh | 24
80 | 72 | 800 | 67 | S/T | 0.704
80 | 72 | 800 | 67 | ∆T | 19.6
80 | 72 | 800 | 67 | LDB | 60.4
80 | 72 | 800 | 67 | LWB | 57.6
80 | 72 | 800 | 67 | kW | 1.24
84 | 72 | 800 | 70 | MBh | 26.5
84 | 72 | 800 | 70 | S/T | 0.672
84 | 72 | 800 | 70 | ∆T | 20.6
84 | 72 | 800 | 70 | LDB | 63.4
84 | 72 | 800 | 70 | LWB | 60.2
84 | 72 | 800 | 70 | kW | 1.39
86 | 72 | 800 | 72 | MBh | 28.2
86 | 72 | 800 | 72 | S/T | 0.663
86 | 72 | 800 | 72 | ∆T | 21.6
86 | 72 | 800 | 72 | LDB | 64.4
86 | 72 | 800 | 72 | LWB | 62
86 | 72 | 800 | 72 | kW | 1.49
90 | 72 | 800 | 75 | MBh | 28.9
90 | 72 | 800 | 75 | S/T | 0.616
90 | 72 | 800 | 75 | ∆T | 20.6
90 | 72 | 800 | 75 | LDB | 69.4
90 | 72 | 800 | 75 | LWB | 65.5
90 | 72 | 800 | 75 | kW | 1.46
68 | 75 | 800 | 57 | MBh | 15.6
68 | 75 | 800 | 57 | S/T | 0.878
68 | 75 | 800 | 57 | ∆T | 15.9
68 | 75 | 800 | 57 | LDB | 52.1
68 | 75 | 800 | 57 | LWB | 49.6
68 | 75 | 800 | 57 | kW | 0.77
72 | 75 | 800 | 61 | MBh | 18.9
72 | 75 | 800 | 61 | S/T | 0.815
72 | 75 | 800 | 61 | ∆T | 17.8
72 | 75 | 800 | 61 | LDB | 54.2
72 | 75 | 800 | 61 | LWB | 52.7
72 | 75 | 800 | 61 | kW | 0.96
77 | 75 | 800 | 64 | MBh | 21.5
77 | 75 | 800 | 64 | S/T | 0.758
77 | 75 | 800 | 64 | ∆T | 18.9
77 | 75 | 800 | 64 | LDB | 58.1
77 | 75 | 800 | 64 | LWB | 55
77 | 75 | 800 | 64 | kW | 1.11
80 | 75 | 800 | 67 | MBh | 24
80 | 75 | 800 | 67 | S/T | 0.704
80 | 75 | 800 | 67 | ∆T | 19.6
80 | 75 | 800 | 67 | LDB | 60.4
80 | 75 | 800 | 67 | LWB | 57.6
80 | 75 | 800 | 67 | kW | 1.26
84 | 75 | 800 | 70 | MBh | 26.5
84 | 75 | 800 | 70 | S/T | 0.672
84 | 75 | 800 | 70 | ∆T | 20.6
84 | 75 | 800 | 70 | LDB | 63.4
84 | 75 | 800 | 70 | LWB | 60.2
84 | 75 | 800 | 70 | kW | 1.41
86 | 75 | 800 | 72 | MBh | 28
86 | 75 | 800 | 72 | S/T | 0.661
86 | 75 | 800 | 72 | ∆T | 21.4
86 | 75 | 800 | 72 | LDB | 64.6
86 | 75 | 800 | 72 | LWB | 62.1
86 | 75 | 800 | 72 | kW | 1.5
90 | 75 | 800 | 75 | MBh | 28.5
90 | 75 | 800 | 75 | S/T | 0.618
90 | 75 | 800 | 75 | ∆T | 20.4
90 | 75 | 800 | 75 | LDB | 69.6
90 | 75 | 800 | 75 | LWB | 65.6
90 | 75 | 800 | 75 | kW | 1.46
68 | 79 | 800 | 57 | MBh | 15.6
68 | 79 | 800 | 57 | S/T | 0.878
68 | 79 | 800 | 57 | ∆T | 15.9
68 | 79 | 800 | 57 | LDB | 52.1
68 | 79 | 800 | 57 | LWB | 49.6
68 | 79 | 800 | 57 | kW | 0.79
72 | 79 | 800 | 61 | MBh | 18.9
72 | 79 | 800 | 61 | S/T | 0.815
72 | 79 | 800 | 61 | ∆T | 17.8
72 | 79 | 800 | 61 | LDB | 54.2
72 | 79 | 800 | 61 | LWB | 52.7
72 | 79 | 800 | 61 | kW | 0.98
77 | 79 | 800 | 64 | MBh | 21.5
77 | 79 | 800 | 64 | S/T | 0.758
77 | 79 | 800 | 64 | ∆T | 18.9
77 | 79 | 800 | 64 | LDB | 58.1
77 | 79 | 800 | 64 | LWB | 55
77 | 79 | 800 | 64 | kW | 1.13
80 | 79 | 800 | 67 | MBh | 24
80 | 79 | 800 | 67 | S/T | 0.704
80 | 79 | 800 | 67 | ∆T | 19.6
80 | 79 | 800 | 67 | LDB | 60.4
80 | 79 | 800 | 67 | LWB | 57.6
80 | 79 | 800 | 67 | kW | 1.29
84 | 79 | 800 | 70 | MBh | 26.5
84 | 79 | 800 | 70 | S/T | 0.672
84 | 79 | 800 | 70 | ∆T | 20.6
84 | 79 | 800 | 70 | LDB | 63.4
84 | 79 | 800 | 70 | LWB | 60.2
84 | 79 | 800 | 70 | kW | 1.49
86 | 79 | 800 | 72 | MBh | 27.6
86 | 79 | 800 | 72 | S/T | 0.663
86 | 79 | 800 | 72 | ∆T | 21.2
86 | 79 | 800 | 72 | LDB | 64.8
86 | 79 | 800 | 72 | LWB | 62.2
86 | 79 | 800 | 72 | kW | 1.58
90 | 79 | 800 | 75 | MBh | 28.1
90 | 79 | 800 | 75 | S/T | 0.619
90 | 79 | 800 | 75 | ∆T | 20.1
90 | 79 | 800 | 75 | LDB | 69.9
90 | 79 | 800 | 75 | LWB | 65.8
90 | 79 | 800 | 75 | kW | 1.59
68 | 83 | 800 | 57 | MBh | 15.6
68 | 83 | 800 | 57 | S/T | 0.878
68 | 83 | 800 | 57 | ∆T | 15.9
68 | 83 | 800 | 57 | LDB | 52.1
68 | 83 | 800 | 57 | LWB | 49.6
68 | 83 | 800 | 57 | kW | 0.8
72 | 83 | 800 | 61 | MBh | 18.9
72 | 83 | 800 | 61 | S/T | 0.815
72 | 83 | 800 | 61 | ∆T | 17.8
72 | 83 | 800 | 61 | LDB | 54.2
72 | 83 | 800 | 61 | LWB | 52.7
72 | 83 | 800 | 61 | kW | 1.04
77 | 83 | 800 | 64 | MBh | 21.5
77 | 83 | 800 | 64 | S/T | 0.758
77 | 83 | 800 | 64 | ∆T | 18.9
77 | 83 | 800 | 64 | LDB | 58.1
77 | 83 | 800 | 64 | LWB | 55
77 | 83 | 800 | 64 | kW | 1.24
80 | 83 | 800 | 67 | MBh | 24
80 | 83 | 800 | 67 | S/T | 0.704
80 | 83 | 800 | 67 | ∆T | 19.6
80 | 83 | 800 | 67 | LDB | 60.4
80 | 83 | 800 | 67 | LWB | 57.6
80 | 83 | 800 | 67 | kW | 1.46
84 | 83 | 800 | 70 | MBh | 26.5
84 | 83 | 800 | 70 | S/T | 0.672
84 | 83 | 800 | 70 | ∆T | 20.6
84 | 83 | 800 | 70 | LDB | 63.4
84 | 83 | 800 | 70 | LWB | 60.2
84 | 83 | 800 | 70 | kW | 1.7
86 | 83 | 800 | 72 | MBh | 27.1
86 | 83 | 800 | 72 | S/T | 0.664
86 | 83 | 800 | 72 | ∆T | 20.8
86 | 83 | 800 | 72 | LDB | 65.2
86 | 83 | 800 | 72 | LWB | 62.4
86 | 83 | 800 | 72 | kW | 1.74
90 | 83 | 800 | 75 | MBh | 27.6
90 | 83 | 800 | 75 | S/T | 0.62
90 | 83 | 800 | 75 | ∆T | 19.8
90 | 83 | 800 | 75 | LDB | 70.2
90 | 83 | 800 | 75 | LWB | 66
90 | 83 | 800 | 75 | kW | 1.75
68 | 87 | 800 | 57 | MBh | 15.6
68 | 87 | 800 | 57 | S/T | 0.878
68 | 87 | 800 | 57 | ∆T | 15.9
68 | 87 | 800 | 57 | LDB | 52.1
68 | 87 | 800 | 57 | LWB | 49.6
68 | 87 | 800 | 57 | kW | 0.9
72 | 87 | 800 | 61 | MBh | 18.9
72 | 87 | 800 | 61 | S/T | 0.815
72 | 87 | 800 | 61 | ∆T | 17.8
72 | 87 | 800 | 61 | LDB | 54.2
72 | 87 | 800 | 61 | LWB | 52.7
72 | 87 | 800 | 61 | kW | 1.17
77 | 87 | 800 | 64 | MBh | 21.5
77 | 87 | 800 | 64 | S/T | 0.758
77 | 87 | 800 | 64 | ∆T | 18.9
77 | 87 | 800 | 64 | LDB | 58.1
77 | 87 | 800 | 64 | LWB | 55
77 | 87 | 800 | 64 | kW | 1.4
80 | 87 | 800 | 67 | MBh | 24
80 | 87 | 800 | 67 | S/T | 0.704
80 | 87 | 800 | 67 | ∆T | 19.6
80 | 87 | 800 | 67 | LDB | 60.4
80 | 87 | 800 | 67 | LWB | 57.6
80 | 87 | 800 | 67 | kW | 1.64
84 | 87 | 800 | 70 | MBh | 26.4
84 | 87 | 800 | 70 | S/T | 0.67
84 | 87 | 800 | 70 | ∆T | 20.5
84 | 87 | 800 | 70 | LDB | 63.5
84 | 87 | 800 | 70 | LWB | 60.2
84 | 87 | 800 | 70 | kW | 1.89
86 | 87 | 800 | 72 | MBh | 26.7
86 | 87 | 800 | 72 | S/T | 0.663
86 | 87 | 800 | 72 | ∆T | 20.5
86 | 87 | 800 | 72 | LDB | 65.5
86 | 87 | 800 | 72 | LWB | 62.6
86 | 87 | 800 | 72 | kW | 1.9
90 | 87 | 800 | 75 | MBh | 27.2
90 | 87 | 800 | 75 | S/T | 0.618
90 | 87 | 800 | 75 | ∆T | 19.4
90 | 87 | 800 | 75 | LDB | 70.6
90 | 87 | 800 | 75 | LWB | 66.1
90 | 87 | 800 | 75 | kW | 1.91
68 | 91 | 800 | 57 | MBh | 15.6
68 | 91 | 800 | 57 | S/T | 0.878
68 | 91 | 800 | 57 | ∆T | 15.9
68 | 91 | 800 | 57 | LDB | 52.1
68 | 91 | 800 | 57 | LWB | 49.6
68 | 91 | 800 | 57 | kW | 1
72 | 91 | 800 | 61 | MBh | 18.9
72 | 91 | 800 | 61 | S/T | 0.815
72 | 91 | 800 | 61 | ∆T | 17.8
72 | 91 | 800 | 61 | LDB | 54.2
72 | 91 | 800 | 61 | LWB | 52.7
72 | 91 | 800 | 61 | kW | 1.3
77 | 91 | 800 | 64 | MBh | 21.5
77 | 91 | 800 | 64 | S/T | 0.758
77 | 91 | 800 | 64 | ∆T | 18.9
77 | 91 | 800 | 64 | LDB | 58.1
77 | 91 | 800 | 64 | LWB | 55
77 | 91 | 800 | 64 | kW | 1.56
80 | 91 | 800 | 67 | MBh | 24
80 | 91 | 800 | 67 | S/T | 0.704
80 | 91 | 800 | 67 | ∆T | 19.6
80 | 91 | 800 | 67 | LDB | 60.4
80 | 91 | 800 | 67 | LWB | 57.6
80 | 91 | 800 | 67 | kW | 1.84
84 | 91 | 800 | 70 | MBh | 25.9
84 | 91 | 800 | 70 | S/T | 0.668
84 | 91 | 800 | 70 | ∆T | 20
84 | 91 | 800 | 70 | LDB | 64
84 | 91 | 800 | 70 | LWB | 60.5
84 | 91 | 800 | 70 | kW | 2.05
86 | 91 | 800 | 72 | MBh | 26.2
86 | 91 | 800 | 72 | S/T | 0.664
86 | 91 | 800 | 72 | ∆T | 20.1
86 | 91 | 800 | 72 | LDB | 65.9
86 | 91 | 800 | 72 | LWB | 62.8
86 | 91 | 800 | 72 | kW | 2.06
90 | 91 | 800 | 75 | MBh | 26.7
90 | 91 | 800 | 75 | S/T | 0.618
90 | 91 | 800 | 75 | ∆T | 19.1
90 | 91 | 800 | 75 | LDB | 70.9
90 | 91 | 800 | 75 | LWB | 66.3
90 | 91 | 800 | 75 | kW | 2.08
68 | 93 | 800 | 57 | MBh | 15.6
68 | 93 | 800 | 57 | S/T | 0.878
68 | 93 | 800 | 57 | ∆T | 15.9
68 | 93 | 800 | 57 | LDB | 52.1
68 | 93 | 800 | 57 | LWB | 49.6
68 | 93 | 800 | 57 | kW | 1.05
72 | 93 | 800 | 61 | MBh | 18.9
72 | 93 | 800 | 61 | S/T | 0.815
72 | 93 | 800 | 61 | ∆T | 17.8
72 | 93 | 800 | 61 | LDB | 54.2
72 | 93 | 800 | 61 | LWB | 52.7
72 | 93 | 800 | 61 | kW | 1.38
77 | 93 | 800 | 64 | MBh | 21.5
77 | 93 | 800 | 64 | S/T | 0.758
77 | 93 | 800 | 64 | ∆T | 18.9
77 | 93 | 800 | 64 | LDB | 58.1
77 | 93 | 800 | 64 | LWB | 55
77 | 93 | 800 | 64 | kW | 1.65
80 | 93 | 800 | 67 | MBh | 24
80 | 93 | 800 | 67 | S/T | 0.704
80 | 93 | 800 | 67 | ∆T | 19.6
80 | 93 | 800 | 67 | LDB | 60.4
80 | 93 | 800 | 67 | LWB | 57.6
80 | 93 | 800 | 67 | kW | 1.94
84 | 93 | 800 | 70 | MBh | 25.7
84 | 93 | 800 | 70 | S/T | 0.669
84 | 93 | 800 | 70 | ∆T | 19.9
84 | 93 | 800 | 70 | LDB | 64.1
84 | 93 | 800 | 70 | LWB | 60.5
84 | 93 | 800 | 70 | kW | 2.14
86 | 93 | 800 | 72 | MBh | 26
86 | 93 | 800 | 72 | S/T | 0.662
86 | 93 | 800 | 72 | ∆T | 19.9
86 | 93 | 800 | 72 | LDB | 66.1
86 | 93 | 800 | 72 | LWB | 62.9
86 | 93 | 800 | 72 | kW | 2.15
90 | 93 | 800 | 75 | MBh | 26.5
90 | 93 | 800 | 75 | S/T | 0.619
90 | 93 | 800 | 75 | ∆T | 19
90 | 93 | 800 | 75 | LDB | 71
90 | 93 | 800 | 75 | LWB | 66.4
90 | 93 | 800 | 75 | kW | 2.16
68 | 95 | 800 | 57 | MBh | 15.6
68 | 95 | 800 | 57 | S/T | 0.878
68 | 95 | 800 | 57 | ∆T | 15.9
68 | 95 | 800 | 57 | LDB | 52.1
68 | 95 | 800 | 57 | LWB | 49.6
68 | 95 | 800 | 57 | kW | 1.11
72 | 95 | 800 | 61 | MBh | 18.9
72 | 95 | 800 | 61 | S/T | 0.815
72 | 95 | 800 | 61 | ∆T | 17.8
72 | 95 | 800 | 61 | LDB | 54.2
72 | 95 | 800 | 61 | LWB | 52.7
72 | 95 | 800 | 61 | kW | 1.45
77 | 95 | 800 | 64 | MBh | 21.5
77 | 95 | 800 | 64 | S/T | 0.758
77 | 95 | 800 | 64 | ∆T | 18.9
77 | 95 | 800 | 64 | LDB | 58.1
77 | 95 | 800 | 64 | LWB | 55
77 | 95 | 800 | 64 | kW | 1.74
80 | 95 | 800 | 67 | MBh | 24
80 | 95 | 800 | 67 | S/T | 0.704
80 | 95 | 800 | 67 | ∆T | 19.6
80 | 95 | 800 | 67 | LDB | 60.4
80 | 95 | 800 | 67 | LWB | 57.6
80 | 95 | 800 | 67 | kW | 2.05
84 | 95 | 800 | 70 | MBh | 25.5
84 | 95 | 800 | 70 | S/T | 0.667
84 | 95 | 800 | 70 | ∆T | 19.7
84 | 95 | 800 | 70 | LDB | 64.3
84 | 95 | 800 | 70 | LWB | 60.6
84 | 95 | 800 | 70 | kW | 2.22
86 | 95 | 800 | 72 | MBh | 25.8
86 | 95 | 800 | 72 | S/T | 0.663
86 | 95 | 800 | 72 | ∆T | 19.8
86 | 95 | 800 | 72 | LDB | 66.2
86 | 95 | 800 | 72 | LWB | 62.9
86 | 95 | 800 | 72 | kW | 2.23
90 | 95 | 800 | 75 | MBh | 26.3
90 | 95 | 800 | 75 | S/T | 0.616
90 | 95 | 800 | 75 | ∆T | 18.8
90 | 95 | 800 | 75 | LDB | 71.2
90 | 95 | 800 | 75 | LWB | 66.4
90 | 95 | 800 | 75 | kW | 2.24
68 | 99 | 800 | 57 | MBh | 15.6
68 | 99 | 800 | 57 | S/T | 0.878
68 | 99 | 800 | 57 | ∆T | 15.9
68 | 99 | 800 | 57 | LDB | 52.1
68 | 99 | 800 | 57 | LWB | 49.6
68 | 99 | 800 | 57 | kW | 1.22
72 | 99 | 800 | 61 | MBh | 18.9
72 | 99 | 800 | 61 | S/T | 0.815
72 | 99 | 800 | 61 | ∆T | 17.8
72 | 99 | 800 | 61 | LDB | 54.2
72 | 99 | 800 | 61 | LWB | 52.7
72 | 99 | 800 | 61 | kW | 1.6
77 | 99 | 800 | 64 | MBh | 21.5
77 | 99 | 800 | 64 | S/T | 0.758
77 | 99 | 800 | 64 | ∆T | 18.9
77 | 99 | 800 | 64 | LDB | 58.1
77 | 99 | 800 | 64 | LWB | 55
77 | 99 | 800 | 64 | kW | 1.93
80 | 99 | 800 | 67 | MBh | 24
80 | 99 | 800 | 67 | S/T | 0.704
80 | 99 | 800 | 67 | ∆T | 19.6
80 | 99 | 800 | 67 | LDB | 60.4
80 | 99 | 800 | 67 | LWB | 57.6
80 | 99 | 800 | 67 | kW | 2.28
84 | 99 | 800 | 70 | MBh | 25
84 | 99 | 800 | 70 | S/T | 0.672
84 | 99 | 800 | 70 | ∆T | 19.4
84 | 99 | 800 | 70 | LDB | 64.6
84 | 99 | 800 | 70 | LWB | 60.8
84 | 99 | 800 | 70 | kW | 2.38
86 | 99 | 800 | 72 | MBh | 25.3
86 | 99 | 800 | 72 | S/T | 0.664
86 | 99 | 800 | 72 | ∆T | 19.4
86 | 99 | 800 | 72 | LDB | 66.6
86 | 99 | 800 | 72 | LWB | 63.1
86 | 99 | 800 | 72 | kW | 2.39
90 | 99 | 800 | 75 | MBh | 25.8
90 | 99 | 800 | 75 | S/T | 0.62
90 | 99 | 800 | 75 | ∆T | 18.5
90 | 99 | 800 | 75 | LDB | 71.5
90 | 99 | 800 | 75 | LWB | 66.6
90 | 99 | 800 | 75 | kW | 2.41
68 | 103 | 800 | 57 | MBh | 15.6
68 | 103 | 800 | 57 | S/T | 0.878
68 | 103 | 800 | 57 | ∆T | 15.9
68 | 103 | 800 | 57 | LDB | 52.1
68 | 103 | 800 | 57 | LWB | 49.6
68 | 103 | 800 | 57 | kW | 1.35
72 | 103 | 800 | 61 | MBh | 18.9
72 | 103 | 800 | 61 | S/T | 0.815
72 | 103 | 800 | 61 | ∆T | 17.8
72 | 103 | 800 | 61 | LDB | 54.2
72 | 103 | 800 | 61 | LWB | 52.7
72 | 103 | 800 | 61 | kW | 1.77
77 | 103 | 800 | 64 | MBh | 21.5
77 | 103 | 800 | 64 | S/T | 0.758
77 | 103 | 800 | 64 | ∆T | 18.9
77 | 103 | 800 | 64 | LDB | 58.1
77 | 103 | 800 | 64 | LWB | 55
77 | 103 | 800 | 64 | kW | 2.13
80 | 103 | 800 | 67 | MBh | 24
80 | 103 | 800 | 67 | S/T | 0.704
80 | 103 | 800 | 67 | ∆T | 19.6
80 | 103 | 800 | 67 | LDB | 60.4
80 | 103 | 800 | 67 | LWB | 57.6
80 | 103 | 800 | 67 | kW | 2.51
84 | 103 | 800 | 70 | MBh | 24.6
84 | 103 | 800 | 70 | S/T | 0.671
84 | 103 | 800 | 70 | ∆T | 19.1
84 | 103 | 800 | 70 | LDB | 64.9
84 | 103 | 800 | 70 | LWB | 61
84 | 103 | 800 | 70 | kW | 2.55
86 | 103 | 800 | 72 | MBh | 24.9
86 | 103 | 800 | 72 | S/T | 0.663
86 | 103 | 800 | 72 | ∆T | 19.1
86 | 103 | 800 | 72 | LDB | 66.9
86 | 103 | 800 | 72 | LWB | 63.3
86 | 103 | 800 | 72 | kW | 2.56
90 | 103 | 800 | 75 | MBh | 25.4
90 | 103 | 800 | 75 | S/T | 0.622
90 | 103 | 800 | 75 | ∆T | 18.3
90 | 103 | 800 | 75 | LDB | 71.7
90 | 103 | 800 | 75 | LWB | 66.7
90 | 103 | 800 | 75 | kW | 2.58
68 | 106 | 800 | 57 | MBh | 15.6
68 | 106 | 800 | 57 | S/T | 0.878
68 | 106 | 800 | 57 | ∆T | 15.9
68 | 106 | 800 | 57 | LDB | 52.1
68 | 106 | 800 | 57 | LWB | 49.6
68 | 106 | 800 | 57 | kW | 1.44
72 | 106 | 800 | 61 | MBh | 18.9
72 | 106 | 800 | 61 | S/T | 0.815
72 | 106 | 800 | 61 | ∆T | 17.8
72 | 106 | 800 | 61 | LDB | 54.2
72 | 106 | 800 | 61 | LWB | 52.7
72 | 106 | 800 | 61 | kW | 1.9
77 | 106 | 800 | 64 | MBh | 21.5
77 | 106 | 800 | 64 | S/T | 0.758
77 | 106 | 800 | 64 | ∆T | 18.9
77 | 106 | 800 | 64 | LDB | 58.1
77 | 106 | 800 | 64 | LWB | 55
77 | 106 | 800 | 64 | kW | 2.29
80 | 106 | 800 | 67 | MBh | 23.7
80 | 106 | 800 | 67 | S/T | 0.709
80 | 106 | 800 | 67 | ∆T | 19.4
80 | 106 | 800 | 67 | LDB | 60.6
80 | 106 | 800 | 67 | LWB | 57.7
80 | 106 | 800 | 67 | kW | 2.65
84 | 106 | 800 | 70 | MBh | 24.2
84 | 106 | 800 | 70 | S/T | 0.674
84 | 106 | 800 | 70 | ∆T | 18.9
84 | 106 | 800 | 70 | LDB | 65.1
84 | 106 | 800 | 70 | LWB | 61.1
84 | 106 | 800 | 70 | kW | 2.67
86 | 106 | 800 | 72 | MBh | 24.6
86 | 106 | 800 | 72 | S/T | 0.663
86 | 106 | 800 | 72 | ∆T | 18.9
86 | 106 | 800 | 72 | LDB | 67.1
86 | 106 | 800 | 72 | LWB | 63.4
86 | 106 | 800 | 72 | kW | 2.68
90 | 106 | 800 | 75 | MBh | 25.1
90 | 106 | 800 | 75 | S/T | 0.622
90 | 106 | 800 | 75 | ∆T | 18.1
90 | 106 | 800 | 75 | LDB | 71.9
90 | 106 | 800 | 75 | LWB | 66.9
90 | 106 | 800 | 75 | kW | 2.7
68 | 110 | 800 | 57 | MBh | 15.6
68 | 110 | 800 | 57 | S/T | 0.878
68 | 110 | 800 | 57 | ∆T | 15.9
68 | 110 | 800 | 57 | LDB | 52.1
68 | 110 | 800 | 57 | LWB | 49.6
68 | 110 | 800 | 57 | kW | 1.58
72 | 110 | 800 | 61 | MBh | 18.9
72 | 110 | 800 | 61 | S/T | 0.815
72 | 110 | 800 | 61 | ∆T | 17.8
72 | 110 | 800 | 61 | LDB | 54.2
72 | 110 | 800 | 61 | LWB | 52.7
72 | 110 | 800 | 61 | kW | 2.09
77 | 110 | 800 | 64 | MBh | 21.5
77 | 110 | 800 | 64 | S/T | 0.758
77 | 110 | 800 | 64 | ∆T | 18.9
77 | 110 | 800 | 64 | LDB | 58.1
77 | 110 | 800 | 64 | LWB | 55
77 | 110 | 800 | 64 | kW | 2.51
80 | 110 | 800 | 67 | MBh | 23.3
80 | 110 | 800 | 67 | S/T | 0.708
80 | 110 | 800 | 67 | ∆T | 19.1
80 | 110 | 800 | 67 | LDB | 60.9
80 | 110 | 800 | 67 | LWB | 57.9
80 | 110 | 800 | 67 | kW | 2.81
84 | 110 | 800 | 70 | MBh | 23.8
84 | 110 | 800 | 70 | S/T | 0.672
84 | 110 | 800 | 70 | ∆T | 18.5
84 | 110 | 800 | 70 | LDB | 65.5
84 | 110 | 800 | 70 | LWB | 61.3
84 | 110 | 800 | 70 | kW | 2.84
86 | 110 | 800 | 72 | MBh | 24.1
86 | 110 | 800 | 72 | S/T | 0.664
86 | 110 | 800 | 72 | ∆T | 18.5
86 | 110 | 800 | 72 | LDB | 67.5
86 | 110 | 800 | 72 | LWB | 63.6
86 | 110 | 800 | 72 | kW | 2.85
90 | 110 | 800 | 75 | MBh | 24.1
90 | 110 | 800 | 75 | S/T | 0.622
90 | 110 | 800 | 75 | ∆T | 17.4
90 | 110 | 800 | 75 | LDB | 72.6
90 | 110 | 800 | 75 | LWB | 67.2
90 | 110 | 800 | 75 | kW | 2.85
68 | 115 | 800 | 57 | MBh | 15.6
68 | 115 | 800 | 57 | S/T | 0.878
68 | 115 | 800 | 57 | ∆T | 15.9
68 | 115 | 800 | 57 | LDB | 52.1
68 | 115 | 800 | 57 | LWB | 49.6
68 | 115 | 800 | 57 | kW | 1.77
72 | 115 | 800 | 61 | MBh | 18.9
72 | 115 | 800 | 61 | S/T | 0.815
72 | 115 | 800 | 61 | ∆T | 17.8
72 | 115 | 800 | 61 | LDB | 54.2
72 | 115 | 800 | 61 | LWB | 52.7
72 | 115 | 800 | 61 | kW | 2.34
77 | 115 | 800 | 64 | MBh | 21.5
77 | 115 | 800 | 64 | S/T | 0.758
77 | 115 | 800 | 64 | ∆T | 18.9
77 | 115 | 800 | 64 | LDB | 58.1
77 | 115 | 800 | 64 | LWB | 55
77 | 115 | 800 | 64 | kW | 2.82
80 | 115 | 800 | 67 | MBh | 22.5
80 | 115 | 800 | 67 | S/T | 0.707
80 | 115 | 800 | 67 | ∆T | 18.4
80 | 115 | 800 | 67 | LDB | 61.6
80 | 115 | 800 | 67 | LWB | 58.2
80 | 115 | 800 | 67 | kW | 3.01
84 | 115 | 800 | 70 | MBh | 22.5
84 | 115 | 800 | 70 | S/T | 0.671
84 | 115 | 800 | 70 | ∆T | 17.5
84 | 115 | 800 | 70 | LDB | 66.5
84 | 115 | 800 | 70 | LWB | 61.8
84 | 115 | 800 | 70 | kW | 3.01
86 | 115 | 800 | 72 | MBh | 22.5
86 | 115 | 800 | 72 | S/T | 0.662
86 | 115 | 800 | 72 | ∆T | 17.2
86 | 115 | 800 | 72 | LDB | 68.8
86 | 115 | 800 | 72 | LWB | 64.2
86 | 115 | 800 | 72 | kW | 3.01
90 | 115 | 800 | 75 | MBh | 22.5
90 | 115 | 800 | 75 | S/T | 0.622
90 | 115 | 800 | 75 | ∆T | 16.2
90 | 115 | 800 | 75 | LDB | 73.8
90 | 115 | 800 | 75 | LWB | 67.8
90 | 115 | 800 | 75 | kW | 3.01
68 | 118 | 800 | 57 | MBh | 15.6
68 | 118 | 800 | 57 | S/T | 0.878
68 | 118 | 800 | 57 | ∆T | 15.9
68 | 118 | 800 | 57 | LDB | 52.1
68 | 118 | 800 | 57 | LWB | 49.6
68 | 118 | 800 | 57 | kW | 1.89
72 | 118 | 800 | 61 | MBh | 18.9
72 | 118 | 800 | 61 | S/T | 0.815
72 | 118 | 800 | 61 | ∆T | 17.8
72 | 118 | 800 | 61 | LDB | 54.2
72 | 118 | 800 | 61 | LWB | 52.7
72 | 118 | 800 | 61 | kW | 2.5
77 | 118 | 800 | 64 | MBh | 19.3
77 | 118 | 800 | 64 | S/T | 0.762
77 | 118 | 800 | 64 | ∆T | 17
77 | 118 | 800 | 64 | LDB | 60
77 | 118 | 800 | 64 | LWB | 56
77 | 118 | 800 | 64 | kW | 2.56
80 | 118 | 800 | 67 | MBh | 19.3
80 | 118 | 800 | 67 | S/T | 0.71
80 | 118 | 800 | 67 | ∆T | 15.9
80 | 118 | 800 | 67 | LDB | 64.1
80 | 118 | 800 | 67 | LWB | 59.6
80 | 118 | 800 | 67 | kW | 2.56
84 | 118 | 800 | 70 | MBh | 19.3
84 | 118 | 800 | 70 | S/T | 0.674
84 | 118 | 800 | 70 | ∆T | 15
84 | 118 | 800 | 70 | LDB | 69
84 | 118 | 800 | 70 | LWB | 63.1
84 | 118 | 800 | 70 | kW | 2.56
86 | 118 | 800 | 72 | MBh | 19.3
86 | 118 | 800 | 72 | S/T | 0.663
86 | 118 | 800 | 72 | ∆T | 14.8
86 | 118 | 800 | 72 | LDB | 71.2
86 | 118 | 800 | 72 | LWB | 65.4
86 | 118 | 800 | 72 | kW | 2.56
90 | 118 | 800 | 75 | MBh | 19.3
90 | 118 | 800 | 75 | S/T | 0.622
90 | 118 | 800 | 75 | ∆T | 13.9
90 | 118 | 800 | 75 | LDB | 76.1
90 | 118 | 800 | 75 | LWB | 68.9
90 | 118 | 800 | 75 | kW | 2.56
68 | 122 | 800 | 57 | MBh | 14.7
68 | 122 | 800 | 57 | S/T | 0.878
68 | 122 | 800 | 57 | ∆T | 14.9
68 | 122 | 800 | 57 | LDB | 53.1
68 | 122 | 800 | 57 | LWB | 50.1
68 | 122 | 800 | 57 | kW | 1.89
72 | 122 | 800 | 61 | MBh | 14.7
72 | 122 | 800 | 61 | S/T | 0.816
72 | 122 | 800 | 61 | ∆T | 13.9
72 | 122 | 800 | 61 | LDB | 58.1
72 | 122 | 800 | 61 | LWB | 54.6
72 | 122 | 800 | 61 | kW | 1.89
77 | 122 | 800 | 64 | MBh | 14.7
77 | 122 | 800 | 64 | S/T | 0.762
77 | 122 | 800 | 64 | ∆T | 13
77 | 122 | 800 | 64 | LDB | 64
77 | 122 | 800 | 64 | LWB | 58
77 | 122 | 800 | 64 | kW | 1.89
80 | 122 | 800 | 67 | MBh | 14.7
80 | 122 | 800 | 67 | S/T | 0.707
80 | 122 | 800 | 67 | ∆T | 12
80 | 122 | 800 | 67 | LDB | 68
80 | 122 | 800 | 67 | LWB | 61.4
80 | 122 | 800 | 67 | kW | 1.89
84 | 122 | 800 | 70 | MBh | 14.7
84 | 122 | 800 | 70 | S/T | 0.673
84 | 122 | 800 | 70 | ∆T | 11.5
84 | 122 | 800 | 70 | LDB | 72.5
84 | 122 | 800 | 70 | LWB | 64.8
84 | 122 | 800 | 70 | kW | 1.89
86 | 122 | 800 | 72 | MBh | 14.7
86 | 122 | 800 | 72 | S/T | 0.665
86 | 122 | 800 | 72 | ∆T | 11.3
86 | 122 | 800 | 72 | LDB | 74.7
86 | 122 | 800 | 72 | LWB | 67.1
86 | 122 | 800 | 72 | kW | 1.89
90 | 122 | 800 | 75 | MBh | 14.7
90 | 122 | 800 | 75 | S/T | 0.622
90 | 122 | 800 | 75 | ∆T | 10.6
90 | 122 | 800 | 75 | LDB | 79.4
90 | 122 | 800 | 75 | LWB | 70.4
90 | 122 | 800 | 75 | kW | 1.89

## RZA24AAVJU - FTA24AAVJUA
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 800 | 57 | MBh | 15.6 | 64 | 60 | 61 | 32.4 | 3.14
68 | 23 | 800 | 57 | S/T | 0.878 | 64 | 60 | 65 | 30 | 2.85
68 | 23 | 800 | 57 | ∆T | 15.9 | 64 | 60 | 68 | 28.2 | 2.66
68 | 23 | 800 | 57 | LDB | 52.1 | 64 | 60 | 70 | 27 | 2.54
68 | 23 | 800 | 57 | LWB | 49.6 | 64 | 60 | 72 | 25.8 | 2.43
68 | 23 | 800 | 57 | kW | 0.6 | 64 | 60 | 75 | 24 | 2.28
72 | 23 | 800 | 61 | MBh | 18.9 | 60 | 56 | 61 | 32.4 | 3.29
72 | 23 | 800 | 61 | S/T | 0.815 | 60 | 56 | 65 | 30 | 2.97
72 | 23 | 800 | 61 | ∆T | 17.8 | 60 | 56 | 68 | 28.2 | 2.76
72 | 23 | 800 | 61 | LDB | 54.2 | 60 | 56 | 70 | 27 | 2.63
72 | 23 | 800 | 61 | LWB | 52.7 | 60 | 56 | 72 | 25.8 | 2.51
72 | 23 | 800 | 61 | kW | 0.74 | 60 | 56 | 75 | 24 | 2.34
77 | 23 | 800 | 64 | MBh | 21.5 | 57 | 53 | 61 | 32.4 | 3.4
77 | 23 | 800 | 64 | S/T | 0.758 | 57 | 53 | 65 | 30 | 3.07
77 | 23 | 800 | 64 | ∆T | 18.9 | 57 | 53 | 68 | 28.2 | 2.84
77 | 23 | 800 | 64 | LDB | 58.1 | 57 | 53 | 70 | 27 | 2.7
77 | 23 | 800 | 64 | LWB | 55 | 57 | 53 | 72 | 25.8 | 2.57
77 | 23 | 800 | 64 | kW | 0.85 | 57 | 53 | 75 | 24 | 2.4
80 | 23 | 800 | 67 | MBh | 24 | 54 | 50 | 61 | 32.4 | 3.53
80 | 23 | 800 | 67 | S/T | 0.704 | 54 | 50 | 65 | 30 | 3.18
80 | 23 | 800 | 67 | ∆T | 19.6 | 54 | 50 | 68 | 28.2 | 2.93
80 | 23 | 800 | 67 | LDB | 60.4 | 54 | 50 | 70 | 27 | 2.78
80 | 23 | 800 | 67 | LWB | 57.6 | 54 | 50 | 72 | 25.8 | 2.64
80 | 23 | 800 | 67 | kW | 0.96 | 54 | 50 | 75 | 24 | 2.45
84 | 23 | 800 | 70 | MBh | 26.5 | 51 | 47 | 61 | 32.4 | 3.67
84 | 23 | 800 | 70 | S/T | 0.672 | 51 | 47 | 65 | 30 | 3.29
84 | 23 | 800 | 70 | ∆T | 20.6 | 51 | 47 | 68 | 28.2 | 3.03
84 | 23 | 800 | 70 | LDB | 63.4 | 51 | 47 | 70 | 27 | 2.87
84 | 23 | 800 | 70 | LWB | 60.2 | 51 | 47 | 72 | 25.8 | 2.72
84 | 23 | 800 | 70 | kW | 1.08 | 51 | 47 | 75 | 24 | 2.52
86 | 23 | 800 | 72 | MBh | 28.2 | 47 | 43 | 61 | 32.4 | 3.89
86 | 23 | 800 | 72 | S/T | 0.663 | 47 | 43 | 65 | 30 | 3.47
86 | 23 | 800 | 72 | ∆T | 21.6 | 47 | 43 | 68 | 28.2 | 3.18
86 | 23 | 800 | 72 | LDB | 64.4 | 47 | 43 | 70 | 27 | 3.01
86 | 23 | 800 | 72 | LWB | 62 | 47 | 43 | 72 | 25.8 | 2.84
86 | 23 | 800 | 72 | kW | 1.16 | 47 | 43 | 75 | 24 | 2.62
90 | 23 | 800 | 75 | MBh | 30.7 | 44 | 40 | 61 | 32.4 | 4.06
90 | 23 | 800 | 75 | S/T | 0.619 | 44 | 40 | 65 | 30 | 3.61
90 | 23 | 800 | 75 | ∆T | 22 | 44 | 40 | 68 | 28.2 | 3.31
90 | 23 | 800 | 75 | LDB | 68 | 44 | 40 | 70 | 27 | 3.12
90 | 23 | 800 | 75 | LWB | 64.8 | 44 | 40 | 72 | 25.8 | 2.95
90 | 23 | 800 | 75 | kW | 1.28 | 44 | 40 | 75 | 24 | 2.7
68 | 30 | 800 | 57 | MBh | 15.6 | 39 | 36 | 61 | 32.4 | 4.33
68 | 30 | 800 | 57 | S/T | 0.878 | 39 | 36 | 65 | 30 | 3.84
68 | 30 | 800 | 57 | ∆T | 15.9 | 39 | 36 | 68 | 28.2 | 3.5
68 | 30 | 800 | 57 | LDB | 52.1 | 39 | 36 | 70 | 27 | 3.29
68 | 30 | 800 | 57 | LWB | 49.6 | 39 | 36 | 72 | 25.8 | 3.1
68 | 30 | 800 | 57 | kW | 0.62 | 39 | 36 | 75 | 24 | 2.83
72 | 30 | 800 | 61 | MBh | 18.9 | 35 | 32 | 61 | 31.7 | 4.3
72 | 30 | 800 | 61 | S/T | 0.815 | 35 | 32 | 65 | 30 | 4.09
72 | 30 | 800 | 61 | ∆T | 17.8 | 35 | 32 | 68 | 28.2 | 3.72
72 | 30 | 800 | 61 | LDB | 54.2 | 35 | 32 | 70 | 27 | 3.49
72 | 30 | 800 | 61 | LWB | 52.7 | 35 | 32 | 72 | 25.8 | 3.27
72 | 30 | 800 | 61 | kW | 0.76 | 35 | 32 | 75 | 24 | 2.98
77 | 30 | 800 | 64 | MBh | 21.5 | 30 | 28 | 61 | 30.1 | 3.92
77 | 30 | 800 | 64 | S/T | 0.758 | 30 | 28 | 65 | 30 | 4.38
77 | 30 | 800 | 64 | ∆T | 18.9 | 30 | 28 | 68 | 28.2 | 3.97
77 | 30 | 800 | 64 | LDB | 58.1 | 30 | 28 | 70 | 27 | 3.72
77 | 30 | 800 | 64 | LWB | 55 | 30 | 28 | 72 | 25.8 | 3.48
77 | 30 | 800 | 64 | kW | 0.88 | 30 | 28 | 75 | 24 | 3.15
80 | 30 | 800 | 67 | MBh | 24 | 26 | 24 | 61 | 28.6 | 3.56
80 | 30 | 800 | 67 | S/T | 0.704 | 26 | 24 | 65 | 28.6 | 4.18
80 | 30 | 800 | 67 | ∆T | 19.6 | 26 | 24 | 68 | 28.2 | 4.24
80 | 30 | 800 | 67 | LDB | 60.4 | 26 | 24 | 70 | 27 | 3.98
80 | 30 | 800 | 67 | LWB | 57.6 | 26 | 24 | 72 | 25.8 | 3.72
80 | 30 | 800 | 67 | kW | 0.99 | 26 | 24 | 75 | 24 | 3.35
84 | 30 | 800 | 70 | MBh | 26.5 | 22 | 20 | 61 | 27 | 3.24
84 | 30 | 800 | 70 | S/T | 0.672 | 22 | 20 | 65 | 27 | 3.77
84 | 30 | 800 | 70 | ∆T | 20.6 | 22 | 20 | 68 | 27 | 4.03
84 | 30 | 800 | 70 | LDB | 63.4 | 22 | 20 | 70 | 27 | 4.03
84 | 30 | 800 | 70 | LWB | 60.2 | 22 | 20 | 72 | 25.8 | 4
84 | 30 | 800 | 70 | kW | 1.12 | 22 | 20 | 75 | 24 | 3.58
86 | 30 | 800 | 72 | MBh | 28.2 | 19 | 18 | 61 | 26.3 | 3.1
86 | 30 | 800 | 72 | S/T | 0.663 | 19 | 18 | 65 | 26.3 | 3.58
86 | 30 | 800 | 72 | ∆T | 21.6 | 19 | 18 | 68 | 26.3 | 3.93
86 | 30 | 800 | 72 | LDB | 64.4 | 19 | 18 | 70 | 26.3 | 3.93
86 | 30 | 800 | 72 | LWB | 62 | 19 | 18 | 72 | 25.8 | 3.93
86 | 30 | 800 | 72 | kW | 1.2 | 19 | 18 | 75 | 24 | 3.72
90 | 30 | 800 | 75 | MBh | 30.7 | 17 | 16 | 61 | 25.3 | 2.95
90 | 30 | 800 | 75 | S/T | 0.619 | 17 | 16 | 65 | 25.3 | 3.36
90 | 30 | 800 | 75 | ∆T | 22 | 17 | 16 | 68 | 25.3 | 3.8
90 | 30 | 800 | 75 | LDB | 68 | 17 | 16 | 70 | 25.3 | 3.8
90 | 30 | 800 | 75 | LWB | 64.8 | 17 | 16 | 72 | 25.3 | 3.8
90 | 30 | 800 | 75 | kW | 1.32 | 17 | 16 | 75 | 24 | 3.8
68 | 40 | 800 | 57 | MBh | 15.6 | 15 | 14 | 61 | 24.7 | 2.88
68 | 40 | 800 | 57 | S/T | 0.878 | 15 | 14 | 65 | 24.7 | 3.24
68 | 40 | 800 | 57 | ∆T | 15.9 | 15 | 14 | 68 | 24.7 | 3.65
68 | 40 | 800 | 57 | LDB | 52.1 | 15 | 14 | 70 | 24.7 | 3.72
68 | 40 | 800 | 57 | LWB | 49.6 | 15 | 14 | 72 | 24.7 | 3.72
68 | 40 | 800 | 57 | kW | 0.65 | 15 | 14 | 75 | 24 | 3.72
72 | 40 | 800 | 61 | MBh | 18.9 | 13 | 12 | 61 | 23.9 | 2.81
72 | 40 | 800 | 61 | S/T | 0.815 | 13 | 12 | 65 | 23.9 | 3.09
72 | 40 | 800 | 61 | ∆T | 17.8 | 13 | 12 | 68 | 23.9 | 3.46
72 | 40 | 800 | 61 | LDB | 54.2 | 13 | 12 | 70 | 23.9 | 3.62
72 | 40 | 800 | 61 | LWB | 52.7 | 13 | 12 | 72 | 23.9 | 3.62
72 | 40 | 800 | 61 | kW | 0.8 | 13 | 12 | 75 | 23.9 | 3.62
77 | 40 | 800 | 64 | MBh | 21.5 | 10 | 9 | 61 | 22.6 | 2.75
77 | 40 | 800 | 64 | S/T | 0.758 | 10 | 9 | 65 | 22.6 | 2.88
77 | 40 | 800 | 64 | ∆T | 18.9 | 10 | 9 | 68 | 22.6 | 3.15
77 | 40 | 800 | 64 | LDB | 58.1 | 10 | 9 | 70 | 22.6 | 3.42
77 | 40 | 800 | 64 | LWB | 55 | 10 | 9 | 72 | 22.6 | 3.44
77 | 40 | 800 | 64 | kW | 0.92 | 10 | 9 | 75 | 22.6 | 3.44
80 | 40 | 800 | 67 | MBh | 24 | 6 | 5 | 61 | 21.2 | 2.82
80 | 40 | 800 | 67 | S/T | 0.704 | 6 | 5 | 65 | 21.2 | 2.76
80 | 40 | 800 | 67 | ∆T | 19.6 | 6 | 5 | 68 | 21.2 | 2.91
80 | 40 | 800 | 67 | LDB | 60.4 | 6 | 5 | 70 | 21.2 | 3.11
80 | 40 | 800 | 67 | LWB | 57.6 | 6 | 5 | 72 | 21.2 | 3.26
80 | 40 | 800 | 67 | kW | 1.04 | 6 | 5 | 75 | 21.2 | 3.26
84 | 40 | 800 | 70 | MBh | 26.5 | -2 | -2 | 61 | 18.4 | 2.89
84 | 40 | 800 | 70 | S/T | 0.672 | -2 | -2 | 65 | 18.4 | 2.89
84 | 40 | 800 | 70 | ∆T | 20.6 | -2 | -2 | 68 | 18.4 | 2.77
84 | 40 | 800 | 70 | LDB | 63.4 | -2 | -2 | 70 | 18.4 | 2.75
84 | 40 | 800 | 70 | LWB | 60.2 | -2 | -2 | 72 | 18.4 | 2.83
84 | 40 | 800 | 70 | kW | 1.17 | -2 | -2 | 75 | 18.4 | 2.89
86 | 40 | 800 | 72 | MBh | 28.2 | -4 | -4 | 61 | 17.7 | 2.79
86 | 40 | 800 | 72 | S/T | 0.663 | -4 | -4 | 65 | 17.7 | 2.79
86 | 40 | 800 | 72 | ∆T | 21.6 | -4 | -4 | 68 | 17.7 | 2.79
86 | 40 | 800 | 72 | LDB | 64.4 | -4 | -4 | 70 | 17.7 | 2.75
86 | 40 | 800 | 72 | LWB | 62 | -4 | -4 | 72 | 17.7 | 2.76
86 | 40 | 800 | 72 | kW | 1.26 | -4 | -4 | 75 | 17.7 | 2.79
90 | 40 | 800 | 75 | MBh | 30.7
90 | 40 | 800 | 75 | S/T | 0.619
90 | 40 | 800 | 75 | ∆T | 22
90 | 40 | 800 | 75 | LDB | 68
90 | 40 | 800 | 75 | LWB | 64.8
90 | 40 | 800 | 75 | kW | 1.39
68 | 50 | 800 | 57 | MBh | 15.6
68 | 50 | 800 | 57 | S/T | 0.878
68 | 50 | 800 | 57 | ∆T | 15.9
68 | 50 | 800 | 57 | LDB | 52.1
68 | 50 | 800 | 57 | LWB | 49.6
68 | 50 | 800 | 57 | kW | 0.68
72 | 50 | 800 | 61 | MBh | 18.9
72 | 50 | 800 | 61 | S/T | 0.815
72 | 50 | 800 | 61 | ∆T | 17.8
72 | 50 | 800 | 61 | LDB | 54.2
72 | 50 | 800 | 61 | LWB | 52.7
72 | 50 | 800 | 61 | kW | 0.84
77 | 50 | 800 | 64 | MBh | 21.5
77 | 50 | 800 | 64 | S/T | 0.758
77 | 50 | 800 | 64 | ∆T | 18.9
77 | 50 | 800 | 64 | LDB | 58.1
77 | 50 | 800 | 64 | LWB | 55
77 | 50 | 800 | 64 | kW | 0.97
80 | 50 | 800 | 67 | MBh | 24
80 | 50 | 800 | 67 | S/T | 0.704
80 | 50 | 800 | 67 | ∆T | 19.6
80 | 50 | 800 | 67 | LDB | 60.4
80 | 50 | 800 | 67 | LWB | 57.6
80 | 50 | 800 | 67 | kW | 1.1
84 | 50 | 800 | 70 | MBh | 26.5
84 | 50 | 800 | 70 | S/T | 0.672
84 | 50 | 800 | 70 | ∆T | 20.6
84 | 50 | 800 | 70 | LDB | 63.4
84 | 50 | 800 | 70 | LWB | 60.2
84 | 50 | 800 | 70 | kW | 1.23
86 | 50 | 800 | 72 | MBh | 28.2
86 | 50 | 800 | 72 | S/T | 0.663
86 | 50 | 800 | 72 | ∆T | 21.6
86 | 50 | 800 | 72 | LDB | 64.4
86 | 50 | 800 | 72 | LWB | 62
86 | 50 | 800 | 72 | kW | 1.32
90 | 50 | 800 | 75 | MBh | 30.7
90 | 50 | 800 | 75 | S/T | 0.619
90 | 50 | 800 | 75 | ∆T | 22
90 | 50 | 800 | 75 | LDB | 68
90 | 50 | 800 | 75 | LWB | 64.8
90 | 50 | 800 | 75 | kW | 1.46
68 | 54 | 800 | 57 | MBh | 15.6
68 | 54 | 800 | 57 | S/T | 0.878
68 | 54 | 800 | 57 | ∆T | 15.9
68 | 54 | 800 | 57 | LDB | 52.1
68 | 54 | 800 | 57 | LWB | 49.6
68 | 54 | 800 | 57 | kW | 0.69
72 | 54 | 800 | 61 | MBh | 18.9
72 | 54 | 800 | 61 | S/T | 0.815
72 | 54 | 800 | 61 | ∆T | 17.8
72 | 54 | 800 | 61 | LDB | 54.2
72 | 54 | 800 | 61 | LWB | 52.7
72 | 54 | 800 | 61 | kW | 0.86
77 | 54 | 800 | 64 | MBh | 21.5
77 | 54 | 800 | 64 | S/T | 0.758
77 | 54 | 800 | 64 | ∆T | 18.9
77 | 54 | 800 | 64 | LDB | 58.1
77 | 54 | 800 | 64 | LWB | 55
77 | 54 | 800 | 64 | kW | 0.99
80 | 54 | 800 | 67 | MBh | 24
80 | 54 | 800 | 67 | S/T | 0.704
80 | 54 | 800 | 67 | ∆T | 19.6
80 | 54 | 800 | 67 | LDB | 60.4
80 | 54 | 800 | 67 | LWB | 57.6
80 | 54 | 800 | 67 | kW | 1.12
84 | 54 | 800 | 70 | MBh | 26.5
84 | 54 | 800 | 70 | S/T | 0.672
84 | 54 | 800 | 70 | ∆T | 20.6
84 | 54 | 800 | 70 | LDB | 63.4
84 | 54 | 800 | 70 | LWB | 60.2
84 | 54 | 800 | 70 | kW | 1.26
86 | 54 | 800 | 72 | MBh | 28.2
86 | 54 | 800 | 72 | S/T | 0.663
86 | 54 | 800 | 72 | ∆T | 21.6
86 | 54 | 800 | 72 | LDB | 64.4
86 | 54 | 800 | 72 | LWB | 62
86 | 54 | 800 | 72 | kW | 1.35
90 | 54 | 800 | 75 | MBh | 30.7
90 | 54 | 800 | 75 | S/T | 0.619
90 | 54 | 800 | 75 | ∆T | 22
90 | 54 | 800 | 75 | LDB | 68
90 | 54 | 800 | 75 | LWB | 64.8
90 | 54 | 800 | 75 | kW | 1.49
68 | 58 | 800 | 57 | MBh | 15.6
68 | 58 | 800 | 57 | S/T | 0.878
68 | 58 | 800 | 57 | ∆T | 15.9
68 | 58 | 800 | 57 | LDB | 52.1
68 | 58 | 800 | 57 | LWB | 49.6
68 | 58 | 800 | 57 | kW | 0.7
72 | 58 | 800 | 61 | MBh | 18.9
72 | 58 | 800 | 61 | S/T | 0.815
72 | 58 | 800 | 61 | ∆T | 17.8
72 | 58 | 800 | 61 | LDB | 54.2
72 | 58 | 800 | 61 | LWB | 52.7
72 | 58 | 800 | 61 | kW | 0.87
77 | 58 | 800 | 64 | MBh | 21.5
77 | 58 | 800 | 64 | S/T | 0.758
77 | 58 | 800 | 64 | ∆T | 18.9
77 | 58 | 800 | 64 | LDB | 58.1
77 | 58 | 800 | 64 | LWB | 55
77 | 58 | 800 | 64 | kW | 1.01
80 | 58 | 800 | 67 | MBh | 24
80 | 58 | 800 | 67 | S/T | 0.704
80 | 58 | 800 | 67 | ∆T | 19.6
80 | 58 | 800 | 67 | LDB | 60.4
80 | 58 | 800 | 67 | LWB | 57.6
80 | 58 | 800 | 67 | kW | 1.14
84 | 58 | 800 | 70 | MBh | 26.5
84 | 58 | 800 | 70 | S/T | 0.672
84 | 58 | 800 | 70 | ∆T | 20.6
84 | 58 | 800 | 70 | LDB | 63.4
84 | 58 | 800 | 70 | LWB | 60.2
84 | 58 | 800 | 70 | kW | 1.28
86 | 58 | 800 | 72 | MBh | 28.2
86 | 58 | 800 | 72 | S/T | 0.663
86 | 58 | 800 | 72 | ∆T | 21.6
86 | 58 | 800 | 72 | LDB | 64.4
86 | 58 | 800 | 72 | LWB | 62
86 | 58 | 800 | 72 | kW | 1.38
90 | 58 | 800 | 75 | MBh | 30.5
90 | 58 | 800 | 75 | S/T | 0.616
90 | 58 | 800 | 75 | ∆T | 21.8
90 | 58 | 800 | 75 | LDB | 68.2
90 | 58 | 800 | 75 | LWB | 64.9
90 | 58 | 800 | 75 | kW | 1.5
68 | 62 | 800 | 57 | MBh | 15.6
68 | 62 | 800 | 57 | S/T | 0.878
68 | 62 | 800 | 57 | ∆T | 15.9
68 | 62 | 800 | 57 | LDB | 52.1
68 | 62 | 800 | 57 | LWB | 49.6
68 | 62 | 800 | 57 | kW | 0.72
72 | 62 | 800 | 61 | MBh | 18.9
72 | 62 | 800 | 61 | S/T | 0.815
72 | 62 | 800 | 61 | ∆T | 17.8
72 | 62 | 800 | 61 | LDB | 54.2
72 | 62 | 800 | 61 | LWB | 52.7
72 | 62 | 800 | 61 | kW | 0.89
77 | 62 | 800 | 64 | MBh | 21.5
77 | 62 | 800 | 64 | S/T | 0.758
77 | 62 | 800 | 64 | ∆T | 18.9
77 | 62 | 800 | 64 | LDB | 58.1
77 | 62 | 800 | 64 | LWB | 55
77 | 62 | 800 | 64 | kW | 1.03
80 | 62 | 800 | 67 | MBh | 24
80 | 62 | 800 | 67 | S/T | 0.704
80 | 62 | 800 | 67 | ∆T | 19.6
80 | 62 | 800 | 67 | LDB | 60.4
80 | 62 | 800 | 67 | LWB | 57.6
80 | 62 | 800 | 67 | kW | 1.17
84 | 62 | 800 | 70 | MBh | 26.5
84 | 62 | 800 | 70 | S/T | 0.672
84 | 62 | 800 | 70 | ∆T | 20.6
84 | 62 | 800 | 70 | LDB | 63.4
84 | 62 | 800 | 70 | LWB | 60.2
84 | 62 | 800 | 70 | kW | 1.31
86 | 62 | 800 | 72 | MBh | 28.2
86 | 62 | 800 | 72 | S/T | 0.663
86 | 62 | 800 | 72 | ∆T | 21.6
86 | 62 | 800 | 72 | LDB | 64.4
86 | 62 | 800 | 72 | LWB | 62
86 | 62 | 800 | 72 | kW | 1.41
90 | 62 | 800 | 75 | MBh | 30
90 | 62 | 800 | 75 | S/T | 0.617
90 | 62 | 800 | 75 | ∆T | 21.4
90 | 62 | 800 | 75 | LDB | 68.6
90 | 62 | 800 | 75 | LWB | 65.1
90 | 62 | 800 | 75 | kW | 1.49
68 | 66 | 800 | 57 | MBh | 15.6
68 | 66 | 800 | 57 | S/T | 0.878
68 | 66 | 800 | 57 | ∆T | 15.9
68 | 66 | 800 | 57 | LDB | 52.1
68 | 66 | 800 | 57 | LWB | 49.6
68 | 66 | 800 | 57 | kW | 0.73
72 | 66 | 800 | 61 | MBh | 18.9
72 | 66 | 800 | 61 | S/T | 0.815
72 | 66 | 800 | 61 | ∆T | 17.8
72 | 66 | 800 | 61 | LDB | 54.2
72 | 66 | 800 | 61 | LWB | 52.7
72 | 66 | 800 | 61 | kW | 0.91
77 | 66 | 800 | 64 | MBh | 21.5
77 | 66 | 800 | 64 | S/T | 0.758
77 | 66 | 800 | 64 | ∆T | 18.9
77 | 66 | 800 | 64 | LDB | 58.1
77 | 66 | 800 | 64 | LWB | 55
77 | 66 | 800 | 64 | kW | 1.05
80 | 66 | 800 | 67 | MBh | 24
80 | 66 | 800 | 67 | S/T | 0.704
80 | 66 | 800 | 67 | ∆T | 19.6
80 | 66 | 800 | 67 | LDB | 60.4
80 | 66 | 800 | 67 | LWB | 57.6
80 | 66 | 800 | 67 | kW | 1.19
84 | 66 | 800 | 70 | MBh | 26.5
84 | 66 | 800 | 70 | S/T | 0.672
84 | 66 | 800 | 70 | ∆T | 20.6
84 | 66 | 800 | 70 | LDB | 63.4
84 | 66 | 800 | 70 | LWB | 60.2
84 | 66 | 800 | 70 | kW | 1.34
86 | 66 | 800 | 72 | MBh | 28.2
86 | 66 | 800 | 72 | S/T | 0.663
86 | 66 | 800 | 72 | ∆T | 21.6
86 | 66 | 800 | 72 | LDB | 64.4
86 | 66 | 800 | 72 | LWB | 62
86 | 66 | 800 | 72 | kW | 1.44
90 | 66 | 800 | 75 | MBh | 29.6
90 | 66 | 800 | 75 | S/T | 0.618
90 | 66 | 800 | 75 | ∆T | 21.2
90 | 66 | 800 | 75 | LDB | 68.8
90 | 66 | 800 | 75 | LWB | 65.2
90 | 66 | 800 | 75 | kW | 1.48
68 | 70 | 800 | 57 | MBh | 15.6
68 | 70 | 800 | 57 | S/T | 0.878
68 | 70 | 800 | 57 | ∆T | 15.9
68 | 70 | 800 | 57 | LDB | 52.1
68 | 70 | 800 | 57 | LWB | 49.6
68 | 70 | 800 | 57 | kW | 0.75
72 | 70 | 800 | 61 | MBh | 18.9
72 | 70 | 800 | 61 | S/T | 0.815
72 | 70 | 800 | 61 | ∆T | 17.8
72 | 70 | 800 | 61 | LDB | 54.2
72 | 70 | 800 | 61 | LWB | 52.7
72 | 70 | 800 | 61 | kW | 0.93
77 | 70 | 800 | 64 | MBh | 21.5
77 | 70 | 800 | 64 | S/T | 0.758
77 | 70 | 800 | 64 | ∆T | 18.9
77 | 70 | 800 | 64 | LDB | 58.1
77 | 70 | 800 | 64 | LWB | 55
77 | 70 | 800 | 64 | kW | 1.07
80 | 70 | 800 | 67 | MBh | 24
80 | 70 | 800 | 67 | S/T | 0.704
80 | 70 | 800 | 67 | ∆T | 19.6
80 | 70 | 800 | 67 | LDB | 60.4
80 | 70 | 800 | 67 | LWB | 57.6
80 | 70 | 800 | 67 | kW | 1.22
84 | 70 | 800 | 70 | MBh | 26.5
84 | 70 | 800 | 70 | S/T | 0.672
84 | 70 | 800 | 70 | ∆T | 20.6
84 | 70 | 800 | 70 | LDB | 63.4
84 | 70 | 800 | 70 | LWB | 60.2
84 | 70 | 800 | 70 | kW | 1.37
86 | 70 | 800 | 72 | MBh | 28.2
86 | 70 | 800 | 72 | S/T | 0.663
86 | 70 | 800 | 72 | ∆T | 21.6
86 | 70 | 800 | 72 | LDB | 64.4
86 | 70 | 800 | 72 | LWB | 62
86 | 70 | 800 | 72 | kW | 1.47
90 | 70 | 800 | 75 | MBh | 29.1
90 | 70 | 800 | 75 | S/T | 0.619
90 | 70 | 800 | 75 | ∆T | 20.8
90 | 70 | 800 | 75 | LDB | 69.2
90 | 70 | 800 | 75 | LWB | 65.4
90 | 70 | 800 | 75 | kW | 1.47
68 | 72 | 800 | 57 | MBh | 15.6
68 | 72 | 800 | 57 | S/T | 0.878
68 | 72 | 800 | 57 | ∆T | 15.9
68 | 72 | 800 | 57 | LDB | 52.1
68 | 72 | 800 | 57 | LWB | 49.6
68 | 72 | 800 | 57 | kW | 0.76
72 | 72 | 800 | 61 | MBh | 18.9
72 | 72 | 800 | 61 | S/T | 0.815
72 | 72 | 800 | 61 | ∆T | 17.8
72 | 72 | 800 | 61 | LDB | 54.2
72 | 72 | 800 | 61 | LWB | 52.7
72 | 72 | 800 | 61 | kW | 0.94
77 | 72 | 800 | 64 | MBh | 21.5
77 | 72 | 800 | 64 | S/T | 0.758
77 | 72 | 800 | 64 | ∆T | 18.9
77 | 72 | 800 | 64 | LDB | 58.1
77 | 72 | 800 | 64 | LWB | 55
77 | 72 | 800 | 64 | kW | 1.09
80 | 72 | 800 | 67 | MBh | 24
80 | 72 | 800 | 67 | S/T | 0.704
80 | 72 | 800 | 67 | ∆T | 19.6
80 | 72 | 800 | 67 | LDB | 60.4
80 | 72 | 800 | 67 | LWB | 57.6
80 | 72 | 800 | 67 | kW | 1.24
84 | 72 | 800 | 70 | MBh | 26.5
84 | 72 | 800 | 70 | S/T | 0.672
84 | 72 | 800 | 70 | ∆T | 20.6
84 | 72 | 800 | 70 | LDB | 63.4
84 | 72 | 800 | 70 | LWB | 60.2
84 | 72 | 800 | 70 | kW | 1.39
86 | 72 | 800 | 72 | MBh | 28.2
86 | 72 | 800 | 72 | S/T | 0.663
86 | 72 | 800 | 72 | ∆T | 21.6
86 | 72 | 800 | 72 | LDB | 64.4
86 | 72 | 800 | 72 | LWB | 62
86 | 72 | 800 | 72 | kW | 1.49
90 | 72 | 800 | 75 | MBh | 28.9
90 | 72 | 800 | 75 | S/T | 0.616
90 | 72 | 800 | 75 | ∆T | 20.6
90 | 72 | 800 | 75 | LDB | 69.4
90 | 72 | 800 | 75 | LWB | 65.5
90 | 72 | 800 | 75 | kW | 1.46
68 | 75 | 800 | 57 | MBh | 15.6
68 | 75 | 800 | 57 | S/T | 0.878
68 | 75 | 800 | 57 | ∆T | 15.9
68 | 75 | 800 | 57 | LDB | 52.1
68 | 75 | 800 | 57 | LWB | 49.6
68 | 75 | 800 | 57 | kW | 0.77
72 | 75 | 800 | 61 | MBh | 18.9
72 | 75 | 800 | 61 | S/T | 0.815
72 | 75 | 800 | 61 | ∆T | 17.8
72 | 75 | 800 | 61 | LDB | 54.2
72 | 75 | 800 | 61 | LWB | 52.7
72 | 75 | 800 | 61 | kW | 0.96
77 | 75 | 800 | 64 | MBh | 21.5
77 | 75 | 800 | 64 | S/T | 0.758
77 | 75 | 800 | 64 | ∆T | 18.9
77 | 75 | 800 | 64 | LDB | 58.1
77 | 75 | 800 | 64 | LWB | 55
77 | 75 | 800 | 64 | kW | 1.11
80 | 75 | 800 | 67 | MBh | 24
80 | 75 | 800 | 67 | S/T | 0.704
80 | 75 | 800 | 67 | ∆T | 19.6
80 | 75 | 800 | 67 | LDB | 60.4
80 | 75 | 800 | 67 | LWB | 57.6
80 | 75 | 800 | 67 | kW | 1.26
84 | 75 | 800 | 70 | MBh | 26.5
84 | 75 | 800 | 70 | S/T | 0.672
84 | 75 | 800 | 70 | ∆T | 20.6
84 | 75 | 800 | 70 | LDB | 63.4
84 | 75 | 800 | 70 | LWB | 60.2
84 | 75 | 800 | 70 | kW | 1.41
86 | 75 | 800 | 72 | MBh | 28
86 | 75 | 800 | 72 | S/T | 0.661
86 | 75 | 800 | 72 | ∆T | 21.4
86 | 75 | 800 | 72 | LDB | 64.6
86 | 75 | 800 | 72 | LWB | 62.1
86 | 75 | 800 | 72 | kW | 1.5
90 | 75 | 800 | 75 | MBh | 28.5
90 | 75 | 800 | 75 | S/T | 0.618
90 | 75 | 800 | 75 | ∆T | 20.4
90 | 75 | 800 | 75 | LDB | 69.6
90 | 75 | 800 | 75 | LWB | 65.6
90 | 75 | 800 | 75 | kW | 1.46
68 | 79 | 800 | 57 | MBh | 15.6
68 | 79 | 800 | 57 | S/T | 0.878
68 | 79 | 800 | 57 | ∆T | 15.9
68 | 79 | 800 | 57 | LDB | 52.1
68 | 79 | 800 | 57 | LWB | 49.6
68 | 79 | 800 | 57 | kW | 0.79
72 | 79 | 800 | 61 | MBh | 18.9
72 | 79 | 800 | 61 | S/T | 0.815
72 | 79 | 800 | 61 | ∆T | 17.8
72 | 79 | 800 | 61 | LDB | 54.2
72 | 79 | 800 | 61 | LWB | 52.7
72 | 79 | 800 | 61 | kW | 0.98
77 | 79 | 800 | 64 | MBh | 21.5
77 | 79 | 800 | 64 | S/T | 0.758
77 | 79 | 800 | 64 | ∆T | 18.9
77 | 79 | 800 | 64 | LDB | 58.1
77 | 79 | 800 | 64 | LWB | 55
77 | 79 | 800 | 64 | kW | 1.13
80 | 79 | 800 | 67 | MBh | 24
80 | 79 | 800 | 67 | S/T | 0.704
80 | 79 | 800 | 67 | ∆T | 19.6
80 | 79 | 800 | 67 | LDB | 60.4
80 | 79 | 800 | 67 | LWB | 57.6
80 | 79 | 800 | 67 | kW | 1.29
84 | 79 | 800 | 70 | MBh | 26.5
84 | 79 | 800 | 70 | S/T | 0.672
84 | 79 | 800 | 70 | ∆T | 20.6
84 | 79 | 800 | 70 | LDB | 63.4
84 | 79 | 800 | 70 | LWB | 60.2
84 | 79 | 800 | 70 | kW | 1.49
86 | 79 | 800 | 72 | MBh | 27.6
86 | 79 | 800 | 72 | S/T | 0.663
86 | 79 | 800 | 72 | ∆T | 21.2
86 | 79 | 800 | 72 | LDB | 64.8
86 | 79 | 800 | 72 | LWB | 62.2
86 | 79 | 800 | 72 | kW | 1.58
90 | 79 | 800 | 75 | MBh | 28.1
90 | 79 | 800 | 75 | S/T | 0.619
90 | 79 | 800 | 75 | ∆T | 20.1
90 | 79 | 800 | 75 | LDB | 69.9
90 | 79 | 800 | 75 | LWB | 65.8
90 | 79 | 800 | 75 | kW | 1.59
68 | 83 | 800 | 57 | MBh | 15.6
68 | 83 | 800 | 57 | S/T | 0.878
68 | 83 | 800 | 57 | ∆T | 15.9
68 | 83 | 800 | 57 | LDB | 52.1
68 | 83 | 800 | 57 | LWB | 49.6
68 | 83 | 800 | 57 | kW | 0.8
72 | 83 | 800 | 61 | MBh | 18.9
72 | 83 | 800 | 61 | S/T | 0.815
72 | 83 | 800 | 61 | ∆T | 17.8
72 | 83 | 800 | 61 | LDB | 54.2
72 | 83 | 800 | 61 | LWB | 52.7
72 | 83 | 800 | 61 | kW | 1.04
77 | 83 | 800 | 64 | MBh | 21.5
77 | 83 | 800 | 64 | S/T | 0.758
77 | 83 | 800 | 64 | ∆T | 18.9
77 | 83 | 800 | 64 | LDB | 58.1
77 | 83 | 800 | 64 | LWB | 55
77 | 83 | 800 | 64 | kW | 1.24
80 | 83 | 800 | 67 | MBh | 24
80 | 83 | 800 | 67 | S/T | 0.704
80 | 83 | 800 | 67 | ∆T | 19.6
80 | 83 | 800 | 67 | LDB | 60.4
80 | 83 | 800 | 67 | LWB | 57.6
80 | 83 | 800 | 67 | kW | 1.46
84 | 83 | 800 | 70 | MBh | 26.5
84 | 83 | 800 | 70 | S/T | 0.672
84 | 83 | 800 | 70 | ∆T | 20.6
84 | 83 | 800 | 70 | LDB | 63.4
84 | 83 | 800 | 70 | LWB | 60.2
84 | 83 | 800 | 70 | kW | 1.7
86 | 83 | 800 | 72 | MBh | 27.1
86 | 83 | 800 | 72 | S/T | 0.664
86 | 83 | 800 | 72 | ∆T | 20.8
86 | 83 | 800 | 72 | LDB | 65.2
86 | 83 | 800 | 72 | LWB | 62.4
86 | 83 | 800 | 72 | kW | 1.74
90 | 83 | 800 | 75 | MBh | 27.6
90 | 83 | 800 | 75 | S/T | 0.62
90 | 83 | 800 | 75 | ∆T | 19.8
90 | 83 | 800 | 75 | LDB | 70.2
90 | 83 | 800 | 75 | LWB | 66
90 | 83 | 800 | 75 | kW | 1.75
68 | 87 | 800 | 57 | MBh | 15.6
68 | 87 | 800 | 57 | S/T | 0.878
68 | 87 | 800 | 57 | ∆T | 15.9
68 | 87 | 800 | 57 | LDB | 52.1
68 | 87 | 800 | 57 | LWB | 49.6
68 | 87 | 800 | 57 | kW | 0.9
72 | 87 | 800 | 61 | MBh | 18.9
72 | 87 | 800 | 61 | S/T | 0.815
72 | 87 | 800 | 61 | ∆T | 17.8
72 | 87 | 800 | 61 | LDB | 54.2
72 | 87 | 800 | 61 | LWB | 52.7
72 | 87 | 800 | 61 | kW | 1.17
77 | 87 | 800 | 64 | MBh | 21.5
77 | 87 | 800 | 64 | S/T | 0.758
77 | 87 | 800 | 64 | ∆T | 18.9
77 | 87 | 800 | 64 | LDB | 58.1
77 | 87 | 800 | 64 | LWB | 55
77 | 87 | 800 | 64 | kW | 1.4
80 | 87 | 800 | 67 | MBh | 24
80 | 87 | 800 | 67 | S/T | 0.704
80 | 87 | 800 | 67 | ∆T | 19.6
80 | 87 | 800 | 67 | LDB | 60.4
80 | 87 | 800 | 67 | LWB | 57.6
80 | 87 | 800 | 67 | kW | 1.64
84 | 87 | 800 | 70 | MBh | 26.4
84 | 87 | 800 | 70 | S/T | 0.67
84 | 87 | 800 | 70 | ∆T | 20.5
84 | 87 | 800 | 70 | LDB | 63.5
84 | 87 | 800 | 70 | LWB | 60.2
84 | 87 | 800 | 70 | kW | 1.89
86 | 87 | 800 | 72 | MBh | 26.7
86 | 87 | 800 | 72 | S/T | 0.663
86 | 87 | 800 | 72 | ∆T | 20.5
86 | 87 | 800 | 72 | LDB | 65.5
86 | 87 | 800 | 72 | LWB | 62.6
86 | 87 | 800 | 72 | kW | 1.9
90 | 87 | 800 | 75 | MBh | 27.2
90 | 87 | 800 | 75 | S/T | 0.618
90 | 87 | 800 | 75 | ∆T | 19.4
90 | 87 | 800 | 75 | LDB | 70.6
90 | 87 | 800 | 75 | LWB | 66.1
90 | 87 | 800 | 75 | kW | 1.91
68 | 91 | 800 | 57 | MBh | 15.6
68 | 91 | 800 | 57 | S/T | 0.878
68 | 91 | 800 | 57 | ∆T | 15.9
68 | 91 | 800 | 57 | LDB | 52.1
68 | 91 | 800 | 57 | LWB | 49.6
68 | 91 | 800 | 57 | kW | 1
72 | 91 | 800 | 61 | MBh | 18.9
72 | 91 | 800 | 61 | S/T | 0.815
72 | 91 | 800 | 61 | ∆T | 17.8
72 | 91 | 800 | 61 | LDB | 54.2
72 | 91 | 800 | 61 | LWB | 52.7
72 | 91 | 800 | 61 | kW | 1.3
77 | 91 | 800 | 64 | MBh | 21.5
77 | 91 | 800 | 64 | S/T | 0.758
77 | 91 | 800 | 64 | ∆T | 18.9
77 | 91 | 800 | 64 | LDB | 58.1
77 | 91 | 800 | 64 | LWB | 55
77 | 91 | 800 | 64 | kW | 1.56
80 | 91 | 800 | 67 | MBh | 24
80 | 91 | 800 | 67 | S/T | 0.704
80 | 91 | 800 | 67 | ∆T | 19.6
80 | 91 | 800 | 67 | LDB | 60.4
80 | 91 | 800 | 67 | LWB | 57.6
80 | 91 | 800 | 67 | kW | 1.84
84 | 91 | 800 | 70 | MBh | 25.9
84 | 91 | 800 | 70 | S/T | 0.668
84 | 91 | 800 | 70 | ∆T | 20
84 | 91 | 800 | 70 | LDB | 64
84 | 91 | 800 | 70 | LWB | 60.5
84 | 91 | 800 | 70 | kW | 2.05
86 | 91 | 800 | 72 | MBh | 26.2
86 | 91 | 800 | 72 | S/T | 0.664
86 | 91 | 800 | 72 | ∆T | 20.1
86 | 91 | 800 | 72 | LDB | 65.9
86 | 91 | 800 | 72 | LWB | 62.8
86 | 91 | 800 | 72 | kW | 2.06
90 | 91 | 800 | 75 | MBh | 26.7
90 | 91 | 800 | 75 | S/T | 0.618
90 | 91 | 800 | 75 | ∆T | 19.1
90 | 91 | 800 | 75 | LDB | 70.9
90 | 91 | 800 | 75 | LWB | 66.3
90 | 91 | 800 | 75 | kW | 2.08
68 | 93 | 800 | 57 | MBh | 15.6
68 | 93 | 800 | 57 | S/T | 0.878
68 | 93 | 800 | 57 | ∆T | 15.9
68 | 93 | 800 | 57 | LDB | 52.1
68 | 93 | 800 | 57 | LWB | 49.6
68 | 93 | 800 | 57 | kW | 1.05
72 | 93 | 800 | 61 | MBh | 18.9
72 | 93 | 800 | 61 | S/T | 0.815
72 | 93 | 800 | 61 | ∆T | 17.8
72 | 93 | 800 | 61 | LDB | 54.2
72 | 93 | 800 | 61 | LWB | 52.7
72 | 93 | 800 | 61 | kW | 1.38
77 | 93 | 800 | 64 | MBh | 21.5
77 | 93 | 800 | 64 | S/T | 0.758
77 | 93 | 800 | 64 | ∆T | 18.9
77 | 93 | 800 | 64 | LDB | 58.1
77 | 93 | 800 | 64 | LWB | 55
77 | 93 | 800 | 64 | kW | 1.65
80 | 93 | 800 | 67 | MBh | 24
80 | 93 | 800 | 67 | S/T | 0.704
80 | 93 | 800 | 67 | ∆T | 19.6
80 | 93 | 800 | 67 | LDB | 60.4
80 | 93 | 800 | 67 | LWB | 57.6
80 | 93 | 800 | 67 | kW | 1.94
84 | 93 | 800 | 70 | MBh | 25.7
84 | 93 | 800 | 70 | S/T | 0.669
84 | 93 | 800 | 70 | ∆T | 19.9
84 | 93 | 800 | 70 | LDB | 64.1
84 | 93 | 800 | 70 | LWB | 60.5
84 | 93 | 800 | 70 | kW | 2.14
86 | 93 | 800 | 72 | MBh | 26
86 | 93 | 800 | 72 | S/T | 0.662
86 | 93 | 800 | 72 | ∆T | 19.9
86 | 93 | 800 | 72 | LDB | 66.1
86 | 93 | 800 | 72 | LWB | 62.9
86 | 93 | 800 | 72 | kW | 2.15
90 | 93 | 800 | 75 | MBh | 26.5
90 | 93 | 800 | 75 | S/T | 0.619
90 | 93 | 800 | 75 | ∆T | 19
90 | 93 | 800 | 75 | LDB | 71
90 | 93 | 800 | 75 | LWB | 66.4
90 | 93 | 800 | 75 | kW | 2.16
68 | 95 | 800 | 57 | MBh | 15.6
68 | 95 | 800 | 57 | S/T | 0.878
68 | 95 | 800 | 57 | ∆T | 15.9
68 | 95 | 800 | 57 | LDB | 52.1
68 | 95 | 800 | 57 | LWB | 49.6
68 | 95 | 800 | 57 | kW | 1.11
72 | 95 | 800 | 61 | MBh | 18.9
72 | 95 | 800 | 61 | S/T | 0.815
72 | 95 | 800 | 61 | ∆T | 17.8
72 | 95 | 800 | 61 | LDB | 54.2
72 | 95 | 800 | 61 | LWB | 52.7
72 | 95 | 800 | 61 | kW | 1.45
77 | 95 | 800 | 64 | MBh | 21.5
77 | 95 | 800 | 64 | S/T | 0.758
77 | 95 | 800 | 64 | ∆T | 18.9
77 | 95 | 800 | 64 | LDB | 58.1
77 | 95 | 800 | 64 | LWB | 55
77 | 95 | 800 | 64 | kW | 1.74
80 | 95 | 800 | 67 | MBh | 24
80 | 95 | 800 | 67 | S/T | 0.704
80 | 95 | 800 | 67 | ∆T | 19.6
80 | 95 | 800 | 67 | LDB | 60.4
80 | 95 | 800 | 67 | LWB | 57.6
80 | 95 | 800 | 67 | kW | 2.05
84 | 95 | 800 | 70 | MBh | 25.5
84 | 95 | 800 | 70 | S/T | 0.667
84 | 95 | 800 | 70 | ∆T | 19.7
84 | 95 | 800 | 70 | LDB | 64.3
84 | 95 | 800 | 70 | LWB | 60.6
84 | 95 | 800 | 70 | kW | 2.22
86 | 95 | 800 | 72 | MBh | 25.8
86 | 95 | 800 | 72 | S/T | 0.663
86 | 95 | 800 | 72 | ∆T | 19.8
86 | 95 | 800 | 72 | LDB | 66.2
86 | 95 | 800 | 72 | LWB | 62.9
86 | 95 | 800 | 72 | kW | 2.23
90 | 95 | 800 | 75 | MBh | 26.3
90 | 95 | 800 | 75 | S/T | 0.616
90 | 95 | 800 | 75 | ∆T | 18.8
90 | 95 | 800 | 75 | LDB | 71.2
90 | 95 | 800 | 75 | LWB | 66.4
90 | 95 | 800 | 75 | kW | 2.24
68 | 99 | 800 | 57 | MBh | 15.6
68 | 99 | 800 | 57 | S/T | 0.878
68 | 99 | 800 | 57 | ∆T | 15.9
68 | 99 | 800 | 57 | LDB | 52.1
68 | 99 | 800 | 57 | LWB | 49.6
68 | 99 | 800 | 57 | kW | 1.22
72 | 99 | 800 | 61 | MBh | 18.9
72 | 99 | 800 | 61 | S/T | 0.815
72 | 99 | 800 | 61 | ∆T | 17.8
72 | 99 | 800 | 61 | LDB | 54.2
72 | 99 | 800 | 61 | LWB | 52.7
72 | 99 | 800 | 61 | kW | 1.6
77 | 99 | 800 | 64 | MBh | 21.5
77 | 99 | 800 | 64 | S/T | 0.758
77 | 99 | 800 | 64 | ∆T | 18.9
77 | 99 | 800 | 64 | LDB | 58.1
77 | 99 | 800 | 64 | LWB | 55
77 | 99 | 800 | 64 | kW | 1.93
80 | 99 | 800 | 67 | MBh | 24
80 | 99 | 800 | 67 | S/T | 0.704
80 | 99 | 800 | 67 | ∆T | 19.6
80 | 99 | 800 | 67 | LDB | 60.4
80 | 99 | 800 | 67 | LWB | 57.6
80 | 99 | 800 | 67 | kW | 2.28
84 | 99 | 800 | 70 | MBh | 25
84 | 99 | 800 | 70 | S/T | 0.672
84 | 99 | 800 | 70 | ∆T | 19.4
84 | 99 | 800 | 70 | LDB | 64.6
84 | 99 | 800 | 70 | LWB | 60.8
84 | 99 | 800 | 70 | kW | 2.38
86 | 99 | 800 | 72 | MBh | 25.3
86 | 99 | 800 | 72 | S/T | 0.664
86 | 99 | 800 | 72 | ∆T | 19.4
86 | 99 | 800 | 72 | LDB | 66.6
86 | 99 | 800 | 72 | LWB | 63.1
86 | 99 | 800 | 72 | kW | 2.39
90 | 99 | 800 | 75 | MBh | 25.8
90 | 99 | 800 | 75 | S/T | 0.62
90 | 99 | 800 | 75 | ∆T | 18.5
90 | 99 | 800 | 75 | LDB | 71.5
90 | 99 | 800 | 75 | LWB | 66.6
90 | 99 | 800 | 75 | kW | 2.41
68 | 103 | 800 | 57 | MBh | 15.6
68 | 103 | 800 | 57 | S/T | 0.878
68 | 103 | 800 | 57 | ∆T | 15.9
68 | 103 | 800 | 57 | LDB | 52.1
68 | 103 | 800 | 57 | LWB | 49.6
68 | 103 | 800 | 57 | kW | 1.35
72 | 103 | 800 | 61 | MBh | 18.9
72 | 103 | 800 | 61 | S/T | 0.815
72 | 103 | 800 | 61 | ∆T | 17.8
72 | 103 | 800 | 61 | LDB | 54.2
72 | 103 | 800 | 61 | LWB | 52.7
72 | 103 | 800 | 61 | kW | 1.77
77 | 103 | 800 | 64 | MBh | 21.5
77 | 103 | 800 | 64 | S/T | 0.758
77 | 103 | 800 | 64 | ∆T | 18.9
77 | 103 | 800 | 64 | LDB | 58.1
77 | 103 | 800 | 64 | LWB | 55
77 | 103 | 800 | 64 | kW | 2.13
80 | 103 | 800 | 67 | MBh | 24
80 | 103 | 800 | 67 | S/T | 0.704
80 | 103 | 800 | 67 | ∆T | 19.6
80 | 103 | 800 | 67 | LDB | 60.4
80 | 103 | 800 | 67 | LWB | 57.6
80 | 103 | 800 | 67 | kW | 2.51
84 | 103 | 800 | 70 | MBh | 24.6
84 | 103 | 800 | 70 | S/T | 0.671
84 | 103 | 800 | 70 | ∆T | 19.1
84 | 103 | 800 | 70 | LDB | 64.9
84 | 103 | 800 | 70 | LWB | 61
84 | 103 | 800 | 70 | kW | 2.55
86 | 103 | 800 | 72 | MBh | 24.9
86 | 103 | 800 | 72 | S/T | 0.663
86 | 103 | 800 | 72 | ∆T | 19.1
86 | 103 | 800 | 72 | LDB | 66.9
86 | 103 | 800 | 72 | LWB | 63.3
86 | 103 | 800 | 72 | kW | 2.56
90 | 103 | 800 | 75 | MBh | 25.4
90 | 103 | 800 | 75 | S/T | 0.622
90 | 103 | 800 | 75 | ∆T | 18.3
90 | 103 | 800 | 75 | LDB | 71.7
90 | 103 | 800 | 75 | LWB | 66.7
90 | 103 | 800 | 75 | kW | 2.58
68 | 106 | 800 | 57 | MBh | 15.6
68 | 106 | 800 | 57 | S/T | 0.878
68 | 106 | 800 | 57 | ∆T | 15.9
68 | 106 | 800 | 57 | LDB | 52.1
68 | 106 | 800 | 57 | LWB | 49.6
68 | 106 | 800 | 57 | kW | 1.44
72 | 106 | 800 | 61 | MBh | 18.9
72 | 106 | 800 | 61 | S/T | 0.815
72 | 106 | 800 | 61 | ∆T | 17.8
72 | 106 | 800 | 61 | LDB | 54.2
72 | 106 | 800 | 61 | LWB | 52.7
72 | 106 | 800 | 61 | kW | 1.9
77 | 106 | 800 | 64 | MBh | 21.5
77 | 106 | 800 | 64 | S/T | 0.758
77 | 106 | 800 | 64 | ∆T | 18.9
77 | 106 | 800 | 64 | LDB | 58.1
77 | 106 | 800 | 64 | LWB | 55
77 | 106 | 800 | 64 | kW | 2.29
80 | 106 | 800 | 67 | MBh | 23.7
80 | 106 | 800 | 67 | S/T | 0.709
80 | 106 | 800 | 67 | ∆T | 19.4
80 | 106 | 800 | 67 | LDB | 60.6
80 | 106 | 800 | 67 | LWB | 57.7
80 | 106 | 800 | 67 | kW | 2.65
84 | 106 | 800 | 70 | MBh | 24.2
84 | 106 | 800 | 70 | S/T | 0.674
84 | 106 | 800 | 70 | ∆T | 18.9
84 | 106 | 800 | 70 | LDB | 65.1
84 | 106 | 800 | 70 | LWB | 61.1
84 | 106 | 800 | 70 | kW | 2.67
86 | 106 | 800 | 72 | MBh | 24.6
86 | 106 | 800 | 72 | S/T | 0.663
86 | 106 | 800 | 72 | ∆T | 18.9
86 | 106 | 800 | 72 | LDB | 67.1
86 | 106 | 800 | 72 | LWB | 63.4
86 | 106 | 800 | 72 | kW | 2.68
90 | 106 | 800 | 75 | MBh | 25.1
90 | 106 | 800 | 75 | S/T | 0.622
90 | 106 | 800 | 75 | ∆T | 18.1
90 | 106 | 800 | 75 | LDB | 71.9
90 | 106 | 800 | 75 | LWB | 66.9
90 | 106 | 800 | 75 | kW | 2.7
68 | 110 | 800 | 57 | MBh | 15.6
68 | 110 | 800 | 57 | S/T | 0.878
68 | 110 | 800 | 57 | ∆T | 15.9
68 | 110 | 800 | 57 | LDB | 52.1
68 | 110 | 800 | 57 | LWB | 49.6
68 | 110 | 800 | 57 | kW | 1.58
72 | 110 | 800 | 61 | MBh | 18.9
72 | 110 | 800 | 61 | S/T | 0.815
72 | 110 | 800 | 61 | ∆T | 17.8
72 | 110 | 800 | 61 | LDB | 54.2
72 | 110 | 800 | 61 | LWB | 52.7
72 | 110 | 800 | 61 | kW | 2.09
77 | 110 | 800 | 64 | MBh | 21.5
77 | 110 | 800 | 64 | S/T | 0.758
77 | 110 | 800 | 64 | ∆T | 18.9
77 | 110 | 800 | 64 | LDB | 58.1
77 | 110 | 800 | 64 | LWB | 55
77 | 110 | 800 | 64 | kW | 2.51
80 | 110 | 800 | 67 | MBh | 23.3
80 | 110 | 800 | 67 | S/T | 0.708
80 | 110 | 800 | 67 | ∆T | 19.1
80 | 110 | 800 | 67 | LDB | 60.9
80 | 110 | 800 | 67 | LWB | 57.9
80 | 110 | 800 | 67 | kW | 2.81
84 | 110 | 800 | 70 | MBh | 23.8
84 | 110 | 800 | 70 | S/T | 0.672
84 | 110 | 800 | 70 | ∆T | 18.5
84 | 110 | 800 | 70 | LDB | 65.5
84 | 110 | 800 | 70 | LWB | 61.3
84 | 110 | 800 | 70 | kW | 2.84
86 | 110 | 800 | 72 | MBh | 24.1
86 | 110 | 800 | 72 | S/T | 0.664
86 | 110 | 800 | 72 | ∆T | 18.5
86 | 110 | 800 | 72 | LDB | 67.5
86 | 110 | 800 | 72 | LWB | 63.6
86 | 110 | 800 | 72 | kW | 2.85
90 | 110 | 800 | 75 | MBh | 24.1
90 | 110 | 800 | 75 | S/T | 0.622
90 | 110 | 800 | 75 | ∆T | 17.4
90 | 110 | 800 | 75 | LDB | 72.6
90 | 110 | 800 | 75 | LWB | 67.2
90 | 110 | 800 | 75 | kW | 2.85
68 | 115 | 800 | 57 | MBh | 15.6
68 | 115 | 800 | 57 | S/T | 0.878
68 | 115 | 800 | 57 | ∆T | 15.9
68 | 115 | 800 | 57 | LDB | 52.1
68 | 115 | 800 | 57 | LWB | 49.6
68 | 115 | 800 | 57 | kW | 1.77
72 | 115 | 800 | 61 | MBh | 18.9
72 | 115 | 800 | 61 | S/T | 0.815
72 | 115 | 800 | 61 | ∆T | 17.8
72 | 115 | 800 | 61 | LDB | 54.2
72 | 115 | 800 | 61 | LWB | 52.7
72 | 115 | 800 | 61 | kW | 2.34
77 | 115 | 800 | 64 | MBh | 21.5
77 | 115 | 800 | 64 | S/T | 0.758
77 | 115 | 800 | 64 | ∆T | 18.9
77 | 115 | 800 | 64 | LDB | 58.1
77 | 115 | 800 | 64 | LWB | 55
77 | 115 | 800 | 64 | kW | 2.82
80 | 115 | 800 | 67 | MBh | 22.5
80 | 115 | 800 | 67 | S/T | 0.707
80 | 115 | 800 | 67 | ∆T | 18.4
80 | 115 | 800 | 67 | LDB | 61.6
80 | 115 | 800 | 67 | LWB | 58.2
80 | 115 | 800 | 67 | kW | 3.01
84 | 115 | 800 | 70 | MBh | 22.5
84 | 115 | 800 | 70 | S/T | 0.671
84 | 115 | 800 | 70 | ∆T | 17.5
84 | 115 | 800 | 70 | LDB | 66.5
84 | 115 | 800 | 70 | LWB | 61.8
84 | 115 | 800 | 70 | kW | 3.01
86 | 115 | 800 | 72 | MBh | 22.5
86 | 115 | 800 | 72 | S/T | 0.662
86 | 115 | 800 | 72 | ∆T | 17.2
86 | 115 | 800 | 72 | LDB | 68.8
86 | 115 | 800 | 72 | LWB | 64.2
86 | 115 | 800 | 72 | kW | 3.01
90 | 115 | 800 | 75 | MBh | 22.5
90 | 115 | 800 | 75 | S/T | 0.622
90 | 115 | 800 | 75 | ∆T | 16.2
90 | 115 | 800 | 75 | LDB | 73.8
90 | 115 | 800 | 75 | LWB | 67.8
90 | 115 | 800 | 75 | kW | 3.01
68 | 118 | 800 | 57 | MBh | 15.6
68 | 118 | 800 | 57 | S/T | 0.878
68 | 118 | 800 | 57 | ∆T | 15.9
68 | 118 | 800 | 57 | LDB | 52.1
68 | 118 | 800 | 57 | LWB | 49.6
68 | 118 | 800 | 57 | kW | 1.89
72 | 118 | 800 | 61 | MBh | 18.9
72 | 118 | 800 | 61 | S/T | 0.815
72 | 118 | 800 | 61 | ∆T | 17.8
72 | 118 | 800 | 61 | LDB | 54.2
72 | 118 | 800 | 61 | LWB | 52.7
72 | 118 | 800 | 61 | kW | 2.5
77 | 118 | 800 | 64 | MBh | 19.3
77 | 118 | 800 | 64 | S/T | 0.762
77 | 118 | 800 | 64 | ∆T | 17
77 | 118 | 800 | 64 | LDB | 60
77 | 118 | 800 | 64 | LWB | 56
77 | 118 | 800 | 64 | kW | 2.56
80 | 118 | 800 | 67 | MBh | 19.3
80 | 118 | 800 | 67 | S/T | 0.71
80 | 118 | 800 | 67 | ∆T | 15.9
80 | 118 | 800 | 67 | LDB | 64.1
80 | 118 | 800 | 67 | LWB | 59.6
80 | 118 | 800 | 67 | kW | 2.56
84 | 118 | 800 | 70 | MBh | 19.3
84 | 118 | 800 | 70 | S/T | 0.674
84 | 118 | 800 | 70 | ∆T | 15
84 | 118 | 800 | 70 | LDB | 69
84 | 118 | 800 | 70 | LWB | 63.1
84 | 118 | 800 | 70 | kW | 2.56
86 | 118 | 800 | 72 | MBh | 19.3
86 | 118 | 800 | 72 | S/T | 0.663
86 | 118 | 800 | 72 | ∆T | 14.8
86 | 118 | 800 | 72 | LDB | 71.2
86 | 118 | 800 | 72 | LWB | 65.4
86 | 118 | 800 | 72 | kW | 2.56
90 | 118 | 800 | 75 | MBh | 19.3
90 | 118 | 800 | 75 | S/T | 0.622
90 | 118 | 800 | 75 | ∆T | 13.9
90 | 118 | 800 | 75 | LDB | 76.1
90 | 118 | 800 | 75 | LWB | 68.9
90 | 118 | 800 | 75 | kW | 2.56
68 | 122 | 800 | 57 | MBh | 14.7
68 | 122 | 800 | 57 | S/T | 0.878
68 | 122 | 800 | 57 | ∆T | 14.9
68 | 122 | 800 | 57 | LDB | 53.1
68 | 122 | 800 | 57 | LWB | 50.1
68 | 122 | 800 | 57 | kW | 1.89
72 | 122 | 800 | 61 | MBh | 14.7
72 | 122 | 800 | 61 | S/T | 0.816
72 | 122 | 800 | 61 | ∆T | 13.9
72 | 122 | 800 | 61 | LDB | 58.1
72 | 122 | 800 | 61 | LWB | 54.6
72 | 122 | 800 | 61 | kW | 1.89
77 | 122 | 800 | 64 | MBh | 14.7
77 | 122 | 800 | 64 | S/T | 0.762
77 | 122 | 800 | 64 | ∆T | 13
77 | 122 | 800 | 64 | LDB | 64
77 | 122 | 800 | 64 | LWB | 58
77 | 122 | 800 | 64 | kW | 1.89
80 | 122 | 800 | 67 | MBh | 14.7
80 | 122 | 800 | 67 | S/T | 0.707
80 | 122 | 800 | 67 | ∆T | 12
80 | 122 | 800 | 67 | LDB | 68
80 | 122 | 800 | 67 | LWB | 61.4
80 | 122 | 800 | 67 | kW | 1.89
84 | 122 | 800 | 70 | MBh | 14.7
84 | 122 | 800 | 70 | S/T | 0.673
84 | 122 | 800 | 70 | ∆T | 11.5
84 | 122 | 800 | 70 | LDB | 72.5
84 | 122 | 800 | 70 | LWB | 64.8
84 | 122 | 800 | 70 | kW | 1.89
86 | 122 | 800 | 72 | MBh | 14.7
86 | 122 | 800 | 72 | S/T | 0.665
86 | 122 | 800 | 72 | ∆T | 11.3
86 | 122 | 800 | 72 | LDB | 74.7
86 | 122 | 800 | 72 | LWB | 67.1
86 | 122 | 800 | 72 | kW | 1.89
90 | 122 | 800 | 75 | MBh | 14.7
90 | 122 | 800 | 75 | S/T | 0.622
90 | 122 | 800 | 75 | ∆T | 10.6
90 | 122 | 800 | 75 | LDB | 79.4
90 | 122 | 800 | 75 | LWB | 70.4
90 | 122 | 800 | 75 | kW | 1.89

## RZA30AAVJU - FTA30AAVJUD
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1000 | 57 | MBh | 19.1 | 64 | 60 | 61 | 42 | 3.99
68 | 23 | 1000 | 57 | S/T | 0.806 | 64 | 60 | 65 | 38.9 | 3.63
68 | 23 | 1000 | 57 | ∆T | 14.3 | 64 | 60 | 68 | 36.6 | 3.38
68 | 23 | 1000 | 57 | LDB | 53.7 | 64 | 60 | 70 | 35 | 3.23
68 | 23 | 1000 | 57 | LWB | 49.8 | 64 | 60 | 72 | 33.4 | 3.08
68 | 23 | 1000 | 57 | kW | 0.79 | 64 | 60 | 75 | 31.1 | 2.87
72 | 23 | 1000 | 61 | MBh | 23.2 | 60 | 56 | 61 | 42 | 4.16
72 | 23 | 1000 | 61 | S/T | 0.78 | 60 | 56 | 65 | 38.9 | 3.77
72 | 23 | 1000 | 61 | ∆T | 16.8 | 60 | 56 | 68 | 36.6 | 3.51
72 | 23 | 1000 | 61 | LDB | 55.2 | 60 | 56 | 70 | 35 | 3.34
72 | 23 | 1000 | 61 | LWB | 52.8 | 60 | 56 | 72 | 33.4 | 3.18
72 | 23 | 1000 | 61 | kW | 0.96 | 60 | 56 | 75 | 31.1 | 2.96
77 | 23 | 1000 | 64 | MBh | 26.3 | 57 | 53 | 61 | 42 | 4.3
77 | 23 | 1000 | 64 | S/T | 0.76 | 57 | 53 | 65 | 38.9 | 3.89
77 | 23 | 1000 | 64 | ∆T | 18.5 | 57 | 53 | 68 | 36.6 | 3.61
77 | 23 | 1000 | 64 | LDB | 58.5 | 57 | 53 | 70 | 35 | 3.44
77 | 23 | 1000 | 64 | LWB | 55.2 | 57 | 53 | 72 | 33.4 | 3.27
77 | 23 | 1000 | 64 | kW | 1.11 | 57 | 53 | 75 | 31.1 | 3.03
80 | 23 | 1000 | 67 | MBh | 29.4 | 54 | 50 | 61 | 42 | 4.45
80 | 23 | 1000 | 67 | S/T | 0.711 | 54 | 50 | 65 | 38.9 | 4.02
80 | 23 | 1000 | 67 | ∆T | 19.4 | 54 | 50 | 68 | 36.6 | 3.73
80 | 23 | 1000 | 67 | LDB | 60.6 | 54 | 50 | 70 | 35 | 3.54
80 | 23 | 1000 | 67 | LWB | 57.8 | 54 | 50 | 72 | 33.4 | 3.36
80 | 23 | 1000 | 67 | kW | 1.26 | 54 | 50 | 75 | 31.1 | 3.11
84 | 23 | 1000 | 70 | MBh | 32.5 | 51 | 47 | 61 | 42 | 4.62
84 | 23 | 1000 | 70 | S/T | 0.668 | 51 | 47 | 65 | 38.9 | 4.16
84 | 23 | 1000 | 70 | ∆T | 20.1 | 51 | 47 | 68 | 36.6 | 3.85
84 | 23 | 1000 | 70 | LDB | 63.9 | 51 | 47 | 70 | 35 | 3.65
84 | 23 | 1000 | 70 | LWB | 60.4 | 51 | 47 | 72 | 33.4 | 3.47
84 | 23 | 1000 | 70 | kW | 1.41 | 51 | 47 | 75 | 31.1 | 3.2
86 | 23 | 1000 | 72 | MBh | 34.6 | 47 | 43 | 61 | 42 | 4.86
86 | 23 | 1000 | 72 | S/T | 0.659 | 47 | 43 | 65 | 38.9 | 4.37
86 | 23 | 1000 | 72 | ∆T | 21.1 | 47 | 43 | 68 | 36.6 | 4.03
86 | 23 | 1000 | 72 | LDB | 64.9 | 47 | 43 | 70 | 35 | 3.82
86 | 23 | 1000 | 72 | LWB | 62.2 | 47 | 43 | 72 | 33.4 | 3.62
86 | 23 | 1000 | 72 | kW | 1.51 | 47 | 43 | 75 | 31.1 | 3.33
90 | 23 | 1000 | 75 | MBh | 37.7 | 44 | 40 | 61 | 42 | 5.06
90 | 23 | 1000 | 75 | S/T | 0.61 | 44 | 40 | 65 | 38.9 | 4.55
90 | 23 | 1000 | 75 | ∆T | 21.3 | 44 | 40 | 68 | 36.6 | 4.19
90 | 23 | 1000 | 75 | LDB | 68.7 | 44 | 40 | 70 | 35 | 3.96
90 | 23 | 1000 | 75 | LWB | 65 | 44 | 40 | 72 | 33.4 | 3.74
90 | 23 | 1000 | 75 | kW | 1.67 | 44 | 40 | 75 | 31.1 | 3.44
68 | 30 | 1000 | 57 | MBh | 19.1 | 39 | 36 | 61 | 42 | 5.36
68 | 30 | 1000 | 57 | S/T | 0.806 | 39 | 36 | 65 | 38.9 | 4.8
68 | 30 | 1000 | 57 | ∆T | 14.3 | 39 | 36 | 68 | 36.6 | 4.41
68 | 30 | 1000 | 57 | LDB | 53.7 | 39 | 36 | 70 | 35 | 4.16
68 | 30 | 1000 | 57 | LWB | 49.8 | 39 | 36 | 72 | 33.4 | 3.93
68 | 30 | 1000 | 57 | kW | 0.81 | 39 | 36 | 75 | 31.1 | 3.6
72 | 30 | 1000 | 61 | MBh | 23.2 | 35 | 32 | 61 | 42 | 5.71
72 | 30 | 1000 | 61 | S/T | 0.78 | 35 | 32 | 65 | 38.9 | 5.09
72 | 30 | 1000 | 61 | ∆T | 16.8 | 35 | 32 | 68 | 36.6 | 4.67
72 | 30 | 1000 | 61 | LDB | 55.2 | 35 | 32 | 70 | 35 | 4.4
72 | 30 | 1000 | 61 | LWB | 52.8 | 35 | 32 | 72 | 33.4 | 4.14
72 | 30 | 1000 | 61 | kW | 0.99 | 35 | 32 | 75 | 31.1 | 3.78
77 | 30 | 1000 | 64 | MBh | 26.3 | 30 | 28 | 61 | 42 | 6.1
77 | 30 | 1000 | 64 | S/T | 0.76 | 30 | 28 | 65 | 38.9 | 5.43
77 | 30 | 1000 | 64 | ∆T | 18.5 | 30 | 28 | 68 | 36.6 | 4.96
77 | 30 | 1000 | 64 | LDB | 58.5 | 30 | 28 | 70 | 35 | 4.66
77 | 30 | 1000 | 64 | LWB | 55.2 | 30 | 28 | 72 | 33.4 | 4.38
77 | 30 | 1000 | 64 | kW | 1.14 | 30 | 28 | 75 | 31.1 | 3.99
80 | 30 | 1000 | 67 | MBh | 29.4 | 26 | 24 | 61 | 42 | 6.38
80 | 30 | 1000 | 67 | S/T | 0.711 | 26 | 24 | 65 | 38.9 | 5.81
80 | 30 | 1000 | 67 | ∆T | 19.4 | 26 | 24 | 68 | 36.6 | 5.29
80 | 30 | 1000 | 67 | LDB | 60.6 | 26 | 24 | 70 | 35 | 4.97
80 | 30 | 1000 | 67 | LWB | 57.8 | 26 | 24 | 72 | 33.4 | 4.66
80 | 30 | 1000 | 67 | kW | 1.3 | 26 | 24 | 75 | 31.1 | 4.23
84 | 30 | 1000 | 70 | MBh | 32.5 | 22 | 20 | 61 | 42 | 6.07
84 | 30 | 1000 | 70 | S/T | 0.668 | 22 | 20 | 65 | 38.9 | 6.25
84 | 30 | 1000 | 70 | ∆T | 20.1 | 22 | 20 | 68 | 36.6 | 5.68
84 | 30 | 1000 | 70 | LDB | 63.9 | 22 | 20 | 70 | 35 | 5.33
84 | 30 | 1000 | 70 | LWB | 60.4 | 22 | 20 | 72 | 33.4 | 4.99
84 | 30 | 1000 | 70 | kW | 1.45 | 22 | 20 | 75 | 31.1 | 4.51
86 | 30 | 1000 | 72 | MBh | 34.6 | 19 | 18 | 61 | 41.2 | 5.9
86 | 30 | 1000 | 72 | S/T | 0.659 | 19 | 18 | 65 | 38.9 | 6.4
86 | 30 | 1000 | 72 | ∆T | 21.1 | 19 | 18 | 68 | 36.6 | 5.9
86 | 30 | 1000 | 72 | LDB | 64.9 | 19 | 18 | 70 | 35 | 5.52
86 | 30 | 1000 | 72 | LWB | 62.2 | 19 | 18 | 72 | 33.4 | 5.17
86 | 30 | 1000 | 72 | kW | 1.56 | 19 | 18 | 75 | 31.1 | 4.66
90 | 30 | 1000 | 75 | MBh | 37.7 | 17 | 16 | 61 | 40 | 5.67
90 | 30 | 1000 | 75 | S/T | 0.61 | 17 | 16 | 65 | 38.9 | 6.19
90 | 30 | 1000 | 75 | ∆T | 21.3 | 17 | 16 | 68 | 36.6 | 6.19
90 | 30 | 1000 | 75 | LDB | 68.7 | 17 | 16 | 70 | 35 | 5.79
90 | 30 | 1000 | 75 | LWB | 65 | 17 | 16 | 72 | 33.4 | 5.41
90 | 30 | 1000 | 75 | kW | 1.73 | 17 | 16 | 75 | 31.1 | 4.87
68 | 40 | 1000 | 57 | MBh | 19.1 | 15 | 14 | 61 | 39.3 | 5.53
68 | 40 | 1000 | 57 | S/T | 0.806 | 15 | 14 | 65 | 38.9 | 6.06
68 | 40 | 1000 | 57 | ∆T | 14.3 | 15 | 14 | 68 | 36.6 | 6.39
68 | 40 | 1000 | 57 | LDB | 53.7 | 15 | 14 | 70 | 35 | 5.97
68 | 40 | 1000 | 57 | LWB | 49.8 | 15 | 14 | 72 | 33.4 | 5.57
68 | 40 | 1000 | 57 | kW | 0.84 | 15 | 14 | 75 | 31.1 | 5.01
72 | 40 | 1000 | 61 | MBh | 23.2 | 13 | 12 | 61 | 38.3 | 5.33
72 | 40 | 1000 | 61 | S/T | 0.78 | 13 | 12 | 65 | 38.3 | 5.88
72 | 40 | 1000 | 61 | ∆T | 16.8 | 13 | 12 | 68 | 36.6 | 6.28
72 | 40 | 1000 | 61 | LDB | 55.2 | 13 | 12 | 70 | 35 | 6.22
72 | 40 | 1000 | 61 | LWB | 52.8 | 13 | 12 | 72 | 33.4 | 5.8
72 | 40 | 1000 | 61 | kW | 1.04 | 13 | 12 | 75 | 31.1 | 5.21
77 | 40 | 1000 | 64 | MBh | 26.3 | 10 | 9 | 61 | 36.7 | 4.96
77 | 40 | 1000 | 64 | S/T | 0.76 | 10 | 9 | 65 | 36.7 | 5.53
77 | 40 | 1000 | 64 | ∆T | 18.5 | 10 | 9 | 68 | 36.6 | 5.96
77 | 40 | 1000 | 64 | LDB | 58.5 | 10 | 9 | 70 | 35 | 6.24
77 | 40 | 1000 | 64 | LWB | 55.2 | 10 | 9 | 72 | 33.4 | 6.25
77 | 40 | 1000 | 64 | kW | 1.2 | 10 | 9 | 75 | 31.1 | 5.6
80 | 40 | 1000 | 67 | MBh | 29.4 | 6 | 5 | 61 | 35 | 4.55
80 | 40 | 1000 | 67 | S/T | 0.711 | 6 | 5 | 65 | 35 | 5.15
80 | 40 | 1000 | 67 | ∆T | 19.4 | 6 | 5 | 68 | 35 | 5.4
80 | 40 | 1000 | 67 | LDB | 60.6 | 6 | 5 | 70 | 35 | 5.4
80 | 40 | 1000 | 67 | LWB | 57.8 | 6 | 5 | 72 | 33.4 | 5.4
80 | 40 | 1000 | 67 | kW | 1.36 | 6 | 5 | 75 | 31.1 | 5.4
84 | 40 | 1000 | 70 | MBh | 32.5 | -2 | -2 | 61 | 30 | 3.56
84 | 40 | 1000 | 70 | S/T | 0.668 | -2 | -2 | 65 | 30 | 4.23
84 | 40 | 1000 | 70 | ∆T | 20.1 | -2 | -2 | 68 | 30 | 4.73
84 | 40 | 1000 | 70 | LDB | 63.9 | -2 | -2 | 70 | 30 | 4.86
84 | 40 | 1000 | 70 | LWB | 60.4 | -2 | -2 | 72 | 30 | 4.86
84 | 40 | 1000 | 70 | kW | 1.53 | -2 | -2 | 75 | 30 | 4.86
86 | 40 | 1000 | 72 | MBh | 34.6 | -4 | -4 | 61 | 28.7 | 3.27
86 | 40 | 1000 | 72 | S/T | 0.659 | -4 | -4 | 65 | 28.7 | 3.96
86 | 40 | 1000 | 72 | ∆T | 21.1 | -4 | -4 | 68 | 28.7 | 4.48
86 | 40 | 1000 | 72 | LDB | 64.9 | -4 | -4 | 70 | 28.7 | 4.72
86 | 40 | 1000 | 72 | LWB | 62.2 | -4 | -4 | 72 | 28.7 | 4.72
86 | 40 | 1000 | 72 | kW | 1.64 | -4 | -4 | 75 | 28.7 | 4.72
90 | 40 | 1000 | 75 | MBh | 37.7
90 | 40 | 1000 | 75 | S/T | 0.61
90 | 40 | 1000 | 75 | ∆T | 21.3
90 | 40 | 1000 | 75 | LDB | 68.7
90 | 40 | 1000 | 75 | LWB | 65
90 | 40 | 1000 | 75 | kW | 1.81
68 | 50 | 1000 | 57 | MBh | 19.1
68 | 50 | 1000 | 57 | S/T | 0.806
68 | 50 | 1000 | 57 | ∆T | 14.3
68 | 50 | 1000 | 57 | LDB | 53.7
68 | 50 | 1000 | 57 | LWB | 49.8
68 | 50 | 1000 | 57 | kW | 0.88
72 | 50 | 1000 | 61 | MBh | 23.2
72 | 50 | 1000 | 61 | S/T | 0.78
72 | 50 | 1000 | 61 | ∆T | 16.8
72 | 50 | 1000 | 61 | LDB | 55.2
72 | 50 | 1000 | 61 | LWB | 52.8
72 | 50 | 1000 | 61 | kW | 1.09
77 | 50 | 1000 | 64 | MBh | 26.3
77 | 50 | 1000 | 64 | S/T | 0.76
77 | 50 | 1000 | 64 | ∆T | 18.5
77 | 50 | 1000 | 64 | LDB | 58.5
77 | 50 | 1000 | 64 | LWB | 55.2
77 | 50 | 1000 | 64 | kW | 1.26
80 | 50 | 1000 | 67 | MBh | 29.4
80 | 50 | 1000 | 67 | S/T | 0.711
80 | 50 | 1000 | 67 | ∆T | 19.4
80 | 50 | 1000 | 67 | LDB | 60.6
80 | 50 | 1000 | 67 | LWB | 57.8
80 | 50 | 1000 | 67 | kW | 1.43
84 | 50 | 1000 | 70 | MBh | 32.5
84 | 50 | 1000 | 70 | S/T | 0.668
84 | 50 | 1000 | 70 | ∆T | 20.1
84 | 50 | 1000 | 70 | LDB | 63.9
84 | 50 | 1000 | 70 | LWB | 60.4
84 | 50 | 1000 | 70 | kW | 1.61
86 | 50 | 1000 | 72 | MBh | 34.6
86 | 50 | 1000 | 72 | S/T | 0.659
86 | 50 | 1000 | 72 | ∆T | 21.1
86 | 50 | 1000 | 72 | LDB | 64.9
86 | 50 | 1000 | 72 | LWB | 62.2
86 | 50 | 1000 | 72 | kW | 1.72
90 | 50 | 1000 | 75 | MBh | 37.7
90 | 50 | 1000 | 75 | S/T | 0.61
90 | 50 | 1000 | 75 | ∆T | 21.3
90 | 50 | 1000 | 75 | LDB | 68.7
90 | 50 | 1000 | 75 | LWB | 65
90 | 50 | 1000 | 75 | kW | 1.9
68 | 54 | 1000 | 57 | MBh | 19.1
68 | 54 | 1000 | 57 | S/T | 0.806
68 | 54 | 1000 | 57 | ∆T | 14.3
68 | 54 | 1000 | 57 | LDB | 53.7
68 | 54 | 1000 | 57 | LWB | 49.8
68 | 54 | 1000 | 57 | kW | 0.9
72 | 54 | 1000 | 61 | MBh | 23.2
72 | 54 | 1000 | 61 | S/T | 0.78
72 | 54 | 1000 | 61 | ∆T | 16.8
72 | 54 | 1000 | 61 | LDB | 55.2
72 | 54 | 1000 | 61 | LWB | 52.8
72 | 54 | 1000 | 61 | kW | 1.11
77 | 54 | 1000 | 64 | MBh | 26.3
77 | 54 | 1000 | 64 | S/T | 0.76
77 | 54 | 1000 | 64 | ∆T | 18.5
77 | 54 | 1000 | 64 | LDB | 58.5
77 | 54 | 1000 | 64 | LWB | 55.2
77 | 54 | 1000 | 64 | kW | 1.28
80 | 54 | 1000 | 67 | MBh | 29.4
80 | 54 | 1000 | 67 | S/T | 0.711
80 | 54 | 1000 | 67 | ∆T | 19.4
80 | 54 | 1000 | 67 | LDB | 60.6
80 | 54 | 1000 | 67 | LWB | 57.8
80 | 54 | 1000 | 67 | kW | 1.46
84 | 54 | 1000 | 70 | MBh | 32.5
84 | 54 | 1000 | 70 | S/T | 0.668
84 | 54 | 1000 | 70 | ∆T | 20.1
84 | 54 | 1000 | 70 | LDB | 63.9
84 | 54 | 1000 | 70 | LWB | 60.4
84 | 54 | 1000 | 70 | kW | 1.64
86 | 54 | 1000 | 72 | MBh | 34.6
86 | 54 | 1000 | 72 | S/T | 0.659
86 | 54 | 1000 | 72 | ∆T | 21.1
86 | 54 | 1000 | 72 | LDB | 64.9
86 | 54 | 1000 | 72 | LWB | 62.2
86 | 54 | 1000 | 72 | kW | 1.76
90 | 54 | 1000 | 75 | MBh | 37.7
90 | 54 | 1000 | 75 | S/T | 0.61
90 | 54 | 1000 | 75 | ∆T | 21.3
90 | 54 | 1000 | 75 | LDB | 68.7
90 | 54 | 1000 | 75 | LWB | 65
90 | 54 | 1000 | 75 | kW | 1.94
68 | 58 | 1000 | 57 | MBh | 19.1
68 | 58 | 1000 | 57 | S/T | 0.806
68 | 58 | 1000 | 57 | ∆T | 14.3
68 | 58 | 1000 | 57 | LDB | 53.7
68 | 58 | 1000 | 57 | LWB | 49.8
68 | 58 | 1000 | 57 | kW | 0.92
72 | 58 | 1000 | 61 | MBh | 23.2
72 | 58 | 1000 | 61 | S/T | 0.78
72 | 58 | 1000 | 61 | ∆T | 16.8
72 | 58 | 1000 | 61 | LDB | 55.2
72 | 58 | 1000 | 61 | LWB | 52.8
72 | 58 | 1000 | 61 | kW | 1.14
77 | 58 | 1000 | 64 | MBh | 26.3
77 | 58 | 1000 | 64 | S/T | 0.76
77 | 58 | 1000 | 64 | ∆T | 18.5
77 | 58 | 1000 | 64 | LDB | 58.5
77 | 58 | 1000 | 64 | LWB | 55.2
77 | 58 | 1000 | 64 | kW | 1.31
80 | 58 | 1000 | 67 | MBh | 29.4
80 | 58 | 1000 | 67 | S/T | 0.711
80 | 58 | 1000 | 67 | ∆T | 19.4
80 | 58 | 1000 | 67 | LDB | 60.6
80 | 58 | 1000 | 67 | LWB | 57.8
80 | 58 | 1000 | 67 | kW | 1.49
84 | 58 | 1000 | 70 | MBh | 32.5
84 | 58 | 1000 | 70 | S/T | 0.668
84 | 58 | 1000 | 70 | ∆T | 20.1
84 | 58 | 1000 | 70 | LDB | 63.9
84 | 58 | 1000 | 70 | LWB | 60.4
84 | 58 | 1000 | 70 | kW | 1.67
86 | 58 | 1000 | 72 | MBh | 34.6
86 | 58 | 1000 | 72 | S/T | 0.659
86 | 58 | 1000 | 72 | ∆T | 21.1
86 | 58 | 1000 | 72 | LDB | 64.9
86 | 58 | 1000 | 72 | LWB | 62.2
86 | 58 | 1000 | 72 | kW | 1.8
90 | 58 | 1000 | 75 | MBh | 37.3
90 | 58 | 1000 | 75 | S/T | 0.609
90 | 58 | 1000 | 75 | ∆T | 21
90 | 58 | 1000 | 75 | LDB | 69
90 | 58 | 1000 | 75 | LWB | 65.1
90 | 58 | 1000 | 75 | kW | 1.95
68 | 62 | 1000 | 57 | MBh | 19.1
68 | 62 | 1000 | 57 | S/T | 0.806
68 | 62 | 1000 | 57 | ∆T | 14.3
68 | 62 | 1000 | 57 | LDB | 53.7
68 | 62 | 1000 | 57 | LWB | 49.8
68 | 62 | 1000 | 57 | kW | 0.94
72 | 62 | 1000 | 61 | MBh | 23.2
72 | 62 | 1000 | 61 | S/T | 0.78
72 | 62 | 1000 | 61 | ∆T | 16.8
72 | 62 | 1000 | 61 | LDB | 55.2
72 | 62 | 1000 | 61 | LWB | 52.8
72 | 62 | 1000 | 61 | kW | 1.16
77 | 62 | 1000 | 64 | MBh | 26.3
77 | 62 | 1000 | 64 | S/T | 0.76
77 | 62 | 1000 | 64 | ∆T | 18.5
77 | 62 | 1000 | 64 | LDB | 58.5
77 | 62 | 1000 | 64 | LWB | 55.2
77 | 62 | 1000 | 64 | kW | 1.34
80 | 62 | 1000 | 67 | MBh | 29.4
80 | 62 | 1000 | 67 | S/T | 0.711
80 | 62 | 1000 | 67 | ∆T | 19.4
80 | 62 | 1000 | 67 | LDB | 60.6
80 | 62 | 1000 | 67 | LWB | 57.8
80 | 62 | 1000 | 67 | kW | 1.52
84 | 62 | 1000 | 70 | MBh | 32.5
84 | 62 | 1000 | 70 | S/T | 0.668
84 | 62 | 1000 | 70 | ∆T | 20.1
84 | 62 | 1000 | 70 | LDB | 63.9
84 | 62 | 1000 | 70 | LWB | 60.4
84 | 62 | 1000 | 70 | kW | 1.71
86 | 62 | 1000 | 72 | MBh | 34.6
86 | 62 | 1000 | 72 | S/T | 0.659
86 | 62 | 1000 | 72 | ∆T | 21.1
86 | 62 | 1000 | 72 | LDB | 64.9
86 | 62 | 1000 | 72 | LWB | 62.2
86 | 62 | 1000 | 72 | kW | 1.84
90 | 62 | 1000 | 75 | MBh | 36.8
90 | 62 | 1000 | 75 | S/T | 0.609
90 | 62 | 1000 | 75 | ∆T | 20.7
90 | 62 | 1000 | 75 | LDB | 69.3
90 | 62 | 1000 | 75 | LWB | 65.3
90 | 62 | 1000 | 75 | kW | 1.99
68 | 66 | 1000 | 57 | MBh | 19.1
68 | 66 | 1000 | 57 | S/T | 0.806
68 | 66 | 1000 | 57 | ∆T | 14.3
68 | 66 | 1000 | 57 | LDB | 53.7
68 | 66 | 1000 | 57 | LWB | 49.8
68 | 66 | 1000 | 57 | kW | 0.96
72 | 66 | 1000 | 61 | MBh | 23.2
72 | 66 | 1000 | 61 | S/T | 0.78
72 | 66 | 1000 | 61 | ∆T | 16.8
72 | 66 | 1000 | 61 | LDB | 55.2
72 | 66 | 1000 | 61 | LWB | 52.8
72 | 66 | 1000 | 61 | kW | 1.19
77 | 66 | 1000 | 64 | MBh | 26.3
77 | 66 | 1000 | 64 | S/T | 0.76
77 | 66 | 1000 | 64 | ∆T | 18.5
77 | 66 | 1000 | 64 | LDB | 58.5
77 | 66 | 1000 | 64 | LWB | 55.2
77 | 66 | 1000 | 64 | kW | 1.37
80 | 66 | 1000 | 67 | MBh | 29.4
80 | 66 | 1000 | 67 | S/T | 0.711
80 | 66 | 1000 | 67 | ∆T | 19.4
80 | 66 | 1000 | 67 | LDB | 60.6
80 | 66 | 1000 | 67 | LWB | 57.8
80 | 66 | 1000 | 67 | kW | 1.56
84 | 66 | 1000 | 70 | MBh | 32.5
84 | 66 | 1000 | 70 | S/T | 0.668
84 | 66 | 1000 | 70 | ∆T | 20.1
84 | 66 | 1000 | 70 | LDB | 63.9
84 | 66 | 1000 | 70 | LWB | 60.4
84 | 66 | 1000 | 70 | kW | 1.81
86 | 66 | 1000 | 72 | MBh | 34.6
86 | 66 | 1000 | 72 | S/T | 0.659
86 | 66 | 1000 | 72 | ∆T | 21.1
86 | 66 | 1000 | 72 | LDB | 64.9
86 | 66 | 1000 | 72 | LWB | 62.2
86 | 66 | 1000 | 72 | kW | 1.98
90 | 66 | 1000 | 75 | MBh | 36.2
90 | 66 | 1000 | 75 | S/T | 0.61
90 | 66 | 1000 | 75 | ∆T | 20.5
90 | 66 | 1000 | 75 | LDB | 69.5
90 | 66 | 1000 | 75 | LWB | 65.5
90 | 66 | 1000 | 75 | kW | 2.1
68 | 70 | 1000 | 57 | MBh | 19.1
68 | 70 | 1000 | 57 | S/T | 0.806
68 | 70 | 1000 | 57 | ∆T | 14.3
68 | 70 | 1000 | 57 | LDB | 53.7
68 | 70 | 1000 | 57 | LWB | 49.8
68 | 70 | 1000 | 57 | kW | 0.98
72 | 70 | 1000 | 61 | MBh | 23.2
72 | 70 | 1000 | 61 | S/T | 0.78
72 | 70 | 1000 | 61 | ∆T | 16.8
72 | 70 | 1000 | 61 | LDB | 55.2
72 | 70 | 1000 | 61 | LWB | 52.8
72 | 70 | 1000 | 61 | kW | 1.21
77 | 70 | 1000 | 64 | MBh | 26.3
77 | 70 | 1000 | 64 | S/T | 0.76
77 | 70 | 1000 | 64 | ∆T | 18.5
77 | 70 | 1000 | 64 | LDB | 58.5
77 | 70 | 1000 | 64 | LWB | 55.2
77 | 70 | 1000 | 64 | kW | 1.44
80 | 70 | 1000 | 67 | MBh | 29.4
80 | 70 | 1000 | 67 | S/T | 0.711
80 | 70 | 1000 | 67 | ∆T | 19.4
80 | 70 | 1000 | 67 | LDB | 60.6
80 | 70 | 1000 | 67 | LWB | 57.8
80 | 70 | 1000 | 67 | kW | 1.69
84 | 70 | 1000 | 70 | MBh | 32.5
84 | 70 | 1000 | 70 | S/T | 0.668
84 | 70 | 1000 | 70 | ∆T | 20.1
84 | 70 | 1000 | 70 | LDB | 63.9
84 | 70 | 1000 | 70 | LWB | 60.4
84 | 70 | 1000 | 70 | kW | 1.96
86 | 70 | 1000 | 72 | MBh | 34.6
86 | 70 | 1000 | 72 | S/T | 0.659
86 | 70 | 1000 | 72 | ∆T | 21.1
86 | 70 | 1000 | 72 | LDB | 64.9
86 | 70 | 1000 | 72 | LWB | 62.2
86 | 70 | 1000 | 72 | kW | 2.15
90 | 70 | 1000 | 75 | MBh | 35.7
90 | 70 | 1000 | 75 | S/T | 0.608
90 | 70 | 1000 | 75 | ∆T | 20.1
90 | 70 | 1000 | 75 | LDB | 69.9
90 | 70 | 1000 | 75 | LWB | 65.6
90 | 70 | 1000 | 75 | kW | 2.21
68 | 72 | 1000 | 57 | MBh | 19.1
68 | 72 | 1000 | 57 | S/T | 0.806
68 | 72 | 1000 | 57 | ∆T | 14.3
68 | 72 | 1000 | 57 | LDB | 53.7
68 | 72 | 1000 | 57 | LWB | 49.8
68 | 72 | 1000 | 57 | kW | 0.99
72 | 72 | 1000 | 61 | MBh | 23.2
72 | 72 | 1000 | 61 | S/T | 0.78
72 | 72 | 1000 | 61 | ∆T | 16.8
72 | 72 | 1000 | 61 | LDB | 55.2
72 | 72 | 1000 | 61 | LWB | 52.8
72 | 72 | 1000 | 61 | kW | 1.25
77 | 72 | 1000 | 64 | MBh | 26.3
77 | 72 | 1000 | 64 | S/T | 0.76
77 | 72 | 1000 | 64 | ∆T | 18.5
77 | 72 | 1000 | 64 | LDB | 58.5
77 | 72 | 1000 | 64 | LWB | 55.2
77 | 72 | 1000 | 64 | kW | 1.49
80 | 72 | 1000 | 67 | MBh | 29.4
80 | 72 | 1000 | 67 | S/T | 0.711
80 | 72 | 1000 | 67 | ∆T | 19.4
80 | 72 | 1000 | 67 | LDB | 60.6
80 | 72 | 1000 | 67 | LWB | 57.8
80 | 72 | 1000 | 67 | kW | 1.75
84 | 72 | 1000 | 70 | MBh | 32.5
84 | 72 | 1000 | 70 | S/T | 0.668
84 | 72 | 1000 | 70 | ∆T | 20.1
84 | 72 | 1000 | 70 | LDB | 63.9
84 | 72 | 1000 | 70 | LWB | 60.4
84 | 72 | 1000 | 70 | kW | 2.03
86 | 72 | 1000 | 72 | MBh | 34.6
86 | 72 | 1000 | 72 | S/T | 0.659
86 | 72 | 1000 | 72 | ∆T | 21.1
86 | 72 | 1000 | 72 | LDB | 64.9
86 | 72 | 1000 | 72 | LWB | 62.2
86 | 72 | 1000 | 72 | kW | 2.23
90 | 72 | 1000 | 75 | MBh | 35.4
90 | 72 | 1000 | 75 | S/T | 0.61
90 | 72 | 1000 | 75 | ∆T | 20
90 | 72 | 1000 | 75 | LDB | 70
90 | 72 | 1000 | 75 | LWB | 65.7
90 | 72 | 1000 | 75 | kW | 2.27
68 | 75 | 1000 | 57 | MBh | 19.1
68 | 75 | 1000 | 57 | S/T | 0.806
68 | 75 | 1000 | 57 | ∆T | 14.3
68 | 75 | 1000 | 57 | LDB | 53.7
68 | 75 | 1000 | 57 | LWB | 49.8
68 | 75 | 1000 | 57 | kW | 1.02
72 | 75 | 1000 | 61 | MBh | 23.2
72 | 75 | 1000 | 61 | S/T | 0.78
72 | 75 | 1000 | 61 | ∆T | 16.8
72 | 75 | 1000 | 61 | LDB | 55.2
72 | 75 | 1000 | 61 | LWB | 52.8
72 | 75 | 1000 | 61 | kW | 1.32
77 | 75 | 1000 | 64 | MBh | 26.3
77 | 75 | 1000 | 64 | S/T | 0.76
77 | 75 | 1000 | 64 | ∆T | 18.5
77 | 75 | 1000 | 64 | LDB | 58.5
77 | 75 | 1000 | 64 | LWB | 55.2
77 | 75 | 1000 | 64 | kW | 1.58
80 | 75 | 1000 | 67 | MBh | 29.4
80 | 75 | 1000 | 67 | S/T | 0.711
80 | 75 | 1000 | 67 | ∆T | 19.4
80 | 75 | 1000 | 67 | LDB | 60.6
80 | 75 | 1000 | 67 | LWB | 57.8
80 | 75 | 1000 | 67 | kW | 1.85
84 | 75 | 1000 | 70 | MBh | 32.5
84 | 75 | 1000 | 70 | S/T | 0.668
84 | 75 | 1000 | 70 | ∆T | 20.1
84 | 75 | 1000 | 70 | LDB | 63.9
84 | 75 | 1000 | 70 | LWB | 60.4
84 | 75 | 1000 | 70 | kW | 2.15
86 | 75 | 1000 | 72 | MBh | 34.4
86 | 75 | 1000 | 72 | S/T | 0.66
86 | 75 | 1000 | 72 | ∆T | 21
86 | 75 | 1000 | 72 | LDB | 65
86 | 75 | 1000 | 72 | LWB | 62.3
86 | 75 | 1000 | 72 | kW | 2.34
90 | 75 | 1000 | 75 | MBh | 35
90 | 75 | 1000 | 75 | S/T | 0.609
90 | 75 | 1000 | 75 | ∆T | 19.7
90 | 75 | 1000 | 75 | LDB | 70.3
90 | 75 | 1000 | 75 | LWB | 65.8
90 | 75 | 1000 | 75 | kW | 2.35
68 | 79 | 1000 | 57 | MBh | 19.1
68 | 79 | 1000 | 57 | S/T | 0.806
68 | 79 | 1000 | 57 | ∆T | 14.3
68 | 79 | 1000 | 57 | LDB | 53.7
68 | 79 | 1000 | 57 | LWB | 49.8
68 | 79 | 1000 | 57 | kW | 1.1
72 | 79 | 1000 | 61 | MBh | 23.2
72 | 79 | 1000 | 61 | S/T | 0.78
72 | 79 | 1000 | 61 | ∆T | 16.8
72 | 79 | 1000 | 61 | LDB | 55.2
72 | 79 | 1000 | 61 | LWB | 52.8
72 | 79 | 1000 | 61 | kW | 1.43
77 | 79 | 1000 | 64 | MBh | 26.3
77 | 79 | 1000 | 64 | S/T | 0.76
77 | 79 | 1000 | 64 | ∆T | 18.5
77 | 79 | 1000 | 64 | LDB | 58.5
77 | 79 | 1000 | 64 | LWB | 55.2
77 | 79 | 1000 | 64 | kW | 1.7
80 | 79 | 1000 | 67 | MBh | 29.4
80 | 79 | 1000 | 67 | S/T | 0.711
80 | 79 | 1000 | 67 | ∆T | 19.4
80 | 79 | 1000 | 67 | LDB | 60.6
80 | 79 | 1000 | 67 | LWB | 57.8
80 | 79 | 1000 | 67 | kW | 2
84 | 79 | 1000 | 70 | MBh | 32.5
84 | 79 | 1000 | 70 | S/T | 0.668
84 | 79 | 1000 | 70 | ∆T | 20.1
84 | 79 | 1000 | 70 | LDB | 63.9
84 | 79 | 1000 | 70 | LWB | 60.4
84 | 79 | 1000 | 70 | kW | 2.32
86 | 79 | 1000 | 72 | MBh | 33.8
86 | 79 | 1000 | 72 | S/T | 0.66
86 | 79 | 1000 | 72 | ∆T | 20.6
86 | 79 | 1000 | 72 | LDB | 65.4
86 | 79 | 1000 | 72 | LWB | 62.5
86 | 79 | 1000 | 72 | kW | 2.45
90 | 79 | 1000 | 75 | MBh | 34.4
90 | 79 | 1000 | 75 | S/T | 0.61
90 | 79 | 1000 | 75 | ∆T | 19.4
90 | 79 | 1000 | 75 | LDB | 70.6
90 | 79 | 1000 | 75 | LWB | 66
90 | 79 | 1000 | 75 | kW | 2.47
68 | 83 | 1000 | 57 | MBh | 19.1
68 | 83 | 1000 | 57 | S/T | 0.806
68 | 83 | 1000 | 57 | ∆T | 14.3
68 | 83 | 1000 | 57 | LDB | 53.7
68 | 83 | 1000 | 57 | LWB | 49.8
68 | 83 | 1000 | 57 | kW | 1.18
72 | 83 | 1000 | 61 | MBh | 23.2
72 | 83 | 1000 | 61 | S/T | 0.78
72 | 83 | 1000 | 61 | ∆T | 16.8
72 | 83 | 1000 | 61 | LDB | 55.2
72 | 83 | 1000 | 61 | LWB | 52.8
72 | 83 | 1000 | 61 | kW | 1.53
77 | 83 | 1000 | 64 | MBh | 26.3
77 | 83 | 1000 | 64 | S/T | 0.76
77 | 83 | 1000 | 64 | ∆T | 18.5
77 | 83 | 1000 | 64 | LDB | 58.5
77 | 83 | 1000 | 64 | LWB | 55.2
77 | 83 | 1000 | 64 | kW | 1.83
80 | 83 | 1000 | 67 | MBh | 29.4
80 | 83 | 1000 | 67 | S/T | 0.711
80 | 83 | 1000 | 67 | ∆T | 19.4
80 | 83 | 1000 | 67 | LDB | 60.6
80 | 83 | 1000 | 67 | LWB | 57.8
80 | 83 | 1000 | 67 | kW | 2.15
84 | 83 | 1000 | 70 | MBh | 32.5
84 | 83 | 1000 | 70 | S/T | 0.668
84 | 83 | 1000 | 70 | ∆T | 20.1
84 | 83 | 1000 | 70 | LDB | 63.9
84 | 83 | 1000 | 70 | LWB | 60.4
84 | 83 | 1000 | 70 | kW | 2.5
86 | 83 | 1000 | 72 | MBh | 33.2
86 | 83 | 1000 | 72 | S/T | 0.66
86 | 83 | 1000 | 72 | ∆T | 20.3
86 | 83 | 1000 | 72 | LDB | 65.7
86 | 83 | 1000 | 72 | LWB | 62.7
86 | 83 | 1000 | 72 | kW | 2.56
90 | 83 | 1000 | 75 | MBh | 33.9
90 | 83 | 1000 | 75 | S/T | 0.611
90 | 83 | 1000 | 75 | ∆T | 19.2
90 | 83 | 1000 | 75 | LDB | 70.8
90 | 83 | 1000 | 75 | LWB | 66.1
90 | 83 | 1000 | 75 | kW | 2.58
68 | 87 | 1000 | 57 | MBh | 19.1
68 | 87 | 1000 | 57 | S/T | 0.806
68 | 87 | 1000 | 57 | ∆T | 14.3
68 | 87 | 1000 | 57 | LDB | 53.7
68 | 87 | 1000 | 57 | LWB | 49.8
68 | 87 | 1000 | 57 | kW | 1.26
72 | 87 | 1000 | 61 | MBh | 23.2
72 | 87 | 1000 | 61 | S/T | 0.78
72 | 87 | 1000 | 61 | ∆T | 16.8
72 | 87 | 1000 | 61 | LDB | 55.2
72 | 87 | 1000 | 61 | LWB | 52.8
72 | 87 | 1000 | 61 | kW | 1.64
77 | 87 | 1000 | 64 | MBh | 26.3
77 | 87 | 1000 | 64 | S/T | 0.76
77 | 87 | 1000 | 64 | ∆T | 18.5
77 | 87 | 1000 | 64 | LDB | 58.5
77 | 87 | 1000 | 64 | LWB | 55.2
77 | 87 | 1000 | 64 | kW | 1.96
80 | 87 | 1000 | 67 | MBh | 29.4
80 | 87 | 1000 | 67 | S/T | 0.711
80 | 87 | 1000 | 67 | ∆T | 19.4
80 | 87 | 1000 | 67 | LDB | 60.6
80 | 87 | 1000 | 67 | LWB | 57.8
80 | 87 | 1000 | 67 | kW | 2.32
84 | 87 | 1000 | 70 | MBh | 32.3
84 | 87 | 1000 | 70 | S/T | 0.669
84 | 87 | 1000 | 70 | ∆T | 20
84 | 87 | 1000 | 70 | LDB | 64
84 | 87 | 1000 | 70 | LWB | 60.5
84 | 87 | 1000 | 70 | kW | 2.66
86 | 87 | 1000 | 72 | MBh | 32.7
86 | 87 | 1000 | 72 | S/T | 0.661
86 | 87 | 1000 | 72 | ∆T | 20
86 | 87 | 1000 | 72 | LDB | 66
86 | 87 | 1000 | 72 | LWB | 62.8
86 | 87 | 1000 | 72 | kW | 2.68
90 | 87 | 1000 | 75 | MBh | 33.3
90 | 87 | 1000 | 75 | S/T | 0.61
90 | 87 | 1000 | 75 | ∆T | 18.8
90 | 87 | 1000 | 75 | LDB | 71.2
90 | 87 | 1000 | 75 | LWB | 66.3
90 | 87 | 1000 | 75 | kW | 2.69
68 | 91 | 1000 | 57 | MBh | 19.1
68 | 91 | 1000 | 57 | S/T | 0.806
68 | 91 | 1000 | 57 | ∆T | 14.3
68 | 91 | 1000 | 57 | LDB | 53.7
68 | 91 | 1000 | 57 | LWB | 49.8
68 | 91 | 1000 | 57 | kW | 1.35
72 | 91 | 1000 | 61 | MBh | 23.2
72 | 91 | 1000 | 61 | S/T | 0.78
72 | 91 | 1000 | 61 | ∆T | 16.8
72 | 91 | 1000 | 61 | LDB | 55.2
72 | 91 | 1000 | 61 | LWB | 52.8
72 | 91 | 1000 | 61 | kW | 1.76
77 | 91 | 1000 | 64 | MBh | 26.3
77 | 91 | 1000 | 64 | S/T | 0.76
77 | 91 | 1000 | 64 | ∆T | 18.5
77 | 91 | 1000 | 64 | LDB | 58.5
77 | 91 | 1000 | 64 | LWB | 55.2
77 | 91 | 1000 | 64 | kW | 2.11
80 | 91 | 1000 | 67 | MBh | 29.4
80 | 91 | 1000 | 67 | S/T | 0.711
80 | 91 | 1000 | 67 | ∆T | 19.4
80 | 91 | 1000 | 67 | LDB | 60.6
80 | 91 | 1000 | 67 | LWB | 57.8
80 | 91 | 1000 | 67 | kW | 2.49
84 | 91 | 1000 | 70 | MBh | 31.7
84 | 91 | 1000 | 70 | S/T | 0.669
84 | 91 | 1000 | 70 | ∆T | 19.6
84 | 91 | 1000 | 70 | LDB | 64.4
84 | 91 | 1000 | 70 | LWB | 60.7
84 | 91 | 1000 | 70 | kW | 2.78
86 | 91 | 1000 | 72 | MBh | 32.1
86 | 91 | 1000 | 72 | S/T | 0.66
86 | 91 | 1000 | 72 | ∆T | 19.6
86 | 91 | 1000 | 72 | LDB | 66.4
86 | 91 | 1000 | 72 | LWB | 63
86 | 91 | 1000 | 72 | kW | 2.79
90 | 91 | 1000 | 75 | MBh | 32.8
90 | 91 | 1000 | 75 | S/T | 0.61
90 | 91 | 1000 | 75 | ∆T | 18.5
90 | 91 | 1000 | 75 | LDB | 71.5
90 | 91 | 1000 | 75 | LWB | 66.4
90 | 91 | 1000 | 75 | kW | 2.81
68 | 93 | 1000 | 57 | MBh | 19.1
68 | 93 | 1000 | 57 | S/T | 0.806
68 | 93 | 1000 | 57 | ∆T | 14.3
68 | 93 | 1000 | 57 | LDB | 53.7
68 | 93 | 1000 | 57 | LWB | 49.8
68 | 93 | 1000 | 57 | kW | 1.4
72 | 93 | 1000 | 61 | MBh | 23.2
72 | 93 | 1000 | 61 | S/T | 0.78
72 | 93 | 1000 | 61 | ∆T | 16.8
72 | 93 | 1000 | 61 | LDB | 55.2
72 | 93 | 1000 | 61 | LWB | 52.8
72 | 93 | 1000 | 61 | kW | 1.82
77 | 93 | 1000 | 64 | MBh | 26.3
77 | 93 | 1000 | 64 | S/T | 0.76
77 | 93 | 1000 | 64 | ∆T | 18.5
77 | 93 | 1000 | 64 | LDB | 58.5
77 | 93 | 1000 | 64 | LWB | 55.2
77 | 93 | 1000 | 64 | kW | 2.19
80 | 93 | 1000 | 67 | MBh | 29.4
80 | 93 | 1000 | 67 | S/T | 0.711
80 | 93 | 1000 | 67 | ∆T | 19.4
80 | 93 | 1000 | 67 | LDB | 60.6
80 | 93 | 1000 | 67 | LWB | 57.8
80 | 93 | 1000 | 67 | kW | 2.58
84 | 93 | 1000 | 70 | MBh | 31.5
84 | 93 | 1000 | 70 | S/T | 0.667
84 | 93 | 1000 | 70 | ∆T | 19.4
84 | 93 | 1000 | 70 | LDB | 64.6
84 | 93 | 1000 | 70 | LWB | 60.7
84 | 93 | 1000 | 70 | kW | 2.83
86 | 93 | 1000 | 72 | MBh | 31.9
86 | 93 | 1000 | 72 | S/T | 0.658
86 | 93 | 1000 | 72 | ∆T | 19.4
86 | 93 | 1000 | 72 | LDB | 66.6
86 | 93 | 1000 | 72 | LWB | 63.1
86 | 93 | 1000 | 72 | kW | 2.85
90 | 93 | 1000 | 75 | MBh | 32.5
90 | 93 | 1000 | 75 | S/T | 0.609
90 | 93 | 1000 | 75 | ∆T | 18.3
90 | 93 | 1000 | 75 | LDB | 71.7
90 | 93 | 1000 | 75 | LWB | 66.5
90 | 93 | 1000 | 75 | kW | 2.87
68 | 95 | 1000 | 57 | MBh | 19.1
68 | 95 | 1000 | 57 | S/T | 0.806
68 | 95 | 1000 | 57 | ∆T | 14.3
68 | 95 | 1000 | 57 | LDB | 53.7
68 | 95 | 1000 | 57 | LWB | 49.8
68 | 95 | 1000 | 57 | kW | 1.44
72 | 95 | 1000 | 61 | MBh | 23.2
72 | 95 | 1000 | 61 | S/T | 0.78
72 | 95 | 1000 | 61 | ∆T | 16.8
72 | 95 | 1000 | 61 | LDB | 55.2
72 | 95 | 1000 | 61 | LWB | 52.8
72 | 95 | 1000 | 61 | kW | 1.89
77 | 95 | 1000 | 64 | MBh | 26.3
77 | 95 | 1000 | 64 | S/T | 0.76
77 | 95 | 1000 | 64 | ∆T | 18.5
77 | 95 | 1000 | 64 | LDB | 58.5
77 | 95 | 1000 | 64 | LWB | 55.2
77 | 95 | 1000 | 64 | kW | 2.26
80 | 95 | 1000 | 67 | MBh | 29.4
80 | 95 | 1000 | 67 | S/T | 0.711
80 | 95 | 1000 | 67 | ∆T | 19.4
80 | 95 | 1000 | 67 | LDB | 60.6
80 | 95 | 1000 | 67 | LWB | 57.8
80 | 95 | 1000 | 67 | kW | 2.67
84 | 95 | 1000 | 70 | MBh | 31.2
84 | 95 | 1000 | 70 | S/T | 0.667
84 | 95 | 1000 | 70 | ∆T | 19.3
84 | 95 | 1000 | 70 | LDB | 64.7
84 | 95 | 1000 | 70 | LWB | 60.8
84 | 95 | 1000 | 70 | kW | 2.89
86 | 95 | 1000 | 72 | MBh | 31.6
86 | 95 | 1000 | 72 | S/T | 0.658
86 | 95 | 1000 | 72 | ∆T | 19.3
86 | 95 | 1000 | 72 | LDB | 66.7
86 | 95 | 1000 | 72 | LWB | 63.2
86 | 95 | 1000 | 72 | kW | 2.9
90 | 95 | 1000 | 75 | MBh | 32.2
90 | 95 | 1000 | 75 | S/T | 0.609
90 | 95 | 1000 | 75 | ∆T | 18.1
90 | 95 | 1000 | 75 | LDB | 71.9
90 | 95 | 1000 | 75 | LWB | 66.6
90 | 95 | 1000 | 75 | kW | 2.92
68 | 99 | 1000 | 57 | MBh | 19.1
68 | 99 | 1000 | 57 | S/T | 0.806
68 | 99 | 1000 | 57 | ∆T | 14.3
68 | 99 | 1000 | 57 | LDB | 53.7
68 | 99 | 1000 | 57 | LWB | 49.8
68 | 99 | 1000 | 57 | kW | 1.62
72 | 99 | 1000 | 61 | MBh | 23.2
72 | 99 | 1000 | 61 | S/T | 0.78
72 | 99 | 1000 | 61 | ∆T | 16.8
72 | 99 | 1000 | 61 | LDB | 55.2
72 | 99 | 1000 | 61 | LWB | 52.8
72 | 99 | 1000 | 61 | kW | 2.12
77 | 99 | 1000 | 64 | MBh | 26.3
77 | 99 | 1000 | 64 | S/T | 0.76
77 | 99 | 1000 | 64 | ∆T | 18.5
77 | 99 | 1000 | 64 | LDB | 58.5
77 | 99 | 1000 | 64 | LWB | 55.2
77 | 99 | 1000 | 64 | kW | 2.54
80 | 99 | 1000 | 67 | MBh | 29.4
80 | 99 | 1000 | 67 | S/T | 0.711
80 | 99 | 1000 | 67 | ∆T | 19.4
80 | 99 | 1000 | 67 | LDB | 60.6
80 | 99 | 1000 | 67 | LWB | 57.8
80 | 99 | 1000 | 67 | kW | 3
84 | 99 | 1000 | 70 | MBh | 30.6
84 | 99 | 1000 | 70 | S/T | 0.673
84 | 99 | 1000 | 70 | ∆T | 19.1
84 | 99 | 1000 | 70 | LDB | 64.9
84 | 99 | 1000 | 70 | LWB | 61
84 | 99 | 1000 | 70 | kW | 3.14
86 | 99 | 1000 | 72 | MBh | 31
86 | 99 | 1000 | 72 | S/T | 0.665
86 | 99 | 1000 | 72 | ∆T | 19.1
86 | 99 | 1000 | 72 | LDB | 66.9
86 | 99 | 1000 | 72 | LWB | 63.3
86 | 99 | 1000 | 72 | kW | 3.16
90 | 99 | 1000 | 75 | MBh | 31.7
90 | 99 | 1000 | 75 | S/T | 0.612
90 | 99 | 1000 | 75 | ∆T | 18
90 | 99 | 1000 | 75 | LDB | 72
90 | 99 | 1000 | 75 | LWB | 66.8
90 | 99 | 1000 | 75 | kW | 3.18
68 | 103 | 1000 | 57 | MBh | 19.1
68 | 103 | 1000 | 57 | S/T | 0.806
68 | 103 | 1000 | 57 | ∆T | 14.3
68 | 103 | 1000 | 57 | LDB | 53.7
68 | 103 | 1000 | 57 | LWB | 49.8
68 | 103 | 1000 | 57 | kW | 1.8
72 | 103 | 1000 | 61 | MBh | 23.2
72 | 103 | 1000 | 61 | S/T | 0.78
72 | 103 | 1000 | 61 | ∆T | 16.8
72 | 103 | 1000 | 61 | LDB | 55.2
72 | 103 | 1000 | 61 | LWB | 52.8
72 | 103 | 1000 | 61 | kW | 2.36
77 | 103 | 1000 | 64 | MBh | 26.3
77 | 103 | 1000 | 64 | S/T | 0.76
77 | 103 | 1000 | 64 | ∆T | 18.5
77 | 103 | 1000 | 64 | LDB | 58.5
77 | 103 | 1000 | 64 | LWB | 55.2
77 | 103 | 1000 | 64 | kW | 2.84
80 | 103 | 1000 | 67 | MBh | 29.4
80 | 103 | 1000 | 67 | S/T | 0.711
80 | 103 | 1000 | 67 | ∆T | 19.4
80 | 103 | 1000 | 67 | LDB | 60.6
80 | 103 | 1000 | 67 | LWB | 57.8
80 | 103 | 1000 | 67 | kW | 3.36
84 | 103 | 1000 | 70 | MBh | 30.1
84 | 103 | 1000 | 70 | S/T | 0.671
84 | 103 | 1000 | 70 | ∆T | 18.7
84 | 103 | 1000 | 70 | LDB | 65.3
84 | 103 | 1000 | 70 | LWB | 61.2
84 | 103 | 1000 | 70 | kW | 3.4
86 | 103 | 1000 | 72 | MBh | 30.5
86 | 103 | 1000 | 72 | S/T | 0.662
86 | 103 | 1000 | 72 | ∆T | 18.7
86 | 103 | 1000 | 72 | LDB | 67.3
86 | 103 | 1000 | 72 | LWB | 63.5
86 | 103 | 1000 | 72 | kW | 3.41
90 | 103 | 1000 | 75 | MBh | 31.1
90 | 103 | 1000 | 75 | S/T | 0.614
90 | 103 | 1000 | 75 | ∆T | 17.7
90 | 103 | 1000 | 75 | LDB | 72.3
90 | 103 | 1000 | 75 | LWB | 66.9
90 | 103 | 1000 | 75 | kW | 3.44
68 | 106 | 1000 | 57 | MBh | 19.1
68 | 106 | 1000 | 57 | S/T | 0.806
68 | 106 | 1000 | 57 | ∆T | 14.3
68 | 106 | 1000 | 57 | LDB | 53.7
68 | 106 | 1000 | 57 | LWB | 49.8
68 | 106 | 1000 | 57 | kW | 1.94
72 | 106 | 1000 | 61 | MBh | 23.2
72 | 106 | 1000 | 61 | S/T | 0.78
72 | 106 | 1000 | 61 | ∆T | 16.8
72 | 106 | 1000 | 61 | LDB | 55.2
72 | 106 | 1000 | 61 | LWB | 52.8
72 | 106 | 1000 | 61 | kW | 2.56
77 | 106 | 1000 | 64 | MBh | 26.3
77 | 106 | 1000 | 64 | S/T | 0.76
77 | 106 | 1000 | 64 | ∆T | 18.5
77 | 106 | 1000 | 64 | LDB | 58.5
77 | 106 | 1000 | 64 | LWB | 55.2
77 | 106 | 1000 | 64 | kW | 3.07
80 | 106 | 1000 | 67 | MBh | 29.1
80 | 106 | 1000 | 67 | S/T | 0.715
80 | 106 | 1000 | 67 | ∆T | 19.3
80 | 106 | 1000 | 67 | LDB | 60.7
80 | 106 | 1000 | 67 | LWB | 57.9
80 | 106 | 1000 | 67 | kW | 3.56
84 | 106 | 1000 | 70 | MBh | 29.7
84 | 106 | 1000 | 70 | S/T | 0.67
84 | 106 | 1000 | 70 | ∆T | 18.4
84 | 106 | 1000 | 70 | LDB | 65.6
84 | 106 | 1000 | 70 | LWB | 61.3
84 | 106 | 1000 | 70 | kW | 3.59
86 | 106 | 1000 | 72 | MBh | 30.1
86 | 106 | 1000 | 72 | S/T | 0.661
86 | 106 | 1000 | 72 | ∆T | 18.4
86 | 106 | 1000 | 72 | LDB | 67.6
86 | 106 | 1000 | 72 | LWB | 63.6
86 | 106 | 1000 | 72 | kW | 3.61
90 | 106 | 1000 | 75 | MBh | 30.7
90 | 106 | 1000 | 75 | S/T | 0.612
90 | 106 | 1000 | 75 | ∆T | 17.4
90 | 106 | 1000 | 75 | LDB | 72.6
90 | 106 | 1000 | 75 | LWB | 67
90 | 106 | 1000 | 75 | kW | 3.63
68 | 110 | 1000 | 57 | MBh | 19.1
68 | 110 | 1000 | 57 | S/T | 0.806
68 | 110 | 1000 | 57 | ∆T | 14.3
68 | 110 | 1000 | 57 | LDB | 53.7
68 | 110 | 1000 | 57 | LWB | 49.8
68 | 110 | 1000 | 57 | kW | 2.15
72 | 110 | 1000 | 61 | MBh | 23.2
72 | 110 | 1000 | 61 | S/T | 0.78
72 | 110 | 1000 | 61 | ∆T | 16.8
72 | 110 | 1000 | 61 | LDB | 55.2
72 | 110 | 1000 | 61 | LWB | 52.8
72 | 110 | 1000 | 61 | kW | 2.83
77 | 110 | 1000 | 64 | MBh | 26.3
77 | 110 | 1000 | 64 | S/T | 0.76
77 | 110 | 1000 | 64 | ∆T | 18.5
77 | 110 | 1000 | 64 | LDB | 58.5
77 | 110 | 1000 | 64 | LWB | 55.2
77 | 110 | 1000 | 64 | kW | 3.41
80 | 110 | 1000 | 67 | MBh | 28.5
80 | 110 | 1000 | 67 | S/T | 0.716
80 | 110 | 1000 | 67 | ∆T | 18.9
80 | 110 | 1000 | 67 | LDB | 61.1
80 | 110 | 1000 | 67 | LWB | 58.1
80 | 110 | 1000 | 67 | kW | 3.82
84 | 110 | 1000 | 70 | MBh | 29.1
84 | 110 | 1000 | 70 | S/T | 0.67
84 | 110 | 1000 | 70 | ∆T | 18.1
84 | 110 | 1000 | 70 | LDB | 65.9
84 | 110 | 1000 | 70 | LWB | 61.5
84 | 110 | 1000 | 70 | kW | 3.85
86 | 110 | 1000 | 72 | MBh | 29.5
86 | 110 | 1000 | 72 | S/T | 0.661
86 | 110 | 1000 | 72 | ∆T | 18.1
86 | 110 | 1000 | 72 | LDB | 67.9
86 | 110 | 1000 | 72 | LWB | 63.8
86 | 110 | 1000 | 72 | kW | 3.86
90 | 110 | 1000 | 75 | MBh | 29.5
90 | 110 | 1000 | 75 | S/T | 0.614
90 | 110 | 1000 | 75 | ∆T | 16.8
90 | 110 | 1000 | 75 | LDB | 73.2
90 | 110 | 1000 | 75 | LWB | 67.4
90 | 110 | 1000 | 75 | kW | 3.86
68 | 115 | 1000 | 57 | MBh | 19.1
68 | 115 | 1000 | 57 | S/T | 0.806
68 | 115 | 1000 | 57 | ∆T | 14.3
68 | 115 | 1000 | 57 | LDB | 53.7
68 | 115 | 1000 | 57 | LWB | 49.8
68 | 115 | 1000 | 57 | kW | 2.42
72 | 115 | 1000 | 61 | MBh | 23.2
72 | 115 | 1000 | 61 | S/T | 0.78
72 | 115 | 1000 | 61 | ∆T | 16.8
72 | 115 | 1000 | 61 | LDB | 55.2
72 | 115 | 1000 | 61 | LWB | 52.8
72 | 115 | 1000 | 61 | kW | 3.2
77 | 115 | 1000 | 64 | MBh | 26.3
77 | 115 | 1000 | 64 | S/T | 0.76
77 | 115 | 1000 | 64 | ∆T | 18.5
77 | 115 | 1000 | 64 | LDB | 58.5
77 | 115 | 1000 | 64 | LWB | 55.2
77 | 115 | 1000 | 64 | kW | 3.86
80 | 115 | 1000 | 67 | MBh | 27.5
80 | 115 | 1000 | 67 | S/T | 0.716
80 | 115 | 1000 | 67 | ∆T | 18.2
80 | 115 | 1000 | 67 | LDB | 61.8
80 | 115 | 1000 | 67 | LWB | 58.4
80 | 115 | 1000 | 67 | kW | 4.12
84 | 115 | 1000 | 70 | MBh | 27.5
84 | 115 | 1000 | 70 | S/T | 0.673
84 | 115 | 1000 | 70 | ∆T | 17.1
84 | 115 | 1000 | 70 | LDB | 66.9
84 | 115 | 1000 | 70 | LWB | 62
84 | 115 | 1000 | 70 | kW | 4.12
86 | 115 | 1000 | 72 | MBh | 27.5
86 | 115 | 1000 | 72 | S/T | 0.665
86 | 115 | 1000 | 72 | ∆T | 16.9
86 | 115 | 1000 | 72 | LDB | 69.1
86 | 115 | 1000 | 72 | LWB | 64.4
86 | 115 | 1000 | 72 | kW | 4.12
90 | 115 | 1000 | 75 | MBh | 27.5
90 | 115 | 1000 | 75 | S/T | 0.615
90 | 115 | 1000 | 75 | ∆T | 15.6
90 | 115 | 1000 | 75 | LDB | 74.4
90 | 115 | 1000 | 75 | LWB | 67.9
90 | 115 | 1000 | 75 | kW | 4.12
68 | 118 | 1000 | 57 | MBh | 19.1
68 | 118 | 1000 | 57 | S/T | 0.806
68 | 118 | 1000 | 57 | ∆T | 14.3
68 | 118 | 1000 | 57 | LDB | 53.7
68 | 118 | 1000 | 57 | LWB | 49.8
68 | 118 | 1000 | 57 | kW | 2.6
72 | 118 | 1000 | 61 | MBh | 23.2
72 | 118 | 1000 | 61 | S/T | 0.78
72 | 118 | 1000 | 61 | ∆T | 16.8
72 | 118 | 1000 | 61 | LDB | 55.2
72 | 118 | 1000 | 61 | LWB | 52.8
72 | 118 | 1000 | 61 | kW | 3.44
77 | 118 | 1000 | 64 | MBh | 24.2
77 | 118 | 1000 | 64 | S/T | 0.764
77 | 118 | 1000 | 64 | ∆T | 17.1
77 | 118 | 1000 | 64 | LDB | 59.9
77 | 118 | 1000 | 64 | LWB | 56
77 | 118 | 1000 | 64 | kW | 3.67
80 | 118 | 1000 | 67 | MBh | 24.2
80 | 118 | 1000 | 67 | S/T | 0.715
80 | 118 | 1000 | 67 | ∆T | 16
80 | 118 | 1000 | 67 | LDB | 64
80 | 118 | 1000 | 67 | LWB | 59.5
80 | 118 | 1000 | 67 | kW | 3.67
84 | 118 | 1000 | 70 | MBh | 24.2
84 | 118 | 1000 | 70 | S/T | 0.674
84 | 118 | 1000 | 70 | ∆T | 15.1
84 | 118 | 1000 | 70 | LDB | 68.9
84 | 118 | 1000 | 70 | LWB | 63.1
84 | 118 | 1000 | 70 | kW | 3.67
86 | 118 | 1000 | 72 | MBh | 24.2
86 | 118 | 1000 | 72 | S/T | 0.665
86 | 118 | 1000 | 72 | ∆T | 14.9
86 | 118 | 1000 | 72 | LDB | 71.1
86 | 118 | 1000 | 72 | LWB | 65.4
86 | 118 | 1000 | 72 | kW | 3.67
90 | 118 | 1000 | 75 | MBh | 24.2
90 | 118 | 1000 | 75 | S/T | 0.616
90 | 118 | 1000 | 75 | ∆T | 13.8
90 | 118 | 1000 | 75 | LDB | 76.2
90 | 118 | 1000 | 75 | LWB | 68.9
90 | 118 | 1000 | 75 | kW | 3.67
68 | 122 | 1000 | 57 | MBh | 19.1
68 | 122 | 1000 | 57 | S/T | 0.806
68 | 122 | 1000 | 57 | ∆T | 14.3
68 | 122 | 1000 | 57 | LDB | 53.7
68 | 122 | 1000 | 57 | LWB | 49.8
68 | 122 | 1000 | 57 | kW | 2.85
72 | 122 | 1000 | 61 | MBh | 19.2
72 | 122 | 1000 | 61 | S/T | 0.786
72 | 122 | 1000 | 61 | ∆T | 14
72 | 122 | 1000 | 61 | LDB | 58
72 | 122 | 1000 | 61 | LWB | 54.3
72 | 122 | 1000 | 61 | kW | 2.88
77 | 122 | 1000 | 64 | MBh | 19.2
77 | 122 | 1000 | 64 | S/T | 0.766
77 | 122 | 1000 | 64 | ∆T | 13.6
77 | 122 | 1000 | 64 | LDB | 63.4
77 | 122 | 1000 | 64 | LWB | 57.8
77 | 122 | 1000 | 64 | kW | 2.88
80 | 122 | 1000 | 67 | MBh | 19.2
80 | 122 | 1000 | 67 | S/T | 0.719
80 | 122 | 1000 | 67 | ∆T | 12.8
80 | 122 | 1000 | 67 | LDB | 67.2
80 | 122 | 1000 | 67 | LWB | 61.2
80 | 122 | 1000 | 67 | kW | 2.88
84 | 122 | 1000 | 70 | MBh | 19.2
84 | 122 | 1000 | 70 | S/T | 0.672
84 | 122 | 1000 | 70 | ∆T | 11.9
84 | 122 | 1000 | 70 | LDB | 72.1
84 | 122 | 1000 | 70 | LWB | 64.6
84 | 122 | 1000 | 70 | kW | 2.88
86 | 122 | 1000 | 72 | MBh | 19.2
86 | 122 | 1000 | 72 | S/T | 0.667
86 | 122 | 1000 | 72 | ∆T | 11.9
86 | 122 | 1000 | 72 | LDB | 74.1
86 | 122 | 1000 | 72 | LWB | 66.8
86 | 122 | 1000 | 72 | kW | 2.88
90 | 122 | 1000 | 75 | MBh | 19.2
90 | 122 | 1000 | 75 | S/T | 0.615
90 | 122 | 1000 | 75 | ∆T | 10.9
90 | 122 | 1000 | 75 | LDB | 79.1
90 | 122 | 1000 | 75 | LWB | 70.2
90 | 122 | 1000 | 75 | kW | 2.88

## RZA30AAVJU - FTA30AAVJUA
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1000 | 57 | MBh | 19.1 | 64 | 60 | 61 | 42 | 3.99
68 | 23 | 1000 | 57 | S/T | 0.806 | 64 | 60 | 65 | 38.9 | 3.63
68 | 23 | 1000 | 57 | ∆T | 14.3 | 64 | 60 | 68 | 36.6 | 3.38
68 | 23 | 1000 | 57 | LDB | 53.7 | 64 | 60 | 70 | 35 | 3.23
68 | 23 | 1000 | 57 | LWB | 49.8 | 64 | 60 | 72 | 33.4 | 3.08
68 | 23 | 1000 | 57 | kW | 0.79 | 64 | 60 | 75 | 31.1 | 2.87
72 | 23 | 1000 | 61 | MBh | 23.2 | 60 | 56 | 61 | 42 | 4.16
72 | 23 | 1000 | 61 | S/T | 0.78 | 60 | 56 | 65 | 38.9 | 3.77
72 | 23 | 1000 | 61 | ∆T | 16.8 | 60 | 56 | 68 | 36.6 | 3.51
72 | 23 | 1000 | 61 | LDB | 55.2 | 60 | 56 | 70 | 35 | 3.34
72 | 23 | 1000 | 61 | LWB | 52.8 | 60 | 56 | 72 | 33.4 | 3.18
72 | 23 | 1000 | 61 | kW | 0.96 | 60 | 56 | 75 | 31.1 | 2.96
77 | 23 | 1000 | 64 | MBh | 26.3 | 57 | 53 | 61 | 42 | 4.3
77 | 23 | 1000 | 64 | S/T | 0.76 | 57 | 53 | 65 | 38.9 | 3.89
77 | 23 | 1000 | 64 | ∆T | 18.5 | 57 | 53 | 68 | 36.6 | 3.61
77 | 23 | 1000 | 64 | LDB | 58.5 | 57 | 53 | 70 | 35 | 3.44
77 | 23 | 1000 | 64 | LWB | 55.2 | 57 | 53 | 72 | 33.4 | 3.27
77 | 23 | 1000 | 64 | kW | 1.11 | 57 | 53 | 75 | 31.1 | 3.03
80 | 23 | 1000 | 67 | MBh | 29.4 | 54 | 50 | 61 | 42 | 4.45
80 | 23 | 1000 | 67 | S/T | 0.711 | 54 | 50 | 65 | 38.9 | 4.02
80 | 23 | 1000 | 67 | ∆T | 19.4 | 54 | 50 | 68 | 36.6 | 3.73
80 | 23 | 1000 | 67 | LDB | 60.6 | 54 | 50 | 70 | 35 | 3.54
80 | 23 | 1000 | 67 | LWB | 57.8 | 54 | 50 | 72 | 33.4 | 3.36
80 | 23 | 1000 | 67 | kW | 1.26 | 54 | 50 | 75 | 31.1 | 3.11
84 | 23 | 1000 | 70 | MBh | 32.5 | 51 | 47 | 61 | 42 | 4.62
84 | 23 | 1000 | 70 | S/T | 0.668 | 51 | 47 | 65 | 38.9 | 4.16
84 | 23 | 1000 | 70 | ∆T | 20.1 | 51 | 47 | 68 | 36.6 | 3.85
84 | 23 | 1000 | 70 | LDB | 63.9 | 51 | 47 | 70 | 35 | 3.65
84 | 23 | 1000 | 70 | LWB | 60.4 | 51 | 47 | 72 | 33.4 | 3.47
84 | 23 | 1000 | 70 | kW | 1.41 | 51 | 47 | 75 | 31.1 | 3.2
86 | 23 | 1000 | 72 | MBh | 34.6 | 47 | 43 | 61 | 42 | 4.86
86 | 23 | 1000 | 72 | S/T | 0.659 | 47 | 43 | 65 | 38.9 | 4.37
86 | 23 | 1000 | 72 | ∆T | 21.1 | 47 | 43 | 68 | 36.6 | 4.03
86 | 23 | 1000 | 72 | LDB | 64.9 | 47 | 43 | 70 | 35 | 3.82
86 | 23 | 1000 | 72 | LWB | 62.2 | 47 | 43 | 72 | 33.4 | 3.62
86 | 23 | 1000 | 72 | kW | 1.51 | 47 | 43 | 75 | 31.1 | 3.33
90 | 23 | 1000 | 75 | MBh | 37.7 | 44 | 40 | 61 | 42 | 5.06
90 | 23 | 1000 | 75 | S/T | 0.61 | 44 | 40 | 65 | 38.9 | 4.55
90 | 23 | 1000 | 75 | ∆T | 21.3 | 44 | 40 | 68 | 36.6 | 4.19
90 | 23 | 1000 | 75 | LDB | 68.7 | 44 | 40 | 70 | 35 | 3.96
90 | 23 | 1000 | 75 | LWB | 65 | 44 | 40 | 72 | 33.4 | 3.74
90 | 23 | 1000 | 75 | kW | 1.67 | 44 | 40 | 75 | 31.1 | 3.44
68 | 30 | 1000 | 57 | MBh | 19.1 | 39 | 36 | 61 | 42 | 5.36
68 | 30 | 1000 | 57 | S/T | 0.806 | 39 | 36 | 65 | 38.9 | 4.8
68 | 30 | 1000 | 57 | ∆T | 14.3 | 39 | 36 | 68 | 36.6 | 4.41
68 | 30 | 1000 | 57 | LDB | 53.7 | 39 | 36 | 70 | 35 | 4.16
68 | 30 | 1000 | 57 | LWB | 49.8 | 39 | 36 | 72 | 33.4 | 3.93
68 | 30 | 1000 | 57 | kW | 0.81 | 39 | 36 | 75 | 31.1 | 3.6
72 | 30 | 1000 | 61 | MBh | 23.2 | 35 | 32 | 61 | 42 | 5.71
72 | 30 | 1000 | 61 | S/T | 0.78 | 35 | 32 | 65 | 38.9 | 5.09
72 | 30 | 1000 | 61 | ∆T | 16.8 | 35 | 32 | 68 | 36.6 | 4.67
72 | 30 | 1000 | 61 | LDB | 55.2 | 35 | 32 | 70 | 35 | 4.4
72 | 30 | 1000 | 61 | LWB | 52.8 | 35 | 32 | 72 | 33.4 | 4.14
72 | 30 | 1000 | 61 | kW | 0.99 | 35 | 32 | 75 | 31.1 | 3.78
77 | 30 | 1000 | 64 | MBh | 26.3 | 30 | 28 | 61 | 42 | 6.1
77 | 30 | 1000 | 64 | S/T | 0.76 | 30 | 28 | 65 | 38.9 | 5.43
77 | 30 | 1000 | 64 | ∆T | 18.5 | 30 | 28 | 68 | 36.6 | 4.96
77 | 30 | 1000 | 64 | LDB | 58.5 | 30 | 28 | 70 | 35 | 4.66
77 | 30 | 1000 | 64 | LWB | 55.2 | 30 | 28 | 72 | 33.4 | 4.38
77 | 30 | 1000 | 64 | kW | 1.14 | 30 | 28 | 75 | 31.1 | 3.99
80 | 30 | 1000 | 67 | MBh | 29.4 | 26 | 24 | 61 | 42 | 6.38
80 | 30 | 1000 | 67 | S/T | 0.711 | 26 | 24 | 65 | 38.9 | 5.81
80 | 30 | 1000 | 67 | ∆T | 19.4 | 26 | 24 | 68 | 36.6 | 5.29
80 | 30 | 1000 | 67 | LDB | 60.6 | 26 | 24 | 70 | 35 | 4.97
80 | 30 | 1000 | 67 | LWB | 57.8 | 26 | 24 | 72 | 33.4 | 4.66
80 | 30 | 1000 | 67 | kW | 1.3 | 26 | 24 | 75 | 31.1 | 4.23
84 | 30 | 1000 | 70 | MBh | 32.5 | 22 | 20 | 61 | 42 | 6.07
84 | 30 | 1000 | 70 | S/T | 0.668 | 22 | 20 | 65 | 38.9 | 6.25
84 | 30 | 1000 | 70 | ∆T | 20.1 | 22 | 20 | 68 | 36.6 | 5.68
84 | 30 | 1000 | 70 | LDB | 63.9 | 22 | 20 | 70 | 35 | 5.33
84 | 30 | 1000 | 70 | LWB | 60.4 | 22 | 20 | 72 | 33.4 | 4.99
84 | 30 | 1000 | 70 | kW | 1.45 | 22 | 20 | 75 | 31.1 | 4.51
86 | 30 | 1000 | 72 | MBh | 34.6 | 19 | 18 | 61 | 41.2 | 5.9
86 | 30 | 1000 | 72 | S/T | 0.659 | 19 | 18 | 65 | 38.9 | 6.4
86 | 30 | 1000 | 72 | ∆T | 21.1 | 19 | 18 | 68 | 36.6 | 5.9
86 | 30 | 1000 | 72 | LDB | 64.9 | 19 | 18 | 70 | 35 | 5.52
86 | 30 | 1000 | 72 | LWB | 62.2 | 19 | 18 | 72 | 33.4 | 5.17
86 | 30 | 1000 | 72 | kW | 1.56 | 19 | 18 | 75 | 31.1 | 4.66
90 | 30 | 1000 | 75 | MBh | 37.7 | 17 | 16 | 61 | 40 | 5.67
90 | 30 | 1000 | 75 | S/T | 0.61 | 17 | 16 | 65 | 38.9 | 6.19
90 | 30 | 1000 | 75 | ∆T | 21.3 | 17 | 16 | 68 | 36.6 | 6.19
90 | 30 | 1000 | 75 | LDB | 68.7 | 17 | 16 | 70 | 35 | 5.79
90 | 30 | 1000 | 75 | LWB | 65 | 17 | 16 | 72 | 33.4 | 5.41
90 | 30 | 1000 | 75 | kW | 1.73 | 17 | 16 | 75 | 31.1 | 4.87
68 | 40 | 1000 | 57 | MBh | 19.1 | 15 | 14 | 61 | 39.3 | 5.53
68 | 40 | 1000 | 57 | S/T | 0.806 | 15 | 14 | 65 | 38.9 | 6.06
68 | 40 | 1000 | 57 | ∆T | 14.3 | 15 | 14 | 68 | 36.6 | 6.39
68 | 40 | 1000 | 57 | LDB | 53.7 | 15 | 14 | 70 | 35 | 5.97
68 | 40 | 1000 | 57 | LWB | 49.8 | 15 | 14 | 72 | 33.4 | 5.57
68 | 40 | 1000 | 57 | kW | 0.84 | 15 | 14 | 75 | 31.1 | 5.01
72 | 40 | 1000 | 61 | MBh | 23.2 | 13 | 12 | 61 | 38.3 | 5.33
72 | 40 | 1000 | 61 | S/T | 0.78 | 13 | 12 | 65 | 38.3 | 5.88
72 | 40 | 1000 | 61 | ∆T | 16.8 | 13 | 12 | 68 | 36.6 | 6.28
72 | 40 | 1000 | 61 | LDB | 55.2 | 13 | 12 | 70 | 35 | 6.22
72 | 40 | 1000 | 61 | LWB | 52.8 | 13 | 12 | 72 | 33.4 | 5.8
72 | 40 | 1000 | 61 | kW | 1.04 | 13 | 12 | 75 | 31.1 | 5.21
77 | 40 | 1000 | 64 | MBh | 26.3 | 10 | 9 | 61 | 36.7 | 4.96
77 | 40 | 1000 | 64 | S/T | 0.76 | 10 | 9 | 65 | 36.7 | 5.53
77 | 40 | 1000 | 64 | ∆T | 18.5 | 10 | 9 | 68 | 36.6 | 5.96
77 | 40 | 1000 | 64 | LDB | 58.5 | 10 | 9 | 70 | 35 | 6.24
77 | 40 | 1000 | 64 | LWB | 55.2 | 10 | 9 | 72 | 33.4 | 6.25
77 | 40 | 1000 | 64 | kW | 1.2 | 10 | 9 | 75 | 31.1 | 5.6
80 | 40 | 1000 | 67 | MBh | 29.4 | 6 | 5 | 61 | 35 | 4.55
80 | 40 | 1000 | 67 | S/T | 0.711 | 6 | 5 | 65 | 35 | 5.15
80 | 40 | 1000 | 67 | ∆T | 19.4 | 6 | 5 | 68 | 35 | 5.4
80 | 40 | 1000 | 67 | LDB | 60.6 | 6 | 5 | 70 | 35 | 5.4
80 | 40 | 1000 | 67 | LWB | 57.8 | 6 | 5 | 72 | 33.4 | 5.4
80 | 40 | 1000 | 67 | kW | 1.36 | 6 | 5 | 75 | 31.1 | 5.4
84 | 40 | 1000 | 70 | MBh | 32.5 | -2 | -2 | 61 | 30 | 3.56
84 | 40 | 1000 | 70 | S/T | 0.668 | -2 | -2 | 65 | 30 | 4.23
84 | 40 | 1000 | 70 | ∆T | 20.1 | -2 | -2 | 68 | 30 | 4.73
84 | 40 | 1000 | 70 | LDB | 63.9 | -2 | -2 | 70 | 30 | 4.86
84 | 40 | 1000 | 70 | LWB | 60.4 | -2 | -2 | 72 | 30 | 4.86
84 | 40 | 1000 | 70 | kW | 1.53 | -2 | -2 | 75 | 30 | 4.86
86 | 40 | 1000 | 72 | MBh | 34.6 | -4 | -4 | 61 | 28.7 | 3.27
86 | 40 | 1000 | 72 | S/T | 0.659 | -4 | -4 | 65 | 28.7 | 3.96
86 | 40 | 1000 | 72 | ∆T | 21.1 | -4 | -4 | 68 | 28.7 | 4.48
86 | 40 | 1000 | 72 | LDB | 64.9 | -4 | -4 | 70 | 28.7 | 4.72
86 | 40 | 1000 | 72 | LWB | 62.2 | -4 | -4 | 72 | 28.7 | 4.72
86 | 40 | 1000 | 72 | kW | 1.64 | -4 | -4 | 75 | 28.7 | 4.72
90 | 40 | 1000 | 75 | MBh | 37.7
90 | 40 | 1000 | 75 | S/T | 0.61
90 | 40 | 1000 | 75 | ∆T | 21.3
90 | 40 | 1000 | 75 | LDB | 68.7
90 | 40 | 1000 | 75 | LWB | 65
90 | 40 | 1000 | 75 | kW | 1.81
68 | 50 | 1000 | 57 | MBh | 19.1
68 | 50 | 1000 | 57 | S/T | 0.806
68 | 50 | 1000 | 57 | ∆T | 14.3
68 | 50 | 1000 | 57 | LDB | 53.7
68 | 50 | 1000 | 57 | LWB | 49.8
68 | 50 | 1000 | 57 | kW | 0.88
72 | 50 | 1000 | 61 | MBh | 23.2
72 | 50 | 1000 | 61 | S/T | 0.78
72 | 50 | 1000 | 61 | ∆T | 16.8
72 | 50 | 1000 | 61 | LDB | 55.2
72 | 50 | 1000 | 61 | LWB | 52.8
72 | 50 | 1000 | 61 | kW | 1.09
77 | 50 | 1000 | 64 | MBh | 26.3
77 | 50 | 1000 | 64 | S/T | 0.76
77 | 50 | 1000 | 64 | ∆T | 18.5
77 | 50 | 1000 | 64 | LDB | 58.5
77 | 50 | 1000 | 64 | LWB | 55.2
77 | 50 | 1000 | 64 | kW | 1.26
80 | 50 | 1000 | 67 | MBh | 29.4
80 | 50 | 1000 | 67 | S/T | 0.711
80 | 50 | 1000 | 67 | ∆T | 19.4
80 | 50 | 1000 | 67 | LDB | 60.6
80 | 50 | 1000 | 67 | LWB | 57.8
80 | 50 | 1000 | 67 | kW | 1.43
84 | 50 | 1000 | 70 | MBh | 32.5
84 | 50 | 1000 | 70 | S/T | 0.668
84 | 50 | 1000 | 70 | ∆T | 20.1
84 | 50 | 1000 | 70 | LDB | 63.9
84 | 50 | 1000 | 70 | LWB | 60.4
84 | 50 | 1000 | 70 | kW | 1.61
86 | 50 | 1000 | 72 | MBh | 34.6
86 | 50 | 1000 | 72 | S/T | 0.659
86 | 50 | 1000 | 72 | ∆T | 21.1
86 | 50 | 1000 | 72 | LDB | 64.9
86 | 50 | 1000 | 72 | LWB | 62.2
86 | 50 | 1000 | 72 | kW | 1.72
90 | 50 | 1000 | 75 | MBh | 37.7
90 | 50 | 1000 | 75 | S/T | 0.61
90 | 50 | 1000 | 75 | ∆T | 21.3
90 | 50 | 1000 | 75 | LDB | 68.7
90 | 50 | 1000 | 75 | LWB | 65
90 | 50 | 1000 | 75 | kW | 1.9
68 | 54 | 1000 | 57 | MBh | 19.1
68 | 54 | 1000 | 57 | S/T | 0.806
68 | 54 | 1000 | 57 | ∆T | 14.3
68 | 54 | 1000 | 57 | LDB | 53.7
68 | 54 | 1000 | 57 | LWB | 49.8
68 | 54 | 1000 | 57 | kW | 0.9
72 | 54 | 1000 | 61 | MBh | 23.2
72 | 54 | 1000 | 61 | S/T | 0.78
72 | 54 | 1000 | 61 | ∆T | 16.8
72 | 54 | 1000 | 61 | LDB | 55.2
72 | 54 | 1000 | 61 | LWB | 52.8
72 | 54 | 1000 | 61 | kW | 1.11
77 | 54 | 1000 | 64 | MBh | 26.3
77 | 54 | 1000 | 64 | S/T | 0.76
77 | 54 | 1000 | 64 | ∆T | 18.5
77 | 54 | 1000 | 64 | LDB | 58.5
77 | 54 | 1000 | 64 | LWB | 55.2
77 | 54 | 1000 | 64 | kW | 1.28
80 | 54 | 1000 | 67 | MBh | 29.4
80 | 54 | 1000 | 67 | S/T | 0.711
80 | 54 | 1000 | 67 | ∆T | 19.4
80 | 54 | 1000 | 67 | LDB | 60.6
80 | 54 | 1000 | 67 | LWB | 57.8
80 | 54 | 1000 | 67 | kW | 1.46
84 | 54 | 1000 | 70 | MBh | 32.5
84 | 54 | 1000 | 70 | S/T | 0.668
84 | 54 | 1000 | 70 | ∆T | 20.1
84 | 54 | 1000 | 70 | LDB | 63.9
84 | 54 | 1000 | 70 | LWB | 60.4
84 | 54 | 1000 | 70 | kW | 1.64
86 | 54 | 1000 | 72 | MBh | 34.6
86 | 54 | 1000 | 72 | S/T | 0.659
86 | 54 | 1000 | 72 | ∆T | 21.1
86 | 54 | 1000 | 72 | LDB | 64.9
86 | 54 | 1000 | 72 | LWB | 62.2
86 | 54 | 1000 | 72 | kW | 1.76
90 | 54 | 1000 | 75 | MBh | 37.7
90 | 54 | 1000 | 75 | S/T | 0.61
90 | 54 | 1000 | 75 | ∆T | 21.3
90 | 54 | 1000 | 75 | LDB | 68.7
90 | 54 | 1000 | 75 | LWB | 65
90 | 54 | 1000 | 75 | kW | 1.94
68 | 58 | 1000 | 57 | MBh | 19.1
68 | 58 | 1000 | 57 | S/T | 0.806
68 | 58 | 1000 | 57 | ∆T | 14.3
68 | 58 | 1000 | 57 | LDB | 53.7
68 | 58 | 1000 | 57 | LWB | 49.8
68 | 58 | 1000 | 57 | kW | 0.92
72 | 58 | 1000 | 61 | MBh | 23.2
72 | 58 | 1000 | 61 | S/T | 0.78
72 | 58 | 1000 | 61 | ∆T | 16.8
72 | 58 | 1000 | 61 | LDB | 55.2
72 | 58 | 1000 | 61 | LWB | 52.8
72 | 58 | 1000 | 61 | kW | 1.14
77 | 58 | 1000 | 64 | MBh | 26.3
77 | 58 | 1000 | 64 | S/T | 0.76
77 | 58 | 1000 | 64 | ∆T | 18.5
77 | 58 | 1000 | 64 | LDB | 58.5
77 | 58 | 1000 | 64 | LWB | 55.2
77 | 58 | 1000 | 64 | kW | 1.31
80 | 58 | 1000 | 67 | MBh | 29.4
80 | 58 | 1000 | 67 | S/T | 0.711
80 | 58 | 1000 | 67 | ∆T | 19.4
80 | 58 | 1000 | 67 | LDB | 60.6
80 | 58 | 1000 | 67 | LWB | 57.8
80 | 58 | 1000 | 67 | kW | 1.49
84 | 58 | 1000 | 70 | MBh | 32.5
84 | 58 | 1000 | 70 | S/T | 0.668
84 | 58 | 1000 | 70 | ∆T | 20.1
84 | 58 | 1000 | 70 | LDB | 63.9
84 | 58 | 1000 | 70 | LWB | 60.4
84 | 58 | 1000 | 70 | kW | 1.67
86 | 58 | 1000 | 72 | MBh | 34.6
86 | 58 | 1000 | 72 | S/T | 0.659
86 | 58 | 1000 | 72 | ∆T | 21.1
86 | 58 | 1000 | 72 | LDB | 64.9
86 | 58 | 1000 | 72 | LWB | 62.2
86 | 58 | 1000 | 72 | kW | 1.8
90 | 58 | 1000 | 75 | MBh | 37.3
90 | 58 | 1000 | 75 | S/T | 0.609
90 | 58 | 1000 | 75 | ∆T | 21
90 | 58 | 1000 | 75 | LDB | 69
90 | 58 | 1000 | 75 | LWB | 65.1
90 | 58 | 1000 | 75 | kW | 1.95
68 | 62 | 1000 | 57 | MBh | 19.1
68 | 62 | 1000 | 57 | S/T | 0.806
68 | 62 | 1000 | 57 | ∆T | 14.3
68 | 62 | 1000 | 57 | LDB | 53.7
68 | 62 | 1000 | 57 | LWB | 49.8
68 | 62 | 1000 | 57 | kW | 0.94
72 | 62 | 1000 | 61 | MBh | 23.2
72 | 62 | 1000 | 61 | S/T | 0.78
72 | 62 | 1000 | 61 | ∆T | 16.8
72 | 62 | 1000 | 61 | LDB | 55.2
72 | 62 | 1000 | 61 | LWB | 52.8
72 | 62 | 1000 | 61 | kW | 1.16
77 | 62 | 1000 | 64 | MBh | 26.3
77 | 62 | 1000 | 64 | S/T | 0.76
77 | 62 | 1000 | 64 | ∆T | 18.5
77 | 62 | 1000 | 64 | LDB | 58.5
77 | 62 | 1000 | 64 | LWB | 55.2
77 | 62 | 1000 | 64 | kW | 1.34
80 | 62 | 1000 | 67 | MBh | 29.4
80 | 62 | 1000 | 67 | S/T | 0.711
80 | 62 | 1000 | 67 | ∆T | 19.4
80 | 62 | 1000 | 67 | LDB | 60.6
80 | 62 | 1000 | 67 | LWB | 57.8
80 | 62 | 1000 | 67 | kW | 1.52
84 | 62 | 1000 | 70 | MBh | 32.5
84 | 62 | 1000 | 70 | S/T | 0.668
84 | 62 | 1000 | 70 | ∆T | 20.1
84 | 62 | 1000 | 70 | LDB | 63.9
84 | 62 | 1000 | 70 | LWB | 60.4
84 | 62 | 1000 | 70 | kW | 1.71
86 | 62 | 1000 | 72 | MBh | 34.6
86 | 62 | 1000 | 72 | S/T | 0.659
86 | 62 | 1000 | 72 | ∆T | 21.1
86 | 62 | 1000 | 72 | LDB | 64.9
86 | 62 | 1000 | 72 | LWB | 62.2
86 | 62 | 1000 | 72 | kW | 1.84
90 | 62 | 1000 | 75 | MBh | 36.8
90 | 62 | 1000 | 75 | S/T | 0.609
90 | 62 | 1000 | 75 | ∆T | 20.7
90 | 62 | 1000 | 75 | LDB | 69.3
90 | 62 | 1000 | 75 | LWB | 65.3
90 | 62 | 1000 | 75 | kW | 1.99
68 | 66 | 1000 | 57 | MBh | 19.1
68 | 66 | 1000 | 57 | S/T | 0.806
68 | 66 | 1000 | 57 | ∆T | 14.3
68 | 66 | 1000 | 57 | LDB | 53.7
68 | 66 | 1000 | 57 | LWB | 49.8
68 | 66 | 1000 | 57 | kW | 0.96
72 | 66 | 1000 | 61 | MBh | 23.2
72 | 66 | 1000 | 61 | S/T | 0.78
72 | 66 | 1000 | 61 | ∆T | 16.8
72 | 66 | 1000 | 61 | LDB | 55.2
72 | 66 | 1000 | 61 | LWB | 52.8
72 | 66 | 1000 | 61 | kW | 1.19
77 | 66 | 1000 | 64 | MBh | 26.3
77 | 66 | 1000 | 64 | S/T | 0.76
77 | 66 | 1000 | 64 | ∆T | 18.5
77 | 66 | 1000 | 64 | LDB | 58.5
77 | 66 | 1000 | 64 | LWB | 55.2
77 | 66 | 1000 | 64 | kW | 1.37
80 | 66 | 1000 | 67 | MBh | 29.4
80 | 66 | 1000 | 67 | S/T | 0.711
80 | 66 | 1000 | 67 | ∆T | 19.4
80 | 66 | 1000 | 67 | LDB | 60.6
80 | 66 | 1000 | 67 | LWB | 57.8
80 | 66 | 1000 | 67 | kW | 1.56
84 | 66 | 1000 | 70 | MBh | 32.5
84 | 66 | 1000 | 70 | S/T | 0.668
84 | 66 | 1000 | 70 | ∆T | 20.1
84 | 66 | 1000 | 70 | LDB | 63.9
84 | 66 | 1000 | 70 | LWB | 60.4
84 | 66 | 1000 | 70 | kW | 1.81
86 | 66 | 1000 | 72 | MBh | 34.6
86 | 66 | 1000 | 72 | S/T | 0.659
86 | 66 | 1000 | 72 | ∆T | 21.1
86 | 66 | 1000 | 72 | LDB | 64.9
86 | 66 | 1000 | 72 | LWB | 62.2
86 | 66 | 1000 | 72 | kW | 1.98
90 | 66 | 1000 | 75 | MBh | 36.2
90 | 66 | 1000 | 75 | S/T | 0.61
90 | 66 | 1000 | 75 | ∆T | 20.5
90 | 66 | 1000 | 75 | LDB | 69.5
90 | 66 | 1000 | 75 | LWB | 65.5
90 | 66 | 1000 | 75 | kW | 2.1
68 | 70 | 1000 | 57 | MBh | 19.1
68 | 70 | 1000 | 57 | S/T | 0.806
68 | 70 | 1000 | 57 | ∆T | 14.3
68 | 70 | 1000 | 57 | LDB | 53.7
68 | 70 | 1000 | 57 | LWB | 49.8
68 | 70 | 1000 | 57 | kW | 0.98
72 | 70 | 1000 | 61 | MBh | 23.2
72 | 70 | 1000 | 61 | S/T | 0.78
72 | 70 | 1000 | 61 | ∆T | 16.8
72 | 70 | 1000 | 61 | LDB | 55.2
72 | 70 | 1000 | 61 | LWB | 52.8
72 | 70 | 1000 | 61 | kW | 1.21
77 | 70 | 1000 | 64 | MBh | 26.3
77 | 70 | 1000 | 64 | S/T | 0.76
77 | 70 | 1000 | 64 | ∆T | 18.5
77 | 70 | 1000 | 64 | LDB | 58.5
77 | 70 | 1000 | 64 | LWB | 55.2
77 | 70 | 1000 | 64 | kW | 1.44
80 | 70 | 1000 | 67 | MBh | 29.4
80 | 70 | 1000 | 67 | S/T | 0.711
80 | 70 | 1000 | 67 | ∆T | 19.4
80 | 70 | 1000 | 67 | LDB | 60.6
80 | 70 | 1000 | 67 | LWB | 57.8
80 | 70 | 1000 | 67 | kW | 1.69
84 | 70 | 1000 | 70 | MBh | 32.5
84 | 70 | 1000 | 70 | S/T | 0.668
84 | 70 | 1000 | 70 | ∆T | 20.1
84 | 70 | 1000 | 70 | LDB | 63.9
84 | 70 | 1000 | 70 | LWB | 60.4
84 | 70 | 1000 | 70 | kW | 1.96
86 | 70 | 1000 | 72 | MBh | 34.6
86 | 70 | 1000 | 72 | S/T | 0.659
86 | 70 | 1000 | 72 | ∆T | 21.1
86 | 70 | 1000 | 72 | LDB | 64.9
86 | 70 | 1000 | 72 | LWB | 62.2
86 | 70 | 1000 | 72 | kW | 2.15
90 | 70 | 1000 | 75 | MBh | 35.7
90 | 70 | 1000 | 75 | S/T | 0.608
90 | 70 | 1000 | 75 | ∆T | 20.1
90 | 70 | 1000 | 75 | LDB | 69.9
90 | 70 | 1000 | 75 | LWB | 65.6
90 | 70 | 1000 | 75 | kW | 2.21
68 | 72 | 1000 | 57 | MBh | 19.1
68 | 72 | 1000 | 57 | S/T | 0.806
68 | 72 | 1000 | 57 | ∆T | 14.3
68 | 72 | 1000 | 57 | LDB | 53.7
68 | 72 | 1000 | 57 | LWB | 49.8
68 | 72 | 1000 | 57 | kW | 0.99
72 | 72 | 1000 | 61 | MBh | 23.2
72 | 72 | 1000 | 61 | S/T | 0.78
72 | 72 | 1000 | 61 | ∆T | 16.8
72 | 72 | 1000 | 61 | LDB | 55.2
72 | 72 | 1000 | 61 | LWB | 52.8
72 | 72 | 1000 | 61 | kW | 1.25
77 | 72 | 1000 | 64 | MBh | 26.3
77 | 72 | 1000 | 64 | S/T | 0.76
77 | 72 | 1000 | 64 | ∆T | 18.5
77 | 72 | 1000 | 64 | LDB | 58.5
77 | 72 | 1000 | 64 | LWB | 55.2
77 | 72 | 1000 | 64 | kW | 1.49
80 | 72 | 1000 | 67 | MBh | 29.4
80 | 72 | 1000 | 67 | S/T | 0.711
80 | 72 | 1000 | 67 | ∆T | 19.4
80 | 72 | 1000 | 67 | LDB | 60.6
80 | 72 | 1000 | 67 | LWB | 57.8
80 | 72 | 1000 | 67 | kW | 1.75
84 | 72 | 1000 | 70 | MBh | 32.5
84 | 72 | 1000 | 70 | S/T | 0.668
84 | 72 | 1000 | 70 | ∆T | 20.1
84 | 72 | 1000 | 70 | LDB | 63.9
84 | 72 | 1000 | 70 | LWB | 60.4
84 | 72 | 1000 | 70 | kW | 2.03
86 | 72 | 1000 | 72 | MBh | 34.6
86 | 72 | 1000 | 72 | S/T | 0.659
86 | 72 | 1000 | 72 | ∆T | 21.1
86 | 72 | 1000 | 72 | LDB | 64.9
86 | 72 | 1000 | 72 | LWB | 62.2
86 | 72 | 1000 | 72 | kW | 2.23
90 | 72 | 1000 | 75 | MBh | 35.4
90 | 72 | 1000 | 75 | S/T | 0.61
90 | 72 | 1000 | 75 | ∆T | 20
90 | 72 | 1000 | 75 | LDB | 70
90 | 72 | 1000 | 75 | LWB | 65.7
90 | 72 | 1000 | 75 | kW | 2.27
68 | 75 | 1000 | 57 | MBh | 19.1
68 | 75 | 1000 | 57 | S/T | 0.806
68 | 75 | 1000 | 57 | ∆T | 14.3
68 | 75 | 1000 | 57 | LDB | 53.7
68 | 75 | 1000 | 57 | LWB | 49.8
68 | 75 | 1000 | 57 | kW | 1.02
72 | 75 | 1000 | 61 | MBh | 23.2
72 | 75 | 1000 | 61 | S/T | 0.78
72 | 75 | 1000 | 61 | ∆T | 16.8
72 | 75 | 1000 | 61 | LDB | 55.2
72 | 75 | 1000 | 61 | LWB | 52.8
72 | 75 | 1000 | 61 | kW | 1.32
77 | 75 | 1000 | 64 | MBh | 26.3
77 | 75 | 1000 | 64 | S/T | 0.76
77 | 75 | 1000 | 64 | ∆T | 18.5
77 | 75 | 1000 | 64 | LDB | 58.5
77 | 75 | 1000 | 64 | LWB | 55.2
77 | 75 | 1000 | 64 | kW | 1.58
80 | 75 | 1000 | 67 | MBh | 29.4
80 | 75 | 1000 | 67 | S/T | 0.711
80 | 75 | 1000 | 67 | ∆T | 19.4
80 | 75 | 1000 | 67 | LDB | 60.6
80 | 75 | 1000 | 67 | LWB | 57.8
80 | 75 | 1000 | 67 | kW | 1.85
84 | 75 | 1000 | 70 | MBh | 32.5
84 | 75 | 1000 | 70 | S/T | 0.668
84 | 75 | 1000 | 70 | ∆T | 20.1
84 | 75 | 1000 | 70 | LDB | 63.9
84 | 75 | 1000 | 70 | LWB | 60.4
84 | 75 | 1000 | 70 | kW | 2.15
86 | 75 | 1000 | 72 | MBh | 34.4
86 | 75 | 1000 | 72 | S/T | 0.66
86 | 75 | 1000 | 72 | ∆T | 21
86 | 75 | 1000 | 72 | LDB | 65
86 | 75 | 1000 | 72 | LWB | 62.3
86 | 75 | 1000 | 72 | kW | 2.34
90 | 75 | 1000 | 75 | MBh | 35
90 | 75 | 1000 | 75 | S/T | 0.609
90 | 75 | 1000 | 75 | ∆T | 19.7
90 | 75 | 1000 | 75 | LDB | 70.3
90 | 75 | 1000 | 75 | LWB | 65.8
90 | 75 | 1000 | 75 | kW | 2.35
68 | 79 | 1000 | 57 | MBh | 19.1
68 | 79 | 1000 | 57 | S/T | 0.806
68 | 79 | 1000 | 57 | ∆T | 14.3
68 | 79 | 1000 | 57 | LDB | 53.7
68 | 79 | 1000 | 57 | LWB | 49.8
68 | 79 | 1000 | 57 | kW | 1.1
72 | 79 | 1000 | 61 | MBh | 23.2
72 | 79 | 1000 | 61 | S/T | 0.78
72 | 79 | 1000 | 61 | ∆T | 16.8
72 | 79 | 1000 | 61 | LDB | 55.2
72 | 79 | 1000 | 61 | LWB | 52.8
72 | 79 | 1000 | 61 | kW | 1.43
77 | 79 | 1000 | 64 | MBh | 26.3
77 | 79 | 1000 | 64 | S/T | 0.76
77 | 79 | 1000 | 64 | ∆T | 18.5
77 | 79 | 1000 | 64 | LDB | 58.5
77 | 79 | 1000 | 64 | LWB | 55.2
77 | 79 | 1000 | 64 | kW | 1.7
80 | 79 | 1000 | 67 | MBh | 29.4
80 | 79 | 1000 | 67 | S/T | 0.711
80 | 79 | 1000 | 67 | ∆T | 19.4
80 | 79 | 1000 | 67 | LDB | 60.6
80 | 79 | 1000 | 67 | LWB | 57.8
80 | 79 | 1000 | 67 | kW | 2
84 | 79 | 1000 | 70 | MBh | 32.5
84 | 79 | 1000 | 70 | S/T | 0.668
84 | 79 | 1000 | 70 | ∆T | 20.1
84 | 79 | 1000 | 70 | LDB | 63.9
84 | 79 | 1000 | 70 | LWB | 60.4
84 | 79 | 1000 | 70 | kW | 2.32
86 | 79 | 1000 | 72 | MBh | 33.8
86 | 79 | 1000 | 72 | S/T | 0.66
86 | 79 | 1000 | 72 | ∆T | 20.6
86 | 79 | 1000 | 72 | LDB | 65.4
86 | 79 | 1000 | 72 | LWB | 62.5
86 | 79 | 1000 | 72 | kW | 2.45
90 | 79 | 1000 | 75 | MBh | 34.4
90 | 79 | 1000 | 75 | S/T | 0.61
90 | 79 | 1000 | 75 | ∆T | 19.4
90 | 79 | 1000 | 75 | LDB | 70.6
90 | 79 | 1000 | 75 | LWB | 66
90 | 79 | 1000 | 75 | kW | 2.47
68 | 83 | 1000 | 57 | MBh | 19.1
68 | 83 | 1000 | 57 | S/T | 0.806
68 | 83 | 1000 | 57 | ∆T | 14.3
68 | 83 | 1000 | 57 | LDB | 53.7
68 | 83 | 1000 | 57 | LWB | 49.8
68 | 83 | 1000 | 57 | kW | 1.18
72 | 83 | 1000 | 61 | MBh | 23.2
72 | 83 | 1000 | 61 | S/T | 0.78
72 | 83 | 1000 | 61 | ∆T | 16.8
72 | 83 | 1000 | 61 | LDB | 55.2
72 | 83 | 1000 | 61 | LWB | 52.8
72 | 83 | 1000 | 61 | kW | 1.53
77 | 83 | 1000 | 64 | MBh | 26.3
77 | 83 | 1000 | 64 | S/T | 0.76
77 | 83 | 1000 | 64 | ∆T | 18.5
77 | 83 | 1000 | 64 | LDB | 58.5
77 | 83 | 1000 | 64 | LWB | 55.2
77 | 83 | 1000 | 64 | kW | 1.83
80 | 83 | 1000 | 67 | MBh | 29.4
80 | 83 | 1000 | 67 | S/T | 0.711
80 | 83 | 1000 | 67 | ∆T | 19.4
80 | 83 | 1000 | 67 | LDB | 60.6
80 | 83 | 1000 | 67 | LWB | 57.8
80 | 83 | 1000 | 67 | kW | 2.15
84 | 83 | 1000 | 70 | MBh | 32.5
84 | 83 | 1000 | 70 | S/T | 0.668
84 | 83 | 1000 | 70 | ∆T | 20.1
84 | 83 | 1000 | 70 | LDB | 63.9
84 | 83 | 1000 | 70 | LWB | 60.4
84 | 83 | 1000 | 70 | kW | 2.5
86 | 83 | 1000 | 72 | MBh | 33.2
86 | 83 | 1000 | 72 | S/T | 0.66
86 | 83 | 1000 | 72 | ∆T | 20.3
86 | 83 | 1000 | 72 | LDB | 65.7
86 | 83 | 1000 | 72 | LWB | 62.7
86 | 83 | 1000 | 72 | kW | 2.56
90 | 83 | 1000 | 75 | MBh | 33.9
90 | 83 | 1000 | 75 | S/T | 0.611
90 | 83 | 1000 | 75 | ∆T | 19.2
90 | 83 | 1000 | 75 | LDB | 70.8
90 | 83 | 1000 | 75 | LWB | 66.1
90 | 83 | 1000 | 75 | kW | 2.58
68 | 87 | 1000 | 57 | MBh | 19.1
68 | 87 | 1000 | 57 | S/T | 0.806
68 | 87 | 1000 | 57 | ∆T | 14.3
68 | 87 | 1000 | 57 | LDB | 53.7
68 | 87 | 1000 | 57 | LWB | 49.8
68 | 87 | 1000 | 57 | kW | 1.26
72 | 87 | 1000 | 61 | MBh | 23.2
72 | 87 | 1000 | 61 | S/T | 0.78
72 | 87 | 1000 | 61 | ∆T | 16.8
72 | 87 | 1000 | 61 | LDB | 55.2
72 | 87 | 1000 | 61 | LWB | 52.8
72 | 87 | 1000 | 61 | kW | 1.64
77 | 87 | 1000 | 64 | MBh | 26.3
77 | 87 | 1000 | 64 | S/T | 0.76
77 | 87 | 1000 | 64 | ∆T | 18.5
77 | 87 | 1000 | 64 | LDB | 58.5
77 | 87 | 1000 | 64 | LWB | 55.2
77 | 87 | 1000 | 64 | kW | 1.96
80 | 87 | 1000 | 67 | MBh | 29.4
80 | 87 | 1000 | 67 | S/T | 0.711
80 | 87 | 1000 | 67 | ∆T | 19.4
80 | 87 | 1000 | 67 | LDB | 60.6
80 | 87 | 1000 | 67 | LWB | 57.8
80 | 87 | 1000 | 67 | kW | 2.32
84 | 87 | 1000 | 70 | MBh | 32.3
84 | 87 | 1000 | 70 | S/T | 0.669
84 | 87 | 1000 | 70 | ∆T | 20
84 | 87 | 1000 | 70 | LDB | 64
84 | 87 | 1000 | 70 | LWB | 60.5
84 | 87 | 1000 | 70 | kW | 2.66
86 | 87 | 1000 | 72 | MBh | 32.7
86 | 87 | 1000 | 72 | S/T | 0.661
86 | 87 | 1000 | 72 | ∆T | 20
86 | 87 | 1000 | 72 | LDB | 66
86 | 87 | 1000 | 72 | LWB | 62.8
86 | 87 | 1000 | 72 | kW | 2.68
90 | 87 | 1000 | 75 | MBh | 33.3
90 | 87 | 1000 | 75 | S/T | 0.61
90 | 87 | 1000 | 75 | ∆T | 18.8
90 | 87 | 1000 | 75 | LDB | 71.2
90 | 87 | 1000 | 75 | LWB | 66.3
90 | 87 | 1000 | 75 | kW | 2.69
68 | 91 | 1000 | 57 | MBh | 19.1
68 | 91 | 1000 | 57 | S/T | 0.806
68 | 91 | 1000 | 57 | ∆T | 14.3
68 | 91 | 1000 | 57 | LDB | 53.7
68 | 91 | 1000 | 57 | LWB | 49.8
68 | 91 | 1000 | 57 | kW | 1.35
72 | 91 | 1000 | 61 | MBh | 23.2
72 | 91 | 1000 | 61 | S/T | 0.78
72 | 91 | 1000 | 61 | ∆T | 16.8
72 | 91 | 1000 | 61 | LDB | 55.2
72 | 91 | 1000 | 61 | LWB | 52.8
72 | 91 | 1000 | 61 | kW | 1.76
77 | 91 | 1000 | 64 | MBh | 26.3
77 | 91 | 1000 | 64 | S/T | 0.76
77 | 91 | 1000 | 64 | ∆T | 18.5
77 | 91 | 1000 | 64 | LDB | 58.5
77 | 91 | 1000 | 64 | LWB | 55.2
77 | 91 | 1000 | 64 | kW | 2.11
80 | 91 | 1000 | 67 | MBh | 29.4
80 | 91 | 1000 | 67 | S/T | 0.711
80 | 91 | 1000 | 67 | ∆T | 19.4
80 | 91 | 1000 | 67 | LDB | 60.6
80 | 91 | 1000 | 67 | LWB | 57.8
80 | 91 | 1000 | 67 | kW | 2.49
84 | 91 | 1000 | 70 | MBh | 31.7
84 | 91 | 1000 | 70 | S/T | 0.669
84 | 91 | 1000 | 70 | ∆T | 19.6
84 | 91 | 1000 | 70 | LDB | 64.4
84 | 91 | 1000 | 70 | LWB | 60.7
84 | 91 | 1000 | 70 | kW | 2.78
86 | 91 | 1000 | 72 | MBh | 32.1
86 | 91 | 1000 | 72 | S/T | 0.66
86 | 91 | 1000 | 72 | ∆T | 19.6
86 | 91 | 1000 | 72 | LDB | 66.4
86 | 91 | 1000 | 72 | LWB | 63
86 | 91 | 1000 | 72 | kW | 2.79
90 | 91 | 1000 | 75 | MBh | 32.8
90 | 91 | 1000 | 75 | S/T | 0.61
90 | 91 | 1000 | 75 | ∆T | 18.5
90 | 91 | 1000 | 75 | LDB | 71.5
90 | 91 | 1000 | 75 | LWB | 66.4
90 | 91 | 1000 | 75 | kW | 2.81
68 | 93 | 1000 | 57 | MBh | 19.1
68 | 93 | 1000 | 57 | S/T | 0.806
68 | 93 | 1000 | 57 | ∆T | 14.3
68 | 93 | 1000 | 57 | LDB | 53.7
68 | 93 | 1000 | 57 | LWB | 49.8
68 | 93 | 1000 | 57 | kW | 1.4
72 | 93 | 1000 | 61 | MBh | 23.2
72 | 93 | 1000 | 61 | S/T | 0.78
72 | 93 | 1000 | 61 | ∆T | 16.8
72 | 93 | 1000 | 61 | LDB | 55.2
72 | 93 | 1000 | 61 | LWB | 52.8
72 | 93 | 1000 | 61 | kW | 1.82
77 | 93 | 1000 | 64 | MBh | 26.3
77 | 93 | 1000 | 64 | S/T | 0.76
77 | 93 | 1000 | 64 | ∆T | 18.5
77 | 93 | 1000 | 64 | LDB | 58.5
77 | 93 | 1000 | 64 | LWB | 55.2
77 | 93 | 1000 | 64 | kW | 2.19
80 | 93 | 1000 | 67 | MBh | 29.4
80 | 93 | 1000 | 67 | S/T | 0.711
80 | 93 | 1000 | 67 | ∆T | 19.4
80 | 93 | 1000 | 67 | LDB | 60.6
80 | 93 | 1000 | 67 | LWB | 57.8
80 | 93 | 1000 | 67 | kW | 2.58
84 | 93 | 1000 | 70 | MBh | 31.5
84 | 93 | 1000 | 70 | S/T | 0.667
84 | 93 | 1000 | 70 | ∆T | 19.4
84 | 93 | 1000 | 70 | LDB | 64.6
84 | 93 | 1000 | 70 | LWB | 60.7
84 | 93 | 1000 | 70 | kW | 2.83
86 | 93 | 1000 | 72 | MBh | 31.9
86 | 93 | 1000 | 72 | S/T | 0.658
86 | 93 | 1000 | 72 | ∆T | 19.4
86 | 93 | 1000 | 72 | LDB | 66.6
86 | 93 | 1000 | 72 | LWB | 63.1
86 | 93 | 1000 | 72 | kW | 2.85
90 | 93 | 1000 | 75 | MBh | 32.5
90 | 93 | 1000 | 75 | S/T | 0.609
90 | 93 | 1000 | 75 | ∆T | 18.3
90 | 93 | 1000 | 75 | LDB | 71.7
90 | 93 | 1000 | 75 | LWB | 66.5
90 | 93 | 1000 | 75 | kW | 2.87
68 | 95 | 1000 | 57 | MBh | 19.1
68 | 95 | 1000 | 57 | S/T | 0.806
68 | 95 | 1000 | 57 | ∆T | 14.3
68 | 95 | 1000 | 57 | LDB | 53.7
68 | 95 | 1000 | 57 | LWB | 49.8
68 | 95 | 1000 | 57 | kW | 1.44
72 | 95 | 1000 | 61 | MBh | 23.2
72 | 95 | 1000 | 61 | S/T | 0.78
72 | 95 | 1000 | 61 | ∆T | 16.8
72 | 95 | 1000 | 61 | LDB | 55.2
72 | 95 | 1000 | 61 | LWB | 52.8
72 | 95 | 1000 | 61 | kW | 1.89
77 | 95 | 1000 | 64 | MBh | 26.3
77 | 95 | 1000 | 64 | S/T | 0.76
77 | 95 | 1000 | 64 | ∆T | 18.5
77 | 95 | 1000 | 64 | LDB | 58.5
77 | 95 | 1000 | 64 | LWB | 55.2
77 | 95 | 1000 | 64 | kW | 2.26
80 | 95 | 1000 | 67 | MBh | 29.4
80 | 95 | 1000 | 67 | S/T | 0.711
80 | 95 | 1000 | 67 | ∆T | 19.4
80 | 95 | 1000 | 67 | LDB | 60.6
80 | 95 | 1000 | 67 | LWB | 57.8
80 | 95 | 1000 | 67 | kW | 2.67
84 | 95 | 1000 | 70 | MBh | 31.2
84 | 95 | 1000 | 70 | S/T | 0.667
84 | 95 | 1000 | 70 | ∆T | 19.3
84 | 95 | 1000 | 70 | LDB | 64.7
84 | 95 | 1000 | 70 | LWB | 60.8
84 | 95 | 1000 | 70 | kW | 2.89
86 | 95 | 1000 | 72 | MBh | 31.6
86 | 95 | 1000 | 72 | S/T | 0.658
86 | 95 | 1000 | 72 | ∆T | 19.3
86 | 95 | 1000 | 72 | LDB | 66.7
86 | 95 | 1000 | 72 | LWB | 63.2
86 | 95 | 1000 | 72 | kW | 2.9
90 | 95 | 1000 | 75 | MBh | 32.2
90 | 95 | 1000 | 75 | S/T | 0.609
90 | 95 | 1000 | 75 | ∆T | 18.1
90 | 95 | 1000 | 75 | LDB | 71.9
90 | 95 | 1000 | 75 | LWB | 66.6
90 | 95 | 1000 | 75 | kW | 2.92
68 | 99 | 1000 | 57 | MBh | 19.1
68 | 99 | 1000 | 57 | S/T | 0.806
68 | 99 | 1000 | 57 | ∆T | 14.3
68 | 99 | 1000 | 57 | LDB | 53.7
68 | 99 | 1000 | 57 | LWB | 49.8
68 | 99 | 1000 | 57 | kW | 1.62
72 | 99 | 1000 | 61 | MBh | 23.2
72 | 99 | 1000 | 61 | S/T | 0.78
72 | 99 | 1000 | 61 | ∆T | 16.8
72 | 99 | 1000 | 61 | LDB | 55.2
72 | 99 | 1000 | 61 | LWB | 52.8
72 | 99 | 1000 | 61 | kW | 2.12
77 | 99 | 1000 | 64 | MBh | 26.3
77 | 99 | 1000 | 64 | S/T | 0.76
77 | 99 | 1000 | 64 | ∆T | 18.5
77 | 99 | 1000 | 64 | LDB | 58.5
77 | 99 | 1000 | 64 | LWB | 55.2
77 | 99 | 1000 | 64 | kW | 2.54
80 | 99 | 1000 | 67 | MBh | 29.4
80 | 99 | 1000 | 67 | S/T | 0.711
80 | 99 | 1000 | 67 | ∆T | 19.4
80 | 99 | 1000 | 67 | LDB | 60.6
80 | 99 | 1000 | 67 | LWB | 57.8
80 | 99 | 1000 | 67 | kW | 3
84 | 99 | 1000 | 70 | MBh | 30.6
84 | 99 | 1000 | 70 | S/T | 0.673
84 | 99 | 1000 | 70 | ∆T | 19.1
84 | 99 | 1000 | 70 | LDB | 64.9
84 | 99 | 1000 | 70 | LWB | 61
84 | 99 | 1000 | 70 | kW | 3.14
86 | 99 | 1000 | 72 | MBh | 31
86 | 99 | 1000 | 72 | S/T | 0.665
86 | 99 | 1000 | 72 | ∆T | 19.1
86 | 99 | 1000 | 72 | LDB | 66.9
86 | 99 | 1000 | 72 | LWB | 63.3
86 | 99 | 1000 | 72 | kW | 3.16
90 | 99 | 1000 | 75 | MBh | 31.7
90 | 99 | 1000 | 75 | S/T | 0.612
90 | 99 | 1000 | 75 | ∆T | 18
90 | 99 | 1000 | 75 | LDB | 72
90 | 99 | 1000 | 75 | LWB | 66.8
90 | 99 | 1000 | 75 | kW | 3.18
68 | 103 | 1000 | 57 | MBh | 19.1
68 | 103 | 1000 | 57 | S/T | 0.806
68 | 103 | 1000 | 57 | ∆T | 14.3
68 | 103 | 1000 | 57 | LDB | 53.7
68 | 103 | 1000 | 57 | LWB | 49.8
68 | 103 | 1000 | 57 | kW | 1.8
72 | 103 | 1000 | 61 | MBh | 23.2
72 | 103 | 1000 | 61 | S/T | 0.78
72 | 103 | 1000 | 61 | ∆T | 16.8
72 | 103 | 1000 | 61 | LDB | 55.2
72 | 103 | 1000 | 61 | LWB | 52.8
72 | 103 | 1000 | 61 | kW | 2.36
77 | 103 | 1000 | 64 | MBh | 26.3
77 | 103 | 1000 | 64 | S/T | 0.76
77 | 103 | 1000 | 64 | ∆T | 18.5
77 | 103 | 1000 | 64 | LDB | 58.5
77 | 103 | 1000 | 64 | LWB | 55.2
77 | 103 | 1000 | 64 | kW | 2.84
80 | 103 | 1000 | 67 | MBh | 29.4
80 | 103 | 1000 | 67 | S/T | 0.711
80 | 103 | 1000 | 67 | ∆T | 19.4
80 | 103 | 1000 | 67 | LDB | 60.6
80 | 103 | 1000 | 67 | LWB | 57.8
80 | 103 | 1000 | 67 | kW | 3.36
84 | 103 | 1000 | 70 | MBh | 30.1
84 | 103 | 1000 | 70 | S/T | 0.671
84 | 103 | 1000 | 70 | ∆T | 18.7
84 | 103 | 1000 | 70 | LDB | 65.3
84 | 103 | 1000 | 70 | LWB | 61.2
84 | 103 | 1000 | 70 | kW | 3.4
86 | 103 | 1000 | 72 | MBh | 30.5
86 | 103 | 1000 | 72 | S/T | 0.662
86 | 103 | 1000 | 72 | ∆T | 18.7
86 | 103 | 1000 | 72 | LDB | 67.3
86 | 103 | 1000 | 72 | LWB | 63.5
86 | 103 | 1000 | 72 | kW | 3.41
90 | 103 | 1000 | 75 | MBh | 31.1
90 | 103 | 1000 | 75 | S/T | 0.614
90 | 103 | 1000 | 75 | ∆T | 17.7
90 | 103 | 1000 | 75 | LDB | 72.3
90 | 103 | 1000 | 75 | LWB | 66.9
90 | 103 | 1000 | 75 | kW | 3.44
68 | 106 | 1000 | 57 | MBh | 19.1
68 | 106 | 1000 | 57 | S/T | 0.806
68 | 106 | 1000 | 57 | ∆T | 14.3
68 | 106 | 1000 | 57 | LDB | 53.7
68 | 106 | 1000 | 57 | LWB | 49.8
68 | 106 | 1000 | 57 | kW | 1.94
72 | 106 | 1000 | 61 | MBh | 23.2
72 | 106 | 1000 | 61 | S/T | 0.78
72 | 106 | 1000 | 61 | ∆T | 16.8
72 | 106 | 1000 | 61 | LDB | 55.2
72 | 106 | 1000 | 61 | LWB | 52.8
72 | 106 | 1000 | 61 | kW | 2.56
77 | 106 | 1000 | 64 | MBh | 26.3
77 | 106 | 1000 | 64 | S/T | 0.76
77 | 106 | 1000 | 64 | ∆T | 18.5
77 | 106 | 1000 | 64 | LDB | 58.5
77 | 106 | 1000 | 64 | LWB | 55.2
77 | 106 | 1000 | 64 | kW | 3.07
80 | 106 | 1000 | 67 | MBh | 29.1
80 | 106 | 1000 | 67 | S/T | 0.715
80 | 106 | 1000 | 67 | ∆T | 19.3
80 | 106 | 1000 | 67 | LDB | 60.7
80 | 106 | 1000 | 67 | LWB | 57.9
80 | 106 | 1000 | 67 | kW | 3.56
84 | 106 | 1000 | 70 | MBh | 29.7
84 | 106 | 1000 | 70 | S/T | 0.67
84 | 106 | 1000 | 70 | ∆T | 18.4
84 | 106 | 1000 | 70 | LDB | 65.6
84 | 106 | 1000 | 70 | LWB | 61.3
84 | 106 | 1000 | 70 | kW | 3.59
86 | 106 | 1000 | 72 | MBh | 30.1
86 | 106 | 1000 | 72 | S/T | 0.661
86 | 106 | 1000 | 72 | ∆T | 18.4
86 | 106 | 1000 | 72 | LDB | 67.6
86 | 106 | 1000 | 72 | LWB | 63.6
86 | 106 | 1000 | 72 | kW | 3.61
90 | 106 | 1000 | 75 | MBh | 30.7
90 | 106 | 1000 | 75 | S/T | 0.612
90 | 106 | 1000 | 75 | ∆T | 17.4
90 | 106 | 1000 | 75 | LDB | 72.6
90 | 106 | 1000 | 75 | LWB | 67
90 | 106 | 1000 | 75 | kW | 3.63
68 | 110 | 1000 | 57 | MBh | 19.1
68 | 110 | 1000 | 57 | S/T | 0.806
68 | 110 | 1000 | 57 | ∆T | 14.3
68 | 110 | 1000 | 57 | LDB | 53.7
68 | 110 | 1000 | 57 | LWB | 49.8
68 | 110 | 1000 | 57 | kW | 2.15
72 | 110 | 1000 | 61 | MBh | 23.2
72 | 110 | 1000 | 61 | S/T | 0.78
72 | 110 | 1000 | 61 | ∆T | 16.8
72 | 110 | 1000 | 61 | LDB | 55.2
72 | 110 | 1000 | 61 | LWB | 52.8
72 | 110 | 1000 | 61 | kW | 2.83
77 | 110 | 1000 | 64 | MBh | 26.3
77 | 110 | 1000 | 64 | S/T | 0.76
77 | 110 | 1000 | 64 | ∆T | 18.5
77 | 110 | 1000 | 64 | LDB | 58.5
77 | 110 | 1000 | 64 | LWB | 55.2
77 | 110 | 1000 | 64 | kW | 3.41
80 | 110 | 1000 | 67 | MBh | 28.5
80 | 110 | 1000 | 67 | S/T | 0.716
80 | 110 | 1000 | 67 | ∆T | 18.9
80 | 110 | 1000 | 67 | LDB | 61.1
80 | 110 | 1000 | 67 | LWB | 58.1
80 | 110 | 1000 | 67 | kW | 3.82
84 | 110 | 1000 | 70 | MBh | 29.1
84 | 110 | 1000 | 70 | S/T | 0.67
84 | 110 | 1000 | 70 | ∆T | 18.1
84 | 110 | 1000 | 70 | LDB | 65.9
84 | 110 | 1000 | 70 | LWB | 61.5
84 | 110 | 1000 | 70 | kW | 3.85
86 | 110 | 1000 | 72 | MBh | 29.5
86 | 110 | 1000 | 72 | S/T | 0.661
86 | 110 | 1000 | 72 | ∆T | 18.1
86 | 110 | 1000 | 72 | LDB | 67.9
86 | 110 | 1000 | 72 | LWB | 63.8
86 | 110 | 1000 | 72 | kW | 3.86
90 | 110 | 1000 | 75 | MBh | 29.5
90 | 110 | 1000 | 75 | S/T | 0.614
90 | 110 | 1000 | 75 | ∆T | 16.8
90 | 110 | 1000 | 75 | LDB | 73.2
90 | 110 | 1000 | 75 | LWB | 67.4
90 | 110 | 1000 | 75 | kW | 3.86
68 | 115 | 1000 | 57 | MBh | 19.1
68 | 115 | 1000 | 57 | S/T | 0.806
68 | 115 | 1000 | 57 | ∆T | 14.3
68 | 115 | 1000 | 57 | LDB | 53.7
68 | 115 | 1000 | 57 | LWB | 49.8
68 | 115 | 1000 | 57 | kW | 2.42
72 | 115 | 1000 | 61 | MBh | 23.2
72 | 115 | 1000 | 61 | S/T | 0.78
72 | 115 | 1000 | 61 | ∆T | 16.8
72 | 115 | 1000 | 61 | LDB | 55.2
72 | 115 | 1000 | 61 | LWB | 52.8
72 | 115 | 1000 | 61 | kW | 3.2
77 | 115 | 1000 | 64 | MBh | 26.3
77 | 115 | 1000 | 64 | S/T | 0.76
77 | 115 | 1000 | 64 | ∆T | 18.5
77 | 115 | 1000 | 64 | LDB | 58.5
77 | 115 | 1000 | 64 | LWB | 55.2
77 | 115 | 1000 | 64 | kW | 3.86
80 | 115 | 1000 | 67 | MBh | 27.5
80 | 115 | 1000 | 67 | S/T | 0.716
80 | 115 | 1000 | 67 | ∆T | 18.2
80 | 115 | 1000 | 67 | LDB | 61.8
80 | 115 | 1000 | 67 | LWB | 58.4
80 | 115 | 1000 | 67 | kW | 4.12
84 | 115 | 1000 | 70 | MBh | 27.5
84 | 115 | 1000 | 70 | S/T | 0.673
84 | 115 | 1000 | 70 | ∆T | 17.1
84 | 115 | 1000 | 70 | LDB | 66.9
84 | 115 | 1000 | 70 | LWB | 62
84 | 115 | 1000 | 70 | kW | 4.12
86 | 115 | 1000 | 72 | MBh | 27.5
86 | 115 | 1000 | 72 | S/T | 0.665
86 | 115 | 1000 | 72 | ∆T | 16.9
86 | 115 | 1000 | 72 | LDB | 69.1
86 | 115 | 1000 | 72 | LWB | 64.4
86 | 115 | 1000 | 72 | kW | 4.12
90 | 115 | 1000 | 75 | MBh | 27.5
90 | 115 | 1000 | 75 | S/T | 0.615
90 | 115 | 1000 | 75 | ∆T | 15.6
90 | 115 | 1000 | 75 | LDB | 74.4
90 | 115 | 1000 | 75 | LWB | 67.9
90 | 115 | 1000 | 75 | kW | 4.12
68 | 118 | 1000 | 57 | MBh | 19.1
68 | 118 | 1000 | 57 | S/T | 0.806
68 | 118 | 1000 | 57 | ∆T | 14.3
68 | 118 | 1000 | 57 | LDB | 53.7
68 | 118 | 1000 | 57 | LWB | 49.8
68 | 118 | 1000 | 57 | kW | 2.6
72 | 118 | 1000 | 61 | MBh | 23.2
72 | 118 | 1000 | 61 | S/T | 0.78
72 | 118 | 1000 | 61 | ∆T | 16.8
72 | 118 | 1000 | 61 | LDB | 55.2
72 | 118 | 1000 | 61 | LWB | 52.8
72 | 118 | 1000 | 61 | kW | 3.44
77 | 118 | 1000 | 64 | MBh | 24.2
77 | 118 | 1000 | 64 | S/T | 0.764
77 | 118 | 1000 | 64 | ∆T | 17.1
77 | 118 | 1000 | 64 | LDB | 59.9
77 | 118 | 1000 | 64 | LWB | 56
77 | 118 | 1000 | 64 | kW | 3.67
80 | 118 | 1000 | 67 | MBh | 24.2
80 | 118 | 1000 | 67 | S/T | 0.715
80 | 118 | 1000 | 67 | ∆T | 16
80 | 118 | 1000 | 67 | LDB | 64
80 | 118 | 1000 | 67 | LWB | 59.5
80 | 118 | 1000 | 67 | kW | 3.67
84 | 118 | 1000 | 70 | MBh | 24.2
84 | 118 | 1000 | 70 | S/T | 0.674
84 | 118 | 1000 | 70 | ∆T | 15.1
84 | 118 | 1000 | 70 | LDB | 68.9
84 | 118 | 1000 | 70 | LWB | 63.1
84 | 118 | 1000 | 70 | kW | 3.67
86 | 118 | 1000 | 72 | MBh | 24.2
86 | 118 | 1000 | 72 | S/T | 0.665
86 | 118 | 1000 | 72 | ∆T | 14.9
86 | 118 | 1000 | 72 | LDB | 71.1
86 | 118 | 1000 | 72 | LWB | 65.4
86 | 118 | 1000 | 72 | kW | 3.67
90 | 118 | 1000 | 75 | MBh | 24.2
90 | 118 | 1000 | 75 | S/T | 0.616
90 | 118 | 1000 | 75 | ∆T | 13.8
90 | 118 | 1000 | 75 | LDB | 76.2
90 | 118 | 1000 | 75 | LWB | 68.9
90 | 118 | 1000 | 75 | kW | 3.67
68 | 122 | 1000 | 57 | MBh | 19.1
68 | 122 | 1000 | 57 | S/T | 0.806
68 | 122 | 1000 | 57 | ∆T | 14.3
68 | 122 | 1000 | 57 | LDB | 53.7
68 | 122 | 1000 | 57 | LWB | 49.8
68 | 122 | 1000 | 57 | kW | 2.85
72 | 122 | 1000 | 61 | MBh | 19.2
72 | 122 | 1000 | 61 | S/T | 0.786
72 | 122 | 1000 | 61 | ∆T | 14
72 | 122 | 1000 | 61 | LDB | 58
72 | 122 | 1000 | 61 | LWB | 54.3
72 | 122 | 1000 | 61 | kW | 2.88
77 | 122 | 1000 | 64 | MBh | 19.2
77 | 122 | 1000 | 64 | S/T | 0.766
77 | 122 | 1000 | 64 | ∆T | 13.6
77 | 122 | 1000 | 64 | LDB | 63.4
77 | 122 | 1000 | 64 | LWB | 57.8
77 | 122 | 1000 | 64 | kW | 2.88
80 | 122 | 1000 | 67 | MBh | 19.2
80 | 122 | 1000 | 67 | S/T | 0.719
80 | 122 | 1000 | 67 | ∆T | 12.8
80 | 122 | 1000 | 67 | LDB | 67.2
80 | 122 | 1000 | 67 | LWB | 61.2
80 | 122 | 1000 | 67 | kW | 2.88
84 | 122 | 1000 | 70 | MBh | 19.2
84 | 122 | 1000 | 70 | S/T | 0.672
84 | 122 | 1000 | 70 | ∆T | 11.9
84 | 122 | 1000 | 70 | LDB | 72.1
84 | 122 | 1000 | 70 | LWB | 64.6
84 | 122 | 1000 | 70 | kW | 2.88
86 | 122 | 1000 | 72 | MBh | 19.2
86 | 122 | 1000 | 72 | S/T | 0.667
86 | 122 | 1000 | 72 | ∆T | 11.9
86 | 122 | 1000 | 72 | LDB | 74.1
86 | 122 | 1000 | 72 | LWB | 66.8
86 | 122 | 1000 | 72 | kW | 2.88
90 | 122 | 1000 | 75 | MBh | 19.2
90 | 122 | 1000 | 75 | S/T | 0.615
90 | 122 | 1000 | 75 | ∆T | 10.9
90 | 122 | 1000 | 75 | LDB | 79.1
90 | 122 | 1000 | 75 | LWB | 70.2
90 | 122 | 1000 | 75 | kW | 2.88

## RZA36AAVJU - FTA36AAVJUD
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1050 | 57 | MBh | 22.7 | 64 | 60 | 61 | 48.6 | 4.17
68 | 23 | 1050 | 57 | S/T | 0.789 | 64 | 60 | 65 | 45 | 3.78
68 | 23 | 1050 | 57 | ∆T | 15.8 | 64 | 60 | 68 | 42.3 | 3.53
68 | 23 | 1050 | 57 | LDB | 52.2 | 64 | 60 | 70 | 40.5 | 3.37
68 | 23 | 1050 | 57 | LWB | 48.7 | 64 | 60 | 72 | 38.7 | 3.23
68 | 23 | 1050 | 57 | kW | 1.03 | 64 | 60 | 75 | 36 | 3.05
72 | 23 | 1050 | 61 | MBh | 27.6 | 60 | 56 | 61 | 48.6 | 4.37
72 | 23 | 1050 | 61 | S/T | 0.746 | 60 | 56 | 65 | 45 | 3.94
72 | 23 | 1050 | 61 | ∆T | 18.2 | 60 | 56 | 68 | 42.3 | 3.66
72 | 23 | 1050 | 61 | LDB | 53.8 | 60 | 56 | 70 | 40.5 | 3.49
72 | 23 | 1050 | 61 | LWB | 51.6 | 60 | 56 | 72 | 38.7 | 3.33
72 | 23 | 1050 | 61 | kW | 1.26 | 60 | 56 | 75 | 36 | 3.13
77 | 23 | 1050 | 64 | MBh | 31.3 | 57 | 53 | 61 | 48.6 | 4.53
77 | 23 | 1050 | 64 | S/T | 0.716 | 57 | 53 | 65 | 45 | 4.07
77 | 23 | 1050 | 64 | ∆T | 19.8 | 57 | 53 | 68 | 42.3 | 3.76
77 | 23 | 1050 | 64 | LDB | 57.2 | 57 | 53 | 70 | 40.5 | 3.58
77 | 23 | 1050 | 64 | LWB | 54 | 57 | 53 | 72 | 38.7 | 3.41
77 | 23 | 1050 | 64 | kW | 1.45 | 57 | 53 | 75 | 36 | 3.19
80 | 23 | 1050 | 67 | MBh | 35 | 54 | 50 | 61 | 48.6 | 4.71
80 | 23 | 1050 | 67 | S/T | 0.677 | 54 | 50 | 65 | 45 | 4.21
80 | 23 | 1050 | 67 | ∆T | 20.9 | 54 | 50 | 68 | 42.3 | 3.89
80 | 23 | 1050 | 67 | LDB | 59.1 | 54 | 50 | 70 | 40.5 | 3.69
80 | 23 | 1050 | 67 | LWB | 56.4 | 54 | 50 | 72 | 38.7 | 3.51
80 | 23 | 1050 | 67 | kW | 1.64 | 54 | 50 | 75 | 36 | 3.27
84 | 23 | 1050 | 70 | MBh | 38.7 | 51 | 47 | 61 | 48.6 | 4.91
84 | 23 | 1050 | 70 | S/T | 0.638 | 51 | 47 | 65 | 45 | 4.38
84 | 23 | 1050 | 70 | ∆T | 21.8 | 51 | 47 | 68 | 42.3 | 4.02
84 | 23 | 1050 | 70 | LDB | 62.2 | 51 | 47 | 70 | 40.5 | 3.81
84 | 23 | 1050 | 70 | LWB | 59 | 51 | 47 | 72 | 38.7 | 3.61
84 | 23 | 1050 | 70 | kW | 1.84 | 51 | 47 | 75 | 36 | 3.35
86 | 23 | 1050 | 72 | MBh | 41.1 | 47 | 43 | 61 | 48.6 | 5.21
86 | 23 | 1050 | 72 | S/T | 0.63 | 47 | 43 | 65 | 45 | 4.62
86 | 23 | 1050 | 72 | ∆T | 22.8 | 47 | 43 | 68 | 42.3 | 4.23
86 | 23 | 1050 | 72 | LDB | 63.2 | 47 | 43 | 70 | 40.5 | 3.99
86 | 23 | 1050 | 72 | LWB | 60.8 | 47 | 43 | 72 | 38.7 | 3.77
86 | 23 | 1050 | 72 | kW | 1.98 | 47 | 43 | 75 | 36 | 3.47
90 | 23 | 1050 | 75 | MBh | 44.8 | 44 | 40 | 61 | 48.6 | 5.47
90 | 23 | 1050 | 75 | S/T | 0.598 | 44 | 40 | 65 | 45 | 4.83
90 | 23 | 1050 | 75 | ∆T | 23.6 | 44 | 40 | 68 | 42.3 | 4.4
90 | 23 | 1050 | 75 | LDB | 66.4 | 44 | 40 | 70 | 40.5 | 4.14
90 | 23 | 1050 | 75 | LWB | 63.5 | 44 | 40 | 72 | 38.7 | 3.9
90 | 23 | 1050 | 75 | kW | 2.19 | 44 | 40 | 75 | 36 | 3.58
68 | 30 | 1050 | 57 | MBh | 22.7 | 39 | 36 | 61 | 48.6 | 5.85
68 | 30 | 1050 | 57 | S/T | 0.789 | 39 | 36 | 65 | 45 | 5.14
68 | 30 | 1050 | 57 | ∆T | 15.8 | 39 | 36 | 68 | 42.3 | 4.67
68 | 30 | 1050 | 57 | LDB | 52.2 | 39 | 36 | 70 | 40.5 | 4.38
68 | 30 | 1050 | 57 | LWB | 48.7 | 39 | 36 | 72 | 38.7 | 4.11
68 | 30 | 1050 | 57 | kW | 1.06 | 39 | 36 | 75 | 36 | 3.75
72 | 30 | 1050 | 61 | MBh | 27.6 | 35 | 32 | 61 | 48.6 | 6.3
72 | 30 | 1050 | 61 | S/T | 0.746 | 35 | 32 | 65 | 45 | 5.51
72 | 30 | 1050 | 61 | ∆T | 18.2 | 35 | 32 | 68 | 42.3 | 4.98
72 | 30 | 1050 | 61 | LDB | 53.8 | 35 | 32 | 70 | 40.5 | 4.65
72 | 30 | 1050 | 61 | LWB | 51.6 | 35 | 32 | 72 | 38.7 | 4.35
72 | 30 | 1050 | 61 | kW | 1.3 | 35 | 32 | 75 | 36 | 3.95
77 | 30 | 1050 | 64 | MBh | 31.3 | 30 | 28 | 61 | 48.6 | 6.82
77 | 30 | 1050 | 64 | S/T | 0.716 | 30 | 28 | 65 | 45 | 5.93
77 | 30 | 1050 | 64 | ∆T | 19.8 | 30 | 28 | 68 | 42.3 | 5.34
77 | 30 | 1050 | 64 | LDB | 57.2 | 30 | 28 | 70 | 40.5 | 4.97
77 | 30 | 1050 | 64 | LWB | 54 | 30 | 28 | 72 | 38.7 | 4.64
77 | 30 | 1050 | 64 | kW | 1.5 | 30 | 28 | 75 | 36 | 4.18
80 | 30 | 1050 | 67 | MBh | 35 | 26 | 24 | 61 | 48.6 | 6.97
80 | 30 | 1050 | 67 | S/T | 0.677 | 26 | 24 | 65 | 45 | 6.43
80 | 30 | 1050 | 67 | ∆T | 20.9 | 26 | 24 | 68 | 42.3 | 5.76
80 | 30 | 1050 | 67 | LDB | 59.1 | 26 | 24 | 70 | 40.5 | 5.35
80 | 30 | 1050 | 67 | LWB | 56.4 | 26 | 24 | 72 | 38.7 | 4.97
80 | 30 | 1050 | 67 | kW | 1.7 | 26 | 24 | 75 | 36 | 4.45
84 | 30 | 1050 | 70 | MBh | 38.7 | 22 | 20 | 61 | 48.5 | 6.64
84 | 30 | 1050 | 70 | S/T | 0.638 | 22 | 20 | 65 | 45 | 7.02
84 | 30 | 1050 | 70 | ∆T | 21.8 | 22 | 20 | 68 | 42.3 | 6.27
84 | 30 | 1050 | 70 | LDB | 62.2 | 22 | 20 | 70 | 40.5 | 5.81
84 | 30 | 1050 | 70 | LWB | 59 | 22 | 20 | 72 | 38.7 | 5.37
84 | 30 | 1050 | 70 | kW | 1.9 | 22 | 20 | 75 | 36 | 4.78
86 | 30 | 1050 | 72 | MBh | 41.1 | 19 | 18 | 61 | 47.2 | 6.47
86 | 30 | 1050 | 72 | S/T | 0.63 | 19 | 18 | 65 | 45 | 6.99
86 | 30 | 1050 | 72 | ∆T | 22.8 | 19 | 18 | 68 | 42.3 | 6.56
86 | 30 | 1050 | 72 | LDB | 63.2 | 19 | 18 | 70 | 40.5 | 6.06
86 | 30 | 1050 | 72 | LWB | 60.8 | 19 | 18 | 72 | 38.7 | 5.6
86 | 30 | 1050 | 72 | kW | 2.05 | 19 | 18 | 75 | 36 | 4.97
90 | 30 | 1050 | 75 | MBh | 44.8 | 17 | 16 | 61 | 45.6 | 6.24
90 | 30 | 1050 | 75 | S/T | 0.598 | 17 | 16 | 65 | 45 | 6.77
90 | 30 | 1050 | 75 | ∆T | 23.6 | 17 | 16 | 68 | 42.3 | 6.95
90 | 30 | 1050 | 75 | LDB | 66.4 | 17 | 16 | 70 | 40.5 | 6.42
90 | 30 | 1050 | 75 | LWB | 63.5 | 17 | 16 | 72 | 38.7 | 5.92
90 | 30 | 1050 | 75 | kW | 2.26 | 17 | 16 | 75 | 36 | 5.23
68 | 40 | 1050 | 57 | MBh | 22.7 | 15 | 14 | 61 | 44.7 | 6.09
68 | 40 | 1050 | 57 | S/T | 0.789 | 15 | 14 | 65 | 44.7 | 6.64
68 | 40 | 1050 | 57 | ∆T | 15.8 | 15 | 14 | 68 | 42.3 | 7.05
68 | 40 | 1050 | 57 | LDB | 52.2 | 15 | 14 | 70 | 40.5 | 6.65
68 | 40 | 1050 | 57 | LWB | 48.7 | 15 | 14 | 72 | 38.7 | 6.13
68 | 40 | 1050 | 57 | kW | 1.11 | 15 | 14 | 75 | 36 | 5.41
72 | 40 | 1050 | 61 | MBh | 27.6 | 13 | 12 | 61 | 43.4 | 5.88
72 | 40 | 1050 | 61 | S/T | 0.746 | 13 | 12 | 65 | 43.4 | 6.45
72 | 40 | 1050 | 61 | ∆T | 18.2 | 13 | 12 | 68 | 42.3 | 6.87
72 | 40 | 1050 | 61 | LDB | 53.8 | 13 | 12 | 70 | 40.5 | 6.99
72 | 40 | 1050 | 61 | LWB | 51.6 | 13 | 12 | 72 | 38.7 | 6.43
72 | 40 | 1050 | 61 | kW | 1.36 | 13 | 12 | 75 | 36 | 5.66
77 | 40 | 1050 | 64 | MBh | 31.3 | 10 | 9 | 61 | 41.2 | 5.5
77 | 40 | 1050 | 64 | S/T | 0.716 | 10 | 9 | 65 | 41.2 | 6.09
77 | 40 | 1050 | 64 | ∆T | 19.8 | 10 | 9 | 68 | 41.2 | 6.53
77 | 40 | 1050 | 64 | LDB | 57.2 | 10 | 9 | 70 | 40.5 | 6.83
77 | 40 | 1050 | 64 | LWB | 54 | 10 | 9 | 72 | 38.7 | 7.03
77 | 40 | 1050 | 64 | kW | 1.57 | 10 | 9 | 75 | 36 | 6.16
80 | 40 | 1050 | 67 | MBh | 35 | 6 | 5 | 61 | 39 | 5.07
80 | 40 | 1050 | 67 | S/T | 0.677 | 6 | 5 | 65 | 39 | 5.69
80 | 40 | 1050 | 67 | ∆T | 20.9 | 6 | 5 | 68 | 39 | 5.71
80 | 40 | 1050 | 67 | LDB | 59.1 | 6 | 5 | 70 | 39 | 5.71
80 | 40 | 1050 | 67 | LWB | 56.4 | 6 | 5 | 72 | 38.7 | 5.71
80 | 40 | 1050 | 67 | kW | 1.78 | 6 | 5 | 75 | 36 | 5.71
84 | 40 | 1050 | 70 | MBh | 38.7 | -2 | -2 | 61 | 32.1 | 4.04
84 | 40 | 1050 | 70 | S/T | 0.638 | -2 | -2 | 65 | 32.1 | 4.74
84 | 40 | 1050 | 70 | ∆T | 21.8 | -2 | -2 | 68 | 32.1 | 4.8
84 | 40 | 1050 | 70 | LDB | 62.2 | -2 | -2 | 70 | 32.1 | 4.8
84 | 40 | 1050 | 70 | LWB | 59 | -2 | -2 | 72 | 32.1 | 4.8
84 | 40 | 1050 | 70 | kW | 2 | -2 | -2 | 75 | 32.1 | 4.8
86 | 40 | 1050 | 72 | MBh | 41.1 | -4 | -4 | 61 | 30.4 | 3.74
86 | 40 | 1050 | 72 | S/T | 0.63 | -4 | -4 | 65 | 30.4 | 4.46
86 | 40 | 1050 | 72 | ∆T | 22.8 | -4 | -4 | 68 | 30.4 | 4.57
86 | 40 | 1050 | 72 | LDB | 63.2 | -4 | -4 | 70 | 30.4 | 4.57
86 | 40 | 1050 | 72 | LWB | 60.8 | -4 | -4 | 72 | 30.4 | 4.57
86 | 40 | 1050 | 72 | kW | 2.15 | -4 | -4 | 75 | 30.4 | 4.57
90 | 40 | 1050 | 75 | MBh | 44.8
90 | 40 | 1050 | 75 | S/T | 0.598
90 | 40 | 1050 | 75 | ∆T | 23.6
90 | 40 | 1050 | 75 | LDB | 66.4
90 | 40 | 1050 | 75 | LWB | 63.5
90 | 40 | 1050 | 75 | kW | 2.37
68 | 50 | 1050 | 57 | MBh | 22.7
68 | 50 | 1050 | 57 | S/T | 0.789
68 | 50 | 1050 | 57 | ∆T | 15.8
68 | 50 | 1050 | 57 | LDB | 52.2
68 | 50 | 1050 | 57 | LWB | 48.7
68 | 50 | 1050 | 57 | kW | 1.16
72 | 50 | 1050 | 61 | MBh | 27.6
72 | 50 | 1050 | 61 | S/T | 0.746
72 | 50 | 1050 | 61 | ∆T | 18.2
72 | 50 | 1050 | 61 | LDB | 53.8
72 | 50 | 1050 | 61 | LWB | 51.6
72 | 50 | 1050 | 61 | kW | 1.43
77 | 50 | 1050 | 64 | MBh | 31.3
77 | 50 | 1050 | 64 | S/T | 0.716
77 | 50 | 1050 | 64 | ∆T | 19.8
77 | 50 | 1050 | 64 | LDB | 57.2
77 | 50 | 1050 | 64 | LWB | 54
77 | 50 | 1050 | 64 | kW | 1.65
80 | 50 | 1050 | 67 | MBh | 35
80 | 50 | 1050 | 67 | S/T | 0.677
80 | 50 | 1050 | 67 | ∆T | 20.9
80 | 50 | 1050 | 67 | LDB | 59.1
80 | 50 | 1050 | 67 | LWB | 56.4
80 | 50 | 1050 | 67 | kW | 1.87
84 | 50 | 1050 | 70 | MBh | 38.7
84 | 50 | 1050 | 70 | S/T | 0.638
84 | 50 | 1050 | 70 | ∆T | 21.8
84 | 50 | 1050 | 70 | LDB | 62.2
84 | 50 | 1050 | 70 | LWB | 59
84 | 50 | 1050 | 70 | kW | 2.1
86 | 50 | 1050 | 72 | MBh | 41.1
86 | 50 | 1050 | 72 | S/T | 0.63
86 | 50 | 1050 | 72 | ∆T | 22.8
86 | 50 | 1050 | 72 | LDB | 63.2
86 | 50 | 1050 | 72 | LWB | 60.8
86 | 50 | 1050 | 72 | kW | 2.26
90 | 50 | 1050 | 75 | MBh | 44.8
90 | 50 | 1050 | 75 | S/T | 0.598
90 | 50 | 1050 | 75 | ∆T | 23.6
90 | 50 | 1050 | 75 | LDB | 66.4
90 | 50 | 1050 | 75 | LWB | 63.5
90 | 50 | 1050 | 75 | kW | 2.49
68 | 54 | 1050 | 57 | MBh | 22.7
68 | 54 | 1050 | 57 | S/T | 0.789
68 | 54 | 1050 | 57 | ∆T | 15.8
68 | 54 | 1050 | 57 | LDB | 52.2
68 | 54 | 1050 | 57 | LWB | 48.7
68 | 54 | 1050 | 57 | kW | 1.18
72 | 54 | 1050 | 61 | MBh | 27.6
72 | 54 | 1050 | 61 | S/T | 0.746
72 | 54 | 1050 | 61 | ∆T | 18.2
72 | 54 | 1050 | 61 | LDB | 53.8
72 | 54 | 1050 | 61 | LWB | 51.6
72 | 54 | 1050 | 61 | kW | 1.46
77 | 54 | 1050 | 64 | MBh | 31.3
77 | 54 | 1050 | 64 | S/T | 0.716
77 | 54 | 1050 | 64 | ∆T | 19.8
77 | 54 | 1050 | 64 | LDB | 57.2
77 | 54 | 1050 | 64 | LWB | 54
77 | 54 | 1050 | 64 | kW | 1.68
80 | 54 | 1050 | 67 | MBh | 35
80 | 54 | 1050 | 67 | S/T | 0.677
80 | 54 | 1050 | 67 | ∆T | 20.9
80 | 54 | 1050 | 67 | LDB | 59.1
80 | 54 | 1050 | 67 | LWB | 56.4
80 | 54 | 1050 | 67 | kW | 1.91
84 | 54 | 1050 | 70 | MBh | 38.7
84 | 54 | 1050 | 70 | S/T | 0.638
84 | 54 | 1050 | 70 | ∆T | 21.8
84 | 54 | 1050 | 70 | LDB | 62.2
84 | 54 | 1050 | 70 | LWB | 59
84 | 54 | 1050 | 70 | kW | 2.15
86 | 54 | 1050 | 72 | MBh | 41.1
86 | 54 | 1050 | 72 | S/T | 0.63
86 | 54 | 1050 | 72 | ∆T | 22.8
86 | 54 | 1050 | 72 | LDB | 63.2
86 | 54 | 1050 | 72 | LWB | 60.8
86 | 54 | 1050 | 72 | kW | 2.3
90 | 54 | 1050 | 75 | MBh | 44.8
90 | 54 | 1050 | 75 | S/T | 0.598
90 | 54 | 1050 | 75 | ∆T | 23.6
90 | 54 | 1050 | 75 | LDB | 66.4
90 | 54 | 1050 | 75 | LWB | 63.5
90 | 54 | 1050 | 75 | kW | 2.54
68 | 58 | 1050 | 57 | MBh | 22.7
68 | 58 | 1050 | 57 | S/T | 0.789
68 | 58 | 1050 | 57 | ∆T | 15.8
68 | 58 | 1050 | 57 | LDB | 52.2
68 | 58 | 1050 | 57 | LWB | 48.7
68 | 58 | 1050 | 57 | kW | 1.2
72 | 58 | 1050 | 61 | MBh | 27.6
72 | 58 | 1050 | 61 | S/T | 0.746
72 | 58 | 1050 | 61 | ∆T | 18.2
72 | 58 | 1050 | 61 | LDB | 53.8
72 | 58 | 1050 | 61 | LWB | 51.6
72 | 58 | 1050 | 61 | kW | 1.49
77 | 58 | 1050 | 64 | MBh | 31.3
77 | 58 | 1050 | 64 | S/T | 0.716
77 | 58 | 1050 | 64 | ∆T | 19.8
77 | 58 | 1050 | 64 | LDB | 57.2
77 | 58 | 1050 | 64 | LWB | 54
77 | 58 | 1050 | 64 | kW | 1.72
80 | 58 | 1050 | 67 | MBh | 35
80 | 58 | 1050 | 67 | S/T | 0.677
80 | 58 | 1050 | 67 | ∆T | 20.9
80 | 58 | 1050 | 67 | LDB | 59.1
80 | 58 | 1050 | 67 | LWB | 56.4
80 | 58 | 1050 | 67 | kW | 1.95
84 | 58 | 1050 | 70 | MBh | 38.7
84 | 58 | 1050 | 70 | S/T | 0.638
84 | 58 | 1050 | 70 | ∆T | 21.8
84 | 58 | 1050 | 70 | LDB | 62.2
84 | 58 | 1050 | 70 | LWB | 59
84 | 58 | 1050 | 70 | kW | 2.19
86 | 58 | 1050 | 72 | MBh | 41.1
86 | 58 | 1050 | 72 | S/T | 0.63
86 | 58 | 1050 | 72 | ∆T | 22.8
86 | 58 | 1050 | 72 | LDB | 63.2
86 | 58 | 1050 | 72 | LWB | 60.8
86 | 58 | 1050 | 72 | kW | 2.35
90 | 58 | 1050 | 75 | MBh | 44.4
90 | 58 | 1050 | 75 | S/T | 0.597
90 | 58 | 1050 | 75 | ∆T | 23.4
90 | 58 | 1050 | 75 | LDB | 66.6
90 | 58 | 1050 | 75 | LWB | 63.6
90 | 58 | 1050 | 75 | kW | 2.55
68 | 62 | 1050 | 57 | MBh | 22.7
68 | 62 | 1050 | 57 | S/T | 0.789
68 | 62 | 1050 | 57 | ∆T | 15.8
68 | 62 | 1050 | 57 | LDB | 52.2
68 | 62 | 1050 | 57 | LWB | 48.7
68 | 62 | 1050 | 57 | kW | 1.23
72 | 62 | 1050 | 61 | MBh | 27.6
72 | 62 | 1050 | 61 | S/T | 0.746
72 | 62 | 1050 | 61 | ∆T | 18.2
72 | 62 | 1050 | 61 | LDB | 53.8
72 | 62 | 1050 | 61 | LWB | 51.6
72 | 62 | 1050 | 61 | kW | 1.52
77 | 62 | 1050 | 64 | MBh | 31.3
77 | 62 | 1050 | 64 | S/T | 0.716
77 | 62 | 1050 | 64 | ∆T | 19.8
77 | 62 | 1050 | 64 | LDB | 57.2
77 | 62 | 1050 | 64 | LWB | 54
77 | 62 | 1050 | 64 | kW | 1.75
80 | 62 | 1050 | 67 | MBh | 35
80 | 62 | 1050 | 67 | S/T | 0.677
80 | 62 | 1050 | 67 | ∆T | 20.9
80 | 62 | 1050 | 67 | LDB | 59.1
80 | 62 | 1050 | 67 | LWB | 56.4
80 | 62 | 1050 | 67 | kW | 1.99
84 | 62 | 1050 | 70 | MBh | 38.7
84 | 62 | 1050 | 70 | S/T | 0.638
84 | 62 | 1050 | 70 | ∆T | 21.8
84 | 62 | 1050 | 70 | LDB | 62.2
84 | 62 | 1050 | 70 | LWB | 59
84 | 62 | 1050 | 70 | kW | 2.24
86 | 62 | 1050 | 72 | MBh | 41.1
86 | 62 | 1050 | 72 | S/T | 0.63
86 | 62 | 1050 | 72 | ∆T | 22.8
86 | 62 | 1050 | 72 | LDB | 63.2
86 | 62 | 1050 | 72 | LWB | 60.8
86 | 62 | 1050 | 72 | kW | 2.41
90 | 62 | 1050 | 75 | MBh | 43.8
90 | 62 | 1050 | 75 | S/T | 0.598
90 | 62 | 1050 | 75 | ∆T | 23.1
90 | 62 | 1050 | 75 | LDB | 66.9
90 | 62 | 1050 | 75 | LWB | 63.8
90 | 62 | 1050 | 75 | kW | 2.61
68 | 66 | 1050 | 57 | MBh | 22.7
68 | 66 | 1050 | 57 | S/T | 0.789
68 | 66 | 1050 | 57 | ∆T | 15.8
68 | 66 | 1050 | 57 | LDB | 52.2
68 | 66 | 1050 | 57 | LWB | 48.7
68 | 66 | 1050 | 57 | kW | 1.25
72 | 66 | 1050 | 61 | MBh | 27.6
72 | 66 | 1050 | 61 | S/T | 0.746
72 | 66 | 1050 | 61 | ∆T | 18.2
72 | 66 | 1050 | 61 | LDB | 53.8
72 | 66 | 1050 | 61 | LWB | 51.6
72 | 66 | 1050 | 61 | kW | 1.55
77 | 66 | 1050 | 64 | MBh | 31.3
77 | 66 | 1050 | 64 | S/T | 0.716
77 | 66 | 1050 | 64 | ∆T | 19.8
77 | 66 | 1050 | 64 | LDB | 57.2
77 | 66 | 1050 | 64 | LWB | 54
77 | 66 | 1050 | 64 | kW | 1.79
80 | 66 | 1050 | 67 | MBh | 35
80 | 66 | 1050 | 67 | S/T | 0.677
80 | 66 | 1050 | 67 | ∆T | 20.9
80 | 66 | 1050 | 67 | LDB | 59.1
80 | 66 | 1050 | 67 | LWB | 56.4
80 | 66 | 1050 | 67 | kW | 2.04
84 | 66 | 1050 | 70 | MBh | 38.7
84 | 66 | 1050 | 70 | S/T | 0.638
84 | 66 | 1050 | 70 | ∆T | 21.8
84 | 66 | 1050 | 70 | LDB | 62.2
84 | 66 | 1050 | 70 | LWB | 59
84 | 66 | 1050 | 70 | kW | 2.37
86 | 66 | 1050 | 72 | MBh | 41.1
86 | 66 | 1050 | 72 | S/T | 0.63
86 | 66 | 1050 | 72 | ∆T | 22.8
86 | 66 | 1050 | 72 | LDB | 63.2
86 | 66 | 1050 | 72 | LWB | 60.8
86 | 66 | 1050 | 72 | kW | 2.6
90 | 66 | 1050 | 75 | MBh | 43.1
90 | 66 | 1050 | 75 | S/T | 0.599
90 | 66 | 1050 | 75 | ∆T | 22.8
90 | 66 | 1050 | 75 | LDB | 67.2
90 | 66 | 1050 | 75 | LWB | 64
90 | 66 | 1050 | 75 | kW | 2.75
68 | 70 | 1050 | 57 | MBh | 22.7
68 | 70 | 1050 | 57 | S/T | 0.789
68 | 70 | 1050 | 57 | ∆T | 15.8
68 | 70 | 1050 | 57 | LDB | 52.2
68 | 70 | 1050 | 57 | LWB | 48.7
68 | 70 | 1050 | 57 | kW | 1.28
72 | 70 | 1050 | 61 | MBh | 27.6
72 | 70 | 1050 | 61 | S/T | 0.746
72 | 70 | 1050 | 61 | ∆T | 18.2
72 | 70 | 1050 | 61 | LDB | 53.8
72 | 70 | 1050 | 61 | LWB | 51.6
72 | 70 | 1050 | 61 | kW | 1.59
77 | 70 | 1050 | 64 | MBh | 31.3
77 | 70 | 1050 | 64 | S/T | 0.716
77 | 70 | 1050 | 64 | ∆T | 19.8
77 | 70 | 1050 | 64 | LDB | 57.2
77 | 70 | 1050 | 64 | LWB | 54
77 | 70 | 1050 | 64 | kW | 1.88
80 | 70 | 1050 | 67 | MBh | 35
80 | 70 | 1050 | 67 | S/T | 0.677
80 | 70 | 1050 | 67 | ∆T | 20.9
80 | 70 | 1050 | 67 | LDB | 59.1
80 | 70 | 1050 | 67 | LWB | 56.4
80 | 70 | 1050 | 67 | kW | 2.21
84 | 70 | 1050 | 70 | MBh | 38.7
84 | 70 | 1050 | 70 | S/T | 0.638
84 | 70 | 1050 | 70 | ∆T | 21.8
84 | 70 | 1050 | 70 | LDB | 62.2
84 | 70 | 1050 | 70 | LWB | 59
84 | 70 | 1050 | 70 | kW | 2.56
86 | 70 | 1050 | 72 | MBh | 41.1
86 | 70 | 1050 | 72 | S/T | 0.63
86 | 70 | 1050 | 72 | ∆T | 22.8
86 | 70 | 1050 | 72 | LDB | 63.2
86 | 70 | 1050 | 72 | LWB | 60.8
86 | 70 | 1050 | 72 | kW | 2.81
90 | 70 | 1050 | 75 | MBh | 42.4
90 | 70 | 1050 | 75 | S/T | 0.599
90 | 70 | 1050 | 75 | ∆T | 22.4
90 | 70 | 1050 | 75 | LDB | 67.6
90 | 70 | 1050 | 75 | LWB | 64.2
90 | 70 | 1050 | 75 | kW | 2.9
68 | 72 | 1050 | 57 | MBh | 22.7
68 | 72 | 1050 | 57 | S/T | 0.789
68 | 72 | 1050 | 57 | ∆T | 15.8
68 | 72 | 1050 | 57 | LDB | 52.2
68 | 72 | 1050 | 57 | LWB | 48.7
68 | 72 | 1050 | 57 | kW | 1.29
72 | 72 | 1050 | 61 | MBh | 27.6
72 | 72 | 1050 | 61 | S/T | 0.746
72 | 72 | 1050 | 61 | ∆T | 18.2
72 | 72 | 1050 | 61 | LDB | 53.8
72 | 72 | 1050 | 61 | LWB | 51.6
72 | 72 | 1050 | 61 | kW | 1.64
77 | 72 | 1050 | 64 | MBh | 31.3
77 | 72 | 1050 | 64 | S/T | 0.716
77 | 72 | 1050 | 64 | ∆T | 19.8
77 | 72 | 1050 | 64 | LDB | 57.2
77 | 72 | 1050 | 64 | LWB | 54
77 | 72 | 1050 | 64 | kW | 1.95
80 | 72 | 1050 | 67 | MBh | 35
80 | 72 | 1050 | 67 | S/T | 0.677
80 | 72 | 1050 | 67 | ∆T | 20.9
80 | 72 | 1050 | 67 | LDB | 59.1
80 | 72 | 1050 | 67 | LWB | 56.4
80 | 72 | 1050 | 67 | kW | 2.29
84 | 72 | 1050 | 70 | MBh | 38.7
84 | 72 | 1050 | 70 | S/T | 0.638
84 | 72 | 1050 | 70 | ∆T | 21.8
84 | 72 | 1050 | 70 | LDB | 62.2
84 | 72 | 1050 | 70 | LWB | 59
84 | 72 | 1050 | 70 | kW | 2.66
86 | 72 | 1050 | 72 | MBh | 41.1
86 | 72 | 1050 | 72 | S/T | 0.63
86 | 72 | 1050 | 72 | ∆T | 22.8
86 | 72 | 1050 | 72 | LDB | 63.2
86 | 72 | 1050 | 72 | LWB | 60.8
86 | 72 | 1050 | 72 | kW | 2.92
90 | 72 | 1050 | 75 | MBh | 42.1
90 | 72 | 1050 | 75 | S/T | 0.599
90 | 72 | 1050 | 75 | ∆T | 22.2
90 | 72 | 1050 | 75 | LDB | 67.8
90 | 72 | 1050 | 75 | LWB | 64.3
90 | 72 | 1050 | 75 | kW | 2.97
68 | 75 | 1050 | 57 | MBh | 22.7
68 | 75 | 1050 | 57 | S/T | 0.789
68 | 75 | 1050 | 57 | ∆T | 15.8
68 | 75 | 1050 | 57 | LDB | 52.2
68 | 75 | 1050 | 57 | LWB | 48.7
68 | 75 | 1050 | 57 | kW | 1.34
72 | 75 | 1050 | 61 | MBh | 27.6
72 | 75 | 1050 | 61 | S/T | 0.746
72 | 75 | 1050 | 61 | ∆T | 18.2
72 | 75 | 1050 | 61 | LDB | 53.8
72 | 75 | 1050 | 61 | LWB | 51.6
72 | 75 | 1050 | 61 | kW | 1.73
77 | 75 | 1050 | 64 | MBh | 31.3
77 | 75 | 1050 | 64 | S/T | 0.716
77 | 75 | 1050 | 64 | ∆T | 19.8
77 | 75 | 1050 | 64 | LDB | 57.2
77 | 75 | 1050 | 64 | LWB | 54
77 | 75 | 1050 | 64 | kW | 2.07
80 | 75 | 1050 | 67 | MBh | 35
80 | 75 | 1050 | 67 | S/T | 0.677
80 | 75 | 1050 | 67 | ∆T | 20.9
80 | 75 | 1050 | 67 | LDB | 59.1
80 | 75 | 1050 | 67 | LWB | 56.4
80 | 75 | 1050 | 67 | kW | 2.43
84 | 75 | 1050 | 70 | MBh | 38.7
84 | 75 | 1050 | 70 | S/T | 0.638
84 | 75 | 1050 | 70 | ∆T | 21.8
84 | 75 | 1050 | 70 | LDB | 62.2
84 | 75 | 1050 | 70 | LWB | 59
84 | 75 | 1050 | 70 | kW | 2.82
86 | 75 | 1050 | 72 | MBh | 40.9
86 | 75 | 1050 | 72 | S/T | 0.631
86 | 75 | 1050 | 72 | ∆T | 22.8
86 | 75 | 1050 | 72 | LDB | 63.2
86 | 75 | 1050 | 72 | LWB | 60.8
86 | 75 | 1050 | 72 | kW | 3.06
90 | 75 | 1050 | 75 | MBh | 41.6
90 | 75 | 1050 | 75 | S/T | 0.599
90 | 75 | 1050 | 75 | ∆T | 22
90 | 75 | 1050 | 75 | LDB | 68
90 | 75 | 1050 | 75 | LWB | 64.5
90 | 75 | 1050 | 75 | kW | 3.08
68 | 79 | 1050 | 57 | MBh | 22.7
68 | 79 | 1050 | 57 | S/T | 0.789
68 | 79 | 1050 | 57 | ∆T | 15.8
68 | 79 | 1050 | 57 | LDB | 52.2
68 | 79 | 1050 | 57 | LWB | 48.7
68 | 79 | 1050 | 57 | kW | 1.44
72 | 79 | 1050 | 61 | MBh | 27.6
72 | 79 | 1050 | 61 | S/T | 0.746
72 | 79 | 1050 | 61 | ∆T | 18.2
72 | 79 | 1050 | 61 | LDB | 53.8
72 | 79 | 1050 | 61 | LWB | 51.6
72 | 79 | 1050 | 61 | kW | 1.87
77 | 79 | 1050 | 64 | MBh | 31.3
77 | 79 | 1050 | 64 | S/T | 0.716
77 | 79 | 1050 | 64 | ∆T | 19.8
77 | 79 | 1050 | 64 | LDB | 57.2
77 | 79 | 1050 | 64 | LWB | 54
77 | 79 | 1050 | 64 | kW | 2.23
80 | 79 | 1050 | 67 | MBh | 35
80 | 79 | 1050 | 67 | S/T | 0.677
80 | 79 | 1050 | 67 | ∆T | 20.9
80 | 79 | 1050 | 67 | LDB | 59.1
80 | 79 | 1050 | 67 | LWB | 56.4
80 | 79 | 1050 | 67 | kW | 2.62
84 | 79 | 1050 | 70 | MBh | 38.7
84 | 79 | 1050 | 70 | S/T | 0.638
84 | 79 | 1050 | 70 | ∆T | 21.8
84 | 79 | 1050 | 70 | LDB | 62.2
84 | 79 | 1050 | 70 | LWB | 59
84 | 79 | 1050 | 70 | kW | 3.04
86 | 79 | 1050 | 72 | MBh | 40.2
86 | 79 | 1050 | 72 | S/T | 0.632
86 | 79 | 1050 | 72 | ∆T | 22.4
86 | 79 | 1050 | 72 | LDB | 63.6
86 | 79 | 1050 | 72 | LWB | 61.1
86 | 79 | 1050 | 72 | kW | 3.21
90 | 79 | 1050 | 75 | MBh | 41
90 | 79 | 1050 | 75 | S/T | 0.598
90 | 79 | 1050 | 75 | ∆T | 21.6
90 | 79 | 1050 | 75 | LDB | 68.4
90 | 79 | 1050 | 75 | LWB | 64.6
90 | 79 | 1050 | 75 | kW | 3.23
68 | 83 | 1050 | 57 | MBh | 22.7
68 | 83 | 1050 | 57 | S/T | 0.789
68 | 83 | 1050 | 57 | ∆T | 15.8
68 | 83 | 1050 | 57 | LDB | 52.2
68 | 83 | 1050 | 57 | LWB | 48.7
68 | 83 | 1050 | 57 | kW | 1.54
72 | 83 | 1050 | 61 | MBh | 27.6
72 | 83 | 1050 | 61 | S/T | 0.746
72 | 83 | 1050 | 61 | ∆T | 18.2
72 | 83 | 1050 | 61 | LDB | 53.8
72 | 83 | 1050 | 61 | LWB | 51.6
72 | 83 | 1050 | 61 | kW | 2.01
77 | 83 | 1050 | 64 | MBh | 31.3
77 | 83 | 1050 | 64 | S/T | 0.716
77 | 83 | 1050 | 64 | ∆T | 19.8
77 | 83 | 1050 | 64 | LDB | 57.2
77 | 83 | 1050 | 64 | LWB | 54
77 | 83 | 1050 | 64 | kW | 2.39
80 | 83 | 1050 | 67 | MBh | 35
80 | 83 | 1050 | 67 | S/T | 0.677
80 | 83 | 1050 | 67 | ∆T | 20.9
80 | 83 | 1050 | 67 | LDB | 59.1
80 | 83 | 1050 | 67 | LWB | 56.4
80 | 83 | 1050 | 67 | kW | 2.82
84 | 83 | 1050 | 70 | MBh | 38.7
84 | 83 | 1050 | 70 | S/T | 0.638
84 | 83 | 1050 | 70 | ∆T | 21.8
84 | 83 | 1050 | 70 | LDB | 62.2
84 | 83 | 1050 | 70 | LWB | 59
84 | 83 | 1050 | 70 | kW | 3.28
86 | 83 | 1050 | 72 | MBh | 39.6
86 | 83 | 1050 | 72 | S/T | 0.631
86 | 83 | 1050 | 72 | ∆T | 22
86 | 83 | 1050 | 72 | LDB | 64
86 | 83 | 1050 | 72 | LWB | 61.2
86 | 83 | 1050 | 72 | kW | 3.36
90 | 83 | 1050 | 75 | MBh | 40.3
90 | 83 | 1050 | 75 | S/T | 0.598
90 | 83 | 1050 | 75 | ∆T | 21.3
90 | 83 | 1050 | 75 | LDB | 68.7
90 | 83 | 1050 | 75 | LWB | 64.8
90 | 83 | 1050 | 75 | kW | 3.38
68 | 87 | 1050 | 57 | MBh | 22.7
68 | 87 | 1050 | 57 | S/T | 0.789
68 | 87 | 1050 | 57 | ∆T | 15.8
68 | 87 | 1050 | 57 | LDB | 52.2
68 | 87 | 1050 | 57 | LWB | 48.7
68 | 87 | 1050 | 57 | kW | 1.65
72 | 87 | 1050 | 61 | MBh | 27.6
72 | 87 | 1050 | 61 | S/T | 0.746
72 | 87 | 1050 | 61 | ∆T | 18.2
72 | 87 | 1050 | 61 | LDB | 53.8
72 | 87 | 1050 | 61 | LWB | 51.6
72 | 87 | 1050 | 61 | kW | 2.15
77 | 87 | 1050 | 64 | MBh | 31.3
77 | 87 | 1050 | 64 | S/T | 0.716
77 | 87 | 1050 | 64 | ∆T | 19.8
77 | 87 | 1050 | 64 | LDB | 57.2
77 | 87 | 1050 | 64 | LWB | 54
77 | 87 | 1050 | 64 | kW | 2.57
80 | 87 | 1050 | 67 | MBh | 35
80 | 87 | 1050 | 67 | S/T | 0.677
80 | 87 | 1050 | 67 | ∆T | 20.9
80 | 87 | 1050 | 67 | LDB | 59.1
80 | 87 | 1050 | 67 | LWB | 56.4
80 | 87 | 1050 | 67 | kW | 3.03
84 | 87 | 1050 | 70 | MBh | 38.4
84 | 87 | 1050 | 70 | S/T | 0.641
84 | 87 | 1050 | 70 | ∆T | 21.7
84 | 87 | 1050 | 70 | LDB | 62.3
84 | 87 | 1050 | 70 | LWB | 59.1
84 | 87 | 1050 | 70 | kW | 3.49
86 | 87 | 1050 | 72 | MBh | 38.9
86 | 87 | 1050 | 72 | S/T | 0.632
86 | 87 | 1050 | 72 | ∆T | 21.7
86 | 87 | 1050 | 72 | LDB | 64.3
86 | 87 | 1050 | 72 | LWB | 61.4
86 | 87 | 1050 | 72 | kW | 3.5
90 | 87 | 1050 | 75 | MBh | 39.7
90 | 87 | 1050 | 75 | S/T | 0.597
90 | 87 | 1050 | 75 | ∆T | 20.9
90 | 87 | 1050 | 75 | LDB | 69.1
90 | 87 | 1050 | 75 | LWB | 65
90 | 87 | 1050 | 75 | kW | 3.53
68 | 91 | 1050 | 57 | MBh | 22.7
68 | 91 | 1050 | 57 | S/T | 0.789
68 | 91 | 1050 | 57 | ∆T | 15.8
68 | 91 | 1050 | 57 | LDB | 52.2
68 | 91 | 1050 | 57 | LWB | 48.7
68 | 91 | 1050 | 57 | kW | 1.77
72 | 91 | 1050 | 61 | MBh | 27.6
72 | 91 | 1050 | 61 | S/T | 0.746
72 | 91 | 1050 | 61 | ∆T | 18.2
72 | 91 | 1050 | 61 | LDB | 53.8
72 | 91 | 1050 | 61 | LWB | 51.6
72 | 91 | 1050 | 61 | kW | 2.31
77 | 91 | 1050 | 64 | MBh | 31.3
77 | 91 | 1050 | 64 | S/T | 0.716
77 | 91 | 1050 | 64 | ∆T | 19.8
77 | 91 | 1050 | 64 | LDB | 57.2
77 | 91 | 1050 | 64 | LWB | 54
77 | 91 | 1050 | 64 | kW | 2.76
80 | 91 | 1050 | 67 | MBh | 35
80 | 91 | 1050 | 67 | S/T | 0.677
80 | 91 | 1050 | 67 | ∆T | 20.9
80 | 91 | 1050 | 67 | LDB | 59.1
80 | 91 | 1050 | 67 | LWB | 56.4
80 | 91 | 1050 | 67 | kW | 3.26
84 | 91 | 1050 | 70 | MBh | 37.8
84 | 91 | 1050 | 70 | S/T | 0.638
84 | 91 | 1050 | 70 | ∆T | 21.3
84 | 91 | 1050 | 70 | LDB | 62.7
84 | 91 | 1050 | 70 | LWB | 59.3
84 | 91 | 1050 | 70 | kW | 3.64
86 | 91 | 1050 | 72 | MBh | 38.3
86 | 91 | 1050 | 72 | S/T | 0.629
86 | 91 | 1050 | 72 | ∆T | 21.3
86 | 91 | 1050 | 72 | LDB | 64.7
86 | 91 | 1050 | 72 | LWB | 61.6
86 | 91 | 1050 | 72 | kW | 3.65
90 | 91 | 1050 | 75 | MBh | 39
90 | 91 | 1050 | 75 | S/T | 0.597
90 | 91 | 1050 | 75 | ∆T | 20.5
90 | 91 | 1050 | 75 | LDB | 69.5
90 | 91 | 1050 | 75 | LWB | 65.2
90 | 91 | 1050 | 75 | kW | 3.68
68 | 93 | 1050 | 57 | MBh | 22.7
68 | 93 | 1050 | 57 | S/T | 0.789
68 | 93 | 1050 | 57 | ∆T | 15.8
68 | 93 | 1050 | 57 | LDB | 52.2
68 | 93 | 1050 | 57 | LWB | 48.7
68 | 93 | 1050 | 57 | kW | 1.83
72 | 93 | 1050 | 61 | MBh | 27.6
72 | 93 | 1050 | 61 | S/T | 0.746
72 | 93 | 1050 | 61 | ∆T | 18.2
72 | 93 | 1050 | 61 | LDB | 53.8
72 | 93 | 1050 | 61 | LWB | 51.6
72 | 93 | 1050 | 61 | kW | 2.39
77 | 93 | 1050 | 64 | MBh | 31.3
77 | 93 | 1050 | 64 | S/T | 0.716
77 | 93 | 1050 | 64 | ∆T | 19.8
77 | 93 | 1050 | 64 | LDB | 57.2
77 | 93 | 1050 | 64 | LWB | 54
77 | 93 | 1050 | 64 | kW | 2.86
80 | 93 | 1050 | 67 | MBh | 35
80 | 93 | 1050 | 67 | S/T | 0.677
80 | 93 | 1050 | 67 | ∆T | 20.9
80 | 93 | 1050 | 67 | LDB | 59.1
80 | 93 | 1050 | 67 | LWB | 56.4
80 | 93 | 1050 | 67 | kW | 3.38
84 | 93 | 1050 | 70 | MBh | 37.5
84 | 93 | 1050 | 70 | S/T | 0.637
84 | 93 | 1050 | 70 | ∆T | 21.1
84 | 93 | 1050 | 70 | LDB | 62.9
84 | 93 | 1050 | 70 | LWB | 59.4
84 | 93 | 1050 | 70 | kW | 3.71
86 | 93 | 1050 | 72 | MBh | 37.9
86 | 93 | 1050 | 72 | S/T | 0.631
86 | 93 | 1050 | 72 | ∆T | 21.1
86 | 93 | 1050 | 72 | LDB | 64.9
86 | 93 | 1050 | 72 | LWB | 61.8
86 | 93 | 1050 | 72 | kW | 3.73
90 | 93 | 1050 | 75 | MBh | 38.7
90 | 93 | 1050 | 75 | S/T | 0.597
90 | 93 | 1050 | 75 | ∆T | 20.4
90 | 93 | 1050 | 75 | LDB | 69.6
90 | 93 | 1050 | 75 | LWB | 65.3
90 | 93 | 1050 | 75 | kW | 3.75
68 | 95 | 1050 | 57 | MBh | 22.7
68 | 95 | 1050 | 57 | S/T | 0.789
68 | 95 | 1050 | 57 | ∆T | 15.8
68 | 95 | 1050 | 57 | LDB | 52.2
68 | 95 | 1050 | 57 | LWB | 48.7
68 | 95 | 1050 | 57 | kW | 1.89
72 | 95 | 1050 | 61 | MBh | 27.6
72 | 95 | 1050 | 61 | S/T | 0.746
72 | 95 | 1050 | 61 | ∆T | 18.2
72 | 95 | 1050 | 61 | LDB | 53.8
72 | 95 | 1050 | 61 | LWB | 51.6
72 | 95 | 1050 | 61 | kW | 2.47
77 | 95 | 1050 | 64 | MBh | 31.3
77 | 95 | 1050 | 64 | S/T | 0.716
77 | 95 | 1050 | 64 | ∆T | 19.8
77 | 95 | 1050 | 64 | LDB | 57.2
77 | 95 | 1050 | 64 | LWB | 54
77 | 95 | 1050 | 64 | kW | 2.96
80 | 95 | 1050 | 67 | MBh | 35
80 | 95 | 1050 | 67 | S/T | 0.677
80 | 95 | 1050 | 67 | ∆T | 20.9
80 | 95 | 1050 | 67 | LDB | 59.1
80 | 95 | 1050 | 67 | LWB | 56.4
80 | 95 | 1050 | 67 | kW | 3.5
84 | 95 | 1050 | 70 | MBh | 37.1
84 | 95 | 1050 | 70 | S/T | 0.639
84 | 95 | 1050 | 70 | ∆T | 20.9
84 | 95 | 1050 | 70 | LDB | 63.1
84 | 95 | 1050 | 70 | LWB | 59.5
84 | 95 | 1050 | 70 | kW | 3.78
86 | 95 | 1050 | 72 | MBh | 37.6
86 | 95 | 1050 | 72 | S/T | 0.63
86 | 95 | 1050 | 72 | ∆T | 20.9
86 | 95 | 1050 | 72 | LDB | 65.1
86 | 95 | 1050 | 72 | LWB | 61.8
86 | 95 | 1050 | 72 | kW | 3.8
90 | 95 | 1050 | 75 | MBh | 38.3
90 | 95 | 1050 | 75 | S/T | 0.598
90 | 95 | 1050 | 75 | ∆T | 20.2
90 | 95 | 1050 | 75 | LDB | 69.8
90 | 95 | 1050 | 75 | LWB | 65.4
90 | 95 | 1050 | 75 | kW | 3.83
68 | 99 | 1050 | 57 | MBh | 22.7
68 | 99 | 1050 | 57 | S/T | 0.789
68 | 99 | 1050 | 57 | ∆T | 15.8
68 | 99 | 1050 | 57 | LDB | 52.2
68 | 99 | 1050 | 57 | LWB | 48.7
68 | 99 | 1050 | 57 | kW | 2.02
72 | 99 | 1050 | 61 | MBh | 27.6
72 | 99 | 1050 | 61 | S/T | 0.746
72 | 99 | 1050 | 61 | ∆T | 18.2
72 | 99 | 1050 | 61 | LDB | 53.8
72 | 99 | 1050 | 61 | LWB | 51.6
72 | 99 | 1050 | 61 | kW | 2.65
77 | 99 | 1050 | 64 | MBh | 31.3
77 | 99 | 1050 | 64 | S/T | 0.716
77 | 99 | 1050 | 64 | ∆T | 19.8
77 | 99 | 1050 | 64 | LDB | 57.2
77 | 99 | 1050 | 64 | LWB | 54
77 | 99 | 1050 | 64 | kW | 3.18
80 | 99 | 1050 | 67 | MBh | 35
80 | 99 | 1050 | 67 | S/T | 0.677
80 | 99 | 1050 | 67 | ∆T | 20.9
80 | 99 | 1050 | 67 | LDB | 59.1
80 | 99 | 1050 | 67 | LWB | 56.4
80 | 99 | 1050 | 67 | kW | 3.76
84 | 99 | 1050 | 70 | MBh | 36.5
84 | 99 | 1050 | 70 | S/T | 0.641
84 | 99 | 1050 | 70 | ∆T | 20.6
84 | 99 | 1050 | 70 | LDB | 63.4
84 | 99 | 1050 | 70 | LWB | 59.7
84 | 99 | 1050 | 70 | kW | 3.93
86 | 99 | 1050 | 72 | MBh | 37
86 | 99 | 1050 | 72 | S/T | 0.632
86 | 99 | 1050 | 72 | ∆T | 20.6
86 | 99 | 1050 | 72 | LDB | 65.4
86 | 99 | 1050 | 72 | LWB | 62
86 | 99 | 1050 | 72 | kW | 3.95
90 | 99 | 1050 | 75 | MBh | 37.7
90 | 99 | 1050 | 75 | S/T | 0.599
90 | 99 | 1050 | 75 | ∆T | 19.9
90 | 99 | 1050 | 75 | LDB | 70.1
90 | 99 | 1050 | 75 | LWB | 65.6
90 | 99 | 1050 | 75 | kW | 3.98
68 | 103 | 1050 | 57 | MBh | 22.7
68 | 103 | 1050 | 57 | S/T | 0.789
68 | 103 | 1050 | 57 | ∆T | 15.8
68 | 103 | 1050 | 57 | LDB | 52.2
68 | 103 | 1050 | 57 | LWB | 48.7
68 | 103 | 1050 | 57 | kW | 2.16
72 | 103 | 1050 | 61 | MBh | 27.6
72 | 103 | 1050 | 61 | S/T | 0.746
72 | 103 | 1050 | 61 | ∆T | 18.2
72 | 103 | 1050 | 61 | LDB | 53.8
72 | 103 | 1050 | 61 | LWB | 51.6
72 | 103 | 1050 | 61 | kW | 2.84
77 | 103 | 1050 | 64 | MBh | 31.3
77 | 103 | 1050 | 64 | S/T | 0.716
77 | 103 | 1050 | 64 | ∆T | 19.8
77 | 103 | 1050 | 64 | LDB | 57.2
77 | 103 | 1050 | 64 | LWB | 54
77 | 103 | 1050 | 64 | kW | 3.41
80 | 103 | 1050 | 67 | MBh | 35
80 | 103 | 1050 | 67 | S/T | 0.677
80 | 103 | 1050 | 67 | ∆T | 20.9
80 | 103 | 1050 | 67 | LDB | 59.1
80 | 103 | 1050 | 67 | LWB | 56.4
80 | 103 | 1050 | 67 | kW | 4.03
84 | 103 | 1050 | 70 | MBh | 35.8
84 | 103 | 1050 | 70 | S/T | 0.642
84 | 103 | 1050 | 70 | ∆T | 20.3
84 | 103 | 1050 | 70 | LDB | 63.7
84 | 103 | 1050 | 70 | LWB | 59.9
84 | 103 | 1050 | 70 | kW | 4.08
86 | 103 | 1050 | 72 | MBh | 36.3
86 | 103 | 1050 | 72 | S/T | 0.634
86 | 103 | 1050 | 72 | ∆T | 20.3
86 | 103 | 1050 | 72 | LDB | 65.7
86 | 103 | 1050 | 72 | LWB | 62.2
86 | 103 | 1050 | 72 | kW | 4.1
90 | 103 | 1050 | 75 | MBh | 37
90 | 103 | 1050 | 75 | S/T | 0.603
90 | 103 | 1050 | 75 | ∆T | 19.7
90 | 103 | 1050 | 75 | LDB | 70.3
90 | 103 | 1050 | 75 | LWB | 65.7
90 | 103 | 1050 | 75 | kW | 4.13
68 | 106 | 1050 | 57 | MBh | 22.7
68 | 106 | 1050 | 57 | S/T | 0.789
68 | 106 | 1050 | 57 | ∆T | 15.8
68 | 106 | 1050 | 57 | LDB | 52.2
68 | 106 | 1050 | 57 | LWB | 48.7
68 | 106 | 1050 | 57 | kW | 2.27
72 | 106 | 1050 | 61 | MBh | 27.6
72 | 106 | 1050 | 61 | S/T | 0.746
72 | 106 | 1050 | 61 | ∆T | 18.2
72 | 106 | 1050 | 61 | LDB | 53.8
72 | 106 | 1050 | 61 | LWB | 51.6
72 | 106 | 1050 | 61 | kW | 2.99
77 | 106 | 1050 | 64 | MBh | 31.3
77 | 106 | 1050 | 64 | S/T | 0.716
77 | 106 | 1050 | 64 | ∆T | 19.8
77 | 106 | 1050 | 64 | LDB | 57.2
77 | 106 | 1050 | 64 | LWB | 54
77 | 106 | 1050 | 64 | kW | 3.59
80 | 106 | 1050 | 67 | MBh | 34.6
80 | 106 | 1050 | 67 | S/T | 0.679
80 | 106 | 1050 | 67 | ∆T | 20.7
80 | 106 | 1050 | 67 | LDB | 59.3
80 | 106 | 1050 | 67 | LWB | 56.5
80 | 106 | 1050 | 67 | kW | 4.16
84 | 106 | 1050 | 70 | MBh | 35.3
84 | 106 | 1050 | 70 | S/T | 0.643
84 | 106 | 1050 | 70 | ∆T | 20
84 | 106 | 1050 | 70 | LDB | 64
84 | 106 | 1050 | 70 | LWB | 60.1
84 | 106 | 1050 | 70 | kW | 4.19
86 | 106 | 1050 | 72 | MBh | 35.8
86 | 106 | 1050 | 72 | S/T | 0.634
86 | 106 | 1050 | 72 | ∆T | 20
86 | 106 | 1050 | 72 | LDB | 66
86 | 106 | 1050 | 72 | LWB | 62.4
86 | 106 | 1050 | 72 | kW | 4.22
90 | 106 | 1050 | 75 | MBh | 36.4
90 | 106 | 1050 | 75 | S/T | 0.602
90 | 106 | 1050 | 75 | ∆T | 19.3
90 | 106 | 1050 | 75 | LDB | 70.7
90 | 106 | 1050 | 75 | LWB | 65.9
90 | 106 | 1050 | 75 | kW | 4.24
68 | 110 | 1050 | 57 | MBh | 22.7
68 | 110 | 1050 | 57 | S/T | 0.789
68 | 110 | 1050 | 57 | ∆T | 15.8
68 | 110 | 1050 | 57 | LDB | 52.2
68 | 110 | 1050 | 57 | LWB | 48.7
68 | 110 | 1050 | 57 | kW | 2.43
72 | 110 | 1050 | 61 | MBh | 27.6
72 | 110 | 1050 | 61 | S/T | 0.746
72 | 110 | 1050 | 61 | ∆T | 18.2
72 | 110 | 1050 | 61 | LDB | 53.8
72 | 110 | 1050 | 61 | LWB | 51.6
72 | 110 | 1050 | 61 | kW | 3.2
77 | 110 | 1050 | 64 | MBh | 31.3
77 | 110 | 1050 | 64 | S/T | 0.716
77 | 110 | 1050 | 64 | ∆T | 19.8
77 | 110 | 1050 | 64 | LDB | 57.2
77 | 110 | 1050 | 64 | LWB | 54
77 | 110 | 1050 | 64 | kW | 3.85
80 | 110 | 1050 | 67 | MBh | 33.9
80 | 110 | 1050 | 67 | S/T | 0.681
80 | 110 | 1050 | 67 | ∆T | 20.4
80 | 110 | 1050 | 67 | LDB | 59.6
80 | 110 | 1050 | 67 | LWB | 56.8
80 | 110 | 1050 | 67 | kW | 4.31
84 | 110 | 1050 | 70 | MBh | 34.6
84 | 110 | 1050 | 70 | S/T | 0.642
84 | 110 | 1050 | 70 | ∆T | 19.6
84 | 110 | 1050 | 70 | LDB | 64.4
84 | 110 | 1050 | 70 | LWB | 60.3
84 | 110 | 1050 | 70 | kW | 4.34
86 | 110 | 1050 | 72 | MBh | 34.6
86 | 110 | 1050 | 72 | S/T | 0.633
86 | 110 | 1050 | 72 | ∆T | 19.3
86 | 110 | 1050 | 72 | LDB | 66.7
86 | 110 | 1050 | 72 | LWB | 62.7
86 | 110 | 1050 | 72 | kW | 4.34
90 | 110 | 1050 | 75 | MBh | 34.6
90 | 110 | 1050 | 75 | S/T | 0.601
90 | 110 | 1050 | 75 | ∆T | 18.3
90 | 110 | 1050 | 75 | LDB | 71.7
90 | 110 | 1050 | 75 | LWB | 66.4
90 | 110 | 1050 | 75 | kW | 4.34
68 | 115 | 1050 | 57 | MBh | 22.7
68 | 115 | 1050 | 57 | S/T | 0.789
68 | 115 | 1050 | 57 | ∆T | 15.8
68 | 115 | 1050 | 57 | LDB | 52.2
68 | 115 | 1050 | 57 | LWB | 48.7
68 | 115 | 1050 | 57 | kW | 2.84
72 | 115 | 1050 | 61 | MBh | 27.6
72 | 115 | 1050 | 61 | S/T | 0.746
72 | 115 | 1050 | 61 | ∆T | 18.2
72 | 115 | 1050 | 61 | LDB | 53.8
72 | 115 | 1050 | 61 | LWB | 51.6
72 | 115 | 1050 | 61 | kW | 3.76
77 | 115 | 1050 | 64 | MBh | 31.2
77 | 115 | 1050 | 64 | S/T | 0.718
77 | 115 | 1050 | 64 | ∆T | 19.8
77 | 115 | 1050 | 64 | LDB | 57.2
77 | 115 | 1050 | 64 | LWB | 54
77 | 115 | 1050 | 64 | kW | 4.51
80 | 115 | 1050 | 67 | MBh | 31.2
80 | 115 | 1050 | 67 | S/T | 0.679
80 | 115 | 1050 | 67 | ∆T | 18.7
80 | 115 | 1050 | 67 | LDB | 61.3
80 | 115 | 1050 | 67 | LWB | 57.7
80 | 115 | 1050 | 67 | kW | 4.51
84 | 115 | 1050 | 70 | MBh | 31.2
84 | 115 | 1050 | 70 | S/T | 0.641
84 | 115 | 1050 | 70 | ∆T | 17.6
84 | 115 | 1050 | 70 | LDB | 66.4
84 | 115 | 1050 | 70 | LWB | 61.3
84 | 115 | 1050 | 70 | kW | 4.51
86 | 115 | 1050 | 72 | MBh | 31.2
86 | 115 | 1050 | 72 | S/T | 0.635
86 | 115 | 1050 | 72 | ∆T | 17.5
86 | 115 | 1050 | 72 | LDB | 68.5
86 | 115 | 1050 | 72 | LWB | 63.7
86 | 115 | 1050 | 72 | kW | 4.51
90 | 115 | 1050 | 75 | MBh | 31.2
90 | 115 | 1050 | 75 | S/T | 0.603
90 | 115 | 1050 | 75 | ∆T | 16.6
90 | 115 | 1050 | 75 | LDB | 73.4
90 | 115 | 1050 | 75 | LWB | 67.3
90 | 115 | 1050 | 75 | kW | 4.51
68 | 118 | 1050 | 57 | MBh | 22.7
68 | 118 | 1050 | 57 | S/T | 0.789
68 | 118 | 1050 | 57 | ∆T | 15.8
68 | 118 | 1050 | 57 | LDB | 52.2
68 | 118 | 1050 | 57 | LWB | 48.7
68 | 118 | 1050 | 57 | kW | 3.17
72 | 118 | 1050 | 61 | MBh | 26.9
72 | 118 | 1050 | 61 | S/T | 0.751
72 | 118 | 1050 | 61 | ∆T | 17.8
72 | 118 | 1050 | 61 | LDB | 54.2
72 | 118 | 1050 | 61 | LWB | 51.9
72 | 118 | 1050 | 61 | kW | 4.03
77 | 118 | 1050 | 64 | MBh | 26.9
77 | 118 | 1050 | 64 | S/T | 0.721
77 | 118 | 1050 | 64 | ∆T | 17.1
77 | 118 | 1050 | 64 | LDB | 59.9
77 | 118 | 1050 | 64 | LWB | 55.5
77 | 118 | 1050 | 64 | kW | 4.03
80 | 118 | 1050 | 67 | MBh | 26.9
80 | 118 | 1050 | 67 | S/T | 0.68
80 | 118 | 1050 | 67 | ∆T | 16.1
80 | 118 | 1050 | 67 | LDB | 63.9
80 | 118 | 1050 | 67 | LWB | 59.1
80 | 118 | 1050 | 67 | kW | 4.03
84 | 118 | 1050 | 70 | MBh | 26.9
84 | 118 | 1050 | 70 | S/T | 0.643
84 | 118 | 1050 | 70 | ∆T | 15.3
84 | 118 | 1050 | 70 | LDB | 68.7
84 | 118 | 1050 | 70 | LWB | 62.6
84 | 118 | 1050 | 70 | kW | 4.03
86 | 118 | 1050 | 72 | MBh | 26.9
86 | 118 | 1050 | 72 | S/T | 0.636
86 | 118 | 1050 | 72 | ∆T | 15.1
86 | 118 | 1050 | 72 | LDB | 70.9
86 | 118 | 1050 | 72 | LWB | 65
86 | 118 | 1050 | 72 | kW | 4.03
90 | 118 | 1050 | 75 | MBh | 26.9
90 | 118 | 1050 | 75 | S/T | 0.602
90 | 118 | 1050 | 75 | ∆T | 14.3
90 | 118 | 1050 | 75 | LDB | 75.7
90 | 118 | 1050 | 75 | LWB | 68.5
90 | 118 | 1050 | 75 | kW | 4.03
68 | 122 | 1050 | 57 | MBh | 21.2
68 | 122 | 1050 | 57 | S/T | 0.792
68 | 122 | 1050 | 57 | ∆T | 14.8
68 | 122 | 1050 | 57 | LDB | 53.2
68 | 122 | 1050 | 57 | LWB | 49.3
68 | 122 | 1050 | 57 | kW | 3.3
72 | 122 | 1050 | 61 | MBh | 21.2
72 | 122 | 1050 | 61 | S/T | 0.75
72 | 122 | 1050 | 61 | ∆T | 14
72 | 122 | 1050 | 61 | LDB | 58
72 | 122 | 1050 | 61 | LWB | 54
72 | 122 | 1050 | 61 | kW | 3.3
77 | 122 | 1050 | 64 | MBh | 21.2
77 | 122 | 1050 | 64 | S/T | 0.722
77 | 122 | 1050 | 64 | ∆T | 13.5
77 | 122 | 1050 | 64 | LDB | 63.5
77 | 122 | 1050 | 64 | LWB | 57.4
77 | 122 | 1050 | 64 | kW | 3.3
80 | 122 | 1050 | 67 | MBh | 21.2
80 | 122 | 1050 | 67 | S/T | 0.684
80 | 122 | 1050 | 67 | ∆T | 12.8
80 | 122 | 1050 | 67 | LDB | 67.2
80 | 122 | 1050 | 67 | LWB | 60.9
80 | 122 | 1050 | 67 | kW | 3.3
84 | 122 | 1050 | 70 | MBh | 21.2
84 | 122 | 1050 | 70 | S/T | 0.646
84 | 122 | 1050 | 70 | ∆T | 12.1
84 | 122 | 1050 | 70 | LDB | 71.9
84 | 122 | 1050 | 70 | LWB | 64.3
84 | 122 | 1050 | 70 | kW | 3.3
86 | 122 | 1050 | 72 | MBh | 21.2
86 | 122 | 1050 | 72 | S/T | 0.637
86 | 122 | 1050 | 72 | ∆T | 11.9
86 | 122 | 1050 | 72 | LDB | 74.1
86 | 122 | 1050 | 72 | LWB | 66.5
86 | 122 | 1050 | 72 | kW | 3.3
90 | 122 | 1050 | 75 | MBh | 21.2
90 | 122 | 1050 | 75 | S/T | 0.604
90 | 122 | 1050 | 75 | ∆T | 11.3
90 | 122 | 1050 | 75 | LDB | 78.7
90 | 122 | 1050 | 75 | LWB | 69.9
90 | 122 | 1050 | 75 | kW | 3.3

## RZA36AAVJU - FTA36AAVJUA
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1050 | 57 | MBh | 22.7 | 64 | 60 | 61 | 48.6 | 4.17
68 | 23 | 1050 | 57 | S/T | 0.789 | 64 | 60 | 65 | 45 | 3.78
68 | 23 | 1050 | 57 | ∆T | 15.8 | 64 | 60 | 68 | 42.3 | 3.53
68 | 23 | 1050 | 57 | LDB | 52.2 | 64 | 60 | 70 | 40.5 | 3.37
68 | 23 | 1050 | 57 | LWB | 48.7 | 64 | 60 | 72 | 38.7 | 3.23
68 | 23 | 1050 | 57 | kW | 1.03 | 64 | 60 | 75 | 36 | 3.05
72 | 23 | 1050 | 61 | MBh | 27.6 | 60 | 56 | 61 | 48.6 | 4.37
72 | 23 | 1050 | 61 | S/T | 0.746 | 60 | 56 | 65 | 45 | 3.94
72 | 23 | 1050 | 61 | ∆T | 18.2 | 60 | 56 | 68 | 42.3 | 3.66
72 | 23 | 1050 | 61 | LDB | 53.8 | 60 | 56 | 70 | 40.5 | 3.49
72 | 23 | 1050 | 61 | LWB | 51.6 | 60 | 56 | 72 | 38.7 | 3.33
72 | 23 | 1050 | 61 | kW | 1.26 | 60 | 56 | 75 | 36 | 3.13
77 | 23 | 1050 | 64 | MBh | 31.3 | 57 | 53 | 61 | 48.6 | 4.53
77 | 23 | 1050 | 64 | S/T | 0.716 | 57 | 53 | 65 | 45 | 4.07
77 | 23 | 1050 | 64 | ∆T | 19.8 | 57 | 53 | 68 | 42.3 | 3.76
77 | 23 | 1050 | 64 | LDB | 57.2 | 57 | 53 | 70 | 40.5 | 3.58
77 | 23 | 1050 | 64 | LWB | 54 | 57 | 53 | 72 | 38.7 | 3.41
77 | 23 | 1050 | 64 | kW | 1.45 | 57 | 53 | 75 | 36 | 3.19
80 | 23 | 1050 | 67 | MBh | 35 | 54 | 50 | 61 | 48.6 | 4.71
80 | 23 | 1050 | 67 | S/T | 0.677 | 54 | 50 | 65 | 45 | 4.21
80 | 23 | 1050 | 67 | ∆T | 20.9 | 54 | 50 | 68 | 42.3 | 3.89
80 | 23 | 1050 | 67 | LDB | 59.1 | 54 | 50 | 70 | 40.5 | 3.69
80 | 23 | 1050 | 67 | LWB | 56.4 | 54 | 50 | 72 | 38.7 | 3.51
80 | 23 | 1050 | 67 | kW | 1.64 | 54 | 50 | 75 | 36 | 3.27
84 | 23 | 1050 | 70 | MBh | 38.7 | 51 | 47 | 61 | 48.6 | 4.91
84 | 23 | 1050 | 70 | S/T | 0.638 | 51 | 47 | 65 | 45 | 4.38
84 | 23 | 1050 | 70 | ∆T | 21.8 | 51 | 47 | 68 | 42.3 | 4.02
84 | 23 | 1050 | 70 | LDB | 62.2 | 51 | 47 | 70 | 40.5 | 3.81
84 | 23 | 1050 | 70 | LWB | 59 | 51 | 47 | 72 | 38.7 | 3.61
84 | 23 | 1050 | 70 | kW | 1.84 | 51 | 47 | 75 | 36 | 3.35
86 | 23 | 1050 | 72 | MBh | 41.1 | 47 | 43 | 61 | 48.6 | 5.21
86 | 23 | 1050 | 72 | S/T | 0.63 | 47 | 43 | 65 | 45 | 4.62
86 | 23 | 1050 | 72 | ∆T | 22.8 | 47 | 43 | 68 | 42.3 | 4.23
86 | 23 | 1050 | 72 | LDB | 63.2 | 47 | 43 | 70 | 40.5 | 3.99
86 | 23 | 1050 | 72 | LWB | 60.8 | 47 | 43 | 72 | 38.7 | 3.77
86 | 23 | 1050 | 72 | kW | 1.98 | 47 | 43 | 75 | 36 | 3.47
90 | 23 | 1050 | 75 | MBh | 44.8 | 44 | 40 | 61 | 48.6 | 5.47
90 | 23 | 1050 | 75 | S/T | 0.598 | 44 | 40 | 65 | 45 | 4.83
90 | 23 | 1050 | 75 | ∆T | 23.6 | 44 | 40 | 68 | 42.3 | 4.4
90 | 23 | 1050 | 75 | LDB | 66.4 | 44 | 40 | 70 | 40.5 | 4.14
90 | 23 | 1050 | 75 | LWB | 63.5 | 44 | 40 | 72 | 38.7 | 3.9
90 | 23 | 1050 | 75 | kW | 2.19 | 44 | 40 | 75 | 36 | 3.58
68 | 30 | 1050 | 57 | MBh | 22.7 | 39 | 36 | 61 | 48.6 | 5.85
68 | 30 | 1050 | 57 | S/T | 0.789 | 39 | 36 | 65 | 45 | 5.14
68 | 30 | 1050 | 57 | ∆T | 15.8 | 39 | 36 | 68 | 42.3 | 4.67
68 | 30 | 1050 | 57 | LDB | 52.2 | 39 | 36 | 70 | 40.5 | 4.38
68 | 30 | 1050 | 57 | LWB | 48.7 | 39 | 36 | 72 | 38.7 | 4.11
68 | 30 | 1050 | 57 | kW | 1.06 | 39 | 36 | 75 | 36 | 3.75
72 | 30 | 1050 | 61 | MBh | 27.6 | 35 | 32 | 61 | 48.6 | 6.3
72 | 30 | 1050 | 61 | S/T | 0.746 | 35 | 32 | 65 | 45 | 5.51
72 | 30 | 1050 | 61 | ∆T | 18.2 | 35 | 32 | 68 | 42.3 | 4.98
72 | 30 | 1050 | 61 | LDB | 53.8 | 35 | 32 | 70 | 40.5 | 4.65
72 | 30 | 1050 | 61 | LWB | 51.6 | 35 | 32 | 72 | 38.7 | 4.35
72 | 30 | 1050 | 61 | kW | 1.3 | 35 | 32 | 75 | 36 | 3.95
77 | 30 | 1050 | 64 | MBh | 31.3 | 30 | 28 | 61 | 48.6 | 6.82
77 | 30 | 1050 | 64 | S/T | 0.716 | 30 | 28 | 65 | 45 | 5.93
77 | 30 | 1050 | 64 | ∆T | 19.8 | 30 | 28 | 68 | 42.3 | 5.34
77 | 30 | 1050 | 64 | LDB | 57.2 | 30 | 28 | 70 | 40.5 | 4.97
77 | 30 | 1050 | 64 | LWB | 54 | 30 | 28 | 72 | 38.7 | 4.64
77 | 30 | 1050 | 64 | kW | 1.5 | 30 | 28 | 75 | 36 | 4.18
80 | 30 | 1050 | 67 | MBh | 35 | 26 | 24 | 61 | 48.6 | 6.97
80 | 30 | 1050 | 67 | S/T | 0.677 | 26 | 24 | 65 | 45 | 6.43
80 | 30 | 1050 | 67 | ∆T | 20.9 | 26 | 24 | 68 | 42.3 | 5.76
80 | 30 | 1050 | 67 | LDB | 59.1 | 26 | 24 | 70 | 40.5 | 5.35
80 | 30 | 1050 | 67 | LWB | 56.4 | 26 | 24 | 72 | 38.7 | 4.97
80 | 30 | 1050 | 67 | kW | 1.7 | 26 | 24 | 75 | 36 | 4.45
84 | 30 | 1050 | 70 | MBh | 38.7 | 22 | 20 | 61 | 48.5 | 6.64
84 | 30 | 1050 | 70 | S/T | 0.638 | 22 | 20 | 65 | 45 | 7.02
84 | 30 | 1050 | 70 | ∆T | 21.8 | 22 | 20 | 68 | 42.3 | 6.27
84 | 30 | 1050 | 70 | LDB | 62.2 | 22 | 20 | 70 | 40.5 | 5.81
84 | 30 | 1050 | 70 | LWB | 59 | 22 | 20 | 72 | 38.7 | 5.37
84 | 30 | 1050 | 70 | kW | 1.9 | 22 | 20 | 75 | 36 | 4.78
86 | 30 | 1050 | 72 | MBh | 41.1 | 19 | 18 | 61 | 47.2 | 6.47
86 | 30 | 1050 | 72 | S/T | 0.63 | 19 | 18 | 65 | 45 | 6.99
86 | 30 | 1050 | 72 | ∆T | 22.8 | 19 | 18 | 68 | 42.3 | 6.56
86 | 30 | 1050 | 72 | LDB | 63.2 | 19 | 18 | 70 | 40.5 | 6.06
86 | 30 | 1050 | 72 | LWB | 60.8 | 19 | 18 | 72 | 38.7 | 5.6
86 | 30 | 1050 | 72 | kW | 2.05 | 19 | 18 | 75 | 36 | 4.97
90 | 30 | 1050 | 75 | MBh | 44.8 | 17 | 16 | 61 | 45.6 | 6.24
90 | 30 | 1050 | 75 | S/T | 0.598 | 17 | 16 | 65 | 45 | 6.77
90 | 30 | 1050 | 75 | ∆T | 23.6 | 17 | 16 | 68 | 42.3 | 6.95
90 | 30 | 1050 | 75 | LDB | 66.4 | 17 | 16 | 70 | 40.5 | 6.42
90 | 30 | 1050 | 75 | LWB | 63.5 | 17 | 16 | 72 | 38.7 | 5.92
90 | 30 | 1050 | 75 | kW | 2.26 | 17 | 16 | 75 | 36 | 5.23
68 | 40 | 1050 | 57 | MBh | 22.7 | 15 | 14 | 61 | 44.7 | 6.09
68 | 40 | 1050 | 57 | S/T | 0.789 | 15 | 14 | 65 | 44.7 | 6.64
68 | 40 | 1050 | 57 | ∆T | 15.8 | 15 | 14 | 68 | 42.3 | 7.05
68 | 40 | 1050 | 57 | LDB | 52.2 | 15 | 14 | 70 | 40.5 | 6.65
68 | 40 | 1050 | 57 | LWB | 48.7 | 15 | 14 | 72 | 38.7 | 6.13
68 | 40 | 1050 | 57 | kW | 1.11 | 15 | 14 | 75 | 36 | 5.41
72 | 40 | 1050 | 61 | MBh | 27.6 | 13 | 12 | 61 | 43.4 | 5.88
72 | 40 | 1050 | 61 | S/T | 0.746 | 13 | 12 | 65 | 43.4 | 6.45
72 | 40 | 1050 | 61 | ∆T | 18.2 | 13 | 12 | 68 | 42.3 | 6.87
72 | 40 | 1050 | 61 | LDB | 53.8 | 13 | 12 | 70 | 40.5 | 6.99
72 | 40 | 1050 | 61 | LWB | 51.6 | 13 | 12 | 72 | 38.7 | 6.43
72 | 40 | 1050 | 61 | kW | 1.36 | 13 | 12 | 75 | 36 | 5.66
77 | 40 | 1050 | 64 | MBh | 31.3 | 10 | 9 | 61 | 41.2 | 5.5
77 | 40 | 1050 | 64 | S/T | 0.716 | 10 | 9 | 65 | 41.2 | 6.09
77 | 40 | 1050 | 64 | ∆T | 19.8 | 10 | 9 | 68 | 41.2 | 6.53
77 | 40 | 1050 | 64 | LDB | 57.2 | 10 | 9 | 70 | 40.5 | 6.83
77 | 40 | 1050 | 64 | LWB | 54 | 10 | 9 | 72 | 38.7 | 7.03
77 | 40 | 1050 | 64 | kW | 1.57 | 10 | 9 | 75 | 36 | 6.16
80 | 40 | 1050 | 67 | MBh | 35 | 6 | 5 | 61 | 39 | 5.07
80 | 40 | 1050 | 67 | S/T | 0.677 | 6 | 5 | 65 | 39 | 5.69
80 | 40 | 1050 | 67 | ∆T | 20.9 | 6 | 5 | 68 | 39 | 5.71
80 | 40 | 1050 | 67 | LDB | 59.1 | 6 | 5 | 70 | 39 | 5.71
80 | 40 | 1050 | 67 | LWB | 56.4 | 6 | 5 | 72 | 38.7 | 5.71
80 | 40 | 1050 | 67 | kW | 1.78 | 6 | 5 | 75 | 36 | 5.71
84 | 40 | 1050 | 70 | MBh | 38.7 | -2 | -2 | 61 | 32.1 | 4.04
84 | 40 | 1050 | 70 | S/T | 0.638 | -2 | -2 | 65 | 32.1 | 4.74
84 | 40 | 1050 | 70 | ∆T | 21.8 | -2 | -2 | 68 | 32.1 | 4.8
84 | 40 | 1050 | 70 | LDB | 62.2 | -2 | -2 | 70 | 32.1 | 4.8
84 | 40 | 1050 | 70 | LWB | 59 | -2 | -2 | 72 | 32.1 | 4.8
84 | 40 | 1050 | 70 | kW | 2 | -2 | -2 | 75 | 32.1 | 4.8
86 | 40 | 1050 | 72 | MBh | 41.1 | -4 | -4 | 61 | 30.4 | 3.74
86 | 40 | 1050 | 72 | S/T | 0.63 | -4 | -4 | 65 | 30.4 | 4.46
86 | 40 | 1050 | 72 | ∆T | 22.8 | -4 | -4 | 68 | 30.4 | 4.57
86 | 40 | 1050 | 72 | LDB | 63.2 | -4 | -4 | 70 | 30.4 | 4.57
86 | 40 | 1050 | 72 | LWB | 60.8 | -4 | -4 | 72 | 30.4 | 4.57
86 | 40 | 1050 | 72 | kW | 2.15 | -4 | -4 | 75 | 30.4 | 4.57
90 | 40 | 1050 | 75 | MBh | 44.8
90 | 40 | 1050 | 75 | S/T | 0.598
90 | 40 | 1050 | 75 | ∆T | 23.6
90 | 40 | 1050 | 75 | LDB | 66.4
90 | 40 | 1050 | 75 | LWB | 63.5
90 | 40 | 1050 | 75 | kW | 2.37
68 | 50 | 1050 | 57 | MBh | 22.7
68 | 50 | 1050 | 57 | S/T | 0.789
68 | 50 | 1050 | 57 | ∆T | 15.8
68 | 50 | 1050 | 57 | LDB | 52.2
68 | 50 | 1050 | 57 | LWB | 48.7
68 | 50 | 1050 | 57 | kW | 1.16
72 | 50 | 1050 | 61 | MBh | 27.6
72 | 50 | 1050 | 61 | S/T | 0.746
72 | 50 | 1050 | 61 | ∆T | 18.2
72 | 50 | 1050 | 61 | LDB | 53.8
72 | 50 | 1050 | 61 | LWB | 51.6
72 | 50 | 1050 | 61 | kW | 1.43
77 | 50 | 1050 | 64 | MBh | 31.3
77 | 50 | 1050 | 64 | S/T | 0.716
77 | 50 | 1050 | 64 | ∆T | 19.8
77 | 50 | 1050 | 64 | LDB | 57.2
77 | 50 | 1050 | 64 | LWB | 54
77 | 50 | 1050 | 64 | kW | 1.65
80 | 50 | 1050 | 67 | MBh | 35
80 | 50 | 1050 | 67 | S/T | 0.677
80 | 50 | 1050 | 67 | ∆T | 20.9
80 | 50 | 1050 | 67 | LDB | 59.1
80 | 50 | 1050 | 67 | LWB | 56.4
80 | 50 | 1050 | 67 | kW | 1.87
84 | 50 | 1050 | 70 | MBh | 38.7
84 | 50 | 1050 | 70 | S/T | 0.638
84 | 50 | 1050 | 70 | ∆T | 21.8
84 | 50 | 1050 | 70 | LDB | 62.2
84 | 50 | 1050 | 70 | LWB | 59
84 | 50 | 1050 | 70 | kW | 2.1
86 | 50 | 1050 | 72 | MBh | 41.1
86 | 50 | 1050 | 72 | S/T | 0.63
86 | 50 | 1050 | 72 | ∆T | 22.8
86 | 50 | 1050 | 72 | LDB | 63.2
86 | 50 | 1050 | 72 | LWB | 60.8
86 | 50 | 1050 | 72 | kW | 2.26
90 | 50 | 1050 | 75 | MBh | 44.8
90 | 50 | 1050 | 75 | S/T | 0.598
90 | 50 | 1050 | 75 | ∆T | 23.6
90 | 50 | 1050 | 75 | LDB | 66.4
90 | 50 | 1050 | 75 | LWB | 63.5
90 | 50 | 1050 | 75 | kW | 2.49
68 | 54 | 1050 | 57 | MBh | 22.7
68 | 54 | 1050 | 57 | S/T | 0.789
68 | 54 | 1050 | 57 | ∆T | 15.8
68 | 54 | 1050 | 57 | LDB | 52.2
68 | 54 | 1050 | 57 | LWB | 48.7
68 | 54 | 1050 | 57 | kW | 1.18
72 | 54 | 1050 | 61 | MBh | 27.6
72 | 54 | 1050 | 61 | S/T | 0.746
72 | 54 | 1050 | 61 | ∆T | 18.2
72 | 54 | 1050 | 61 | LDB | 53.8
72 | 54 | 1050 | 61 | LWB | 51.6
72 | 54 | 1050 | 61 | kW | 1.46
77 | 54 | 1050 | 64 | MBh | 31.3
77 | 54 | 1050 | 64 | S/T | 0.716
77 | 54 | 1050 | 64 | ∆T | 19.8
77 | 54 | 1050 | 64 | LDB | 57.2
77 | 54 | 1050 | 64 | LWB | 54
77 | 54 | 1050 | 64 | kW | 1.68
80 | 54 | 1050 | 67 | MBh | 35
80 | 54 | 1050 | 67 | S/T | 0.677
80 | 54 | 1050 | 67 | ∆T | 20.9
80 | 54 | 1050 | 67 | LDB | 59.1
80 | 54 | 1050 | 67 | LWB | 56.4
80 | 54 | 1050 | 67 | kW | 1.91
84 | 54 | 1050 | 70 | MBh | 38.7
84 | 54 | 1050 | 70 | S/T | 0.638
84 | 54 | 1050 | 70 | ∆T | 21.8
84 | 54 | 1050 | 70 | LDB | 62.2
84 | 54 | 1050 | 70 | LWB | 59
84 | 54 | 1050 | 70 | kW | 2.15
86 | 54 | 1050 | 72 | MBh | 41.1
86 | 54 | 1050 | 72 | S/T | 0.63
86 | 54 | 1050 | 72 | ∆T | 22.8
86 | 54 | 1050 | 72 | LDB | 63.2
86 | 54 | 1050 | 72 | LWB | 60.8
86 | 54 | 1050 | 72 | kW | 2.3
90 | 54 | 1050 | 75 | MBh | 44.8
90 | 54 | 1050 | 75 | S/T | 0.598
90 | 54 | 1050 | 75 | ∆T | 23.6
90 | 54 | 1050 | 75 | LDB | 66.4
90 | 54 | 1050 | 75 | LWB | 63.5
90 | 54 | 1050 | 75 | kW | 2.54
68 | 58 | 1050 | 57 | MBh | 22.7
68 | 58 | 1050 | 57 | S/T | 0.789
68 | 58 | 1050 | 57 | ∆T | 15.8
68 | 58 | 1050 | 57 | LDB | 52.2
68 | 58 | 1050 | 57 | LWB | 48.7
68 | 58 | 1050 | 57 | kW | 1.2
72 | 58 | 1050 | 61 | MBh | 27.6
72 | 58 | 1050 | 61 | S/T | 0.746
72 | 58 | 1050 | 61 | ∆T | 18.2
72 | 58 | 1050 | 61 | LDB | 53.8
72 | 58 | 1050 | 61 | LWB | 51.6
72 | 58 | 1050 | 61 | kW | 1.49
77 | 58 | 1050 | 64 | MBh | 31.3
77 | 58 | 1050 | 64 | S/T | 0.716
77 | 58 | 1050 | 64 | ∆T | 19.8
77 | 58 | 1050 | 64 | LDB | 57.2
77 | 58 | 1050 | 64 | LWB | 54
77 | 58 | 1050 | 64 | kW | 1.72
80 | 58 | 1050 | 67 | MBh | 35
80 | 58 | 1050 | 67 | S/T | 0.677
80 | 58 | 1050 | 67 | ∆T | 20.9
80 | 58 | 1050 | 67 | LDB | 59.1
80 | 58 | 1050 | 67 | LWB | 56.4
80 | 58 | 1050 | 67 | kW | 1.95
84 | 58 | 1050 | 70 | MBh | 38.7
84 | 58 | 1050 | 70 | S/T | 0.638
84 | 58 | 1050 | 70 | ∆T | 21.8
84 | 58 | 1050 | 70 | LDB | 62.2
84 | 58 | 1050 | 70 | LWB | 59
84 | 58 | 1050 | 70 | kW | 2.19
86 | 58 | 1050 | 72 | MBh | 41.1
86 | 58 | 1050 | 72 | S/T | 0.63
86 | 58 | 1050 | 72 | ∆T | 22.8
86 | 58 | 1050 | 72 | LDB | 63.2
86 | 58 | 1050 | 72 | LWB | 60.8
86 | 58 | 1050 | 72 | kW | 2.35
90 | 58 | 1050 | 75 | MBh | 44.4
90 | 58 | 1050 | 75 | S/T | 0.597
90 | 58 | 1050 | 75 | ∆T | 23.4
90 | 58 | 1050 | 75 | LDB | 66.6
90 | 58 | 1050 | 75 | LWB | 63.6
90 | 58 | 1050 | 75 | kW | 2.55
68 | 62 | 1050 | 57 | MBh | 22.7
68 | 62 | 1050 | 57 | S/T | 0.789
68 | 62 | 1050 | 57 | ∆T | 15.8
68 | 62 | 1050 | 57 | LDB | 52.2
68 | 62 | 1050 | 57 | LWB | 48.7
68 | 62 | 1050 | 57 | kW | 1.23
72 | 62 | 1050 | 61 | MBh | 27.6
72 | 62 | 1050 | 61 | S/T | 0.746
72 | 62 | 1050 | 61 | ∆T | 18.2
72 | 62 | 1050 | 61 | LDB | 53.8
72 | 62 | 1050 | 61 | LWB | 51.6
72 | 62 | 1050 | 61 | kW | 1.52
77 | 62 | 1050 | 64 | MBh | 31.3
77 | 62 | 1050 | 64 | S/T | 0.716
77 | 62 | 1050 | 64 | ∆T | 19.8
77 | 62 | 1050 | 64 | LDB | 57.2
77 | 62 | 1050 | 64 | LWB | 54
77 | 62 | 1050 | 64 | kW | 1.75
80 | 62 | 1050 | 67 | MBh | 35
80 | 62 | 1050 | 67 | S/T | 0.677
80 | 62 | 1050 | 67 | ∆T | 20.9
80 | 62 | 1050 | 67 | LDB | 59.1
80 | 62 | 1050 | 67 | LWB | 56.4
80 | 62 | 1050 | 67 | kW | 1.99
84 | 62 | 1050 | 70 | MBh | 38.7
84 | 62 | 1050 | 70 | S/T | 0.638
84 | 62 | 1050 | 70 | ∆T | 21.8
84 | 62 | 1050 | 70 | LDB | 62.2
84 | 62 | 1050 | 70 | LWB | 59
84 | 62 | 1050 | 70 | kW | 2.24
86 | 62 | 1050 | 72 | MBh | 41.1
86 | 62 | 1050 | 72 | S/T | 0.63
86 | 62 | 1050 | 72 | ∆T | 22.8
86 | 62 | 1050 | 72 | LDB | 63.2
86 | 62 | 1050 | 72 | LWB | 60.8
86 | 62 | 1050 | 72 | kW | 2.41
90 | 62 | 1050 | 75 | MBh | 43.8
90 | 62 | 1050 | 75 | S/T | 0.598
90 | 62 | 1050 | 75 | ∆T | 23.1
90 | 62 | 1050 | 75 | LDB | 66.9
90 | 62 | 1050 | 75 | LWB | 63.8
90 | 62 | 1050 | 75 | kW | 2.61
68 | 66 | 1050 | 57 | MBh | 22.7
68 | 66 | 1050 | 57 | S/T | 0.789
68 | 66 | 1050 | 57 | ∆T | 15.8
68 | 66 | 1050 | 57 | LDB | 52.2
68 | 66 | 1050 | 57 | LWB | 48.7
68 | 66 | 1050 | 57 | kW | 1.25
72 | 66 | 1050 | 61 | MBh | 27.6
72 | 66 | 1050 | 61 | S/T | 0.746
72 | 66 | 1050 | 61 | ∆T | 18.2
72 | 66 | 1050 | 61 | LDB | 53.8
72 | 66 | 1050 | 61 | LWB | 51.6
72 | 66 | 1050 | 61 | kW | 1.55
77 | 66 | 1050 | 64 | MBh | 31.3
77 | 66 | 1050 | 64 | S/T | 0.716
77 | 66 | 1050 | 64 | ∆T | 19.8
77 | 66 | 1050 | 64 | LDB | 57.2
77 | 66 | 1050 | 64 | LWB | 54
77 | 66 | 1050 | 64 | kW | 1.79
80 | 66 | 1050 | 67 | MBh | 35
80 | 66 | 1050 | 67 | S/T | 0.677
80 | 66 | 1050 | 67 | ∆T | 20.9
80 | 66 | 1050 | 67 | LDB | 59.1
80 | 66 | 1050 | 67 | LWB | 56.4
80 | 66 | 1050 | 67 | kW | 2.04
84 | 66 | 1050 | 70 | MBh | 38.7
84 | 66 | 1050 | 70 | S/T | 0.638
84 | 66 | 1050 | 70 | ∆T | 21.8
84 | 66 | 1050 | 70 | LDB | 62.2
84 | 66 | 1050 | 70 | LWB | 59
84 | 66 | 1050 | 70 | kW | 2.37
86 | 66 | 1050 | 72 | MBh | 41.1
86 | 66 | 1050 | 72 | S/T | 0.63
86 | 66 | 1050 | 72 | ∆T | 22.8
86 | 66 | 1050 | 72 | LDB | 63.2
86 | 66 | 1050 | 72 | LWB | 60.8
86 | 66 | 1050 | 72 | kW | 2.6
90 | 66 | 1050 | 75 | MBh | 43.1
90 | 66 | 1050 | 75 | S/T | 0.599
90 | 66 | 1050 | 75 | ∆T | 22.8
90 | 66 | 1050 | 75 | LDB | 67.2
90 | 66 | 1050 | 75 | LWB | 64
90 | 66 | 1050 | 75 | kW | 2.75
68 | 70 | 1050 | 57 | MBh | 22.7
68 | 70 | 1050 | 57 | S/T | 0.789
68 | 70 | 1050 | 57 | ∆T | 15.8
68 | 70 | 1050 | 57 | LDB | 52.2
68 | 70 | 1050 | 57 | LWB | 48.7
68 | 70 | 1050 | 57 | kW | 1.28
72 | 70 | 1050 | 61 | MBh | 27.6
72 | 70 | 1050 | 61 | S/T | 0.746
72 | 70 | 1050 | 61 | ∆T | 18.2
72 | 70 | 1050 | 61 | LDB | 53.8
72 | 70 | 1050 | 61 | LWB | 51.6
72 | 70 | 1050 | 61 | kW | 1.59
77 | 70 | 1050 | 64 | MBh | 31.3
77 | 70 | 1050 | 64 | S/T | 0.716
77 | 70 | 1050 | 64 | ∆T | 19.8
77 | 70 | 1050 | 64 | LDB | 57.2
77 | 70 | 1050 | 64 | LWB | 54
77 | 70 | 1050 | 64 | kW | 1.88
80 | 70 | 1050 | 67 | MBh | 35
80 | 70 | 1050 | 67 | S/T | 0.677
80 | 70 | 1050 | 67 | ∆T | 20.9
80 | 70 | 1050 | 67 | LDB | 59.1
80 | 70 | 1050 | 67 | LWB | 56.4
80 | 70 | 1050 | 67 | kW | 2.21
84 | 70 | 1050 | 70 | MBh | 38.7
84 | 70 | 1050 | 70 | S/T | 0.638
84 | 70 | 1050 | 70 | ∆T | 21.8
84 | 70 | 1050 | 70 | LDB | 62.2
84 | 70 | 1050 | 70 | LWB | 59
84 | 70 | 1050 | 70 | kW | 2.56
86 | 70 | 1050 | 72 | MBh | 41.1
86 | 70 | 1050 | 72 | S/T | 0.63
86 | 70 | 1050 | 72 | ∆T | 22.8
86 | 70 | 1050 | 72 | LDB | 63.2
86 | 70 | 1050 | 72 | LWB | 60.8
86 | 70 | 1050 | 72 | kW | 2.81
90 | 70 | 1050 | 75 | MBh | 42.4
90 | 70 | 1050 | 75 | S/T | 0.599
90 | 70 | 1050 | 75 | ∆T | 22.4
90 | 70 | 1050 | 75 | LDB | 67.6
90 | 70 | 1050 | 75 | LWB | 64.2
90 | 70 | 1050 | 75 | kW | 2.9
68 | 72 | 1050 | 57 | MBh | 22.7
68 | 72 | 1050 | 57 | S/T | 0.789
68 | 72 | 1050 | 57 | ∆T | 15.8
68 | 72 | 1050 | 57 | LDB | 52.2
68 | 72 | 1050 | 57 | LWB | 48.7
68 | 72 | 1050 | 57 | kW | 1.29
72 | 72 | 1050 | 61 | MBh | 27.6
72 | 72 | 1050 | 61 | S/T | 0.746
72 | 72 | 1050 | 61 | ∆T | 18.2
72 | 72 | 1050 | 61 | LDB | 53.8
72 | 72 | 1050 | 61 | LWB | 51.6
72 | 72 | 1050 | 61 | kW | 1.64
77 | 72 | 1050 | 64 | MBh | 31.3
77 | 72 | 1050 | 64 | S/T | 0.716
77 | 72 | 1050 | 64 | ∆T | 19.8
77 | 72 | 1050 | 64 | LDB | 57.2
77 | 72 | 1050 | 64 | LWB | 54
77 | 72 | 1050 | 64 | kW | 1.95
80 | 72 | 1050 | 67 | MBh | 35
80 | 72 | 1050 | 67 | S/T | 0.677
80 | 72 | 1050 | 67 | ∆T | 20.9
80 | 72 | 1050 | 67 | LDB | 59.1
80 | 72 | 1050 | 67 | LWB | 56.4
80 | 72 | 1050 | 67 | kW | 2.29
84 | 72 | 1050 | 70 | MBh | 38.7
84 | 72 | 1050 | 70 | S/T | 0.638
84 | 72 | 1050 | 70 | ∆T | 21.8
84 | 72 | 1050 | 70 | LDB | 62.2
84 | 72 | 1050 | 70 | LWB | 59
84 | 72 | 1050 | 70 | kW | 2.66
86 | 72 | 1050 | 72 | MBh | 41.1
86 | 72 | 1050 | 72 | S/T | 0.63
86 | 72 | 1050 | 72 | ∆T | 22.8
86 | 72 | 1050 | 72 | LDB | 63.2
86 | 72 | 1050 | 72 | LWB | 60.8
86 | 72 | 1050 | 72 | kW | 2.92
90 | 72 | 1050 | 75 | MBh | 42.1
90 | 72 | 1050 | 75 | S/T | 0.599
90 | 72 | 1050 | 75 | ∆T | 22.2
90 | 72 | 1050 | 75 | LDB | 67.8
90 | 72 | 1050 | 75 | LWB | 64.3
90 | 72 | 1050 | 75 | kW | 2.97
68 | 75 | 1050 | 57 | MBh | 22.7
68 | 75 | 1050 | 57 | S/T | 0.789
68 | 75 | 1050 | 57 | ∆T | 15.8
68 | 75 | 1050 | 57 | LDB | 52.2
68 | 75 | 1050 | 57 | LWB | 48.7
68 | 75 | 1050 | 57 | kW | 1.34
72 | 75 | 1050 | 61 | MBh | 27.6
72 | 75 | 1050 | 61 | S/T | 0.746
72 | 75 | 1050 | 61 | ∆T | 18.2
72 | 75 | 1050 | 61 | LDB | 53.8
72 | 75 | 1050 | 61 | LWB | 51.6
72 | 75 | 1050 | 61 | kW | 1.73
77 | 75 | 1050 | 64 | MBh | 31.3
77 | 75 | 1050 | 64 | S/T | 0.716
77 | 75 | 1050 | 64 | ∆T | 19.8
77 | 75 | 1050 | 64 | LDB | 57.2
77 | 75 | 1050 | 64 | LWB | 54
77 | 75 | 1050 | 64 | kW | 2.07
80 | 75 | 1050 | 67 | MBh | 35
80 | 75 | 1050 | 67 | S/T | 0.677
80 | 75 | 1050 | 67 | ∆T | 20.9
80 | 75 | 1050 | 67 | LDB | 59.1
80 | 75 | 1050 | 67 | LWB | 56.4
80 | 75 | 1050 | 67 | kW | 2.43
84 | 75 | 1050 | 70 | MBh | 38.7
84 | 75 | 1050 | 70 | S/T | 0.638
84 | 75 | 1050 | 70 | ∆T | 21.8
84 | 75 | 1050 | 70 | LDB | 62.2
84 | 75 | 1050 | 70 | LWB | 59
84 | 75 | 1050 | 70 | kW | 2.82
86 | 75 | 1050 | 72 | MBh | 40.9
86 | 75 | 1050 | 72 | S/T | 0.631
86 | 75 | 1050 | 72 | ∆T | 22.8
86 | 75 | 1050 | 72 | LDB | 63.2
86 | 75 | 1050 | 72 | LWB | 60.8
86 | 75 | 1050 | 72 | kW | 3.06
90 | 75 | 1050 | 75 | MBh | 41.6
90 | 75 | 1050 | 75 | S/T | 0.599
90 | 75 | 1050 | 75 | ∆T | 22
90 | 75 | 1050 | 75 | LDB | 68
90 | 75 | 1050 | 75 | LWB | 64.5
90 | 75 | 1050 | 75 | kW | 3.08
68 | 79 | 1050 | 57 | MBh | 22.7
68 | 79 | 1050 | 57 | S/T | 0.789
68 | 79 | 1050 | 57 | ∆T | 15.8
68 | 79 | 1050 | 57 | LDB | 52.2
68 | 79 | 1050 | 57 | LWB | 48.7
68 | 79 | 1050 | 57 | kW | 1.44
72 | 79 | 1050 | 61 | MBh | 27.6
72 | 79 | 1050 | 61 | S/T | 0.746
72 | 79 | 1050 | 61 | ∆T | 18.2
72 | 79 | 1050 | 61 | LDB | 53.8
72 | 79 | 1050 | 61 | LWB | 51.6
72 | 79 | 1050 | 61 | kW | 1.87
77 | 79 | 1050 | 64 | MBh | 31.3
77 | 79 | 1050 | 64 | S/T | 0.716
77 | 79 | 1050 | 64 | ∆T | 19.8
77 | 79 | 1050 | 64 | LDB | 57.2
77 | 79 | 1050 | 64 | LWB | 54
77 | 79 | 1050 | 64 | kW | 2.23
80 | 79 | 1050 | 67 | MBh | 35
80 | 79 | 1050 | 67 | S/T | 0.677
80 | 79 | 1050 | 67 | ∆T | 20.9
80 | 79 | 1050 | 67 | LDB | 59.1
80 | 79 | 1050 | 67 | LWB | 56.4
80 | 79 | 1050 | 67 | kW | 2.62
84 | 79 | 1050 | 70 | MBh | 38.7
84 | 79 | 1050 | 70 | S/T | 0.638
84 | 79 | 1050 | 70 | ∆T | 21.8
84 | 79 | 1050 | 70 | LDB | 62.2
84 | 79 | 1050 | 70 | LWB | 59
84 | 79 | 1050 | 70 | kW | 3.04
86 | 79 | 1050 | 72 | MBh | 40.2
86 | 79 | 1050 | 72 | S/T | 0.632
86 | 79 | 1050 | 72 | ∆T | 22.4
86 | 79 | 1050 | 72 | LDB | 63.6
86 | 79 | 1050 | 72 | LWB | 61.1
86 | 79 | 1050 | 72 | kW | 3.21
90 | 79 | 1050 | 75 | MBh | 41
90 | 79 | 1050 | 75 | S/T | 0.598
90 | 79 | 1050 | 75 | ∆T | 21.6
90 | 79 | 1050 | 75 | LDB | 68.4
90 | 79 | 1050 | 75 | LWB | 64.6
90 | 79 | 1050 | 75 | kW | 3.23
68 | 83 | 1050 | 57 | MBh | 22.7
68 | 83 | 1050 | 57 | S/T | 0.789
68 | 83 | 1050 | 57 | ∆T | 15.8
68 | 83 | 1050 | 57 | LDB | 52.2
68 | 83 | 1050 | 57 | LWB | 48.7
68 | 83 | 1050 | 57 | kW | 1.54
72 | 83 | 1050 | 61 | MBh | 27.6
72 | 83 | 1050 | 61 | S/T | 0.746
72 | 83 | 1050 | 61 | ∆T | 18.2
72 | 83 | 1050 | 61 | LDB | 53.8
72 | 83 | 1050 | 61 | LWB | 51.6
72 | 83 | 1050 | 61 | kW | 2.01
77 | 83 | 1050 | 64 | MBh | 31.3
77 | 83 | 1050 | 64 | S/T | 0.716
77 | 83 | 1050 | 64 | ∆T | 19.8
77 | 83 | 1050 | 64 | LDB | 57.2
77 | 83 | 1050 | 64 | LWB | 54
77 | 83 | 1050 | 64 | kW | 2.39
80 | 83 | 1050 | 67 | MBh | 35
80 | 83 | 1050 | 67 | S/T | 0.677
80 | 83 | 1050 | 67 | ∆T | 20.9
80 | 83 | 1050 | 67 | LDB | 59.1
80 | 83 | 1050 | 67 | LWB | 56.4
80 | 83 | 1050 | 67 | kW | 2.82
84 | 83 | 1050 | 70 | MBh | 38.7
84 | 83 | 1050 | 70 | S/T | 0.638
84 | 83 | 1050 | 70 | ∆T | 21.8
84 | 83 | 1050 | 70 | LDB | 62.2
84 | 83 | 1050 | 70 | LWB | 59
84 | 83 | 1050 | 70 | kW | 3.28
86 | 83 | 1050 | 72 | MBh | 39.6
86 | 83 | 1050 | 72 | S/T | 0.631
86 | 83 | 1050 | 72 | ∆T | 22
86 | 83 | 1050 | 72 | LDB | 64
86 | 83 | 1050 | 72 | LWB | 61.2
86 | 83 | 1050 | 72 | kW | 3.36
90 | 83 | 1050 | 75 | MBh | 40.3
90 | 83 | 1050 | 75 | S/T | 0.598
90 | 83 | 1050 | 75 | ∆T | 21.3
90 | 83 | 1050 | 75 | LDB | 68.7
90 | 83 | 1050 | 75 | LWB | 64.8
90 | 83 | 1050 | 75 | kW | 3.38
68 | 87 | 1050 | 57 | MBh | 22.7
68 | 87 | 1050 | 57 | S/T | 0.789
68 | 87 | 1050 | 57 | ∆T | 15.8
68 | 87 | 1050 | 57 | LDB | 52.2
68 | 87 | 1050 | 57 | LWB | 48.7
68 | 87 | 1050 | 57 | kW | 1.65
72 | 87 | 1050 | 61 | MBh | 27.6
72 | 87 | 1050 | 61 | S/T | 0.746
72 | 87 | 1050 | 61 | ∆T | 18.2
72 | 87 | 1050 | 61 | LDB | 53.8
72 | 87 | 1050 | 61 | LWB | 51.6
72 | 87 | 1050 | 61 | kW | 2.15
77 | 87 | 1050 | 64 | MBh | 31.3
77 | 87 | 1050 | 64 | S/T | 0.716
77 | 87 | 1050 | 64 | ∆T | 19.8
77 | 87 | 1050 | 64 | LDB | 57.2
77 | 87 | 1050 | 64 | LWB | 54
77 | 87 | 1050 | 64 | kW | 2.57
80 | 87 | 1050 | 67 | MBh | 35
80 | 87 | 1050 | 67 | S/T | 0.677
80 | 87 | 1050 | 67 | ∆T | 20.9
80 | 87 | 1050 | 67 | LDB | 59.1
80 | 87 | 1050 | 67 | LWB | 56.4
80 | 87 | 1050 | 67 | kW | 3.03
84 | 87 | 1050 | 70 | MBh | 38.4
84 | 87 | 1050 | 70 | S/T | 0.641
84 | 87 | 1050 | 70 | ∆T | 21.7
84 | 87 | 1050 | 70 | LDB | 62.3
84 | 87 | 1050 | 70 | LWB | 59.1
84 | 87 | 1050 | 70 | kW | 3.49
86 | 87 | 1050 | 72 | MBh | 38.9
86 | 87 | 1050 | 72 | S/T | 0.632
86 | 87 | 1050 | 72 | ∆T | 21.7
86 | 87 | 1050 | 72 | LDB | 64.3
86 | 87 | 1050 | 72 | LWB | 61.4
86 | 87 | 1050 | 72 | kW | 3.5
90 | 87 | 1050 | 75 | MBh | 39.7
90 | 87 | 1050 | 75 | S/T | 0.597
90 | 87 | 1050 | 75 | ∆T | 20.9
90 | 87 | 1050 | 75 | LDB | 69.1
90 | 87 | 1050 | 75 | LWB | 65
90 | 87 | 1050 | 75 | kW | 3.53
68 | 91 | 1050 | 57 | MBh | 22.7
68 | 91 | 1050 | 57 | S/T | 0.789
68 | 91 | 1050 | 57 | ∆T | 15.8
68 | 91 | 1050 | 57 | LDB | 52.2
68 | 91 | 1050 | 57 | LWB | 48.7
68 | 91 | 1050 | 57 | kW | 1.77
72 | 91 | 1050 | 61 | MBh | 27.6
72 | 91 | 1050 | 61 | S/T | 0.746
72 | 91 | 1050 | 61 | ∆T | 18.2
72 | 91 | 1050 | 61 | LDB | 53.8
72 | 91 | 1050 | 61 | LWB | 51.6
72 | 91 | 1050 | 61 | kW | 2.31
77 | 91 | 1050 | 64 | MBh | 31.3
77 | 91 | 1050 | 64 | S/T | 0.716
77 | 91 | 1050 | 64 | ∆T | 19.8
77 | 91 | 1050 | 64 | LDB | 57.2
77 | 91 | 1050 | 64 | LWB | 54
77 | 91 | 1050 | 64 | kW | 2.76
80 | 91 | 1050 | 67 | MBh | 35
80 | 91 | 1050 | 67 | S/T | 0.677
80 | 91 | 1050 | 67 | ∆T | 20.9
80 | 91 | 1050 | 67 | LDB | 59.1
80 | 91 | 1050 | 67 | LWB | 56.4
80 | 91 | 1050 | 67 | kW | 3.26
84 | 91 | 1050 | 70 | MBh | 37.8
84 | 91 | 1050 | 70 | S/T | 0.638
84 | 91 | 1050 | 70 | ∆T | 21.3
84 | 91 | 1050 | 70 | LDB | 62.7
84 | 91 | 1050 | 70 | LWB | 59.3
84 | 91 | 1050 | 70 | kW | 3.64
86 | 91 | 1050 | 72 | MBh | 38.3
86 | 91 | 1050 | 72 | S/T | 0.629
86 | 91 | 1050 | 72 | ∆T | 21.3
86 | 91 | 1050 | 72 | LDB | 64.7
86 | 91 | 1050 | 72 | LWB | 61.6
86 | 91 | 1050 | 72 | kW | 3.65
90 | 91 | 1050 | 75 | MBh | 39
90 | 91 | 1050 | 75 | S/T | 0.597
90 | 91 | 1050 | 75 | ∆T | 20.5
90 | 91 | 1050 | 75 | LDB | 69.5
90 | 91 | 1050 | 75 | LWB | 65.2
90 | 91 | 1050 | 75 | kW | 3.68
68 | 93 | 1050 | 57 | MBh | 22.7
68 | 93 | 1050 | 57 | S/T | 0.789
68 | 93 | 1050 | 57 | ∆T | 15.8
68 | 93 | 1050 | 57 | LDB | 52.2
68 | 93 | 1050 | 57 | LWB | 48.7
68 | 93 | 1050 | 57 | kW | 1.83
72 | 93 | 1050 | 61 | MBh | 27.6
72 | 93 | 1050 | 61 | S/T | 0.746
72 | 93 | 1050 | 61 | ∆T | 18.2
72 | 93 | 1050 | 61 | LDB | 53.8
72 | 93 | 1050 | 61 | LWB | 51.6
72 | 93 | 1050 | 61 | kW | 2.39
77 | 93 | 1050 | 64 | MBh | 31.3
77 | 93 | 1050 | 64 | S/T | 0.716
77 | 93 | 1050 | 64 | ∆T | 19.8
77 | 93 | 1050 | 64 | LDB | 57.2
77 | 93 | 1050 | 64 | LWB | 54
77 | 93 | 1050 | 64 | kW | 2.86
80 | 93 | 1050 | 67 | MBh | 35
80 | 93 | 1050 | 67 | S/T | 0.677
80 | 93 | 1050 | 67 | ∆T | 20.9
80 | 93 | 1050 | 67 | LDB | 59.1
80 | 93 | 1050 | 67 | LWB | 56.4
80 | 93 | 1050 | 67 | kW | 3.38
84 | 93 | 1050 | 70 | MBh | 37.5
84 | 93 | 1050 | 70 | S/T | 0.637
84 | 93 | 1050 | 70 | ∆T | 21.1
84 | 93 | 1050 | 70 | LDB | 62.9
84 | 93 | 1050 | 70 | LWB | 59.4
84 | 93 | 1050 | 70 | kW | 3.71
86 | 93 | 1050 | 72 | MBh | 37.9
86 | 93 | 1050 | 72 | S/T | 0.631
86 | 93 | 1050 | 72 | ∆T | 21.1
86 | 93 | 1050 | 72 | LDB | 64.9
86 | 93 | 1050 | 72 | LWB | 61.8
86 | 93 | 1050 | 72 | kW | 3.73
90 | 93 | 1050 | 75 | MBh | 38.7
90 | 93 | 1050 | 75 | S/T | 0.597
90 | 93 | 1050 | 75 | ∆T | 20.4
90 | 93 | 1050 | 75 | LDB | 69.6
90 | 93 | 1050 | 75 | LWB | 65.3
90 | 93 | 1050 | 75 | kW | 3.75
68 | 95 | 1050 | 57 | MBh | 22.7
68 | 95 | 1050 | 57 | S/T | 0.789
68 | 95 | 1050 | 57 | ∆T | 15.8
68 | 95 | 1050 | 57 | LDB | 52.2
68 | 95 | 1050 | 57 | LWB | 48.7
68 | 95 | 1050 | 57 | kW | 1.89
72 | 95 | 1050 | 61 | MBh | 27.6
72 | 95 | 1050 | 61 | S/T | 0.746
72 | 95 | 1050 | 61 | ∆T | 18.2
72 | 95 | 1050 | 61 | LDB | 53.8
72 | 95 | 1050 | 61 | LWB | 51.6
72 | 95 | 1050 | 61 | kW | 2.47
77 | 95 | 1050 | 64 | MBh | 31.3
77 | 95 | 1050 | 64 | S/T | 0.716
77 | 95 | 1050 | 64 | ∆T | 19.8
77 | 95 | 1050 | 64 | LDB | 57.2
77 | 95 | 1050 | 64 | LWB | 54
77 | 95 | 1050 | 64 | kW | 2.96
80 | 95 | 1050 | 67 | MBh | 35
80 | 95 | 1050 | 67 | S/T | 0.677
80 | 95 | 1050 | 67 | ∆T | 20.9
80 | 95 | 1050 | 67 | LDB | 59.1
80 | 95 | 1050 | 67 | LWB | 56.4
80 | 95 | 1050 | 67 | kW | 3.5
84 | 95 | 1050 | 70 | MBh | 37.1
84 | 95 | 1050 | 70 | S/T | 0.639
84 | 95 | 1050 | 70 | ∆T | 20.9
84 | 95 | 1050 | 70 | LDB | 63.1
84 | 95 | 1050 | 70 | LWB | 59.5
84 | 95 | 1050 | 70 | kW | 3.78
86 | 95 | 1050 | 72 | MBh | 37.6
86 | 95 | 1050 | 72 | S/T | 0.63
86 | 95 | 1050 | 72 | ∆T | 20.9
86 | 95 | 1050 | 72 | LDB | 65.1
86 | 95 | 1050 | 72 | LWB | 61.8
86 | 95 | 1050 | 72 | kW | 3.8
90 | 95 | 1050 | 75 | MBh | 38.3
90 | 95 | 1050 | 75 | S/T | 0.598
90 | 95 | 1050 | 75 | ∆T | 20.2
90 | 95 | 1050 | 75 | LDB | 69.8
90 | 95 | 1050 | 75 | LWB | 65.4
90 | 95 | 1050 | 75 | kW | 3.83
68 | 99 | 1050 | 57 | MBh | 22.7
68 | 99 | 1050 | 57 | S/T | 0.789
68 | 99 | 1050 | 57 | ∆T | 15.8
68 | 99 | 1050 | 57 | LDB | 52.2
68 | 99 | 1050 | 57 | LWB | 48.7
68 | 99 | 1050 | 57 | kW | 2.02
72 | 99 | 1050 | 61 | MBh | 27.6
72 | 99 | 1050 | 61 | S/T | 0.746
72 | 99 | 1050 | 61 | ∆T | 18.2
72 | 99 | 1050 | 61 | LDB | 53.8
72 | 99 | 1050 | 61 | LWB | 51.6
72 | 99 | 1050 | 61 | kW | 2.65
77 | 99 | 1050 | 64 | MBh | 31.3
77 | 99 | 1050 | 64 | S/T | 0.716
77 | 99 | 1050 | 64 | ∆T | 19.8
77 | 99 | 1050 | 64 | LDB | 57.2
77 | 99 | 1050 | 64 | LWB | 54
77 | 99 | 1050 | 64 | kW | 3.18
80 | 99 | 1050 | 67 | MBh | 35
80 | 99 | 1050 | 67 | S/T | 0.677
80 | 99 | 1050 | 67 | ∆T | 20.9
80 | 99 | 1050 | 67 | LDB | 59.1
80 | 99 | 1050 | 67 | LWB | 56.4
80 | 99 | 1050 | 67 | kW | 3.76
84 | 99 | 1050 | 70 | MBh | 36.5
84 | 99 | 1050 | 70 | S/T | 0.641
84 | 99 | 1050 | 70 | ∆T | 20.6
84 | 99 | 1050 | 70 | LDB | 63.4
84 | 99 | 1050 | 70 | LWB | 59.7
84 | 99 | 1050 | 70 | kW | 3.93
86 | 99 | 1050 | 72 | MBh | 37
86 | 99 | 1050 | 72 | S/T | 0.632
86 | 99 | 1050 | 72 | ∆T | 20.6
86 | 99 | 1050 | 72 | LDB | 65.4
86 | 99 | 1050 | 72 | LWB | 62
86 | 99 | 1050 | 72 | kW | 3.95
90 | 99 | 1050 | 75 | MBh | 37.7
90 | 99 | 1050 | 75 | S/T | 0.599
90 | 99 | 1050 | 75 | ∆T | 19.9
90 | 99 | 1050 | 75 | LDB | 70.1
90 | 99 | 1050 | 75 | LWB | 65.6
90 | 99 | 1050 | 75 | kW | 3.98
68 | 103 | 1050 | 57 | MBh | 22.7
68 | 103 | 1050 | 57 | S/T | 0.789
68 | 103 | 1050 | 57 | ∆T | 15.8
68 | 103 | 1050 | 57 | LDB | 52.2
68 | 103 | 1050 | 57 | LWB | 48.7
68 | 103 | 1050 | 57 | kW | 2.16
72 | 103 | 1050 | 61 | MBh | 27.6
72 | 103 | 1050 | 61 | S/T | 0.746
72 | 103 | 1050 | 61 | ∆T | 18.2
72 | 103 | 1050 | 61 | LDB | 53.8
72 | 103 | 1050 | 61 | LWB | 51.6
72 | 103 | 1050 | 61 | kW | 2.84
77 | 103 | 1050 | 64 | MBh | 31.3
77 | 103 | 1050 | 64 | S/T | 0.716
77 | 103 | 1050 | 64 | ∆T | 19.8
77 | 103 | 1050 | 64 | LDB | 57.2
77 | 103 | 1050 | 64 | LWB | 54
77 | 103 | 1050 | 64 | kW | 3.41
80 | 103 | 1050 | 67 | MBh | 35
80 | 103 | 1050 | 67 | S/T | 0.677
80 | 103 | 1050 | 67 | ∆T | 20.9
80 | 103 | 1050 | 67 | LDB | 59.1
80 | 103 | 1050 | 67 | LWB | 56.4
80 | 103 | 1050 | 67 | kW | 4.03
84 | 103 | 1050 | 70 | MBh | 35.8
84 | 103 | 1050 | 70 | S/T | 0.642
84 | 103 | 1050 | 70 | ∆T | 20.3
84 | 103 | 1050 | 70 | LDB | 63.7
84 | 103 | 1050 | 70 | LWB | 59.9
84 | 103 | 1050 | 70 | kW | 4.08
86 | 103 | 1050 | 72 | MBh | 36.3
86 | 103 | 1050 | 72 | S/T | 0.634
86 | 103 | 1050 | 72 | ∆T | 20.3
86 | 103 | 1050 | 72 | LDB | 65.7
86 | 103 | 1050 | 72 | LWB | 62.2
86 | 103 | 1050 | 72 | kW | 4.1
90 | 103 | 1050 | 75 | MBh | 37
90 | 103 | 1050 | 75 | S/T | 0.603
90 | 103 | 1050 | 75 | ∆T | 19.7
90 | 103 | 1050 | 75 | LDB | 70.3
90 | 103 | 1050 | 75 | LWB | 65.7
90 | 103 | 1050 | 75 | kW | 4.13
68 | 106 | 1050 | 57 | MBh | 22.7
68 | 106 | 1050 | 57 | S/T | 0.789
68 | 106 | 1050 | 57 | ∆T | 15.8
68 | 106 | 1050 | 57 | LDB | 52.2
68 | 106 | 1050 | 57 | LWB | 48.7
68 | 106 | 1050 | 57 | kW | 2.27
72 | 106 | 1050 | 61 | MBh | 27.6
72 | 106 | 1050 | 61 | S/T | 0.746
72 | 106 | 1050 | 61 | ∆T | 18.2
72 | 106 | 1050 | 61 | LDB | 53.8
72 | 106 | 1050 | 61 | LWB | 51.6
72 | 106 | 1050 | 61 | kW | 2.99
77 | 106 | 1050 | 64 | MBh | 31.3
77 | 106 | 1050 | 64 | S/T | 0.716
77 | 106 | 1050 | 64 | ∆T | 19.8
77 | 106 | 1050 | 64 | LDB | 57.2
77 | 106 | 1050 | 64 | LWB | 54
77 | 106 | 1050 | 64 | kW | 3.59
80 | 106 | 1050 | 67 | MBh | 34.6
80 | 106 | 1050 | 67 | S/T | 0.679
80 | 106 | 1050 | 67 | ∆T | 20.7
80 | 106 | 1050 | 67 | LDB | 59.3
80 | 106 | 1050 | 67 | LWB | 56.5
80 | 106 | 1050 | 67 | kW | 4.16
84 | 106 | 1050 | 70 | MBh | 35.3
84 | 106 | 1050 | 70 | S/T | 0.643
84 | 106 | 1050 | 70 | ∆T | 20
84 | 106 | 1050 | 70 | LDB | 64
84 | 106 | 1050 | 70 | LWB | 60.1
84 | 106 | 1050 | 70 | kW | 4.19
86 | 106 | 1050 | 72 | MBh | 35.8
86 | 106 | 1050 | 72 | S/T | 0.634
86 | 106 | 1050 | 72 | ∆T | 20
86 | 106 | 1050 | 72 | LDB | 66
86 | 106 | 1050 | 72 | LWB | 62.4
86 | 106 | 1050 | 72 | kW | 4.22
90 | 106 | 1050 | 75 | MBh | 36.4
90 | 106 | 1050 | 75 | S/T | 0.602
90 | 106 | 1050 | 75 | ∆T | 19.3
90 | 106 | 1050 | 75 | LDB | 70.7
90 | 106 | 1050 | 75 | LWB | 65.9
90 | 106 | 1050 | 75 | kW | 4.24
68 | 110 | 1050 | 57 | MBh | 22.7
68 | 110 | 1050 | 57 | S/T | 0.789
68 | 110 | 1050 | 57 | ∆T | 15.8
68 | 110 | 1050 | 57 | LDB | 52.2
68 | 110 | 1050 | 57 | LWB | 48.7
68 | 110 | 1050 | 57 | kW | 2.43
72 | 110 | 1050 | 61 | MBh | 27.6
72 | 110 | 1050 | 61 | S/T | 0.746
72 | 110 | 1050 | 61 | ∆T | 18.2
72 | 110 | 1050 | 61 | LDB | 53.8
72 | 110 | 1050 | 61 | LWB | 51.6
72 | 110 | 1050 | 61 | kW | 3.2
77 | 110 | 1050 | 64 | MBh | 31.3
77 | 110 | 1050 | 64 | S/T | 0.716
77 | 110 | 1050 | 64 | ∆T | 19.8
77 | 110 | 1050 | 64 | LDB | 57.2
77 | 110 | 1050 | 64 | LWB | 54
77 | 110 | 1050 | 64 | kW | 3.85
80 | 110 | 1050 | 67 | MBh | 33.9
80 | 110 | 1050 | 67 | S/T | 0.681
80 | 110 | 1050 | 67 | ∆T | 20.4
80 | 110 | 1050 | 67 | LDB | 59.6
80 | 110 | 1050 | 67 | LWB | 56.8
80 | 110 | 1050 | 67 | kW | 4.31
84 | 110 | 1050 | 70 | MBh | 34.6
84 | 110 | 1050 | 70 | S/T | 0.642
84 | 110 | 1050 | 70 | ∆T | 19.6
84 | 110 | 1050 | 70 | LDB | 64.4
84 | 110 | 1050 | 70 | LWB | 60.3
84 | 110 | 1050 | 70 | kW | 4.34
86 | 110 | 1050 | 72 | MBh | 34.6
86 | 110 | 1050 | 72 | S/T | 0.633
86 | 110 | 1050 | 72 | ∆T | 19.3
86 | 110 | 1050 | 72 | LDB | 66.7
86 | 110 | 1050 | 72 | LWB | 62.7
86 | 110 | 1050 | 72 | kW | 4.34
90 | 110 | 1050 | 75 | MBh | 34.6
90 | 110 | 1050 | 75 | S/T | 0.601
90 | 110 | 1050 | 75 | ∆T | 18.3
90 | 110 | 1050 | 75 | LDB | 71.7
90 | 110 | 1050 | 75 | LWB | 66.4
90 | 110 | 1050 | 75 | kW | 4.34
68 | 115 | 1050 | 57 | MBh | 22.7
68 | 115 | 1050 | 57 | S/T | 0.789
68 | 115 | 1050 | 57 | ∆T | 15.8
68 | 115 | 1050 | 57 | LDB | 52.2
68 | 115 | 1050 | 57 | LWB | 48.7
68 | 115 | 1050 | 57 | kW | 2.84
72 | 115 | 1050 | 61 | MBh | 27.6
72 | 115 | 1050 | 61 | S/T | 0.746
72 | 115 | 1050 | 61 | ∆T | 18.2
72 | 115 | 1050 | 61 | LDB | 53.8
72 | 115 | 1050 | 61 | LWB | 51.6
72 | 115 | 1050 | 61 | kW | 3.76
77 | 115 | 1050 | 64 | MBh | 31.2
77 | 115 | 1050 | 64 | S/T | 0.718
77 | 115 | 1050 | 64 | ∆T | 19.8
77 | 115 | 1050 | 64 | LDB | 57.2
77 | 115 | 1050 | 64 | LWB | 54
77 | 115 | 1050 | 64 | kW | 4.51
80 | 115 | 1050 | 67 | MBh | 31.2
80 | 115 | 1050 | 67 | S/T | 0.679
80 | 115 | 1050 | 67 | ∆T | 18.7
80 | 115 | 1050 | 67 | LDB | 61.3
80 | 115 | 1050 | 67 | LWB | 57.7
80 | 115 | 1050 | 67 | kW | 4.51
84 | 115 | 1050 | 70 | MBh | 31.2
84 | 115 | 1050 | 70 | S/T | 0.641
84 | 115 | 1050 | 70 | ∆T | 17.6
84 | 115 | 1050 | 70 | LDB | 66.4
84 | 115 | 1050 | 70 | LWB | 61.3
84 | 115 | 1050 | 70 | kW | 4.51
86 | 115 | 1050 | 72 | MBh | 31.2
86 | 115 | 1050 | 72 | S/T | 0.635
86 | 115 | 1050 | 72 | ∆T | 17.5
86 | 115 | 1050 | 72 | LDB | 68.5
86 | 115 | 1050 | 72 | LWB | 63.7
86 | 115 | 1050 | 72 | kW | 4.51
90 | 115 | 1050 | 75 | MBh | 31.2
90 | 115 | 1050 | 75 | S/T | 0.603
90 | 115 | 1050 | 75 | ∆T | 16.6
90 | 115 | 1050 | 75 | LDB | 73.4
90 | 115 | 1050 | 75 | LWB | 67.3
90 | 115 | 1050 | 75 | kW | 4.51
68 | 118 | 1050 | 57 | MBh | 22.7
68 | 118 | 1050 | 57 | S/T | 0.789
68 | 118 | 1050 | 57 | ∆T | 15.8
68 | 118 | 1050 | 57 | LDB | 52.2
68 | 118 | 1050 | 57 | LWB | 48.7
68 | 118 | 1050 | 57 | kW | 3.17
72 | 118 | 1050 | 61 | MBh | 26.9
72 | 118 | 1050 | 61 | S/T | 0.751
72 | 118 | 1050 | 61 | ∆T | 17.8
72 | 118 | 1050 | 61 | LDB | 54.2
72 | 118 | 1050 | 61 | LWB | 51.9
72 | 118 | 1050 | 61 | kW | 4.03
77 | 118 | 1050 | 64 | MBh | 26.9
77 | 118 | 1050 | 64 | S/T | 0.721
77 | 118 | 1050 | 64 | ∆T | 17.1
77 | 118 | 1050 | 64 | LDB | 59.9
77 | 118 | 1050 | 64 | LWB | 55.5
77 | 118 | 1050 | 64 | kW | 4.03
80 | 118 | 1050 | 67 | MBh | 26.9
80 | 118 | 1050 | 67 | S/T | 0.68
80 | 118 | 1050 | 67 | ∆T | 16.1
80 | 118 | 1050 | 67 | LDB | 63.9
80 | 118 | 1050 | 67 | LWB | 59.1
80 | 118 | 1050 | 67 | kW | 4.03
84 | 118 | 1050 | 70 | MBh | 26.9
84 | 118 | 1050 | 70 | S/T | 0.643
84 | 118 | 1050 | 70 | ∆T | 15.3
84 | 118 | 1050 | 70 | LDB | 68.7
84 | 118 | 1050 | 70 | LWB | 62.6
84 | 118 | 1050 | 70 | kW | 4.03
86 | 118 | 1050 | 72 | MBh | 26.9
86 | 118 | 1050 | 72 | S/T | 0.636
86 | 118 | 1050 | 72 | ∆T | 15.1
86 | 118 | 1050 | 72 | LDB | 70.9
86 | 118 | 1050 | 72 | LWB | 65
86 | 118 | 1050 | 72 | kW | 4.03
90 | 118 | 1050 | 75 | MBh | 26.9
90 | 118 | 1050 | 75 | S/T | 0.602
90 | 118 | 1050 | 75 | ∆T | 14.3
90 | 118 | 1050 | 75 | LDB | 75.7
90 | 118 | 1050 | 75 | LWB | 68.5
90 | 118 | 1050 | 75 | kW | 4.03
68 | 122 | 1050 | 57 | MBh | 21.2
68 | 122 | 1050 | 57 | S/T | 0.792
68 | 122 | 1050 | 57 | ∆T | 14.8
68 | 122 | 1050 | 57 | LDB | 53.2
68 | 122 | 1050 | 57 | LWB | 49.3
68 | 122 | 1050 | 57 | kW | 3.3
72 | 122 | 1050 | 61 | MBh | 21.2
72 | 122 | 1050 | 61 | S/T | 0.75
72 | 122 | 1050 | 61 | ∆T | 14
72 | 122 | 1050 | 61 | LDB | 58
72 | 122 | 1050 | 61 | LWB | 54
72 | 122 | 1050 | 61 | kW | 3.3
77 | 122 | 1050 | 64 | MBh | 21.2
77 | 122 | 1050 | 64 | S/T | 0.722
77 | 122 | 1050 | 64 | ∆T | 13.5
77 | 122 | 1050 | 64 | LDB | 63.5
77 | 122 | 1050 | 64 | LWB | 57.4
77 | 122 | 1050 | 64 | kW | 3.3
80 | 122 | 1050 | 67 | MBh | 21.2
80 | 122 | 1050 | 67 | S/T | 0.684
80 | 122 | 1050 | 67 | ∆T | 12.8
80 | 122 | 1050 | 67 | LDB | 67.2
80 | 122 | 1050 | 67 | LWB | 60.9
80 | 122 | 1050 | 67 | kW | 3.3
84 | 122 | 1050 | 70 | MBh | 21.2
84 | 122 | 1050 | 70 | S/T | 0.646
84 | 122 | 1050 | 70 | ∆T | 12.1
84 | 122 | 1050 | 70 | LDB | 71.9
84 | 122 | 1050 | 70 | LWB | 64.3
84 | 122 | 1050 | 70 | kW | 3.3
86 | 122 | 1050 | 72 | MBh | 21.2
86 | 122 | 1050 | 72 | S/T | 0.637
86 | 122 | 1050 | 72 | ∆T | 11.9
86 | 122 | 1050 | 72 | LDB | 74.1
86 | 122 | 1050 | 72 | LWB | 66.5
86 | 122 | 1050 | 72 | kW | 3.3
90 | 122 | 1050 | 75 | MBh | 21.2
90 | 122 | 1050 | 75 | S/T | 0.604
90 | 122 | 1050 | 75 | ∆T | 11.3
90 | 122 | 1050 | 75 | LDB | 78.7
90 | 122 | 1050 | 75 | LWB | 69.9
90 | 122 | 1050 | 75 | kW | 3.3

## RZA42AAVJU - FTA42AAVJUD
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1400 | 57 | MBh | 26.3 | 64 | 60 | 61 | 57.6 | 4.89
68 | 23 | 1400 | 57 | S/T | 0.84 | 64 | 60 | 65 | 53.4 | 4.16
68 | 23 | 1400 | 57 | ∆T | 14.6 | 64 | 60 | 68 | 50.1 | 3.62
68 | 23 | 1400 | 57 | LDB | 53.4 | 64 | 60 | 70 | 48 | 3.27
68 | 23 | 1400 | 57 | LWB | 49.9 | 64 | 60 | 72 | 45.9 | 2.92
68 | 23 | 1400 | 57 | kW | 1.19 | 64 | 60 | 75 | 42.6 | 2.41
72 | 23 | 1400 | 61 | MBh | 32 | 60 | 56 | 61 | 57.6 | 5.23
72 | 23 | 1400 | 61 | S/T | 0.806 | 60 | 56 | 65 | 53.4 | 4.47
72 | 23 | 1400 | 61 | ∆T | 17.1 | 60 | 56 | 68 | 50.1 | 3.9
72 | 23 | 1400 | 61 | LDB | 54.9 | 60 | 56 | 70 | 48 | 3.54
72 | 23 | 1400 | 61 | LWB | 53 | 60 | 56 | 72 | 45.9 | 3.17
72 | 23 | 1400 | 61 | kW | 1.46 | 60 | 56 | 75 | 42.6 | 2.64
77 | 23 | 1400 | 64 | MBh | 36.2 | 57 | 53 | 61 | 57.6 | 5.5
77 | 23 | 1400 | 64 | S/T | 0.779 | 57 | 53 | 65 | 53.4 | 4.71
77 | 23 | 1400 | 64 | ∆T | 18.7 | 57 | 53 | 68 | 50.1 | 4.13
77 | 23 | 1400 | 64 | LDB | 58.3 | 57 | 53 | 70 | 48 | 3.75
77 | 23 | 1400 | 64 | LWB | 55.4 | 57 | 53 | 72 | 45.9 | 3.38
77 | 23 | 1400 | 64 | kW | 1.68 | 57 | 53 | 75 | 42.6 | 2.82
80 | 23 | 1400 | 67 | MBh | 40.5 | 54 | 50 | 61 | 57.6 | 5.79
80 | 23 | 1400 | 67 | S/T | 0.728 | 54 | 50 | 65 | 53.4 | 4.97
80 | 23 | 1400 | 67 | ∆T | 19.5 | 54 | 50 | 68 | 50.1 | 4.37
80 | 23 | 1400 | 67 | LDB | 60.5 | 54 | 50 | 70 | 48 | 3.98
80 | 23 | 1400 | 67 | LWB | 57.9 | 54 | 50 | 72 | 45.9 | 3.59
80 | 23 | 1400 | 67 | kW | 1.9 | 54 | 50 | 75 | 42.6 | 3.02
84 | 23 | 1400 | 70 | MBh | 44.8 | 51 | 47 | 61 | 57.6 | 6.1
84 | 23 | 1400 | 70 | S/T | 0.683 | 51 | 47 | 65 | 53.4 | 5.25
84 | 23 | 1400 | 70 | ∆T | 20.2 | 51 | 47 | 68 | 50.1 | 4.63
84 | 23 | 1400 | 70 | LDB | 63.8 | 51 | 47 | 70 | 48 | 4.22
84 | 23 | 1400 | 70 | LWB | 60.6 | 51 | 47 | 72 | 45.9 | 3.82
84 | 23 | 1400 | 70 | kW | 2.13 | 51 | 47 | 75 | 42.6 | 3.23
86 | 23 | 1400 | 72 | MBh | 47.6 | 47 | 43 | 61 | 57.6 | 6.54
86 | 23 | 1400 | 72 | S/T | 0.676 | 47 | 43 | 65 | 53.4 | 5.65
86 | 23 | 1400 | 72 | ∆T | 21.3 | 47 | 43 | 68 | 50.1 | 5
86 | 23 | 1400 | 72 | LDB | 64.7 | 47 | 43 | 70 | 48 | 4.57
86 | 23 | 1400 | 72 | LWB | 62.4 | 47 | 43 | 72 | 45.9 | 4.15
86 | 23 | 1400 | 72 | kW | 2.29 | 47 | 43 | 75 | 42.6 | 3.52
90 | 23 | 1400 | 75 | MBh | 51.9 | 44 | 40 | 61 | 57.6 | 6.9
90 | 23 | 1400 | 75 | S/T | 0.63 | 44 | 40 | 65 | 53.4 | 5.97
90 | 23 | 1400 | 75 | ∆T | 21.6 | 44 | 40 | 68 | 50.1 | 5.29
90 | 23 | 1400 | 75 | LDB | 68.4 | 44 | 40 | 70 | 48 | 4.85
90 | 23 | 1400 | 75 | LWB | 65.2 | 44 | 40 | 72 | 45.9 | 4.41
90 | 23 | 1400 | 75 | kW | 2.53 | 44 | 40 | 75 | 42.6 | 3.77
68 | 30 | 1400 | 57 | MBh | 26.3 | 39 | 36 | 61 | 57.6 | 7.42
68 | 30 | 1400 | 57 | S/T | 0.84 | 39 | 36 | 65 | 53.4 | 6.44
68 | 30 | 1400 | 57 | ∆T | 14.6 | 39 | 36 | 68 | 50.1 | 5.72
68 | 30 | 1400 | 57 | LDB | 53.4 | 39 | 36 | 70 | 48 | 5.25
68 | 30 | 1400 | 57 | LWB | 49.9 | 39 | 36 | 72 | 45.9 | 4.79
68 | 30 | 1400 | 57 | kW | 1.22 | 39 | 36 | 75 | 42.6 | 4.11
72 | 30 | 1400 | 61 | MBh | 32 | 35 | 32 | 61 | 56.8 | 7.99
72 | 30 | 1400 | 61 | S/T | 0.806 | 35 | 32 | 65 | 53.4 | 6.95
72 | 30 | 1400 | 61 | ∆T | 17.1 | 35 | 32 | 68 | 50.1 | 6.2
72 | 30 | 1400 | 61 | LDB | 54.9 | 35 | 32 | 70 | 48 | 5.7
72 | 30 | 1400 | 61 | LWB | 53 | 35 | 32 | 72 | 45.9 | 5.21
72 | 30 | 1400 | 61 | kW | 1.51 | 35 | 32 | 75 | 42.6 | 4.5
77 | 30 | 1400 | 64 | MBh | 36.2 | 30 | 28 | 61 | 54.3 | 8.33
77 | 30 | 1400 | 64 | S/T | 0.779 | 30 | 28 | 65 | 53.4 | 7.52
77 | 30 | 1400 | 64 | ∆T | 18.7 | 30 | 28 | 68 | 50.1 | 6.72
77 | 30 | 1400 | 64 | LDB | 58.3 | 30 | 28 | 70 | 48 | 6.2
77 | 30 | 1400 | 64 | LWB | 55.4 | 30 | 28 | 72 | 45.9 | 5.68
77 | 30 | 1400 | 64 | kW | 1.73 | 30 | 28 | 75 | 42.6 | 4.92
80 | 30 | 1400 | 67 | MBh | 40.5 | 26 | 24 | 61 | 51.8 | 7.98
80 | 30 | 1400 | 67 | S/T | 0.728 | 26 | 24 | 65 | 51.8 | 8.16
80 | 30 | 1400 | 67 | ∆T | 19.5 | 26 | 24 | 68 | 50.1 | 7.3
80 | 30 | 1400 | 67 | LDB | 60.5 | 26 | 24 | 70 | 48 | 6.74
80 | 30 | 1400 | 67 | LWB | 57.9 | 26 | 24 | 72 | 45.9 | 6.19
80 | 30 | 1400 | 67 | kW | 1.96 | 26 | 24 | 75 | 42.6 | 5.39
84 | 30 | 1400 | 70 | MBh | 44.8 | 22 | 20 | 61 | 49.3 | 7.61
84 | 30 | 1400 | 70 | S/T | 0.683 | 22 | 20 | 65 | 49.3 | 8.14
84 | 30 | 1400 | 70 | ∆T | 20.2 | 22 | 20 | 68 | 49.3 | 7.95
84 | 30 | 1400 | 70 | LDB | 63.8 | 22 | 20 | 70 | 48 | 7.36
84 | 30 | 1400 | 70 | LWB | 60.6 | 22 | 20 | 72 | 45.9 | 6.77
84 | 30 | 1400 | 70 | kW | 2.2 | 22 | 20 | 75 | 42.6 | 5.91
86 | 30 | 1400 | 72 | MBh | 47.6 | 19 | 18 | 61 | 48.1 | 7.41
86 | 30 | 1400 | 72 | S/T | 0.676 | 19 | 18 | 65 | 48.1 | 7.84
86 | 30 | 1400 | 72 | ∆T | 21.3 | 19 | 18 | 68 | 48.1 | 7.84
86 | 30 | 1400 | 72 | LDB | 64.7 | 19 | 18 | 70 | 48 | 7.69
86 | 30 | 1400 | 72 | LWB | 62.4 | 19 | 18 | 72 | 45.9 | 7.08
86 | 30 | 1400 | 72 | kW | 2.37 | 19 | 18 | 75 | 42.6 | 6.19
90 | 30 | 1400 | 75 | MBh | 51.9 | 17 | 16 | 61 | 46.5 | 7.14
90 | 30 | 1400 | 75 | S/T | 0.63 | 17 | 16 | 65 | 46.5 | 7.46
90 | 30 | 1400 | 75 | ∆T | 21.6 | 17 | 16 | 68 | 46.5 | 7.46
90 | 30 | 1400 | 75 | LDB | 68.4 | 17 | 16 | 70 | 46.5 | 7.46
90 | 30 | 1400 | 75 | LWB | 65.2 | 17 | 16 | 72 | 45.9 | 7.46
90 | 30 | 1400 | 75 | kW | 2.61 | 17 | 16 | 75 | 42.6 | 6.58
68 | 40 | 1400 | 57 | MBh | 26.3 | 15 | 14 | 61 | 45.6 | 6.97
68 | 40 | 1400 | 57 | S/T | 0.84 | 15 | 14 | 65 | 45.6 | 7.23
68 | 40 | 1400 | 57 | ∆T | 14.6 | 15 | 14 | 68 | 45.6 | 7.23
68 | 40 | 1400 | 57 | LDB | 53.4 | 15 | 14 | 70 | 45.6 | 7.23
68 | 40 | 1400 | 57 | LWB | 49.9 | 15 | 14 | 72 | 45.6 | 7.23
68 | 40 | 1400 | 57 | kW | 1.28 | 15 | 14 | 75 | 42.6 | 6.82
72 | 40 | 1400 | 61 | MBh | 32 | 13 | 12 | 61 | 44.4 | 6.74
72 | 40 | 1400 | 61 | S/T | 0.806 | 13 | 12 | 65 | 44.4 | 6.93
72 | 40 | 1400 | 61 | ∆T | 17.1 | 13 | 12 | 68 | 44.4 | 6.93
72 | 40 | 1400 | 61 | LDB | 54.9 | 13 | 12 | 70 | 44.4 | 6.93
72 | 40 | 1400 | 61 | LWB | 53 | 13 | 12 | 72 | 44.4 | 6.93
72 | 40 | 1400 | 61 | kW | 1.58 | 13 | 12 | 75 | 42.6 | 6.93
77 | 40 | 1400 | 64 | MBh | 36.2 | 10 | 9 | 61 | 42.2 | 6.3
77 | 40 | 1400 | 64 | S/T | 0.779 | 10 | 9 | 65 | 42.2 | 6.39
77 | 40 | 1400 | 64 | ∆T | 18.7 | 10 | 9 | 68 | 42.2 | 6.39
77 | 40 | 1400 | 64 | LDB | 58.3 | 10 | 9 | 70 | 42.2 | 6.39
77 | 40 | 1400 | 64 | LWB | 55.4 | 10 | 9 | 72 | 42.2 | 6.39
77 | 40 | 1400 | 64 | kW | 1.81 | 10 | 9 | 75 | 42.2 | 6.39
80 | 40 | 1400 | 67 | MBh | 40.5 | 6 | 5 | 61 | 40 | 5.81
80 | 40 | 1400 | 67 | S/T | 0.728 | 6 | 5 | 65 | 40 | 5.86
80 | 40 | 1400 | 67 | ∆T | 19.5 | 6 | 5 | 68 | 40 | 5.86
80 | 40 | 1400 | 67 | LDB | 60.5 | 6 | 5 | 70 | 40 | 5.86
80 | 40 | 1400 | 67 | LWB | 57.9 | 6 | 5 | 72 | 40 | 5.86
80 | 40 | 1400 | 67 | kW | 2.06 | 6 | 5 | 75 | 40 | 5.86
84 | 40 | 1400 | 70 | MBh | 44.8 | -2 | -2 | 61 | 33.1 | 4.63
84 | 40 | 1400 | 70 | S/T | 0.683 | -2 | -2 | 65 | 33.1 | 4.76
84 | 40 | 1400 | 70 | ∆T | 20.2 | -2 | -2 | 68 | 33.1 | 4.76
84 | 40 | 1400 | 70 | LDB | 63.8 | -2 | -2 | 70 | 33.1 | 4.76
84 | 40 | 1400 | 70 | LWB | 60.6 | -2 | -2 | 72 | 33.1 | 4.76
84 | 40 | 1400 | 70 | kW | 2.31 | -2 | -2 | 75 | 33.1 | 4.76
86 | 40 | 1400 | 72 | MBh | 47.6 | -4 | -4 | 61 | 31.4 | 4.29
86 | 40 | 1400 | 72 | S/T | 0.676 | -4 | -4 | 65 | 31.4 | 4.49
86 | 40 | 1400 | 72 | ∆T | 21.3 | -4 | -4 | 68 | 31.4 | 4.49
86 | 40 | 1400 | 72 | LDB | 64.7 | -4 | -4 | 70 | 31.4 | 4.49
86 | 40 | 1400 | 72 | LWB | 62.4 | -4 | -4 | 72 | 31.4 | 4.49
86 | 40 | 1400 | 72 | kW | 2.48 | -4 | -4 | 75 | 31.4 | 4.49
90 | 40 | 1400 | 75 | MBh | 51.9
90 | 40 | 1400 | 75 | S/T | 0.63
90 | 40 | 1400 | 75 | ∆T | 21.6
90 | 40 | 1400 | 75 | LDB | 68.4
90 | 40 | 1400 | 75 | LWB | 65.2
90 | 40 | 1400 | 75 | kW | 2.74
68 | 50 | 1400 | 57 | MBh | 26.3
68 | 50 | 1400 | 57 | S/T | 0.84
68 | 50 | 1400 | 57 | ∆T | 14.6
68 | 50 | 1400 | 57 | LDB | 53.4
68 | 50 | 1400 | 57 | LWB | 49.9
68 | 50 | 1400 | 57 | kW | 1.34
72 | 50 | 1400 | 61 | MBh | 32
72 | 50 | 1400 | 61 | S/T | 0.806
72 | 50 | 1400 | 61 | ∆T | 17.1
72 | 50 | 1400 | 61 | LDB | 54.9
72 | 50 | 1400 | 61 | LWB | 53
72 | 50 | 1400 | 61 | kW | 1.66
77 | 50 | 1400 | 64 | MBh | 36.2
77 | 50 | 1400 | 64 | S/T | 0.779
77 | 50 | 1400 | 64 | ∆T | 18.7
77 | 50 | 1400 | 64 | LDB | 58.3
77 | 50 | 1400 | 64 | LWB | 55.4
77 | 50 | 1400 | 64 | kW | 1.91
80 | 50 | 1400 | 67 | MBh | 40.5
80 | 50 | 1400 | 67 | S/T | 0.728
80 | 50 | 1400 | 67 | ∆T | 19.5
80 | 50 | 1400 | 67 | LDB | 60.5
80 | 50 | 1400 | 67 | LWB | 57.9
80 | 50 | 1400 | 67 | kW | 2.17
84 | 50 | 1400 | 70 | MBh | 44.8
84 | 50 | 1400 | 70 | S/T | 0.683
84 | 50 | 1400 | 70 | ∆T | 20.2
84 | 50 | 1400 | 70 | LDB | 63.8
84 | 50 | 1400 | 70 | LWB | 60.6
84 | 50 | 1400 | 70 | kW | 2.43
86 | 50 | 1400 | 72 | MBh | 47.6
86 | 50 | 1400 | 72 | S/T | 0.676
86 | 50 | 1400 | 72 | ∆T | 21.3
86 | 50 | 1400 | 72 | LDB | 64.7
86 | 50 | 1400 | 72 | LWB | 62.4
86 | 50 | 1400 | 72 | kW | 2.61
90 | 50 | 1400 | 75 | MBh | 51.9
90 | 50 | 1400 | 75 | S/T | 0.63
90 | 50 | 1400 | 75 | ∆T | 21.6
90 | 50 | 1400 | 75 | LDB | 68.4
90 | 50 | 1400 | 75 | LWB | 65.2
90 | 50 | 1400 | 75 | kW | 2.88
68 | 54 | 1400 | 57 | MBh | 26.3
68 | 54 | 1400 | 57 | S/T | 0.84
68 | 54 | 1400 | 57 | ∆T | 14.6
68 | 54 | 1400 | 57 | LDB | 53.4
68 | 54 | 1400 | 57 | LWB | 49.9
68 | 54 | 1400 | 57 | kW | 1.36
72 | 54 | 1400 | 61 | MBh | 32
72 | 54 | 1400 | 61 | S/T | 0.806
72 | 54 | 1400 | 61 | ∆T | 17.1
72 | 54 | 1400 | 61 | LDB | 54.9
72 | 54 | 1400 | 61 | LWB | 53
72 | 54 | 1400 | 61 | kW | 1.69
77 | 54 | 1400 | 64 | MBh | 36.2
77 | 54 | 1400 | 64 | S/T | 0.779
77 | 54 | 1400 | 64 | ∆T | 18.7
77 | 54 | 1400 | 64 | LDB | 58.3
77 | 54 | 1400 | 64 | LWB | 55.4
77 | 54 | 1400 | 64 | kW | 1.95
80 | 54 | 1400 | 67 | MBh | 40.5
80 | 54 | 1400 | 67 | S/T | 0.728
80 | 54 | 1400 | 67 | ∆T | 19.5
80 | 54 | 1400 | 67 | LDB | 60.5
80 | 54 | 1400 | 67 | LWB | 57.9
80 | 54 | 1400 | 67 | kW | 2.21
84 | 54 | 1400 | 70 | MBh | 44.8
84 | 54 | 1400 | 70 | S/T | 0.683
84 | 54 | 1400 | 70 | ∆T | 20.2
84 | 54 | 1400 | 70 | LDB | 63.8
84 | 54 | 1400 | 70 | LWB | 60.6
84 | 54 | 1400 | 70 | kW | 2.48
86 | 54 | 1400 | 72 | MBh | 47.6
86 | 54 | 1400 | 72 | S/T | 0.676
86 | 54 | 1400 | 72 | ∆T | 21.3
86 | 54 | 1400 | 72 | LDB | 64.7
86 | 54 | 1400 | 72 | LWB | 62.4
86 | 54 | 1400 | 72 | kW | 2.67
90 | 54 | 1400 | 75 | MBh | 51.9
90 | 54 | 1400 | 75 | S/T | 0.63
90 | 54 | 1400 | 75 | ∆T | 21.6
90 | 54 | 1400 | 75 | LDB | 68.4
90 | 54 | 1400 | 75 | LWB | 65.2
90 | 54 | 1400 | 75 | kW | 2.94
68 | 58 | 1400 | 57 | MBh | 26.3
68 | 58 | 1400 | 57 | S/T | 0.84
68 | 58 | 1400 | 57 | ∆T | 14.6
68 | 58 | 1400 | 57 | LDB | 53.4
68 | 58 | 1400 | 57 | LWB | 49.9
68 | 58 | 1400 | 57 | kW | 1.39
72 | 58 | 1400 | 61 | MBh | 32
72 | 58 | 1400 | 61 | S/T | 0.806
72 | 58 | 1400 | 61 | ∆T | 17.1
72 | 58 | 1400 | 61 | LDB | 54.9
72 | 58 | 1400 | 61 | LWB | 53
72 | 58 | 1400 | 61 | kW | 1.72
77 | 58 | 1400 | 64 | MBh | 36.2
77 | 58 | 1400 | 64 | S/T | 0.779
77 | 58 | 1400 | 64 | ∆T | 18.7
77 | 58 | 1400 | 64 | LDB | 58.3
77 | 58 | 1400 | 64 | LWB | 55.4
77 | 58 | 1400 | 64 | kW | 1.99
80 | 58 | 1400 | 67 | MBh | 40.5
80 | 58 | 1400 | 67 | S/T | 0.728
80 | 58 | 1400 | 67 | ∆T | 19.5
80 | 58 | 1400 | 67 | LDB | 60.5
80 | 58 | 1400 | 67 | LWB | 57.9
80 | 58 | 1400 | 67 | kW | 2.26
84 | 58 | 1400 | 70 | MBh | 44.8
84 | 58 | 1400 | 70 | S/T | 0.683
84 | 58 | 1400 | 70 | ∆T | 20.2
84 | 58 | 1400 | 70 | LDB | 63.8
84 | 58 | 1400 | 70 | LWB | 60.6
84 | 58 | 1400 | 70 | kW | 2.54
86 | 58 | 1400 | 72 | MBh | 47.6
86 | 58 | 1400 | 72 | S/T | 0.676
86 | 58 | 1400 | 72 | ∆T | 21.3
86 | 58 | 1400 | 72 | LDB | 64.7
86 | 58 | 1400 | 72 | LWB | 62.4
86 | 58 | 1400 | 72 | kW | 2.72
90 | 58 | 1400 | 75 | MBh | 51.4
90 | 58 | 1400 | 75 | S/T | 0.63
90 | 58 | 1400 | 75 | ∆T | 21.4
90 | 58 | 1400 | 75 | LDB | 68.6
90 | 58 | 1400 | 75 | LWB | 65.3
90 | 58 | 1400 | 75 | kW | 2.96
68 | 62 | 1400 | 57 | MBh | 26.3
68 | 62 | 1400 | 57 | S/T | 0.84
68 | 62 | 1400 | 57 | ∆T | 14.6
68 | 62 | 1400 | 57 | LDB | 53.4
68 | 62 | 1400 | 57 | LWB | 49.9
68 | 62 | 1400 | 57 | kW | 1.42
72 | 62 | 1400 | 61 | MBh | 32
72 | 62 | 1400 | 61 | S/T | 0.806
72 | 62 | 1400 | 61 | ∆T | 17.1
72 | 62 | 1400 | 61 | LDB | 54.9
72 | 62 | 1400 | 61 | LWB | 53
72 | 62 | 1400 | 61 | kW | 1.76
77 | 62 | 1400 | 64 | MBh | 36.2
77 | 62 | 1400 | 64 | S/T | 0.779
77 | 62 | 1400 | 64 | ∆T | 18.7
77 | 62 | 1400 | 64 | LDB | 58.3
77 | 62 | 1400 | 64 | LWB | 55.4
77 | 62 | 1400 | 64 | kW | 2.03
80 | 62 | 1400 | 67 | MBh | 40.5
80 | 62 | 1400 | 67 | S/T | 0.728
80 | 62 | 1400 | 67 | ∆T | 19.5
80 | 62 | 1400 | 67 | LDB | 60.5
80 | 62 | 1400 | 67 | LWB | 57.9
80 | 62 | 1400 | 67 | kW | 2.31
84 | 62 | 1400 | 70 | MBh | 44.8
84 | 62 | 1400 | 70 | S/T | 0.683
84 | 62 | 1400 | 70 | ∆T | 20.2
84 | 62 | 1400 | 70 | LDB | 63.8
84 | 62 | 1400 | 70 | LWB | 60.6
84 | 62 | 1400 | 70 | kW | 2.59
86 | 62 | 1400 | 72 | MBh | 47.6
86 | 62 | 1400 | 72 | S/T | 0.676
86 | 62 | 1400 | 72 | ∆T | 21.3
86 | 62 | 1400 | 72 | LDB | 64.7
86 | 62 | 1400 | 72 | LWB | 62.4
86 | 62 | 1400 | 72 | kW | 2.78
90 | 62 | 1400 | 75 | MBh | 50.6
90 | 62 | 1400 | 75 | S/T | 0.63
90 | 62 | 1400 | 75 | ∆T | 21.1
90 | 62 | 1400 | 75 | LDB | 68.9
90 | 62 | 1400 | 75 | LWB | 65.5
90 | 62 | 1400 | 75 | kW | 3.02
68 | 66 | 1400 | 57 | MBh | 26.3
68 | 66 | 1400 | 57 | S/T | 0.84
68 | 66 | 1400 | 57 | ∆T | 14.6
68 | 66 | 1400 | 57 | LDB | 53.4
68 | 66 | 1400 | 57 | LWB | 49.9
68 | 66 | 1400 | 57 | kW | 1.45
72 | 66 | 1400 | 61 | MBh | 32
72 | 66 | 1400 | 61 | S/T | 0.806
72 | 66 | 1400 | 61 | ∆T | 17.1
72 | 66 | 1400 | 61 | LDB | 54.9
72 | 66 | 1400 | 61 | LWB | 53
72 | 66 | 1400 | 61 | kW | 1.8
77 | 66 | 1400 | 64 | MBh | 36.2
77 | 66 | 1400 | 64 | S/T | 0.779
77 | 66 | 1400 | 64 | ∆T | 18.7
77 | 66 | 1400 | 64 | LDB | 58.3
77 | 66 | 1400 | 64 | LWB | 55.4
77 | 66 | 1400 | 64 | kW | 2.07
80 | 66 | 1400 | 67 | MBh | 40.5
80 | 66 | 1400 | 67 | S/T | 0.728
80 | 66 | 1400 | 67 | ∆T | 19.5
80 | 66 | 1400 | 67 | LDB | 60.5
80 | 66 | 1400 | 67 | LWB | 57.9
80 | 66 | 1400 | 67 | kW | 2.36
84 | 66 | 1400 | 70 | MBh | 44.8
84 | 66 | 1400 | 70 | S/T | 0.683
84 | 66 | 1400 | 70 | ∆T | 20.2
84 | 66 | 1400 | 70 | LDB | 63.8
84 | 66 | 1400 | 70 | LWB | 60.6
84 | 66 | 1400 | 70 | kW | 2.74
86 | 66 | 1400 | 72 | MBh | 47.6
86 | 66 | 1400 | 72 | S/T | 0.676
86 | 66 | 1400 | 72 | ∆T | 21.3
86 | 66 | 1400 | 72 | LDB | 64.7
86 | 66 | 1400 | 72 | LWB | 62.4
86 | 66 | 1400 | 72 | kW | 3
90 | 66 | 1400 | 75 | MBh | 49.9
90 | 66 | 1400 | 75 | S/T | 0.631
90 | 66 | 1400 | 75 | ∆T | 20.8
90 | 66 | 1400 | 75 | LDB | 69.2
90 | 66 | 1400 | 75 | LWB | 65.6
90 | 66 | 1400 | 75 | kW | 3.19
68 | 70 | 1400 | 57 | MBh | 26.3
68 | 70 | 1400 | 57 | S/T | 0.844
68 | 70 | 1400 | 57 | ∆T | 14.7
68 | 70 | 1400 | 57 | LDB | 53.3
68 | 70 | 1400 | 57 | LWB | 49.9
68 | 70 | 1400 | 57 | kW | 1.48
72 | 70 | 1400 | 61 | MBh | 32
72 | 70 | 1400 | 61 | S/T | 0.806
72 | 70 | 1400 | 61 | ∆T | 17.1
72 | 70 | 1400 | 61 | LDB | 54.9
72 | 70 | 1400 | 61 | LWB | 53
72 | 70 | 1400 | 61 | kW | 1.84
77 | 70 | 1400 | 64 | MBh | 36.2
77 | 70 | 1400 | 64 | S/T | 0.779
77 | 70 | 1400 | 64 | ∆T | 18.7
77 | 70 | 1400 | 64 | LDB | 58.3
77 | 70 | 1400 | 64 | LWB | 55.4
77 | 70 | 1400 | 64 | kW | 2.18
80 | 70 | 1400 | 67 | MBh | 40.5
80 | 70 | 1400 | 67 | S/T | 0.728
80 | 70 | 1400 | 67 | ∆T | 19.5
80 | 70 | 1400 | 67 | LDB | 60.5
80 | 70 | 1400 | 67 | LWB | 57.9
80 | 70 | 1400 | 67 | kW | 2.55
84 | 70 | 1400 | 70 | MBh | 44.8
84 | 70 | 1400 | 70 | S/T | 0.683
84 | 70 | 1400 | 70 | ∆T | 20.2
84 | 70 | 1400 | 70 | LDB | 63.8
84 | 70 | 1400 | 70 | LWB | 60.6
84 | 70 | 1400 | 70 | kW | 2.96
86 | 70 | 1400 | 72 | MBh | 47.6
86 | 70 | 1400 | 72 | S/T | 0.676
86 | 70 | 1400 | 72 | ∆T | 21.3
86 | 70 | 1400 | 72 | LDB | 64.7
86 | 70 | 1400 | 72 | LWB | 62.4
86 | 70 | 1400 | 72 | kW | 3.25
90 | 70 | 1400 | 75 | MBh | 49.1
90 | 70 | 1400 | 75 | S/T | 0.631
90 | 70 | 1400 | 75 | ∆T | 20.5
90 | 70 | 1400 | 75 | LDB | 69.5
90 | 70 | 1400 | 75 | LWB | 65.8
90 | 70 | 1400 | 75 | kW | 3.36
68 | 72 | 1400 | 57 | MBh | 26.3
68 | 72 | 1400 | 57 | S/T | 0.844
68 | 72 | 1400 | 57 | ∆T | 14.7
68 | 72 | 1400 | 57 | LDB | 53.3
68 | 72 | 1400 | 57 | LWB | 49.9
68 | 72 | 1400 | 57 | kW | 1.49
72 | 72 | 1400 | 61 | MBh | 32
72 | 72 | 1400 | 61 | S/T | 0.806
72 | 72 | 1400 | 61 | ∆T | 17.1
72 | 72 | 1400 | 61 | LDB | 54.9
72 | 72 | 1400 | 61 | LWB | 53
72 | 72 | 1400 | 61 | kW | 1.9
77 | 72 | 1400 | 64 | MBh | 36.2
77 | 72 | 1400 | 64 | S/T | 0.779
77 | 72 | 1400 | 64 | ∆T | 18.7
77 | 72 | 1400 | 64 | LDB | 58.3
77 | 72 | 1400 | 64 | LWB | 55.4
77 | 72 | 1400 | 64 | kW | 2.26
80 | 72 | 1400 | 67 | MBh | 40.5
80 | 72 | 1400 | 67 | S/T | 0.728
80 | 72 | 1400 | 67 | ∆T | 19.5
80 | 72 | 1400 | 67 | LDB | 60.5
80 | 72 | 1400 | 67 | LWB | 57.9
80 | 72 | 1400 | 67 | kW | 2.65
84 | 72 | 1400 | 70 | MBh | 44.8
84 | 72 | 1400 | 70 | S/T | 0.683
84 | 72 | 1400 | 70 | ∆T | 20.2
84 | 72 | 1400 | 70 | LDB | 63.8
84 | 72 | 1400 | 70 | LWB | 60.6
84 | 72 | 1400 | 70 | kW | 3.08
86 | 72 | 1400 | 72 | MBh | 47.6
86 | 72 | 1400 | 72 | S/T | 0.676
86 | 72 | 1400 | 72 | ∆T | 21.3
86 | 72 | 1400 | 72 | LDB | 64.7
86 | 72 | 1400 | 72 | LWB | 62.4
86 | 72 | 1400 | 72 | kW | 3.38
90 | 72 | 1400 | 75 | MBh | 48.7
90 | 72 | 1400 | 75 | S/T | 0.63
90 | 72 | 1400 | 75 | ∆T | 20.3
90 | 72 | 1400 | 75 | LDB | 69.7
90 | 72 | 1400 | 75 | LWB | 65.9
90 | 72 | 1400 | 75 | kW | 3.44
68 | 75 | 1400 | 57 | MBh | 26.3
68 | 75 | 1400 | 57 | S/T | 0.844
68 | 75 | 1400 | 57 | ∆T | 14.7
68 | 75 | 1400 | 57 | LDB | 53.3
68 | 75 | 1400 | 57 | LWB | 49.9
68 | 75 | 1400 | 57 | kW | 1.55
72 | 75 | 1400 | 61 | MBh | 32
72 | 75 | 1400 | 61 | S/T | 0.806
72 | 75 | 1400 | 61 | ∆T | 17.1
72 | 75 | 1400 | 61 | LDB | 54.9
72 | 75 | 1400 | 61 | LWB | 53
72 | 75 | 1400 | 61 | kW | 2.01
77 | 75 | 1400 | 64 | MBh | 36.2
77 | 75 | 1400 | 64 | S/T | 0.779
77 | 75 | 1400 | 64 | ∆T | 18.7
77 | 75 | 1400 | 64 | LDB | 58.3
77 | 75 | 1400 | 64 | LWB | 55.4
77 | 75 | 1400 | 64 | kW | 2.39
80 | 75 | 1400 | 67 | MBh | 40.5
80 | 75 | 1400 | 67 | S/T | 0.728
80 | 75 | 1400 | 67 | ∆T | 19.5
80 | 75 | 1400 | 67 | LDB | 60.5
80 | 75 | 1400 | 67 | LWB | 57.9
80 | 75 | 1400 | 67 | kW | 2.81
84 | 75 | 1400 | 70 | MBh | 44.8
84 | 75 | 1400 | 70 | S/T | 0.683
84 | 75 | 1400 | 70 | ∆T | 20.2
84 | 75 | 1400 | 70 | LDB | 63.8
84 | 75 | 1400 | 70 | LWB | 60.6
84 | 75 | 1400 | 70 | kW | 3.26
86 | 75 | 1400 | 72 | MBh | 47.3
86 | 75 | 1400 | 72 | S/T | 0.677
86 | 75 | 1400 | 72 | ∆T | 21.2
86 | 75 | 1400 | 72 | LDB | 64.8
86 | 75 | 1400 | 72 | LWB | 62.5
86 | 75 | 1400 | 72 | kW | 3.55
90 | 75 | 1400 | 75 | MBh | 48.2
90 | 75 | 1400 | 75 | S/T | 0.631
90 | 75 | 1400 | 75 | ∆T | 20.1
90 | 75 | 1400 | 75 | LDB | 69.9
90 | 75 | 1400 | 75 | LWB | 66
90 | 75 | 1400 | 75 | kW | 3.57
68 | 79 | 1400 | 57 | MBh | 26.3
68 | 79 | 1400 | 57 | S/T | 0.844
68 | 79 | 1400 | 57 | ∆T | 14.7
68 | 79 | 1400 | 57 | LDB | 53.3
68 | 79 | 1400 | 57 | LWB | 49.9
68 | 79 | 1400 | 57 | kW | 1.66
72 | 79 | 1400 | 61 | MBh | 32
72 | 79 | 1400 | 61 | S/T | 0.806
72 | 79 | 1400 | 61 | ∆T | 17.1
72 | 79 | 1400 | 61 | LDB | 54.9
72 | 79 | 1400 | 61 | LWB | 53
72 | 79 | 1400 | 61 | kW | 2.16
77 | 79 | 1400 | 64 | MBh | 36.2
77 | 79 | 1400 | 64 | S/T | 0.779
77 | 79 | 1400 | 64 | ∆T | 18.7
77 | 79 | 1400 | 64 | LDB | 58.3
77 | 79 | 1400 | 64 | LWB | 55.4
77 | 79 | 1400 | 64 | kW | 2.58
80 | 79 | 1400 | 67 | MBh | 40.5
80 | 79 | 1400 | 67 | S/T | 0.728
80 | 79 | 1400 | 67 | ∆T | 19.5
80 | 79 | 1400 | 67 | LDB | 60.5
80 | 79 | 1400 | 67 | LWB | 57.9
80 | 79 | 1400 | 67 | kW | 3.03
84 | 79 | 1400 | 70 | MBh | 44.8
84 | 79 | 1400 | 70 | S/T | 0.683
84 | 79 | 1400 | 70 | ∆T | 20.2
84 | 79 | 1400 | 70 | LDB | 63.8
84 | 79 | 1400 | 70 | LWB | 60.6
84 | 79 | 1400 | 70 | kW | 3.52
86 | 79 | 1400 | 72 | MBh | 46.6
86 | 79 | 1400 | 72 | S/T | 0.676
86 | 79 | 1400 | 72 | ∆T | 20.8
86 | 79 | 1400 | 72 | LDB | 65.2
86 | 79 | 1400 | 72 | LWB | 62.6
86 | 79 | 1400 | 72 | kW | 3.72
90 | 79 | 1400 | 75 | MBh | 47.4
90 | 79 | 1400 | 75 | S/T | 0.631
90 | 79 | 1400 | 75 | ∆T | 19.8
90 | 79 | 1400 | 75 | LDB | 70.2
90 | 79 | 1400 | 75 | LWB | 66.1
90 | 79 | 1400 | 75 | kW | 3.74
68 | 83 | 1400 | 57 | MBh | 26.3
68 | 83 | 1400 | 57 | S/T | 0.844
68 | 83 | 1400 | 57 | ∆T | 14.7
68 | 83 | 1400 | 57 | LDB | 53.3
68 | 83 | 1400 | 57 | LWB | 49.9
68 | 83 | 1400 | 57 | kW | 1.78
72 | 83 | 1400 | 61 | MBh | 32
72 | 83 | 1400 | 61 | S/T | 0.806
72 | 83 | 1400 | 61 | ∆T | 17.1
72 | 83 | 1400 | 61 | LDB | 54.9
72 | 83 | 1400 | 61 | LWB | 53
72 | 83 | 1400 | 61 | kW | 2.32
77 | 83 | 1400 | 64 | MBh | 36.2
77 | 83 | 1400 | 64 | S/T | 0.779
77 | 83 | 1400 | 64 | ∆T | 18.7
77 | 83 | 1400 | 64 | LDB | 58.3
77 | 83 | 1400 | 64 | LWB | 55.4
77 | 83 | 1400 | 64 | kW | 2.77
80 | 83 | 1400 | 67 | MBh | 40.5
80 | 83 | 1400 | 67 | S/T | 0.728
80 | 83 | 1400 | 67 | ∆T | 19.5
80 | 83 | 1400 | 67 | LDB | 60.5
80 | 83 | 1400 | 67 | LWB | 57.9
80 | 83 | 1400 | 67 | kW | 3.26
84 | 83 | 1400 | 70 | MBh | 44.8
84 | 83 | 1400 | 70 | S/T | 0.683
84 | 83 | 1400 | 70 | ∆T | 20.2
84 | 83 | 1400 | 70 | LDB | 63.8
84 | 83 | 1400 | 70 | LWB | 60.6
84 | 83 | 1400 | 70 | kW | 3.79
86 | 83 | 1400 | 72 | MBh | 45.8
86 | 83 | 1400 | 72 | S/T | 0.677
86 | 83 | 1400 | 72 | ∆T | 20.5
86 | 83 | 1400 | 72 | LDB | 65.5
86 | 83 | 1400 | 72 | LWB | 62.8
86 | 83 | 1400 | 72 | kW | 3.88
90 | 83 | 1400 | 75 | MBh | 46.6
90 | 83 | 1400 | 75 | S/T | 0.631
90 | 83 | 1400 | 75 | ∆T | 19.4
90 | 83 | 1400 | 75 | LDB | 70.6
90 | 83 | 1400 | 75 | LWB | 66.3
90 | 83 | 1400 | 75 | kW | 3.91
68 | 87 | 1400 | 57 | MBh | 26.3
68 | 87 | 1400 | 57 | S/T | 0.844
68 | 87 | 1400 | 57 | ∆T | 14.7
68 | 87 | 1400 | 57 | LDB | 53.3
68 | 87 | 1400 | 57 | LWB | 49.9
68 | 87 | 1400 | 57 | kW | 1.91
72 | 87 | 1400 | 61 | MBh | 32
72 | 87 | 1400 | 61 | S/T | 0.806
72 | 87 | 1400 | 61 | ∆T | 17.1
72 | 87 | 1400 | 61 | LDB | 54.9
72 | 87 | 1400 | 61 | LWB | 53
72 | 87 | 1400 | 61 | kW | 2.49
77 | 87 | 1400 | 64 | MBh | 36.2
77 | 87 | 1400 | 64 | S/T | 0.779
77 | 87 | 1400 | 64 | ∆T | 18.7
77 | 87 | 1400 | 64 | LDB | 58.3
77 | 87 | 1400 | 64 | LWB | 55.4
77 | 87 | 1400 | 64 | kW | 2.98
80 | 87 | 1400 | 67 | MBh | 40.5
80 | 87 | 1400 | 67 | S/T | 0.728
80 | 87 | 1400 | 67 | ∆T | 19.5
80 | 87 | 1400 | 67 | LDB | 60.5
80 | 87 | 1400 | 67 | LWB | 57.9
80 | 87 | 1400 | 67 | kW | 3.51
84 | 87 | 1400 | 70 | MBh | 44.5
84 | 87 | 1400 | 70 | S/T | 0.683
84 | 87 | 1400 | 70 | ∆T | 20.1
84 | 87 | 1400 | 70 | LDB | 63.9
84 | 87 | 1400 | 70 | LWB | 60.6
84 | 87 | 1400 | 70 | kW | 4.04
86 | 87 | 1400 | 72 | MBh | 45
86 | 87 | 1400 | 72 | S/T | 0.678
86 | 87 | 1400 | 72 | ∆T | 20.2
86 | 87 | 1400 | 72 | LDB | 65.8
86 | 87 | 1400 | 72 | LWB | 63
86 | 87 | 1400 | 72 | kW | 4.06
90 | 87 | 1400 | 75 | MBh | 45.9
90 | 87 | 1400 | 75 | S/T | 0.632
90 | 87 | 1400 | 75 | ∆T | 19.2
90 | 87 | 1400 | 75 | LDB | 70.8
90 | 87 | 1400 | 75 | LWB | 66.4
90 | 87 | 1400 | 75 | kW | 4.08
68 | 91 | 1400 | 57 | MBh | 26.3
68 | 91 | 1400 | 57 | S/T | 0.844
68 | 91 | 1400 | 57 | ∆T | 14.7
68 | 91 | 1400 | 57 | LDB | 53.3
68 | 91 | 1400 | 57 | LWB | 49.9
68 | 91 | 1400 | 57 | kW | 2.05
72 | 91 | 1400 | 61 | MBh | 32
72 | 91 | 1400 | 61 | S/T | 0.806
72 | 91 | 1400 | 61 | ∆T | 17.1
72 | 91 | 1400 | 61 | LDB | 54.9
72 | 91 | 1400 | 61 | LWB | 53
72 | 91 | 1400 | 61 | kW | 2.67
77 | 91 | 1400 | 64 | MBh | 36.2
77 | 91 | 1400 | 64 | S/T | 0.779
77 | 91 | 1400 | 64 | ∆T | 18.7
77 | 91 | 1400 | 64 | LDB | 58.3
77 | 91 | 1400 | 64 | LWB | 55.4
77 | 91 | 1400 | 64 | kW | 3.2
80 | 91 | 1400 | 67 | MBh | 40.5
80 | 91 | 1400 | 67 | S/T | 0.728
80 | 91 | 1400 | 67 | ∆T | 19.5
80 | 91 | 1400 | 67 | LDB | 60.5
80 | 91 | 1400 | 67 | LWB | 57.9
80 | 91 | 1400 | 67 | kW | 3.77
84 | 91 | 1400 | 70 | MBh | 43.7
84 | 91 | 1400 | 70 | S/T | 0.684
84 | 91 | 1400 | 70 | ∆T | 19.8
84 | 91 | 1400 | 70 | LDB | 64.2
84 | 91 | 1400 | 70 | LWB | 60.8
84 | 91 | 1400 | 70 | kW | 4.21
86 | 91 | 1400 | 72 | MBh | 44.3
86 | 91 | 1400 | 72 | S/T | 0.675
86 | 91 | 1400 | 72 | ∆T | 19.8
86 | 91 | 1400 | 72 | LDB | 66.2
86 | 91 | 1400 | 72 | LWB | 63.1
86 | 91 | 1400 | 72 | kW | 4.23
90 | 91 | 1400 | 75 | MBh | 45.1
90 | 91 | 1400 | 75 | S/T | 0.632
90 | 91 | 1400 | 75 | ∆T | 18.8
90 | 91 | 1400 | 75 | LDB | 71.2
90 | 91 | 1400 | 75 | LWB | 66.6
90 | 91 | 1400 | 75 | kW | 4.26
68 | 93 | 1400 | 57 | MBh | 26.3
68 | 93 | 1400 | 57 | S/T | 0.84
68 | 93 | 1400 | 57 | ∆T | 14.6
68 | 93 | 1400 | 57 | LDB | 53.4
68 | 93 | 1400 | 57 | LWB | 49.9
68 | 93 | 1400 | 57 | kW | 2.12
72 | 93 | 1400 | 61 | MBh | 32
72 | 93 | 1400 | 61 | S/T | 0.806
72 | 93 | 1400 | 61 | ∆T | 17.1
72 | 93 | 1400 | 61 | LDB | 54.9
72 | 93 | 1400 | 61 | LWB | 53
72 | 93 | 1400 | 61 | kW | 2.77
77 | 93 | 1400 | 64 | MBh | 36.2
77 | 93 | 1400 | 64 | S/T | 0.779
77 | 93 | 1400 | 64 | ∆T | 18.7
77 | 93 | 1400 | 64 | LDB | 58.3
77 | 93 | 1400 | 64 | LWB | 55.4
77 | 93 | 1400 | 64 | kW | 3.31
80 | 93 | 1400 | 67 | MBh | 40.5
80 | 93 | 1400 | 67 | S/T | 0.728
80 | 93 | 1400 | 67 | ∆T | 19.5
80 | 93 | 1400 | 67 | LDB | 60.5
80 | 93 | 1400 | 67 | LWB | 57.9
80 | 93 | 1400 | 67 | kW | 3.91
84 | 93 | 1400 | 70 | MBh | 43.3
84 | 93 | 1400 | 70 | S/T | 0.684
84 | 93 | 1400 | 70 | ∆T | 19.6
84 | 93 | 1400 | 70 | LDB | 64.4
84 | 93 | 1400 | 70 | LWB | 60.9
84 | 93 | 1400 | 70 | kW | 4.29
86 | 93 | 1400 | 72 | MBh | 43.9
86 | 93 | 1400 | 72 | S/T | 0.677
86 | 93 | 1400 | 72 | ∆T | 19.6
86 | 93 | 1400 | 72 | LDB | 66.4
86 | 93 | 1400 | 72 | LWB | 63.2
86 | 93 | 1400 | 72 | kW | 4.31
90 | 93 | 1400 | 75 | MBh | 44.7
90 | 93 | 1400 | 75 | S/T | 0.631
90 | 93 | 1400 | 75 | ∆T | 18.7
90 | 93 | 1400 | 75 | LDB | 71.3
90 | 93 | 1400 | 75 | LWB | 66.7
90 | 93 | 1400 | 75 | kW | 4.34
68 | 95 | 1400 | 57 | MBh | 26.3
68 | 95 | 1400 | 57 | S/T | 0.84
68 | 95 | 1400 | 57 | ∆T | 14.6
68 | 95 | 1400 | 57 | LDB | 53.4
68 | 95 | 1400 | 57 | LWB | 49.9
68 | 95 | 1400 | 57 | kW | 2.19
72 | 95 | 1400 | 61 | MBh | 32
72 | 95 | 1400 | 61 | S/T | 0.806
72 | 95 | 1400 | 61 | ∆T | 17.1
72 | 95 | 1400 | 61 | LDB | 54.9
72 | 95 | 1400 | 61 | LWB | 53
72 | 95 | 1400 | 61 | kW | 2.86
77 | 95 | 1400 | 64 | MBh | 36.2
77 | 95 | 1400 | 64 | S/T | 0.779
77 | 95 | 1400 | 64 | ∆T | 18.7
77 | 95 | 1400 | 64 | LDB | 58.3
77 | 95 | 1400 | 64 | LWB | 55.4
77 | 95 | 1400 | 64 | kW | 3.43
80 | 95 | 1400 | 67 | MBh | 40.5
80 | 95 | 1400 | 67 | S/T | 0.728
80 | 95 | 1400 | 67 | ∆T | 19.5
80 | 95 | 1400 | 67 | LDB | 60.5
80 | 95 | 1400 | 67 | LWB | 57.9
80 | 95 | 1400 | 67 | kW | 4.05
84 | 95 | 1400 | 70 | MBh | 43
84 | 95 | 1400 | 70 | S/T | 0.684
84 | 95 | 1400 | 70 | ∆T | 19.4
84 | 95 | 1400 | 70 | LDB | 64.6
84 | 95 | 1400 | 70 | LWB | 61
84 | 95 | 1400 | 70 | kW | 4.38
86 | 95 | 1400 | 72 | MBh | 43.5
86 | 95 | 1400 | 72 | S/T | 0.676
86 | 95 | 1400 | 72 | ∆T | 19.4
86 | 95 | 1400 | 72 | LDB | 66.6
86 | 95 | 1400 | 72 | LWB | 63.3
86 | 95 | 1400 | 72 | kW | 4.4
90 | 95 | 1400 | 75 | MBh | 44.4
90 | 95 | 1400 | 75 | S/T | 0.631
90 | 95 | 1400 | 75 | ∆T | 18.5
90 | 95 | 1400 | 75 | LDB | 71.5
90 | 95 | 1400 | 75 | LWB | 66.8
90 | 95 | 1400 | 75 | kW | 4.43
68 | 99 | 1400 | 57 | MBh | 26.3
68 | 99 | 1400 | 57 | S/T | 0.84
68 | 99 | 1400 | 57 | ∆T | 14.6
68 | 99 | 1400 | 57 | LDB | 53.4
68 | 99 | 1400 | 57 | LWB | 49.9
68 | 99 | 1400 | 57 | kW | 2.34
72 | 99 | 1400 | 61 | MBh | 32
72 | 99 | 1400 | 61 | S/T | 0.806
72 | 99 | 1400 | 61 | ∆T | 17.1
72 | 99 | 1400 | 61 | LDB | 54.9
72 | 99 | 1400 | 61 | LWB | 53
72 | 99 | 1400 | 61 | kW | 3.07
77 | 99 | 1400 | 64 | MBh | 36.2
77 | 99 | 1400 | 64 | S/T | 0.779
77 | 99 | 1400 | 64 | ∆T | 18.7
77 | 99 | 1400 | 64 | LDB | 58.3
77 | 99 | 1400 | 64 | LWB | 55.4
77 | 99 | 1400 | 64 | kW | 3.68
80 | 99 | 1400 | 67 | MBh | 40.5
80 | 99 | 1400 | 67 | S/T | 0.728
80 | 99 | 1400 | 67 | ∆T | 19.5
80 | 99 | 1400 | 67 | LDB | 60.5
80 | 99 | 1400 | 67 | LWB | 57.9
80 | 99 | 1400 | 67 | kW | 4.35
84 | 99 | 1400 | 70 | MBh | 42.2
84 | 99 | 1400 | 70 | S/T | 0.687
84 | 99 | 1400 | 70 | ∆T | 19.2
84 | 99 | 1400 | 70 | LDB | 64.8
84 | 99 | 1400 | 70 | LWB | 61.2
84 | 99 | 1400 | 70 | kW | 4.55
86 | 99 | 1400 | 72 | MBh | 42.8
86 | 99 | 1400 | 72 | S/T | 0.678
86 | 99 | 1400 | 72 | ∆T | 19.2
86 | 99 | 1400 | 72 | LDB | 66.8
86 | 99 | 1400 | 72 | LWB | 63.5
86 | 99 | 1400 | 72 | kW | 4.57
90 | 99 | 1400 | 75 | MBh | 43.6
90 | 99 | 1400 | 75 | S/T | 0.633
90 | 99 | 1400 | 75 | ∆T | 18.3
90 | 99 | 1400 | 75 | LDB | 71.7
90 | 99 | 1400 | 75 | LWB | 66.9
90 | 99 | 1400 | 75 | kW | 4.6
68 | 103 | 1400 | 57 | MBh | 26.3
68 | 103 | 1400 | 57 | S/T | 0.84
68 | 103 | 1400 | 57 | ∆T | 14.6
68 | 103 | 1400 | 57 | LDB | 53.4
68 | 103 | 1400 | 57 | LWB | 49.9
68 | 103 | 1400 | 57 | kW | 2.5
72 | 103 | 1400 | 61 | MBh | 32
72 | 103 | 1400 | 61 | S/T | 0.806
72 | 103 | 1400 | 61 | ∆T | 17.1
72 | 103 | 1400 | 61 | LDB | 54.9
72 | 103 | 1400 | 61 | LWB | 53
72 | 103 | 1400 | 61 | kW | 3.28
77 | 103 | 1400 | 64 | MBh | 36.2
77 | 103 | 1400 | 64 | S/T | 0.779
77 | 103 | 1400 | 64 | ∆T | 18.7
77 | 103 | 1400 | 64 | LDB | 58.3
77 | 103 | 1400 | 64 | LWB | 55.4
77 | 103 | 1400 | 64 | kW | 3.94
80 | 103 | 1400 | 67 | MBh | 40.5
80 | 103 | 1400 | 67 | S/T | 0.728
80 | 103 | 1400 | 67 | ∆T | 19.5
80 | 103 | 1400 | 67 | LDB | 60.5
80 | 103 | 1400 | 67 | LWB | 57.9
80 | 103 | 1400 | 67 | kW | 4.67
84 | 103 | 1400 | 70 | MBh | 41.4
84 | 103 | 1400 | 70 | S/T | 0.688
84 | 103 | 1400 | 70 | ∆T | 18.8
84 | 103 | 1400 | 70 | LDB | 65.2
84 | 103 | 1400 | 70 | LWB | 61.4
84 | 103 | 1400 | 70 | kW | 4.72
86 | 103 | 1400 | 72 | MBh | 42
86 | 103 | 1400 | 72 | S/T | 0.679
86 | 103 | 1400 | 72 | ∆T | 18.8
86 | 103 | 1400 | 72 | LDB | 67.2
86 | 103 | 1400 | 72 | LWB | 63.6
86 | 103 | 1400 | 72 | kW | 4.75
90 | 103 | 1400 | 75 | MBh | 42
90 | 103 | 1400 | 75 | S/T | 0.633
90 | 103 | 1400 | 75 | ∆T | 17.6
90 | 103 | 1400 | 75 | LDB | 72.4
90 | 103 | 1400 | 75 | LWB | 67.2
90 | 103 | 1400 | 75 | kW | 4.75
68 | 106 | 1400 | 57 | MBh | 26.3
68 | 106 | 1400 | 57 | S/T | 0.84
68 | 106 | 1400 | 57 | ∆T | 14.6
68 | 106 | 1400 | 57 | LDB | 53.4
68 | 106 | 1400 | 57 | LWB | 49.9
68 | 106 | 1400 | 57 | kW | 2.63
72 | 106 | 1400 | 61 | MBh | 32
72 | 106 | 1400 | 61 | S/T | 0.806
72 | 106 | 1400 | 61 | ∆T | 17.1
72 | 106 | 1400 | 61 | LDB | 54.9
72 | 106 | 1400 | 61 | LWB | 53
72 | 106 | 1400 | 61 | kW | 3.46
77 | 106 | 1400 | 64 | MBh | 36.2
77 | 106 | 1400 | 64 | S/T | 0.779
77 | 106 | 1400 | 64 | ∆T | 18.7
77 | 106 | 1400 | 64 | LDB | 58.3
77 | 106 | 1400 | 64 | LWB | 55.4
77 | 106 | 1400 | 64 | kW | 4.16
80 | 106 | 1400 | 67 | MBh | 40
80 | 106 | 1400 | 67 | S/T | 0.733
80 | 106 | 1400 | 67 | ∆T | 19.4
80 | 106 | 1400 | 67 | LDB | 60.6
80 | 106 | 1400 | 67 | LWB | 58.1
80 | 106 | 1400 | 67 | kW | 4.82
84 | 106 | 1400 | 70 | MBh | 40.7
84 | 106 | 1400 | 70 | S/T | 0.686
84 | 106 | 1400 | 70 | ∆T | 18.5
84 | 106 | 1400 | 70 | LDB | 65.5
84 | 106 | 1400 | 70 | LWB | 61.5
84 | 106 | 1400 | 70 | kW | 4.84
86 | 106 | 1400 | 72 | MBh | 40.7
86 | 106 | 1400 | 72 | S/T | 0.678
86 | 106 | 1400 | 72 | ∆T | 18.3
86 | 106 | 1400 | 72 | LDB | 67.7
86 | 106 | 1400 | 72 | LWB | 63.9
86 | 106 | 1400 | 72 | kW | 4.84
90 | 106 | 1400 | 75 | MBh | 40.7
90 | 106 | 1400 | 75 | S/T | 0.634
90 | 106 | 1400 | 75 | ∆T | 17.1
90 | 106 | 1400 | 75 | LDB | 72.9
90 | 106 | 1400 | 75 | LWB | 67.5
90 | 106 | 1400 | 75 | kW | 4.84
68 | 110 | 1400 | 57 | MBh | 26.3
68 | 110 | 1400 | 57 | S/T | 0.84
68 | 110 | 1400 | 57 | ∆T | 14.6
68 | 110 | 1400 | 57 | LDB | 53.4
68 | 110 | 1400 | 57 | LWB | 49.9
68 | 110 | 1400 | 57 | kW | 2.81
72 | 110 | 1400 | 61 | MBh | 32
72 | 110 | 1400 | 61 | S/T | 0.806
72 | 110 | 1400 | 61 | ∆T | 17.1
72 | 110 | 1400 | 61 | LDB | 54.9
72 | 110 | 1400 | 61 | LWB | 53
72 | 110 | 1400 | 61 | kW | 3.7
77 | 110 | 1400 | 64 | MBh | 36.2
77 | 110 | 1400 | 64 | S/T | 0.779
77 | 110 | 1400 | 64 | ∆T | 18.7
77 | 110 | 1400 | 64 | LDB | 58.3
77 | 110 | 1400 | 64 | LWB | 55.4
77 | 110 | 1400 | 64 | kW | 4.45
80 | 110 | 1400 | 67 | MBh | 38
80 | 110 | 1400 | 67 | S/T | 0.732
80 | 110 | 1400 | 67 | ∆T | 18.4
80 | 110 | 1400 | 67 | LDB | 61.6
80 | 110 | 1400 | 67 | LWB | 58.5
80 | 110 | 1400 | 67 | kW | 4.79
84 | 110 | 1400 | 70 | MBh | 38
84 | 110 | 1400 | 70 | S/T | 0.687
84 | 110 | 1400 | 70 | ∆T | 17.3
84 | 110 | 1400 | 70 | LDB | 66.7
84 | 110 | 1400 | 70 | LWB | 62.1
84 | 110 | 1400 | 70 | kW | 4.79
86 | 110 | 1400 | 72 | MBh | 38
86 | 110 | 1400 | 72 | S/T | 0.679
86 | 110 | 1400 | 72 | ∆T | 17.1
86 | 110 | 1400 | 72 | LDB | 68.9
86 | 110 | 1400 | 72 | LWB | 64.5
86 | 110 | 1400 | 72 | kW | 4.79
90 | 110 | 1400 | 75 | MBh | 38
90 | 110 | 1400 | 75 | S/T | 0.634
90 | 110 | 1400 | 75 | ∆T | 15.9
90 | 110 | 1400 | 75 | LDB | 74.1
90 | 110 | 1400 | 75 | LWB | 68
90 | 110 | 1400 | 75 | kW | 4.79
68 | 115 | 1400 | 57 | MBh | 26.3
68 | 115 | 1400 | 57 | S/T | 0.84
68 | 115 | 1400 | 57 | ∆T | 14.6
68 | 115 | 1400 | 57 | LDB | 53.4
68 | 115 | 1400 | 57 | LWB | 49.9
68 | 115 | 1400 | 57 | kW | 3.11
72 | 115 | 1400 | 61 | MBh | 31
72 | 115 | 1400 | 61 | S/T | 0.81
72 | 115 | 1400 | 61 | ∆T | 16.6
72 | 115 | 1400 | 61 | LDB | 55.4
72 | 115 | 1400 | 61 | LWB | 53.2
72 | 115 | 1400 | 61 | kW | 3.93
77 | 115 | 1400 | 64 | MBh | 31
77 | 115 | 1400 | 64 | S/T | 0.784
77 | 115 | 1400 | 64 | ∆T | 16.1
77 | 115 | 1400 | 64 | LDB | 60.9
77 | 115 | 1400 | 64 | LWB | 56.7
77 | 115 | 1400 | 64 | kW | 3.93
80 | 115 | 1400 | 67 | MBh | 31
80 | 115 | 1400 | 67 | S/T | 0.732
80 | 115 | 1400 | 67 | ∆T | 15
80 | 115 | 1400 | 67 | LDB | 65
80 | 115 | 1400 | 67 | LWB | 60.2
80 | 115 | 1400 | 67 | kW | 3.93
84 | 115 | 1400 | 70 | MBh | 31
84 | 115 | 1400 | 70 | S/T | 0.687
84 | 115 | 1400 | 70 | ∆T | 14.1
84 | 115 | 1400 | 70 | LDB | 69.9
84 | 115 | 1400 | 70 | LWB | 63.7
84 | 115 | 1400 | 70 | kW | 3.93
86 | 115 | 1400 | 72 | MBh | 31
86 | 115 | 1400 | 72 | S/T | 0.681
86 | 115 | 1400 | 72 | ∆T | 14
86 | 115 | 1400 | 72 | LDB | 72
86 | 115 | 1400 | 72 | LWB | 66
86 | 115 | 1400 | 72 | kW | 3.93
90 | 115 | 1400 | 75 | MBh | 31
90 | 115 | 1400 | 75 | S/T | 0.635
90 | 115 | 1400 | 75 | ∆T | 13
90 | 115 | 1400 | 75 | LDB | 77
90 | 115 | 1400 | 75 | LWB | 69.4
90 | 115 | 1400 | 75 | kW | 3.93
68 | 118 | 1400 | 57 | MBh | 26.3
68 | 118 | 1400 | 57 | S/T | 0.84
68 | 118 | 1400 | 57 | ∆T | 14.6
68 | 118 | 1400 | 57 | LDB | 53.4
68 | 118 | 1400 | 57 | LWB | 49.9
68 | 118 | 1400 | 57 | kW | 3.34
72 | 118 | 1400 | 61 | MBh | 26.8
72 | 118 | 1400 | 61 | S/T | 0.81
72 | 118 | 1400 | 61 | ∆T | 14.4
72 | 118 | 1400 | 61 | LDB | 57.6
72 | 118 | 1400 | 61 | LWB | 54.4
72 | 118 | 1400 | 61 | kW | 3.44
77 | 118 | 1400 | 64 | MBh | 26.8
77 | 118 | 1400 | 64 | S/T | 0.784
77 | 118 | 1400 | 64 | ∆T | 13.9
77 | 118 | 1400 | 64 | LDB | 63.1
77 | 118 | 1400 | 64 | LWB | 57.8
77 | 118 | 1400 | 64 | kW | 3.44
80 | 118 | 1400 | 67 | MBh | 26.8
80 | 118 | 1400 | 67 | S/T | 0.735
80 | 118 | 1400 | 67 | ∆T | 13
80 | 118 | 1400 | 67 | LDB | 67
80 | 118 | 1400 | 67 | LWB | 61.2
80 | 118 | 1400 | 67 | kW | 3.44
84 | 118 | 1400 | 70 | MBh | 26.8
84 | 118 | 1400 | 70 | S/T | 0.69
84 | 118 | 1400 | 70 | ∆T | 12.2
84 | 118 | 1400 | 70 | LDB | 71.8
84 | 118 | 1400 | 70 | LWB | 64.6
84 | 118 | 1400 | 70 | kW | 3.44
86 | 118 | 1400 | 72 | MBh | 26.8
86 | 118 | 1400 | 72 | S/T | 0.683
86 | 118 | 1400 | 72 | ∆T | 12.1
86 | 118 | 1400 | 72 | LDB | 73.9
86 | 118 | 1400 | 72 | LWB | 66.8
86 | 118 | 1400 | 72 | kW | 3.44
90 | 118 | 1400 | 75 | MBh | 26.8
90 | 118 | 1400 | 75 | S/T | 0.634
90 | 118 | 1400 | 75 | ∆T | 11.2
90 | 118 | 1400 | 75 | LDB | 78.8
90 | 118 | 1400 | 75 | LWB | 70.2
90 | 118 | 1400 | 75 | kW | 3.44
68 | 122 | 1400 | 57 | MBh | 21.2
68 | 122 | 1400 | 57 | S/T | 0.849
68 | 122 | 1400 | 57 | ∆T | 11.9
68 | 122 | 1400 | 57 | LDB | 56.1
68 | 122 | 1400 | 57 | LWB | 51.4
68 | 122 | 1400 | 57 | kW | 2.76
72 | 122 | 1400 | 61 | MBh | 21.2
72 | 122 | 1400 | 61 | S/T | 0.811
72 | 122 | 1400 | 61 | ∆T | 11.4
72 | 122 | 1400 | 61 | LDB | 60.6
72 | 122 | 1400 | 61 | LWB | 55.8
72 | 122 | 1400 | 61 | kW | 2.76
77 | 122 | 1400 | 64 | MBh | 21.2
77 | 122 | 1400 | 64 | S/T | 0.783
77 | 122 | 1400 | 64 | ∆T | 11
77 | 122 | 1400 | 64 | LDB | 66
77 | 122 | 1400 | 64 | LWB | 59.1
77 | 122 | 1400 | 64 | kW | 2.76
80 | 122 | 1400 | 67 | MBh | 21.2
80 | 122 | 1400 | 67 | S/T | 0.736
80 | 122 | 1400 | 67 | ∆T | 10.3
80 | 122 | 1400 | 67 | LDB | 69.7
80 | 122 | 1400 | 67 | LWB | 62.5
80 | 122 | 1400 | 67 | kW | 2.76
84 | 122 | 1400 | 70 | MBh | 21.2
84 | 122 | 1400 | 70 | S/T | 0.689
84 | 122 | 1400 | 70 | ∆T | 9.7
84 | 122 | 1400 | 70 | LDB | 74.3
84 | 122 | 1400 | 70 | LWB | 65.8
84 | 122 | 1400 | 70 | kW | 2.76
86 | 122 | 1400 | 72 | MBh | 21.2
86 | 122 | 1400 | 72 | S/T | 0.684
86 | 122 | 1400 | 72 | ∆T | 9.6
86 | 122 | 1400 | 72 | LDB | 76.4
86 | 122 | 1400 | 72 | LWB | 68
86 | 122 | 1400 | 72 | kW | 2.76
90 | 122 | 1400 | 75 | MBh | 21.2
90 | 122 | 1400 | 75 | S/T | 0.637
90 | 122 | 1400 | 75 | ∆T | 8.9
90 | 122 | 1400 | 75 | LDB | 81.1
90 | 122 | 1400 | 75 | LWB | 71.2
90 | 122 | 1400 | 75 | kW | 2.76

## RZA42AAVJU - FTA42AAVJUA
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1400 | 57 | MBh | 26.3 | 64 | 60 | 61 | 57.6 | 4.89
68 | 23 | 1400 | 57 | S/T | 0.84 | 64 | 60 | 65 | 53.4 | 4.16
68 | 23 | 1400 | 57 | ∆T | 14.6 | 64 | 60 | 68 | 50.1 | 3.62
68 | 23 | 1400 | 57 | LDB | 53.4 | 64 | 60 | 70 | 48 | 3.27
68 | 23 | 1400 | 57 | LWB | 49.9 | 64 | 60 | 72 | 45.9 | 2.92
68 | 23 | 1400 | 57 | kW | 1.19 | 64 | 60 | 75 | 42.6 | 2.41
72 | 23 | 1400 | 61 | MBh | 32 | 60 | 56 | 61 | 57.6 | 5.23
72 | 23 | 1400 | 61 | S/T | 0.806 | 60 | 56 | 65 | 53.4 | 4.47
72 | 23 | 1400 | 61 | ∆T | 17.1 | 60 | 56 | 68 | 50.1 | 3.9
72 | 23 | 1400 | 61 | LDB | 54.9 | 60 | 56 | 70 | 48 | 3.54
72 | 23 | 1400 | 61 | LWB | 53 | 60 | 56 | 72 | 45.9 | 3.17
72 | 23 | 1400 | 61 | kW | 1.46 | 60 | 56 | 75 | 42.6 | 2.64
77 | 23 | 1400 | 64 | MBh | 36.2 | 57 | 53 | 61 | 57.6 | 5.5
77 | 23 | 1400 | 64 | S/T | 0.779 | 57 | 53 | 65 | 53.4 | 4.71
77 | 23 | 1400 | 64 | ∆T | 18.7 | 57 | 53 | 68 | 50.1 | 4.13
77 | 23 | 1400 | 64 | LDB | 58.3 | 57 | 53 | 70 | 48 | 3.75
77 | 23 | 1400 | 64 | LWB | 55.4 | 57 | 53 | 72 | 45.9 | 3.38
77 | 23 | 1400 | 64 | kW | 1.68 | 57 | 53 | 75 | 42.6 | 2.82
80 | 23 | 1400 | 67 | MBh | 40.5 | 54 | 50 | 61 | 57.6 | 5.79
80 | 23 | 1400 | 67 | S/T | 0.728 | 54 | 50 | 65 | 53.4 | 4.97
80 | 23 | 1400 | 67 | ∆T | 19.5 | 54 | 50 | 68 | 50.1 | 4.37
80 | 23 | 1400 | 67 | LDB | 60.5 | 54 | 50 | 70 | 48 | 3.98
80 | 23 | 1400 | 67 | LWB | 57.9 | 54 | 50 | 72 | 45.9 | 3.59
80 | 23 | 1400 | 67 | kW | 1.9 | 54 | 50 | 75 | 42.6 | 3.02
84 | 23 | 1400 | 70 | MBh | 44.8 | 51 | 47 | 61 | 57.6 | 6.1
84 | 23 | 1400 | 70 | S/T | 0.683 | 51 | 47 | 65 | 53.4 | 5.25
84 | 23 | 1400 | 70 | ∆T | 20.2 | 51 | 47 | 68 | 50.1 | 4.63
84 | 23 | 1400 | 70 | LDB | 63.8 | 51 | 47 | 70 | 48 | 4.22
84 | 23 | 1400 | 70 | LWB | 60.6 | 51 | 47 | 72 | 45.9 | 3.82
84 | 23 | 1400 | 70 | kW | 2.13 | 51 | 47 | 75 | 42.6 | 3.23
86 | 23 | 1400 | 72 | MBh | 47.6 | 47 | 43 | 61 | 57.6 | 6.54
86 | 23 | 1400 | 72 | S/T | 0.676 | 47 | 43 | 65 | 53.4 | 5.65
86 | 23 | 1400 | 72 | ∆T | 21.3 | 47 | 43 | 68 | 50.1 | 5
86 | 23 | 1400 | 72 | LDB | 64.7 | 47 | 43 | 70 | 48 | 4.57
86 | 23 | 1400 | 72 | LWB | 62.4 | 47 | 43 | 72 | 45.9 | 4.15
86 | 23 | 1400 | 72 | kW | 2.29 | 47 | 43 | 75 | 42.6 | 3.52
90 | 23 | 1400 | 75 | MBh | 51.9 | 44 | 40 | 61 | 57.6 | 6.9
90 | 23 | 1400 | 75 | S/T | 0.63 | 44 | 40 | 65 | 53.4 | 5.97
90 | 23 | 1400 | 75 | ∆T | 21.6 | 44 | 40 | 68 | 50.1 | 5.29
90 | 23 | 1400 | 75 | LDB | 68.4 | 44 | 40 | 70 | 48 | 4.85
90 | 23 | 1400 | 75 | LWB | 65.2 | 44 | 40 | 72 | 45.9 | 4.41
90 | 23 | 1400 | 75 | kW | 2.53 | 44 | 40 | 75 | 42.6 | 3.77
68 | 30 | 1400 | 57 | MBh | 26.3 | 39 | 36 | 61 | 57.6 | 7.42
68 | 30 | 1400 | 57 | S/T | 0.84 | 39 | 36 | 65 | 53.4 | 6.44
68 | 30 | 1400 | 57 | ∆T | 14.6 | 39 | 36 | 68 | 50.1 | 5.72
68 | 30 | 1400 | 57 | LDB | 53.4 | 39 | 36 | 70 | 48 | 5.25
68 | 30 | 1400 | 57 | LWB | 49.9 | 39 | 36 | 72 | 45.9 | 4.79
68 | 30 | 1400 | 57 | kW | 1.22 | 39 | 36 | 75 | 42.6 | 4.11
72 | 30 | 1400 | 61 | MBh | 32 | 35 | 32 | 61 | 56.8 | 7.99
72 | 30 | 1400 | 61 | S/T | 0.806 | 35 | 32 | 65 | 53.4 | 6.95
72 | 30 | 1400 | 61 | ∆T | 17.1 | 35 | 32 | 68 | 50.1 | 6.2
72 | 30 | 1400 | 61 | LDB | 54.9 | 35 | 32 | 70 | 48 | 5.7
72 | 30 | 1400 | 61 | LWB | 53 | 35 | 32 | 72 | 45.9 | 5.21
72 | 30 | 1400 | 61 | kW | 1.51 | 35 | 32 | 75 | 42.6 | 4.5
77 | 30 | 1400 | 64 | MBh | 36.2 | 30 | 28 | 61 | 54.3 | 8.33
77 | 30 | 1400 | 64 | S/T | 0.779 | 30 | 28 | 65 | 53.4 | 7.52
77 | 30 | 1400 | 64 | ∆T | 18.7 | 30 | 28 | 68 | 50.1 | 6.72
77 | 30 | 1400 | 64 | LDB | 58.3 | 30 | 28 | 70 | 48 | 6.2
77 | 30 | 1400 | 64 | LWB | 55.4 | 30 | 28 | 72 | 45.9 | 5.68
77 | 30 | 1400 | 64 | kW | 1.73 | 30 | 28 | 75 | 42.6 | 4.92
80 | 30 | 1400 | 67 | MBh | 40.5 | 26 | 24 | 61 | 51.8 | 7.98
80 | 30 | 1400 | 67 | S/T | 0.728 | 26 | 24 | 65 | 51.8 | 8.16
80 | 30 | 1400 | 67 | ∆T | 19.5 | 26 | 24 | 68 | 50.1 | 7.3
80 | 30 | 1400 | 67 | LDB | 60.5 | 26 | 24 | 70 | 48 | 6.74
80 | 30 | 1400 | 67 | LWB | 57.9 | 26 | 24 | 72 | 45.9 | 6.19
80 | 30 | 1400 | 67 | kW | 1.96 | 26 | 24 | 75 | 42.6 | 5.39
84 | 30 | 1400 | 70 | MBh | 44.8 | 22 | 20 | 61 | 49.3 | 7.61
84 | 30 | 1400 | 70 | S/T | 0.683 | 22 | 20 | 65 | 49.3 | 8.14
84 | 30 | 1400 | 70 | ∆T | 20.2 | 22 | 20 | 68 | 49.3 | 7.95
84 | 30 | 1400 | 70 | LDB | 63.8 | 22 | 20 | 70 | 48 | 7.36
84 | 30 | 1400 | 70 | LWB | 60.6 | 22 | 20 | 72 | 45.9 | 6.77
84 | 30 | 1400 | 70 | kW | 2.2 | 22 | 20 | 75 | 42.6 | 5.91
86 | 30 | 1400 | 72 | MBh | 47.6 | 19 | 18 | 61 | 48.1 | 7.41
86 | 30 | 1400 | 72 | S/T | 0.676 | 19 | 18 | 65 | 48.1 | 7.84
86 | 30 | 1400 | 72 | ∆T | 21.3 | 19 | 18 | 68 | 48.1 | 7.84
86 | 30 | 1400 | 72 | LDB | 64.7 | 19 | 18 | 70 | 48 | 7.69
86 | 30 | 1400 | 72 | LWB | 62.4 | 19 | 18 | 72 | 45.9 | 7.08
86 | 30 | 1400 | 72 | kW | 2.37 | 19 | 18 | 75 | 42.6 | 6.19
90 | 30 | 1400 | 75 | MBh | 51.9 | 17 | 16 | 61 | 46.5 | 7.14
90 | 30 | 1400 | 75 | S/T | 0.63 | 17 | 16 | 65 | 46.5 | 7.46
90 | 30 | 1400 | 75 | ∆T | 21.6 | 17 | 16 | 68 | 46.5 | 7.46
90 | 30 | 1400 | 75 | LDB | 68.4 | 17 | 16 | 70 | 46.5 | 7.46
90 | 30 | 1400 | 75 | LWB | 65.2 | 17 | 16 | 72 | 45.9 | 7.46
90 | 30 | 1400 | 75 | kW | 2.61 | 17 | 16 | 75 | 42.6 | 6.58
68 | 40 | 1400 | 57 | MBh | 26.3 | 15 | 14 | 61 | 45.6 | 6.97
68 | 40 | 1400 | 57 | S/T | 0.84 | 15 | 14 | 65 | 45.6 | 7.23
68 | 40 | 1400 | 57 | ∆T | 14.6 | 15 | 14 | 68 | 45.6 | 7.23
68 | 40 | 1400 | 57 | LDB | 53.4 | 15 | 14 | 70 | 45.6 | 7.23
68 | 40 | 1400 | 57 | LWB | 49.9 | 15 | 14 | 72 | 45.6 | 7.23
68 | 40 | 1400 | 57 | kW | 1.28 | 15 | 14 | 75 | 42.6 | 6.82
72 | 40 | 1400 | 61 | MBh | 32 | 13 | 12 | 61 | 44.4 | 6.74
72 | 40 | 1400 | 61 | S/T | 0.806 | 13 | 12 | 65 | 44.4 | 6.93
72 | 40 | 1400 | 61 | ∆T | 17.1 | 13 | 12 | 68 | 44.4 | 6.93
72 | 40 | 1400 | 61 | LDB | 54.9 | 13 | 12 | 70 | 44.4 | 6.93
72 | 40 | 1400 | 61 | LWB | 53 | 13 | 12 | 72 | 44.4 | 6.93
72 | 40 | 1400 | 61 | kW | 1.58 | 13 | 12 | 75 | 42.6 | 6.93
77 | 40 | 1400 | 64 | MBh | 36.2 | 10 | 9 | 61 | 42.2 | 6.3
77 | 40 | 1400 | 64 | S/T | 0.779 | 10 | 9 | 65 | 42.2 | 6.39
77 | 40 | 1400 | 64 | ∆T | 18.7 | 10 | 9 | 68 | 42.2 | 6.39
77 | 40 | 1400 | 64 | LDB | 58.3 | 10 | 9 | 70 | 42.2 | 6.39
77 | 40 | 1400 | 64 | LWB | 55.4 | 10 | 9 | 72 | 42.2 | 6.39
77 | 40 | 1400 | 64 | kW | 1.81 | 10 | 9 | 75 | 42.2 | 6.39
80 | 40 | 1400 | 67 | MBh | 40.5 | 6 | 5 | 61 | 40 | 5.81
80 | 40 | 1400 | 67 | S/T | 0.728 | 6 | 5 | 65 | 40 | 5.86
80 | 40 | 1400 | 67 | ∆T | 19.5 | 6 | 5 | 68 | 40 | 5.86
80 | 40 | 1400 | 67 | LDB | 60.5 | 6 | 5 | 70 | 40 | 5.86
80 | 40 | 1400 | 67 | LWB | 57.9 | 6 | 5 | 72 | 40 | 5.86
80 | 40 | 1400 | 67 | kW | 2.06 | 6 | 5 | 75 | 40 | 5.86
84 | 40 | 1400 | 70 | MBh | 44.8 | -2 | -2 | 61 | 33.1 | 4.63
84 | 40 | 1400 | 70 | S/T | 0.683 | -2 | -2 | 65 | 33.1 | 4.76
84 | 40 | 1400 | 70 | ∆T | 20.2 | -2 | -2 | 68 | 33.1 | 4.76
84 | 40 | 1400 | 70 | LDB | 63.8 | -2 | -2 | 70 | 33.1 | 4.76
84 | 40 | 1400 | 70 | LWB | 60.6 | -2 | -2 | 72 | 33.1 | 4.76
84 | 40 | 1400 | 70 | kW | 2.31 | -2 | -2 | 75 | 33.1 | 4.76
86 | 40 | 1400 | 72 | MBh | 47.6 | -4 | -4 | 61 | 31.4 | 4.29
86 | 40 | 1400 | 72 | S/T | 0.676 | -4 | -4 | 65 | 31.4 | 4.49
86 | 40 | 1400 | 72 | ∆T | 21.3 | -4 | -4 | 68 | 31.4 | 4.49
86 | 40 | 1400 | 72 | LDB | 64.7 | -4 | -4 | 70 | 31.4 | 4.49
86 | 40 | 1400 | 72 | LWB | 62.4 | -4 | -4 | 72 | 31.4 | 4.49
86 | 40 | 1400 | 72 | kW | 2.48 | -4 | -4 | 75 | 31.4 | 4.49
90 | 40 | 1400 | 75 | MBh | 51.9
90 | 40 | 1400 | 75 | S/T | 0.63
90 | 40 | 1400 | 75 | ∆T | 21.6
90 | 40 | 1400 | 75 | LDB | 68.4
90 | 40 | 1400 | 75 | LWB | 65.2
90 | 40 | 1400 | 75 | kW | 2.74
68 | 50 | 1400 | 57 | MBh | 26.3
68 | 50 | 1400 | 57 | S/T | 0.84
68 | 50 | 1400 | 57 | ∆T | 14.6
68 | 50 | 1400 | 57 | LDB | 53.4
68 | 50 | 1400 | 57 | LWB | 49.9
68 | 50 | 1400 | 57 | kW | 1.34
72 | 50 | 1400 | 61 | MBh | 32
72 | 50 | 1400 | 61 | S/T | 0.806
72 | 50 | 1400 | 61 | ∆T | 17.1
72 | 50 | 1400 | 61 | LDB | 54.9
72 | 50 | 1400 | 61 | LWB | 53
72 | 50 | 1400 | 61 | kW | 1.66
77 | 50 | 1400 | 64 | MBh | 36.2
77 | 50 | 1400 | 64 | S/T | 0.779
77 | 50 | 1400 | 64 | ∆T | 18.7
77 | 50 | 1400 | 64 | LDB | 58.3
77 | 50 | 1400 | 64 | LWB | 55.4
77 | 50 | 1400 | 64 | kW | 1.91
80 | 50 | 1400 | 67 | MBh | 40.5
80 | 50 | 1400 | 67 | S/T | 0.728
80 | 50 | 1400 | 67 | ∆T | 19.5
80 | 50 | 1400 | 67 | LDB | 60.5
80 | 50 | 1400 | 67 | LWB | 57.9
80 | 50 | 1400 | 67 | kW | 2.17
84 | 50 | 1400 | 70 | MBh | 44.8
84 | 50 | 1400 | 70 | S/T | 0.683
84 | 50 | 1400 | 70 | ∆T | 20.2
84 | 50 | 1400 | 70 | LDB | 63.8
84 | 50 | 1400 | 70 | LWB | 60.6
84 | 50 | 1400 | 70 | kW | 2.43
86 | 50 | 1400 | 72 | MBh | 47.6
86 | 50 | 1400 | 72 | S/T | 0.676
86 | 50 | 1400 | 72 | ∆T | 21.3
86 | 50 | 1400 | 72 | LDB | 64.7
86 | 50 | 1400 | 72 | LWB | 62.4
86 | 50 | 1400 | 72 | kW | 2.61
90 | 50 | 1400 | 75 | MBh | 51.9
90 | 50 | 1400 | 75 | S/T | 0.63
90 | 50 | 1400 | 75 | ∆T | 21.6
90 | 50 | 1400 | 75 | LDB | 68.4
90 | 50 | 1400 | 75 | LWB | 65.2
90 | 50 | 1400 | 75 | kW | 2.88
68 | 54 | 1400 | 57 | MBh | 26.3
68 | 54 | 1400 | 57 | S/T | 0.84
68 | 54 | 1400 | 57 | ∆T | 14.6
68 | 54 | 1400 | 57 | LDB | 53.4
68 | 54 | 1400 | 57 | LWB | 49.9
68 | 54 | 1400 | 57 | kW | 1.36
72 | 54 | 1400 | 61 | MBh | 32
72 | 54 | 1400 | 61 | S/T | 0.806
72 | 54 | 1400 | 61 | ∆T | 17.1
72 | 54 | 1400 | 61 | LDB | 54.9
72 | 54 | 1400 | 61 | LWB | 53
72 | 54 | 1400 | 61 | kW | 1.69
77 | 54 | 1400 | 64 | MBh | 36.2
77 | 54 | 1400 | 64 | S/T | 0.779
77 | 54 | 1400 | 64 | ∆T | 18.7
77 | 54 | 1400 | 64 | LDB | 58.3
77 | 54 | 1400 | 64 | LWB | 55.4
77 | 54 | 1400 | 64 | kW | 1.95
80 | 54 | 1400 | 67 | MBh | 40.5
80 | 54 | 1400 | 67 | S/T | 0.728
80 | 54 | 1400 | 67 | ∆T | 19.5
80 | 54 | 1400 | 67 | LDB | 60.5
80 | 54 | 1400 | 67 | LWB | 57.9
80 | 54 | 1400 | 67 | kW | 2.21
84 | 54 | 1400 | 70 | MBh | 44.8
84 | 54 | 1400 | 70 | S/T | 0.683
84 | 54 | 1400 | 70 | ∆T | 20.2
84 | 54 | 1400 | 70 | LDB | 63.8
84 | 54 | 1400 | 70 | LWB | 60.6
84 | 54 | 1400 | 70 | kW | 2.48
86 | 54 | 1400 | 72 | MBh | 47.6
86 | 54 | 1400 | 72 | S/T | 0.676
86 | 54 | 1400 | 72 | ∆T | 21.3
86 | 54 | 1400 | 72 | LDB | 64.7
86 | 54 | 1400 | 72 | LWB | 62.4
86 | 54 | 1400 | 72 | kW | 2.67
90 | 54 | 1400 | 75 | MBh | 51.9
90 | 54 | 1400 | 75 | S/T | 0.63
90 | 54 | 1400 | 75 | ∆T | 21.6
90 | 54 | 1400 | 75 | LDB | 68.4
90 | 54 | 1400 | 75 | LWB | 65.2
90 | 54 | 1400 | 75 | kW | 2.94
68 | 58 | 1400 | 57 | MBh | 26.3
68 | 58 | 1400 | 57 | S/T | 0.84
68 | 58 | 1400 | 57 | ∆T | 14.6
68 | 58 | 1400 | 57 | LDB | 53.4
68 | 58 | 1400 | 57 | LWB | 49.9
68 | 58 | 1400 | 57 | kW | 1.39
72 | 58 | 1400 | 61 | MBh | 32
72 | 58 | 1400 | 61 | S/T | 0.806
72 | 58 | 1400 | 61 | ∆T | 17.1
72 | 58 | 1400 | 61 | LDB | 54.9
72 | 58 | 1400 | 61 | LWB | 53
72 | 58 | 1400 | 61 | kW | 1.72
77 | 58 | 1400 | 64 | MBh | 36.2
77 | 58 | 1400 | 64 | S/T | 0.779
77 | 58 | 1400 | 64 | ∆T | 18.7
77 | 58 | 1400 | 64 | LDB | 58.3
77 | 58 | 1400 | 64 | LWB | 55.4
77 | 58 | 1400 | 64 | kW | 1.99
80 | 58 | 1400 | 67 | MBh | 40.5
80 | 58 | 1400 | 67 | S/T | 0.728
80 | 58 | 1400 | 67 | ∆T | 19.5
80 | 58 | 1400 | 67 | LDB | 60.5
80 | 58 | 1400 | 67 | LWB | 57.9
80 | 58 | 1400 | 67 | kW | 2.26
84 | 58 | 1400 | 70 | MBh | 44.8
84 | 58 | 1400 | 70 | S/T | 0.683
84 | 58 | 1400 | 70 | ∆T | 20.2
84 | 58 | 1400 | 70 | LDB | 63.8
84 | 58 | 1400 | 70 | LWB | 60.6
84 | 58 | 1400 | 70 | kW | 2.54
86 | 58 | 1400 | 72 | MBh | 47.6
86 | 58 | 1400 | 72 | S/T | 0.676
86 | 58 | 1400 | 72 | ∆T | 21.3
86 | 58 | 1400 | 72 | LDB | 64.7
86 | 58 | 1400 | 72 | LWB | 62.4
86 | 58 | 1400 | 72 | kW | 2.72
90 | 58 | 1400 | 75 | MBh | 51.4
90 | 58 | 1400 | 75 | S/T | 0.63
90 | 58 | 1400 | 75 | ∆T | 21.4
90 | 58 | 1400 | 75 | LDB | 68.6
90 | 58 | 1400 | 75 | LWB | 65.3
90 | 58 | 1400 | 75 | kW | 2.96
68 | 62 | 1400 | 57 | MBh | 26.3
68 | 62 | 1400 | 57 | S/T | 0.84
68 | 62 | 1400 | 57 | ∆T | 14.6
68 | 62 | 1400 | 57 | LDB | 53.4
68 | 62 | 1400 | 57 | LWB | 49.9
68 | 62 | 1400 | 57 | kW | 1.42
72 | 62 | 1400 | 61 | MBh | 32
72 | 62 | 1400 | 61 | S/T | 0.806
72 | 62 | 1400 | 61 | ∆T | 17.1
72 | 62 | 1400 | 61 | LDB | 54.9
72 | 62 | 1400 | 61 | LWB | 53
72 | 62 | 1400 | 61 | kW | 1.76
77 | 62 | 1400 | 64 | MBh | 36.2
77 | 62 | 1400 | 64 | S/T | 0.779
77 | 62 | 1400 | 64 | ∆T | 18.7
77 | 62 | 1400 | 64 | LDB | 58.3
77 | 62 | 1400 | 64 | LWB | 55.4
77 | 62 | 1400 | 64 | kW | 2.03
80 | 62 | 1400 | 67 | MBh | 40.5
80 | 62 | 1400 | 67 | S/T | 0.728
80 | 62 | 1400 | 67 | ∆T | 19.5
80 | 62 | 1400 | 67 | LDB | 60.5
80 | 62 | 1400 | 67 | LWB | 57.9
80 | 62 | 1400 | 67 | kW | 2.31
84 | 62 | 1400 | 70 | MBh | 44.8
84 | 62 | 1400 | 70 | S/T | 0.683
84 | 62 | 1400 | 70 | ∆T | 20.2
84 | 62 | 1400 | 70 | LDB | 63.8
84 | 62 | 1400 | 70 | LWB | 60.6
84 | 62 | 1400 | 70 | kW | 2.59
86 | 62 | 1400 | 72 | MBh | 47.6
86 | 62 | 1400 | 72 | S/T | 0.676
86 | 62 | 1400 | 72 | ∆T | 21.3
86 | 62 | 1400 | 72 | LDB | 64.7
86 | 62 | 1400 | 72 | LWB | 62.4
86 | 62 | 1400 | 72 | kW | 2.78
90 | 62 | 1400 | 75 | MBh | 50.6
90 | 62 | 1400 | 75 | S/T | 0.63
90 | 62 | 1400 | 75 | ∆T | 21.1
90 | 62 | 1400 | 75 | LDB | 68.9
90 | 62 | 1400 | 75 | LWB | 65.5
90 | 62 | 1400 | 75 | kW | 3.02
68 | 66 | 1400 | 57 | MBh | 26.3
68 | 66 | 1400 | 57 | S/T | 0.84
68 | 66 | 1400 | 57 | ∆T | 14.6
68 | 66 | 1400 | 57 | LDB | 53.4
68 | 66 | 1400 | 57 | LWB | 49.9
68 | 66 | 1400 | 57 | kW | 1.45
72 | 66 | 1400 | 61 | MBh | 32
72 | 66 | 1400 | 61 | S/T | 0.806
72 | 66 | 1400 | 61 | ∆T | 17.1
72 | 66 | 1400 | 61 | LDB | 54.9
72 | 66 | 1400 | 61 | LWB | 53
72 | 66 | 1400 | 61 | kW | 1.8
77 | 66 | 1400 | 64 | MBh | 36.2
77 | 66 | 1400 | 64 | S/T | 0.779
77 | 66 | 1400 | 64 | ∆T | 18.7
77 | 66 | 1400 | 64 | LDB | 58.3
77 | 66 | 1400 | 64 | LWB | 55.4
77 | 66 | 1400 | 64 | kW | 2.07
80 | 66 | 1400 | 67 | MBh | 40.5
80 | 66 | 1400 | 67 | S/T | 0.728
80 | 66 | 1400 | 67 | ∆T | 19.5
80 | 66 | 1400 | 67 | LDB | 60.5
80 | 66 | 1400 | 67 | LWB | 57.9
80 | 66 | 1400 | 67 | kW | 2.36
84 | 66 | 1400 | 70 | MBh | 44.8
84 | 66 | 1400 | 70 | S/T | 0.683
84 | 66 | 1400 | 70 | ∆T | 20.2
84 | 66 | 1400 | 70 | LDB | 63.8
84 | 66 | 1400 | 70 | LWB | 60.6
84 | 66 | 1400 | 70 | kW | 2.74
86 | 66 | 1400 | 72 | MBh | 47.6
86 | 66 | 1400 | 72 | S/T | 0.676
86 | 66 | 1400 | 72 | ∆T | 21.3
86 | 66 | 1400 | 72 | LDB | 64.7
86 | 66 | 1400 | 72 | LWB | 62.4
86 | 66 | 1400 | 72 | kW | 3
90 | 66 | 1400 | 75 | MBh | 49.9
90 | 66 | 1400 | 75 | S/T | 0.631
90 | 66 | 1400 | 75 | ∆T | 20.8
90 | 66 | 1400 | 75 | LDB | 69.2
90 | 66 | 1400 | 75 | LWB | 65.6
90 | 66 | 1400 | 75 | kW | 3.19
68 | 70 | 1400 | 57 | MBh | 26.3
68 | 70 | 1400 | 57 | S/T | 0.844
68 | 70 | 1400 | 57 | ∆T | 14.7
68 | 70 | 1400 | 57 | LDB | 53.3
68 | 70 | 1400 | 57 | LWB | 49.9
68 | 70 | 1400 | 57 | kW | 1.48
72 | 70 | 1400 | 61 | MBh | 32
72 | 70 | 1400 | 61 | S/T | 0.806
72 | 70 | 1400 | 61 | ∆T | 17.1
72 | 70 | 1400 | 61 | LDB | 54.9
72 | 70 | 1400 | 61 | LWB | 53
72 | 70 | 1400 | 61 | kW | 1.84
77 | 70 | 1400 | 64 | MBh | 36.2
77 | 70 | 1400 | 64 | S/T | 0.779
77 | 70 | 1400 | 64 | ∆T | 18.7
77 | 70 | 1400 | 64 | LDB | 58.3
77 | 70 | 1400 | 64 | LWB | 55.4
77 | 70 | 1400 | 64 | kW | 2.18
80 | 70 | 1400 | 67 | MBh | 40.5
80 | 70 | 1400 | 67 | S/T | 0.728
80 | 70 | 1400 | 67 | ∆T | 19.5
80 | 70 | 1400 | 67 | LDB | 60.5
80 | 70 | 1400 | 67 | LWB | 57.9
80 | 70 | 1400 | 67 | kW | 2.55
84 | 70 | 1400 | 70 | MBh | 44.8
84 | 70 | 1400 | 70 | S/T | 0.683
84 | 70 | 1400 | 70 | ∆T | 20.2
84 | 70 | 1400 | 70 | LDB | 63.8
84 | 70 | 1400 | 70 | LWB | 60.6
84 | 70 | 1400 | 70 | kW | 2.96
86 | 70 | 1400 | 72 | MBh | 47.6
86 | 70 | 1400 | 72 | S/T | 0.676
86 | 70 | 1400 | 72 | ∆T | 21.3
86 | 70 | 1400 | 72 | LDB | 64.7
86 | 70 | 1400 | 72 | LWB | 62.4
86 | 70 | 1400 | 72 | kW | 3.25
90 | 70 | 1400 | 75 | MBh | 49.1
90 | 70 | 1400 | 75 | S/T | 0.631
90 | 70 | 1400 | 75 | ∆T | 20.5
90 | 70 | 1400 | 75 | LDB | 69.5
90 | 70 | 1400 | 75 | LWB | 65.8
90 | 70 | 1400 | 75 | kW | 3.36
68 | 72 | 1400 | 57 | MBh | 26.3
68 | 72 | 1400 | 57 | S/T | 0.844
68 | 72 | 1400 | 57 | ∆T | 14.7
68 | 72 | 1400 | 57 | LDB | 53.3
68 | 72 | 1400 | 57 | LWB | 49.9
68 | 72 | 1400 | 57 | kW | 1.49
72 | 72 | 1400 | 61 | MBh | 32
72 | 72 | 1400 | 61 | S/T | 0.806
72 | 72 | 1400 | 61 | ∆T | 17.1
72 | 72 | 1400 | 61 | LDB | 54.9
72 | 72 | 1400 | 61 | LWB | 53
72 | 72 | 1400 | 61 | kW | 1.9
77 | 72 | 1400 | 64 | MBh | 36.2
77 | 72 | 1400 | 64 | S/T | 0.779
77 | 72 | 1400 | 64 | ∆T | 18.7
77 | 72 | 1400 | 64 | LDB | 58.3
77 | 72 | 1400 | 64 | LWB | 55.4
77 | 72 | 1400 | 64 | kW | 2.26
80 | 72 | 1400 | 67 | MBh | 40.5
80 | 72 | 1400 | 67 | S/T | 0.728
80 | 72 | 1400 | 67 | ∆T | 19.5
80 | 72 | 1400 | 67 | LDB | 60.5
80 | 72 | 1400 | 67 | LWB | 57.9
80 | 72 | 1400 | 67 | kW | 2.65
84 | 72 | 1400 | 70 | MBh | 44.8
84 | 72 | 1400 | 70 | S/T | 0.683
84 | 72 | 1400 | 70 | ∆T | 20.2
84 | 72 | 1400 | 70 | LDB | 63.8
84 | 72 | 1400 | 70 | LWB | 60.6
84 | 72 | 1400 | 70 | kW | 3.08
86 | 72 | 1400 | 72 | MBh | 47.6
86 | 72 | 1400 | 72 | S/T | 0.676
86 | 72 | 1400 | 72 | ∆T | 21.3
86 | 72 | 1400 | 72 | LDB | 64.7
86 | 72 | 1400 | 72 | LWB | 62.4
86 | 72 | 1400 | 72 | kW | 3.38
90 | 72 | 1400 | 75 | MBh | 48.7
90 | 72 | 1400 | 75 | S/T | 0.63
90 | 72 | 1400 | 75 | ∆T | 20.3
90 | 72 | 1400 | 75 | LDB | 69.7
90 | 72 | 1400 | 75 | LWB | 65.9
90 | 72 | 1400 | 75 | kW | 3.44
68 | 75 | 1400 | 57 | MBh | 26.3
68 | 75 | 1400 | 57 | S/T | 0.844
68 | 75 | 1400 | 57 | ∆T | 14.7
68 | 75 | 1400 | 57 | LDB | 53.3
68 | 75 | 1400 | 57 | LWB | 49.9
68 | 75 | 1400 | 57 | kW | 1.55
72 | 75 | 1400 | 61 | MBh | 32
72 | 75 | 1400 | 61 | S/T | 0.806
72 | 75 | 1400 | 61 | ∆T | 17.1
72 | 75 | 1400 | 61 | LDB | 54.9
72 | 75 | 1400 | 61 | LWB | 53
72 | 75 | 1400 | 61 | kW | 2.01
77 | 75 | 1400 | 64 | MBh | 36.2
77 | 75 | 1400 | 64 | S/T | 0.779
77 | 75 | 1400 | 64 | ∆T | 18.7
77 | 75 | 1400 | 64 | LDB | 58.3
77 | 75 | 1400 | 64 | LWB | 55.4
77 | 75 | 1400 | 64 | kW | 2.39
80 | 75 | 1400 | 67 | MBh | 40.5
80 | 75 | 1400 | 67 | S/T | 0.728
80 | 75 | 1400 | 67 | ∆T | 19.5
80 | 75 | 1400 | 67 | LDB | 60.5
80 | 75 | 1400 | 67 | LWB | 57.9
80 | 75 | 1400 | 67 | kW | 2.81
84 | 75 | 1400 | 70 | MBh | 44.8
84 | 75 | 1400 | 70 | S/T | 0.683
84 | 75 | 1400 | 70 | ∆T | 20.2
84 | 75 | 1400 | 70 | LDB | 63.8
84 | 75 | 1400 | 70 | LWB | 60.6
84 | 75 | 1400 | 70 | kW | 3.26
86 | 75 | 1400 | 72 | MBh | 47.3
86 | 75 | 1400 | 72 | S/T | 0.677
86 | 75 | 1400 | 72 | ∆T | 21.2
86 | 75 | 1400 | 72 | LDB | 64.8
86 | 75 | 1400 | 72 | LWB | 62.5
86 | 75 | 1400 | 72 | kW | 3.55
90 | 75 | 1400 | 75 | MBh | 48.2
90 | 75 | 1400 | 75 | S/T | 0.631
90 | 75 | 1400 | 75 | ∆T | 20.1
90 | 75 | 1400 | 75 | LDB | 69.9
90 | 75 | 1400 | 75 | LWB | 66
90 | 75 | 1400 | 75 | kW | 3.57
68 | 79 | 1400 | 57 | MBh | 26.3
68 | 79 | 1400 | 57 | S/T | 0.844
68 | 79 | 1400 | 57 | ∆T | 14.7
68 | 79 | 1400 | 57 | LDB | 53.3
68 | 79 | 1400 | 57 | LWB | 49.9
68 | 79 | 1400 | 57 | kW | 1.66
72 | 79 | 1400 | 61 | MBh | 32
72 | 79 | 1400 | 61 | S/T | 0.806
72 | 79 | 1400 | 61 | ∆T | 17.1
72 | 79 | 1400 | 61 | LDB | 54.9
72 | 79 | 1400 | 61 | LWB | 53
72 | 79 | 1400 | 61 | kW | 2.16
77 | 79 | 1400 | 64 | MBh | 36.2
77 | 79 | 1400 | 64 | S/T | 0.779
77 | 79 | 1400 | 64 | ∆T | 18.7
77 | 79 | 1400 | 64 | LDB | 58.3
77 | 79 | 1400 | 64 | LWB | 55.4
77 | 79 | 1400 | 64 | kW | 2.58
80 | 79 | 1400 | 67 | MBh | 40.5
80 | 79 | 1400 | 67 | S/T | 0.728
80 | 79 | 1400 | 67 | ∆T | 19.5
80 | 79 | 1400 | 67 | LDB | 60.5
80 | 79 | 1400 | 67 | LWB | 57.9
80 | 79 | 1400 | 67 | kW | 3.03
84 | 79 | 1400 | 70 | MBh | 44.8
84 | 79 | 1400 | 70 | S/T | 0.683
84 | 79 | 1400 | 70 | ∆T | 20.2
84 | 79 | 1400 | 70 | LDB | 63.8
84 | 79 | 1400 | 70 | LWB | 60.6
84 | 79 | 1400 | 70 | kW | 3.52
86 | 79 | 1400 | 72 | MBh | 46.6
86 | 79 | 1400 | 72 | S/T | 0.676
86 | 79 | 1400 | 72 | ∆T | 20.8
86 | 79 | 1400 | 72 | LDB | 65.2
86 | 79 | 1400 | 72 | LWB | 62.6
86 | 79 | 1400 | 72 | kW | 3.72
90 | 79 | 1400 | 75 | MBh | 47.4
90 | 79 | 1400 | 75 | S/T | 0.631
90 | 79 | 1400 | 75 | ∆T | 19.8
90 | 79 | 1400 | 75 | LDB | 70.2
90 | 79 | 1400 | 75 | LWB | 66.1
90 | 79 | 1400 | 75 | kW | 3.74
68 | 83 | 1400 | 57 | MBh | 26.3
68 | 83 | 1400 | 57 | S/T | 0.844
68 | 83 | 1400 | 57 | ∆T | 14.7
68 | 83 | 1400 | 57 | LDB | 53.3
68 | 83 | 1400 | 57 | LWB | 49.9
68 | 83 | 1400 | 57 | kW | 1.78
72 | 83 | 1400 | 61 | MBh | 32
72 | 83 | 1400 | 61 | S/T | 0.806
72 | 83 | 1400 | 61 | ∆T | 17.1
72 | 83 | 1400 | 61 | LDB | 54.9
72 | 83 | 1400 | 61 | LWB | 53
72 | 83 | 1400 | 61 | kW | 2.32
77 | 83 | 1400 | 64 | MBh | 36.2
77 | 83 | 1400 | 64 | S/T | 0.779
77 | 83 | 1400 | 64 | ∆T | 18.7
77 | 83 | 1400 | 64 | LDB | 58.3
77 | 83 | 1400 | 64 | LWB | 55.4
77 | 83 | 1400 | 64 | kW | 2.77
80 | 83 | 1400 | 67 | MBh | 40.5
80 | 83 | 1400 | 67 | S/T | 0.728
80 | 83 | 1400 | 67 | ∆T | 19.5
80 | 83 | 1400 | 67 | LDB | 60.5
80 | 83 | 1400 | 67 | LWB | 57.9
80 | 83 | 1400 | 67 | kW | 3.26
84 | 83 | 1400 | 70 | MBh | 44.8
84 | 83 | 1400 | 70 | S/T | 0.683
84 | 83 | 1400 | 70 | ∆T | 20.2
84 | 83 | 1400 | 70 | LDB | 63.8
84 | 83 | 1400 | 70 | LWB | 60.6
84 | 83 | 1400 | 70 | kW | 3.79
86 | 83 | 1400 | 72 | MBh | 45.8
86 | 83 | 1400 | 72 | S/T | 0.677
86 | 83 | 1400 | 72 | ∆T | 20.5
86 | 83 | 1400 | 72 | LDB | 65.5
86 | 83 | 1400 | 72 | LWB | 62.8
86 | 83 | 1400 | 72 | kW | 3.88
90 | 83 | 1400 | 75 | MBh | 46.6
90 | 83 | 1400 | 75 | S/T | 0.631
90 | 83 | 1400 | 75 | ∆T | 19.4
90 | 83 | 1400 | 75 | LDB | 70.6
90 | 83 | 1400 | 75 | LWB | 66.3
90 | 83 | 1400 | 75 | kW | 3.91
68 | 87 | 1400 | 57 | MBh | 26.3
68 | 87 | 1400 | 57 | S/T | 0.844
68 | 87 | 1400 | 57 | ∆T | 14.7
68 | 87 | 1400 | 57 | LDB | 53.3
68 | 87 | 1400 | 57 | LWB | 49.9
68 | 87 | 1400 | 57 | kW | 1.91
72 | 87 | 1400 | 61 | MBh | 32
72 | 87 | 1400 | 61 | S/T | 0.806
72 | 87 | 1400 | 61 | ∆T | 17.1
72 | 87 | 1400 | 61 | LDB | 54.9
72 | 87 | 1400 | 61 | LWB | 53
72 | 87 | 1400 | 61 | kW | 2.49
77 | 87 | 1400 | 64 | MBh | 36.2
77 | 87 | 1400 | 64 | S/T | 0.779
77 | 87 | 1400 | 64 | ∆T | 18.7
77 | 87 | 1400 | 64 | LDB | 58.3
77 | 87 | 1400 | 64 | LWB | 55.4
77 | 87 | 1400 | 64 | kW | 2.98
80 | 87 | 1400 | 67 | MBh | 40.5
80 | 87 | 1400 | 67 | S/T | 0.728
80 | 87 | 1400 | 67 | ∆T | 19.5
80 | 87 | 1400 | 67 | LDB | 60.5
80 | 87 | 1400 | 67 | LWB | 57.9
80 | 87 | 1400 | 67 | kW | 3.51
84 | 87 | 1400 | 70 | MBh | 44.5
84 | 87 | 1400 | 70 | S/T | 0.683
84 | 87 | 1400 | 70 | ∆T | 20.1
84 | 87 | 1400 | 70 | LDB | 63.9
84 | 87 | 1400 | 70 | LWB | 60.6
84 | 87 | 1400 | 70 | kW | 4.04
86 | 87 | 1400 | 72 | MBh | 45
86 | 87 | 1400 | 72 | S/T | 0.678
86 | 87 | 1400 | 72 | ∆T | 20.2
86 | 87 | 1400 | 72 | LDB | 65.8
86 | 87 | 1400 | 72 | LWB | 63
86 | 87 | 1400 | 72 | kW | 4.06
90 | 87 | 1400 | 75 | MBh | 45.9
90 | 87 | 1400 | 75 | S/T | 0.632
90 | 87 | 1400 | 75 | ∆T | 19.2
90 | 87 | 1400 | 75 | LDB | 70.8
90 | 87 | 1400 | 75 | LWB | 66.4
90 | 87 | 1400 | 75 | kW | 4.08
68 | 91 | 1400 | 57 | MBh | 26.3
68 | 91 | 1400 | 57 | S/T | 0.844
68 | 91 | 1400 | 57 | ∆T | 14.7
68 | 91 | 1400 | 57 | LDB | 53.3
68 | 91 | 1400 | 57 | LWB | 49.9
68 | 91 | 1400 | 57 | kW | 2.05
72 | 91 | 1400 | 61 | MBh | 32
72 | 91 | 1400 | 61 | S/T | 0.806
72 | 91 | 1400 | 61 | ∆T | 17.1
72 | 91 | 1400 | 61 | LDB | 54.9
72 | 91 | 1400 | 61 | LWB | 53
72 | 91 | 1400 | 61 | kW | 2.67
77 | 91 | 1400 | 64 | MBh | 36.2
77 | 91 | 1400 | 64 | S/T | 0.779
77 | 91 | 1400 | 64 | ∆T | 18.7
77 | 91 | 1400 | 64 | LDB | 58.3
77 | 91 | 1400 | 64 | LWB | 55.4
77 | 91 | 1400 | 64 | kW | 3.2
80 | 91 | 1400 | 67 | MBh | 40.5
80 | 91 | 1400 | 67 | S/T | 0.728
80 | 91 | 1400 | 67 | ∆T | 19.5
80 | 91 | 1400 | 67 | LDB | 60.5
80 | 91 | 1400 | 67 | LWB | 57.9
80 | 91 | 1400 | 67 | kW | 3.77
84 | 91 | 1400 | 70 | MBh | 43.7
84 | 91 | 1400 | 70 | S/T | 0.684
84 | 91 | 1400 | 70 | ∆T | 19.8
84 | 91 | 1400 | 70 | LDB | 64.2
84 | 91 | 1400 | 70 | LWB | 60.8
84 | 91 | 1400 | 70 | kW | 4.21
86 | 91 | 1400 | 72 | MBh | 44.3
86 | 91 | 1400 | 72 | S/T | 0.675
86 | 91 | 1400 | 72 | ∆T | 19.8
86 | 91 | 1400 | 72 | LDB | 66.2
86 | 91 | 1400 | 72 | LWB | 63.1
86 | 91 | 1400 | 72 | kW | 4.23
90 | 91 | 1400 | 75 | MBh | 45.1
90 | 91 | 1400 | 75 | S/T | 0.632
90 | 91 | 1400 | 75 | ∆T | 18.8
90 | 91 | 1400 | 75 | LDB | 71.2
90 | 91 | 1400 | 75 | LWB | 66.6
90 | 91 | 1400 | 75 | kW | 4.26
68 | 93 | 1400 | 57 | MBh | 26.3
68 | 93 | 1400 | 57 | S/T | 0.84
68 | 93 | 1400 | 57 | ∆T | 14.6
68 | 93 | 1400 | 57 | LDB | 53.4
68 | 93 | 1400 | 57 | LWB | 49.9
68 | 93 | 1400 | 57 | kW | 2.12
72 | 93 | 1400 | 61 | MBh | 32
72 | 93 | 1400 | 61 | S/T | 0.806
72 | 93 | 1400 | 61 | ∆T | 17.1
72 | 93 | 1400 | 61 | LDB | 54.9
72 | 93 | 1400 | 61 | LWB | 53
72 | 93 | 1400 | 61 | kW | 2.77
77 | 93 | 1400 | 64 | MBh | 36.2
77 | 93 | 1400 | 64 | S/T | 0.779
77 | 93 | 1400 | 64 | ∆T | 18.7
77 | 93 | 1400 | 64 | LDB | 58.3
77 | 93 | 1400 | 64 | LWB | 55.4
77 | 93 | 1400 | 64 | kW | 3.31
80 | 93 | 1400 | 67 | MBh | 40.5
80 | 93 | 1400 | 67 | S/T | 0.728
80 | 93 | 1400 | 67 | ∆T | 19.5
80 | 93 | 1400 | 67 | LDB | 60.5
80 | 93 | 1400 | 67 | LWB | 57.9
80 | 93 | 1400 | 67 | kW | 3.91
84 | 93 | 1400 | 70 | MBh | 43.3
84 | 93 | 1400 | 70 | S/T | 0.684
84 | 93 | 1400 | 70 | ∆T | 19.6
84 | 93 | 1400 | 70 | LDB | 64.4
84 | 93 | 1400 | 70 | LWB | 60.9
84 | 93 | 1400 | 70 | kW | 4.29
86 | 93 | 1400 | 72 | MBh | 43.9
86 | 93 | 1400 | 72 | S/T | 0.677
86 | 93 | 1400 | 72 | ∆T | 19.6
86 | 93 | 1400 | 72 | LDB | 66.4
86 | 93 | 1400 | 72 | LWB | 63.2
86 | 93 | 1400 | 72 | kW | 4.31
90 | 93 | 1400 | 75 | MBh | 44.7
90 | 93 | 1400 | 75 | S/T | 0.631
90 | 93 | 1400 | 75 | ∆T | 18.7
90 | 93 | 1400 | 75 | LDB | 71.3
90 | 93 | 1400 | 75 | LWB | 66.7
90 | 93 | 1400 | 75 | kW | 4.34
68 | 95 | 1400 | 57 | MBh | 26.3
68 | 95 | 1400 | 57 | S/T | 0.84
68 | 95 | 1400 | 57 | ∆T | 14.6
68 | 95 | 1400 | 57 | LDB | 53.4
68 | 95 | 1400 | 57 | LWB | 49.9
68 | 95 | 1400 | 57 | kW | 2.19
72 | 95 | 1400 | 61 | MBh | 32
72 | 95 | 1400 | 61 | S/T | 0.806
72 | 95 | 1400 | 61 | ∆T | 17.1
72 | 95 | 1400 | 61 | LDB | 54.9
72 | 95 | 1400 | 61 | LWB | 53
72 | 95 | 1400 | 61 | kW | 2.86
77 | 95 | 1400 | 64 | MBh | 36.2
77 | 95 | 1400 | 64 | S/T | 0.779
77 | 95 | 1400 | 64 | ∆T | 18.7
77 | 95 | 1400 | 64 | LDB | 58.3
77 | 95 | 1400 | 64 | LWB | 55.4
77 | 95 | 1400 | 64 | kW | 3.43
80 | 95 | 1400 | 67 | MBh | 40.5
80 | 95 | 1400 | 67 | S/T | 0.728
80 | 95 | 1400 | 67 | ∆T | 19.5
80 | 95 | 1400 | 67 | LDB | 60.5
80 | 95 | 1400 | 67 | LWB | 57.9
80 | 95 | 1400 | 67 | kW | 4.05
84 | 95 | 1400 | 70 | MBh | 43
84 | 95 | 1400 | 70 | S/T | 0.684
84 | 95 | 1400 | 70 | ∆T | 19.4
84 | 95 | 1400 | 70 | LDB | 64.6
84 | 95 | 1400 | 70 | LWB | 61
84 | 95 | 1400 | 70 | kW | 4.38
86 | 95 | 1400 | 72 | MBh | 43.5
86 | 95 | 1400 | 72 | S/T | 0.676
86 | 95 | 1400 | 72 | ∆T | 19.4
86 | 95 | 1400 | 72 | LDB | 66.6
86 | 95 | 1400 | 72 | LWB | 63.3
86 | 95 | 1400 | 72 | kW | 4.4
90 | 95 | 1400 | 75 | MBh | 44.4
90 | 95 | 1400 | 75 | S/T | 0.631
90 | 95 | 1400 | 75 | ∆T | 18.5
90 | 95 | 1400 | 75 | LDB | 71.5
90 | 95 | 1400 | 75 | LWB | 66.8
90 | 95 | 1400 | 75 | kW | 4.43
68 | 99 | 1400 | 57 | MBh | 26.3
68 | 99 | 1400 | 57 | S/T | 0.84
68 | 99 | 1400 | 57 | ∆T | 14.6
68 | 99 | 1400 | 57 | LDB | 53.4
68 | 99 | 1400 | 57 | LWB | 49.9
68 | 99 | 1400 | 57 | kW | 2.34
72 | 99 | 1400 | 61 | MBh | 32
72 | 99 | 1400 | 61 | S/T | 0.806
72 | 99 | 1400 | 61 | ∆T | 17.1
72 | 99 | 1400 | 61 | LDB | 54.9
72 | 99 | 1400 | 61 | LWB | 53
72 | 99 | 1400 | 61 | kW | 3.07
77 | 99 | 1400 | 64 | MBh | 36.2
77 | 99 | 1400 | 64 | S/T | 0.779
77 | 99 | 1400 | 64 | ∆T | 18.7
77 | 99 | 1400 | 64 | LDB | 58.3
77 | 99 | 1400 | 64 | LWB | 55.4
77 | 99 | 1400 | 64 | kW | 3.68
80 | 99 | 1400 | 67 | MBh | 40.5
80 | 99 | 1400 | 67 | S/T | 0.728
80 | 99 | 1400 | 67 | ∆T | 19.5
80 | 99 | 1400 | 67 | LDB | 60.5
80 | 99 | 1400 | 67 | LWB | 57.9
80 | 99 | 1400 | 67 | kW | 4.35
84 | 99 | 1400 | 70 | MBh | 42.2
84 | 99 | 1400 | 70 | S/T | 0.687
84 | 99 | 1400 | 70 | ∆T | 19.2
84 | 99 | 1400 | 70 | LDB | 64.8
84 | 99 | 1400 | 70 | LWB | 61.2
84 | 99 | 1400 | 70 | kW | 4.55
86 | 99 | 1400 | 72 | MBh | 42.8
86 | 99 | 1400 | 72 | S/T | 0.678
86 | 99 | 1400 | 72 | ∆T | 19.2
86 | 99 | 1400 | 72 | LDB | 66.8
86 | 99 | 1400 | 72 | LWB | 63.5
86 | 99 | 1400 | 72 | kW | 4.57
90 | 99 | 1400 | 75 | MBh | 43.6
90 | 99 | 1400 | 75 | S/T | 0.633
90 | 99 | 1400 | 75 | ∆T | 18.3
90 | 99 | 1400 | 75 | LDB | 71.7
90 | 99 | 1400 | 75 | LWB | 66.9
90 | 99 | 1400 | 75 | kW | 4.6
68 | 103 | 1400 | 57 | MBh | 26.3
68 | 103 | 1400 | 57 | S/T | 0.84
68 | 103 | 1400 | 57 | ∆T | 14.6
68 | 103 | 1400 | 57 | LDB | 53.4
68 | 103 | 1400 | 57 | LWB | 49.9
68 | 103 | 1400 | 57 | kW | 2.5
72 | 103 | 1400 | 61 | MBh | 32
72 | 103 | 1400 | 61 | S/T | 0.806
72 | 103 | 1400 | 61 | ∆T | 17.1
72 | 103 | 1400 | 61 | LDB | 54.9
72 | 103 | 1400 | 61 | LWB | 53
72 | 103 | 1400 | 61 | kW | 3.28
77 | 103 | 1400 | 64 | MBh | 36.2
77 | 103 | 1400 | 64 | S/T | 0.779
77 | 103 | 1400 | 64 | ∆T | 18.7
77 | 103 | 1400 | 64 | LDB | 58.3
77 | 103 | 1400 | 64 | LWB | 55.4
77 | 103 | 1400 | 64 | kW | 3.94
80 | 103 | 1400 | 67 | MBh | 40.5
80 | 103 | 1400 | 67 | S/T | 0.728
80 | 103 | 1400 | 67 | ∆T | 19.5
80 | 103 | 1400 | 67 | LDB | 60.5
80 | 103 | 1400 | 67 | LWB | 57.9
80 | 103 | 1400 | 67 | kW | 4.67
84 | 103 | 1400 | 70 | MBh | 41.4
84 | 103 | 1400 | 70 | S/T | 0.688
84 | 103 | 1400 | 70 | ∆T | 18.8
84 | 103 | 1400 | 70 | LDB | 65.2
84 | 103 | 1400 | 70 | LWB | 61.4
84 | 103 | 1400 | 70 | kW | 4.72
86 | 103 | 1400 | 72 | MBh | 42
86 | 103 | 1400 | 72 | S/T | 0.679
86 | 103 | 1400 | 72 | ∆T | 18.8
86 | 103 | 1400 | 72 | LDB | 67.2
86 | 103 | 1400 | 72 | LWB | 63.6
86 | 103 | 1400 | 72 | kW | 4.75
90 | 103 | 1400 | 75 | MBh | 42
90 | 103 | 1400 | 75 | S/T | 0.633
90 | 103 | 1400 | 75 | ∆T | 17.6
90 | 103 | 1400 | 75 | LDB | 72.4
90 | 103 | 1400 | 75 | LWB | 67.2
90 | 103 | 1400 | 75 | kW | 4.75
68 | 106 | 1400 | 57 | MBh | 26.3
68 | 106 | 1400 | 57 | S/T | 0.84
68 | 106 | 1400 | 57 | ∆T | 14.6
68 | 106 | 1400 | 57 | LDB | 53.4
68 | 106 | 1400 | 57 | LWB | 49.9
68 | 106 | 1400 | 57 | kW | 2.63
72 | 106 | 1400 | 61 | MBh | 32
72 | 106 | 1400 | 61 | S/T | 0.806
72 | 106 | 1400 | 61 | ∆T | 17.1
72 | 106 | 1400 | 61 | LDB | 54.9
72 | 106 | 1400 | 61 | LWB | 53
72 | 106 | 1400 | 61 | kW | 3.46
77 | 106 | 1400 | 64 | MBh | 36.2
77 | 106 | 1400 | 64 | S/T | 0.779
77 | 106 | 1400 | 64 | ∆T | 18.7
77 | 106 | 1400 | 64 | LDB | 58.3
77 | 106 | 1400 | 64 | LWB | 55.4
77 | 106 | 1400 | 64 | kW | 4.16
80 | 106 | 1400 | 67 | MBh | 40
80 | 106 | 1400 | 67 | S/T | 0.733
80 | 106 | 1400 | 67 | ∆T | 19.4
80 | 106 | 1400 | 67 | LDB | 60.6
80 | 106 | 1400 | 67 | LWB | 58.1
80 | 106 | 1400 | 67 | kW | 4.82
84 | 106 | 1400 | 70 | MBh | 40.7
84 | 106 | 1400 | 70 | S/T | 0.686
84 | 106 | 1400 | 70 | ∆T | 18.5
84 | 106 | 1400 | 70 | LDB | 65.5
84 | 106 | 1400 | 70 | LWB | 61.5
84 | 106 | 1400 | 70 | kW | 4.84
86 | 106 | 1400 | 72 | MBh | 40.7
86 | 106 | 1400 | 72 | S/T | 0.678
86 | 106 | 1400 | 72 | ∆T | 18.3
86 | 106 | 1400 | 72 | LDB | 67.7
86 | 106 | 1400 | 72 | LWB | 63.9
86 | 106 | 1400 | 72 | kW | 4.84
90 | 106 | 1400 | 75 | MBh | 40.7
90 | 106 | 1400 | 75 | S/T | 0.634
90 | 106 | 1400 | 75 | ∆T | 17.1
90 | 106 | 1400 | 75 | LDB | 72.9
90 | 106 | 1400 | 75 | LWB | 67.5
90 | 106 | 1400 | 75 | kW | 4.84
68 | 110 | 1400 | 57 | MBh | 26.3
68 | 110 | 1400 | 57 | S/T | 0.84
68 | 110 | 1400 | 57 | ∆T | 14.6
68 | 110 | 1400 | 57 | LDB | 53.4
68 | 110 | 1400 | 57 | LWB | 49.9
68 | 110 | 1400 | 57 | kW | 2.81
72 | 110 | 1400 | 61 | MBh | 32
72 | 110 | 1400 | 61 | S/T | 0.806
72 | 110 | 1400 | 61 | ∆T | 17.1
72 | 110 | 1400 | 61 | LDB | 54.9
72 | 110 | 1400 | 61 | LWB | 53
72 | 110 | 1400 | 61 | kW | 3.7
77 | 110 | 1400 | 64 | MBh | 36.2
77 | 110 | 1400 | 64 | S/T | 0.779
77 | 110 | 1400 | 64 | ∆T | 18.7
77 | 110 | 1400 | 64 | LDB | 58.3
77 | 110 | 1400 | 64 | LWB | 55.4
77 | 110 | 1400 | 64 | kW | 4.45
80 | 110 | 1400 | 67 | MBh | 38
80 | 110 | 1400 | 67 | S/T | 0.732
80 | 110 | 1400 | 67 | ∆T | 18.4
80 | 110 | 1400 | 67 | LDB | 61.6
80 | 110 | 1400 | 67 | LWB | 58.5
80 | 110 | 1400 | 67 | kW | 4.79
84 | 110 | 1400 | 70 | MBh | 38
84 | 110 | 1400 | 70 | S/T | 0.687
84 | 110 | 1400 | 70 | ∆T | 17.3
84 | 110 | 1400 | 70 | LDB | 66.7
84 | 110 | 1400 | 70 | LWB | 62.1
84 | 110 | 1400 | 70 | kW | 4.79
86 | 110 | 1400 | 72 | MBh | 38
86 | 110 | 1400 | 72 | S/T | 0.679
86 | 110 | 1400 | 72 | ∆T | 17.1
86 | 110 | 1400 | 72 | LDB | 68.9
86 | 110 | 1400 | 72 | LWB | 64.5
86 | 110 | 1400 | 72 | kW | 4.79
90 | 110 | 1400 | 75 | MBh | 38
90 | 110 | 1400 | 75 | S/T | 0.634
90 | 110 | 1400 | 75 | ∆T | 15.9
90 | 110 | 1400 | 75 | LDB | 74.1
90 | 110 | 1400 | 75 | LWB | 68
90 | 110 | 1400 | 75 | kW | 4.79
68 | 115 | 1400 | 57 | MBh | 26.3
68 | 115 | 1400 | 57 | S/T | 0.84
68 | 115 | 1400 | 57 | ∆T | 14.6
68 | 115 | 1400 | 57 | LDB | 53.4
68 | 115 | 1400 | 57 | LWB | 49.9
68 | 115 | 1400 | 57 | kW | 3.11
72 | 115 | 1400 | 61 | MBh | 31
72 | 115 | 1400 | 61 | S/T | 0.81
72 | 115 | 1400 | 61 | ∆T | 16.6
72 | 115 | 1400 | 61 | LDB | 55.4
72 | 115 | 1400 | 61 | LWB | 53.2
72 | 115 | 1400 | 61 | kW | 3.93
77 | 115 | 1400 | 64 | MBh | 31
77 | 115 | 1400 | 64 | S/T | 0.784
77 | 115 | 1400 | 64 | ∆T | 16.1
77 | 115 | 1400 | 64 | LDB | 60.9
77 | 115 | 1400 | 64 | LWB | 56.7
77 | 115 | 1400 | 64 | kW | 3.93
80 | 115 | 1400 | 67 | MBh | 31
80 | 115 | 1400 | 67 | S/T | 0.732
80 | 115 | 1400 | 67 | ∆T | 15
80 | 115 | 1400 | 67 | LDB | 65
80 | 115 | 1400 | 67 | LWB | 60.2
80 | 115 | 1400 | 67 | kW | 3.93
84 | 115 | 1400 | 70 | MBh | 31
84 | 115 | 1400 | 70 | S/T | 0.687
84 | 115 | 1400 | 70 | ∆T | 14.1
84 | 115 | 1400 | 70 | LDB | 69.9
84 | 115 | 1400 | 70 | LWB | 63.7
84 | 115 | 1400 | 70 | kW | 3.93
86 | 115 | 1400 | 72 | MBh | 31
86 | 115 | 1400 | 72 | S/T | 0.681
86 | 115 | 1400 | 72 | ∆T | 14
86 | 115 | 1400 | 72 | LDB | 72
86 | 115 | 1400 | 72 | LWB | 66
86 | 115 | 1400 | 72 | kW | 3.93
90 | 115 | 1400 | 75 | MBh | 31
90 | 115 | 1400 | 75 | S/T | 0.635
90 | 115 | 1400 | 75 | ∆T | 13
90 | 115 | 1400 | 75 | LDB | 77
90 | 115 | 1400 | 75 | LWB | 69.4
90 | 115 | 1400 | 75 | kW | 3.93
68 | 118 | 1400 | 57 | MBh | 26.3
68 | 118 | 1400 | 57 | S/T | 0.84
68 | 118 | 1400 | 57 | ∆T | 14.6
68 | 118 | 1400 | 57 | LDB | 53.4
68 | 118 | 1400 | 57 | LWB | 49.9
68 | 118 | 1400 | 57 | kW | 3.34
72 | 118 | 1400 | 61 | MBh | 26.8
72 | 118 | 1400 | 61 | S/T | 0.81
72 | 118 | 1400 | 61 | ∆T | 14.4
72 | 118 | 1400 | 61 | LDB | 57.6
72 | 118 | 1400 | 61 | LWB | 54.4
72 | 118 | 1400 | 61 | kW | 3.44
77 | 118 | 1400 | 64 | MBh | 26.8
77 | 118 | 1400 | 64 | S/T | 0.784
77 | 118 | 1400 | 64 | ∆T | 13.9
77 | 118 | 1400 | 64 | LDB | 63.1
77 | 118 | 1400 | 64 | LWB | 57.8
77 | 118 | 1400 | 64 | kW | 3.44
80 | 118 | 1400 | 67 | MBh | 26.8
80 | 118 | 1400 | 67 | S/T | 0.735
80 | 118 | 1400 | 67 | ∆T | 13
80 | 118 | 1400 | 67 | LDB | 67
80 | 118 | 1400 | 67 | LWB | 61.2
80 | 118 | 1400 | 67 | kW | 3.44
84 | 118 | 1400 | 70 | MBh | 26.8
84 | 118 | 1400 | 70 | S/T | 0.69
84 | 118 | 1400 | 70 | ∆T | 12.2
84 | 118 | 1400 | 70 | LDB | 71.8
84 | 118 | 1400 | 70 | LWB | 64.6
84 | 118 | 1400 | 70 | kW | 3.44
86 | 118 | 1400 | 72 | MBh | 26.8
86 | 118 | 1400 | 72 | S/T | 0.683
86 | 118 | 1400 | 72 | ∆T | 12.1
86 | 118 | 1400 | 72 | LDB | 73.9
86 | 118 | 1400 | 72 | LWB | 66.8
86 | 118 | 1400 | 72 | kW | 3.44
90 | 118 | 1400 | 75 | MBh | 26.8
90 | 118 | 1400 | 75 | S/T | 0.634
90 | 118 | 1400 | 75 | ∆T | 11.2
90 | 118 | 1400 | 75 | LDB | 78.8
90 | 118 | 1400 | 75 | LWB | 70.2
90 | 118 | 1400 | 75 | kW | 3.44
68 | 122 | 1400 | 57 | MBh | 21.2
68 | 122 | 1400 | 57 | S/T | 0.849
68 | 122 | 1400 | 57 | ∆T | 11.9
68 | 122 | 1400 | 57 | LDB | 56.1
68 | 122 | 1400 | 57 | LWB | 51.4
68 | 122 | 1400 | 57 | kW | 2.76
72 | 122 | 1400 | 61 | MBh | 21.2
72 | 122 | 1400 | 61 | S/T | 0.811
72 | 122 | 1400 | 61 | ∆T | 11.4
72 | 122 | 1400 | 61 | LDB | 60.6
72 | 122 | 1400 | 61 | LWB | 55.8
72 | 122 | 1400 | 61 | kW | 2.76
77 | 122 | 1400 | 64 | MBh | 21.2
77 | 122 | 1400 | 64 | S/T | 0.783
77 | 122 | 1400 | 64 | ∆T | 11
77 | 122 | 1400 | 64 | LDB | 66
77 | 122 | 1400 | 64 | LWB | 59.1
77 | 122 | 1400 | 64 | kW | 2.76
80 | 122 | 1400 | 67 | MBh | 21.2
80 | 122 | 1400 | 67 | S/T | 0.736
80 | 122 | 1400 | 67 | ∆T | 10.3
80 | 122 | 1400 | 67 | LDB | 69.7
80 | 122 | 1400 | 67 | LWB | 62.5
80 | 122 | 1400 | 67 | kW | 2.76
84 | 122 | 1400 | 70 | MBh | 21.2
84 | 122 | 1400 | 70 | S/T | 0.689
84 | 122 | 1400 | 70 | ∆T | 9.7
84 | 122 | 1400 | 70 | LDB | 74.3
84 | 122 | 1400 | 70 | LWB | 65.8
84 | 122 | 1400 | 70 | kW | 2.76
86 | 122 | 1400 | 72 | MBh | 21.2
86 | 122 | 1400 | 72 | S/T | 0.684
86 | 122 | 1400 | 72 | ∆T | 9.6
86 | 122 | 1400 | 72 | LDB | 76.4
86 | 122 | 1400 | 72 | LWB | 68
86 | 122 | 1400 | 72 | kW | 2.76
90 | 122 | 1400 | 75 | MBh | 21.2
90 | 122 | 1400 | 75 | S/T | 0.637
90 | 122 | 1400 | 75 | ∆T | 8.9
90 | 122 | 1400 | 75 | LDB | 81.1
90 | 122 | 1400 | 75 | LWB | 71.2
90 | 122 | 1400 | 75 | kW | 2.76

## RZA48AAVJU - FTA48AAVJUD
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1520 | 57 | MBh | 30.5 | 64 | 60 | 61 | 66 | 5.44
68 | 23 | 1520 | 57 | S/T | 0.807 | 64 | 60 | 65 | 61.1 | 4.53
68 | 23 | 1520 | 57 | ∆T | 15 | 64 | 60 | 68 | 57.5 | 3.98
68 | 23 | 1520 | 57 | LDB | 53 | 64 | 60 | 70 | 55 | 3.68
68 | 23 | 1520 | 57 | LWB | 49.4 | 64 | 60 | 72 | 52.5 | 3.43
68 | 23 | 1520 | 57 | kW | 1.55 | 64 | 60 | 75 | 48.9 | 3.16
72 | 23 | 1520 | 61 | MBh | 37.1 | 60 | 56 | 61 | 66 | 5.92
72 | 23 | 1520 | 61 | S/T | 0.763 | 60 | 56 | 65 | 61.1 | 4.88
72 | 23 | 1520 | 61 | ∆T | 17.2 | 60 | 56 | 68 | 57.5 | 4.25
72 | 23 | 1520 | 61 | LDB | 54.8 | 60 | 56 | 70 | 55 | 3.9
72 | 23 | 1520 | 61 | LWB | 52.4 | 60 | 56 | 72 | 52.5 | 3.61
72 | 23 | 1520 | 61 | kW | 1.91 | 60 | 56 | 75 | 48.9 | 3.27
77 | 23 | 1520 | 64 | MBh | 42 | 57 | 53 | 61 | 66 | 6.34
77 | 23 | 1520 | 64 | S/T | 0.729 | 57 | 53 | 65 | 61.1 | 5.2
77 | 23 | 1520 | 64 | ∆T | 18.6 | 57 | 53 | 68 | 57.5 | 4.49
77 | 23 | 1520 | 64 | LDB | 58.4 | 57 | 53 | 70 | 55 | 4.1
77 | 23 | 1520 | 64 | LWB | 54.8 | 57 | 53 | 72 | 52.5 | 3.76
77 | 23 | 1520 | 64 | kW | 2.19 | 57 | 53 | 75 | 48.9 | 3.37
80 | 23 | 1520 | 67 | MBh | 47 | 54 | 50 | 61 | 66 | 6.81
80 | 23 | 1520 | 67 | S/T | 0.681 | 54 | 50 | 65 | 61.1 | 5.55
80 | 23 | 1520 | 67 | ∆T | 19.5 | 54 | 50 | 68 | 57.5 | 4.77
80 | 23 | 1520 | 67 | LDB | 60.5 | 54 | 50 | 70 | 55 | 4.33
80 | 23 | 1520 | 67 | LWB | 57.3 | 54 | 50 | 72 | 52.5 | 3.95
80 | 23 | 1520 | 67 | kW | 2.48 | 54 | 50 | 75 | 48.9 | 3.49
84 | 23 | 1520 | 70 | MBh | 52 | 51 | 47 | 61 | 66 | 7.34
84 | 23 | 1520 | 70 | S/T | 0.65 | 51 | 47 | 65 | 61.1 | 5.96
84 | 23 | 1520 | 70 | ∆T | 20.6 | 51 | 47 | 68 | 57.5 | 5.09
84 | 23 | 1520 | 70 | LDB | 63.4 | 51 | 47 | 70 | 55 | 4.59
84 | 23 | 1520 | 70 | LWB | 59.9 | 51 | 47 | 72 | 52.5 | 4.16
84 | 23 | 1520 | 70 | kW | 2.78 | 51 | 47 | 75 | 48.9 | 3.64
86 | 23 | 1520 | 72 | MBh | 55.3 | 47 | 43 | 61 | 65.3 | 8.16
86 | 23 | 1520 | 72 | S/T | 0.642 | 47 | 43 | 65 | 61.1 | 6.58
86 | 23 | 1520 | 72 | ∆T | 21.6 | 47 | 43 | 68 | 57.5 | 5.59
86 | 23 | 1520 | 72 | LDB | 64.4 | 47 | 43 | 70 | 55 | 5.01
86 | 23 | 1520 | 72 | LWB | 61.7 | 47 | 43 | 72 | 52.5 | 4.51
86 | 23 | 1520 | 72 | kW | 2.99 | 47 | 43 | 75 | 48.9 | 3.89
90 | 23 | 1520 | 75 | MBh | 60.2 | 44 | 40 | 61 | 63.4 | 8.42
90 | 23 | 1520 | 75 | S/T | 0.61 | 44 | 40 | 65 | 61.1 | 7.13
90 | 23 | 1520 | 75 | ∆T | 22.4 | 44 | 40 | 68 | 57.5 | 6.03
90 | 23 | 1520 | 75 | LDB | 67.6 | 44 | 40 | 70 | 55 | 5.39
90 | 23 | 1520 | 75 | LWB | 64.5 | 44 | 40 | 72 | 52.5 | 4.82
90 | 23 | 1520 | 75 | kW | 3.3 | 44 | 40 | 75 | 48.9 | 4.11
68 | 30 | 1520 | 57 | MBh | 30.5 | 39 | 36 | 61 | 60.8 | 8.14
68 | 30 | 1520 | 57 | S/T | 0.807 | 39 | 36 | 65 | 60.8 | 7.97
68 | 30 | 1520 | 57 | ∆T | 15 | 39 | 36 | 68 | 57.5 | 6.71
68 | 30 | 1520 | 57 | LDB | 53 | 39 | 36 | 70 | 55 | 5.97
68 | 30 | 1520 | 57 | LWB | 49.4 | 39 | 36 | 72 | 52.5 | 5.31
68 | 30 | 1520 | 57 | kW | 1.6 | 39 | 36 | 75 | 48.9 | 4.47
72 | 30 | 1520 | 61 | MBh | 37.1 | 35 | 32 | 61 | 58.2 | 7.84
72 | 30 | 1520 | 61 | S/T | 0.763 | 35 | 32 | 65 | 58.2 | 8.37
72 | 30 | 1520 | 61 | ∆T | 17.2 | 35 | 32 | 68 | 57.5 | 7.53
72 | 30 | 1520 | 61 | LDB | 54.8 | 35 | 32 | 70 | 55 | 6.68
72 | 30 | 1520 | 61 | LWB | 52.4 | 35 | 32 | 72 | 52.5 | 5.91
72 | 30 | 1520 | 61 | kW | 1.97 | 35 | 32 | 75 | 48.9 | 4.93
77 | 30 | 1520 | 64 | MBh | 42 | 30 | 28 | 61 | 55.6 | 7.51
77 | 30 | 1520 | 64 | S/T | 0.729 | 30 | 28 | 65 | 55.6 | 8.06
77 | 30 | 1520 | 64 | ∆T | 18.6 | 30 | 28 | 68 | 55.6 | 8.48
77 | 30 | 1520 | 64 | LDB | 58.4 | 30 | 28 | 70 | 55 | 7.53
77 | 30 | 1520 | 64 | LWB | 54.8 | 30 | 28 | 72 | 52.5 | 6.64
77 | 30 | 1520 | 64 | kW | 2.26 | 30 | 28 | 75 | 48.9 | 5.49
80 | 30 | 1520 | 67 | MBh | 47 | 26 | 24 | 61 | 53 | 7.15
80 | 30 | 1520 | 67 | S/T | 0.681 | 26 | 24 | 65 | 53 | 7.73
80 | 30 | 1520 | 67 | ∆T | 19.5 | 26 | 24 | 68 | 53 | 8.16
80 | 30 | 1520 | 67 | LDB | 60.5 | 26 | 24 | 70 | 53 | 8.45
80 | 30 | 1520 | 67 | LWB | 57.3 | 26 | 24 | 72 | 52.5 | 7.54
80 | 30 | 1520 | 67 | kW | 2.56 | 26 | 24 | 75 | 48.9 | 6.18
84 | 30 | 1520 | 70 | MBh | 52 | 22 | 20 | 61 | 50.5 | 6.76
84 | 30 | 1520 | 70 | S/T | 0.65 | 22 | 20 | 65 | 50.5 | 7.37
84 | 30 | 1520 | 70 | ∆T | 20.6 | 22 | 20 | 68 | 50.5 | 7.82
84 | 30 | 1520 | 70 | LDB | 63.4 | 22 | 20 | 70 | 50.5 | 8.13
84 | 30 | 1520 | 70 | LWB | 59.9 | 22 | 20 | 72 | 50.5 | 8.35
84 | 30 | 1520 | 70 | kW | 2.87 | 22 | 20 | 75 | 48.9 | 7.04
86 | 30 | 1520 | 72 | MBh | 55.3 | 19 | 18 | 61 | 49.2 | 6.55
86 | 30 | 1520 | 72 | S/T | 0.642 | 19 | 18 | 65 | 49.2 | 7.17
86 | 30 | 1520 | 72 | ∆T | 21.6 | 19 | 18 | 68 | 49.2 | 7.64
86 | 30 | 1520 | 72 | LDB | 64.4 | 19 | 18 | 70 | 49.2 | 7.95
86 | 30 | 1520 | 72 | LWB | 61.7 | 19 | 18 | 72 | 49.2 | 8.03
86 | 30 | 1520 | 72 | kW | 3.09 | 19 | 18 | 75 | 48.9 | 7.54
90 | 30 | 1520 | 75 | MBh | 60.2 | 17 | 16 | 61 | 47.6 | 6.27
90 | 30 | 1520 | 75 | S/T | 0.61 | 17 | 16 | 65 | 47.6 | 6.91
90 | 30 | 1520 | 75 | ∆T | 22.4 | 17 | 16 | 68 | 47.6 | 7.39
90 | 30 | 1520 | 75 | LDB | 67.6 | 17 | 16 | 70 | 47.6 | 7.64
90 | 30 | 1520 | 75 | LWB | 64.5 | 17 | 16 | 72 | 47.6 | 7.64
90 | 30 | 1520 | 75 | kW | 3.41 | 17 | 16 | 75 | 47.6 | 7.64
68 | 40 | 1520 | 57 | MBh | 30.5 | 15 | 14 | 61 | 46.6 | 6.09
68 | 40 | 1520 | 57 | S/T | 0.807 | 15 | 14 | 65 | 46.6 | 6.75
68 | 40 | 1520 | 57 | ∆T | 15 | 15 | 14 | 68 | 46.6 | 7.24
68 | 40 | 1520 | 57 | LDB | 53 | 15 | 14 | 70 | 46.6 | 7.4
68 | 40 | 1520 | 57 | LWB | 49.4 | 15 | 14 | 72 | 46.6 | 7.4
68 | 40 | 1520 | 57 | kW | 1.67 | 15 | 14 | 75 | 46.6 | 7.4
72 | 40 | 1520 | 61 | MBh | 37.1 | 13 | 12 | 61 | 45.3 | 5.85
72 | 40 | 1520 | 61 | S/T | 0.763 | 13 | 12 | 65 | 45.3 | 6.52
72 | 40 | 1520 | 61 | ∆T | 17.2 | 13 | 12 | 68 | 45.3 | 7.03
72 | 40 | 1520 | 61 | LDB | 54.8 | 13 | 12 | 70 | 45.3 | 7.08
72 | 40 | 1520 | 61 | LWB | 52.4 | 13 | 12 | 72 | 45.3 | 7.08
72 | 40 | 1520 | 61 | kW | 2.06 | 13 | 12 | 75 | 45.3 | 7.08
77 | 40 | 1520 | 64 | MBh | 42 | 10 | 9 | 61 | 43.1 | 5.39
77 | 40 | 1520 | 64 | S/T | 0.729 | 10 | 9 | 65 | 43.1 | 6.09
77 | 40 | 1520 | 64 | ∆T | 18.6 | 10 | 9 | 68 | 43.1 | 6.53
77 | 40 | 1520 | 64 | LDB | 58.4 | 10 | 9 | 70 | 43.1 | 6.53
77 | 40 | 1520 | 64 | LWB | 54.8 | 10 | 9 | 72 | 43.1 | 6.53
77 | 40 | 1520 | 64 | kW | 2.37 | 10 | 9 | 75 | 43.1 | 6.53
80 | 40 | 1520 | 67 | MBh | 47 | 6 | 5 | 61 | 40.8 | 4.88
80 | 40 | 1520 | 67 | S/T | 0.681 | 6 | 5 | 65 | 40.8 | 5.62
80 | 40 | 1520 | 67 | ∆T | 19.5 | 6 | 5 | 68 | 40.8 | 5.98
80 | 40 | 1520 | 67 | LDB | 60.5 | 6 | 5 | 70 | 40.8 | 5.98
80 | 40 | 1520 | 67 | LWB | 57.3 | 6 | 5 | 72 | 40.8 | 5.98
80 | 40 | 1520 | 67 | kW | 2.69 | 6 | 5 | 75 | 40.8 | 5.98
84 | 40 | 1520 | 70 | MBh | 52 | -2 | -2 | 61 | 33.8 | 3.64
84 | 40 | 1520 | 70 | S/T | 0.65 | -2 | -2 | 65 | 33.8 | 4.48
84 | 40 | 1520 | 70 | ∆T | 20.6 | -2 | -2 | 68 | 33.8 | 4.84
84 | 40 | 1520 | 70 | LDB | 63.4 | -2 | -2 | 70 | 33.8 | 4.84
84 | 40 | 1520 | 70 | LWB | 59.9 | -2 | -2 | 72 | 33.8 | 4.84
84 | 40 | 1520 | 70 | kW | 3.02 | -2 | -2 | 75 | 33.8 | 4.84
86 | 40 | 1520 | 72 | MBh | 55.3 | -4 | -4 | 61 | 32 | 3.29
86 | 40 | 1520 | 72 | S/T | 0.642 | -4 | -4 | 65 | 32 | 4.15
86 | 40 | 1520 | 72 | ∆T | 21.6 | -4 | -4 | 68 | 32 | 4.56
86 | 40 | 1520 | 72 | LDB | 64.4 | -4 | -4 | 70 | 32 | 4.56
86 | 40 | 1520 | 72 | LWB | 61.7 | -4 | -4 | 72 | 32 | 4.56
86 | 40 | 1520 | 72 | kW | 3.24 | -4 | -4 | 75 | 32 | 4.56
90 | 40 | 1520 | 75 | MBh | 60.2
90 | 40 | 1520 | 75 | S/T | 0.61
90 | 40 | 1520 | 75 | ∆T | 22.4
90 | 40 | 1520 | 75 | LDB | 67.6
90 | 40 | 1520 | 75 | LWB | 64.5
90 | 40 | 1520 | 75 | kW | 3.58
68 | 50 | 1520 | 57 | MBh | 30.5
68 | 50 | 1520 | 57 | S/T | 0.807
68 | 50 | 1520 | 57 | ∆T | 15
68 | 50 | 1520 | 57 | LDB | 53
68 | 50 | 1520 | 57 | LWB | 49.4
68 | 50 | 1520 | 57 | kW | 1.75
72 | 50 | 1520 | 61 | MBh | 37.1
72 | 50 | 1520 | 61 | S/T | 0.763
72 | 50 | 1520 | 61 | ∆T | 17.2
72 | 50 | 1520 | 61 | LDB | 54.8
72 | 50 | 1520 | 61 | LWB | 52.4
72 | 50 | 1520 | 61 | kW | 2.16
77 | 50 | 1520 | 64 | MBh | 42
77 | 50 | 1520 | 64 | S/T | 0.729
77 | 50 | 1520 | 64 | ∆T | 18.6
77 | 50 | 1520 | 64 | LDB | 58.4
77 | 50 | 1520 | 64 | LWB | 54.8
77 | 50 | 1520 | 64 | kW | 2.49
80 | 50 | 1520 | 67 | MBh | 47
80 | 50 | 1520 | 67 | S/T | 0.681
80 | 50 | 1520 | 67 | ∆T | 19.5
80 | 50 | 1520 | 67 | LDB | 60.5
80 | 50 | 1520 | 67 | LWB | 57.3
80 | 50 | 1520 | 67 | kW | 2.82
84 | 50 | 1520 | 70 | MBh | 52
84 | 50 | 1520 | 70 | S/T | 0.65
84 | 50 | 1520 | 70 | ∆T | 20.6
84 | 50 | 1520 | 70 | LDB | 63.4
84 | 50 | 1520 | 70 | LWB | 59.9
84 | 50 | 1520 | 70 | kW | 3.17
86 | 50 | 1520 | 72 | MBh | 55.3
86 | 50 | 1520 | 72 | S/T | 0.642
86 | 50 | 1520 | 72 | ∆T | 21.6
86 | 50 | 1520 | 72 | LDB | 64.4
86 | 50 | 1520 | 72 | LWB | 61.7
86 | 50 | 1520 | 72 | kW | 3.41
90 | 50 | 1520 | 75 | MBh | 60.2
90 | 50 | 1520 | 75 | S/T | 0.61
90 | 50 | 1520 | 75 | ∆T | 22.4
90 | 50 | 1520 | 75 | LDB | 67.6
90 | 50 | 1520 | 75 | LWB | 64.5
90 | 50 | 1520 | 75 | kW | 3.76
68 | 54 | 1520 | 57 | MBh | 30.5
68 | 54 | 1520 | 57 | S/T | 0.81
68 | 54 | 1520 | 57 | ∆T | 15
68 | 54 | 1520 | 57 | LDB | 53
68 | 54 | 1520 | 57 | LWB | 49.4
68 | 54 | 1520 | 57 | kW | 1.78
72 | 54 | 1520 | 61 | MBh | 37.1
72 | 54 | 1520 | 61 | S/T | 0.763
72 | 54 | 1520 | 61 | ∆T | 17.2
72 | 54 | 1520 | 61 | LDB | 54.8
72 | 54 | 1520 | 61 | LWB | 52.4
72 | 54 | 1520 | 61 | kW | 2.2
77 | 54 | 1520 | 64 | MBh | 42
77 | 54 | 1520 | 64 | S/T | 0.729
77 | 54 | 1520 | 64 | ∆T | 18.6
77 | 54 | 1520 | 64 | LDB | 58.4
77 | 54 | 1520 | 64 | LWB | 54.8
77 | 54 | 1520 | 64 | kW | 2.54
80 | 54 | 1520 | 67 | MBh | 47
80 | 54 | 1520 | 67 | S/T | 0.681
80 | 54 | 1520 | 67 | ∆T | 19.5
80 | 54 | 1520 | 67 | LDB | 60.5
80 | 54 | 1520 | 67 | LWB | 57.3
80 | 54 | 1520 | 67 | kW | 2.88
84 | 54 | 1520 | 70 | MBh | 52
84 | 54 | 1520 | 70 | S/T | 0.65
84 | 54 | 1520 | 70 | ∆T | 20.6
84 | 54 | 1520 | 70 | LDB | 63.4
84 | 54 | 1520 | 70 | LWB | 59.9
84 | 54 | 1520 | 70 | kW | 3.24
86 | 54 | 1520 | 72 | MBh | 55.3
86 | 54 | 1520 | 72 | S/T | 0.642
86 | 54 | 1520 | 72 | ∆T | 21.6
86 | 54 | 1520 | 72 | LDB | 64.4
86 | 54 | 1520 | 72 | LWB | 61.7
86 | 54 | 1520 | 72 | kW | 3.48
90 | 54 | 1520 | 75 | MBh | 60.2
90 | 54 | 1520 | 75 | S/T | 0.61
90 | 54 | 1520 | 75 | ∆T | 22.4
90 | 54 | 1520 | 75 | LDB | 67.6
90 | 54 | 1520 | 75 | LWB | 64.5
90 | 54 | 1520 | 75 | kW | 3.84
68 | 58 | 1520 | 57 | MBh | 30.5
68 | 58 | 1520 | 57 | S/T | 0.81
68 | 58 | 1520 | 57 | ∆T | 15
68 | 58 | 1520 | 57 | LDB | 53
68 | 58 | 1520 | 57 | LWB | 49.4
68 | 58 | 1520 | 57 | kW | 1.81
72 | 58 | 1520 | 61 | MBh | 37.1
72 | 58 | 1520 | 61 | S/T | 0.763
72 | 58 | 1520 | 61 | ∆T | 17.2
72 | 58 | 1520 | 61 | LDB | 54.8
72 | 58 | 1520 | 61 | LWB | 52.4
72 | 58 | 1520 | 61 | kW | 2.25
77 | 58 | 1520 | 64 | MBh | 42
77 | 58 | 1520 | 64 | S/T | 0.729
77 | 58 | 1520 | 64 | ∆T | 18.6
77 | 58 | 1520 | 64 | LDB | 58.4
77 | 58 | 1520 | 64 | LWB | 54.8
77 | 58 | 1520 | 64 | kW | 2.59
80 | 58 | 1520 | 67 | MBh | 47
80 | 58 | 1520 | 67 | S/T | 0.681
80 | 58 | 1520 | 67 | ∆T | 19.5
80 | 58 | 1520 | 67 | LDB | 60.5
80 | 58 | 1520 | 67 | LWB | 57.3
80 | 58 | 1520 | 67 | kW | 2.95
84 | 58 | 1520 | 70 | MBh | 52
84 | 58 | 1520 | 70 | S/T | 0.65
84 | 58 | 1520 | 70 | ∆T | 20.6
84 | 58 | 1520 | 70 | LDB | 63.4
84 | 58 | 1520 | 70 | LWB | 59.9
84 | 58 | 1520 | 70 | kW | 3.31
86 | 58 | 1520 | 72 | MBh | 55.3
86 | 58 | 1520 | 72 | S/T | 0.642
86 | 58 | 1520 | 72 | ∆T | 21.6
86 | 58 | 1520 | 72 | LDB | 64.4
86 | 58 | 1520 | 72 | LWB | 61.7
86 | 58 | 1520 | 72 | kW | 3.55
90 | 58 | 1520 | 75 | MBh | 59.6
90 | 58 | 1520 | 75 | S/T | 0.609
90 | 58 | 1520 | 75 | ∆T | 22.1
90 | 58 | 1520 | 75 | LDB | 67.9
90 | 58 | 1520 | 75 | LWB | 64.6
90 | 58 | 1520 | 75 | kW | 3.85
68 | 62 | 1520 | 57 | MBh | 30.5
68 | 62 | 1520 | 57 | S/T | 0.81
68 | 62 | 1520 | 57 | ∆T | 15
68 | 62 | 1520 | 57 | LDB | 53
68 | 62 | 1520 | 57 | LWB | 49.4
68 | 62 | 1520 | 57 | kW | 1.85
72 | 62 | 1520 | 61 | MBh | 37.1
72 | 62 | 1520 | 61 | S/T | 0.763
72 | 62 | 1520 | 61 | ∆T | 17.2
72 | 62 | 1520 | 61 | LDB | 54.8
72 | 62 | 1520 | 61 | LWB | 52.4
72 | 62 | 1520 | 61 | kW | 2.3
77 | 62 | 1520 | 64 | MBh | 42
77 | 62 | 1520 | 64 | S/T | 0.729
77 | 62 | 1520 | 64 | ∆T | 18.6
77 | 62 | 1520 | 64 | LDB | 58.4
77 | 62 | 1520 | 64 | LWB | 54.8
77 | 62 | 1520 | 64 | kW | 2.65
80 | 62 | 1520 | 67 | MBh | 47
80 | 62 | 1520 | 67 | S/T | 0.681
80 | 62 | 1520 | 67 | ∆T | 19.5
80 | 62 | 1520 | 67 | LDB | 60.5
80 | 62 | 1520 | 67 | LWB | 57.3
80 | 62 | 1520 | 67 | kW | 3.01
84 | 62 | 1520 | 70 | MBh | 52
84 | 62 | 1520 | 70 | S/T | 0.65
84 | 62 | 1520 | 70 | ∆T | 20.6
84 | 62 | 1520 | 70 | LDB | 63.4
84 | 62 | 1520 | 70 | LWB | 59.9
84 | 62 | 1520 | 70 | kW | 3.38
86 | 62 | 1520 | 72 | MBh | 55.3
86 | 62 | 1520 | 72 | S/T | 0.642
86 | 62 | 1520 | 72 | ∆T | 21.6
86 | 62 | 1520 | 72 | LDB | 64.4
86 | 62 | 1520 | 72 | LWB | 61.7
86 | 62 | 1520 | 72 | kW | 3.63
90 | 62 | 1520 | 75 | MBh | 58.8
90 | 62 | 1520 | 75 | S/T | 0.609
90 | 62 | 1520 | 75 | ∆T | 21.8
90 | 62 | 1520 | 75 | LDB | 68.2
90 | 62 | 1520 | 75 | LWB | 64.7
90 | 62 | 1520 | 75 | kW | 3.94
68 | 66 | 1520 | 57 | MBh | 30.5
68 | 66 | 1520 | 57 | S/T | 0.81
68 | 66 | 1520 | 57 | ∆T | 15
68 | 66 | 1520 | 57 | LDB | 53
68 | 66 | 1520 | 57 | LWB | 49.4
68 | 66 | 1520 | 57 | kW | 1.89
72 | 66 | 1520 | 61 | MBh | 37.1
72 | 66 | 1520 | 61 | S/T | 0.763
72 | 66 | 1520 | 61 | ∆T | 17.2
72 | 66 | 1520 | 61 | LDB | 54.8
72 | 66 | 1520 | 61 | LWB | 52.4
72 | 66 | 1520 | 61 | kW | 2.35
77 | 66 | 1520 | 64 | MBh | 42
77 | 66 | 1520 | 64 | S/T | 0.729
77 | 66 | 1520 | 64 | ∆T | 18.6
77 | 66 | 1520 | 64 | LDB | 58.4
77 | 66 | 1520 | 64 | LWB | 54.8
77 | 66 | 1520 | 64 | kW | 2.71
80 | 66 | 1520 | 67 | MBh | 47
80 | 66 | 1520 | 67 | S/T | 0.681
80 | 66 | 1520 | 67 | ∆T | 19.5
80 | 66 | 1520 | 67 | LDB | 60.5
80 | 66 | 1520 | 67 | LWB | 57.3
80 | 66 | 1520 | 67 | kW | 3.08
84 | 66 | 1520 | 70 | MBh | 52
84 | 66 | 1520 | 70 | S/T | 0.65
84 | 66 | 1520 | 70 | ∆T | 20.6
84 | 66 | 1520 | 70 | LDB | 63.4
84 | 66 | 1520 | 70 | LWB | 59.9
84 | 66 | 1520 | 70 | kW | 3.57
86 | 66 | 1520 | 72 | MBh | 55.3
86 | 66 | 1520 | 72 | S/T | 0.644
86 | 66 | 1520 | 72 | ∆T | 21.7
86 | 66 | 1520 | 72 | LDB | 64.3
86 | 66 | 1520 | 72 | LWB | 61.7
86 | 66 | 1520 | 72 | kW | 3.92
90 | 66 | 1520 | 75 | MBh | 57.9
90 | 66 | 1520 | 75 | S/T | 0.61
90 | 66 | 1520 | 75 | ∆T | 21.5
90 | 66 | 1520 | 75 | LDB | 68.5
90 | 66 | 1520 | 75 | LWB | 64.9
90 | 66 | 1520 | 75 | kW | 4.16
68 | 70 | 1520 | 57 | MBh | 30.5
68 | 70 | 1520 | 57 | S/T | 0.81
68 | 70 | 1520 | 57 | ∆T | 15
68 | 70 | 1520 | 57 | LDB | 53
68 | 70 | 1520 | 57 | LWB | 49.4
68 | 70 | 1520 | 57 | kW | 1.93
72 | 70 | 1520 | 61 | MBh | 37.1
72 | 70 | 1520 | 61 | S/T | 0.763
72 | 70 | 1520 | 61 | ∆T | 17.2
72 | 70 | 1520 | 61 | LDB | 54.8
72 | 70 | 1520 | 61 | LWB | 52.4
72 | 70 | 1520 | 61 | kW | 2.4
77 | 70 | 1520 | 64 | MBh | 42
77 | 70 | 1520 | 64 | S/T | 0.729
77 | 70 | 1520 | 64 | ∆T | 18.6
77 | 70 | 1520 | 64 | LDB | 58.4
77 | 70 | 1520 | 64 | LWB | 54.8
77 | 70 | 1520 | 64 | kW | 2.84
80 | 70 | 1520 | 67 | MBh | 47
80 | 70 | 1520 | 67 | S/T | 0.681
80 | 70 | 1520 | 67 | ∆T | 19.5
80 | 70 | 1520 | 67 | LDB | 60.5
80 | 70 | 1520 | 67 | LWB | 57.3
80 | 70 | 1520 | 67 | kW | 3.33
84 | 70 | 1520 | 70 | MBh | 52
84 | 70 | 1520 | 70 | S/T | 0.652
84 | 70 | 1520 | 70 | ∆T | 20.7
84 | 70 | 1520 | 70 | LDB | 63.3
84 | 70 | 1520 | 70 | LWB | 59.9
84 | 70 | 1520 | 70 | kW | 3.86
86 | 70 | 1520 | 72 | MBh | 55.3
86 | 70 | 1520 | 72 | S/T | 0.644
86 | 70 | 1520 | 72 | ∆T | 21.7
86 | 70 | 1520 | 72 | LDB | 64.3
86 | 70 | 1520 | 72 | LWB | 61.7
86 | 70 | 1520 | 72 | kW | 4.24
90 | 70 | 1520 | 75 | MBh | 57
90 | 70 | 1520 | 75 | S/T | 0.611
90 | 70 | 1520 | 75 | ∆T | 21.2
90 | 70 | 1520 | 75 | LDB | 68.8
90 | 70 | 1520 | 75 | LWB | 65.1
90 | 70 | 1520 | 75 | kW | 4.38
68 | 72 | 1520 | 57 | MBh | 30.5
68 | 72 | 1520 | 57 | S/T | 0.81
68 | 72 | 1520 | 57 | ∆T | 15
68 | 72 | 1520 | 57 | LDB | 53
68 | 72 | 1520 | 57 | LWB | 49.4
68 | 72 | 1520 | 57 | kW | 1.95
72 | 72 | 1520 | 61 | MBh | 37.1
72 | 72 | 1520 | 61 | S/T | 0.763
72 | 72 | 1520 | 61 | ∆T | 17.2
72 | 72 | 1520 | 61 | LDB | 54.8
72 | 72 | 1520 | 61 | LWB | 52.4
72 | 72 | 1520 | 61 | kW | 2.48
77 | 72 | 1520 | 64 | MBh | 42
77 | 72 | 1520 | 64 | S/T | 0.731
77 | 72 | 1520 | 64 | ∆T | 18.7
77 | 72 | 1520 | 64 | LDB | 58.3
77 | 72 | 1520 | 64 | LWB | 54.8
77 | 72 | 1520 | 64 | kW | 2.95
80 | 72 | 1520 | 67 | MBh | 47
80 | 72 | 1520 | 67 | S/T | 0.681
80 | 72 | 1520 | 67 | ∆T | 19.5
80 | 72 | 1520 | 67 | LDB | 60.5
80 | 72 | 1520 | 67 | LWB | 57.3
80 | 72 | 1520 | 67 | kW | 3.46
84 | 72 | 1520 | 70 | MBh | 52
84 | 72 | 1520 | 70 | S/T | 0.652
84 | 72 | 1520 | 70 | ∆T | 20.7
84 | 72 | 1520 | 70 | LDB | 63.3
84 | 72 | 1520 | 70 | LWB | 59.9
84 | 72 | 1520 | 70 | kW | 4.02
86 | 72 | 1520 | 72 | MBh | 55.3
86 | 72 | 1520 | 72 | S/T | 0.644
86 | 72 | 1520 | 72 | ∆T | 21.7
86 | 72 | 1520 | 72 | LDB | 64.3
86 | 72 | 1520 | 72 | LWB | 61.7
86 | 72 | 1520 | 72 | kW | 4.41
90 | 72 | 1520 | 75 | MBh | 56.6
90 | 72 | 1520 | 75 | S/T | 0.61
90 | 72 | 1520 | 75 | ∆T | 21
90 | 72 | 1520 | 75 | LDB | 69
90 | 72 | 1520 | 75 | LWB | 65.2
90 | 72 | 1520 | 75 | kW | 4.49
68 | 75 | 1520 | 57 | MBh | 30.5
68 | 75 | 1520 | 57 | S/T | 0.81
68 | 75 | 1520 | 57 | ∆T | 15
68 | 75 | 1520 | 57 | LDB | 53
68 | 75 | 1520 | 57 | LWB | 49.4
68 | 75 | 1520 | 57 | kW | 2.02
72 | 75 | 1520 | 61 | MBh | 37.1
72 | 75 | 1520 | 61 | S/T | 0.763
72 | 75 | 1520 | 61 | ∆T | 17.2
72 | 75 | 1520 | 61 | LDB | 54.8
72 | 75 | 1520 | 61 | LWB | 52.4
72 | 75 | 1520 | 61 | kW | 2.62
77 | 75 | 1520 | 64 | MBh | 42
77 | 75 | 1520 | 64 | S/T | 0.731
77 | 75 | 1520 | 64 | ∆T | 18.7
77 | 75 | 1520 | 64 | LDB | 58.3
77 | 75 | 1520 | 64 | LWB | 54.8
77 | 75 | 1520 | 64 | kW | 3.12
80 | 75 | 1520 | 67 | MBh | 47
80 | 75 | 1520 | 67 | S/T | 0.681
80 | 75 | 1520 | 67 | ∆T | 19.5
80 | 75 | 1520 | 67 | LDB | 60.5
80 | 75 | 1520 | 67 | LWB | 57.3
80 | 75 | 1520 | 67 | kW | 3.66
84 | 75 | 1520 | 70 | MBh | 52
84 | 75 | 1520 | 70 | S/T | 0.652
84 | 75 | 1520 | 70 | ∆T | 20.7
84 | 75 | 1520 | 70 | LDB | 63.3
84 | 75 | 1520 | 70 | LWB | 59.9
84 | 75 | 1520 | 70 | kW | 4.26
86 | 75 | 1520 | 72 | MBh | 54.9
86 | 75 | 1520 | 72 | S/T | 0.645
86 | 75 | 1520 | 72 | ∆T | 21.6
86 | 75 | 1520 | 72 | LDB | 64.4
86 | 75 | 1520 | 72 | LWB | 61.7
86 | 75 | 1520 | 72 | kW | 4.62
90 | 75 | 1520 | 75 | MBh | 55.9
90 | 75 | 1520 | 75 | S/T | 0.61
90 | 75 | 1520 | 75 | ∆T | 20.8
90 | 75 | 1520 | 75 | LDB | 69.2
90 | 75 | 1520 | 75 | LWB | 65.3
90 | 75 | 1520 | 75 | kW | 4.65
68 | 79 | 1520 | 57 | MBh | 30.5
68 | 79 | 1520 | 57 | S/T | 0.81
68 | 79 | 1520 | 57 | ∆T | 15
68 | 79 | 1520 | 57 | LDB | 53
68 | 79 | 1520 | 57 | LWB | 49.4
68 | 79 | 1520 | 57 | kW | 2.17
72 | 79 | 1520 | 61 | MBh | 37.1
72 | 79 | 1520 | 61 | S/T | 0.763
72 | 79 | 1520 | 61 | ∆T | 17.2
72 | 79 | 1520 | 61 | LDB | 54.8
72 | 79 | 1520 | 61 | LWB | 52.4
72 | 79 | 1520 | 61 | kW | 2.82
77 | 79 | 1520 | 64 | MBh | 42
77 | 79 | 1520 | 64 | S/T | 0.731
77 | 79 | 1520 | 64 | ∆T | 18.7
77 | 79 | 1520 | 64 | LDB | 58.3
77 | 79 | 1520 | 64 | LWB | 54.8
77 | 79 | 1520 | 64 | kW | 3.36
80 | 79 | 1520 | 67 | MBh | 47
80 | 79 | 1520 | 67 | S/T | 0.681
80 | 79 | 1520 | 67 | ∆T | 19.5
80 | 79 | 1520 | 67 | LDB | 60.5
80 | 79 | 1520 | 67 | LWB | 57.3
80 | 79 | 1520 | 67 | kW | 3.95
84 | 79 | 1520 | 70 | MBh | 52
84 | 79 | 1520 | 70 | S/T | 0.652
84 | 79 | 1520 | 70 | ∆T | 20.7
84 | 79 | 1520 | 70 | LDB | 63.3
84 | 79 | 1520 | 70 | LWB | 59.9
84 | 79 | 1520 | 70 | kW | 4.59
86 | 79 | 1520 | 72 | MBh | 54
86 | 79 | 1520 | 72 | S/T | 0.644
86 | 79 | 1520 | 72 | ∆T | 21.2
86 | 79 | 1520 | 72 | LDB | 64.8
86 | 79 | 1520 | 72 | LWB | 61.9
86 | 79 | 1520 | 72 | kW | 4.84
90 | 79 | 1520 | 75 | MBh | 55
90 | 79 | 1520 | 75 | S/T | 0.611
90 | 79 | 1520 | 75 | ∆T | 20.5
90 | 79 | 1520 | 75 | LDB | 69.5
90 | 79 | 1520 | 75 | LWB | 65.5
90 | 79 | 1520 | 75 | kW | 4.88
68 | 83 | 1520 | 57 | MBh | 30.5
68 | 83 | 1520 | 57 | S/T | 0.81
68 | 83 | 1520 | 57 | ∆T | 15
68 | 83 | 1520 | 57 | LDB | 53
68 | 83 | 1520 | 57 | LWB | 49.4
68 | 83 | 1520 | 57 | kW | 2.33
72 | 83 | 1520 | 61 | MBh | 37.1
72 | 83 | 1520 | 61 | S/T | 0.763
72 | 83 | 1520 | 61 | ∆T | 17.2
72 | 83 | 1520 | 61 | LDB | 54.8
72 | 83 | 1520 | 61 | LWB | 52.4
72 | 83 | 1520 | 61 | kW | 3.03
77 | 83 | 1520 | 64 | MBh | 42
77 | 83 | 1520 | 64 | S/T | 0.731
77 | 83 | 1520 | 64 | ∆T | 18.7
77 | 83 | 1520 | 64 | LDB | 58.3
77 | 83 | 1520 | 64 | LWB | 54.8
77 | 83 | 1520 | 64 | kW | 3.61
80 | 83 | 1520 | 67 | MBh | 47
80 | 83 | 1520 | 67 | S/T | 0.681
80 | 83 | 1520 | 67 | ∆T | 19.5
80 | 83 | 1520 | 67 | LDB | 60.5
80 | 83 | 1520 | 67 | LWB | 57.3
80 | 83 | 1520 | 67 | kW | 4.25
84 | 83 | 1520 | 70 | MBh | 52
84 | 83 | 1520 | 70 | S/T | 0.652
84 | 83 | 1520 | 70 | ∆T | 20.7
84 | 83 | 1520 | 70 | LDB | 63.3
84 | 83 | 1520 | 70 | LWB | 59.9
84 | 83 | 1520 | 70 | kW | 4.95
86 | 83 | 1520 | 72 | MBh | 53.2
86 | 83 | 1520 | 72 | S/T | 0.645
86 | 83 | 1520 | 72 | ∆T | 20.9
86 | 83 | 1520 | 72 | LDB | 65.1
86 | 83 | 1520 | 72 | LWB | 62.1
86 | 83 | 1520 | 72 | kW | 5.07
90 | 83 | 1520 | 75 | MBh | 54.1
90 | 83 | 1520 | 75 | S/T | 0.61
90 | 83 | 1520 | 75 | ∆T | 20.1
90 | 83 | 1520 | 75 | LDB | 69.9
90 | 83 | 1520 | 75 | LWB | 65.6
90 | 83 | 1520 | 75 | kW | 5.1
68 | 87 | 1520 | 57 | MBh | 30.5
68 | 87 | 1520 | 57 | S/T | 0.81
68 | 87 | 1520 | 57 | ∆T | 15
68 | 87 | 1520 | 57 | LDB | 53
68 | 87 | 1520 | 57 | LWB | 49.4
68 | 87 | 1520 | 57 | kW | 2.49
72 | 87 | 1520 | 61 | MBh | 37.1
72 | 87 | 1520 | 61 | S/T | 0.763
72 | 87 | 1520 | 61 | ∆T | 17.2
72 | 87 | 1520 | 61 | LDB | 54.8
72 | 87 | 1520 | 61 | LWB | 52.4
72 | 87 | 1520 | 61 | kW | 3.25
77 | 87 | 1520 | 64 | MBh | 42
77 | 87 | 1520 | 64 | S/T | 0.731
77 | 87 | 1520 | 64 | ∆T | 18.7
77 | 87 | 1520 | 64 | LDB | 58.3
77 | 87 | 1520 | 64 | LWB | 54.8
77 | 87 | 1520 | 64 | kW | 3.88
80 | 87 | 1520 | 67 | MBh | 47
80 | 87 | 1520 | 67 | S/T | 0.681
80 | 87 | 1520 | 67 | ∆T | 19.5
80 | 87 | 1520 | 67 | LDB | 60.5
80 | 87 | 1520 | 67 | LWB | 57.3
80 | 87 | 1520 | 67 | kW | 4.57
84 | 87 | 1520 | 70 | MBh | 51.6
84 | 87 | 1520 | 70 | S/T | 0.653
84 | 87 | 1520 | 70 | ∆T | 20.5
84 | 87 | 1520 | 70 | LDB | 63.5
84 | 87 | 1520 | 70 | LWB | 59.9
84 | 87 | 1520 | 70 | kW | 5.26
86 | 87 | 1520 | 72 | MBh | 52.3
86 | 87 | 1520 | 72 | S/T | 0.644
86 | 87 | 1520 | 72 | ∆T | 20.5
86 | 87 | 1520 | 72 | LDB | 65.5
86 | 87 | 1520 | 72 | LWB | 62.3
86 | 87 | 1520 | 72 | kW | 5.29
90 | 87 | 1520 | 75 | MBh | 53.2
90 | 87 | 1520 | 75 | S/T | 0.611
90 | 87 | 1520 | 75 | ∆T | 19.8
90 | 87 | 1520 | 75 | LDB | 70.2
90 | 87 | 1520 | 75 | LWB | 65.8
90 | 87 | 1520 | 75 | kW | 5.32
68 | 91 | 1520 | 57 | MBh | 30.5
68 | 91 | 1520 | 57 | S/T | 0.81
68 | 91 | 1520 | 57 | ∆T | 15
68 | 91 | 1520 | 57 | LDB | 53
68 | 91 | 1520 | 57 | LWB | 49.4
68 | 91 | 1520 | 57 | kW | 2.67
72 | 91 | 1520 | 61 | MBh | 37.1
72 | 91 | 1520 | 61 | S/T | 0.763
72 | 91 | 1520 | 61 | ∆T | 17.2
72 | 91 | 1520 | 61 | LDB | 54.8
72 | 91 | 1520 | 61 | LWB | 52.4
72 | 91 | 1520 | 61 | kW | 3.48
77 | 91 | 1520 | 64 | MBh | 42
77 | 91 | 1520 | 64 | S/T | 0.731
77 | 91 | 1520 | 64 | ∆T | 18.7
77 | 91 | 1520 | 64 | LDB | 58.3
77 | 91 | 1520 | 64 | LWB | 54.8
77 | 91 | 1520 | 64 | kW | 4.17
80 | 91 | 1520 | 67 | MBh | 47
80 | 91 | 1520 | 67 | S/T | 0.681
80 | 91 | 1520 | 67 | ∆T | 19.5
80 | 91 | 1520 | 67 | LDB | 60.5
80 | 91 | 1520 | 67 | LWB | 57.3
80 | 91 | 1520 | 67 | kW | 4.92
84 | 91 | 1520 | 70 | MBh | 50.7
84 | 91 | 1520 | 70 | S/T | 0.653
84 | 91 | 1520 | 70 | ∆T | 20.2
84 | 91 | 1520 | 70 | LDB | 63.8
84 | 91 | 1520 | 70 | LWB | 60.1
84 | 91 | 1520 | 70 | kW | 5.49
86 | 91 | 1520 | 72 | MBh | 51.4
86 | 91 | 1520 | 72 | S/T | 0.644
86 | 91 | 1520 | 72 | ∆T | 20.2
86 | 91 | 1520 | 72 | LDB | 65.8
86 | 91 | 1520 | 72 | LWB | 62.5
86 | 91 | 1520 | 72 | kW | 5.51
90 | 91 | 1520 | 75 | MBh | 52.4
90 | 91 | 1520 | 75 | S/T | 0.609
90 | 91 | 1520 | 75 | ∆T | 19.4
90 | 91 | 1520 | 75 | LDB | 70.6
90 | 91 | 1520 | 75 | LWB | 66
90 | 91 | 1520 | 75 | kW | 5.55
68 | 93 | 1520 | 57 | MBh | 30.5
68 | 93 | 1520 | 57 | S/T | 0.81
68 | 93 | 1520 | 57 | ∆T | 15
68 | 93 | 1520 | 57 | LDB | 53
68 | 93 | 1520 | 57 | LWB | 49.4
68 | 93 | 1520 | 57 | kW | 2.76
72 | 93 | 1520 | 61 | MBh | 37.1
72 | 93 | 1520 | 61 | S/T | 0.763
72 | 93 | 1520 | 61 | ∆T | 17.2
72 | 93 | 1520 | 61 | LDB | 54.8
72 | 93 | 1520 | 61 | LWB | 52.4
72 | 93 | 1520 | 61 | kW | 3.61
77 | 93 | 1520 | 64 | MBh | 42
77 | 93 | 1520 | 64 | S/T | 0.729
77 | 93 | 1520 | 64 | ∆T | 18.6
77 | 93 | 1520 | 64 | LDB | 58.4
77 | 93 | 1520 | 64 | LWB | 54.8
77 | 93 | 1520 | 64 | kW | 4.32
80 | 93 | 1520 | 67 | MBh | 47
80 | 93 | 1520 | 67 | S/T | 0.681
80 | 93 | 1520 | 67 | ∆T | 19.5
80 | 93 | 1520 | 67 | LDB | 60.5
80 | 93 | 1520 | 67 | LWB | 57.3
80 | 93 | 1520 | 67 | kW | 5.1
84 | 93 | 1520 | 70 | MBh | 50.3
84 | 93 | 1520 | 70 | S/T | 0.652
84 | 93 | 1520 | 70 | ∆T | 20
84 | 93 | 1520 | 70 | LDB | 64
84 | 93 | 1520 | 70 | LWB | 60.2
84 | 93 | 1520 | 70 | kW | 5.6
86 | 93 | 1520 | 72 | MBh | 51
86 | 93 | 1520 | 72 | S/T | 0.643
86 | 93 | 1520 | 72 | ∆T | 20
86 | 93 | 1520 | 72 | LDB | 66
86 | 93 | 1520 | 72 | LWB | 62.5
86 | 93 | 1520 | 72 | kW | 5.62
90 | 93 | 1520 | 75 | MBh | 51.9
90 | 93 | 1520 | 75 | S/T | 0.611
90 | 93 | 1520 | 75 | ∆T | 19.3
90 | 93 | 1520 | 75 | LDB | 70.7
90 | 93 | 1520 | 75 | LWB | 66.1
90 | 93 | 1520 | 75 | kW | 5.66
68 | 95 | 1520 | 57 | MBh | 30.5
68 | 95 | 1520 | 57 | S/T | 0.81
68 | 95 | 1520 | 57 | ∆T | 15
68 | 95 | 1520 | 57 | LDB | 53
68 | 95 | 1520 | 57 | LWB | 49.4
68 | 95 | 1520 | 57 | kW | 2.85
72 | 95 | 1520 | 61 | MBh | 37.1
72 | 95 | 1520 | 61 | S/T | 0.763
72 | 95 | 1520 | 61 | ∆T | 17.2
72 | 95 | 1520 | 61 | LDB | 54.8
72 | 95 | 1520 | 61 | LWB | 52.4
72 | 95 | 1520 | 61 | kW | 3.73
77 | 95 | 1520 | 64 | MBh | 42
77 | 95 | 1520 | 64 | S/T | 0.729
77 | 95 | 1520 | 64 | ∆T | 18.6
77 | 95 | 1520 | 64 | LDB | 58.4
77 | 95 | 1520 | 64 | LWB | 54.8
77 | 95 | 1520 | 64 | kW | 4.47
80 | 95 | 1520 | 67 | MBh | 47
80 | 95 | 1520 | 67 | S/T | 0.681
80 | 95 | 1520 | 67 | ∆T | 19.5
80 | 95 | 1520 | 67 | LDB | 60.5
80 | 95 | 1520 | 67 | LWB | 57.3
80 | 95 | 1520 | 67 | kW | 5.28
84 | 95 | 1520 | 70 | MBh | 49.9
84 | 95 | 1520 | 70 | S/T | 0.651
84 | 95 | 1520 | 70 | ∆T | 19.8
84 | 95 | 1520 | 70 | LDB | 64.2
84 | 95 | 1520 | 70 | LWB | 60.3
84 | 95 | 1520 | 70 | kW | 5.71
86 | 95 | 1520 | 72 | MBh | 50.5
86 | 95 | 1520 | 72 | S/T | 0.644
86 | 95 | 1520 | 72 | ∆T | 19.8
86 | 95 | 1520 | 72 | LDB | 66.2
86 | 95 | 1520 | 72 | LWB | 62.7
86 | 95 | 1520 | 72 | kW | 5.74
90 | 95 | 1520 | 75 | MBh | 51.5
90 | 95 | 1520 | 75 | S/T | 0.61
90 | 95 | 1520 | 75 | ∆T | 19.1
90 | 95 | 1520 | 75 | LDB | 70.9
90 | 95 | 1520 | 75 | LWB | 66.1
90 | 95 | 1520 | 75 | kW | 5.78
68 | 99 | 1520 | 57 | MBh | 30.5
68 | 99 | 1520 | 57 | S/T | 0.81
68 | 99 | 1520 | 57 | ∆T | 15
68 | 99 | 1520 | 57 | LDB | 53
68 | 99 | 1520 | 57 | LWB | 49.4
68 | 99 | 1520 | 57 | kW | 3.05
72 | 99 | 1520 | 61 | MBh | 37.1
72 | 99 | 1520 | 61 | S/T | 0.763
72 | 99 | 1520 | 61 | ∆T | 17.2
72 | 99 | 1520 | 61 | LDB | 54.8
72 | 99 | 1520 | 61 | LWB | 52.4
72 | 99 | 1520 | 61 | kW | 4
77 | 99 | 1520 | 64 | MBh | 42
77 | 99 | 1520 | 64 | S/T | 0.729
77 | 99 | 1520 | 64 | ∆T | 18.6
77 | 99 | 1520 | 64 | LDB | 58.4
77 | 99 | 1520 | 64 | LWB | 54.8
77 | 99 | 1520 | 64 | kW | 4.8
80 | 99 | 1520 | 67 | MBh | 47
80 | 99 | 1520 | 67 | S/T | 0.681
80 | 99 | 1520 | 67 | ∆T | 19.5
80 | 99 | 1520 | 67 | LDB | 60.5
80 | 99 | 1520 | 67 | LWB | 57.3
80 | 99 | 1520 | 67 | kW | 5.67
84 | 99 | 1520 | 70 | MBh | 49
84 | 99 | 1520 | 70 | S/T | 0.653
84 | 99 | 1520 | 70 | ∆T | 19.5
84 | 99 | 1520 | 70 | LDB | 64.5
84 | 99 | 1520 | 70 | LWB | 60.5
84 | 99 | 1520 | 70 | kW | 5.93
86 | 99 | 1520 | 72 | MBh | 49.6
86 | 99 | 1520 | 72 | S/T | 0.647
86 | 99 | 1520 | 72 | ∆T | 19.6
86 | 99 | 1520 | 72 | LDB | 66.4
86 | 99 | 1520 | 72 | LWB | 62.8
86 | 99 | 1520 | 72 | kW | 5.96
90 | 99 | 1520 | 75 | MBh | 50
90 | 99 | 1520 | 75 | S/T | 0.612
90 | 99 | 1520 | 75 | ∆T | 18.6
90 | 99 | 1520 | 75 | LDB | 71.4
90 | 99 | 1520 | 75 | LWB | 66.4
90 | 99 | 1520 | 75 | kW | 5.98
68 | 103 | 1520 | 57 | MBh | 30.5
68 | 103 | 1520 | 57 | S/T | 0.81
68 | 103 | 1520 | 57 | ∆T | 15
68 | 103 | 1520 | 57 | LDB | 53
68 | 103 | 1520 | 57 | LWB | 49.4
68 | 103 | 1520 | 57 | kW | 3.26
72 | 103 | 1520 | 61 | MBh | 37.1
72 | 103 | 1520 | 61 | S/T | 0.763
72 | 103 | 1520 | 61 | ∆T | 17.2
72 | 103 | 1520 | 61 | LDB | 54.8
72 | 103 | 1520 | 61 | LWB | 52.4
72 | 103 | 1520 | 61 | kW | 4.28
77 | 103 | 1520 | 64 | MBh | 42
77 | 103 | 1520 | 64 | S/T | 0.729
77 | 103 | 1520 | 64 | ∆T | 18.6
77 | 103 | 1520 | 64 | LDB | 58.4
77 | 103 | 1520 | 64 | LWB | 54.8
77 | 103 | 1520 | 64 | kW | 5.14
80 | 103 | 1520 | 67 | MBh | 47
80 | 103 | 1520 | 67 | S/T | 0.681
80 | 103 | 1520 | 67 | ∆T | 19.5
80 | 103 | 1520 | 67 | LDB | 60.5
80 | 103 | 1520 | 67 | LWB | 57.3
80 | 103 | 1520 | 67 | kW | 6.08
84 | 103 | 1520 | 70 | MBh | 47.9
84 | 103 | 1520 | 70 | S/T | 0.653
84 | 103 | 1520 | 70 | ∆T | 19.1
84 | 103 | 1520 | 70 | LDB | 64.9
84 | 103 | 1520 | 70 | LWB | 60.7
84 | 103 | 1520 | 70 | kW | 6.15
86 | 103 | 1520 | 72 | MBh | 47.9
86 | 103 | 1520 | 72 | S/T | 0.647
86 | 103 | 1520 | 72 | ∆T | 18.9
86 | 103 | 1520 | 72 | LDB | 67.1
86 | 103 | 1520 | 72 | LWB | 63.2
86 | 103 | 1520 | 72 | kW | 6.15
90 | 103 | 1520 | 75 | MBh | 47.9
90 | 103 | 1520 | 75 | S/T | 0.614
90 | 103 | 1520 | 75 | ∆T | 17.9
90 | 103 | 1520 | 75 | LDB | 72.1
90 | 103 | 1520 | 75 | LWB | 66.8
90 | 103 | 1520 | 75 | kW | 6.15
68 | 106 | 1520 | 57 | MBh | 30.5
68 | 106 | 1520 | 57 | S/T | 0.81
68 | 106 | 1520 | 57 | ∆T | 15
68 | 106 | 1520 | 57 | LDB | 53
68 | 106 | 1520 | 57 | LWB | 49.4
68 | 106 | 1520 | 57 | kW | 3.42
72 | 106 | 1520 | 61 | MBh | 37.1
72 | 106 | 1520 | 61 | S/T | 0.763
72 | 106 | 1520 | 61 | ∆T | 17.2
72 | 106 | 1520 | 61 | LDB | 54.8
72 | 106 | 1520 | 61 | LWB | 52.4
72 | 106 | 1520 | 61 | kW | 4.51
77 | 106 | 1520 | 64 | MBh | 42
77 | 106 | 1520 | 64 | S/T | 0.729
77 | 106 | 1520 | 64 | ∆T | 18.6
77 | 106 | 1520 | 64 | LDB | 58.4
77 | 106 | 1520 | 64 | LWB | 54.8
77 | 106 | 1520 | 64 | kW | 5.42
80 | 106 | 1520 | 67 | MBh | 46.3
80 | 106 | 1520 | 67 | S/T | 0.683
80 | 106 | 1520 | 67 | ∆T | 19.2
80 | 106 | 1520 | 67 | LDB | 60.8
80 | 106 | 1520 | 67 | LWB | 57.4
80 | 106 | 1520 | 67 | kW | 6.26
84 | 106 | 1520 | 70 | MBh | 46.3
84 | 106 | 1520 | 70 | S/T | 0.654
84 | 106 | 1520 | 70 | ∆T | 18.5
84 | 106 | 1520 | 70 | LDB | 65.5
84 | 106 | 1520 | 70 | LWB | 61.1
84 | 106 | 1520 | 70 | kW | 6.26
86 | 106 | 1520 | 72 | MBh | 46.3
86 | 106 | 1520 | 72 | S/T | 0.646
86 | 106 | 1520 | 72 | ∆T | 18.2
86 | 106 | 1520 | 72 | LDB | 67.8
86 | 106 | 1520 | 72 | LWB | 63.5
86 | 106 | 1520 | 72 | kW | 6.26
90 | 106 | 1520 | 75 | MBh | 46.3
90 | 106 | 1520 | 75 | S/T | 0.613
90 | 106 | 1520 | 75 | ∆T | 17.3
90 | 106 | 1520 | 75 | LDB | 72.7
90 | 106 | 1520 | 75 | LWB | 67.1
90 | 106 | 1520 | 75 | kW | 6.26
68 | 110 | 1520 | 57 | MBh | 30.5
68 | 110 | 1520 | 57 | S/T | 0.81
68 | 110 | 1520 | 57 | ∆T | 15
68 | 110 | 1520 | 57 | LDB | 53
68 | 110 | 1520 | 57 | LWB | 49.4
68 | 110 | 1520 | 57 | kW | 3.66
72 | 110 | 1520 | 61 | MBh | 37.1
72 | 110 | 1520 | 61 | S/T | 0.763
72 | 110 | 1520 | 61 | ∆T | 17.2
72 | 110 | 1520 | 61 | LDB | 54.8
72 | 110 | 1520 | 61 | LWB | 52.4
72 | 110 | 1520 | 61 | kW | 4.82
77 | 110 | 1520 | 64 | MBh | 40.1
77 | 110 | 1520 | 64 | S/T | 0.731
77 | 110 | 1520 | 64 | ∆T | 17.8
77 | 110 | 1520 | 64 | LDB | 59.2
77 | 110 | 1520 | 64 | LWB | 55.2
77 | 110 | 1520 | 64 | kW | 5.41
80 | 110 | 1520 | 67 | MBh | 40.1
80 | 110 | 1520 | 67 | S/T | 0.683
80 | 110 | 1520 | 67 | ∆T | 16.7
80 | 110 | 1520 | 67 | LDB | 63.3
80 | 110 | 1520 | 67 | LWB | 58.8
80 | 110 | 1520 | 67 | kW | 5.41
84 | 110 | 1520 | 70 | MBh | 40.1
84 | 110 | 1520 | 70 | S/T | 0.656
84 | 110 | 1520 | 70 | ∆T | 16
84 | 110 | 1520 | 70 | LDB | 68
84 | 110 | 1520 | 70 | LWB | 62.4
84 | 110 | 1520 | 70 | kW | 5.41
86 | 110 | 1520 | 72 | MBh | 40.1
86 | 110 | 1520 | 72 | S/T | 0.648
86 | 110 | 1520 | 72 | ∆T | 15.8
86 | 110 | 1520 | 72 | LDB | 70.2
86 | 110 | 1520 | 72 | LWB | 64.7
86 | 110 | 1520 | 72 | kW | 5.41
90 | 110 | 1520 | 75 | MBh | 40.1
90 | 110 | 1520 | 75 | S/T | 0.613
90 | 110 | 1520 | 75 | ∆T | 15
90 | 110 | 1520 | 75 | LDB | 75
90 | 110 | 1520 | 75 | LWB | 68.3
90 | 110 | 1520 | 75 | kW | 5.41
68 | 115 | 1520 | 57 | MBh | 30.5
68 | 115 | 1520 | 57 | S/T | 0.81
68 | 115 | 1520 | 57 | ∆T | 15
68 | 115 | 1520 | 57 | LDB | 53
68 | 115 | 1520 | 57 | LWB | 49.4
68 | 115 | 1520 | 57 | kW | 3.97
72 | 115 | 1520 | 61 | MBh | 32.4
72 | 115 | 1520 | 61 | S/T | 0.765
72 | 115 | 1520 | 61 | ∆T | 15.1
72 | 115 | 1520 | 61 | LDB | 56.9
72 | 115 | 1520 | 61 | LWB | 53.5
72 | 115 | 1520 | 61 | kW | 4.32
77 | 115 | 1520 | 64 | MBh | 32.4
77 | 115 | 1520 | 64 | S/T | 0.731
77 | 115 | 1520 | 64 | ∆T | 14.4
77 | 115 | 1520 | 64 | LDB | 62.6
77 | 115 | 1520 | 64 | LWB | 57
77 | 115 | 1520 | 64 | kW | 4.32
80 | 115 | 1520 | 67 | MBh | 32.4
80 | 115 | 1520 | 67 | S/T | 0.685
80 | 115 | 1520 | 67 | ∆T | 13.5
80 | 115 | 1520 | 67 | LDB | 66.5
80 | 115 | 1520 | 67 | LWB | 60.5
80 | 115 | 1520 | 67 | kW | 4.32
84 | 115 | 1520 | 70 | MBh | 32.4
84 | 115 | 1520 | 70 | S/T | 0.654
84 | 115 | 1520 | 70 | ∆T | 12.9
84 | 115 | 1520 | 70 | LDB | 71.1
84 | 115 | 1520 | 70 | LWB | 63.9
84 | 115 | 1520 | 70 | kW | 4.32
86 | 115 | 1520 | 72 | MBh | 32.4
86 | 115 | 1520 | 72 | S/T | 0.648
86 | 115 | 1520 | 72 | ∆T | 12.8
86 | 115 | 1520 | 72 | LDB | 73.2
86 | 115 | 1520 | 72 | LWB | 66.2
86 | 115 | 1520 | 72 | kW | 4.32
90 | 115 | 1520 | 75 | MBh | 32.4
90 | 115 | 1520 | 75 | S/T | 0.614
90 | 115 | 1520 | 75 | ∆T | 12.1
90 | 115 | 1520 | 75 | LDB | 77.9
90 | 115 | 1520 | 75 | LWB | 69.6
90 | 115 | 1520 | 75 | kW | 4.32
68 | 118 | 1520 | 57 | MBh | 27.7
68 | 118 | 1520 | 57 | S/T | 0.812
68 | 118 | 1520 | 57 | ∆T | 13.7
68 | 118 | 1520 | 57 | LDB | 54.3
68 | 118 | 1520 | 57 | LWB | 50.1
68 | 118 | 1520 | 57 | kW | 3.67
72 | 118 | 1520 | 61 | MBh | 27.7
72 | 118 | 1520 | 61 | S/T | 0.769
72 | 118 | 1520 | 61 | ∆T | 13
72 | 118 | 1520 | 61 | LDB | 59
72 | 118 | 1520 | 61 | LWB | 54.7
72 | 118 | 1520 | 61 | kW | 3.67
77 | 118 | 1520 | 64 | MBh | 27.7
77 | 118 | 1520 | 64 | S/T | 0.733
77 | 118 | 1520 | 64 | ∆T | 12.4
77 | 118 | 1520 | 64 | LDB | 64.6
77 | 118 | 1520 | 64 | LWB | 58.1
77 | 118 | 1520 | 64 | kW | 3.67
80 | 118 | 1520 | 67 | MBh | 27.7
80 | 118 | 1520 | 67 | S/T | 0.686
80 | 118 | 1520 | 67 | ∆T | 11.6
80 | 118 | 1520 | 67 | LDB | 68.4
80 | 118 | 1520 | 67 | LWB | 61.5
80 | 118 | 1520 | 67 | kW | 3.67
84 | 118 | 1520 | 70 | MBh | 27.7
84 | 118 | 1520 | 70 | S/T | 0.657
84 | 118 | 1520 | 70 | ∆T | 11.1
84 | 118 | 1520 | 70 | LDB | 72.9
84 | 118 | 1520 | 70 | LWB | 64.9
84 | 118 | 1520 | 70 | kW | 3.67
86 | 118 | 1520 | 72 | MBh | 27.7
86 | 118 | 1520 | 72 | S/T | 0.65
86 | 118 | 1520 | 72 | ∆T | 11
86 | 118 | 1520 | 72 | LDB | 75
86 | 118 | 1520 | 72 | LWB | 67.1
86 | 118 | 1520 | 72 | kW | 3.67
90 | 118 | 1520 | 75 | MBh | 27.7
90 | 118 | 1520 | 75 | S/T | 0.617
90 | 118 | 1520 | 75 | ∆T | 10.4
90 | 118 | 1520 | 75 | LDB | 79.6
90 | 118 | 1520 | 75 | LWB | 70.4
90 | 118 | 1520 | 75 | kW | 3.67
68 | 122 | 1520 | 57 | MBh | 21.5
68 | 122 | 1520 | 57 | S/T | 0.814
68 | 122 | 1520 | 57 | ∆T | 10.7
68 | 122 | 1520 | 57 | LDB | 57.3
68 | 122 | 1520 | 57 | LWB | 51.7
68 | 122 | 1520 | 57 | kW | 2.82
72 | 122 | 1520 | 61 | MBh | 21.5
72 | 122 | 1520 | 61 | S/T | 0.767
72 | 122 | 1520 | 61 | ∆T | 10.1
72 | 122 | 1520 | 61 | LDB | 61.9
72 | 122 | 1520 | 61 | LWB | 56.2
72 | 122 | 1520 | 61 | kW | 2.82
77 | 122 | 1520 | 64 | MBh | 21.5
77 | 122 | 1520 | 64 | S/T | 0.735
77 | 122 | 1520 | 64 | ∆T | 9.6
77 | 122 | 1520 | 64 | LDB | 67.4
77 | 122 | 1520 | 64 | LWB | 59.5
77 | 122 | 1520 | 64 | kW | 2.82
80 | 122 | 1520 | 67 | MBh | 21.5
80 | 122 | 1520 | 67 | S/T | 0.688
80 | 122 | 1520 | 67 | ∆T | 9
80 | 122 | 1520 | 67 | LDB | 71
80 | 122 | 1520 | 67 | LWB | 62.8
80 | 122 | 1520 | 67 | kW | 2.82
84 | 122 | 1520 | 70 | MBh | 21.5
84 | 122 | 1520 | 70 | S/T | 0.66
84 | 122 | 1520 | 70 | ∆T | 8.7
84 | 122 | 1520 | 70 | LDB | 75.3
84 | 122 | 1520 | 70 | LWB | 66.1
84 | 122 | 1520 | 70 | kW | 2.82
86 | 122 | 1520 | 72 | MBh | 21.5
86 | 122 | 1520 | 72 | S/T | 0.651
86 | 122 | 1520 | 72 | ∆T | 8.5
86 | 122 | 1520 | 72 | LDB | 77.5
86 | 122 | 1520 | 72 | LWB | 68.2
86 | 122 | 1520 | 72 | kW | 2.82
90 | 122 | 1520 | 75 | MBh | 21.5
90 | 122 | 1520 | 75 | S/T | 0.619
90 | 122 | 1520 | 75 | ∆T | 8.1
90 | 122 | 1520 | 75 | LDB | 81.9
90 | 122 | 1520 | 75 | LWB | 71.5
90 | 122 | 1520 | 75 | kW | 2.82

## RZA48AAVJU - FTA48AAVJUA
IDB | OA Ambient | Airflow | IWB | VALUE | RESULT | Ambient DB | Ambient WB | IDB | MBH | kW
68 | 23 | 1520 | 57 | MBh | 30.5 | 64 | 60 | 61 | 66 | 5.44
68 | 23 | 1520 | 57 | S/T | 0.807 | 64 | 60 | 65 | 61.1 | 4.53
68 | 23 | 1520 | 57 | ∆T | 15 | 64 | 60 | 68 | 57.5 | 3.98
68 | 23 | 1520 | 57 | LDB | 53 | 64 | 60 | 70 | 55 | 3.68
68 | 23 | 1520 | 57 | LWB | 49.4 | 64 | 60 | 72 | 52.5 | 3.43
68 | 23 | 1520 | 57 | kW | 1.55 | 64 | 60 | 75 | 48.9 | 3.16
72 | 23 | 1520 | 61 | MBh | 37.1 | 60 | 56 | 61 | 66 | 5.92
72 | 23 | 1520 | 61 | S/T | 0.763 | 60 | 56 | 65 | 61.1 | 4.88
72 | 23 | 1520 | 61 | ∆T | 17.2 | 60 | 56 | 68 | 57.5 | 4.25
72 | 23 | 1520 | 61 | LDB | 54.8 | 60 | 56 | 70 | 55 | 3.9
72 | 23 | 1520 | 61 | LWB | 52.4 | 60 | 56 | 72 | 52.5 | 3.61
72 | 23 | 1520 | 61 | kW | 1.91 | 60 | 56 | 75 | 48.9 | 3.27
77 | 23 | 1520 | 64 | MBh | 42 | 57 | 53 | 61 | 66 | 6.34
77 | 23 | 1520 | 64 | S/T | 0.729 | 57 | 53 | 65 | 61.1 | 5.2
77 | 23 | 1520 | 64 | ∆T | 18.6 | 57 | 53 | 68 | 57.5 | 4.49
77 | 23 | 1520 | 64 | LDB | 58.4 | 57 | 53 | 70 | 55 | 4.1
77 | 23 | 1520 | 64 | LWB | 54.8 | 57 | 53 | 72 | 52.5 | 3.76
77 | 23 | 1520 | 64 | kW | 2.19 | 57 | 53 | 75 | 48.9 | 3.37
80 | 23 | 1520 | 67 | MBh | 47 | 54 | 50 | 61 | 66 | 6.81
80 | 23 | 1520 | 67 | S/T | 0.681 | 54 | 50 | 65 | 61.1 | 5.55
80 | 23 | 1520 | 67 | ∆T | 19.5 | 54 | 50 | 68 | 57.5 | 4.77
80 | 23 | 1520 | 67 | LDB | 60.5 | 54 | 50 | 70 | 55 | 4.33
80 | 23 | 1520 | 67 | LWB | 57.3 | 54 | 50 | 72 | 52.5 | 3.95
80 | 23 | 1520 | 67 | kW | 2.48 | 54 | 50 | 75 | 48.9 | 3.49
84 | 23 | 1520 | 70 | MBh | 52 | 51 | 47 | 61 | 66 | 7.34
84 | 23 | 1520 | 70 | S/T | 0.65 | 51 | 47 | 65 | 61.1 | 5.96
84 | 23 | 1520 | 70 | ∆T | 20.6 | 51 | 47 | 68 | 57.5 | 5.09
84 | 23 | 1520 | 70 | LDB | 63.4 | 51 | 47 | 70 | 55 | 4.59
84 | 23 | 1520 | 70 | LWB | 59.9 | 51 | 47 | 72 | 52.5 | 4.16
84 | 23 | 1520 | 70 | kW | 2.78 | 51 | 47 | 75 | 48.9 | 3.64
86 | 23 | 1520 | 72 | MBh | 55.3 | 47 | 43 | 61 | 65.3 | 8.16
86 | 23 | 1520 | 72 | S/T | 0.642 | 47 | 43 | 65 | 61.1 | 6.58
86 | 23 | 1520 | 72 | ∆T | 21.6 | 47 | 43 | 68 | 57.5 | 5.59
86 | 23 | 1520 | 72 | LDB | 64.4 | 47 | 43 | 70 | 55 | 5.01
86 | 23 | 1520 | 72 | LWB | 61.7 | 47 | 43 | 72 | 52.5 | 4.51
86 | 23 | 1520 | 72 | kW | 2.99 | 47 | 43 | 75 | 48.9 | 3.89
90 | 23 | 1520 | 75 | MBh | 60.2 | 44 | 40 | 61 | 63.4 | 8.42
90 | 23 | 1520 | 75 | S/T | 0.61 | 44 | 40 | 65 | 61.1 | 7.13
90 | 23 | 1520 | 75 | ∆T | 22.4 | 44 | 40 | 68 | 57.5 | 6.03
90 | 23 | 1520 | 75 | LDB | 67.6 | 44 | 40 | 70 | 55 | 5.39
90 | 23 | 1520 | 75 | LWB | 64.5 | 44 | 40 | 72 | 52.5 | 4.82
90 | 23 | 1520 | 75 | kW | 3.3 | 44 | 40 | 75 | 48.9 | 4.11
68 | 30 | 1520 | 57 | MBh | 30.5 | 39 | 36 | 61 | 60.8 | 8.14
68 | 30 | 1520 | 57 | S/T | 0.807 | 39 | 36 | 65 | 60.8 | 7.97
68 | 30 | 1520 | 57 | ∆T | 15 | 39 | 36 | 68 | 57.5 | 6.71
68 | 30 | 1520 | 57 | LDB | 53 | 39 | 36 | 70 | 55 | 5.97
68 | 30 | 1520 | 57 | LWB | 49.4 | 39 | 36 | 72 | 52.5 | 5.31
68 | 30 | 1520 | 57 | kW | 1.6 | 39 | 36 | 75 | 48.9 | 4.47
72 | 30 | 1520 | 61 | MBh | 37.1 | 35 | 32 | 61 | 58.2 | 7.84
72 | 30 | 1520 | 61 | S/T | 0.763 | 35 | 32 | 65 | 58.2 | 8.37
72 | 30 | 1520 | 61 | ∆T | 17.2 | 35 | 32 | 68 | 57.5 | 7.53
72 | 30 | 1520 | 61 | LDB | 54.8 | 35 | 32 | 70 | 55 | 6.68
72 | 30 | 1520 | 61 | LWB | 52.4 | 35 | 32 | 72 | 52.5 | 5.91
72 | 30 | 1520 | 61 | kW | 1.97 | 35 | 32 | 75 | 48.9 | 4.93
77 | 30 | 1520 | 64 | MBh | 42 | 30 | 28 | 61 | 55.6 | 7.51
77 | 30 | 1520 | 64 | S/T | 0.729 | 30 | 28 | 65 | 55.6 | 8.06
77 | 30 | 1520 | 64 | ∆T | 18.6 | 30 | 28 | 68 | 55.6 | 8.48
77 | 30 | 1520 | 64 | LDB | 58.4 | 30 | 28 | 70 | 55 | 7.53
77 | 30 | 1520 | 64 | LWB | 54.8 | 30 | 28 | 72 | 52.5 | 6.64
77 | 30 | 1520 | 64 | kW | 2.26 | 30 | 28 | 75 | 48.9 | 5.49
80 | 30 | 1520 | 67 | MBh | 47 | 26 | 24 | 61 | 53 | 7.15
80 | 30 | 1520 | 67 | S/T | 0.681 | 26 | 24 | 65 | 53 | 7.73
80 | 30 | 1520 | 67 | ∆T | 19.5 | 26 | 24 | 68 | 53 | 8.16
80 | 30 | 1520 | 67 | LDB | 60.5 | 26 | 24 | 70 | 53 | 8.45
80 | 30 | 1520 | 67 | LWB | 57.3 | 26 | 24 | 72 | 52.5 | 7.54
80 | 30 | 1520 | 67 | kW | 2.56 | 26 | 24 | 75 | 48.9 | 6.18
84 | 30 | 1520 | 70 | MBh | 52 | 22 | 20 | 61 | 50.5 | 6.76
84 | 30 | 1520 | 70 | S/T | 0.65 | 22 | 20 | 65 | 50.5 | 7.37
84 | 30 | 1520 | 70 | ∆T | 20.6 | 22 | 20 | 68 | 50.5 | 7.82
84 | 30 | 1520 | 70 | LDB | 63.4 | 22 | 20 | 70 | 50.5 | 8.13
84 | 30 | 1520 | 70 | LWB | 59.9 | 22 | 20 | 72 | 50.5 | 8.35
84 | 30 | 1520 | 70 | kW | 2.87 | 22 | 20 | 75 | 48.9 | 7.04
86 | 30 | 1520 | 72 | MBh | 55.3 | 19 | 18 | 61 | 49.2 | 6.55
86 | 30 | 1520 | 72 | S/T | 0.642 | 19 | 18 | 65 | 49.2 | 7.17
86 | 30 | 1520 | 72 | ∆T | 21.6 | 19 | 18 | 68 | 49.2 | 7.64
86 | 30 | 1520 | 72 | LDB | 64.4 | 19 | 18 | 70 | 49.2 | 7.95
86 | 30 | 1520 | 72 | LWB | 61.7 | 19 | 18 | 72 | 49.2 | 8.03
86 | 30 | 1520 | 72 | kW | 3.09 | 19 | 18 | 75 | 48.9 | 7.54
90 | 30 | 1520 | 75 | MBh | 60.2 | 17 | 16 | 61 | 47.6 | 6.27
90 | 30 | 1520 | 75 | S/T | 0.61 | 17 | 16 | 65 | 47.6 | 6.91
90 | 30 | 1520 | 75 | ∆T | 22.4 | 17 | 16 | 68 | 47.6 | 7.39
90 | 30 | 1520 | 75 | LDB | 67.6 | 17 | 16 | 70 | 47.6 | 7.64
90 | 30 | 1520 | 75 | LWB | 64.5 | 17 | 16 | 72 | 47.6 | 7.64
90 | 30 | 1520 | 75 | kW | 3.41 | 17 | 16 | 75 | 47.6 | 7.64
68 | 40 | 1520 | 57 | MBh | 30.5 | 15 | 14 | 61 | 46.6 | 6.09
68 | 40 | 1520 | 57 | S/T | 0.807 | 15 | 14 | 65 | 46.6 | 6.75
68 | 40 | 1520 | 57 | ∆T | 15 | 15 | 14 | 68 | 46.6 | 7.24
68 | 40 | 1520 | 57 | LDB | 53 | 15 | 14 | 70 | 46.6 | 7.4
68 | 40 | 1520 | 57 | LWB | 49.4 | 15 | 14 | 72 | 46.6 | 7.4
68 | 40 | 1520 | 57 | kW | 1.67 | 15 | 14 | 75 | 46.6 | 7.4
72 | 40 | 1520 | 61 | MBh | 37.1 | 13 | 12 | 61 | 45.3 | 5.85
72 | 40 | 1520 | 61 | S/T | 0.763 | 13 | 12 | 65 | 45.3 | 6.52
72 | 40 | 1520 | 61 | ∆T | 17.2 | 13 | 12 | 68 | 45.3 | 7.03
72 | 40 | 1520 | 61 | LDB | 54.8 | 13 | 12 | 70 | 45.3 | 7.08
72 | 40 | 1520 | 61 | LWB | 52.4 | 13 | 12 | 72 | 45.3 | 7.08
72 | 40 | 1520 | 61 | kW | 2.06 | 13 | 12 | 75 | 45.3 | 7.08
77 | 40 | 1520 | 64 | MBh | 42 | 10 | 9 | 61 | 43.1 | 5.39
77 | 40 | 1520 | 64 | S/T | 0.729 | 10 | 9 | 65 | 43.1 | 6.09
77 | 40 | 1520 | 64 | ∆T | 18.6 | 10 | 9 | 68 | 43.1 | 6.53
77 | 40 | 1520 | 64 | LDB | 58.4 | 10 | 9 | 70 | 43.1 | 6.53
77 | 40 | 1520 | 64 | LWB | 54.8 | 10 | 9 | 72 | 43.1 | 6.53
77 | 40 | 1520 | 64 | kW | 2.37 | 10 | 9 | 75 | 43.1 | 6.53
80 | 40 | 1520 | 67 | MBh | 47 | 6 | 5 | 61 | 40.8 | 4.88
80 | 40 | 1520 | 67 | S/T | 0.681 | 6 | 5 | 65 | 40.8 | 5.62
80 | 40 | 1520 | 67 | ∆T | 19.5 | 6 | 5 | 68 | 40.8 | 5.98
80 | 40 | 1520 | 67 | LDB | 60.5 | 6 | 5 | 70 | 40.8 | 5.98
80 | 40 | 1520 | 67 | LWB | 57.3 | 6 | 5 | 72 | 40.8 | 5.98
80 | 40 | 1520 | 67 | kW | 2.69 | 6 | 5 | 75 | 40.8 | 5.98
84 | 40 | 1520 | 70 | MBh | 52 | -2 | -2 | 61 | 33.8 | 3.64
84 | 40 | 1520 | 70 | S/T | 0.65 | -2 | -2 | 65 | 33.8 | 4.48
84 | 40 | 1520 | 70 | ∆T | 20.6 | -2 | -2 | 68 | 33.8 | 4.84
84 | 40 | 1520 | 70 | LDB | 63.4 | -2 | -2 | 70 | 33.8 | 4.84
84 | 40 | 1520 | 70 | LWB | 59.9 | -2 | -2 | 72 | 33.8 | 4.84
84 | 40 | 1520 | 70 | kW | 3.02 | -2 | -2 | 75 | 33.8 | 4.84
86 | 40 | 1520 | 72 | MBh | 55.3 | -4 | -4 | 61 | 32 | 3.29
86 | 40 | 1520 | 72 | S/T | 0.642 | -4 | -4 | 65 | 32 | 4.15
86 | 40 | 1520 | 72 | ∆T | 21.6 | -4 | -4 | 68 | 32 | 4.56
86 | 40 | 1520 | 72 | LDB | 64.4 | -4 | -4 | 70 | 32 | 4.56
86 | 40 | 1520 | 72 | LWB | 61.7 | -4 | -4 | 72 | 32 | 4.56
86 | 40 | 1520 | 72 | kW | 3.24 | -4 | -4 | 75 | 32 | 4.56
90 | 40 | 1520 | 75 | MBh | 60.2
90 | 40 | 1520 | 75 | S/T | 0.61
90 | 40 | 1520 | 75 | ∆T | 22.4
90 | 40 | 1520 | 75 | LDB | 67.6
90 | 40 | 1520 | 75 | LWB | 64.5
90 | 40 | 1520 | 75 | kW | 3.58
68 | 50 | 1520 | 57 | MBh | 30.5
68 | 50 | 1520 | 57 | S/T | 0.807
68 | 50 | 1520 | 57 | ∆T | 15
68 | 50 | 1520 | 57 | LDB | 53
68 | 50 | 1520 | 57 | LWB | 49.4
68 | 50 | 1520 | 57 | kW | 1.75
72 | 50 | 1520 | 61 | MBh | 37.1
72 | 50 | 1520 | 61 | S/T | 0.763
72 | 50 | 1520 | 61 | ∆T | 17.2
72 | 50 | 1520 | 61 | LDB | 54.8
72 | 50 | 1520 | 61 | LWB | 52.4
72 | 50 | 1520 | 61 | kW | 2.16
77 | 50 | 1520 | 64 | MBh | 42
77 | 50 | 1520 | 64 | S/T | 0.729
77 | 50 | 1520 | 64 | ∆T | 18.6
77 | 50 | 1520 | 64 | LDB | 58.4
77 | 50 | 1520 | 64 | LWB | 54.8
77 | 50 | 1520 | 64 | kW | 2.49
80 | 50 | 1520 | 67 | MBh | 47
80 | 50 | 1520 | 67 | S/T | 0.681
80 | 50 | 1520 | 67 | ∆T | 19.5
80 | 50 | 1520 | 67 | LDB | 60.5
80 | 50 | 1520 | 67 | LWB | 57.3
80 | 50 | 1520 | 67 | kW | 2.82
84 | 50 | 1520 | 70 | MBh | 52
84 | 50 | 1520 | 70 | S/T | 0.65
84 | 50 | 1520 | 70 | ∆T | 20.6
84 | 50 | 1520 | 70 | LDB | 63.4
84 | 50 | 1520 | 70 | LWB | 59.9
84 | 50 | 1520 | 70 | kW | 3.17
86 | 50 | 1520 | 72 | MBh | 55.3
86 | 50 | 1520 | 72 | S/T | 0.642
86 | 50 | 1520 | 72 | ∆T | 21.6
86 | 50 | 1520 | 72 | LDB | 64.4
86 | 50 | 1520 | 72 | LWB | 61.7
86 | 50 | 1520 | 72 | kW | 3.41
90 | 50 | 1520 | 75 | MBh | 60.2
90 | 50 | 1520 | 75 | S/T | 0.61
90 | 50 | 1520 | 75 | ∆T | 22.4
90 | 50 | 1520 | 75 | LDB | 67.6
90 | 50 | 1520 | 75 | LWB | 64.5
90 | 50 | 1520 | 75 | kW | 3.76
68 | 54 | 1520 | 57 | MBh | 30.5
68 | 54 | 1520 | 57 | S/T | 0.81
68 | 54 | 1520 | 57 | ∆T | 15
68 | 54 | 1520 | 57 | LDB | 53
68 | 54 | 1520 | 57 | LWB | 49.4
68 | 54 | 1520 | 57 | kW | 1.78
72 | 54 | 1520 | 61 | MBh | 37.1
72 | 54 | 1520 | 61 | S/T | 0.763
72 | 54 | 1520 | 61 | ∆T | 17.2
72 | 54 | 1520 | 61 | LDB | 54.8
72 | 54 | 1520 | 61 | LWB | 52.4
72 | 54 | 1520 | 61 | kW | 2.2
77 | 54 | 1520 | 64 | MBh | 42
77 | 54 | 1520 | 64 | S/T | 0.729
77 | 54 | 1520 | 64 | ∆T | 18.6
77 | 54 | 1520 | 64 | LDB | 58.4
77 | 54 | 1520 | 64 | LWB | 54.8
77 | 54 | 1520 | 64 | kW | 2.54
80 | 54 | 1520 | 67 | MBh | 47
80 | 54 | 1520 | 67 | S/T | 0.681
80 | 54 | 1520 | 67 | ∆T | 19.5
80 | 54 | 1520 | 67 | LDB | 60.5
80 | 54 | 1520 | 67 | LWB | 57.3
80 | 54 | 1520 | 67 | kW | 2.88
84 | 54 | 1520 | 70 | MBh | 52
84 | 54 | 1520 | 70 | S/T | 0.65
84 | 54 | 1520 | 70 | ∆T | 20.6
84 | 54 | 1520 | 70 | LDB | 63.4
84 | 54 | 1520 | 70 | LWB | 59.9
84 | 54 | 1520 | 70 | kW | 3.24
86 | 54 | 1520 | 72 | MBh | 55.3
86 | 54 | 1520 | 72 | S/T | 0.642
86 | 54 | 1520 | 72 | ∆T | 21.6
86 | 54 | 1520 | 72 | LDB | 64.4
86 | 54 | 1520 | 72 | LWB | 61.7
86 | 54 | 1520 | 72 | kW | 3.48
90 | 54 | 1520 | 75 | MBh | 60.2
90 | 54 | 1520 | 75 | S/T | 0.61
90 | 54 | 1520 | 75 | ∆T | 22.4
90 | 54 | 1520 | 75 | LDB | 67.6
90 | 54 | 1520 | 75 | LWB | 64.5
90 | 54 | 1520 | 75 | kW | 3.84
68 | 58 | 1520 | 57 | MBh | 30.5
68 | 58 | 1520 | 57 | S/T | 0.81
68 | 58 | 1520 | 57 | ∆T | 15
68 | 58 | 1520 | 57 | LDB | 53
68 | 58 | 1520 | 57 | LWB | 49.4
68 | 58 | 1520 | 57 | kW | 1.81
72 | 58 | 1520 | 61 | MBh | 37.1
72 | 58 | 1520 | 61 | S/T | 0.763
72 | 58 | 1520 | 61 | ∆T | 17.2
72 | 58 | 1520 | 61 | LDB | 54.8
72 | 58 | 1520 | 61 | LWB | 52.4
72 | 58 | 1520 | 61 | kW | 2.25
77 | 58 | 1520 | 64 | MBh | 42
77 | 58 | 1520 | 64 | S/T | 0.729
77 | 58 | 1520 | 64 | ∆T | 18.6
77 | 58 | 1520 | 64 | LDB | 58.4
77 | 58 | 1520 | 64 | LWB | 54.8
77 | 58 | 1520 | 64 | kW | 2.59
80 | 58 | 1520 | 67 | MBh | 47
80 | 58 | 1520 | 67 | S/T | 0.681
80 | 58 | 1520 | 67 | ∆T | 19.5
80 | 58 | 1520 | 67 | LDB | 60.5
80 | 58 | 1520 | 67 | LWB | 57.3
80 | 58 | 1520 | 67 | kW | 2.95
84 | 58 | 1520 | 70 | MBh | 52
84 | 58 | 1520 | 70 | S/T | 0.65
84 | 58 | 1520 | 70 | ∆T | 20.6
84 | 58 | 1520 | 70 | LDB | 63.4
84 | 58 | 1520 | 70 | LWB | 59.9
84 | 58 | 1520 | 70 | kW | 3.31
86 | 58 | 1520 | 72 | MBh | 55.3
86 | 58 | 1520 | 72 | S/T | 0.642
86 | 58 | 1520 | 72 | ∆T | 21.6
86 | 58 | 1520 | 72 | LDB | 64.4
86 | 58 | 1520 | 72 | LWB | 61.7
86 | 58 | 1520 | 72 | kW | 3.55
90 | 58 | 1520 | 75 | MBh | 59.6
90 | 58 | 1520 | 75 | S/T | 0.609
90 | 58 | 1520 | 75 | ∆T | 22.1
90 | 58 | 1520 | 75 | LDB | 67.9
90 | 58 | 1520 | 75 | LWB | 64.6
90 | 58 | 1520 | 75 | kW | 3.85
68 | 62 | 1520 | 57 | MBh | 30.5
68 | 62 | 1520 | 57 | S/T | 0.81
68 | 62 | 1520 | 57 | ∆T | 15
68 | 62 | 1520 | 57 | LDB | 53
68 | 62 | 1520 | 57 | LWB | 49.4
68 | 62 | 1520 | 57 | kW | 1.85
72 | 62 | 1520 | 61 | MBh | 37.1
72 | 62 | 1520 | 61 | S/T | 0.763
72 | 62 | 1520 | 61 | ∆T | 17.2
72 | 62 | 1520 | 61 | LDB | 54.8
72 | 62 | 1520 | 61 | LWB | 52.4
72 | 62 | 1520 | 61 | kW | 2.3
77 | 62 | 1520 | 64 | MBh | 42
77 | 62 | 1520 | 64 | S/T | 0.729
77 | 62 | 1520 | 64 | ∆T | 18.6
77 | 62 | 1520 | 64 | LDB | 58.4
77 | 62 | 1520 | 64 | LWB | 54.8
77 | 62 | 1520 | 64 | kW | 2.65
80 | 62 | 1520 | 67 | MBh | 47
80 | 62 | 1520 | 67 | S/T | 0.681
80 | 62 | 1520 | 67 | ∆T | 19.5
80 | 62 | 1520 | 67 | LDB | 60.5
80 | 62 | 1520 | 67 | LWB | 57.3
80 | 62 | 1520 | 67 | kW | 3.01
84 | 62 | 1520 | 70 | MBh | 52
84 | 62 | 1520 | 70 | S/T | 0.65
84 | 62 | 1520 | 70 | ∆T | 20.6
84 | 62 | 1520 | 70 | LDB | 63.4
84 | 62 | 1520 | 70 | LWB | 59.9
84 | 62 | 1520 | 70 | kW | 3.38
86 | 62 | 1520 | 72 | MBh | 55.3
86 | 62 | 1520 | 72 | S/T | 0.642
86 | 62 | 1520 | 72 | ∆T | 21.6
86 | 62 | 1520 | 72 | LDB | 64.4
86 | 62 | 1520 | 72 | LWB | 61.7
86 | 62 | 1520 | 72 | kW | 3.63
90 | 62 | 1520 | 75 | MBh | 58.8
90 | 62 | 1520 | 75 | S/T | 0.609
90 | 62 | 1520 | 75 | ∆T | 21.8
90 | 62 | 1520 | 75 | LDB | 68.2
90 | 62 | 1520 | 75 | LWB | 64.7
90 | 62 | 1520 | 75 | kW | 3.94
68 | 66 | 1520 | 57 | MBh | 30.5
68 | 66 | 1520 | 57 | S/T | 0.81
68 | 66 | 1520 | 57 | ∆T | 15
68 | 66 | 1520 | 57 | LDB | 53
68 | 66 | 1520 | 57 | LWB | 49.4
68 | 66 | 1520 | 57 | kW | 1.89
72 | 66 | 1520 | 61 | MBh | 37.1
72 | 66 | 1520 | 61 | S/T | 0.763
72 | 66 | 1520 | 61 | ∆T | 17.2
72 | 66 | 1520 | 61 | LDB | 54.8
72 | 66 | 1520 | 61 | LWB | 52.4
72 | 66 | 1520 | 61 | kW | 2.35
77 | 66 | 1520 | 64 | MBh | 42
77 | 66 | 1520 | 64 | S/T | 0.729
77 | 66 | 1520 | 64 | ∆T | 18.6
77 | 66 | 1520 | 64 | LDB | 58.4
77 | 66 | 1520 | 64 | LWB | 54.8
77 | 66 | 1520 | 64 | kW | 2.71
80 | 66 | 1520 | 67 | MBh | 47
80 | 66 | 1520 | 67 | S/T | 0.681
80 | 66 | 1520 | 67 | ∆T | 19.5
80 | 66 | 1520 | 67 | LDB | 60.5
80 | 66 | 1520 | 67 | LWB | 57.3
80 | 66 | 1520 | 67 | kW | 3.08
84 | 66 | 1520 | 70 | MBh | 52
84 | 66 | 1520 | 70 | S/T | 0.65
84 | 66 | 1520 | 70 | ∆T | 20.6
84 | 66 | 1520 | 70 | LDB | 63.4
84 | 66 | 1520 | 70 | LWB | 59.9
84 | 66 | 1520 | 70 | kW | 3.57
86 | 66 | 1520 | 72 | MBh | 55.3
86 | 66 | 1520 | 72 | S/T | 0.644
86 | 66 | 1520 | 72 | ∆T | 21.7
86 | 66 | 1520 | 72 | LDB | 64.3
86 | 66 | 1520 | 72 | LWB | 61.7
86 | 66 | 1520 | 72 | kW | 3.92
90 | 66 | 1520 | 75 | MBh | 57.9
90 | 66 | 1520 | 75 | S/T | 0.61
90 | 66 | 1520 | 75 | ∆T | 21.5
90 | 66 | 1520 | 75 | LDB | 68.5
90 | 66 | 1520 | 75 | LWB | 64.9
90 | 66 | 1520 | 75 | kW | 4.16
68 | 70 | 1520 | 57 | MBh | 30.5
68 | 70 | 1520 | 57 | S/T | 0.81
68 | 70 | 1520 | 57 | ∆T | 15
68 | 70 | 1520 | 57 | LDB | 53
68 | 70 | 1520 | 57 | LWB | 49.4
68 | 70 | 1520 | 57 | kW | 1.93
72 | 70 | 1520 | 61 | MBh | 37.1
72 | 70 | 1520 | 61 | S/T | 0.763
72 | 70 | 1520 | 61 | ∆T | 17.2
72 | 70 | 1520 | 61 | LDB | 54.8
72 | 70 | 1520 | 61 | LWB | 52.4
72 | 70 | 1520 | 61 | kW | 2.4
77 | 70 | 1520 | 64 | MBh | 42
77 | 70 | 1520 | 64 | S/T | 0.729
77 | 70 | 1520 | 64 | ∆T | 18.6
77 | 70 | 1520 | 64 | LDB | 58.4
77 | 70 | 1520 | 64 | LWB | 54.8
77 | 70 | 1520 | 64 | kW | 2.84
80 | 70 | 1520 | 67 | MBh | 47
80 | 70 | 1520 | 67 | S/T | 0.681
80 | 70 | 1520 | 67 | ∆T | 19.5
80 | 70 | 1520 | 67 | LDB | 60.5
80 | 70 | 1520 | 67 | LWB | 57.3
80 | 70 | 1520 | 67 | kW | 3.33
84 | 70 | 1520 | 70 | MBh | 52
84 | 70 | 1520 | 70 | S/T | 0.652
84 | 70 | 1520 | 70 | ∆T | 20.7
84 | 70 | 1520 | 70 | LDB | 63.3
84 | 70 | 1520 | 70 | LWB | 59.9
84 | 70 | 1520 | 70 | kW | 3.86
86 | 70 | 1520 | 72 | MBh | 55.3
86 | 70 | 1520 | 72 | S/T | 0.644
86 | 70 | 1520 | 72 | ∆T | 21.7
86 | 70 | 1520 | 72 | LDB | 64.3
86 | 70 | 1520 | 72 | LWB | 61.7
86 | 70 | 1520 | 72 | kW | 4.24
90 | 70 | 1520 | 75 | MBh | 57
90 | 70 | 1520 | 75 | S/T | 0.611
90 | 70 | 1520 | 75 | ∆T | 21.2
90 | 70 | 1520 | 75 | LDB | 68.8
90 | 70 | 1520 | 75 | LWB | 65.1
90 | 70 | 1520 | 75 | kW | 4.38
68 | 72 | 1520 | 57 | MBh | 30.5
68 | 72 | 1520 | 57 | S/T | 0.81
68 | 72 | 1520 | 57 | ∆T | 15
68 | 72 | 1520 | 57 | LDB | 53
68 | 72 | 1520 | 57 | LWB | 49.4
68 | 72 | 1520 | 57 | kW | 1.95
72 | 72 | 1520 | 61 | MBh | 37.1
72 | 72 | 1520 | 61 | S/T | 0.763
72 | 72 | 1520 | 61 | ∆T | 17.2
72 | 72 | 1520 | 61 | LDB | 54.8
72 | 72 | 1520 | 61 | LWB | 52.4
72 | 72 | 1520 | 61 | kW | 2.48
77 | 72 | 1520 | 64 | MBh | 42
77 | 72 | 1520 | 64 | S/T | 0.731
77 | 72 | 1520 | 64 | ∆T | 18.7
77 | 72 | 1520 | 64 | LDB | 58.3
77 | 72 | 1520 | 64 | LWB | 54.8
77 | 72 | 1520 | 64 | kW | 2.95
80 | 72 | 1520 | 67 | MBh | 47
80 | 72 | 1520 | 67 | S/T | 0.681
80 | 72 | 1520 | 67 | ∆T | 19.5
80 | 72 | 1520 | 67 | LDB | 60.5
80 | 72 | 1520 | 67 | LWB | 57.3
80 | 72 | 1520 | 67 | kW | 3.46
84 | 72 | 1520 | 70 | MBh | 52
84 | 72 | 1520 | 70 | S/T | 0.652
84 | 72 | 1520 | 70 | ∆T | 20.7
84 | 72 | 1520 | 70 | LDB | 63.3
84 | 72 | 1520 | 70 | LWB | 59.9
84 | 72 | 1520 | 70 | kW | 4.02
86 | 72 | 1520 | 72 | MBh | 55.3
86 | 72 | 1520 | 72 | S/T | 0.644
86 | 72 | 1520 | 72 | ∆T | 21.7
86 | 72 | 1520 | 72 | LDB | 64.3
86 | 72 | 1520 | 72 | LWB | 61.7
86 | 72 | 1520 | 72 | kW | 4.41
90 | 72 | 1520 | 75 | MBh | 56.6
90 | 72 | 1520 | 75 | S/T | 0.61
90 | 72 | 1520 | 75 | ∆T | 21
90 | 72 | 1520 | 75 | LDB | 69
90 | 72 | 1520 | 75 | LWB | 65.2
90 | 72 | 1520 | 75 | kW | 4.49
68 | 75 | 1520 | 57 | MBh | 30.5
68 | 75 | 1520 | 57 | S/T | 0.81
68 | 75 | 1520 | 57 | ∆T | 15
68 | 75 | 1520 | 57 | LDB | 53
68 | 75 | 1520 | 57 | LWB | 49.4
68 | 75 | 1520 | 57 | kW | 2.02
72 | 75 | 1520 | 61 | MBh | 37.1
72 | 75 | 1520 | 61 | S/T | 0.763
72 | 75 | 1520 | 61 | ∆T | 17.2
72 | 75 | 1520 | 61 | LDB | 54.8
72 | 75 | 1520 | 61 | LWB | 52.4
72 | 75 | 1520 | 61 | kW | 2.62
77 | 75 | 1520 | 64 | MBh | 42
77 | 75 | 1520 | 64 | S/T | 0.731
77 | 75 | 1520 | 64 | ∆T | 18.7
77 | 75 | 1520 | 64 | LDB | 58.3
77 | 75 | 1520 | 64 | LWB | 54.8
77 | 75 | 1520 | 64 | kW | 3.12
80 | 75 | 1520 | 67 | MBh | 47
80 | 75 | 1520 | 67 | S/T | 0.681
80 | 75 | 1520 | 67 | ∆T | 19.5
80 | 75 | 1520 | 67 | LDB | 60.5
80 | 75 | 1520 | 67 | LWB | 57.3
80 | 75 | 1520 | 67 | kW | 3.66
84 | 75 | 1520 | 70 | MBh | 52
84 | 75 | 1520 | 70 | S/T | 0.652
84 | 75 | 1520 | 70 | ∆T | 20.7
84 | 75 | 1520 | 70 | LDB | 63.3
84 | 75 | 1520 | 70 | LWB | 59.9
84 | 75 | 1520 | 70 | kW | 4.26
86 | 75 | 1520 | 72 | MBh | 54.9
86 | 75 | 1520 | 72 | S/T | 0.645
86 | 75 | 1520 | 72 | ∆T | 21.6
86 | 75 | 1520 | 72 | LDB | 64.4
86 | 75 | 1520 | 72 | LWB | 61.7
86 | 75 | 1520 | 72 | kW | 4.62
90 | 75 | 1520 | 75 | MBh | 55.9
90 | 75 | 1520 | 75 | S/T | 0.61
90 | 75 | 1520 | 75 | ∆T | 20.8
90 | 75 | 1520 | 75 | LDB | 69.2
90 | 75 | 1520 | 75 | LWB | 65.3
90 | 75 | 1520 | 75 | kW | 4.65
68 | 79 | 1520 | 57 | MBh | 30.5
68 | 79 | 1520 | 57 | S/T | 0.81
68 | 79 | 1520 | 57 | ∆T | 15
68 | 79 | 1520 | 57 | LDB | 53
68 | 79 | 1520 | 57 | LWB | 49.4
68 | 79 | 1520 | 57 | kW | 2.17
72 | 79 | 1520 | 61 | MBh | 37.1
72 | 79 | 1520 | 61 | S/T | 0.763
72 | 79 | 1520 | 61 | ∆T | 17.2
72 | 79 | 1520 | 61 | LDB | 54.8
72 | 79 | 1520 | 61 | LWB | 52.4
72 | 79 | 1520 | 61 | kW | 2.82
77 | 79 | 1520 | 64 | MBh | 42
77 | 79 | 1520 | 64 | S/T | 0.731
77 | 79 | 1520 | 64 | ∆T | 18.7
77 | 79 | 1520 | 64 | LDB | 58.3
77 | 79 | 1520 | 64 | LWB | 54.8
77 | 79 | 1520 | 64 | kW | 3.36
80 | 79 | 1520 | 67 | MBh | 47
80 | 79 | 1520 | 67 | S/T | 0.681
80 | 79 | 1520 | 67 | ∆T | 19.5
80 | 79 | 1520 | 67 | LDB | 60.5
80 | 79 | 1520 | 67 | LWB | 57.3
80 | 79 | 1520 | 67 | kW | 3.95
84 | 79 | 1520 | 70 | MBh | 52
84 | 79 | 1520 | 70 | S/T | 0.652
84 | 79 | 1520 | 70 | ∆T | 20.7
84 | 79 | 1520 | 70 | LDB | 63.3
84 | 79 | 1520 | 70 | LWB | 59.9
84 | 79 | 1520 | 70 | kW | 4.59
86 | 79 | 1520 | 72 | MBh | 54
86 | 79 | 1520 | 72 | S/T | 0.644
86 | 79 | 1520 | 72 | ∆T | 21.2
86 | 79 | 1520 | 72 | LDB | 64.8
86 | 79 | 1520 | 72 | LWB | 61.9
86 | 79 | 1520 | 72 | kW | 4.84
90 | 79 | 1520 | 75 | MBh | 55
90 | 79 | 1520 | 75 | S/T | 0.611
90 | 79 | 1520 | 75 | ∆T | 20.5
90 | 79 | 1520 | 75 | LDB | 69.5
90 | 79 | 1520 | 75 | LWB | 65.5
90 | 79 | 1520 | 75 | kW | 4.88
68 | 83 | 1520 | 57 | MBh | 30.5
68 | 83 | 1520 | 57 | S/T | 0.81
68 | 83 | 1520 | 57 | ∆T | 15
68 | 83 | 1520 | 57 | LDB | 53
68 | 83 | 1520 | 57 | LWB | 49.4
68 | 83 | 1520 | 57 | kW | 2.33
72 | 83 | 1520 | 61 | MBh | 37.1
72 | 83 | 1520 | 61 | S/T | 0.763
72 | 83 | 1520 | 61 | ∆T | 17.2
72 | 83 | 1520 | 61 | LDB | 54.8
72 | 83 | 1520 | 61 | LWB | 52.4
72 | 83 | 1520 | 61 | kW | 3.03
77 | 83 | 1520 | 64 | MBh | 42
77 | 83 | 1520 | 64 | S/T | 0.731
77 | 83 | 1520 | 64 | ∆T | 18.7
77 | 83 | 1520 | 64 | LDB | 58.3
77 | 83 | 1520 | 64 | LWB | 54.8
77 | 83 | 1520 | 64 | kW | 3.61
80 | 83 | 1520 | 67 | MBh | 47
80 | 83 | 1520 | 67 | S/T | 0.681
80 | 83 | 1520 | 67 | ∆T | 19.5
80 | 83 | 1520 | 67 | LDB | 60.5
80 | 83 | 1520 | 67 | LWB | 57.3
80 | 83 | 1520 | 67 | kW | 4.25
84 | 83 | 1520 | 70 | MBh | 52
84 | 83 | 1520 | 70 | S/T | 0.652
84 | 83 | 1520 | 70 | ∆T | 20.7
84 | 83 | 1520 | 70 | LDB | 63.3
84 | 83 | 1520 | 70 | LWB | 59.9
84 | 83 | 1520 | 70 | kW | 4.95
86 | 83 | 1520 | 72 | MBh | 53.2
86 | 83 | 1520 | 72 | S/T | 0.645
86 | 83 | 1520 | 72 | ∆T | 20.9
86 | 83 | 1520 | 72 | LDB | 65.1
86 | 83 | 1520 | 72 | LWB | 62.1
86 | 83 | 1520 | 72 | kW | 5.07
90 | 83 | 1520 | 75 | MBh | 54.1
90 | 83 | 1520 | 75 | S/T | 0.61
90 | 83 | 1520 | 75 | ∆T | 20.1
90 | 83 | 1520 | 75 | LDB | 69.9
90 | 83 | 1520 | 75 | LWB | 65.6
90 | 83 | 1520 | 75 | kW | 5.1
68 | 87 | 1520 | 57 | MBh | 30.5
68 | 87 | 1520 | 57 | S/T | 0.81
68 | 87 | 1520 | 57 | ∆T | 15
68 | 87 | 1520 | 57 | LDB | 53
68 | 87 | 1520 | 57 | LWB | 49.4
68 | 87 | 1520 | 57 | kW | 2.49
72 | 87 | 1520 | 61 | MBh | 37.1
72 | 87 | 1520 | 61 | S/T | 0.763
72 | 87 | 1520 | 61 | ∆T | 17.2
72 | 87 | 1520 | 61 | LDB | 54.8
72 | 87 | 1520 | 61 | LWB | 52.4
72 | 87 | 1520 | 61 | kW | 3.25
77 | 87 | 1520 | 64 | MBh | 42
77 | 87 | 1520 | 64 | S/T | 0.731
77 | 87 | 1520 | 64 | ∆T | 18.7
77 | 87 | 1520 | 64 | LDB | 58.3
77 | 87 | 1520 | 64 | LWB | 54.8
77 | 87 | 1520 | 64 | kW | 3.88
80 | 87 | 1520 | 67 | MBh | 47
80 | 87 | 1520 | 67 | S/T | 0.681
80 | 87 | 1520 | 67 | ∆T | 19.5
80 | 87 | 1520 | 67 | LDB | 60.5
80 | 87 | 1520 | 67 | LWB | 57.3
80 | 87 | 1520 | 67 | kW | 4.57
84 | 87 | 1520 | 70 | MBh | 51.6
84 | 87 | 1520 | 70 | S/T | 0.653
84 | 87 | 1520 | 70 | ∆T | 20.5
84 | 87 | 1520 | 70 | LDB | 63.5
84 | 87 | 1520 | 70 | LWB | 59.9
84 | 87 | 1520 | 70 | kW | 5.26
86 | 87 | 1520 | 72 | MBh | 52.3
86 | 87 | 1520 | 72 | S/T | 0.644
86 | 87 | 1520 | 72 | ∆T | 20.5
86 | 87 | 1520 | 72 | LDB | 65.5
86 | 87 | 1520 | 72 | LWB | 62.3
86 | 87 | 1520 | 72 | kW | 5.29
90 | 87 | 1520 | 75 | MBh | 53.2
90 | 87 | 1520 | 75 | S/T | 0.611
90 | 87 | 1520 | 75 | ∆T | 19.8
90 | 87 | 1520 | 75 | LDB | 70.2
90 | 87 | 1520 | 75 | LWB | 65.8
90 | 87 | 1520 | 75 | kW | 5.32
68 | 91 | 1520 | 57 | MBh | 30.5
68 | 91 | 1520 | 57 | S/T | 0.81
68 | 91 | 1520 | 57 | ∆T | 15
68 | 91 | 1520 | 57 | LDB | 53
68 | 91 | 1520 | 57 | LWB | 49.4
68 | 91 | 1520 | 57 | kW | 2.67
72 | 91 | 1520 | 61 | MBh | 37.1
72 | 91 | 1520 | 61 | S/T | 0.763
72 | 91 | 1520 | 61 | ∆T | 17.2
72 | 91 | 1520 | 61 | LDB | 54.8
72 | 91 | 1520 | 61 | LWB | 52.4
72 | 91 | 1520 | 61 | kW | 3.48
77 | 91 | 1520 | 64 | MBh | 42
77 | 91 | 1520 | 64 | S/T | 0.731
77 | 91 | 1520 | 64 | ∆T | 18.7
77 | 91 | 1520 | 64 | LDB | 58.3
77 | 91 | 1520 | 64 | LWB | 54.8
77 | 91 | 1520 | 64 | kW | 4.17
80 | 91 | 1520 | 67 | MBh | 47
80 | 91 | 1520 | 67 | S/T | 0.681
80 | 91 | 1520 | 67 | ∆T | 19.5
80 | 91 | 1520 | 67 | LDB | 60.5
80 | 91 | 1520 | 67 | LWB | 57.3
80 | 91 | 1520 | 67 | kW | 4.92
84 | 91 | 1520 | 70 | MBh | 50.7
84 | 91 | 1520 | 70 | S/T | 0.653
84 | 91 | 1520 | 70 | ∆T | 20.2
84 | 91 | 1520 | 70 | LDB | 63.8
84 | 91 | 1520 | 70 | LWB | 60.1
84 | 91 | 1520 | 70 | kW | 5.49
86 | 91 | 1520 | 72 | MBh | 51.4
86 | 91 | 1520 | 72 | S/T | 0.644
86 | 91 | 1520 | 72 | ∆T | 20.2
86 | 91 | 1520 | 72 | LDB | 65.8
86 | 91 | 1520 | 72 | LWB | 62.5
86 | 91 | 1520 | 72 | kW | 5.51
90 | 91 | 1520 | 75 | MBh | 52.4
90 | 91 | 1520 | 75 | S/T | 0.609
90 | 91 | 1520 | 75 | ∆T | 19.4
90 | 91 | 1520 | 75 | LDB | 70.6
90 | 91 | 1520 | 75 | LWB | 66
90 | 91 | 1520 | 75 | kW | 5.55
68 | 93 | 1520 | 57 | MBh | 30.5
68 | 93 | 1520 | 57 | S/T | 0.81
68 | 93 | 1520 | 57 | ∆T | 15
68 | 93 | 1520 | 57 | LDB | 53
68 | 93 | 1520 | 57 | LWB | 49.4
68 | 93 | 1520 | 57 | kW | 2.76
72 | 93 | 1520 | 61 | MBh | 37.1
72 | 93 | 1520 | 61 | S/T | 0.763
72 | 93 | 1520 | 61 | ∆T | 17.2
72 | 93 | 1520 | 61 | LDB | 54.8
72 | 93 | 1520 | 61 | LWB | 52.4
72 | 93 | 1520 | 61 | kW | 3.61
77 | 93 | 1520 | 64 | MBh | 42
77 | 93 | 1520 | 64 | S/T | 0.729
77 | 93 | 1520 | 64 | ∆T | 18.6
77 | 93 | 1520 | 64 | LDB | 58.4
77 | 93 | 1520 | 64 | LWB | 54.8
77 | 93 | 1520 | 64 | kW | 4.32
80 | 93 | 1520 | 67 | MBh | 47
80 | 93 | 1520 | 67 | S/T | 0.681
80 | 93 | 1520 | 67 | ∆T | 19.5
80 | 93 | 1520 | 67 | LDB | 60.5
80 | 93 | 1520 | 67 | LWB | 57.3
80 | 93 | 1520 | 67 | kW | 5.1
84 | 93 | 1520 | 70 | MBh | 50.3
84 | 93 | 1520 | 70 | S/T | 0.652
84 | 93 | 1520 | 70 | ∆T | 20
84 | 93 | 1520 | 70 | LDB | 64
84 | 93 | 1520 | 70 | LWB | 60.2
84 | 93 | 1520 | 70 | kW | 5.6
86 | 93 | 1520 | 72 | MBh | 51
86 | 93 | 1520 | 72 | S/T | 0.643
86 | 93 | 1520 | 72 | ∆T | 20
86 | 93 | 1520 | 72 | LDB | 66
86 | 93 | 1520 | 72 | LWB | 62.5
86 | 93 | 1520 | 72 | kW | 5.62
90 | 93 | 1520 | 75 | MBh | 51.9
90 | 93 | 1520 | 75 | S/T | 0.611
90 | 93 | 1520 | 75 | ∆T | 19.3
90 | 93 | 1520 | 75 | LDB | 70.7
90 | 93 | 1520 | 75 | LWB | 66.1
90 | 93 | 1520 | 75 | kW | 5.66
68 | 95 | 1520 | 57 | MBh | 30.5
68 | 95 | 1520 | 57 | S/T | 0.81
68 | 95 | 1520 | 57 | ∆T | 15
68 | 95 | 1520 | 57 | LDB | 53
68 | 95 | 1520 | 57 | LWB | 49.4
68 | 95 | 1520 | 57 | kW | 2.85
72 | 95 | 1520 | 61 | MBh | 37.1
72 | 95 | 1520 | 61 | S/T | 0.763
72 | 95 | 1520 | 61 | ∆T | 17.2
72 | 95 | 1520 | 61 | LDB | 54.8
72 | 95 | 1520 | 61 | LWB | 52.4
72 | 95 | 1520 | 61 | kW | 3.73
77 | 95 | 1520 | 64 | MBh | 42
77 | 95 | 1520 | 64 | S/T | 0.729
77 | 95 | 1520 | 64 | ∆T | 18.6
77 | 95 | 1520 | 64 | LDB | 58.4
77 | 95 | 1520 | 64 | LWB | 54.8
77 | 95 | 1520 | 64 | kW | 4.47
80 | 95 | 1520 | 67 | MBh | 47
80 | 95 | 1520 | 67 | S/T | 0.681
80 | 95 | 1520 | 67 | ∆T | 19.5
80 | 95 | 1520 | 67 | LDB | 60.5
80 | 95 | 1520 | 67 | LWB | 57.3
80 | 95 | 1520 | 67 | kW | 5.28
84 | 95 | 1520 | 70 | MBh | 49.9
84 | 95 | 1520 | 70 | S/T | 0.651
84 | 95 | 1520 | 70 | ∆T | 19.8
84 | 95 | 1520 | 70 | LDB | 64.2
84 | 95 | 1520 | 70 | LWB | 60.3
84 | 95 | 1520 | 70 | kW | 5.71
86 | 95 | 1520 | 72 | MBh | 50.5
86 | 95 | 1520 | 72 | S/T | 0.644
86 | 95 | 1520 | 72 | ∆T | 19.8
86 | 95 | 1520 | 72 | LDB | 66.2
86 | 95 | 1520 | 72 | LWB | 62.7
86 | 95 | 1520 | 72 | kW | 5.74
90 | 95 | 1520 | 75 | MBh | 51.5
90 | 95 | 1520 | 75 | S/T | 0.61
90 | 95 | 1520 | 75 | ∆T | 19.1
90 | 95 | 1520 | 75 | LDB | 70.9
90 | 95 | 1520 | 75 | LWB | 66.1
90 | 95 | 1520 | 75 | kW | 5.78
68 | 99 | 1520 | 57 | MBh | 30.5
68 | 99 | 1520 | 57 | S/T | 0.81
68 | 99 | 1520 | 57 | ∆T | 15
68 | 99 | 1520 | 57 | LDB | 53
68 | 99 | 1520 | 57 | LWB | 49.4
68 | 99 | 1520 | 57 | kW | 3.05
72 | 99 | 1520 | 61 | MBh | 37.1
72 | 99 | 1520 | 61 | S/T | 0.763
72 | 99 | 1520 | 61 | ∆T | 17.2
72 | 99 | 1520 | 61 | LDB | 54.8
72 | 99 | 1520 | 61 | LWB | 52.4
72 | 99 | 1520 | 61 | kW | 4
77 | 99 | 1520 | 64 | MBh | 42
77 | 99 | 1520 | 64 | S/T | 0.729
77 | 99 | 1520 | 64 | ∆T | 18.6
77 | 99 | 1520 | 64 | LDB | 58.4
77 | 99 | 1520 | 64 | LWB | 54.8
77 | 99 | 1520 | 64 | kW | 4.8
80 | 99 | 1520 | 67 | MBh | 47
80 | 99 | 1520 | 67 | S/T | 0.681
80 | 99 | 1520 | 67 | ∆T | 19.5
80 | 99 | 1520 | 67 | LDB | 60.5
80 | 99 | 1520 | 67 | LWB | 57.3
80 | 99 | 1520 | 67 | kW | 5.67
84 | 99 | 1520 | 70 | MBh | 49
84 | 99 | 1520 | 70 | S/T | 0.653
84 | 99 | 1520 | 70 | ∆T | 19.5
84 | 99 | 1520 | 70 | LDB | 64.5
84 | 99 | 1520 | 70 | LWB | 60.5
84 | 99 | 1520 | 70 | kW | 5.93
86 | 99 | 1520 | 72 | MBh | 49.6
86 | 99 | 1520 | 72 | S/T | 0.647
86 | 99 | 1520 | 72 | ∆T | 19.6
86 | 99 | 1520 | 72 | LDB | 66.4
86 | 99 | 1520 | 72 | LWB | 62.8
86 | 99 | 1520 | 72 | kW | 5.96
90 | 99 | 1520 | 75 | MBh | 50
90 | 99 | 1520 | 75 | S/T | 0.612
90 | 99 | 1520 | 75 | ∆T | 18.6
90 | 99 | 1520 | 75 | LDB | 71.4
90 | 99 | 1520 | 75 | LWB | 66.4
90 | 99 | 1520 | 75 | kW | 5.98
68 | 103 | 1520 | 57 | MBh | 30.5
68 | 103 | 1520 | 57 | S/T | 0.81
68 | 103 | 1520 | 57 | ∆T | 15
68 | 103 | 1520 | 57 | LDB | 53
68 | 103 | 1520 | 57 | LWB | 49.4
68 | 103 | 1520 | 57 | kW | 3.26
72 | 103 | 1520 | 61 | MBh | 37.1
72 | 103 | 1520 | 61 | S/T | 0.763
72 | 103 | 1520 | 61 | ∆T | 17.2
72 | 103 | 1520 | 61 | LDB | 54.8
72 | 103 | 1520 | 61 | LWB | 52.4
72 | 103 | 1520 | 61 | kW | 4.28
77 | 103 | 1520 | 64 | MBh | 42
77 | 103 | 1520 | 64 | S/T | 0.729
77 | 103 | 1520 | 64 | ∆T | 18.6
77 | 103 | 1520 | 64 | LDB | 58.4
77 | 103 | 1520 | 64 | LWB | 54.8
77 | 103 | 1520 | 64 | kW | 5.14
80 | 103 | 1520 | 67 | MBh | 47
80 | 103 | 1520 | 67 | S/T | 0.681
80 | 103 | 1520 | 67 | ∆T | 19.5
80 | 103 | 1520 | 67 | LDB | 60.5
80 | 103 | 1520 | 67 | LWB | 57.3
80 | 103 | 1520 | 67 | kW | 6.08
84 | 103 | 1520 | 70 | MBh | 47.9
84 | 103 | 1520 | 70 | S/T | 0.653
84 | 103 | 1520 | 70 | ∆T | 19.1
84 | 103 | 1520 | 70 | LDB | 64.9
84 | 103 | 1520 | 70 | LWB | 60.7
84 | 103 | 1520 | 70 | kW | 6.15
86 | 103 | 1520 | 72 | MBh | 47.9
86 | 103 | 1520 | 72 | S/T | 0.647
86 | 103 | 1520 | 72 | ∆T | 18.9
86 | 103 | 1520 | 72 | LDB | 67.1
86 | 103 | 1520 | 72 | LWB | 63.2
86 | 103 | 1520 | 72 | kW | 6.15
90 | 103 | 1520 | 75 | MBh | 47.9
90 | 103 | 1520 | 75 | S/T | 0.614
90 | 103 | 1520 | 75 | ∆T | 17.9
90 | 103 | 1520 | 75 | LDB | 72.1
90 | 103 | 1520 | 75 | LWB | 66.8
90 | 103 | 1520 | 75 | kW | 6.15
68 | 106 | 1520 | 57 | MBh | 30.5
68 | 106 | 1520 | 57 | S/T | 0.81
68 | 106 | 1520 | 57 | ∆T | 15
68 | 106 | 1520 | 57 | LDB | 53
68 | 106 | 1520 | 57 | LWB | 49.4
68 | 106 | 1520 | 57 | kW | 3.42
72 | 106 | 1520 | 61 | MBh | 37.1
72 | 106 | 1520 | 61 | S/T | 0.763
72 | 106 | 1520 | 61 | ∆T | 17.2
72 | 106 | 1520 | 61 | LDB | 54.8
72 | 106 | 1520 | 61 | LWB | 52.4
72 | 106 | 1520 | 61 | kW | 4.51
77 | 106 | 1520 | 64 | MBh | 42
77 | 106 | 1520 | 64 | S/T | 0.729
77 | 106 | 1520 | 64 | ∆T | 18.6
77 | 106 | 1520 | 64 | LDB | 58.4
77 | 106 | 1520 | 64 | LWB | 54.8
77 | 106 | 1520 | 64 | kW | 5.42
80 | 106 | 1520 | 67 | MBh | 46.3
80 | 106 | 1520 | 67 | S/T | 0.683
80 | 106 | 1520 | 67 | ∆T | 19.2
80 | 106 | 1520 | 67 | LDB | 60.8
80 | 106 | 1520 | 67 | LWB | 57.4
80 | 106 | 1520 | 67 | kW | 6.26
84 | 106 | 1520 | 70 | MBh | 46.3
84 | 106 | 1520 | 70 | S/T | 0.654
84 | 106 | 1520 | 70 | ∆T | 18.5
84 | 106 | 1520 | 70 | LDB | 65.5
84 | 106 | 1520 | 70 | LWB | 61.1
84 | 106 | 1520 | 70 | kW | 6.26
86 | 106 | 1520 | 72 | MBh | 46.3
86 | 106 | 1520 | 72 | S/T | 0.646
86 | 106 | 1520 | 72 | ∆T | 18.2
86 | 106 | 1520 | 72 | LDB | 67.8
86 | 106 | 1520 | 72 | LWB | 63.5
86 | 106 | 1520 | 72 | kW | 6.26
90 | 106 | 1520 | 75 | MBh | 46.3
90 | 106 | 1520 | 75 | S/T | 0.613
90 | 106 | 1520 | 75 | ∆T | 17.3
90 | 106 | 1520 | 75 | LDB | 72.7
90 | 106 | 1520 | 75 | LWB | 67.1
90 | 106 | 1520 | 75 | kW | 6.26
68 | 110 | 1520 | 57 | MBh | 30.5
68 | 110 | 1520 | 57 | S/T | 0.81
68 | 110 | 1520 | 57 | ∆T | 15
68 | 110 | 1520 | 57 | LDB | 53
68 | 110 | 1520 | 57 | LWB | 49.4
68 | 110 | 1520 | 57 | kW | 3.66
72 | 110 | 1520 | 61 | MBh | 37.1
72 | 110 | 1520 | 61 | S/T | 0.763
72 | 110 | 1520 | 61 | ∆T | 17.2
72 | 110 | 1520 | 61 | LDB | 54.8
72 | 110 | 1520 | 61 | LWB | 52.4
72 | 110 | 1520 | 61 | kW | 4.82
77 | 110 | 1520 | 64 | MBh | 40.1
77 | 110 | 1520 | 64 | S/T | 0.731
77 | 110 | 1520 | 64 | ∆T | 17.8
77 | 110 | 1520 | 64 | LDB | 59.2
77 | 110 | 1520 | 64 | LWB | 55.2
77 | 110 | 1520 | 64 | kW | 5.41
80 | 110 | 1520 | 67 | MBh | 40.1
80 | 110 | 1520 | 67 | S/T | 0.683
80 | 110 | 1520 | 67 | ∆T | 16.7
80 | 110 | 1520 | 67 | LDB | 63.3
80 | 110 | 1520 | 67 | LWB | 58.8
80 | 110 | 1520 | 67 | kW | 5.41
84 | 110 | 1520 | 70 | MBh | 40.1
84 | 110 | 1520 | 70 | S/T | 0.656
84 | 110 | 1520 | 70 | ∆T | 16
84 | 110 | 1520 | 70 | LDB | 68
84 | 110 | 1520 | 70 | LWB | 62.4
84 | 110 | 1520 | 70 | kW | 5.41
86 | 110 | 1520 | 72 | MBh | 40.1
86 | 110 | 1520 | 72 | S/T | 0.648
86 | 110 | 1520 | 72 | ∆T | 15.8
86 | 110 | 1520 | 72 | LDB | 70.2
86 | 110 | 1520 | 72 | LWB | 64.7
86 | 110 | 1520 | 72 | kW | 5.41
90 | 110 | 1520 | 75 | MBh | 40.1
90 | 110 | 1520 | 75 | S/T | 0.613
90 | 110 | 1520 | 75 | ∆T | 15
90 | 110 | 1520 | 75 | LDB | 75
90 | 110 | 1520 | 75 | LWB | 68.3
90 | 110 | 1520 | 75 | kW | 5.41
68 | 115 | 1520 | 57 | MBh | 30.5
68 | 115 | 1520 | 57 | S/T | 0.81
68 | 115 | 1520 | 57 | ∆T | 15
68 | 115 | 1520 | 57 | LDB | 53
68 | 115 | 1520 | 57 | LWB | 49.4
68 | 115 | 1520 | 57 | kW | 3.97
72 | 115 | 1520 | 61 | MBh | 32.4
72 | 115 | 1520 | 61 | S/T | 0.765
72 | 115 | 1520 | 61 | ∆T | 15.1
72 | 115 | 1520 | 61 | LDB | 56.9
72 | 115 | 1520 | 61 | LWB | 53.5
72 | 115 | 1520 | 61 | kW | 4.32
77 | 115 | 1520 | 64 | MBh | 32.4
77 | 115 | 1520 | 64 | S/T | 0.731
77 | 115 | 1520 | 64 | ∆T | 14.4
77 | 115 | 1520 | 64 | LDB | 62.6
77 | 115 | 1520 | 64 | LWB | 57
77 | 115 | 1520 | 64 | kW | 4.32
80 | 115 | 1520 | 67 | MBh | 32.4
80 | 115 | 1520 | 67 | S/T | 0.685
80 | 115 | 1520 | 67 | ∆T | 13.5
80 | 115 | 1520 | 67 | LDB | 66.5
80 | 115 | 1520 | 67 | LWB | 60.5
80 | 115 | 1520 | 67 | kW | 4.32
84 | 115 | 1520 | 70 | MBh | 32.4
84 | 115 | 1520 | 70 | S/T | 0.654
84 | 115 | 1520 | 70 | ∆T | 12.9
84 | 115 | 1520 | 70 | LDB | 71.1
84 | 115 | 1520 | 70 | LWB | 63.9
84 | 115 | 1520 | 70 | kW | 4.32
86 | 115 | 1520 | 72 | MBh | 32.4
86 | 115 | 1520 | 72 | S/T | 0.648
86 | 115 | 1520 | 72 | ∆T | 12.8
86 | 115 | 1520 | 72 | LDB | 73.2
86 | 115 | 1520 | 72 | LWB | 66.2
86 | 115 | 1520 | 72 | kW | 4.32
90 | 115 | 1520 | 75 | MBh | 32.4
90 | 115 | 1520 | 75 | S/T | 0.614
90 | 115 | 1520 | 75 | ∆T | 12.1
90 | 115 | 1520 | 75 | LDB | 77.9
90 | 115 | 1520 | 75 | LWB | 69.6
90 | 115 | 1520 | 75 | kW | 4.32
68 | 118 | 1520 | 57 | MBh | 27.7
68 | 118 | 1520 | 57 | S/T | 0.812
68 | 118 | 1520 | 57 | ∆T | 13.7
68 | 118 | 1520 | 57 | LDB | 54.3
68 | 118 | 1520 | 57 | LWB | 50.1
68 | 118 | 1520 | 57 | kW | 3.67
72 | 118 | 1520 | 61 | MBh | 27.7
72 | 118 | 1520 | 61 | S/T | 0.769
72 | 118 | 1520 | 61 | ∆T | 13
72 | 118 | 1520 | 61 | LDB | 59
72 | 118 | 1520 | 61 | LWB | 54.7
72 | 118 | 1520 | 61 | kW | 3.67
77 | 118 | 1520 | 64 | MBh | 27.7
77 | 118 | 1520 | 64 | S/T | 0.733
77 | 118 | 1520 | 64 | ∆T | 12.4
77 | 118 | 1520 | 64 | LDB | 64.6
77 | 118 | 1520 | 64 | LWB | 58.1
77 | 118 | 1520 | 64 | kW | 3.67
80 | 118 | 1520 | 67 | MBh | 27.7
80 | 118 | 1520 | 67 | S/T | 0.686
80 | 118 | 1520 | 67 | ∆T | 11.6
80 | 118 | 1520 | 67 | LDB | 68.4
80 | 118 | 1520 | 67 | LWB | 61.5
80 | 118 | 1520 | 67 | kW | 3.67
84 | 118 | 1520 | 70 | MBh | 27.7
84 | 118 | 1520 | 70 | S/T | 0.657
84 | 118 | 1520 | 70 | ∆T | 11.1
84 | 118 | 1520 | 70 | LDB | 72.9
84 | 118 | 1520 | 70 | LWB | 64.9
84 | 118 | 1520 | 70 | kW | 3.67
86 | 118 | 1520 | 72 | MBh | 27.7
86 | 118 | 1520 | 72 | S/T | 0.65
86 | 118 | 1520 | 72 | ∆T | 11
86 | 118 | 1520 | 72 | LDB | 75
86 | 118 | 1520 | 72 | LWB | 67.1
86 | 118 | 1520 | 72 | kW | 3.67
90 | 118 | 1520 | 75 | MBh | 27.7
90 | 118 | 1520 | 75 | S/T | 0.617
90 | 118 | 1520 | 75 | ∆T | 10.4
90 | 118 | 1520 | 75 | LDB | 79.6
90 | 118 | 1520 | 75 | LWB | 70.4
90 | 118 | 1520 | 75 | kW | 3.67
68 | 122 | 1520 | 57 | MBh | 21.5
68 | 122 | 1520 | 57 | S/T | 0.814
68 | 122 | 1520 | 57 | ∆T | 10.7
68 | 122 | 1520 | 57 | LDB | 57.3
68 | 122 | 1520 | 57 | LWB | 51.7
68 | 122 | 1520 | 57 | kW | 2.82
72 | 122 | 1520 | 61 | MBh | 21.5
72 | 122 | 1520 | 61 | S/T | 0.767
72 | 122 | 1520 | 61 | ∆T | 10.1
72 | 122 | 1520 | 61 | LDB | 61.9
72 | 122 | 1520 | 61 | LWB | 56.2
72 | 122 | 1520 | 61 | kW | 2.82
77 | 122 | 1520 | 64 | MBh | 21.5
77 | 122 | 1520 | 64 | S/T | 0.735
77 | 122 | 1520 | 64 | ∆T | 9.6
77 | 122 | 1520 | 64 | LDB | 67.4
77 | 122 | 1520 | 64 | LWB | 59.5
77 | 122 | 1520 | 64 | kW | 2.82
80 | 122 | 1520 | 67 | MBh | 21.5
80 | 122 | 1520 | 67 | S/T | 0.688
80 | 122 | 1520 | 67 | ∆T | 9
80 | 122 | 1520 | 67 | LDB | 71
80 | 122 | 1520 | 67 | LWB | 62.8
80 | 122 | 1520 | 67 | kW | 2.82
84 | 122 | 1520 | 70 | MBh | 21.5
84 | 122 | 1520 | 70 | S/T | 0.66
84 | 122 | 1520 | 70 | ∆T | 8.7
84 | 122 | 1520 | 70 | LDB | 75.3
84 | 122 | 1520 | 70 | LWB | 66.1
84 | 122 | 1520 | 70 | kW | 2.82
86 | 122 | 1520 | 72 | MBh | 21.5
86 | 122 | 1520 | 72 | S/T | 0.651
86 | 122 | 1520 | 72 | ∆T | 8.5
86 | 122 | 1520 | 72 | LDB | 77.5
86 | 122 | 1520 | 72 | LWB | 68.2
86 | 122 | 1520 | 72 | kW | 2.82
90 | 122 | 1520 | 75 | MBh | 21.5
90 | 122 | 1520 | 75 | S/T | 0.619
90 | 122 | 1520 | 75 | ∆T | 8.1
90 | 122 | 1520 | 75 | LDB | 81.9
90 | 122 | 1520 | 75 | LWB | 71.5
90 | 122 | 1520 | 75 | kW | 2.82