## SCHEDULE
SCHEDULE RANGE | [16 empty] | FILTERS |  |  |  |  | DOCUMENTATION
VERTICAL WALL MOUNTED PACKAGED AIR HANDLING UNIT SCHEDULE | [16 empty] | TONS | ELECTRICAL | STAGES | HEAT PUMP OR AC | ELECTRIC HEAT | SUBMITTAL (OUTDOOR UNIT) | SUBMITTAL (INDOOR UNIT) | SUBMITTAL (SYSTEM) | ENGINEERING MANUAL (SYSTEM) | ENGINEERING MANUAL (OUTDOOR UNIT) | ENGINEERING MANUAL (INDOOR UNIT) | CAPACITY TABLE | INSTALLATION MANUAL (OUTDOOR) | INSTALLATION MANUAL (INDOOR) | INSTALLATION MANUAL (SYSTEM) | REVIT (OUTDOOR) | REVIT (INDOOR) | REVIT (SYSTEM) | CAD (OUTDOOR) | CAD (INDOOR) | CAD (SYSTEM) | CONTROLS OPTIONS | OPERATION MANUAL
MAKE | MODEL | NOMINAL SIZE (TONS) | CFM | TOTAL CAPACITY | SENSIBLE CAPACITY | COOLING STAGES | OUTSIDE AIR (°F) | ENTERING AIR DB/WB (°F) | HEAT PUMP CAPACITY (47ºF AMBIENT) | AUX. ELECTRIC HEAT (KW) | VOLTS-HZ-PH | MCA | MOCP | REFRIGERANT | EER | IEER
MARVAIR | MGH3090AA | 7.5 | 3500 | 89000 | 69092 | 2 | 95 | 80/67 | - | 0 | 208/60/1 | 54.5 | 60 | R-454B | 11.2 | 11.8 | 7.5 | 208/60/1 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3090AA | 7.5 | 3500 | 89000 | 69092 | 2 | 95 | 80/67 | - | 5 | 208/60/1 | 57.6 | 70 | R-454B | 11.2 | 11.8 | 7.5 | 208/60/1 | 2 | COOLING ONLY | 5 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3090AA | 7.5 | 3500 | 89000 | 69092 | 2 | 95 | 80/67 | - | 10 | 208/60/1 | 83.7 | 90 | R-454B | 11.2 | 11.8 | 7.5 | 208/60/1 | 2 | COOLING ONLY | 10 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3090AA | 7.5 | 3500 | 89000 | 69092 | 2 | 95 | 80/67 | - | 15 | 208/60/1 | 109.7 | 110 | R-454B | 11.2 | 11.8 | 7.5 | 208/60/1 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3090AC | 7.5 | 3500 | 89000 | 69092 | 2 | 95 | 80/67 | - | 0 | 208/60/3 | 38.5 | 40 | R-454B | 11.2 | 11.8 | 7.5 | 208/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3090AC | 7.5 | 3500 | 89000 | 69092 | 2 | 95 | 80/67 | - | 9 | 208/60/3 | 50.6 | 60 | R-454B | 11.2 | 11.8 | 7.5 | 208/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3090AC | 7.5 | 3500 | 89000 | 69092 | 2 | 95 | 80/67 | - | 15 | 208/60/3 | 68.7 | 70 | R-454B | 11.2 | 11.8 | 7.5 | 208/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3090AC | 7.5 | 3500 | 89000 | 69092 | 2 | 95 | 80/67 | - | 18 | 208/60/3 | 77.7 | 80 | R-454B | 11.2 | 11.8 | 7.5 | 208/60/3 | 2 | COOLING ONLY | 18 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3090AD | 7.5 | 3500 | 89000 | 69092 | 2 | 95 | 80/67 | - | 0 | 460/60/3 | 21.4 | 25 | R-454B | 11.2 | 11.8 | 7.5 | 460/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3090AD | 7.5 | 3500 | 89000 | 69092 | 2 | 95 | 80/67 | - | 9 | 460/60/3 | 26.4 | 30 | R-454B | 11.2 | 11.8 | 7.5 | 460/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3090AD | 7.5 | 3500 | 89000 | 69092 | 2 | 95 | 80/67 | - | 15 | 460/60/3 | 35.4 | 40 | R-454B | 11.2 | 11.8 | 7.5 | 460/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3090AD | 7.5 | 3500 | 89000 | 69092 | 2 | 95 | 80/67 | - | 18 | 460/60/3 | 39.9 | 40 | R-454B | 11.2 | 11.8 | 7.5 | 460/60/3 | 2 | COOLING ONLY | 18 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3120AA | 10 | 4000 | 118000 | 91706 | 2 | 95 | 80/67 | - | 0 | 208/60/1 | 82.3 | 90 | R-454B | 11.6 | 11.5 | 10 | 208/60/1 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3120AA | 10 | 4000 | 118000 | 91706 | 2 | 95 | 80/67 | - | 5 | 208/60/1 | 82.3 | 90 | R-454B | 11.6 | 11.5 | 10 | 208/60/1 | 2 | COOLING ONLY | 5 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3120AA | 10 | 4000 | 118000 | 91706 | 2 | 95 | 80/67 | - | 10 | 208/60/1 | 102.9 | 110 | R-454B | 11.6 | 11.5 | 10 | 208/60/1 | 2 | COOLING ONLY | 10 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3120AA | 10 | 4000 | 118000 | 91706 | 2 | 95 | 80/67 | - | 15 | 208/60/1 | 128.9 | 150 | R-454B | 11.6 | 11.5 | 10 | 208/60/1 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3120AC | 10 | 4000 | 118000 | 91706 | 2 | 95 | 80/67 | - | 0 | 208/60/3 | 57.5 | 60 | R-454B | 11.6 | 11.5 | 10 | 208/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3120AC | 10 | 4000 | 118000 | 91706 | 2 | 95 | 80/67 | - | 9 | 208/60/3 | 67.3 | 70 | R-454B | 11.6 | 11.5 | 10 | 208/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3120AC | 10 | 4000 | 118000 | 91706 | 2 | 95 | 80/67 | - | 15 | 208/60/3 | 85.4 | 90 | R-454B | 11.6 | 11.5 | 10 | 208/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3120AC | 10 | 4000 | 118000 | 91706 | 2 | 95 | 80/67 | - | 18 | 208/60/3 | 94.4 | 100 | R-454B | 11.6 | 11.5 | 10 | 208/60/3 | 2 | COOLING ONLY | 18 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3120AD | 10 | 4000 | 118000 | 91706 | 2 | 95 | 80/67 | - | 0 | 460/60/3 | 28.5 | 30 | R-454B | 11.6 | 11.5 | 10 | 460/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3120AD | 10 | 4000 | 118000 | 91706 | 2 | 95 | 80/67 | - | 9 | 460/60/3 | 33.4 | 35 | R-454B | 11.6 | 11.5 | 10 | 460/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3120AD | 10 | 4000 | 118000 | 91706 | 2 | 95 | 80/67 | - | 15 | 460/60/3 | 42.4 | 45 | R-454B | 11.6 | 11.5 | 10 | 460/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3120AD | 10 | 4000 | 118000 | 91706 | 2 | 95 | 80/67 | - | 18 | 460/60/3 | 46.9 | 50 | R-454B | 11.6 | 11.5 | 10 | 460/60/3 | 2 | COOLING ONLY | 18 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3150AC | 12.5 | 4500 | 146000 | 106434 | 2 | 95 | 80/67 | - | 0 | 208/60/3 | 81 | 90 | R-454B | 10.2 | 10.9 | 12.5 | 208/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3150AC | 12.5 | 4500 | 146000 | 106434 | 2 | 95 | 80/67 | - | 9 | 208/60/3 | 81 | 90 | R-454B | 10.2 | 10.9 | 12.5 | 208/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3150AC | 12.5 | 4500 | 146000 | 106434 | 2 | 95 | 80/67 | - | 15 | 208/60/3 | 97.1 | 110 | R-454B | 10.2 | 10.9 | 12.5 | 208/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3150AC | 12.5 | 4500 | 146000 | 106434 | 2 | 95 | 80/67 | - | 18 | 208/60/3 | 106.1 | 110 | R-454B | 10.2 | 10.9 | 12.5 | 208/60/3 | 2 | COOLING ONLY | 18 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3150AD | 12.5 | 4500 | 146000 | 106434 | 2 | 95 | 80/67 | - | 0 | 460/60/3 | 35 | 35 | R-454B | 10.2 | 10.9 | 12.5 | 460/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3150AD | 12.5 | 4500 | 146000 | 106434 | 2 | 95 | 80/67 | - | 9 | 460/60/3 | 36.6 | 40 | R-454B | 10.2 | 10.9 | 12.5 | 460/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3150AD | 12.5 | 4500 | 146000 | 106434 | 2 | 95 | 80/67 | - | 15 | 460/60/3 | 45.6 | 50 | R-454B | 10.2 | 10.9 | 12.5 | 460/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3150AD | 12.5 | 4500 | 146000 | 106434 | 2 | 95 | 80/67 | - | 18 | 460/60/3 | 50.1 | 60 | R-454B | 10.2 | 10.9 | 12.5 | 460/60/3 | 2 | COOLING ONLY | 18 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3180AC | 15 | 6000 | 182000 | 136830 | 2 | 95 | 80/67 | - | 0 | 208/60/3 | 100.4 | 110 | R-454B | 9.8 | 11.1 | 15 | 208/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3180AC | 15 | 6000 | 182000 | 136830 | 2 | 95 | 80/67 | - | 9 | 208/60/3 | 100.4 | 110 | R-454B | 9.8 | 11.1 | 15 | 208/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3180AC | 15 | 6000 | 182000 | 136830 | 2 | 95 | 80/67 | - | 15 | 208/60/3 | 112 | 125 | R-454B | 9.8 | 11.1 | 15 | 208/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3180AC | 15 | 6000 | 182000 | 136830 | 2 | 95 | 80/67 | - | 18 | 208/60/3 | 121 | 125 | R-454B | 9.8 | 11.1 | 15 | 208/60/3 | 2 | COOLING ONLY | 18 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3180AD | 15 | 6000 | 182000 | 136830 | 2 | 95 | 80/67 | - | 0 | 460/60/3 | 47.7 | 50 | R-454B | 9.8 | 11.1 | 15 | 460/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3180AD | 15 | 6000 | 182000 | 136830 | 2 | 95 | 80/67 | - | 9 | 460/60/3 | 47.7 | 50 | R-454B | 9.8 | 11.1 | 15 | 460/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3180AD | 15 | 6000 | 182000 | 136830 | 2 | 95 | 80/67 | - | 15 | 460/60/3 | 54.6 | 60 | R-454B | 9.8 | 11.1 | 15 | 460/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MGH3180AD | 15 | 6000 | 182000 | 136830 | 2 | 95 | 80/67 | - | 18 | 460/60/3 | 59.1 | 60 | R-454B | 9.8 | 11.1 | 15 | 460/60/3 | 2 | COOLING ONLY | 18 |  |  | MARVAIR MGH DATA SHEET | [6 empty] | MARVAIR MGH IOM
MARVAIR | MAH1018A | 1.5 | 660 | 17500 | 13472 | 1 | 95 | 80/67 | - | 0 | 208/60/1 | 14.8 | 20 | R-454B | 11 | - | 1.5 | 208/60/1 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1020A | 1.66 | 760 | 20000 | 15619 | 1 | 95 | 80/67 | - | 0 | 208/60/1 | 19.2 | 25 | R-454B | 11 | - | 1.66 | 208/60/1 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 0 | 208/60/1 | 21.2 | 30 | R-454B | 11 | - | 2 | 208/60/1 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 0 | 208/60/1 | 23.2 | 35 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 0 | 208/60/1 | 24.7 | 35 | R-454B | 11 | - | 3 | 208/60/1 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 0 | 208/60/1 | 32.7 | 50 | R-454B | 11.5 | - | 3.5 | 208/60/1 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 0 | 208/60/1 | 39.3 | 60 | R-454B | 11 | - | 4 | 208/60/1 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 0 | 208/60/1 | 40.9 | 60 | R-454B | 11 | - | 5 | 208/60/1 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 0 | 208/60/1 | 51.1 | 80 | R-454B | 11 | - | 6 | 208/60/1 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 0 | 208/60/3 | 16.7 | 20 | R-454B | 11 | - | 2 | 208/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 0 | 208/60/3 | 22.3 | 35 | R-454B | 11 | - | 2.5 | 208/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 0 | 208/60/3 | 21.6 | 30 | R-454B | 11 | - | 3 | 208/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 0 | 208/60/3 | 25.4 | 35 | R-454B | 11.5 | - | 3.5 | 208/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 0 | 208/60/3 | 27.3 | 40 | R-454B | 11 | - | 4 | 208/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 0 | 208/60/3 | 31.3 | 45 | R-454B | 11 | - | 5 | 208/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 0 | 208/60/3 | 38.1 | 60 | R-454B | 11 | - | 6 | 208/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 0 | 460/60/3 | 9.5 | 15 | R-454B | 11 | - | 2 | 460/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 0 | 460/60/3 | 9.6 | 15 | R-454B | 11 | - | 2.5 | 460/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 0 | 460/60/3 | 11.2 | 15 | R-454B | 11 | - | 3 | 460/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 0 | 460/60/3 | 12 | 15 | R-454B | 11.5 | - | 3.5 | 460/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 0 | 460/60/3 | 13.2 | 15 | R-454B | 11 | - | 4 | 460/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 0 | 460/60/3 | 14.5 | 20 | R-454B | 11 | - | 5 | 460/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 0 | 460/60/3 | 16.1 | 20 | R-454B | 11 | - | 6 | 460/60/3 | 1 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1018A | 1.5 | 660 | 17500 | 13472 | 1 | 95 | 80/67 | - | 2.2 | 208/60/1 | 26.2 | 30 | R-454B | 11 | - | 1.5 | 208/60/1 | 1 | COOLING ONLY | 2.2 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1018A | 1.5 | 660 | 17500 | 13472 | 1 | 95 | 80/67 | - | 3.6 | 208/60/1 | 33.5 | 35 | R-454B | 11 | - | 1.5 | 208/60/1 | 1 | COOLING ONLY | 3.6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1020A | 1.66 | 760 | 20000 | 15619 | 1 | 95 | 80/67 | - | 4 | 208/60/1 | 40 | 45 | R-454B | 11 | - | 1.66 | 208/60/1 | 1 | COOLING ONLY | 4 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1020A | 1.66 | 760 | 20000 | 15619 | 1 | 95 | 80/67 | - | 5 | 208/60/1 | 45.2 | 50 | R-454B | 11 | - | 1.66 | 208/60/1 | 1 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1020A | 1.66 | 760 | 20000 | 15619 | 1 | 95 | 80/67 | - | 6 | 208/60/1 | 50.4 | 60 | R-454B | 11 | - | 1.66 | 208/60/1 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1020A | 1.66 | 760 | 20000 | 15619 | 1 | 95 | 80/67 | - | 8 | 208/60/1 | 60.8 | 70 | R-454B | 11 | - | 1.66 | 208/60/1 | 1 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1020A | 1.66 | 760 | 20000 | 15619 | 1 | 95 | 80/67 | - | 10 | 208/60/1 | 71.3 | 80 | R-454B | 11 | - | 1.66 | 208/60/1 | 1 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 4 | 208/60/1 | 42 | 45 | R-454B | 11 | - | 2 | 208/60/1 | 1 | COOLING ONLY | 4 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 5 | 208/60/1 | 47.2 | 50 | R-454B | 11 | - | 2 | 208/60/1 | 1 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 6 | 208/60/1 | 52.4 | 60 | R-454B | 11 | - | 2 | 208/60/1 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 8 | 208/60/1 | 62.8 | 70 | R-454B | 11 | - | 2 | 208/60/1 | 1 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 10 | 208/60/1 | 73.3 | 80 | R-454B | 11 | - | 2 | 208/60/1 | 1 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 4 | 208/60/1 | 44 | 50 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | COOLING ONLY | 4 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 5 | 208/60/1 | 49.2 | 50 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 6 | 208/60/1 | 54.4 | 60 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 8 | 208/60/1 | 64.8 | 70 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 10 | 208/60/1 | 75.3 | 80 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 12 | 208/60/1 | 85.7 | 90 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 15 | 208/60/1 | 101.3 | 110 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 4 | 208/60/1 | 45.5 | 50 | R-454B | 11 | - | 3 | 208/60/1 | 1 | COOLING ONLY | 4 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 5 | 208/60/1 | 50.7 | 60 | R-454B | 11 | - | 3 | 208/60/1 | 1 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 6 | 208/60/1 | 55.9 | 60 | R-454B | 11 | - | 3 | 208/60/1 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 8 | 208/60/1 | 66.3 | 70 | R-454B | 11 | - | 3 | 208/60/1 | 1 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 10 | 208/60/1 | 76.8 | 80 | R-454B | 11 | - | 3 | 208/60/1 | 1 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 12 | 208/60/1 | 87.2 | 90 | R-454B | 11 | - | 3 | 208/60/1 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 15 | 208/60/1 | 102.8 | 110 | R-454B | 11 | - | 3 | 208/60/1 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 5 | 208/60/1 | 58.7 | 90 | R-454B | 11.5 | - | 3.5 | 208/60/1 | 1 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 6 | 208/60/1 | 63.9 | 90 | R-454B | 11.5 | - | 3.5 | 208/60/1 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 8 | 208/60/1 | 74.3 | 80 | R-454B | 11.5 | - | 3.5 | 208/60/1 | 1 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 10 | 208/60/1 | 84.7 | 90 | R-454B | 11.5 | - | 3.5 | 208/60/1 | 1 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 12 | 208/60/1 | 95.2 | 100 | R-454B | 11.5 | - | 3.5 | 208/60/1 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 15 | 208/60/1 | 110.8 | 125 | R-454B | 11.5 | - | 3.5 | 208/60/1 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 5 | 208/60/1 | 65.3 | 80 | R-454B | 11 | - | 4 | 208/60/1 | 1 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 6 | 208/60/1 | 70.6 | 80 | R-454B | 11 | - | 4 | 208/60/1 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 8 | 208/60/1 | 81 | 90 | R-454B | 11 | - | 4 | 208/60/1 | 1 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 10 | 208/60/1 | 91.4 | 100 | R-454B | 11 | - | 4 | 208/60/1 | 1 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 12 | 208/60/1 | 101.8 | 110 | R-454B | 11 | - | 4 | 208/60/1 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 15 | 208/60/1 | 117.4 | 125 | R-454B | 11 | - | 4 | 208/60/1 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 5 | 208/60/1 | 67 | 80 | R-454B | 11 | - | 5 | 208/60/1 | 1 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 6 | 208/60/1 | 72.2 | 80 | R-454B | 11 | - | 5 | 208/60/1 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 8 | 208/60/1 | 82.6 | 90 | R-454B | 11 | - | 5 | 208/60/1 | 1 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 10 | 208/60/1 | 93 | 100 | R-454B | 11 | - | 5 | 208/60/1 | 1 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 12 | 208/60/1 | 103.4 | 110 | R-454B | 11 | - | 5 | 208/60/1 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 15 | 208/60/1 | 119.1 | 125 | R-454B | 11 | - | 5 | 208/60/1 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 5 | 208/60/1 | 77.1 | 100 | R-454B | 11 | - | 6 | 208/60/1 | 1 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 6 | 208/60/1 | 82.4 | 100 | R-454B | 11 | - | 6 | 208/60/1 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 8 | 208/60/1 | 92.8 | 110 | R-454B | 11 | - | 6 | 208/60/1 | 1 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 10 | 208/60/1 | 103.2 | 125 | R-454B | 11 | - | 6 | 208/60/1 | 1 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 12 | 208/60/1 | 113.6 | 125 | R-454B | 11 | - | 6 | 208/60/1 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 15 | 208/60/1 | 129.2 | 150 | R-454B | 11 | - | 6 | 208/60/1 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 6 | 208/60/3 | 34.7 | 35 | R-454B | 11 | - | 2 | 208/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 9 | 208/60/3 | 43.7 | 45 | R-454B | 11 | - | 2 | 208/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 12 | 208/60/3 | 52.8 | 60 | R-454B | 11 | - | 2 | 208/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 6 | 208/60/3 | 40.3 | 45 | R-454B | 11 | - | 2.5 | 208/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 9 | 208/60/3 | 49.4 | 50 | R-454B | 11 | - | 2.5 | 208/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 12 | 208/60/3 | 58.4 | 60 | R-454B | 11 | - | 2.5 | 208/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 15 | 208/60/3 | 67.4 | 70 | R-454B | 11 | - | 2.5 | 208/60/3 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 6 | 208/60/3 | 39.6 | 45 | R-454B | 11 | - | 3 | 208/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 9 | 208/60/3 | 48.6 | 50 | R-454B | 11 | - | 3 | 208/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 12 | 208/60/3 | 57.6 | 60 | R-454B | 11 | - | 3 | 208/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 15 | 208/60/3 | 66.7 | 70 | R-454B | 11 | - | 3 | 208/60/3 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 6 | 208/60/3 | 43.4 | 50 | R-454B | 11.5 | - | 3.5 | 208/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 9 | 208/60/3 | 52.5 | 60 | R-454B | 11.5 | - | 3.5 | 208/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 12 | 208/60/3 | 61.5 | 70 | R-454B | 11.5 | - | 3.5 | 208/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 15 | 208/60/3 | 70.5 | 80 | R-454B | 11.5 | - | 3.5 | 208/60/3 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 6 | 208/60/1 | 45.3 | 50 | R-454B | 11 | - | 4 | 208/60/1 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 9 | 208/60/1 | 54.4 | 60 | R-454B | 11 | - | 4 | 208/60/1 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 12 | 208/60/1 | 63.4 | 70 | R-454B | 11 | - | 4 | 208/60/1 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 15 | 208/60/1 | 72.4 | 80 | R-454B | 11 | - | 4 | 208/60/1 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 6 | 208/60/3 | 49.3 | 60 | R-454B | 11 | - | 5 | 208/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 9 | 208/60/3 | 58.4 | 60 | R-454B | 11 | - | 5 | 208/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 12 | 208/60/3 | 67.4 | 70 | R-454B | 11 | - | 5 | 208/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 15 | 208/60/3 | 76.4 | 80 | R-454B | 11 | - | 5 | 208/60/3 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 6 | 208/60/3 | 56.1 | 70 | R-454B | 11 | - | 6 | 208/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 9 | 208/60/3 | 65.2 | 80 | R-454B | 11 | - | 6 | 208/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 12 | 208/60/3 | 74.2 | 80 | R-454B | 11 | - | 6 | 208/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 15 | 208/60/3 | 83.2 | 90 | R-454B | 11 | - | 6 | 208/60/3 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 6 | 460/60/3 | 18.5 | 20 | R-454B | 11 | - | 2 | 460/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 9 | 460/60/3 | 23.1 | 25 | R-454B | 11 | - | 2 | 460/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1024A | 2 | 850 | 24000 | 17703 | 1 | 95 | 80/67 | - | 12 | 460/60/3 | 27.6 | 30 | R-454B | 11 | - | 2 | 460/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 6 | 460/60/3 | 18.6 | 20 | R-454B | 11 | - | 2.5 | 460/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 9 | 460/60/3 | 23.2 | 25 | R-454B | 11 | - | 2.5 | 460/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 12 | 460/60/3 | 27.7 | 30 | R-454B | 11 | - | 2.5 | 460/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1030A | 2.5 | 1070 | 29000 | 21994 | 1 | 95 | 80/67 | - | 15 | 460/60/3 | 32.2 | 35 | R-454B | 11 | - | 2.5 | 460/60/3 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 6 | 460/60/3 | 20.2 | 25 | R-454B | 11 | - | 3 | 460/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 9 | 460/60/3 | 24.7 | 25 | R-454B | 11 | - | 3 | 460/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 12 | 460/60/3 | 29.2 | 30 | R-454B | 11 | - | 3 | 460/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1036A | 3 | 1200 | 35000 | 24980 | 1 | 95 | 80/67 | - | 15 | 460/60/3 | 33.7 | 35 | R-454B | 11 | - | 3 | 460/60/3 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 6 | 460/60/3 | 21 | 25 | R-454B | 11.5 | - | 3.5 | 460/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 9 | 460/60/3 | 25.5 | 30 | R-454B | 11.5 | - | 3.5 | 460/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 12 | 460/60/3 | 30 | 30 | R-454B | 11.5 | - | 3.5 | 460/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1042A | 3.5 | 1250 | 41000 | 29022 | 1 | 95 | 80/67 | - | 15 | 460/60/3 | 34.5 | 35 | R-454B | 11.5 | - | 3.5 | 460/60/3 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 6 | 460/60/3 | 22.2 | 25 | R-454B | 11 | - | 4 | 460/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 9 | 460/60/3 | 26.7 | 30 | R-454B | 11 | - | 4 | 460/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 12 | 460/60/3 | 31.2 | 35 | R-454B | 11 | - | 4 | 460/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1048A | 4 | 1400 | 45000 | 31964 | 1 | 95 | 80/67 | - | 15 | 460/60/3 | 35.7 | 40 | R-454B | 11 | - | 4 | 460/60/3 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 6 | 460/60/3 | 23.5 | 25 | R-454B | 11 | - | 5 | 460/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 9 | 460/60/3 | 28.1 | 30 | R-454B | 11 | - | 5 | 460/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 12 | 460/60/3 | 32.6 | 35 | R-454B | 11 | - | 5 | 460/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1060A | 5 | 1750 | 54600 | 38972 | 1 | 95 | 80/67 | - | 15 | 460/60/3 | 37.1 | 40 | R-454B | 11 | - | 5 | 460/60/3 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 6 | 460/60/3 | 25.1 | 30 | R-454B | 11 | - | 6 | 460/60/3 | 1 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 9 | 460/60/3 | 29.6 | 35 | R-454B | 11 | - | 6 | 460/60/3 | 1 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 12 | 460/60/3 | 34.1 | 35 | R-454B | 11 | - | 6 | 460/60/3 | 1 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH1072A | 6 | 2000 | 70000 | 45709 | 1 | 95 | 80/67 | - | 15 | 460/60/3 | 38.6 | 40 | R-454B | 11 | - | 6 | 460/60/3 | 1 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 0 | 208/60/1 | 19.2 | 25 | R-454B | 11 | - | 2 | 208/60/1 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 0 | 208/60/1 | 24.6 | 35 | R-454B | 11 | - | 2.5 | 208/60/1 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 0 | 208/60/1 | 24.3 | 35 | R-454B | 11 | - | 3 | 208/60/1 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 0 | 208/60/1 | 32.2 | 50 | R-454B | 11 | - | 3.5 | 208/60/1 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 0 | 208/60/1 | 34.2 | 50 | R-454B | 11 | - | 4 | 208/60/1 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 0 | 208/60/1 | 42.8 | 60 | R-454B | 11 | - | 5 | 208/60/1 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH2072A | 6 | 2100 | 66000 | 42000 | 2 | 95 | 80/67 | - | 0 | 208/60/1 | 38.3 | 60 | R-454B | 10 | - | 6 | 208/60/1 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 0 | 208/60/3 | 14.2 | 20 | R-454B | 11 | - | 2 | 208/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 0 | 208/60/3 | 16.2 | 20 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 0 | 208/60/3 | 18.7 | 25 | R-454B | 11 | - | 3 | 208/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 0 | 208/60/3 | 23.8 | 35 | R-454B | 11 | - | 3.5 | 208/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 0 | 208/60/3 | 26.2 | 35 | R-454B | 11 | - | 4 | 208/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 0 | 208/60/3 | 28.6 | 40 | R-454B | 11 | - | 5 | 208/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH2072A | 6 | 2100 | 66000 | 42000 | 2 | 95 | 80/67 | - | 0 | 208/60/3 | 39.1 | 60 | R-454B | 10 | - | 6 | 208/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 0 | 460/60/3 | 7.9 | 15 | R-454B | 11 | - | 2 | 460/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 0 | 460/60/3 | 9.3 | 15 | R-454B | 11 | - | 2.5 | 460/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 0 | 460/60/3 | 9.9 | 15 | R-454B | 11 | - | 3 | 460/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 0 | 460/60/3 | 12.8 | 15 | R-454B | 11 | - | 3.5 | 460/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 0 | 460/60/3 | 14.2 | 20 | R-454B | 11 | - | 4 | 460/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 0 | 460/60/3 | 14.3 | 20 | R-454B | 11 | - | 5 | 460/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH2072A | 6 | 2100 | 66000 | 42000 | 2 | 95 | 80/67 | - | 0 | 460/60/3 | 16.9 | 25 | R-454B | 10 | - | 6 | 460/60/3 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 4 | 208/60/1 | 23.6 | 25 | R-454B | 11 | - | 2 | 208/60/1 | 2 | COOLING ONLY | 4 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 5 | 208/60/1 | 28.8 | 30 | R-454B | 11 | - | 2 | 208/60/1 | 2 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 6 | 208/60/1 | 34.1 | 35 | R-454B | 11 | - | 2 | 208/60/1 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 8 | 208/60/1 | 44.5 | 45 | R-454B | 11 | - | 2 | 208/60/1 | 2 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 10 | 208/60/1 | 54.9 | 60 | R-454B | 11 | - | 2 | 208/60/1 | 2 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 4 | 208/60/3 | 24.9 | 35 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 | COOLING ONLY | 4 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 5 | 208/60/3 | 30.1 | 35 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 6 | 208/60/3 | 35.4 | 40 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 8 | 208/60/3 | 45.8 | 50 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 10 | 208/60/3 | 56.2 | 60 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 12 | 208/60/3 | 66.6 | 70 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 15 | 208/60/3 | 82.2 | 90 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 4 | 208/60/1 | 24.9 | 35 | R-454B | 11 | - | 3 | 208/60/1 | 2 | COOLING ONLY | 4 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 5 | 208/60/1 | 30.1 | 35 | R-454B | 11 | - | 3 | 208/60/1 | 2 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 6 | 208/60/1 | 35.4 | 40 | R-454B | 11 | - | 3 | 208/60/1 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 8 | 208/60/1 | 45.8 | 50 | R-454B | 11 | - | 3 | 208/60/1 | 2 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 10 | 208/60/1 | 56.2 | 60 | R-454B | 11 | - | 3 | 208/60/1 | 2 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 12 | 208/60/1 | 66.6 | 70 | R-454B | 11 | - | 3 | 208/60/1 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 15 | 208/60/1 | 82.2 | 90 | R-454B | 11 | - | 3 | 208/60/1 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 4 | 208/60/1 | 32.2 | 50 | R-454B | 11 | - | 3.5 | 208/60/1 | 2 | COOLING ONLY | 4 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 5 | 208/60/1 | 32.2 | 50 | R-454B | 11 | - | 3.5 | 208/60/1 | 2 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 6 | 208/60/1 | 35.4 | 50 | R-454B | 11 | - | 3.5 | 208/60/1 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 8 | 208/60/1 | 45.8 | 50 | R-454B | 11 | - | 3.5 | 208/60/1 | 2 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 10 | 208/60/1 | 56.2 | 60 | R-454B | 11 | - | 3.5 | 208/60/1 | 2 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 12 | 208/60/1 | 66.6 | 70 | R-454B | 11 | - | 3.5 | 208/60/1 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 15 | 208/60/1 | 82.2 | 80 | R-454B | 11 | - | 3.5 | 208/60/1 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 4 | 208/60/1 | 34.2 | 50 | R-454B | 11 | - | 4 | 208/60/1 | 2 | COOLING ONLY | 4 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 5 | 208/60/1 | 34.2 | 50 | R-454B | 11 | - | 4 | 208/60/1 | 2 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 6 | 208/60/1 | 37.3 | 50 | R-454B | 11 | - | 4 | 208/60/1 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 8 | 208/60/1 | 47.7 | 50 | R-454B | 11 | - | 4 | 208/60/1 | 2 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 10 | 208/60/1 | 58.1 | 60 | R-454B | 11 | - | 4 | 208/60/1 | 2 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 12 | 208/60/1 | 68.5 | 70 | R-454B | 11 | - | 4 | 208/60/1 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 15 | 208/60/1 | 84.1 | 90 | R-454B | 11 | - | 4 | 208/60/1 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 4 | 208/60/1 | 42.8 | 60 | R-454B | 11 | - | 5 | 208/60/1 | 2 | COOLING ONLY | 4 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 5 | 208/60/1 | 42.8 | 60 | R-454B | 11 | - | 5 | 208/60/1 | 2 | COOLING ONLY | 5 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 6 | 208/60/1 | 42.8 | 60 | R-454B | 11 | - | 5 | 208/60/1 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 8 | 208/60/1 | 47.7 | 60 | R-454B | 11 | - | 5 | 208/60/1 | 2 | COOLING ONLY | 8 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 10 | 208/60/1 | 58.1 | 60 | R-454B | 11 | - | 5 | 208/60/1 | 2 | COOLING ONLY | 10 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 12 | 208/60/1 | 68.5 | 70 | R-454B | 11 | - | 5 | 208/60/1 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 15 | 208/60/1 | 84.1 | 90 | R-454B | 11 | - | 5 | 208/60/1 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH2072A | 6 | 2100 | 66000 | 42000 | 2 | 95 | 80/67 | - | 0 | 208/60/1 | 38.3 | 60 | R-454B | 10 | - | 6 | 208/60/1 | 2 | COOLING ONLY | 0 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 6 | 208/60/3 | 20.8 | 25 | R-454B | 11 | - | 2 | 208/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 9 | 208/60/3 | 29.9 | 30 | R-454B | 11 | - | 2 | 208/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 12 | 208/60/3 | 38.9 | 40 | R-454B | 11 | - | 2 | 208/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 15 | 208/60/3 | 47.9 | 50 | R-454B | 11 | - | 2 | 208/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 6 | 208/60/3 | 22.1 | 25 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 9 | 208/60/3 | 31.2 | 35 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 12 | 208/60/3 | 40.2 | 45 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 15 | 208/60/3 | 49.2 | 50 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 6 | 208/60/3 | 22.1 | 25 | R-454B | 11 | - | 3 | 208/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 9 | 208/60/3 | 31.2 | 35 | R-454B | 11 | - | 3 | 208/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 12 | 208/60/3 | 40.2 | 45 | R-454B | 11 | - | 3 | 208/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 15 | 208/60/3 | 49.2 | 50 | R-454B | 11 | - | 3 | 208/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 6 | 208/60/3 | 23.8 | 35 | R-454B | 11 | - | 3.5 | 208/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 9 | 208/60/3 | 31.2 | 35 | R-454B | 11 | - | 3.5 | 208/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 12 | 208/60/3 | 40.2 | 45 | R-454B | 11 | - | 3.5 | 208/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 15 | 208/60/3 | 49.2 | 50 | R-454B | 11 | - | 3.5 | 208/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 6 | 208/60/3 | 26.2 | 35 | R-454B | 11 | - | 4 | 208/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 9 | 208/60/3 | 33.1 | 35 | R-454B | 11 | - | 4 | 208/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 12 | 208/60/3 | 42.1 | 45 | R-454B | 11 | - | 4 | 208/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 15 | 208/60/3 | 51.1 | 60 | R-454B | 11 | - | 4 | 208/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 6 | 208/60/3 | 28.6 | 40 | R-454B | 11 | - | 5 | 208/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 9 | 208/60/3 | 33.1 | 40 | R-454B | 11 | - | 5 | 208/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 12 | 208/60/3 | 42.1 | 45 | R-454B | 11 | - | 5 | 208/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 15 | 208/60/3 | 51.1 | 60 | R-454B | 11 | - | 5 | 208/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH2072A | 6 | 2100 | 66000 | 42000 | 2 | 95 | 80/67 | - | 6 | 208/60/3 | 39.1 | 60 | R-454B | 10 | - | 6 | 208/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH2072A | 6 | 2100 | 66000 | 42000 | 2 | 95 | 80/67 | - | 9 | 208/60/3 | 39.1 | 60 | R-454B | 10 | - | 6 | 208/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH2072A | 6 | 2100 | 66000 | 42000 | 2 | 95 | 80/67 | - | 12 | 208/60/3 | 42.9 | 60 | R-454B | 10 | - | 6 | 208/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH2072A | 6 | 2100 | 66000 | 42000 | 2 | 95 | 80/67 | - | 15 | 208/60/3 | 51.9 | 60 | R-454B | 10 | - | 6 | 208/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 6 | 460/60/3 | 10.4 | 15 | R-454B | 11 | - | 2 | 460/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 9 | 460/60/3 | 14.9 | 15 | R-454B | 11 | - | 2 | 460/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 12 | 460/60/3 | 19.4 | 20 | R-454B | 11 | - | 2 | 460/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2024A | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | - | 15 | 460/60/3 | 24 | 25 | R-454B | 11 | - | 2 | 460/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 6 | 460/60/3 | 11.2 | 15 | R-454B | 11 | - | 2.5 | 460/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 9 | 460/60/3 | 15.7 | 20 | R-454B | 11 | - | 2.5 | 460/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 12 | 460/60/3 | 20.2 | 25 | R-454B | 11 | - | 2.5 | 460/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2030A | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | - | 15 | 460/60/3 | 24.7 | 25 | R-454B | 11 | - | 2.5 | 460/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 6 | 460/60/3 | 11.2 | 15 | R-454B | 11 | - | 3 | 460/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 9 | 460/60/3 | 15.7 | 20 | R-454B | 11 | - | 3 | 460/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 12 | 460/60/3 | 20.2 | 25 | R-454B | 11 | - | 3 | 460/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2036A | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | - | 15 | 460/60/3 | 24.7 | 25 | R-454B | 11 | - | 3 | 460/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 6 | 460/60/3 | 12.8 | 15 | R-454B | 11 | - | 3.5 | 460/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 9 | 460/60/3 | 15.6 | 20 | R-454B | 11 | - | 3.5 | 460/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 12 | 460/60/3 | 20.1 | 25 | R-454B | 11 | - | 3.5 | 460/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2042A | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | - | 15 | 460/60/3 | 24.6 | 25 | R-454B | 11 | - | 3.5 | 460/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 6 | 460/60/3 | 14.2 | 20 | R-454B | 11 | - | 4 | 460/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 9 | 460/60/3 | 16.5 | 20 | R-454B | 11 | - | 4 | 460/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 12 | 460/60/3 | 21 | 25 | R-454B | 11 | - | 4 | 460/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2048A | 4 | 1500 | 46000 | 31000 | 2 | 95 | 80/67 | - | 15 | 460/60/3 | 25.6 | 30 | R-454B | 11 | - | 4 | 460/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 6 | 460/60/3 | 14.3 | 20 | R-454B | 11 | - | 5 | 460/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 9 | 460/60/3 | 16.5 | 20 | R-454B | 11 | - | 5 | 460/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 12 | 460/60/3 | 21 | 25 | R-454B | 11 | - | 5 | 460/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH2060A | 5 | 1800 | 54000 | 36500 | 2 | 95 | 80/67 | - | 15 | 460/60/3 | 25.6 | 30 | R-454B | 11 | - | 5 | 460/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH2072A | 6 | 2100 | 66000 | 42000 | 2 | 95 | 80/67 | - | 6 | 460/60/3 | 16.9 | 25 | R-454B | 10 | - | 6 | 460/60/3 | 2 | COOLING ONLY | 6 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH2072A | 6 | 2100 | 66000 | 42000 | 2 | 95 | 80/67 | - | 9 | 460/60/3 | 16.9 | 25 | R-454B | 10 | - | 6 | 460/60/3 | 2 | COOLING ONLY | 9 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH2072A | 6 | 2100 | 66000 | 42000 | 2 | 95 | 80/67 | - | 12 | 460/60/3 | 21.4 | 25 | R-454B | 10 | - | 6 | 460/60/3 | 2 | COOLING ONLY | 12 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MGH2072A | 6 | 2100 | 66000 | 42000 | 2 | 95 | 80/67 | - | 15 | 460/60/3 | 26 | 30 | R-454B | 10 | - | 6 | 460/60/3 | 2 | COOLING ONLY | 15 |  |  | MARVAIR MAH (COOLING ONLY) DATA SHEET | [6 empty] | MARVAIR MAH (COOLING ONLY) IOM
MARVAIR | MAH1020H | 1.66 | 800 | 20000 | 15000 | 1 | 95 | 80/67 | 20000 | 0 | 208/60/1 | 19.2 | 25 | R-454B | 11 | - | 1.66 | 208/60/1 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 0 | 208/60/1 | 21.2 | 30 | R-454B | 11 | - | 2 | 208/60/1 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 0 | 208/60/1 | 24.5 | 35 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 0 | 208/60/1 | 26 | 40 | R-454B | 11 | - | 3 | 208/60/1 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 0 | 208/60/1 | 32.7 | 50 | R-454B | 11 | - | 3.5 | 208/60/1 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 0 | 208/60/1 | 37.4 | 50 | R-454B | 11 | - | 4 | 208/60/1 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 0 | 208/60/1 | 44.3 | 60 | R-454B | 11 | - | 5 | 208/60/1 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 0 | 208/60/1 | 19.2 | 25 | R-454B | 11 | - | 2 | 208/60/1 | 2 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 0 | 208/60/1 | 25.9 | 40 | R-454B | 11 | - | 2.5 | 208/60/1 | 2 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 0 | 208/60/1 | 25.9 | 40 | R-454B | 11 | - | 3 | 208/60/1 | 2 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2042 | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | 35400 | 0 | 208/60/1 | 32.2 | 50 | R-454B | 11 | - | 3.5 | 208/60/1 | 2 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 0 | 208/60/1 | 32.3 | 50 | R-454B | 11 | - | 4 | 208/60/1 | 2 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 0 | 208/60/1 | 42.8 | 60 | R-454B | 11 | - | 5 | 208/60/1 | 2 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1020H | 1.66 | 800 | 20000 | 15000 | 1 | 95 | 80/67 | 20000 | 4 | 208/60/1 | 40 | 45 | R-454B | 11 | - | 1.66 | 208/60/1 | 1 | HEAT PUMP | 4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1020H | 1.66 | 800 | 20000 | 15000 | 1 | 95 | 80/67 | 20000 | 5 | 208/60/1 | 45.2 | 50 | R-454B | 11 | - | 1.66 | 208/60/1 | 1 | HEAT PUMP | 5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1020H | 1.66 | 800 | 20000 | 15000 | 1 | 95 | 80/67 | 20000 | 6 | 208/60/1 | 50.4 | 60 | R-454B | 11 | - | 1.66 | 208/60/1 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1020H | 1.66 | 800 | 20000 | 15000 | 1 | 95 | 80/67 | 20000 | 8 | 208/60/1 | 60.8 | 70 | R-454B | 11 | - | 1.66 | 208/60/1 | 1 | HEAT PUMP | 8 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1020H | 1.66 | 800 | 20000 | 15000 | 1 | 95 | 80/67 | 20000 | 10 | 208/60/1 | 71.3 | 80 | R-454B | 11 | - | 1.66 | 208/60/1 | 1 | HEAT PUMP | 10 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 4 | 208/60/1 | 42 | 45 | R-454B | 11 | - | 2 | 208/60/1 | 1 | HEAT PUMP | 4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 5 | 208/60/1 | 47.2 | 50 | R-454B | 11 | - | 2 | 208/60/1 | 1 | HEAT PUMP | 5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 6 | 208/60/1 | 52.4 | 60 | R-454B | 11 | - | 2 | 208/60/1 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 8 | 208/60/1 | 62.8 | 70 | R-454B | 11 | - | 2 | 208/60/1 | 1 | HEAT PUMP | 8 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 10 | 208/60/1 | 73.3 | 80 | R-454B | 11 | - | 2 | 208/60/1 | 1 | HEAT PUMP | 10 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 4 | 208/60/1 | 45.3 | 50 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | HEAT PUMP | 4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 5 | 208/60/1 | 50.5 | 60 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | HEAT PUMP | 5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 6 | 208/60/1 | 55.7 | 60 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 8 | 208/60/1 | 66.1 | 70 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | HEAT PUMP | 8 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 10 | 208/60/1 | 76.6 | 80 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | HEAT PUMP | 10 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 12 | 208/60/1 | 87 | 90 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 15 | 208/60/1 | 102.6 | 110 | R-454B | 11 | - | 2.5 | 208/60/1 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 4 | 208/60/1 | 46.8 | 50 | R-454B | 11 | - | 3 | 208/60/1 | 1 | HEAT PUMP | 4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 5 | 208/60/1 | 52 | 60 | R-454B | 11 | - | 3 | 208/60/1 | 1 | HEAT PUMP | 5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 6 | 208/60/1 | 57.2 | 60 | R-454B | 11 | - | 3 | 208/60/1 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 8 | 208/60/1 | 67.6 | 70 | R-454B | 11 | - | 3 | 208/60/1 | 1 | HEAT PUMP | 8 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 10 | 208/60/1 | 78.1 | 80 | R-454B | 11 | - | 3 | 208/60/1 | 1 | HEAT PUMP | 10 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 12 | 208/60/1 | 88.5 | 90 | R-454B | 11 | - | 3 | 208/60/1 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 15 | 208/60/1 | 104.1 | 110 | R-454B | 11 | - | 3 | 208/60/1 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 4 | 208/60/1 | 53.5 | 60 | R-454B | 11 | - | 3.5 | 208/60/1 | 1 | HEAT PUMP | 4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 5 | 208/60/1 | 58.7 | 70 | R-454B | 11 | - | 3.5 | 208/60/1 | 1 | HEAT PUMP | 5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 10 | 208/60/1 | 84.7 | 90 | R-454B | 11 | - | 3.5 | 208/60/1 | 1 | HEAT PUMP | 10 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 12 | 208/60/1 | 95.2 | 100 | R-454B | 11 | - | 3.5 | 208/60/1 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 15 | 208/60/1 | 110.8 | 125 | R-454B | 11 | - | 3.5 | 208/60/1 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 4 | 208/60/1 | 58.2 | 70 | R-454B | 11 | - | 4 | 208/60/1 | 1 | HEAT PUMP | 4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 5 | 208/60/1 | 63.4 | 80 | R-454B | 11 | - | 4 | 208/60/1 | 1 | HEAT PUMP | 5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 10 | 208/60/1 | 89.5 | 100 | R-454B | 11 | - | 4 | 208/60/1 | 1 | HEAT PUMP | 10 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 12 | 208/60/1 | 99.9 | 100 | R-454B | 11 | - | 4 | 208/60/1 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 15 | 208/60/1 | 115.5 | 125 | R-454B | 11 | - | 4 | 208/60/1 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 4 | 208/60/1 | 65.1 | 80 | R-454B | 11 | - | 5 | 208/60/1 | 1 | HEAT PUMP | 4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 5 | 208/60/1 | 70.3 | 90 | R-454B | 11 | - | 5 | 208/60/1 | 1 | HEAT PUMP | 5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 10 | 208/60/1 | 96.4 | 110 | R-454B | 11 | - | 5 | 208/60/1 | 1 | HEAT PUMP | 10 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 12 | 208/60/1 | 106.8 | 110 | R-454B | 11 | - | 5 | 208/60/1 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 15 | 208/60/1 | 122.4 | 125 | R-454B | 11 | - | 5 | 208/60/1 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 0 | 208/60/3 | 16.7 | 20 | R-454B | 11 | - | 2 | 208/60/3 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 0 | 208/60/3 | 23.6 | 35 | R-454B | 11 | - | 2.5 | 208/60/3 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 0 | 208/60/3 | 22.9 | 35 | R-454B | 11 | - | 3 | 208/60/3 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 0 | 208/60/3 | 25.4 | 35 | R-454B | 11 | - | 3.5 | 208/60/3 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 0 | 208/60/3 | 25.4 | 35 | R-454B | 11 | - | 4 | 208/60/3 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 0 | 208/60/3 | 35.6 | 50 | R-454B | 11 | - | 5 | 208/60/3 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 6 | 208/60/3 | 34.7 | 35 | R-454B | 11 | - | 2 | 208/60/3 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 9 | 208/60/3 | 43.7 | 45 | R-454B | 11 | - | 2 | 208/60/3 | 1 | HEAT PUMP | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 12 | 208/60/3 | 52.8 | 60 | R-454B | 11 | - | 2 | 208/60/3 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 15 | 208/60/3 | 61.8 | 70 | R-454B | 11 | - | 2 | 208/60/3 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 6 | 208/60/3 | 41.6 | 50 | R-454B | 11 | - | 2.5 | 208/60/3 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 9 | 208/60/3 | 50.7 | 60 | R-454B | 11 | - | 2.5 | 208/60/3 | 1 | HEAT PUMP | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 12 | 208/60/3 | 59.7 | 60 | R-454B | 11 | - | 2.5 | 208/60/3 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 15 | 208/60/3 | 68.7 | 70 | R-454B | 11 | - | 2.5 | 208/60/3 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 6 | 208/60/3 | 40.9 | 45 | R-454B | 11 | - | 3 | 208/60/3 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 9 | 208/60/3 | 49.9 | 50 | R-454B | 11 | - | 3 | 208/60/3 | 1 | HEAT PUMP | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 12 | 208/60/3 | 58.9 | 60 | R-454B | 11 | - | 3 | 208/60/3 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 15 | 208/60/3 | 68 | 70 | R-454B | 11 | - | 3 | 208/60/3 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 6 | 208/60/3 | 43.4 | 50 | R-454B | 11 | - | 3.5 | 208/60/3 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 9 | 208/60/3 | 52.5 | 60 | R-454B | 11 | - | 3.5 | 208/60/3 | 1 | HEAT PUMP | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 12 | 208/60/3 | 61.5 | 70 | R-454B | 11 | - | 3.5 | 208/60/3 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 15 | 208/60/3 | 70.5 | 80 | R-454B | 11 | - | 3.5 | 208/60/3 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 6 | 208/60/3 | 43.4 | 50 | R-454B | 11 | - | 4 | 208/60/3 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 9 | 208/60/3 | 52.5 | 60 | R-454B | 11 | - | 4 | 208/60/3 | 1 | HEAT PUMP | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 12 | 208/60/3 | 61.5 | 70 | R-454B | 11 | - | 4 | 208/60/3 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 15 | 208/60/3 | 70.5 | 80 | R-454B | 11 | - | 4 | 208/60/3 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 43.4 | 208/60/3 | 53.6 | 60 | R-454B | 11 | - | 5 | 208/60/3 | 1 | HEAT PUMP | 43.4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 52.5 | 208/60/3 | 62.6 | 70 | R-454B | 11 | - | 5 | 208/60/3 | 1 | HEAT PUMP | 52.5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 61.5 | 208/60/3 | 71.6 | 80 | R-454B | 11 | - | 5 | 208/60/3 | 1 | HEAT PUMP | 61.5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 70.5 | 208/60/3 | 80.7 | 90 | R-454B | 11 | - | 5 | 208/60/3 | 1 | HEAT PUMP | 70.5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 0 | 460/60/3 | 9.5 | 15 | R-454B | 11 | - | 2 | 460/60/3 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 0 | 460/60/3 | 10.2 | 15 | R-454B | 11 | - | 2.5 | 460/60/3 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 0 | 460/60/3 | 11.1 | 15 | R-454B | 11 | - | 3 | 460/60/3 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 0 | 460/60/3 | 12 | 15 | R-454B | 11 | - | 3.5 | 460/60/3 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 0 | 460/60/3 | 12.2 | 15 | R-454B | 11 | - | 4 | 460/60/3 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 0 | 460/60/3 | 16.5 | 20 | R-454B | 11 | - | 5 | 460/60/3 | 1 | HEAT PUMP | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 6 | 460/60/3 | 18.5 | 20 | R-454B | 11 | - | 2 | 460/60/3 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 9 | 460/60/3 | 23.1 | 25 | R-454B | 11 | - | 2 | 460/60/3 | 1 | HEAT PUMP | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 12 | 460/60/3 | 27.6 | 30 | R-454B | 11 | - | 2 | 460/60/3 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1024H | 2 | 820 | 24000 | 18600 | 1 | 95 | 80/67 | 24000 | 15 | 460/60/3 | 32.1 | 35 | R-454B | 11 | - | 2 | 460/60/3 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 6 | 460/60/3 | 19.2 | 20 | R-454B | 11 | - | 2.5 | 460/60/3 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 9 | 460/60/3 | 23.7 | 25 | R-454B | 11 | - | 2.5 | 460/60/3 | 1 | HEAT PUMP | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 12 | 460/60/3 | 28.2 | 30 | R-454B | 11 | - | 2.5 | 460/60/3 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1030H | 2.5 | 1150 | 29000 | 21500 | 1 | 95 | 80/67 | 27000 | 15 | 460/60/3 | 32.7 | 35 | R-454B | 11 | - | 2.5 | 460/60/3 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 6 | 460/60/3 | 20.1 | 25 | R-454B | 11 | - | 3 | 460/60/3 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 9 | 460/60/3 | 24.6 | 25 | R-454B | 11 | - | 3 | 460/60/3 | 1 | HEAT PUMP | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 12 | 460/60/3 | 29.1 | 30 | R-454B | 11 | - | 3 | 460/60/3 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1036H | 3 | 1200 | 35000 | 24500 | 1 | 95 | 80/67 | 30000 | 15 | 460/60/3 | 33.6 | 35 | R-454B | 11 | - | 3 | 460/60/3 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 6 | 460/60/3 | 21 | 25 | R-454B | 11 | - | 3.5 | 460/60/3 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 9 | 460/60/3 | 25.5 | 30 | R-454B | 11 | - | 3.5 | 460/60/3 | 1 | HEAT PUMP | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 12 | 460/60/3 | 30 | 30 | R-454B | 11 | - | 3.5 | 460/60/3 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1042H | 3.5 | 1350 | 42000 | 27400 | 1 | 95 | 80/67 | 35400 | 15 | 460/60/3 | 34.5 | 35 | R-454B | 11 | - | 3.5 | 460/60/3 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 6 | 460/60/3 | 21.2 | 25 | R-454B | 11 | - | 4 | 460/60/3 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 9 | 460/60/3 | 25.7 | 30 | R-454B | 11 | - | 4 | 460/60/3 | 1 | HEAT PUMP | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 12 | 460/60/3 | 30.2 | 35 | R-454B | 11 | - | 4 | 460/60/3 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1048H | 4 | 1700 | 46000 | 31000 | 1 | 95 | 80/67 | 42000 | 15 | 460/60/3 | 34.8 | 35 | R-454B | 11 | - | 4 | 460/60/3 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 6 | 460/60/3 | 25.5 | 30 | R-454B | 11 | - | 5 | 460/60/3 | 1 | HEAT PUMP | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 9 | 460/60/3 | 30.1 | 35 | R-454B | 11 | - | 5 | 460/60/3 | 1 | HEAT PUMP | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 12 | 460/60/3 | 34.6 | 35 | R-454B | 11 | - | 5 | 460/60/3 | 1 | HEAT PUMP | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH1060H | 5 | 1750 | 57000 | 36900 | 1 | 95 | 80/67 | 51000 | 15 | 460/60/3 | 39.1 | 40 | R-454B | 11 | - | 5 | 460/60/3 | 1 | HEAT PUMP | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 4 | 208/60/1 | 40 | 45 | R-454B | 11 | - | 2 | 208/60/1 | 2 |  | 4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 5 | 208/60/1 | 45.2 | 50 | R-454B | 11 | - | 2 | 208/60/1 | 2 |  | 5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 6 | 208/60/1 | 50.4 | 60 | R-454B | 11 | - | 2 | 208/60/1 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 8 | 208/60/1 | 60.8 | 70 | R-454B | 11 | - | 2 | 208/60/1 | 2 |  | 8 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 10 | 208/60/1 | 71.3 | 80 | R-454B | 11 | - | 2 | 208/60/1 | 2 |  | 10 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 4 | 208/60/1 | 46.7 | 50 | R-454B | 11 | - | 2.5 | 208/60/1 | 2 |  | 4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 5 | 208/60/1 | 51.9 | 60 | R-454B | 11 | - | 2.5 | 208/60/1 | 2 |  | 5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 6 | 208/60/1 | 57.1 | 60 | R-454B | 11 | - | 2.5 | 208/60/1 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 8 | 208/60/1 | 67.5 | 70 | R-454B | 11 | - | 2.5 | 208/60/1 | 2 |  | 8 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 10 | 208/60/1 | 77.9 | 80 | R-454B | 11 | - | 2.5 | 208/60/1 | 2 |  | 10 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 4 | 208/60/1 | 46.7 | 50 | R-454B | 11 | - | 3 | 208/60/1 | 2 |  | 4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 5 | 208/60/1 | 51.9 | 60 | R-454B | 11 | - | 3 | 208/60/1 | 2 |  | 5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 6 | 208/60/1 | 57.1 | 60 | R-454B | 11 | - | 3 | 208/60/1 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 8 | 208/60/1 | 67.5 | 70 | R-454B | 11 | - | 3 | 208/60/1 | 2 |  | 8 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 10 | 208/60/1 | 77.9 | 80 | R-454B | 11 | - | 3 | 208/60/1 | 2 |  | 10 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 4 | 208/60/1 | 53 | 60 | R-454B | 11 | - | 4 | 208/60/1 | 2 |  | 4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 5 | 208/60/1 | 58.2 | 70 | R-454B | 11 | - | 4 | 208/60/1 | 2 |  | 5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 6 | 208/60/1 | 63.4 | 70 | R-454B | 11 | - | 4 | 208/60/1 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 8 | 208/60/1 | 73.8 | 80 | R-454B | 11 | - | 4 | 208/60/1 | 2 |  | 8 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 10 | 208/60/1 | 84.2 | 90 | R-454B | 11 | - | 4 | 208/60/1 | 2 |  | 10 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 12 | 208/60/1 | 94.7 | 100 | R-454B | 11 | - | 4 | 208/60/1 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 15 | 208/60/1 | 110.3 | 125 | R-454B | 11 | - | 4 | 208/60/1 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 4 | 208/60/1 | 63.6 | 80 | R-454B | 11 | - | 5 | 208/60/1 | 2 |  | 4 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 5 | 208/60/1 | 68.8 | 80 | R-454B | 11 | - | 5 | 208/60/1 | 2 |  | 5 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 6 | 208/60/1 | 74.1 | 90 | R-454B | 11 | - | 5 | 208/60/1 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 8 | 208/60/1 | 84.5 | 100 | R-454B | 11 | - | 5 | 208/60/1 | 2 |  | 8 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 10 | 208/60/1 | 94.9 | 100 | R-454B | 11 | - | 5 | 208/60/1 | 2 |  | 10 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 12 | 208/60/1 | 105.3 | 110 | R-454B | 11 | - | 5 | 208/60/1 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 15 | 208/60/1 | 120.9 | 125 | R-454B | 11 | - | 5 | 208/60/1 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 0 | 208/60/3 | 14.2 | 20 | R-454B | 11 | - | 2 | 208/60/3 | 2 |  | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 0 | 208/60/3 | 17.5 | 25 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 |  | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 0 | 208/60/3 | 20 | 25 | R-454B | 11 | - | 3 | 208/60/3 | 2 |  | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2042 | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | 35400 | 0 | 208/60/3 | 23.8 | 35 | R-454B | 11 | - | 3.5 | 208/60/3 | 2 |  | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 0 | 208/60/3 | 24.3 | 35 | R-454B | 11 | - | 4 | 208/60/3 | 2 |  | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 0 | 208/60/3 | 28.6 | 40 | R-454B | 11 | - | 5 | 208/60/3 | 2 |  | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 6 | 208/60/3 | 32.2 | 35 | R-454B | 11 | - | 2 | 208/60/3 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 9 | 208/60/3 | 41.2 | 45 | R-454B | 11 | - | 2 | 208/60/3 | 2 |  | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 12 | 208/60/3 | 50.3 | 60 | R-454B | 11 | - | 2 | 208/60/3 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 15 | 208/60/3 | 59.3 | 60 | R-454B | 11 | - | 2 | 208/60/3 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 6 | 208/60/3 | 35.5 | 40 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 9 | 208/60/3 | 44.5 | 45 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 |  | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 12 | 208/60/3 | 53.6 | 60 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 15 | 208/60/3 | 62.6 | 70 | R-454B | 11 | - | 2.5 | 208/60/3 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 6 | 208/60/3 | 38 | 40 | R-454B | 11 | - | 3 | 208/60/3 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 9 | 208/60/3 | 47 | 50 | R-454B | 11 | - | 3 | 208/60/3 | 2 |  | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 12 | 208/60/3 | 56.1 | 60 | R-454B | 11 | - | 3 | 208/60/3 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 15 | 208/60/3 | 65.1 | 70 | R-454B | 11 | - | 3 | 208/60/3 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2042 | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | 35400 | 6 | 208/60/3 | 41.8 | 45 | R-454B | 11 | - | 3.5 | 208/60/3 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2042 | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | 35400 | 9 | 208/60/3 | 50.8 | 60 | R-454B | 11 | - | 3.5 | 208/60/3 | 2 |  | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2042 | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | 35400 | 12 | 208/60/3 | 59.9 | 60 | R-454B | 11 | - | 3.5 | 208/60/3 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2042 | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | 35400 | 15 | 208/60/3 | 68.9 | 70 | R-454B | 11 | - | 3.5 | 208/60/3 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 6 | 208/60/3 | 42.3 | 50 | R-454B | 11 | - | 4 | 208/60/3 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 9 | 208/60/3 | 51.3 | 60 | R-454B | 11 | - | 4 | 208/60/3 | 2 |  | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 12 | 208/60/3 | 60.4 | 70 | R-454B | 11 | - | 4 | 208/60/3 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 15 | 208/60/3 | 69.4 | 70 | R-454B | 11 | - | 4 | 208/60/3 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 6 | 208/60/3 | 46.6 | 50 | R-454B | 11 | - | 5 | 208/60/3 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 9 | 208/60/3 | 55.6 | 60 | R-454B | 11 | - | 5 | 208/60/3 | 2 |  | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 12 | 208/60/3 | 64.6 | 70 | R-454B | 11 | - | 5 | 208/60/3 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 15 | 208/60/3 | 73.7 | 80 | R-454B | 11 | - | 5 | 208/60/3 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 0 | 460/60/3 | 7.9 | 20 | R-454B | 11 | - | 2 | 460/60/3 | 2 |  | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 0 | 460/60/3 | 9.8 | 20 | R-454B | 11 | - | 2.5 | 460/60/3 | 2 |  | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 0 | 460/60/3 | 9.8 | 20 | R-454B | 11 | - | 3 | 460/60/3 | 2 |  | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2042 | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | 35400 | 0 | 460/60/3 | 12.8 | 25 | R-454B | 11 | - | 3.5 | 460/60/3 | 2 |  | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 0 | 460/60/3 | 13.2 | 25 | R-454B | 11 | - | 4 | 460/60/3 | 2 |  | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 0 | 460/60/3 | 14.3 | 25 | R-454B | 11 | - | 5 | 460/60/3 | 2 |  | 0 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 6 | 460/60/3 | 16.9 | 20 | R-454B | 11 | - | 2 | 460/60/3 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 9 | 460/60/3 | 21.4 | 25 | R-454B | 11 | - | 2 | 460/60/3 | 2 |  | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 12 | 460/60/3 | 25.9 | 30 | R-454B | 11 | - | 2 | 460/60/3 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2024H | 2 | 950 | 20600 | 16500 | 2 | 95 | 80/67 | 21000 | 15 | 460/60/3 | 30.5 | 35 | R-454B | 11 | - | 2 | 460/60/3 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 6 | 460/60/3 | 18.8 | 20 | R-454B | 11 | - | 2.5 | 460/60/3 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 9 | 460/60/3 | 23.3 | 25 | R-454B | 11 | - | 2.5 | 460/60/3 | 2 |  | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 12 | 460/60/3 | 27.8 | 30 | R-454B | 11 | - | 2.5 | 460/60/3 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2030H | 2.5 | 1050 | 29000 | 20300 | 2 | 95 | 80/67 | 25000 | 15 | 460/60/3 | 32.4 | 35 | R-454B | 11 | - | 2.5 | 460/60/3 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 6 | 460/60/3 | 18.8 | 20 | R-454B | 11 | - | 3 | 460/60/3 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 9 | 460/60/3 | 23.3 | 25 | R-454B | 11 | - | 3 | 460/60/3 | 2 |  | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 12 | 460/60/3 | 27.8 | 30 | R-454B | 11 | - | 3 | 460/60/3 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2036H | 3 | 1180 | 33000 | 23100 | 2 | 95 | 80/67 | 30000 | 15 | 460/60/3 | 32.4 | 35 | R-454B | 11 | - | 3 | 460/60/3 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2042 | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | 35400 | 6 | 460/60/3 | 21.8 | 25 | R-454B | 11 | - | 3.5 | 460/60/3 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2042 | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | 35400 | 9 | 460/60/3 | 26.4 | 30 | R-454B | 11 | - | 3.5 | 460/60/3 | 2 |  | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2042 | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | 35400 | 12 | 460/60/3 | 30.9 | 35 | R-454B | 11 | - | 3.5 | 460/60/3 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2042 | 3.5 | 1350 | 40000 | 27200 | 2 | 95 | 80/67 | 35400 | 15 | 460/60/3 | 35.4 | 40 | R-454B | 11 | - | 3.5 | 460/60/3 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 6 | 460/60/3 | 22.2 | 25 | R-454B | 11 | - | 4 | 460/60/3 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 9 | 460/60/3 | 26.7 | 30 | R-454B | 11 | - | 4 | 460/60/3 | 2 |  | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 12 | 460/60/3 | 31.2 | 35 | R-454B | 11 | - | 4 | 460/60/3 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2048H | 4 | 1700 | 46000 | 31000 | 2 | 95 | 80/67 | 42000 | 15 | 460/60/3 | 35.8 | 40 | R-454B | 11 | - | 4 | 460/60/3 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 6 | 460/60/3 | 23.3 | 25 | R-454B | 11 | - | 5 | 460/60/3 | 2 |  | 6 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 9 | 460/60/3 | 27.8 | 30 | R-454B | 11 | - | 5 | 460/60/3 | 2 |  | 9 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 12 | 460/60/3 | 32.3 | 35 | R-454B | 11 | - | 5 | 460/60/3 | 2 |  | 12 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM
MARVAIR | MAH2060H | 5 | 1750 | 56000 | 39200 | 2 | 95 | 80/67 | 50500 | 15 | 460/60/3 | 36.8 | 40 | R-454B | 11 | - | 5 | 460/60/3 | 2 |  | 15 |  |  | MARVAIR MAH (HEAT PUMP) DATA SHEET | [6 empty] | MARVAIR MAH (HEAT PUMP) IOM

## SCHEDULE NOTES
STANDARD OPTIONS/ACCESSORIES:
1- | Baked on finish over galvanneal steel outer panel
2- | Copper tube, aluminum fin evaporator & condenser coil
3- | High & low pressure switch
4- | Liquid line temperature monitoring & control
5- | Phase monitor (3-phase units only)
6- | Factory installed disconnect
7- | 2" MERV-8 filter
8- | Electric heat, if scheduled, shall be single point power
OPTIONAL ACCESSORIES:
1- | Factory installed economizer
2- | 2-Position motorized fresh air damper w/ pressure relief ventilation
3- | 2-Position motorized fresh air damper w/ pressure relief ventilation & independent control
5- | Coastal environmental package:
| - | Corrosion resistant fasteners
| - | Sealed or partially sealed condenser fan motor
| - | Insitu coating applied to all exposed internal copper and metal in the condenser section
| - | Protective coating on condenser coil
6- | All coat package:
| - | Corrosion resistant fasteners
| - | Sealed or partially sealed condenser fan motor
| - | Insitu coating applied to all exposed internal copper and metal in the condenser section
| - | Protective coating on condenser coil
| - | Impregnated polyurethane on evaporator coil and Insitu coating on all exterior and interior components and sheet metal
7- | Stainless steel exterior (replaces all standard exterior painted surfaces with stainless steel)
8- | Stainless steel unit (replaces all interior and exterior steel sheet metal parts with stainless steel)
9- | Fresh air damper (field installed on either the left or right hand side of the unit)